## Cover
This document is shared for the purposes of learning legacy. It is a snapshot in time and hence many of the links within the document will
become obsolete over time. Some links/document references will refer to a document storage location that isn't accessible.
Document Title: |  | Asset Naming And Labelling Convention Document
Document Number: |  | CRL1-XRL-Z3-ADDSD-CR001-50413
Document Revision: |  | 6.0
Document History
Revision: | Date: | Prepared By: | Checked By: | Authorised By: | Reason for Issue
1.0 | 2014-06-10 |  |  |  | First Issue
2.0 | 2014-11-06 |  |  |  | Additions for newly configured classes.
3.0 | 2015-09-01 |  |  |  | Simplification to Asset Naming Convention and addition of labelling guidelines and equipment naming guidance
4.0 | 2016-05-13 |  |  |  | Simplification of labelling instructions and guidance provided on naming of PFUs and FUs
5.0 | 2017-04-21 |  |  |  | General update Labelling convention clarification
6.0 | 2017-08-07 |  |  |  | General update Labelling convention clarification
This document contains proprietary information. No part of this document may be reproduced without prior written consent from the chief executive of Crossrail Ltd.

## Asset Naming Convention
|  | Asset Code (when assigning Cable to Asset) | Asset Tag Naming Information |  | Asset Tag Labelling Information
Class Name | Class Code |  | Asset Tag Naming Convention | Naming Example(s) | Asset Tag Label Required? | Asset Tag Label Instructions | Label Line 1 Convention | Label Line 2 Convention | Label Line 3 Convention | Label Line 4 Convention
Plate anchors | L112 | PLA | PLATE ANCHOR [nn] | PLATE ANCHOR 01 | No | - | - | - | - | -
Grouted anchors | L113 | GRA | GROUTED ANCHOR [nn] | GROUTED ANCHOR 01 | No | - | - | - | - | -
Sheet piles | L151 | SHP | SHEET PILE [GRID REFERENCE] | SHEET PILE BC05-BE05 | No | - | - | - | - | -
Diaphragm Walls and Slurry Walls | L152 | DSW | [DIAPHRAGM/SLURRY] WALL [GRID REFERENCE] | DIAPHRAGM WALL AB01-AB05 SLURRY WALL KF55-JT58 | No | - | - | - | - | -
Precast Concrete Retaining Units | L1531 | PCR | WALL [GRID REFERENCE] | WALL AB01-AB05 | No | - | - | - | - | -
Precast Concrete Lining Systems | L1532 | CLS | RING [nnnn] {OR} TBM RING [nnnn] | RING 0001 {OR} TBM RING 1234 | Conditional | Due to the way that bored tunnels are constructed, each ring should have its ring number temporarily applied with paint or a similar marker at the point of construction. Subsequently, permanent Asset Tag Labels should be applied to every 10th ring. The label will be applied approximately at the level of the tunnel centre line on the same side as the evacuation walkway. | Asset Tag ID | As per Asset Name | L1532-[Designer alternative ID] | -
Fabricated Metal Lining System | L1533 | MLS | RING [nnnn] | RING 0001 | Yes | Each ring in a cross passage shall be labelled, approximately at the level of the tunnel centre line | Asset Tag ID | As per Asset Name | L1533-[Designer alternative ID] | -
Sprayed Concrete Lining System | L1534 | SCO | SCL SECTION [nn] | SCL SECTION 01 | No | - | - | - | - | -
Cast In Situ Concrete Lining Systems | L1535 | CCO | CONCRETE LINING SECTION [nn] | CONCRETE LINING SECTION 01 | No | - | - | - | - | -
Gabions | L155 | GAB | GABION WALL [GRID REFERENCE] | GABION WALL AB01-AB05 | No | - | - | - | - | -
Secant Piles | L158 | SEC | SECANT PILED WALL [GRID REFERENCE] | SECANT PILED WALL BC05-BE05 | No | - | - | - | - | -
Steel Bridge Girder | L21101 | SBG | STEEL BRIDGE GIRDER [nnn] | STEEL BRIDGE GIRDER 001 | No | - | - | - | - | -
Bridge Bearings | L21109 | BDB | BRIDGE BEARING [nn] | BRIDGE BEARING 01 | Yes | The Asset Tag Label is to be affixed onto an adjacent permanent structure close to the Bridge Bearing | Asset Tag ID | As per Asset Name | L21109-[Designer alternative ID] | -
Channel Drains | L212332 | CHD | CHANNEL DRAIN [nnn] | CHANNEL DRAIN 001 | No | - | - | - | - | -
Hard Standing Road Surface/Kerbs | L21251 | RSK | [HARD STANDING ROAD SURFACE/KERB] [nnn] | HARD STANDING ROAD SURFACE 001 KERB 001 | No | - | - | - | - | -
Guardrails | L21253 | GDS | GUARDRAIL [nnn] | GUARDRAIL 001 | No | - | - | - | - | -
Baseplate | L21321 | BAS | BASEPLATE [nnnnn] | BASEPLATE 00001 | Yes | Every 10th Pair of baseplates shall be labelled. Note: If there is a change in track form between the labels the last baseplate of the form and the first baseplate of the new form shall be labelled. The exception to this is at Pudding Mill Lane/Marshgate Bridge where each baseplate shall be labelled due to the skew. | Asset Tag ID | As per Asset Name | L21321-[Designer alternative ID] | -
Sleeper | L21322 | SLE | SLEEPER [nnnnn] | SLEEPER 00001 | Yes | Sleepers will have an Asset Tag Label every tenth sleeper Note: If there is a change in track form between the labels the last sleeper of the form and the first sleeper of the new form shall be labelled. It is also recommended that a label is included on every Sateba S1 and S2 as these are limited in quantity and difficult to differentiate from the most common sleepers, the Sateba S3. It is recommended that if and when the sleepers require to be labelled with the Asset Tag Labels from assets other than the sleeper itself, the sleeper should also have a Sleeper Asset Tag Label if it is not already required. Where a Track Maintenance Access Point is present, a track sleeper asset tag label should be affixed to every sleeper. | Asset Tag ID | As per Asset Name | L21322-[Designer alternative ID] | -
Bearers | L21323 | BER | BEARER [nnnnn] | BEARER 00001 | Yes | Each Bearer to have an asset tag label adjacent to the asset. | Asset Tag ID | As per Asset Name | L21323-[Designer alternative ID] | -
Slide chairs | L21324 | SLC | SLIDE CHAIR [nnn] | SLIDE CHAIR 001 | No | Each set of Switches & Crossings (S&C) will have a unique identity as a functional unit and where the S&C is located on slab track a label for the S&C will be located at the switch toes. The components such as the slide chairs will be associated with the S&C label so no further Asset Tag Label will be required. | - | - | - | -
Rail | L21331 | RAL | RAIL [nnnn] | RAIL 0001 | Yes | Asset Tag label required where there is a change (at start and end of each section) in rail steel/section and that this will be marked on the concrete (not sleeper) on the 3rd bed either side of the weld (on ballasted track it will be placed on the 3rd sleeper). | Asset Tag ID | As per Asset Name | L21331-[Designer alternative ID] | -
Check Rail | L21333 | CRL | CHECK RAIL [nnn] | CHECK RAIL 001 | Yes | An Asset Tag Label will be attached to the track slab at the each end of the check rail. If the check rail is longer than 100m then additional Asset Tag Labels will be attached to the slab every 100m. | Asset Tag ID | As per Asset Name | L21333-[Designer alternative ID] | -
Switch Half Set | L21334 | SHS | SWITCH HALF SET [nnn] | SWITCH HALF SET 001 | Yes | An Asset Tag Label will be fixed in the Cess adjacent to the Switch Half Set. | Asset Tag ID | As per Asset Name | L21334-[Designer alternative ID] | -
Crossing | L21335 | CRX | CROSSING [nnn] | CROSSING 001 | Yes | An Asset Tag Label will be attached to the bearer closest to the nose. | Asset Tag ID | As per Asset Name | L21335-[Designer alternative ID] | -
Rail Weld | L213391 | RLW | RAIL WELD [nnnn] | RAIL WELD 0001 | No | The location of welds will vary throughout the life of the track system, therefore there is no requirement for Asset Tag labelling beyond the standardised weld marking system described below. All welds on site shall be marked with a stamp or a label at the outer side of the railhead in accordance with the industry standards. The mark shall indicate the welder reference number, the month and the year of the execution of the weld. | - | - | - | -
Rail Joints | L213392 | RLJ | RAIL JOINT [nnnn] | RAIL JOINT 0001 | Yes | Where the rail joint is installed on a slab track bed then an Asset Tag Label will be attached to the slab adjacent to the location of the rail joint. On ballasted Track the label shall be affixed to the nearest sleeper. | Asset Tag ID | As per Asset Name | L213392-[Designer alternative ID] | -
Adjustment Switches | L213393 | ADJ | ADJUSTMENT SWITCH [nnn] | ADJUSTMENT SWITCH 0001 | Yes | Where the adjustment switch is installed on a slab track bed then an Asset Tag Label will be attached to the slab adjacent to the location of the adjustment switch. Where the adjustment switch is located on ballasted track the label shall be fixed to the nearest sleeper. | Asset Tag ID | As per Asset Name | L213393-[Designer alternative ID] | -
Ballast | L21361 | BAL | BALLAST [nn] | BALLAST 01 | No | - | - | - | - | -
Standard Track Slab | L21362 | TKS | STANDARD TRACK SLAB [nn] | STANDARD TRACK SLAB 01 | Yes | It is required that each standard track slab will have an Asset Tag Label attached at each end. Each slab is labelled at the start and finish of the slab section. | Asset Tag ID | As per Asset Name | L21362-[Designer alternative ID] | -
Direct Fix Track Slab | L21363 | DFS | DIRECT FIX TRACK SLAB [nnn] | DIRECT FIX TRACK SLAB 011 | No | - | - | - | - | -
Floating Track Slab | L21364 | FTS | FLOATING TRACK SLAB [nn] | FLOATING TRACK SLAB 01 | Yes | Each floating track slab will have an Asset Tag Label attached at each end on the top surface in the centre of the four foot. | Asset Tag ID | As per Asset Name | L21364-[Designer alternative ID] | -
Floating Track Slab (Sprung) | L21365 | FTG | FLOATING TRACK SLAB (SPRUNG) [nn] | FLOATING TRACK SLAB (SPRUNG) 01 | Yes | Each floating track slab (sprung) will have an Asset Tag Label attached at each end on the top surface in the centre of the four foot. | Asset Tag ID | As per Asset Name | L21365-[Designer alternative ID] | -
Shear Key | L213661 | SHK | SHEAR KEY [nnnn] | SHEAR KEY 0012 | Yes | One Asset Tag Label to be fixed on a group of 4 shear keys (each key to be an asset tag) adjacent to the Slab Label in the 4' | Asset Tag ID | As per Asset Name | L213661-[Designer alternative ID] | -
GERB Spring Housing | L213662 | GSH | GERB SPRING HOUSING [nnn] | GERB SPRING HOUSING 012 | Yes | Each Asset Tag to have a label on the top surface of the concrete slab. | Asset Tag ID | As per Asset Name | L213662-[Designer alternative ID] | -
Braking Block Assembly | L213663 | BBA | BRAKING BLOCK ASSEMBLY [nnn] | BRAKING BLOCK ASSEMBLY 999 | Yes | Each Asset Tag to have a label on the face of the concrete upstand (Kerb) | Asset Tag ID | As per Asset Name | L213663-[Designer alternative ID] | -
Lateral Bearing Assembly | L213664 | LBA | LATERAL BEARING ASSEMBLY [nnn] | LATERAL BEARING ASSEMBLY 010 | Yes | Each Asset Tag to have a label on the face of the concrete upstand (Kerb) | Asset Tag ID | As per Asset Name | L213664-[Designer alternative ID] | -
Vertical Slab Bearing | L213665 | VSB | VERTICAL SLAB BEARING [nnn] | VERTICAL SLAB BEARING 123 | No | - | - | - | - | -
Track Drainage Catch Pit | L21371 | DCP | TRACK DRAINAGE CATCH PITS [nnn] {OR} TRACK DRAINAGE CATCH PIT [nnn] | TRACK DRAINAGE CATCH PITS 001 {OR} TRACK DRAINAGE CATCH PIT 001 | Yes | An Asset Tag will be attached to the slab adjacent to the catch pit. | Asset Tag ID | As per Asset Name | L21371-[Designer alternative ID] | -
Sump | L21372 | SUM | SUMP [nn] | SUMP 01 | Yes | An Asset Tag Label will be placed on the wall or floor next to the asset, in a visible location. | Asset Tag ID | As per Asset Name | L21372-[Designer alternative ID] | -
Rail Lubricators | L21391 | RLL | RAIL LUBRICATOR [nnnn] | RAIL LUBRICATOR 0031 | Yes | An Asset Tag Label will be fixed to slab adjacent to the lubricant distribution unit and an Asset Tag Label will be attached to tunnel wall adjacent to the lubricant reservoir. | Asset Tag ID | As per Asset Name | L21391-[Designer alternative ID] | -
Track Friction Modifiers | L21392 | TFM | TRACK FRICTION MODIFIER [nnnn] | TRACK FRICTION MODIFIER 0301 | Yes | An Asset Tag Label will be fixed to slab adjacent to the lubricant distribution unit and an Asset Tag Label will be attached to tunnel wall adjacent to the lubricant reservoir. | Asset Tag ID | As per Asset Name | L21392-[Designer alternative ID] | -
Track Maintenance Access Points (vehicular / pedestrian) | L21393 | TAP | TRACK ACCESS POINT [nnn] | TRACK ACCESS POINT 001 | Yes | For those located on slab track, a label will be attached to the slab at each end approaching the Track Maintenance Access Point (TMAP) from both east and west direcitons. For ballasted track, labels will be attached to the sleepers at each end of the access point adjacent to the panel. However in these locations, it is recommended that if the sleeper does not already require a label (i.e. as required 1 in 10 sleepers are labelled), that the sleeper have a Sleeper Asset Tag Label attached in addition to the TMAP Asset Tag Label. It is recommended that the TMAP Asset Tag Label is of size 150 x 80 mm. This will ensure it is differentiated from the Sleeper Asset Tag Labels and the Track Slab labels. | Asset Tag ID | As per Asset Name | L21393-[Designer alternative ID] | -
Train Arrestors | L21394 | TAR | TRAIN ARRESTOR [nnn] | TRAIN ARRESTOR 001 | Yes | An Asset Tag Label shall be attached to the slab track or sleepers above which the buffer stops are located. | Asset Tag ID | As per Asset Name | L21394-[Designer alternative ID] | -
Derailment containment | L21395 | DRC | DERAILMENT CONTAINMENT [nnn] | DERAILMENT CONTAINMENT 001 | Yes | An Asset Tag Label will be attached to the slab adjacent to each end of the derailment containment system. If the derailment containment is on ballasted track the Asset Tag Label will be attached to the sleepers at each end. Where the derailment containment system is longer than 100 metres, additional Asset Tag Labels will be attached to the slab or sleepers every 100 metres. For Connaught rail arrangement RfL Require one label at each end of the total length plus each joint labelled. | Asset Tag ID | As per Asset Name | L21395-[Designer alternative ID] | -
Point Heater Element | L21396 | PTH | POINT HEATER ELEMENT [nnn] | POINT HEATER ELEMENT 001 | Yes | An Asset Tag Label will be attached to the track bed adjacent to the connection from the power supply to the point heater. | Asset Tag ID | As per Asset Name | L21396-[Designer alternative ID] | -
Marker Boards | L21397 | MAB | MARKER BOARD [nnn] {OR} MARKER BOARD [xxnnn] | MARKER BOARD 001 {OR} MARKER BOARD XR359 | Yes | An Asset Tag Label will be attached to the track bed adjacent to the Marker Board. | Asset Tag ID | As per Asset Name | L21397-[Designer alternative ID] | -
Disconnection Box | L21398 | DCB | DISCONNECTION BOX [nnn] {OR} DISCONNECTION BOX [xxx/xxx] | DISCONNECTION BOX 001 {OR} DISCONNECTION BOX TWD/TEC | Yes | An Asset Tag Label shall shall be attached adjacent to the Disconnection Box on a permanennt structure. | Asset Tag ID | As per Asset Name | L21398-[Designer alternative ID] | -
Track Circuit Interrupter | L21399 | TCI | TRACK CIRCUIT INTERRUPTER [nnn] {OR} TRACK CIRCUIT INTERRUPTER [xxx/xxx - xxx/xxx] | TRACK CIRCUIT INTERRUPTER 123 {OR} TRACK CIRCUIT INTERRUPTER ABC/XYZ - FTY/MAH | Yes | An Asset Tag Label will be attached adjacent to the place where the asset is to be located. | Asset Tag ID | As per Asset Name | L21399-[Designer alternative ID] | -
Cabinet | L215611 | CAB | CABINET [nnn] {OR} CABINET [xxx/xxx - xxx/xxx] | CABINET 001 {OR} CABINET ABC/SDF - ABD/FTY | Yes | For Cabinets, the (white) Asset Tag label will be positioned at the top left corner of the cabinet door, so long as it does not obstruct operation. If this is not acceptable, the label can be positioned at the bottom left corner of the cubicle door or in a consistent position throughout. Cabinets with complex equipment in should feature a schematic of the Cabinet and associated Asset Tags and Equipment Tags within will be affixed to or adjacent to the Cabinet. See also CRL1-XRL-Z3-GUI-CR001-50071: Public Facing Labelling Guidance where asset is in public accessible area. | Asset Tag ID | As per Asset Name | L215611-[Designer alternative ID] | -
Slot Interface | L215612 | SLI | SLOT INTERFACE [nnn] | SLOT INTERFACE 001 | No | The Slot Interface will be labelled as part of the Cabinet schematic, this schematic identifies associated Asset Tags and Equipment Tags within the cabinet and will be affixed to or adjacent to the Cabinet. | - | - | - | -
COM Board | L215613 | COM | COM BOARD [nnn] | COM BOARD 001 | Yes | The COM Board will be labelled as part of the Rack schematic, this schematic identifies associated Asset Tags and Equipment Tags within the Rack and will be affixed to or adjacent to the Rack. | Asset Tag ID | As per Asset Name | L215613-[Designer alternative ID] | -
Axle Counter Evaluator Power Supply | L215614 | ACE | AXLE COUNTER POWER SUPPLY [nnn] | AXLE COUNTER POWER SUPPLY 001 | Yes | An Asset Tag Label will be attached to the Evaluator Power Supply in a way that does not interfere with its performance. | Asset Tag ID | As per Asset Name | L215614-[Designer alternative ID] | -
Axle Counter Detection Head Junction Box | L215615 | AXJ | AXLE COUNTER JUNCTION BOX [nnn] | AXLE COUNTER JUNCTION BOX 001 | Yes | An Asset Tag label will be attached adjacent to the Junction Box in a way that does not interfere with its performance. | Asset Tag ID | As per Asset Name | L215615-[Designer alternative ID] | -
Axle Counter Detection Head RSR123 | L215616 | ACD | AXLE COUNTER DETECTION HEAD [nnn] {OR} AXLE COUNTER DETECTION HEAD [xxx/xxx] | AXLE COUNTER DETECTION HEAD 001 {OR} AXLE COUNTER DETECTION HEAD [XXX/XXX] | Yes | An Asset Tag will be attached adjacent to the Sensor. | Asset Tag ID | As per Asset Name | L215616-[Designer alternative ID] | -
Point Machine | L215621 | PTM | POINT MACHINE [nnnn] | POINT MACHINE 0101 | Yes | An Asset Tag label will be attached to the point machine in a way that does not interfere with its performance. | Asset Tag ID | As per Asset Name | L215621-[Designer alternative ID] | -
Motor Module | L215622 | MMD | MOTOR MODULE [nnn] | MOTOR MODULE 001 | Yes | An Asset Tag label will be attached adjacent to the motor module. | Asset Tag ID | As per Asset Name | L215622-[Designer alternative ID] | -
Drive Module | L215623 | DMD | DRIVE MODULE [nnn] | DRIVE MODULE 001 | Yes | An Asset Tag Label will be attached adjacent to the drive module. | Asset Tag ID | As per Asset Name | L215623-[Designer alternative ID] | -
Escapement Module | L215624 | EMD | ESCAPEMENT MODULE [nnn] | ESCAPEMENT MODULE 001 | Yes | An Asset Tag Label will be attached to the Escapement Module in a way that does not interfere with its performance. | Asset Tag ID | As per Asset Name | L215624-[Designer alternative ID] | -
Control Module | L215625 | CMD | CONTROL MODULE [nnn] | CONTROL MODULE 001 | Yes | An Asset Tag label will be attached adjacent to the drive module | Asset Tag ID | As per Asset Name | L215625-[Designer alternative ID] | -
Rodding | L215626 | ROD | RODDING [nnn] | RODDING 001 | Yes | An Asset Tag Label will be attached to place where the asset is to be located in a clearly visible position that will not impede its performance. | Asset Tag ID | As per Asset Name | L215626-[Designer alternative ID] | -
Stretcher Bar | L215627 | SBR | STRETCHER BAR [nnnn] | STRETCHER BAR 0501 | No | - | - | - | - | -
Supplementary Drive | L215628 | SDR | SUPPLEMENTARY DRIVE [nnn] | SUPPLEMENTARY DRIVE 001 | Yes | An Asset Tag Label will be attached to place where the asset is to be located in a clearly visible position that will not impede its performance. | Asset Tag ID | As per Asset Name | L215628-[Designer alternative ID] | -
Supplementary detection box | L215629 | SDB | SUPPLEMENTARY DETECTION BOX [nnn] | SUPPLEMENTARY DETECTION BOX 001 | Yes | An Asset Tag Label will be attached to place where the asset is to be located in a clearly visible position that will not impede its performance. | Asset Tag ID | As per Asset Name | L215629-[Designer alternative ID] | -
Balise | L215631 | BLS | BALISE [nnn] {OR} BALISE [xxx-xxnn] | BALISE 001 {OR} BALISE BDS-EB09 | No | - | - | - | - | -
Relocatable Equipment Building | L215632 | REB | RELOCATABLE EQUIPMENT BUILDING [nn] | RELOCATABLE EQUIPMENT BUILDING 01 | Yes | Each Relocatable Equipment Building will have a unique identity. An Asset Tag Label shall be affixed to the building on the inside adjacent to the door. | Asset Tag ID | As per Asset Name | L215632-[Designer alternative ID] | -
Full Size Location Case (LOC) - 3 TFM | L215634 | FLC | LOCATION CASE [nnn] | LOCATION CASE 001 | Yes | An Asset Tag Label will be attached to the Location Case affixed to the Case on the outside of the door. | Asset Tag ID | As per Asset Name | L215634-[Designer alternative ID] | -
Location Case Bases | L215635 | LCB | LOCATION CASE BASE [nnn] | LOCATION CASE BASE 001 | Yes | An Asset Tag Label should be applied on the visible top side of the base. | Asset Tag ID | As per Asset Name | L215635-[Designer alternative ID] | -
Line Wide Overview Display (LWOD) | L215651 | LWD | LINE WIDE OVERVIEW DISPLAY [nn] | LINE WIDE OVERVIEW DISPLAY 01 | Yes | An Asset Tag label will be attached to the Rail IT Video Wall in a way that does not interfere with its performance. Where multiple screens are used to make up the Line Wide Overview Display unit a single label shall be place on the bottom left single unit to cover all screens. Each individual screen is a replaceable unit (consumable) and therefore do not require an individual Tag. | Asset Tag ID | As per Asset Name | L215651-[Designer alternative ID] | -
Signal Relays | L215653 | SRY | SIGNAL RELAY [nnn] | SIGNAL RELAY 001 | Yes | An Asset Tag label will be attached to a location adjacent to the Relay. | Asset Tag ID | As per Asset Name | L215653-[Designer alternative ID] | -
Automatic Power Control (APC) Magnets | L215654 | APC | AUTO POWER CONTROL MAGNETS [nnn] {OR} AUTO POWER CONTROL MAGNET [nnn] | AUTO POWER CONTROL MAGNETS 001 {OR} AUTO POWER CONTROL MAGNET 001 | No | - | - | - | - | -
Signal Head | L215655 | SHD | SIGNAL HEAD [nnn] | SIGNAL HEAD 001 | Yes | An Asset Tag label will be attached to the Signal Head in a way that does not interfere with its performance. | Asset Tag ID | As per Asset Name | L215655-[Designer alternative ID] | -
Current Transformers | L215656 | CTF | CURRENT TRANSFORMERS [nnn] {OR} CURRENT TRANSFORMER [nnn] | CURRENT TRANSFORMERS 001 {OR} CURRENT TRANSFORMER 001 | Yes | An Asset Tag label will be attached to the Current Transformer in a way that does not interfere with its performance. | Asset Tag ID | As per Asset Name | L215656-[Designer alternative ID] | -
Clamp sensor DC (4-20mA output) | L215657 | CSD | DC CLAMP SENSOR [nnn] | DC CLAMP SENSOR 001 | No | - | - | - | - | -
Odometer pulse generator (OPG) | L215658 | OPG | ODOMETER PULSE GENERATOR [nnn] | ODOMETER PULSE GENERATOR 001 | Yes | An Asset Tag label will be attached to the Odometer Pulse Generator in a way that does not interfere with its performance. | Asset Tag ID | As per Asset Name | L215658-[Designer alternative ID] | -
Bund Pump for transformer plinths | L217124 | BDP | BUND PUMP [nnn] | BUND PUMP 001 | Yes | An Asset Tag Label will be placed on the wall or floor next to the asset, in a visible location. | Asset Tag ID | As per Asset Name | L217124-[Designer alternative ID] | -
Pipes for sewers and drains | L21721 | PSD | SEWER PIPE [nnn] | SEWER PIPE 001 | Conditional | Multiple Asset Tag Labels will be required for pipe assets: · At each end of the asset; · Sections of pipe greater than 100m long should have labels spaced at intervals such that the maximum distance between labels is 100m unless pipes are buried, in which case they will not be labelled; · Where linear assets cross over/under each other or over/under other assets; · At points where linear assets pass through walls where they will be labelled on each side of the wall. | Asset Tag ID | As per Asset Name | L21721-[Designer alternative ID] | -
Pipe Couplings/Connectors | L21723 | PCC | PIPE COUPLING [nnnn] | PIPE COUPLING 0401 | No | - | - | - | - | -
Manhole | L217241 | MAH | MANHOLE [nnn] | MANHOLE 001 | Yes | An Asset Tag Label will not be placed on the physical item but will be placed on a permanent structure next to the item. The Asset Tag Label will be in a position that can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. In high traffic areas (pedestrian or vehicular) or circumstance where the asset is not located adjacent to a permanent structure, the Asset Tag Label is to be placed within the Manhole close to the entry/exit point and easily visable upon lifting the access cover. The positioning of the Asset Tag must not be a hazard nor affect the integrity/ongoing operation of the asset. | Asset Tag ID | As per Asset Name | L217241-[Designer alternative ID] | -
Rodding Eye | L217242 | ROE | RODDING EYE [nnn] | RODDING EYE 001 | Yes | An Asset Tag Label shall be placed adjacent to the Rodding Eye on a permanent structure wherever possible. | Asset Tag ID | As per Asset Name | L217242-[Designer alternative ID] | -
Gully Pot | L21727 | GPT | GULLY POT [nnn] | GULLY POT 001 | No | The Asset Tag Label will be placed on the Drainage System Functional Unit. | - | - | - | -
Vent Pipe | L21728 | VEP | VENT PIPE [nnn] | VENT PIPE 001 | Yes | Asset Tag Labels will not be placed on the physical item but will be placed on a permanent structure next to the item. The asset tag label will be in a position that can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L21728-[Designer alternative ID] | -
Drainage Screen | L21731 | DRS | [TRAP or SCREEN] [nnn] | TRAP 001 SCREEN 001 | Yes | Asset Tag Labels will not be placed on the physical item but will be placed on a permanent structure next to the item. The asset tag label will be in a position that can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L21731-[Designer alternative ID] | -
Traps | L21734 | TRP | TRAP [nnn] | TRAP 001 | No | The Asset Tag Label will not be placed on the physical item but will be placed on the drainage system. | - | - | - | -
Complete Masts | L21831 | CPM | MAST [nnn] | MAST 001 | Yes | An Asset Tag Label will be attached to the mast foundation in a location where it can be viewed from a position of safety and where it will not be obscured by the mast itself or any other equipment. | Asset Tag ID | As per Asset Name | L21831-[Designer alternative ID] | -
Lighting columns & Masts | L21833 | LCS | LIGHTING COLUMN [nnn] | LIGHTING COLUMN [nnn] | Yes | The Asset Tag Label shall be placed in the mast hatch itself | Asset Tag ID | As per Asset Name | L21833-[Designer alternative ID] | -
Two Track Cantilever (TTC) | L21851 | TTC | TWO TRACK CANTILEVER [nnn] | TWO TRACK CANTILEVER 001 | Yes | An Asset Tag Label should be attached at the base or foundation of the asset. It should be located in an easily accessible position, visible from the ground. | Asset Tag ID | As per Asset Name | L21851-[Designer alternative ID] | -
Cantilever Tube (and Fastenings) | L21852 | CTB | CANTILEVER TUBE (AND FASTENINGS) [nnn] | CANTILEVER TUBE (AND FASTENINGS) 123 | Yes | An Asset Tag label should be attached at the base or foundation of the corresponding support asset e.g. the Two Track Cantilever. It should be located in an easily accessible position, visible from the ground. | Asset Tag ID | As per Asset Name | L21852-[Designer alternative ID] | -
Portal structure | L2186 | PTS | PORTAL STRUCTURE [nnn] | PORTAL STRUCTURE 002 | Yes | An Asset Tag label will be attached to both feet of the portal structure at points that are easily visible and safe. | Asset Tag ID | As per Asset Name | L2186-[Designer alternative ID] | -
Drainage Tank (Separator/Attenuation) | L21913 | DGT | DRAINAGE TANK [nnn] | DRAINAGE TANK 001 | Yes | An Asset Tag Label will not be placed on the physical item but will be placed on a permanent structure next to the item. The Asset Tag Label will be in a position that can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L21913-[Designer alternative ID] | -
Pad foundations | L311 | PDF | PAD FOUNDATION [GRID REFERENCE] | PAD FOUNDATION AX34-AY42 | No | - | - | - | - | -
Raft foundations | L312 | RFF | RAFT FOUNDATION [GRID REFERENCE] | RAFT FOUNDATION AX34-AY36 | No | - | - | - | - | -
Driven Cast In Place Piles | L31411 | CPP | DRIVEN CAST IN PLACE PILES - GROUP [x] | DRIVEN CAST IN PLACE PILES - GROUP A | No | - | - | - | - | -
Precast Piles | L31412 | PRP | PRECAST PILES - GROUP [x] | PRECAST PILES - GROUP A | No | - | - | - | - | -
Steel piles | L31413 | STP | STEEL PILES - GROUP [x] | STEEL PILES - GROUP A | No | - | - | - | - | -
Columns bases | L316 | CLB | COLUMN BASE [GRID] | COLUMN BASE AB05 | No | - | - | - | - | -
Masonry Structure | L328 | MAS | [WALL/ARCH/SHAFT] [GRID START-GRID END] | WALL TH15-WA11 ARCH DC32-DC34 SHAFT ER45-EV50 | No | - | - | - | - | -
Beam (Cast in situ) | L3311 | BEM | [LEVEL] BEAM [GRID START-GRID END] | L3 BEAM BB07-BB09 | No | - | - | - | - | -
Column (Cast in situ) | L3312 | COL | [LEVEL] COLUMN [GRID] | L3 COLUMN AB05 | No | - | - | - | - | -
Wall (Cast in situ) | L3313 | WAL | [LEVEL] WALL [GRID START-GRID END] | L3 WALL CB07-CB09 | No | - | - | - | - | -
Slab (Cast in situ) | L3314 | SLA | [LEVEL] SLAB [GRID FOR NOTIONAL CENTRE OF SLAB] {OR} TRACK BASE SLAB [nnn] | L4 SLAB CB07 {OR} TRACK SLAB BASE 123 | No | - | - | - | - | -
Complete concrete frames | L341 | CCF | [LEVEL] COMPLETE CONCRETE FRAME [GRID START-GRID END] | L2 COMPLETE CONCRETE FRAME BB07-BB09 | No | - | - | - | - | -
Slab Pre Cast | L3421 | SPC | [LEVEL] SLAB [GRID FOR NOTIONAL CENTRE OF SLAB] | L4 SLAB CB07 | No | - | - | - | - | -
Beam Pre Cast | L3431 | BPC | [LEVEL] BEAM [GRID START-GRID END] | L3 BEAM BB07-BB09 | No | - | - | - | - | -
Column Pre Cast | L3432 | CPC | [LEVEL] COLUMN [GRID] | L3 COLUMN AB05 | No | - | - | - | - | -
Props | L3433 | PRO | PROP [GRID START-GRID END] | PROP BB07-BB09 | No | - | - | - | - | -
Complete Frames (Metal) | L351 | CFM | COMPLETE FRAMES (METAL) [GRID START-GRID END] {OR} COMPLETE FRAME (METAL) [GRID START-GRID END] | COMPLETE FRAMES (METAL) BB07-BB09 {OR} COMPLETE FRAME (METAL) BB07-BB09 | No | - | - | - | - | -
Castellated sections | L3521 | CTS | CASTELLATED SECTION [GRID START-GRID END] | CASTELLATED SECTION BB07-BB09 | No | - | - | - | - | -
Curved sections | L3522 | CVS | CURVED SECTION [GRID START-GRID END] | CURVED SECTION BB07-BB09 | No | - | - | - | - | -
Trusses | L3523 | TSS | TRUSS [GRID START-GRID END] | TRUSS BB07-BB09 | No | - | - | - | - | -
Lattice joists | L3524 | LCJ | LATTICE JOIST [GRID START-GRID END] | LATTICE JOIST BB07-BB09 | No | - | - | - | - | -
Space frames/decks | L3525 | SFD | SPACE FRAMES/DECKS [GRID FOR NOTIONAL CENTRE OF SPACE FRAME/DECK] {OR} SPACE FRAME/DECK [GRID FOR NOTIONAL CENTRE OF SPACE FRAME/DECK] | SPACE FRAMES/DECKS CB07 {OR} SPACE FRAME/DECK CB07 | No | - | - | - | - | -
Steel Columns | L3541 | STC | [LEVEL] – COLUMN [GRID REFERENCE] | L1 – COLUMN AC05 | No | - | - | - | - | -
Steel Beams | L3542 | STB | [LEVEL] – BEAM [GRID REFERENCE] | L1 – BEAM AC05 | No | - | - | - | - | -
Curtain walls | L3811 | CTW | CURTAIN WALL [GRID REFERENCE] | CURTAIN WALL AC05-AE05 | No | - | - | - | - | -
Roof | L3826 | ROO | ROOF [nnn] | ROOF 001 | No | - | - | - | - | -
Partitions Non Structural Internal Walls | L384 | PSW | PARTITION WALL [GRID REFERENCE] | PARTITION WALL AC05-AE05 | No | - | - | - | - | -
Access floors | L386 | ACF | ACCESS FLOOR [GRID FOR NOTIONAL CENTRE OF SLAB] | ACCESS FLOOR AB62 | No | - | - | - | - | -
Suspended ceilings | L387 | SSC | SUSPENDED CEILING [nnn] | SUSPENDED CEILING 001 | No | - | - | - | - | -
Door Side Hung | L41101 | DSH | DOOR [nnn] {OR} DOOR [nnn][A or B] | DOOR 001 {OR} DOOR 123A | Yes | An Asset Tag Label should be applied on each side of a door, approximately 1800mm from floor level and in the approximate mid-point of the door. Where this location is not possible ie blocked for a safety critical label, then the contractor should use best endeavours to locate the label in a visible position and consistently across all such instances throughout the facility ie adjacent to hinge side of door ay 1800mm from floor level. | Asset Tag ID | As per Asset Name | L41101-[Designer alternative ID] | -
Door Revolving | L41102 | DRV | DOOR [nnn] | DOOR 001 | Yes | An Asset Tag label should be applied to the outer canopy of the door above each entry point. | Asset Tag ID | As per Asset Name | L41102-[Designer alternative ID] | -
Door Sliding | L41103 | DSD | DOOR [nnn] | DOOR 001 | Yes | An Asset Tag Label should be applied on each side of a door, approximately 1800mm from floor level and in the approximate mid-point of the door. | Asset Tag ID | As per Asset Name | L41103-[Designer alternative ID] | -
Door Sliding/Folding | L41104 | DSF | DOOR [nnn] | DOOR 001 | Yes | An Asset Tag Label should be applied on each side of a door, approximately 1800mm from floor level and in the approximate mid-point of the door. | Asset Tag ID | As per Asset Name | L41104-[Designer alternative ID] | -
Automatic Sliding Doors | L41109 | ASD | DOOR [nnn] {OR} AUTOMATIC SLIDING DOOR [nnn][A or B] | DOOR 001 {OR} AUTOMATIC SLIDING DOOR 001A | Yes | This Asset will have an Asset Tag Label attached adjacent to the physical item but shall not impair performance of the asset. | Asset Tag ID | As per Asset Name | L41109-[Designer alternative ID] | -
Controlled Environment Door | L41123 | CED | DOOR [nnn] | DOOR 001 | Yes | Asset Tag Labels will be placed on the wall by the frame of the controlled environment door. They will be placed in a position that can be viewed without the need for specialist access equipment and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L41123-[Designer alternative ID] | -
Platform Screen Doors | L41126 | PED | PLATFORM SCREEN DOOR [nn] | PLATFORM SCREEN DOOR 01 | No | This Asset Class does not require its own asset tag label. Each Platform Screen Door and associated assembly and panels will be identified with a functional unit label to reduce the number of labels in the passenger areas. This component will be associated with the Platform Screen Door functional unit. | - | - | - | -
Emergency Egress Doors (EED) | L41127 | EED | EMERGENCY EGRESS DOOR [nn] | EMERGENCY EGRESS DOOR 01 | No | This Asset Class does not require its own asset tag label. Each Platform edge door and associated assembly and panels will be identified with a functional unit label to reduce the number of labels in the passenger areas. This component will be associated with the Platform Edge Door functional unit. | - | - | - | -
Hatches | L412 | HAT | HATCH [nnn] | HATCH 001 | Yes | A hatch will normally have a label for the Asset Tag attached to the physical item on the outer face of the opening section, in a position that shall not impair performance of the hatch. Exceptions may be made for hatches in public facing areas or floor hatches, where the label should be placed on the inside face of the hatch. For hatches located on track slab, an asset tag label to be fixed centrally above the hatch on the concrete. See also CRL1-XRL-Z3-GUI-CR001-50071: Public Facing Labelling Guidance where asset is in public accessible area. | Asset Tag ID | As per Asset Name | L412-[Designer alternative ID] | -
Louvres | L41311 | LVS | LOUVRE [nnn] | LOUVRE 001 | Yes | A Louvre will have only an Asset Tag Label attached adjacent to the physical item but in a position that shall not impair performance of the Louvre. | Asset Tag ID | As per Asset Name | L41311-[Designer alternative ID] | -
Windows | L41312 | WDW | WINDOW [nnn] | WINDOW 001 | No | - | Asset Tag ID | As per Asset Name | L41312-[Designer alternative ID] | -
Rooflights | L414 | RFS | ROOFLIGHT [nnn] | ROOFLIGHT 001 | Yes | A rooflight will have only a label for the Asset Tag attached to the physical item on the frame but shall not impair performance of the rooflight. | Asset Tag ID | As per Asset Name | L414-[Designer alternative ID] | -
Door Sliding Mechanisms | L417 | DSM | DOOR SLIDING MECHANISM [nnn] | DOOR SLIDING MECHANISM 001 | Yes | A door sliding mechanism will have an Asset Tag Label attached adjacent to the physical item but shall not impair performance of the sliding mechanism. | Asset Tag ID | As per Asset Name | L417-[Designer alternative ID] | -
Door openers | L41811 | DRO | DOOR OPENER [nnn] | DOOR OPENER 001 | Yes | An Asset Tag Label to identify the door opener shall be attached to the door below the opener | Asset Tag ID | As per Asset Name | L41811-[Designer alternative ID] | -
Manual handle (on trackside) | L418131 | MHT | MANUAL HANDLE [nnn] | MANUAL HANDLE 001 | Yes | A Manual handle will have an Asset Tag Label attached adjacent to the physical item but shall not impair performance of the handle. | Asset Tag ID | As per Asset Name | L418131-[Designer alternative ID] | -
Platform Screen Door Frames | L41814 | PSF | PLATFORM SCREEN DOOR FRAME [nn] | PLATFORM SCREEN DOOR FRAME 01 | No | Each Platform screen door and associated assembly and panels will be identified with a functional unit label to reduce the number of labels in the passenger areas. The function label will be placed above each door. This component will be associated with the Platform Screen Door functional unit, and therefore does not require its own asset tag label. | - | - | - | -
Magnetic Door Holder | L41815 | MDH | MAGNETIC DOOR HOLDER [nnn] | MAGNETIC DOOR HOLDER 001 | Yes | An Asset Tag Label will be attached adjacent to the place where the asset is to be located. | Asset Tag ID | As per Asset Name | L41815-[Designer alternative ID] | -
Automatic Door Locking System Mechanism | L4181841 | ADL | AUTO DOOR LOCKING MECHANISM [nn] | AUTO DOOR LOCKING MECHANISM 01 | No | A schematic with the Asset Tag will identify the required location of the asset. | - | - | - | -
Manual Door Lock | L418187 | MDL | MANUAL DOOR LOCK [nn] | MANUAL DOOR LOCK 01 | No | This Asset Class does not require its own asset tag label. Each Platform edge door and associated assembly and panels will be identified with a functional unit label to reduce the number of labels in the passenger areas. This component will be associated with the Platform Edge Door functional unit. | - | - | - | -
Grilles - Security Bars - Meshes | L4242 | GSB | [GRILLES or SECURITY BARS or MESH] [nnn] {OR} PES GRILLE [UPPER or LOWER] [n or nA or nB] | GRILLES 001 MESH 001 SECURITY BARS 001 {OR} PES GRILLE UPPER 1A PES GRILLE LOWER 2 | No | - | Asset Tag ID | As per Asset Name | L4242-[Designer alternative ID] | -
Ramp | L4311 | RMP | RAMP [nnn] | RAMP 001 | Yes | An Asset Tag label shall be placed on the ground at one end of the ramp if it is up to 5 meters long and on both ends of the ramp if it is more than 5 meters long. | Asset Tag ID | As per Asset Name | L4311-[Designer alternative ID] | -
Walkway | L43121 | WKW | WALKWAY [nnn] | WALKWAY 001 | Yes | An Asset Tag Label will be placed at each end of the Walkway | Asset Tag ID | As per Asset Name | L43121-[Designer alternative ID] | -
Access ladders | L43211 | ACL | ACCESS LADDER [nnn] | ACCESS LADDER 001 | Yes | Asset Tag Label to be affixed at the bottom of the ladder on the right hand edge approximately 1.5m off the ground or start of the ladder. | Asset Tag ID | As per Asset Name | L43211-[Designer alternative ID] | -
Straight stairs | L43221 | STS | STAIRWAY [nnn] | STAIRWAY 001 | No | - | - | - | - | -
Security Fence Around Sites (Palisade) | L4411 | SFP | SECURITY FENCE [nnn] | SECURITY FENCE 001 | No | - | - | - | - | -
Barrier Gates | L4412 | BGS | BARRIER GATES [nnn] {OR} BARRIER GATE [nnn] | BARRIER GATES 001 {OR} BARRIER GATE 001 | Yes | An Asset Tag Label will be attached to place where the asset is to be located in a clearly visible location that will not impede its performance. See also CRL1-XRL-Z3-GUI-CR001-50071: Public Facing Labelling Guidance where asset is in public accessible area. | Asset Tag ID | As per Asset Name | L4412-[Designer alternative ID] | -
Wire Mesh Fencing | L4413 | WMF | WIRE MESH FENCING [nnn] | WIRE MESH FENCING 001 | No | - | - | - | - | -
Barriers Handrail | L4422 | BHR | HANDRAIL [nnn] | HANDRAIL 001 | No | - | - | - | - | -
Belt Barriers | L4423 | BEB | BELT BARRIER [nnn] | BELT BARRIER 001 | No | - | - | - | - | -
Fall Protection System | L4424 | FPS | FALL PROTECTION [nnn] | FALL PROTECTION 001 | Yes | An Asset Tag Label shall be fixed to an adjacent permanent structure. | Asset Tag ID | As per Asset Name | L4424-[Designer alternative ID] | -
Flood Barrier | L445 | FLB | FLOOD BARRIER [nn] | FLOOD BARRIER 01 | Conditional | Flood Barriers are only require an asset tag label to be where they consist of removable equipment items (i.e. not Concrete Walls). The Asset Tag Label will be placed on a permanent structure adjacent to the position where the Barrier is to be erected/located in Flood conditions. The Asset Tag Label must be easily viewable without the need for specialist access equipment or railway possessions. | Asset Tag ID | As per Asset Name | L445-[Designer alternative ID] | -
Sluice Gate | L446 | SLG | SLUICE GATE [nnn] | SLUICE GATE 001 | Yes | An Asset Tag Label shall be fixed to an adjacent permanent structure. | Asset Tag ID | As per Asset Name | L446-[Designer alternative ID] | -
Ticket Barriers | L453 | TKB | TICKET BARRIER [nn] | TICKET BARRIER 01 | Yes | An Asset Tag Label is required to cover each Barrier, each is required to be numbered sequently to identify its sequence in the run. | Asset Tag ID | As per Asset Name | L453-[Designer alternative ID] | -
Gate Line Attendance Point (GLA) | L455 | GLA | GATE LINE ATTENDANCE POINT [n] | GATE LINE ATTENDANCE POINT 1 | Yes | An Asset Tag Label will be attached to place where the asset is to be located in a clearly visible position that will not impede its performance.. | Asset Tag ID | As per Asset Name | L455-[Designer alternative ID] | -
Wall cladding sections | L511 | WCS | WALL CLADDING [nnn] | WALL CLADDING 001 | No | - | - | - | - | -
Fixed Panels | L5132 | FXP | FIXED PANEL [nn] | FIXED PANEL 01 | No | This Asset Class does not require its own asset tag label. Each Platform edge door and associated assembly and panels will be identified with a functional unit label to reduce the number of labels in the passenger areas. This component will be associated with the Platform Edge Door functional unit. | - | - | - | -
Wall coverings | L515 | WCV | WALL COVERING [nnn] | WALL COVERING 001 | No | It is not expected that Wall Coverings will have a label attached. | - | - | - | -
Roof membranes | L524 | RFM | ROOF MEMBRANE [nn] | ROOF MEMBRANE 01 | No | It is not expected that Roof membrane assets will require labels to be applied. | - | - | - | -
Green Roof | L528 | GRF | GREEN ROOF [nn] | GREEN ROOF 01 | No | It is not expected that Green Roof assets will require labels to be applied. | - | - | - | -
Pavings | L534 | PVG | PAVING ZONE [nnn] | PAVING ZONE 001 | No | It is not expected that pavings will have a label attached. | - | - | - | -
Floor Screed | L535 | FLS | FLOOR SCREED [nnn] | FLOOR SCREED 001 | No | It is not expected that screed flooring will have a label attached to it. | - | - | - | -
Floor Covering Sheets Flexible Sheets | L536 | FCS | FLOOR COVERING [nnn] | FLOOR COVERING 001 | No | It is not expected that Floor Covering assets will require labels to be applied. | - | - | - | -
Anti-Vibration Mounts | L539121 | AVM | ANTI-VIBRATION MOUNT [nnn] | ANTI-VIBRATION MOUNT 001 | No | This Asset Class does not require its own asset tag label. Each Platform edge door and associated assembly and panels will be identified with a functional unit label to reduce the number of labels in the passenger areas. This component will be associated with the Platform Edge Door functional unit. | - | - | - | -
Hollow sections | L65123 | HWS | HOLLOW SECTION [nnn] | HOLLOW SECTION 001 | No | - | - | - | - | -
Light Alloy Sections | L6513 | LAS | LIGHT ALLOY SECTION [nnn] | LIGHT ALLOY SECTION 001 | No | - | - | - | - | -
Plastic sections | L6514 | PCS | PLASTIC SECTION [nnn] | PLASTIC SECTION 001 | No | - | - | - | - | -
Architectural glass | L661313 | AGS | GLASS PANEL [nnn] | GLASS PANEL 001 | No | - | - | - | - | -
Sheet Floor Grating | L661411 | SFG | FLOOR GRATING (STEEL/PLASTIC) [nnn] | FLOOR GRATING (STEEL/PLASTIC) 001 | No | - | - | - | - | -
Sheet Steel | L661414 | SST | SHEET STEEL [nnn] | SHEET STEEL 001 | No | - | - | - | - | -
Fire Stopping Insulations | L681141 | FSI | FIRE STOPPING INSULATION [nnn] | FIRE STOPPING INSULATION 001 | Yes | Fire stopping insulations will have one set of Asset Tag Labels that should be provided on both sides of the stopping/both sides of the penetration in the compartment which the stopping is installed in. | Asset Tag ID | As per Asset Name | L681141-[Designer alternative ID] | -
Fire Collars | L681142 | FCO | FIRE COLLAR [nnn] | FIRE COLLAR 001 | Yes | Fire collars will have one set of Asset Tag Labels will not be placed on the physical item but will be placed on a permanent structure next to the item in a position that can be can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. If an asset is inaccessible, or would be impractical to label directly, for example, a pump in a wet well, a fan inside ducting, a sensor behind cladding etc. Then the Asset Tag label should be attached at the nearest adjacent point where it is unambiguous which asset is being referred to, for example: • Adjacent to the collar on the wall or ceiling, | Asset Tag ID | As per Asset Name | L681142-[Designer alternative ID] | -
Multi Cable Transits | L681143 | MCT | MULTI CABLE TRANSIT [nnn] | MULTI CABLE TRANSIT 001 | Yes | Multi Cable Transits will have one set of Asset Tag Labels. Labels will be attached to the wall or bulkhead adjacent to the transit. | Asset Tag ID | As per Asset Name | L681143-[Designer alternative ID] | -
Anti-pigeon Wires/Netting | L68621 | APW | ANTI-PIGEON DETERRENT [nnn] | ANTI-PIGEON DETERRENT 001 | No | A schematic with the asset tag will identify the required location of the asset. | - | - | - | -
Heating/Cooling Packaged Pressurisation Units | L71112 | HPU | PACKAGED PRESSURISATION UNIT [nnn] | PACKAGED PRESSURISATION UNIT 001 | Yes | Packaged plumbing units will have an Asset Tag Label placed on a permanent structure next to the item in a position that can be can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L71112-[Designer alternative ID] | -
Cylinders | L711222 | CYL | CYLINDER [nnn] | CYLINDER 001 | Yes | Cylinders will have an Asset Tag Label placed on a permanent structure next to the item in a position that can be can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L711222-[Designer alternative ID] | -
Supply Water Tanks | L711223 | WTK | SUPPLY WATER TANK [nnn] | SUPPLY WATER TANK 001 | Yes | Supply water tanks will have an Asset Tag Label attached to their plinth or on the wall adjacent to the tank. | Asset Tag ID | As per Asset Name | L711223-[Designer alternative ID] | -
Calorifiers | L71133 | CAL | CALORIFIER [nnn] | CALORIFIER 001 | Yes | An Asset Tag Labels will be placed on a permanent structure next to the item in a position that can be can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L71133-[Designer alternative ID] | -
Instantaneous water heaters | L71134 | IWH | WATER HEATER [nnn] | WATER HEATER 001 | Yes | An Asset Tag Labels will be placed on a permanent structure next to the item in a position that can be can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L71134-[Designer alternative ID] | -
Expansion Vessel | L711353 | EXV | EXPANSION VESSEL [nnn] | EXPANSION VESSEL 001 | Yes | An Asset Tag Labels will be placed on a permanent structure next to the item in a position that can be can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L711353-[Designer alternative ID] | -
Pump Controls | L71147 | PCL | PUMP CONTROLS [nnn] {OR} PUMP CONTROL [nnn] | PUMP CONTROLS 001 {OR} PUMP CONTROL 001 | Yes | An Asset Tag Labels will be placed on a permanent structure next to the item in a position that can be can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L71147-[Designer alternative ID] | -
Guide rails | L711481 | GUR | GUIDE RAILS [nn] {OR} GUIDE RAIL [nn] | GUIDE RAILS 01 {OR} GUIDE RAIL 01 | Yes | Guide rails will have only an Asset Tag Label attached near to the physical item but shall not impair performance of the Equipment. The label should be viewable without entering the sump. This is because this asset is not expected to be a regularly serviced asset and it is not expected to be regularly removed or moved. | Asset Tag ID | As per Asset Name | L711481-[Designer alternative ID] | -
Lifting beam | L711482 | LTB | LIFTING BEAM [nn] | LIFTING BEAM 01 | Yes | Lifting beams will have only an Asset Tag Labels attached to the physical item but in a position that shall not impair performance of the Equipment. This is because this asset is not expected to be a regularly serviced asset and it is not expected to be regularly removed or moved. | Asset Tag ID | As per Asset Name | L711482-[Designer alternative ID] | -
Winch | L711483 | WIN | WINCH [nnn] | WINCH 002 | Yes | Winches will have an Asset Tag Label attached to the permanent structure on which it is mounted where it is easily visible. | Asset Tag ID | As per Asset Name | L711483-[Designer alternative ID] | -
Jib and Davit Cranes | L711485 | JDC | JIB CRANE [nnn] | JIB CRANE 002 | Yes | An Asset Tag will be placed on the foot of the jib crane, at a point of safety which will be easily accessible and visible for the maintainer. | Asset Tag ID | As per Asset Name | L711485-[Designer alternative ID] | -
Water Softeners Conditioners | L71152 | WSC | WATER [SOFTENER or CONDITIONER] [nnn] | WATER SOFTENER 001 WATER CONDITIONER 001 | Yes | Water softeners/conditioners will have an Asset Tag Label not placed on the physical item but will be placed on a permanent structure next to the item in a position that can be can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L71152-[Designer alternative ID] | -
Supply pipes | L71162 | SPP | SUPPLY PIPE [nnnn] | SUPPLY PIPE 0011 | Yes | Each pipe’s purpose will be identified in accordance with British Standard 1710 with an asset label adjacent to the BS identification marking. Multiple Asset Tag Labels will be required for pipe assets: · At each end of the asset; · Sections of pipe greater than 100m long should have labels spaced at intervals such that the maximum distance between labels is 100m; · Where linear assets cross over/under each other or over/under other assets; · At points where linear assets pass through walls where they will be labelled on each side of the wall. | Asset Tag ID | As per Asset Name | L71162-[Designer alternative ID] | -
Expansion Joints And Compensators | L71164 | EJC | EXPANSION JOINT [nnn] | EXPANSION JOINT 001 | Yes | Asset Tag Label not to be placed on the physical item but will be placed on a permanent structure next to the item. The Asset Tag Label will be in a position that can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L71164-[Designer alternative ID] | -
Geothermal Loops | L71167 | GLP | GEOTHERMAL LOOP [nnn] | GEOTHERMAL LOOP 001 | No | - | - | - | - | -
Water meters | L7118 | WMT | WATER METER [nnn] | WATER METER 002 | Yes | Asset Tag Label not to be placed on the physical item but will be placed on a permanent structure next to the item. The Asset Tag Label will be in a position that can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L7118-[Designer alternative ID] | -
Gaseous fire suppression | L7162 | GFS | GASEOUS FIRE SUPPRESSION [nnn] | GASEOUS FIRE SUPPRESSION 002 | Yes | Gaseous fire suppression will have only an Asset Tag Label attached to the physical item but in a position that shall not impair performance of the equipment. This is because it is not expected to be regularly removed or moved. | Asset Tag ID | As per Asset Name | L7162-[Designer alternative ID] | -
Water mist (fine water spray) | L7164 | WMS | WATER MIST [nnn] | WATER MIST 002 | Yes | Asset Tag Label not to be placed on the physical item but will be placed on a permanent structure next to the item. The Asset Tag Label will be in a position that can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L7164-[Designer alternative ID] | -
Fire sprinklers | L7165 | FSS | FIRE SPRINKLER [nnn] | FIRE SPRINKLER 002 | Yes | Fire sprinklers will have only an Asset Tag Label attached to the physical item but in a position that shall not impair performance of the equipment. This is because this asset is not expected to be a regularly serviced asset and it is not expected to be regularly removed or moved. | Asset Tag ID | As per Asset Name | L7165-[Designer alternative ID] | -
Fire hydrants | L71671 | FHS | FIRE HYDRANT [nnn] | FIRE HYDRANT 002 | Yes | Fire hydrants will have an Asset Tag Label attached to the structure on which it is mounted where it is easily visible. See also CRL1-XRL-Z3-GUI-CR001-50071: Public Facing Labeling Guidance where asset is in public accessible area. | Asset Tag ID | As per Asset Name | L71671-[Designer alternative ID] | -
Riser pipe work | L71675 | RPW | RISER PIPEWORK [nnn] | RISER PIPEWORK 001 | Yes | Multiple Asset Tag Labels will be required for pipe assets: · At each end of the asset; · Sections of pipe greater than 100m long should have labels spaced at intervals such that the maximum distance between labels is 100m unless pipes are buried, in which case they will not be labelled; · Where linear assets cross over/under each other or over/under other assets; · At points where linear assets pass through walls where they will be labelled on each side of the wall. | Asset Tag ID | As per Asset Name | L71675-[Designer alternative ID] | -
Breeching inlets | L71676 | BRI | BREECHING INLET [nnn] | BREECHING INLET 002 | Yes | Breeching inlets will have an Asset Tag Label attached to the structure on which it is mounted where it is easily visible. | Asset Tag ID | As per Asset Name | L71676-[Designer alternative ID] | -
Pressure Gauge | L71677 | PRG | PRESSURE GAUGE [nnn] | PRESSURE GAUGE 007 | Yes | An Asset Tag Label will be attached adjacent to the place where the asset is to be located. | Asset Tag ID | As per Asset Name | L71677-[Designer alternative ID] | -
Pressure Switch | L71678 | PRS | PRESSURE SWITCH [nnn] | PRESSURE SWITCH 007 | Yes | An Asset Tag Label will be attached adjacent to the place where the asset is to be located. | Asset Tag ID | As per Asset Name | L71678-[Designer alternative ID] | -
Pumps | L7171 | PPS | PUMP [nnn] - [PUMP TYPE] | PUMP 002 - SEWAGE PUMP 003 - CHILLED WATER | Yes | Pumps will have an Asset Tag Label placed not on the physical item but will be placed on a permanent structure next to the item in a position that can be can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L7171-[Designer alternative ID] | -
Valves | L7172 | VLV | VALVE [nnn] | VALVE 001 | Conditional | Valves will have an Asset Tag attached to the physical item but in a position that shall not impair performance of the asset. Valves used for the isolation of end equipment are not required to be labelled (eg 15mm isolation valves under a sink). Within plant rooms Valves should have a number tag attached that correspnds to the wall mounted schematic system drawings | Asset Tag ID | As per Asset Name | L7172-[Designer alternative ID] | -
Services Sanitary equipment | L721 | SSE | [SANITARY EQUIPMENT TYPE] [nn] | TOILET 01 SINK 01 | No | - | - | - | - | -
Messroom Equipment | L726 | MRE | [MESSROOM EQUIPMENT TYPE] [nn] | FRIDGE 01 MICROWAVE 01 | Yes | Messroom Equipment will only have an Asset Tag Label attached to the physical asset. | Asset Tag ID | As per Asset Name | L726-[Designer alternative ID] | -
Complete pipe/guttering systems | L73141 | CPG | PIPE/GUTTERING SYSTEM [nnn] | PIPE/GUTTERING SYSTEM 002 | Yes | Multiple Asset Tag Labels will be required for pipe assets: · At each end of the asset; · Sections of pipe greater than 100m long should have labels spaced at intervals such that the maximum distance between labels is 100m; · Where linear assets cross over/under each other or over/under other assets; · At points where linear assets pass through walls where they will be labelled on each side of the wall. | Asset Tag ID | As per Asset Name | L73141-[Designer alternative ID] | -
Matt Wells | L73148 | MTW | MAT WELL [nn] | MAT WELL 001 | No | The Asset Tag Label will not be required due to the asset not being visible when situated within an adjacent structure. | - | - | - | -
Drainage Inspection Chambers | L73149 | DIC | INSPECTION CHAMBER [nnn] | INSPECTION CHAMBER 001 | No | An asset tag is not required as this will be placed on the drainage system. | - | - | - | -
Emergency Stop Push Button | L73331 | ESB | EMERGENCY STOP BUTTON [nnn] | EMERGENCY STOP BUTTON 001 | Conditional | The Crossrail standard prescribes the minimum labelling requirement; On occasion a contractor identifies an asset that they believe is of such importance it should be labelled. In such instances Crossrail would support the labelling of assets beyond the minimum requirement described within the Crossrail Asset Naming and Labelling Convention. | Asset Tag ID | As per Asset Name | L73331-[Designer alternative ID] | -
Batteries | L7411 | BAT | BATTERY [nnn] | BATTERY 001 | Yes | Batteries that are individually labelled will have an Asset Tag Label attached to the physical casing or housing that shall not impair performance of the Equipment. The labelling requirement may alternatively be fulfilled by providing a schematic which must clearly identify which Asset Tag belongs to each physical battery. All Schematics (as is with labels) must comply with the requirements as set out within the Asset Identification Standard (CRL1-XRL-O6-STD-CR001-00031) | Asset Tag ID | As per Asset Name | L7411-[Designer alternative ID] | -
UPS | L7412 | UPS | UPS [nnn] | UPS 002 | Yes | UPS will have only an Asset Tag Label attached to the physical casing or housing but shall not impair performance of the Equipment. | Asset Tag ID | As per Asset Name | L7412-[Designer alternative ID] | -
Battery Chargers | L7414 | BCH | BATTERY CHARGER [nnn] | BATTERY CHARGER 001 | Yes | An Asset Tag Label will be attached to the asset location, if there is a requirement for the charger to be located in a specific place. | Asset Tag ID | As per Asset Name | L7414-[Designer alternative ID] | -
Transformers | L74221 | TRS | TRANSFORMER [nnn] | TRANSFORMER 001 | Yes | An Asset Tag Label will be attached to a permanent fixture near the transformer in a point of safety that is easily accessible. | Asset Tag ID | As per Asset Name | L74221-[Designer alternative ID] | -
Autotransformer | L74223 | ATR | AUTOTRANSFORMER [nnn] | AUTOTRANSFORMER 002 | Yes | Being in an exterior location with no surrounding walls, Autotransformers will have Asset Tag Labels on the ground adjacent to the asset foundation. | Asset Tag ID | As per Asset Name | L74223-[Designer alternative ID] | -
Power Supply | L74225 | PWS | POWER SUPPLY [nnn] | POWER SUPPLY 001 | Yes | An Asset Tag label will be attached to the Power Supply unit in a way that does not interfere with its performance. | Asset Tag ID | As per Asset Name | L74225-[Designer alternative ID] | -
Solar Panel/Collector | L74226 | SOL | SOLAR PANEL [nnn] | SOLAR PANEL 501 | Yes | An Asset Tag Label will be placed on a permanent structure next to the item in a position that can be can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L74226-[Designer alternative ID] | -
Motor | L74231 | MTR | MOTOR [nnn] | MOTOR 001 | Yes | An Asset Tag Labels will be placed on a permanent structure next to the item in a position that can be can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L74231-[Designer alternative ID] | -
Driver Units | L74233 | DRU | DRIVER UNIT [nnn] | DRIVER UNIT 001 | Yes | An Asset Tag will not be placed on the physical item but will be placed on a permanent structure next to the item in a position that can be can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L74233-[Designer alternative ID] | -
Traction Power Circuit Breaker | L74321 | TPC | TRACTION POWER CIRCUIT BREAKER [nnn] | TRACTION POWER CIRCUIT BREAKER 001 | Yes | An Asset Tag Labels will be placed on a permanent structure next to the item in a position that can be can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L74321-[Designer alternative ID] | -
Manual Disconnectors | L74324 | MDC | MANUAL DISCONNECTOR [nnn] | MANUAL DISCONNECTOR 001 | Yes | An Asset Tag Label will be attached to a permanent fixture near the physical item at a point of safety where it is easily visible. | Asset Tag ID | As per Asset Name | L74324-[Designer alternative ID] | -
Protective Devices | L74325 | PTD | PROTECTIVE DEVICE [nnn] | PROTECTIVE DEVICE 001 | No | - | - | - | - | -
Conductor Rod | L74331 | COR | CONDUCTOR ROD [nnn] | CONDUCTOR ROD 001 | Yes | Conductor rods will only have Asset Tag Labels, these will not be placed on the physical item but will be placed on a permanent structure next to the item in a position that can be can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L74331-[Designer alternative ID] | -
Conductor Tape | L74332 | COT | CONDUCTOR TAPE [nnn] | CONDUCTOR TAPE 001 | Yes | Multiple Asset Tag Labels will be required for conductor tape: · At each end of the asset; · Sections of tape greater than 100m long should have labels spaced at intervals such that the maximum distance between labels is 100m | Asset Tag ID | As per Asset Name | L74332-[Designer alternative ID] | -
Surge Suppression | L74333 | SSP | SURGE SUPPRESSION [nnn] | SURGE SUPPRESSION 001 | Yes | An Asset Tag Labels will be placed on a permanent structure next to the item in a position that can be can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L74333-[Designer alternative ID] | -
Earthwire | L743343 | EAW | [SOURCE], CABLE-[CABLE TYPE]: [DESIGN ALTERNATIVE ASSET ID], [DESTINATION] | MAIN SWITCHBOARD ETH, CABLE-E: A-0011, UPS EMERG LIGHTING SWITCHBOARD WTH | Yes | A cable shall be identified at each end, within 12m intervals in stations, within 100m intervals in tunnels and either side of penetrations along its route. In each space through which it passes, within 500mm of its entry into/ exit from a space and within 500mm of each termination or joint. Refer to the Asset Identification Standard for example label images | Asset Tag ID | [Source] (i.e. MAIN SWITCHBOARD ETH) | Cable-[Cable Type]: [Drawing Asset ID] (i.e. CABLE-E: A-0011) | [Destination] (i.e. UPS EMERG LIGHTING SWITCHBOARD WTH)
Earth Bar | L74341 | EAB | EARTH BAR [nnn] | EARTH BAR 001 | Yes | Earth bars will have only an Asset Tag Label attached to the physical item but in a position that shall not impair performance of the equipment. This is because this asset is not expected to be a regularly serviced asset and it is not expected to be regularly removed or moved. | Asset Tag ID | As per Asset Name | L74341-[Designer alternative ID] | -
Earth Mat | L74342 | EAM | EARTH MAT [nnn] | EARTH MAT 001 | No | - | - | - | - | -
Earth Rods | L74344 | EAR | EARTH ROD [nnn] | EARTH ROD 001 | Yes | Earth rods will have Asset Tag Labels, these will not be placed on the physical item but will be placed on a permanent structure next to the item in a position that can be can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L74344-[Designer alternative ID] | -
Junction Box | L74348 | JCN | JUNCTION BOX [nnn] | JUNCTION BOX 001 | Conditional | The Crossrail standard prescribes the minimum labelling requirement; On occasion a contractor identifies an asset that they believe is of such importance it should be labelled. In such instances Crossrail would support the labelling of assets beyond the minimum requirement described within the Crossrail Asset Naming and Labelling Convention. | Asset Tag ID | As per Asset Name | L74348-[Designer alternative ID] | -
Harmonic Filter | L7442 | HAR | HARMONIC FILTER [nnn] | HARMONIC FILTER 001 | No | - | - | - | - | -
Power Correction Panel | L7443 | PCP | POWER CORRECTION PANEL [nnn] | POWER CORRECTION PANEL 001 | No | - | - | - | - | -
EMC Filter | L7444 | EMC | EMC FILTER [nnn] | EMC FILTER 004 | Yes | An Asset Tag Label will be attached adjacent to the place where the asset is to be located. | Asset Tag ID | As per Asset Name | L7444-[Designer alternative ID] | -
Watt Hour Meter | L74521 | WHM | WATT-HOUR METER [nnn] | WATT-HOUR METER 001 | Yes | An Asset Tag Label will be placed on a permanent structure next to the item in a position that can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. Where the asset is contained within a larger item e.g. a distribution board it may not be possible to place an actual Asset Tag Label near to the asset in a safe manner; in this instance the use of a schematic will be permissible that shows all the corresponding Asset Tag Labels for the distribution board. | Asset Tag ID | As per Asset Name | L74521-[Designer alternative ID] | -
Test Point | L7453 | TPT | TEST POINT [nnn] | TEST POINT 002 | Yes | Test points will have an Asset Tag attached to the physical item but shall not impair performance of the equipment. This is because this asset is not expected to be a regularly serviced asset and it is not expected to be regularly removed or moved. | Asset Tag ID | As per Asset Name | L7453-[Designer alternative ID] | -
Control Switches | L74611 | SWT | SWITCH [nnn] | SWITCH 001 | Yes | Switches will have an Asset Tag Label attached to the physical item in a position that shall not impair performance of the equipment. This is because this asset is not expected to be a regularly serviced asset and it is not expected to be regularly removed or moved. | Asset Tag ID | As per Asset Name | L74611-[Designer alternative ID] | -
Distribution Board | L74612 | DBB | DISTRIBUTION BOARD [nnn] | DISTRIBUTION BOARD 001 | Yes | Distribution boards will have an Asset Tag Label attached to the physical item but shall not impair performance of the equipment. This is because this asset is expected to be a regularly serviced asset. | Asset Tag ID | As per Asset Name | L74612-[Designer alternative ID] | -
Switch Board | L74613 | SWB | SWITCH BOARD [nnn] | SWITCH BOARD 001 | Yes | Switch Boards will have an Asset Tag attached to the physical item but shall not impair performance of the equipment. This is because this asset it is not expected to be regularly removed or moved. | Asset Tag ID | As per Asset Name | L74613-[Designer alternative ID] | -
Automatic Transfer Switches (ATS) | L74614 | ATS | AUTO TRANSFER SWITCH [nnn] | AUTO TRANSFER SWITCH 001 | Yes | An Asset Tag Labels will be placed on a permanent structure next to the item in a position that can be can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L74614-[Designer alternative ID] | -
Motorised OHLE Section Switch | L746154 | MSS | OHLE SECTION SWITCH [nnn] | OHLE SECTION SWITCH 001 | Yes | An Asset Tag Labels will be placed on a permanent structure next to the item in a position that can be can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L746154-[Designer alternative ID] | -
Isolator | L746155 | ISO | ISOLATOR [nnn] | ISOLATOR 001 | Yes | An Asset Tag Labels will be placed on a permanent structure next to the item in a position that can be can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L746155-[Designer alternative ID] | -
Wiring cables | L746211 | WGC | [SOURCE], CABLE-[CABLE TYPE]: [DESIGN ALTERNATIVE ASSET ID], [DESTINATION] | LV-B MAIN SWITCHBOARD ETH, CABLE-P: A-0011, UPS EMERG LIGHTING SWITCHBOARD WTH | Yes | A cable shall be identified at each end, within 12m intervals in stations, within 100m intervals in tunnels and either side of penetrations along its route. In each space through which it passes, within 500mm of its entry into/ exit from a space and within 500mm of each termination or joint. Refer to the Asset Identification Standard for example label images. | Asset Tag ID | [Source] (i.e. LV-B MAIN SWITCHBOARD ETH) | Cable-[Cable Type]: [Drawing Asset ID] (i.e. CABLE-P: A-0011) | [Destination] (i.e. UPS EMERG LIGHTING SWITCHBOARD WTH)
Fire Alarm Cabling | L746212 | FAC | [CABLE TYPE]-[SOURCE]-[DESTINATION], [DESIGN ALTERNATIVE ASSET ID] | C-CAB-012-FOS-014, A-0011 | Yes | A cable shall be identified at each end, within 100m intervals in stations, within 100m intervals in tunnels and either side of penetrations along its route. In each space through which it passes, within 500mm of its entry into/ exit from a space and within 500mm of each termination or joint. Refer to the Asset Identification Standard for example label images. Destination numbering must be consistent with 'LU11 SOR Interchange Communications Legacy Asset Numbering' document (CRL1-LU-R3-RGN-CR001-50004) | Asset Tag ID | [CABLE TYPE]-[SOURCE-nnn]-[DESTINATION-nnn] (i.e. C-CAB-012-FOS-014) | [Designer alternative ID] | -
Contact wire | L746213 | CWE | [SOURCE], CABLE-[CABLE TYPE]: [DESIGN ALTERNATIVE ASSET ID], [DESTINATION] | TWO TRACK CANTILEVER 001, CABLE-P: A-0011, TWO TRACK CANTILEVER 005 | No | As contact wire will be in contact with the train pantograph, it will not have a label attached to it. | Asset Tag ID | [Source] (i.e. TWO TRACK CANTILEVER 001) | - | [Destination] (i.e. TWO TRACK CANTILEVER 005)
HV cables | L74622 | HVC | [SOURCE], CABLE-[CABLE TYPE]: [DESIGN ALTERNATIVE ASSET ID], [DESTINATION] | HV-B MAIN SWITCHBOARD ETH, CABLE-P: A-0011, UPS EMERG LIGHTING SWITCHBOARD WTH | Yes | A circuit (including 3 single core cables working as one feeder) shall be identified at each end, within 12m intervals in stations, within 100m intervals in tunnels and either side of penetrations along its route. In each space through which it passes, within 500mm of its entry into/ exit from a space and within 500mm of each termination. | Asset Tag ID | [Source] (i.e. HV-B MAIN SWITCHBOARD ETH) | Cable-[Cable Type]: [Drawing Asset ID] (i.e. CABLE-P: A-0011) | [Destination] (i.e. UPS EMERG LIGHTING SWITCHBOARD WTH)
Return Current Bus Bar (RCBB) | L746231 | RCB | RETURN CURRENT BUSBAR [nnn] | RETURN CURRENT BUSBAR 001 | Yes | Return Current Bus Bars will have Asset Tag Labels, these will not be placed on the physical item but will be placed on a permanent structure next to the item in a position that can be can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L746231-[Designer alternative ID] | -
Spider Plates | L746232 | SDP | SPIDER PLATE [nnn] | SPIDER PLATE 001 | Yes | Spider Plates will have an Asset Tag Label attached to the physical item that shall not impair performance of the equipment. | Asset Tag ID | As per Asset Name | L746232-[Designer alternative ID] | -
BusBar | L746233 | BUS | BUSBAR [nnn] | BUSBAR 001 | Yes | Busbars will have Asset Tag Labels, these will not be placed on the physical item but will be placed on a permanent structure next to the item in a position that can be can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L746233-[Designer alternative ID] | -
Busbar Trunking | L746234 | BTG | BUSBAR TRUNKING [nnn] | BUSBAR TRUNKING 001 | No | - | - | - | - | -
Antenna | L74624 | ANT | ANTENNA [nnn] {OR} ANTENNA [xxx/xxx - xxx/xxx] | ANTENNA 002 {OR} ANTENNA ABC/XYZ - FTW/WTF | Yes | An Asset Tag Label shall be applied adjacent to the Antenna e.g. on the fixing bracket (if installed) or permanent structure. | Asset Tag ID | [CABLE TYPE]-[SOURCE-nnn]-[DESTINATION-nnn] (i.e. C-CAB-012-FOS-014) | Cable-[Cable Type]: [Drawing Asset ID] (i.e. CABLE-P: A-0011) | -
Negative insulated feeder cable | L74625 | NIF | [SOURCE], CABLE-[CABLE TYPE]: [DESIGN ALTERNATIVE ASSET ID], [DESTINATION] | AUTO TRANSFORMER 001 ETH-HV-N, CABLE-P: A-0011, AUTO TRANSFORMER 002 WTH | Yes | A cable shall be identified at each end, within 12m intervals in stations, within 100m intervals in tunnels and either side of penetrations along its route. In each space through which it passes, within 500mm of its entry into/ exit from a space and within 500mm of each termination or joint. Refer to the Asset Identification Standard for example label images. | Asset Tag ID | [Source] (i.e. AUTO TRANSFORMER 001 ETH-HV-N) | [Designer alternative ID] | [Destination] (i.e. AUTO TRANSFORMER 002 WTH)
Rigid bar system (ROC) | L74626 | ROC | RIGID BAR [nnn] | RIGID BAR 001 | Yes | Multiple Asset Tag Labels may be required for cable assets: At each end of the asset; Where cables cross over/under each other or other obstructions, labels should be applied at each side of the obstruction; Sections of cable greater than 100m long should have labels spaced at intervals such that the maximum distance between labels is 100m; At points where cables pass through walls or poles where they will be labelled on each side of the wall. | Asset Tag ID | As per Asset Name | L74626-[Designer alternative ID] | -
Droppers | L74627 | DPP | DROPTUBE [nnn] | DROPTUBE 001 | No | No specific Asset Tag Labels are required. They can be accounted by the isolators placed on them which will have an Asset Tag Label. | - | - | - | -
Control Cables | L746291 | CCS | [CABLE TYPE]-[SOURCE]-[DESTINATION], [DESIGN ALTERNATIVE ASSET ID] | C-CAB-012-CAM-014, A-0011 | Yes | A cable shall be identified at each end, within 100m intervals in tunnels and either side of penetrations along its route. In each space through which it passes, within 500mm of its entry into/ exit from a space and within 500mm of each termination or joint. Refer to the Asset Identification Standard for example label images. Destination numbering must be consistent with 'LU11 SOR Interchange Communications Legacy Asset Numbering' document (CRL1-LU-R3-RGN-CR001-50004) | Asset Tag ID | [CABLE TYPE]-[SOURCE-nnn]-[DESTINATION-nnn] (i.e. C-CAB-012-FOS-014) | [Designer alternative ID] | -
Catenary wire | L746292 | CNW | CATENARY WIRE [nnn] | CATENARY WIRE 001 | Yes | Multiple Asset Tag Labels may be required for cable assets: At each end of the asset; Sections of cable greater than 100m long should have labels spaced at intervals such that the maximum distance between labels is 100m; | Asset Tag ID | As per Asset Name | L746292-[Designer alternative ID] | -
Neutral section | L746293 | NTS | NEUTRAL SECTION [nnn] | NEUTRAL SECTION 001 | Yes | Asset Tag Labelling for the Neutral Section will consist of signage that will be located on the mast located in the Neutral Section. It will be placed in a position that can be can be viewed safely without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L746293-[Designer alternative ID] | -
25kV Insulators | L7463 | KVI | 25KV INSULATOR [nnn] | 25KV INSULATOR 001 | No | - | - | - | - | -
Switchgear | L74641 | SWG | SWITCHGEAR [nnn] | SWITCHGEAR 002 | Yes | Asset Tag Labels will not be placed on the physical item but will be placed on a permanent structure next to the item in a position that can be can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. Each Panel will also have a “circuit designation” label identifying the electrical section that the panel is feeding or the purpose of the panel e.g. “Bus Riser”. This label will be fixed to the front of the switchgear. | Asset Tag ID | As per Asset Name | L74641-[Designer alternative ID] | -
Section insulator | L74671 | SCI | SECTION INSULATOR [nnn] | SECTION INSULATOR 001 | Yes | An Asset Tag Labels will be placed on a permanent structure next to the item in a position that can be can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L74671-[Designer alternative ID] | -
Cable Marshalling Cabinets | L7468 | CMB | CABLE MARSHALLING CABINET [nnn] | CABLE MARSHALLING CABINET 001 | Yes | Cable Marshalling cabinets will have an Asset Tag Label attached to the physical item but in a position that shall not impair performance of the equipment. This is because this asset is not expected to be a regularly serviced asset and it is not expected to be regularly removed or moved. | Asset Tag ID | As per Asset Name | L7468-[Designer alternative ID] | -
Gear Box | L7469 | GRB | GEAR BOX [nnn] | GEAR BOX 001 | Yes | An Asset Tag Label will be placed on a permanent structure next to the item in a position that can be can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L7469-[Designer alternative ID] | -
Socket outlets | L74714 | SKO | SOCKET OUTLET [nnn] | SOCKET OUTLET 001 | No | - | - | - | - | -
Spur Outlets | L74715 | SPO | SPUR OUTLET [nnn] | SPUR OUTLET 001 | Yes | Spur outlets will have an Asset Tag Label attached to the physical item but also in a position that shall not impair performance of the equipment. | Asset Tag ID | As per Asset Name | L74715-[Designer alternative ID] | -
Maintenance Sockets | L74716 | MTS | MAINTENANCE SOCKET [nnn] | MAINTENANCE SOCKET 001 | Yes | Maintenance sockets will have an Asset Tag Label attached to the physical item but in a position that shall not impair performance of the equipment. | Asset Tag ID | As per Asset Name | L74716-[Designer alternative ID] | -
Fixed luminaires for general lighting | L74731 | FLL | LUMINAIRE [[nnn] or [nnnn]] {OR} PES LUMINAIRE [[nnn] or [nnnn]] | LUMINAIRE 0201 {OR} PES LUMINAIRE 123 | Yes | Fixed luminaries for general lighting will have an Asset Tag attached to the physical item but shall not impair performance of the equipment. This is because this asset is not expected to be a regularly serviced asset and it is not expected to be regularly removed or moved. See also CRL1-XRL-Z3-GUI-CR001-50071: Public Facing Labelling Guidance where asset is in public accessible area. | Asset Tag ID | As per Asset Name | L74731-[Designer alternative ID] | -
Switchable signage | L7473221 | SWS | SWITCHABLE SIGNAGE [nnn] | SWITCHABLE SIGNAGE 001 | Yes | An Asset Tag Label will be placed on a permanent structure next to the item in a position that can be can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. See also CRL1-XRL-Z3-GUI-CR001-50071: Public Facing Labelling Guidance where asset is in public accessible area. | Asset Tag ID | As per Asset Name | L7473221-[Designer alternative ID] | -
Non-Switchable Signage | L7473222 | NSS | NON-SWITCHABLE SIGNAGE [nnn] | NON-SWITCHABLE SIGNAGE 001 | Yes | An Asset Tag Label will be placed on a permanent structure next to the item in a position that can be can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. See also CRL1-XRL-Z3-GUI-CR001-50071: Public Facing Labelling Guidance where asset is in public accessible area. | Asset Tag ID | As per Asset Name | L7473222-[Designer alternative ID] | -
Plate Switches & Multi Gang Grid | L747352 | PSG | PLATE SWITCH [nnn] | PLATE SWITCH 001 | Conditional | Plate Switches will have an Asset Tag Label attached to the physical item but in a position that shall not impair performance of the equipment. This is because this asset is not expected to be a regularly serviced asset and it is not expected to be regularly removed or moved. Light switches will only require an asset tag label when connected to a DALI system. | Asset Tag ID | As per Asset Name | L747352-[Designer alternative ID] | -
Light Sensitive Switches | L747354 | LSS | LIGHT-SENSITIVE SWITCH [nnn] | LIGHT-SENSITIVE SWITCH 001 | Yes | Light sensitive switches will have an Asset Tag Label attached to the physical item but in a position that shall not impair performance of the equipment. This is because this asset is not expected to be a regularly serviced asset and it is not expected to be regularly removed or moved. | Asset Tag ID | As per Asset Name | L747354-[Designer alternative ID] | -
Tensioning Equipment | L748 | TEN | TENSIONING EQUIPMENT [nnn] | TENSIONING EQUIPMENT 001 | Yes | An Asset Tag Label will be placed on a permanent structure next to the item in a position that can be can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L748-[Designer alternative ID] | -
Condenser | L75142 | CDN | AIRCON UNIT [nnn] | AIRCON UNIT 001 | Yes | An Asset Tag Label will be placed on a permanent structure next to the item in a position that can be can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L75142-[Designer alternative ID] | -
Fan Coil Unit | L75145 | FCU | FAN COIL UNIT [nnn] | FAN COIL UNIT 001 | Yes | Fan coil units will have an Asset Tag Label attached to the physical item but in a position that shall not impair performance of the equipment. This is because this asset is not expected to be a regularly serviced asset and it is not expected to be regularly removed or moved. | Asset Tag ID | As per Asset Name | L75145-[Designer alternative ID] | -
VAV Controller (Mixing Box / Valve) | L75146 | VAV | VAV CONTROLLER [nnn] | VAV CONTROLLER 001 | Yes | The Asset Tag Label will be placed on the Functional Unit the VAV Controller is serving. | Asset Tag ID | As per Asset Name | L75146-[Designer alternative ID] | -
Air Handling Unit (AHU) | L7515 | AHU | AIR HANDLING UNIT [nnn] | AIR HANDLING UNIT 001 | Yes | Air Handling Units (AHU) will have a label representing the Asset Tag Label attached to the Unit itself, preferably at eye level. | Asset Tag ID | As per Asset Name | L7515-[Designer alternative ID] | -
Convectors | L75221 | CNV | CONVECTOR [nnn] | CONVECTOR 001 | Yes | Electric Heaters will have an Asset Tag Label placed on a permanent structure next to the item in a position that can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L75221-[Designer alternative ID] | -
Trace Heating Element | L752293 | TCH | TRACE HEATING [nnn] | TRACE HEATING 001 | Yes | Trace heating will have an Asset Tag Label attached to the physical item but in a position that shall not impair performance of the equipment. This is because this asset is not expected to be a regularly serviced asset and it is not expected to be regularly removed or moved. Final labelling locations should be determined from the perspective of the future asset maintainer, taking into account line of sight and peripheral vision. This is particularly important for a trace heating element where only one label would be required for a smaller asset - but where a degree of uncertainty may arise and immediate identification of a Trace Heating Element is not possible, then additional labels should be considered and affixed at either side of penetrations along its route (in each space through which it passes). | Asset Tag ID | As per Asset Name | L752293-[Designer alternative ID] | -
Air Cooled Chillers | L75256 | ACC | AIR COOLED CHILLER [nnn] | AIR COOLED CHILLERS 001 | Yes | An Asset Tag Label will be placed on a permanent structure next to the item in a position that can be can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L75256-[Designer alternative ID] | -
Refrigerant Pipe Work | L75257 | RFP | REFRIGERANT PIPE WORK [nnn] | REFRIGERANT PIPE WORK 001 | Yes | Multiple Asset Tag Labels will be required for pipe assets as follows: 1.At each end of the asset; 2.Sections of pipe greater than 100m long should have labels spaced at intervals such that the maximum distance between labels is 100m; 3.Where linear assets cross over/under each other or over/under other assets; 4.At points where linear assets pass through walls where they will be labelled on each side of the wall. | Asset Tag ID | As per Asset Name | L75257-[Designer alternative ID] | -
Run around coil | L75281 | RAC | RUN AROUND COIL [nnn] | RUN AROUND COIL 001 | Yes | An Asset Tag Label will be placed on a permanent structure next to the item in a position that can be can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L75281-[Designer alternative ID] | -
Ventilation System Heat Exchanger | L75282 | VHE | COOLING COIL [nnn] | COOLING COIL 001 | Yes | An Asset Tag Label will be placed on a permanent structure next to the item in a position that can be can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L75282-[Designer alternative ID] | -
Heater Battery | L75283 | HTB | HEATER BATTERY [nnn] | HEATER BATTERY 001 | Yes | An Asset Tag Label will be placed on a permanent structure next to the item in a position that can be can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L75283-[Designer alternative ID] | -
HVAC Fans | L7533 | HVF | HVAC FAN [nnn] | HVAC FAN 001 | Yes | HVAC Fans will have an Asset Tag Label placed on a permanent structure next to the item in a position that can be can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L7533-[Designer alternative ID] | -
Fan Tray | L753451 | FTY | FAN TRAY [nnn] | FAN TRAY 001 | No | A schematic with the Asset Tag will identify the required location, Tag ID and name of the asset. | - | - | - | -
Tunnel Ventilation Fans | L75347 | TVF | TUNNEL VENTILATION FAN [nnn] | TUNNEL VENTILATION FAN 001 | Yes | A Tunnel Ventilation Fan will have an Asset Tag Label attached adjacent to the physical item but shall not impair performance of the fan. | Asset Tag ID | As per Asset Name | L75347-[Designer alternative ID] | -
Treatment of circulation liquids | L7541 | TCL | [TREATMENT UNIT TYPE] [nnn] | DIRT SEPARATOR 001 | Yes | An Asset Tag Label will be placed on a permanent structure next to the item in a position that can be can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L7541-[Designer alternative ID] | -
Room thermostats | L75514 | RMT | THERMOSTAT [nnn] | THERMOSTAT 001 | Conditional | Room thermostats will have an Asset Tag Label attached to the physical item but shall not impair performance of the equipment. This is because this asset is not expected to be a regularly serviced asset and it is not expected to be regularly removed or moved. An asset tag label is not required where the thermostast is part of a packaged system. | Asset Tag ID | As per Asset Name | L75514-[Designer alternative ID] | -
Pressure controls | L75521 | PSC | PRESSURE CONTROL [nnn] | PRESSURE CONTROL 001 | Conditional | Pressure controls will have an Asset Tag Label placed on a permanent structure next to the item in a position that can be can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. An asset tag label is not required where the pressure control is part of a packaged system. | Asset Tag ID | As per Asset Name | L75521-[Designer alternative ID] | -
Flow Control Device | L75522 | FCD | FLOW CONTROL DEVICE [nnn] | FLOW CONTROL DEVICE 001 | Yes | An Asset Tag Label will be placed on a permanent structure next to the item in a position that can be can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L75522-[Designer alternative ID] | -
Pressure Sensors | L755241 | PSS | PRESSURE SENSOR [nnn] | PRESSURE SENSOR 001 | No | A schematic with the asset tag will identify the required location of the asset. | - | - | - | -
Vibration Sensors | L755242 | VBS | VIBRATION SENSOR [nnn] | VIBRATION SENSOR 001 | Conditional | An Asset Tag Label shall be placed on a permanent structure next to the item in a position that can be can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. An asset tag label is not required where the vibration sensor is part of a packaged system. | Asset Tag ID | As per Asset Name | L755242-[Designer alternative ID] | -
Temperature Sensors | L755243 | TPS | TEMPERATURE SENSOR [nnn] | TEMPERATURE SENSOR 001 | Conditional | An Asset Tag Label shall be placed on a permanent structure next to the item in a position that can be can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. An asset tag label is not required where the temperature sensor is part of a packaged system. | Asset Tag ID | As per Asset Name | L755243-[Designer alternative ID] | -
Fireman's Override Switch | L75531 | FOS | FIREMANS OVERRIDE SWITCH [nnn] | FIREMANS OVERRIDE SWITCH 001 | Yes | A Fireman’s override switch will have a single Asset Tag Label which will not be placed on the physical item but will be placed on a permanent structure next to the item in a position that can be can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L75531-[Designer alternative ID] | -
Variable Speed Drives | L75533 | INV | INVERTER [nnn] | INVERTER 001 | Yes | Inverters will have an Asset Tag Label placed on a permanent structure next to the item in a position that can be can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L75533-[Designer alternative ID] | -
Actuators | L75534 | ACT | ACTUATOR [nnn] | ACTUATOR 001 | Yes | Actuators will have an Asset Tag Label placed on a permanent structure next to the item in a position that can be can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L75534-[Designer alternative ID] | -
VRF Branch Control Box | L75535 | VRF | VRF BRANCH CONTROL BOX [nnn] | VRF BRANCH CONTROL BOX 001 | Yes | An Asset Tag Label will be placed on a permanent structure next to the item in a position that can be viewed and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L75535-[Designer alternative ID] | -
Interface Units | L75541 | IFU | INTERFACE UNIT [nnn] | INTERFACE UNIT 001 | Yes | An Asset Tag Label will be placed on a permanent structure next to the item in a position that can be viewed and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L75541-[Designer alternative ID] | -
Anemometer | L7557 | ANE | ANEMOMETER [nnn] | ANEMOMETER 001 | Yes | An Asset Tag Label will be attached to a permanent structure adjacent to the asset. | Asset Tag ID | As per Asset Name | L7557-[Designer alternative ID] | -
Dampers | L75611 | DMP | DAMPERS [nnn] {OR} DAMPER [nnn] | DAMPERS 001 {OR} DAMPER 001 | Yes | Dampers will have an Asset Tag Label attached to the physical item but in a position that shall not impair performance of the equipment. This is because this asset is not expected to be a regularly serviced asset and it is not expected to be regularly removed or moved. | Asset Tag ID | As per Asset Name | L75611-[Designer alternative ID] | -
Ducts | L756110 | DCT | [EXTRACTION or SUPPLY] DUCT [nnnn] | EXTRACTION DUCT 0301 SUPPLY DUCT 0601 | Yes | Multiple Asset Tag Labels will be required for duct assets: · At each end of the asset; · Sections of duct greater than 20m long should have labels spaced at intervals such that the maximum distance between labels is 20m · At points where linear assets pass through walls where they will be labelled on each side of the wall. | Asset Tag ID | As per Asset Name | L756110-[Designer alternative ID] | -
Fire dampers for air ductlines | L75612 | FDD | FIRE DAMPERS [nnn] {OR} FIRE DAMPER [nnn] | FIRE DAMPERS 001 {OR} FIRE DAMPERS 001 | Yes | Fire dampers for air ducts will have an Asset Tag Labels attached to the physical item but shall be positioned to not impair performance of the equipment. This is because it is not expected to be regularly removed or moved. | Asset Tag ID | As per Asset Name | L75612-[Designer alternative ID] | -
Flexible Connection Assembly | L756161 | FCA | FLEXIBLE CONNECTION ASSEMBLY [nnn] | FLEXIBLE CONNECTION ASSEMBLY 001 | Yes | An Asset Tag Label will be attached to a permanent structure adjacent to the asset. | Asset Tag ID | As per Asset Name | L756161-[Designer alternative ID] | -
Transition sections | L756162 | TRA | TRANSITION SECTION [nnn] | TRANSITION SECTION 001 | Yes | An Asset Tag Label will be placed on a permanent structure next to the item in a position that can be can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L756162-[Designer alternative ID] | -
Insitu Concrete Drawpits | L756171 | ICD | CONCRETE DRAWPIT [nnn] | CONCRETE DRAWPIT 001 | No | The Asset Tag Label will not be placed on the physical item but will be placed on each of the services the draw pit is providing access to. | - | - | - | -
Duct silencers | L75618 | DSS | DUCT SILENCER [nnn] | DUCT SILENCER 001 | Yes | If the Duct silencers is not serviceable or reusable then it will have only an Asset Tag Label attached to the physical item but shall not impair performance of the equipment. This is because this asset is not expected to be a regularly serviced asset and it is not expected to be regularly removed or moved. | Asset Tag ID | As per Asset Name | L75618-[Designer alternative ID] | -
Expansion Bellows | L75619 | EXB | EXPANSION BELLOWS [nnn] {OR} EXPANSION BELLOW [nnn] | EXPANSION BELLOWS 001 {OR} EXPANSION BELLOW 001 | Yes | Expansion Bellows will have an Asset Tag Label attached to the physical item but shall not impair performance of the equipment. This is because this asset is not expected to be a regularly serviced asset and it is not expected to be regularly removed or moved. | Asset Tag ID | As per Asset Name | L75619-[Designer alternative ID] | -
Duct Grilles | L75631 | DCG | DUCT GRILLES [nnn] {OR} DUCT GRILLE [nnn] | DUCT GRILLES 001 {OR} DUCT GRILLE 001 | Yes | A Grille will have an Asset Tag attached to the physical item but shall not impair performance of the equipment. This is because this asset is not expected to be a regularly serviced asset and it is not expected to be regularly removed or moved. | Asset Tag ID | As per Asset Name | L75631-[Designer alternative ID] | -
Attenuator | L761110 | ATT | ATTENUATOR [nnn] | ATTENUATOR 001 | Yes | An Asset Tag Label will be attached to place where the asset is to be located. | Asset Tag ID | As per Asset Name | L761110-[Designer alternative ID] | -
Induction Loop Panel | L761121 | ILP | INDUCTION LOOP PANEL [nnn] | INDUCTION LOOP PANEL 001 | Yes | An Asset Tag Label will be attached to place where the asset is to be located. | Asset Tag ID | As per Asset Name | L761121-[Designer alternative ID] | -
Amplifiers | L76115 | AMP | AMPLIFIER [nnn] | AMPLIFIER 001 | Yes | Amplifiers will an Asset Tag Labels placed on a permanent structure next to the item in a position that can be can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L76115-[Designer alternative ID] | -
Loudspeakers | L76116 | LSK | LOUDSPEAKER [nnn] | LOUDSPEAKER 001 | Yes | Loudspeakers will have an Asset Tag Label placed on a permanent structure next to the item in a position that can be can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. See also CRL1-XRL-Z3-GUI-CR001-50071: Public Facing Labelling Guidance where asset is in public accessible area. | Asset Tag ID | As per Asset Name | L76116-[Designer alternative ID] | -
Microphones | L76117 | MIC | MICROPHONE [nnn] | MICROPHONE 001 | Yes | Microphones have an Asset Tag Labels placed on a permanent structure next to the item in a position that can be can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L76117-[Designer alternative ID] | -
Sound Attenuation Equipment | L76119 | SAE | SOUND ATTENUATOR [nnn] | SOUND ATTENUATOR 001 | Yes | An Asset Tag Label will be placed on a permanent structure next to the item in a position that can be can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L76119-[Designer alternative ID] | -
Customer Information Displays | L76125 | CIS | CUSTOMER INFORMATION DISPLAY [nnn] | CUSTOMER INFORMATION DISPLAY 001 | Yes | An Asset Tag Label will be placed on a permanent structure next to the item in a position that can be can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L76125-[Designer alternative ID] | -
Audio Switch/Receiver | L761322 | ASR | RECEIVER [nnn] | RECEIVER 001 | Yes | An Asset Tag Label will be placed on a permanent structure next to the item in a position that can be can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L761322-[Designer alternative ID] | -
Encoders & Decoders | L761323 | END | [ENCODER or DECODER] [nnn] | ENCODER 001 DECODER 001 | No | A schematic with the Asset Tag will identify the required location of the asset. | - | - | - | -
Radio Transceiver | L761324 | RTC | RADIO TRANSCEIVER [nnn] | RADIO TRANSCEIVER 001 | Yes | An Asset Tag Label will be placed on a permanent structure next to the item in a position that can be can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L761324-[Designer alternative ID] | -
AV Recording Equipment | L76133 | AVR | AV RECORDING EQUIPMENT [nnn] | AV RECORDING EQUIPMENT 001 | Yes | Asset Tag labels will be placed on a permanent structure next to the item. The Asset Tag Label will be in a position that can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L76133-[Designer alternative ID] | -
Server | L76134 | SVR | SERVER [nnn] | SERVER 001 | Yes | An Asset Tag Label will be placed on a permanent structure next to the item in a position that can be can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L76134-[Designer alternative ID] | -
Video Monitors / Walls | L761361 | VMW | VIDEO [MONITOR or WALL] [nnn] | VIDEO MONITOR 001 VIDEO WALL 001 | Yes | An Asset Tag Label will be placed on a permanent structure next to the item in a position that can be can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L761361-[Designer alternative ID] | -
KVM Switch | L76137 | KVM | KVM SWITCH [nnn] | KVM SWITCH 001 | No | - | - | - | - | -
End of line termination | L7615 | TMP | TERMINATION POINTS [nnn] | TERMINATION POINTS 001 | No | A schematic with the Asset Tag will identify the required location of the asset. | - | - | - | -
Code reading systems | L76212 | CRS | CODE READER [nnn] | CODE READER 001 | Yes | Access controls will have an Asset Tag Label adjacent to the asset. | Asset Tag ID | As per Asset Name | L76212-[Designer alternative ID] | -
Micro Switch Contacts For Doors And Windows | L762203 | MSC | MICROSWITCH CONTACT [nnn] | MICROSWITCH CONTACT 001 | Yes | Micro switch contacts will have an Asset Tag Label attached to the physical item but in a position that shall not impair performance of the equipment. | Asset Tag ID | As per Asset Name | L762203-[Designer alternative ID] | -
Infra Red Radiation Detectors | L762208 | IRD | INFRA RED RADIATION DETECTOR [nnn] | INFRA RED RADIATION DETECTOR 001 | Yes | Infra-red radiation detectors will have an Asset Tag Label attached to the physical item but shall not impair performance of the equipment. This is because this asset is not expected to be a regularly serviced asset and it is not expected to be regularly removed or moved. | Asset Tag ID | As per Asset Name | L762208-[Designer alternative ID] | -
Noise Sensor | L7622091 | NSR | NOISE SENSOR [nnn] | NOISE SENSOR 001 | Yes | An Asset Tag Label will be attached to place where the asset is to be located. | Asset Tag ID | As per Asset Name | L7622091-[Designer alternative ID] | -
Gap Monitoring/Object Sensor | L762215 | GMG | GAP MONITOR [nnn] | GAP MONITOR 001 | No | Each Detector and associated assembly will be identified with a Primary Functional Unit label to reduce the number of labels in the passenger areas, this label will be placed above each door. This component will be associated with the Platform Edge Door Primary Functional Unit, and therefore does not require its own asset tag label. | - | - | - | -
Control and indicating equipment | L76252 | CIE | CONTROL AND INDICATING EQUIPMENT [nnn] | CONTROL AND INDICATING EQUIPMENT 001 | Yes | An Asset Tag Label will be placed on a permanent structure next to the item in a position that can be can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L76252-[Designer alternative ID] | -
Multi Detectors | L762532 | MDT | MULTI DETECTOR [nnn] | MULTI DETECTOR 001 | Yes | An Asset Tag Label will be placed on a permanent structure next to the item in a position that can be can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L762532-[Designer alternative ID] | -
Linear Heat Detectors | L762533 | LHD | LINEAR HEAT DETECTOR [nnn] | LINEAR HEAT DETECTOR 001 | Yes | Linear heat detectors will have an Asset Tag Label attached to the physical item but in a position that shall not impair performance of the Equipment. This is because this asset is not expected to be a regularly serviced asset and it is not expected to be regularly removed or moved. | Asset Tag ID | As per Asset Name | L762533-[Designer alternative ID] | -
Aspirating Detectors | L762534 | APD | ASPIRATING DETECTOR [nnn] | ASPIRATING DETECTOR 001 | Yes | Aspirating detectors will have an Asset Tag Label attached to the physical item but in a position that shall not impair performance of the Equipment. This is because it is not expected to be regularly removed or moved. | Asset Tag ID | As per Asset Name | L762534-[Designer alternative ID] | -
Dual Beam Detectors | L762535 | DBD | DUAL BEAM DETECTOR [nnn] | DUAL BEAM DETECTOR 001 | Yes | Dual beam detectors will have an Asset Tag Label attached to the physical item but in a position that shall not impair performance of the Equipment. This is because it is not expected to be regularly removed or moved. | Asset Tag ID | As per Asset Name | L762535-[Designer alternative ID] | -
Fire/smoke detectors | L762536 | FSD | SMOKE/FIRE DETECTOR [nnn] | SMOKE/FIRE DETECTOR 001 | Yes | An Asset Tag Label will be attached next to the fire/smoke detectors at a point of safety where it is easily visible. | Asset Tag ID | As per Asset Name | L762536-[Designer alternative ID] | -
Alarms/sounders | L76254 | ALS | ALARM/SOUNDER [nnn] | ALARM/SOUNDER 001 | Yes | Alarms/sounders will have an Asset Tag Label attached to the physical item but in a position that shall not impair performance of the equipment. This is because this asset is not expected to be a regularly serviced asset and it is not expected to be regularly removed or moved. | Asset Tag ID | As per Asset Name | L76254-[Designer alternative ID] | -
Manual Call Point | L76255 | MCP | MANUAL CALL POINT [nnn] | MANUAL CALL POINT 001 | Yes | Manual Call Points will have an Asset Tag attached to the physical item but in a position that shall not impair performance of the equipment. This is because this asset is not expected to be a regularly serviced asset and it is not expected to be regularly removed or moved. | Asset Tag ID | As per Asset Name | L76255-[Designer alternative ID] | -
Beacons | L76256 | BEA | BEACON [nnn] | BEACON 001 | Yes | Beacons will have an Asset Tag Label attached to the physical item but in a position that shall not impair performance of the equipment. This is because this asset is not expected to be a regularly serviced asset and it is not expected to be regularly removed or moved. | Asset Tag ID | As per Asset Name | L76256-[Designer alternative ID] | -
Fire Alarm Mid-Line Isolator | L76257 | FAI | FIRE ALARM ISOLATOR [nnn] | FIRE ALARM ISOLATOR 001 | Yes | An Asset Tag Label will be attached to the place where the asset is to be located | Asset Tag ID | As per Asset Name | L76257-[Designer alternative ID] | -
Cameras | L76261 | CAM | CAMERA [nnn] | CAMERA 001 | Yes | An Asset Tag Label will be attached to the place where the asset is to be located. See also CRL1-XRL-Z3-GUI-CR001-55071: Public Facing Labelling Guidance where asset is in public accessible area. | Asset Tag ID | As per Asset Name | L76261-[Designer alternative ID] | -
CCTV Keyboard | L76263 | CCK | CCTV KEYBOARD [nnn] | CCTV KEYBOARD 001 | Yes | An Asset Tag Label will be attached to place where the asset is to be located. | Asset Tag ID | As per Asset Name | L76263-[Designer alternative ID] | -
Data/Telephone Point | L76264 | DTP | DATA/TELEPHONE POINT [nnn] | DATA/TELEPHONE POINT 001 | No | - | - | - | - | -
Video Processor | L76265 | VIP | VIDEO PROCESSOR [nnn] | VIDEO PROCESSOR 001 | Yes | An Asset Tag Label will be attached adjacent to the place where the asset is to be located. | Asset Tag ID | As per Asset Name | L76265-[Designer alternative ID] | -
Patch Panel | L76266 | PPL | PATCH PANEL [nnn] | PATCH PANEL 001 | Yes | An Asset Tag Label will be attached adjacent to the place where the asset is to be located. | Asset Tag ID | As per Asset Name | L76266-[Designer alternative ID] | -
Phone | L763113 | PHN | PHONE [nnn] | PHONE 001 | No | - | - | - | - | -
Help Point Device | L7631221 | HPD | HELP POINT DEVICE [nnn] | HELP POINT DEVICE 001 | Yes | An Asset Tag Label will be attached to place where the asset is to be located. | Asset Tag ID | As per Asset Name | L7631221-[Designer alternative ID] | -
Mobile Communication Handset | L76314 | MCH | MOBILE HANDSET [nnn] | MOBILE HANDSET 001 | No | - | - | - | - | -
Dispatcher Terminal | L76315 | DIT | DISPATCHER TERMINAL [nnn] | DISPATCHER TERMINAL 006 | Yes | An Asset Tag Label will be attached adjacent to the place where the asset is to be located. | Asset Tag ID | As per Asset Name | L76315-[Designer alternative ID] | -
Digital controllers/outstations | L7641 | DCO | OUTSTATION [nnn] | OUTSTATION 001 | Yes | An Asset Tag Label will be placed on a permanent structure next to the item in a position that can be can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L7641-[Designer alternative ID] | -
Head end computer | L7642 | HEC | HEAD END COMPUTER [nnn] | HEAD END COMPUTER 001 | Yes | Head end computers will have an Asset Tag Label placed on a permanent structure next to the item in a position that can be can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L7642-[Designer alternative ID] | -
Analogue to digital converters | L7643 | ADC | ANALOGUE TO DIGITAL CONVERTOR [nnn] | ANALOGUE TO DIGITAL CONVERTOR 001 | Yes | An Asset Tag Label will be placed on a permanent structure next to the item in a position that can be can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L7643-[Designer alternative ID] | -
Gateway to DALI | L7644 | GTD | GATEWAY TO DALI [nnn] | GATEWAY TO DALI 001 | Yes | An Asset Tag Label will be placed on a permanent structure next to the item in a position that can be can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L7644-[Designer alternative ID] | -
Alarm printer | L7645 | ALP | ALARM PRINTER [nnn] | ALARM PRINTER 001 | Yes | Alarm printers will have an Asset Tag Label placed on a permanent structure next to the item in a position that can be can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L7645-[Designer alternative ID] | -
Fibre Optic Cable | L7662 | FOC | [CABLE TYPE]-[SOURCE]-[DESTINATION], [DESIGN ALTERNATIVE ASSET ID] | D-CAB-012-CAM-014, A-0011 | Yes | A cable shall be identified at each end, within 100m intervals in tunnels and either side of penetrations along its route. In each space through which it passes, within 500mm of its entry into/ exit from a space and within 500mm of each termination or joint. Refer to the Asset Identification Standard for example label images. Destination numbering must be consistent with 'LU11 SOR Interchange Communications Legacy Asset Numbering' document (CRL1-LU-R3-RGN-CR001-50004) | Asset Tag ID | [CABLE TYPE]-[SOURCE-nnn]-[DESTINATION-nnn] (i.e. C-CAB-012-FOS-014) | [Designer alternative ID] | -
Cable Connectors | L76631 | CCN | CABLE CONNECTOR [nnn] | CABLE CONNECTOR 001 | No | A schematic with the Asset Tag will identify the required location of the asset. | - | - | - | -
Coupler | L76632 | CPR | COUPLER [nnn] | COUPLER 001 | No | A schematic with the Asset Tag will identify the required location of the asset. | - | - | - | -
Diplexer/Combiner | L76633 | DPX | DIPLEXER [nnn] | DIPLEXER 001 | No | A schematic with the Asset Tag will identify the required location of the asset. | - | - | - | -
Fibre Master Unit | L76634 | FMU | FIBRE MASTER UNIT [nnn] | FIBRE MASTER UNIT 001 | No | A schematic with the Asset Tag will identify the required location of the asset. | - | - | - | -
Repeater Unit | L76635 | RPU | REPEATER UNIT [nnn] | REPEATER UNIT 001 | Yes | An Asset Tag Label will be placed on a permanent structure next to the item in a position that can be can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L76635-[Designer alternative ID] | -
Splitter | L76636 | SPL | SPLITTER [nnn] | SPLITTER 001 | Yes | An Asset Tag Label will be placed on a permanent structure next to the item in a position that can be can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L76636-[Designer alternative ID] | -
Firewall | L76637 | FRW | FIREWALL [nnn] | FIREWALL 001 | No | A schematic with the Asset Tag will identify the required location of the asset. | - | - | - | -
RTU Equipment (Remote Terminal Unit) | L76639 | RTU | REMOTE TERMINAL UNIT [nnn] | REMOTE TERMINAL UNIT 001 | Yes | An Asset Tag Label will be placed on a permanent structure next to the item in a position that can be can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L76639-[Designer alternative ID] | -
Copper Based Communications Cable | L7664 | CCC | [CABLE TYPE]-[SOURCE]-[DESTINATION] [DRAWING/SCHEMATIC ID] | D-CAB-012-CAM-014 A-0011 | Yes | A cable shall be identified at each end, within 100m intervals in tunnels and either side of penetrations along its route. In each space through which it passes, within 500mm of its entry into/ exit from a space and within 500mm of each termination or joint. Refer to the Asset Identification Standard for example label images. | Asset Tag ID | [CABLE TYPE]-[SOURCE-nnn]-[DESTINATION-nnn] (i.e. C-CAB-012-FOS-014) | [Designer alternative ID] | -
Ethernet Cable | L7665 | ETC | [CABLE TYPE]-[SOURCE]-[DESTINATION], [DESIGN ALTERNATIVE ASSET ID] | D-CAB-012-CAM-014, A-0011 | Yes | A cable shall be identified at each end, within 100m intervals in tunnels and either side of penetrations along its route. In each space through which it passes, within 500mm of its entry into/ exit from a space and within 500mm of each termination or joint. Refer to the Asset Identification Standard for example label images. Destination numbering must be consistent with 'LU11 SOR Interchange Communications Legacy Asset Numbering' document (CRL1-LU-R3-RGN-CR001-50004) | Asset Tag ID | [CABLE TYPE]-[SOURCE-nnn]-[DESTINATION-nnn] (i.e. C-CAB-012-FOS-014) | [Designer alternative ID] | -
Leaky Feeder Cable | L7666 | LFC | [CABLE TYPE]-[SOURCE]-[DESTINATION], [DESIGN ALTERNATIVE ASSET ID] | D-CAB-012-CAM-014, A-0011 | Yes | A cable shall be identified at each end, within 100m intervals in tunnels and either side of penetrations along its route. In each space through which it passes, within 500mm of its entry into/ exit from a space and within 500mm of each termination or joint. Refer to the Asset Identification Standard for example label images. Destination numbering must be consistent with 'LU11 SOR Interchange Communications Legacy Asset Numbering' document (CRL1-LU-R3-RGN-CR001-50004) | Asset Tag ID | [CABLE TYPE]-[SOURCE-nnn]-[DESTINATION-nnn] (i.e. C-CAB-012-FOS-014) | [Designer alternative ID] | -
DALI | L767 | DAL | DALI [nnn] | DALI 001 | Yes | An Asset Tag Label will be placed on a permanent structure next to the item in a position that can be can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L767-[Designer alternative ID] | -
Fibre Optic Splice Cabinet | L7681 | FSC | FIBRE OPTIC SPLICE CABINET [nnn] {OR} FIBRE OPTIC SPLICE CABINET [xxx/xxx - xxx/xxx] | FIBRE OPTIC SPLICE CABINET 001 {OR} FIBRE OPTIC SPLICE CABINET MJD/ISA - VBA/GOD | Yes | An Asset Tag Label will be attached to place where the asset is to be located. | Asset Tag ID | As per Asset Name | L7681-[Designer alternative ID] | -
Network Card | L76810 | NWC | NETWORK CARD [nnn] | NETWORK CARD 001 | No | A schematic with the Asset Tag will identify the required location of the asset. | - | - | - | -
IP Gateway | L76812 | IPG | IP GATEWAY [nnn] | IP GATEWAY 001 | Yes | IP Gateways will have an Asset Tag Label, these will not be placed on the physical item but will be placed on a permanent structure next to the item in a position that can be viewed or where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L76812-[Designer alternative ID] | -
Transponder/RFID Tag | L76813 | TPR | TRANSPONDER [nnn] {OR} TRANSPONDER [xxx/xxx - xxx/xxx] | TRANSPONDER [nnn] {OR} TRANSPONDER [ABC/XYZ - WED/FRT] | Yes | An Asset Tag Label will be attached adjacent to the place where the asset is to be located. | Asset Tag ID | As per Asset Name | L76813-[Designer alternative ID] | -
Interface Converter | L76814 | ITC | INTERFACE CONVERTER [nnn] | INTERFACE CONVERTER 003 | Yes | An Asset Tag Label will be attached adjacent to the place where the asset is to be located. | Asset Tag ID | As per Asset Name | L76814-[Designer alternative ID] | -
Modem | L76815 | MDM | MODEM [nnn] | MODEM 005 | Yes | An Asset Tag Label will be attached adjacent to the place where the asset is to be located. | Asset Tag ID | As per Asset Name | L76815-[Designer alternative ID] | -
Optical Distribution Frame | L76816 | ODF | OPTICAL DISTRIBUTION FRAME [nnn] | OPTICAL DISTRIBUTION FRAME 009 | Yes | An Asset Tag Label will be attached adjacent to the place where the asset is to be located. | Asset Tag ID | As per Asset Name | L76816-[Designer alternative ID] | -
Network Switches | L7683 | NWS | NETWORK SWITCH [nnn] | NETWORK SWITCH 001 | Yes | Network Switches will have an Asset Tag Label, these will not be placed on the physical item but will be placed on a permanent structure next to the item in a position that can be can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L7683-[Designer alternative ID] | -
Routers | L7684 | RTR | ROUTER [nnn] | ROUTER 001 | Yes | Routers will have an Asset Tag Label placed on a permanent structure next to the item in a position that can be can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L7684-[Designer alternative ID] | -
Data Recorder | L7685 | DAR | DATA RECORDER [nnn] | DATA RECORDER 001 | Yes | An Asset Tag Label will be placed on a permanent structure next to the item in a position that can be can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L7685-[Designer alternative ID] | -
Radio Base Station | L7687 | RBS | RADIO BASE STATION [nnn] {OR} RADIO BASE STATION [xxx/xxx-xxx/xxx] | RADIO BASE STATION 001 {OR} RADIO BASE STATION ABC/XYZ-EFG/PQR | Yes | An Asset Tag Label will be attached to the location of the base station. | Asset Tag ID | As per Asset Name | L7687-[Designer alternative ID] | -
Gantries | L7734 | GAN | GANTRY [nnn] | GANTRY 001 | Yes | An Asset Tag Label should be applied at the access point of the gantry on an easily visible point. If there is an access point on both sides then two labels should be used. | Asset Tag ID | As per Asset Name | L7734-[Designer alternative ID] | -
Cable Ducts (Troughs) | L78222 | CDT | CABLE DUCT [nnn] | CABLE DUCT 001 | Conditional | UTX Cable Ducts will have an Asset Tag Label All other cable ducts will not require an Asset Tag Label | Asset Tag ID | As per Asset Name | L78222-[Designer alternative ID] | -
Troughing | L7824 | TRG | TROUGHING [nnn] | TROUGHING 001 | No | - | - | - | - | -
Cable Containment | L7825 | CMS | CABLE CONTAINMENT [nnn] | CABLE CONTAINMENT 001 | Yes | Cable containment will require an asset tag for each independent CMS at each location (LCS code). Multiple labels may be required. Labels should be attached to the fixed part of the cable management system where it enters and exits each room as well as where it starts/ends e.g. at a junction with Plant. Labels are not required where containment is buried e.g. conduit within walls. | Asset Tag ID | As per Asset Name | L7825-[Designer alternative ID] | -
Thermal insulation and linings | L7841 | TIL | THERMAL INSULATION/LINING [nnn] | THERMAL INSULATION/LINING 001 | No | - | - | - | - | -
Liquid Level Switches | L786141 | LLS | LIQUID LEVEL SWITCH [nnn] | LIQUID LEVEL SWITCH 001 | Yes | Liquid level switches will have an Asset Tag Label attached to the physical item but in a position that shall not impair performance of the equipment. This is because this asset is not expected to be a regularly serviced asset and it is not expected to be regularly removed or moved. | Asset Tag ID | As per Asset Name | L786141-[Designer alternative ID] | -
Hydrocarbon detector | L78617 | HCD | HYDROCARBON DETECTOR [nnn] | HYDROCARBON DETECTOR 001 | Yes | Hydrocarbon detectors will have an Asset Tag Label attached to the physical item but in a position that shall not impair performance of the equipment. This is because this asset is not expected to be a regularly serviced asset and it is not expected to be regularly removed or moved. | Asset Tag ID | As per Asset Name | L78617-[Designer alternative ID] | -
Gas detector | L78618 | GDR | GAS DETECTOR [nnn] | GAS DETECTOR 001 | Yes | Gas detectors will have an Asset Tag Label attached to the physical item but in a position that shall not impair performance of the equipment. This is because this asset is not expected to be a regularly serviced asset and it is not expected to be regularly removed or moved. | Asset Tag ID | As per Asset Name | L78618-[Designer alternative ID] | -
Leak detection | L78621 | LDR | LEAK DETECTOR [nnn] | LEAK DETECTOR 001 | No | The Asset Tag Label will be placed on the Functional Unit the detection is serving. | - | - | - | -
Control Panel | L7864 | CPL | CONTROL PANEL [nnn] | CONTROL PANEL 001 | Yes | An Asset Tag Label will be placed on a permanent structure next to the item in a position that can be can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L7864-[Designer alternative ID] | -
Stilling Tubes | L7866 | STT | STILLING TUBE [nnn] | STILLING TUBE 001 | Yes | Asset Tag labels will not be attached to the stilling tube but will be placed on a permanent structure next to the item. The Asset Tag Label will be grouped with the other Asset Tag Labels associated with the sump in a position that can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L7866-[Designer alternative ID] | -
Bollards | L81101 | BOL | BOLLARDS [nnn] {OR} BOLLARD [nnn] | BOLLARDS 011 {OR} BOLLARD 011 | No | - | - | - | - | -
Security Mirror | L81106 | SMI | SECURITY MIRROR [nnn] | SECURITY MIRROR 002 | Yes | An Asset Tag Label will be attached adjacent to the place where the asset is to be located. | Asset Tag ID | As per Asset Name | L81106-[Designer alternative ID] | -
Pedestrian signs, finger posts | L81112 | PES | PEDESTRIAN SIGNAGE [nnn] | PEDESTRIAN SIGNAGE 001 | No | The Asset Tag Label is not required on each individual sign. The Asset Tag is related to the device the sign is located/attached at e.g. Bridge, Platform. | - | - | - | -
Retractable Mounting System | L81115 | RMS | RETRACTABLE MOUNTING SYSTEM [nnn] | RETRACTABLE MOUNTING SYSTEM 001 | Yes | An Asset Tag Label shall be attached to the base or adjacent permanent structure. | Asset Tag ID | As per Asset Name | L81115-[Designer alternative ID] | -
Benches | L82255 | BEN | BENCH [nnn] | BENCH 001 | Yes | A bench will only have a label for the Asset Tag attached to the physical item on underside of the bench at either end of the asset. See also CRL1-XRL-Z3-GUI-CR001-50071: Public Facing Labelling Guidance where asset is in public accessible area. | Asset Tag ID | As per Asset Name | L82255-[Designer alternative ID] | -
Memory Card | L825131 | MMC | MEMORY CARD [nnn] | MEMORY CARD 001 | No | A schematic with the Asset Tag Label will identify the required location of the asset. | - | - | - | -
Platform Edge Support Brackets | L8262 | PSB | PLATFORM EDGE SUPPORT BRACKET [nnn] | PLATFORM EDGE SUPPORT BRACKET 001 | Yes | An Asset Tag label will be attached to the asset in a way that does not affect its performance. | Asset Tag ID | As per Asset Name | L8262-[Designer alternative ID] | -
Kitchen furniture | L831 | KIT | [FURNITURE TYPE] [nnn] | CUPBOARD 001 | Yes | An Asset Tag Label is to be placed in a discreet location that is accessible but not in immediate line of sight on the external part of the item. | Asset Tag ID | As per Asset Name | L831-[Designer alternative ID] | -
Fixed Panels with digital screens | L84521 | FDS | DIGITAL SCREEN [nnn] | DIGITAL SCREEN 001 | No | A cable shall be identified within 500mm of its entry into / exit from a space and within 500mm of each termination or joint. Refer to the Asset Identification Standard for example label images. Destination numbering must be consistent with 'LU11 SOR Interchange Communications Legacy Asset Numbering' document (CRL1-LU-R3-RGN-CR001-50004) | - | - | - | -
Work Station | L853121 | WKS | WORK STATION [nnn] | WORK STATION 001 | Yes | An Asset Tag Label will be attached to place where the asset is to be located. | Asset Tag ID | As per Asset Name | L853121-[Designer alternative ID] | -
Printer | L85344 | PRN | PRINTER [nnn] | PRINTER 001 | Yes | An Asset Tag Label will be attached to place where the asset is to be located. | Asset Tag ID | As per Asset Name | L85344-[Designer alternative ID] | -
Equipment Support Structure | L868 | ESU | EQUIPMENT SUPPORT STRUCTURE [nnnn] | EQUIPMENT SUPPORT STRUCTURE 1975 | Yes | An Asset Tag label shall be attached to the Equipment Support Structure itself in a position that shall not interfere with its performance. | Asset Tag ID | As per Asset Name | L868-[Designer alternative ID] | -
Totem | L869 | TTM | TOTEM [nnn] | TOTEM 001 | Yes | A totem will only be labelled with a metallic Asset Tag and this will be located at the base section. | Asset Tag ID | As per Asset Name | L869-[Designer alternative ID] | -
Master Clock | L87351 | MCL | MASTER CLOCK [nnn] | MASTER CLOCK 001 | Yes | An Asset Tag Labels will be placed on a permanent structure next to the item in a position that can be can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L87351-[Designer alternative ID] | -
Station Clock | L87352 | SCL | STATION CLOCK [nnn] | STATION CLOCK 001 | Yes | An Asset Tag Label will be placed on a permanent structure next to the item in a position that can be can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. See also CRL1-XRL-Z3-GUI-CR001-50071: Public Facing Labelling Guidance where asset is in public accessible area. | Asset Tag ID | As per Asset Name | L87352-[Designer alternative ID] | -
Fire extinguishers | L881 | FEX | FIRE EXTINGUISHER [nnn] | FIRE EXTINGUISHER 001 | Yes | Fire extinguishers will have an Asset Tag Label placed on a permanent structure next to the item in a position that can be can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered. | Asset Tag ID | As per Asset Name | L881-[Designer alternative ID] | -
Cabinets around PHPs | L892 | CAP | HELP POINT FRAME [nnn] | HELP POINT FRAME 001 | Yes | The Asset Tag Label will be placed adjacent to the frame such as on the platform wall or within the frame inner section. See also CRL1-XRL-Z3-GUI-CR001-50071: Public Facing Labelling Guidance where asset is in public accessible area. | Asset Tag ID | As per Asset Name | L892-[Designer alternative ID] | -
Note on F3: No = No Asset Tag Label Required Yes = Asset Tag Label Required Con = Conditional

## PFU Naming Convention
|  | Asset Code (when assigning Cable to Asset) | Asset Tag Naming Information |  | Asset Tag Labelling Information
Class Name | Class Code |  | Asset Tag Naming Convention | Naming Example(s) | Asset Tag Label Required? | Asset Tag Label Instructions | Label Line 1 Convention | Label Line 2 Convention | Label Line 3 Convention | Label Line 4 Convention
Door System (Arch) | PFU001 | - | Door System (Arch) [nn] at [Location] | Door System (Arch) 01 at Paddington Station | No | - | - | - | - | -
Floor System | PFU002 | - | Floor System [nn] at [Location] | Floor System 01 at Paddington Station | No | - | - | - | - | -
Furniture System | PFU003 | - | Furniture System [nn] at [Location] | Furniture System 01 at Paddington Station | No | - | - | - | - | -
Roof System | PFU005 | - | Roof System [nn] at [Location] | Roof System 01 at Paddington Station | No | - | - | - | - | -
Wall Cladding System | PFU006 | - | Wall Cladding System [nn] at [Location] | Wall Cladding System 01 at Paddington Station | No | - | - | - | - | -
Cross Passage | PFU007 | - | Cross Passage [nn] at [Location] | Cross Passage 01 at Tottenham Court Road Station | Conditional | An Asset Tag Label to be fixed at each end (start and finish) of the Cross Passage. Lables should only be used in the route sections and not at Stations. | - | - | - | -
Concourse | PFU010 | - | Concourse [nn] at [Location] | Concourse 01 at Paddington Station | No | - | - | - | - | -
Passageway Connecting Tunnel | PFU011 | - | Passageway Connecting Tunnel [nn] at [Location] | Passageway Connecting Tunnel 01 at Tottenham Court Road Station | Conditional | An Asset Tag Label is to be fixed at each end (start and finish) of the Passageway Connecting Tunnel. Labels are not required at LU stations. | - | - | - | -
Shaft | PFU013 | - | Shaft [nn] at [Location] | Shaft 01 at Tottenham Court Road Station | No | - | - | - | - | -
Tunnel System | PFU015 | - | Tunnel System at [Location] | Tunnel System at Paddington Station to Bond Street Station | No | - | - | - | - | -
Surface Building | PFU018 | - | Surface Building [nn] at [Location] | Surface Building 01 at Custom House Station | No | - | - | - | - | -
Underground Box Structure | PFU019 | - | Underground Box Structure [nn] at [Location] | Underground Box Structure 01 at Paddington Station | No | - | - | - | - | -
Retaining Walls | PFU020 | - | Retaining Walls [nn] at [Location] | Retaining Walls 01 at Paddington Station | No | - | - | - | - | -
Linear Structural Staircase | PFU021 | - | Linear Structural Staircase [nn] at [Location] | Linear Structural Staircase 01 at Paddington Station | No | - | - | - | - | -
Escalator Slab | PFU022 | - | Escalator Slab [nn] at [Location] | Escalator Slab 01 at Paddington Station | No | - | - | - | - | -
Bridge System | PFU023 | - | Bridge System [nn] at [Location] | Bridge System 01 at Paddington Station | Yes | An Asset Tag Label to be fixed at Track level on the abutment wall | - | - | - | -
Building Management System (BMS) | PFU024 | - | Building Management System (BMS) [nn] at [Location] | Building Management System (BMS) 01 at Paddington Station | No | - | - | - | - | -
Public Address / Voice Alarm (PA/VA) | PFU025 | - | Public Address / Voice Alarm (PA/VA) [nn] at [Location] | Public Address / Voice Alarm (PA/VA) 01 at Paddington Station | No | - | - | - | - | -
Customer Information System (CIS) | PFU026 | - | Customer Information System (CIS) [nn] at [Location] | Customer Information System (CIS) 01 at Paddington Station | No | - | - | - | - | -
GSM-R Radio System | PFU027 | - | GSM-R Radio System | GSM-R Radio System | No | - | - | - | - | -
Airwave Radio System (ACRL) | PFU028 | - | Airwave Radio System (ACRL) | Airwave Radio System (ACRL) | No | - | - | - | - | -
LFEPA Radio System | PFU029 | - | LFEPA Radio System | LFEPA Radio System | No | - | - | - | - | -
Public Cellular Radio (PCR) Radiating Infrastructure | PFU030 | - | Public Cellular Radio (PCR) Radiating Infrastructure | Public Cellular Radio (PCR) Radiating Infrastructure | No | - | - | - | - | -
Telephone System | PFU031 | - | Telephone System | Telephone System | No | - | - | - | - | -
Station Management System | PFU032 | - | Station Management System [nn] at [Location] | Station Management System 01 at Paddington Station | No | - | - | - | - | -
Central Management System SCADA | PFU033 | - | Central Management System SCADA | Central Management System SCADA | No | - | - | - | - | -
Optical Fibre Network | PFU034 | - | Optical Fibre Network | Optical Fibre Network | No | - | - | - | - | -
Crossrail Data Network (CDN) | PFU035 | - | Crossrail Data Network (CDN) | Crossrail Data Network (CDN) | No | - | - | - | - | -
Private Mobile Radio (PMR) Radiating Infrastructure | PFU036 | - | Private Mobile Radio (PMR) Radiating Infrastructure | Private Mobile Radio (PMR) Radiating Infrastructure | No | - | - | - | - | -
Cable Management System (Linear) | PFU037 | - | Cable Management System (Linear) | Cable Management System (Linear) | No | - | - | - | - | -
Overhead Line Equipment (OLE) | PFU038 | - | Overhead Line Equipment (OLE) | Overhead Line Equipment (OLE) | No | - | - | - | - | -
Track System Plain Line | PFU039 | - | Track System Plain Line | Track System Plain Line | No | - | - | - | - | -
Switches & Crossings (S&C) | PFU040 | - | Switches & Crossings (S&C) | Switches & Crossings (S&C) | No | - | - | - | - | -
Tunnel: Fire Main (TFM) | PFU041 | - | Tunnel: Fire Main (TFM) | Tunnel: Fire Main (TFM) | No | - | - | - | - | -
Track Drainage | PFU042 | - | Track Drainage [nn] | Track Drainage [nn] | No | - | - | - | - | -
Closed Circuit Television (CCTV) | PFU045 | - | Closed Circuit Television (CCTV) [nn] at [Location] | Closed Circuit Television (CCTV) 01 at Paddington Station | No | - | - | - | - | -
Door System (M&E) | PFU046 | - | Door System (M&E) [nn] at [Location] | Door System (M&E) 01 at Paddington Station | No | - | - | - | - | -
Driver Only Operation (DOO) CCTV | PFU047 | - | Driver Only Operation (DOO) CCTV [nn] at [Location] | Driver Only Operation (DOO) CCTV 01 at Paddington Station | No | - | - | - | - | -
Earthing System (Traction) | PFU048 | - | Earthing System (Traction) [nn] at [Location] | Earthing System (Traction) 01 at Paddington Station | No | - | - | - | - | -
Escalator | PFU049 | - | Escalator [nn] at [Location] | Escalator 01 at Paddington Station | Yes | One PFU label shall be located at the castell isolator for each PFU instance | - | - | - | -
Fire Detection/Protection System | PFU050 | - | Fire Detection/Protection System [nn] at [Location] | Fire Detection/Protection System 01 at Paddington Station | No | - | - | - | - | -
Flood Protection Barriers System | PFU051 | - | Flood Protection Barriers System [nn] at [Location] | Flood Protection Barriers System 01 at Paddington Station | No | - | - | - | - | -
Heating, Ventilation and Air Condition System (HVAC) | PFU052 | - | Heating, Ventilation and Air Condition System (HVAC) [nn] at [Location] | Heating, Ventilation and Air Condition System (HVAC) 01 at Paddington Station | No | - | - | - | - | -
Traction Power System | PFU053 | - | Traction Power System [nn] at [Location] | Traction Power System 01 at Paddington Station | No | - | - | - | - | -
Fire Suppression and Compartmentation System | PFU054 | - | Fire Suppression and Compartmentation System [nn] at [Location] | Fire Suppression and Compartmentation System 01 at Paddington Station | No | - | - | - | - | -
Lift | PFU055 | - | Lift [nn] at [Location] | Lift 01 at Paddington Station | Yes | One PFU label shall be located at the castell isolator for each PFU instance | - | - | - | -
Lighting (LGT) | PFU057 | - | Lighting (LGT) [nn] at [Location] | Lighting (LGT) 01 at Paddington Station | No | - | - | - | - | -
Lighting Control System (DALI) | PFU058 | - | Lighting Control System (DALI) [nn] at [Location] | Lighting Control System (DALI) 01 at Paddington Station | No | - | - | - | - | -
Lightning Protection System | PFU059 | - | Lightning Protection System [nn] at [Location] | Lightning Protection System 01 at Paddington Station | No | - | - | - | - | -
LV Power System | PFU061 | - | LV Power System [nn] at [Location] | LV Power System 01 at Paddington Station | No | - | - | - | - | -
Sanitary Equipment System | PFU063 | - | Sanitary Equipment System [nn] at [Location] | Sanitary Equipment System 01 at Paddington Station | No | - | - | - | - | -
Shaft Pressurisation System | PFU064 | - | Shaft Pressurisation System [nn] at [Location] | Shaft Pressurisation System 01 at Paddington Station | No | - | - | - | - | -
Signage (SGN) | PFU065 | - | Signage (SGN) [nn] at [Location] | Signage (SGN) 01 at Paddington Station | No | - | - | - | - | -
Tunnel Ventilation System (TVS) | PFU066 | - | Tunnel Ventilation System (TVS) | Tunnel Ventilation System (TVS) | No | - | - | - | - | -
Tunnel: Walkway System (TWS) | PFU067 | - | Tunnel: Walkway System (TWS) | Tunnel: Walkway System (TWS) | No | - | - | - | - | -
Uninterruptible Power Supply (UPS) | PFU069 | - | Uninterruptible Power Supply (UPS) [nn] at [Location] | Uninterruptible Power Supply (UPS) 01 at Paddington Station | No | - | - | - | - | -
Water Distribution System | PFU070 | - | Water Distribution System [nn] at [Location] | Water Distribution System 01 at Paddington Station | No | - | - | - | - | -
Local Drainage Foul Water System | PFU072 | - | Local Drainage Foul Water System [nn] at [Location] | Local Drainage Foul Water System 01 at Paddington Station | No | - | - | - | - | -
Local Drainage Non-Foul Water System | PFU073 | - | Local Drainage Non-Foul Water System [nn] at [Location] | Local Drainage Non-Foul Water System 01 at Paddington Station | No | - | - | - | - | -
S&CS - Automatic Train Control (ATC) | PFU074 | - | S&CS - Automatic Train Control (ATC) | S&CS - Automatic Train Control (ATC) | No | - | - | - | - | -
S&CS - Automatic Train Supervision (ATS) | PFU075 | - | S&CS - Automatic Train Supervision (ATS) | S&CS - Automatic Train Supervision (ATS) | No | - | - | - | - | -
S&CS - Interlocking (IXL) | PFU076 | - | S&CS - Interlocking (IXL) | S&CS - Interlocking (IXL) | No | - | - | - | - | -
S&CS - Radio Communication System (RCS) | PFU077 | - | S&CS - Radio Communication System (RCS) | S&CS - Radio Communication System (RCS) | No | - | - | - | - | -
Advertising Screens System | PFU043 | - | Advertising Screens System [nn] at [Location] | Advertising Screens System 01 at Paddington Station | No | - | - | - | - | -
Platform Screen Doors (PSD) | PFU078 | - | Platform Screen Doors (PSD) [nn] at [Location] | Platform Screen Doors (PSD) 01 at Paddington Station | No | - | - | - | - | -
Access Gantry | PFU079 | - | Access Gantry [nn] at [Location] | Access Gantry 01 at Paddington Station | No | - | - | - | - | -
Lift Support Tower | PFU081 | - | Lift Support Tower [nn] at [Location] | Lift Support Tower 01 at Custom House Station | Yes | An Asset Tag Label is to be fixed to the Bottom and upper levels of the Support Tower | - | - | - | -
HV System (Non-Traction) | PFU083 | - | HV System (Non-Traction) [nn] at [Location] | HV System (Non-Traction) 01 at Paddington Station | No | - | - | - | - | -
Equipment Cabinets | PFU084 | - | Equipment Cabinets [nn] at [Location] | Equipment Cabinets 01 at Paddington Station | No | - | - | - | - | -
Structural Foundation System | PFU086 | - | Structural Foundation System [nn] at [Location] | Structural Foundation System 01 at Paddington Station | No | - | - | - | - | -
Earthing System (Facility) | PFU085 | - | Earthing System (Facility) [nn] at [Location] | Earthing System (Facility) 01 at Paddington Station | No | - | - | - | - | -
Non-Structural Walls | PFU087 | - | Non-Structural Walls [nn] at [Location] | Non-Structural Walls 01 at Paddington Station | No | - | - | - | - | -
Link Tunnel | PFU088 | - | Link Tunnel [nn] at [Location] | Link Tunnel 01 at Paddington Station | Yes | An Asset Tag Label is to be fixed at each end (start and finish) of the Link Tunnel at a height and position for it to be read from a safe position e.g. adjacent to the walkway at head height | - | - | - | -
Platform Structure | PFU089 | - | Platform Structure [A or B] at [Location] | Platform Structure A at Paddington Station | Yes | An Asset Tag Label is to be fixed at each end (start and finish) of the Platform Structure | - | - | - | -
Safety Protection System | PFU090 | - | Safety Protection System [nn] at [Location] | Safety Protection System 01 at Paddington Station | No | - | - | - | - | -
Window System | PFU091 | - | Window System [nn] at [Location] | Window System 01 at Paddington Station | No | - | - | - | - | -
Suspended Ceiling System | PFU092 | - | Suspended Ceiling System [nn] at [Location] | Suspended Ceiling System 01 at Paddington Station | No | - | - | - | - | -
Cable Management System (Geographic) | PFU093 | - | Cable Management System (Geographic) [nn] at [Location] | Cable Management System (Geographic) 01 at Paddington Station | No | - | - | - | - | -
Adit | PFU094 | - | Adit [nn] at [Location] | Adit 01 at Paddington Station | Yes | Label to be fixed at each end (start and finish) of the Adit. | - | - | - | -
Portal Frame Structure | PFU095 | - | Portal Frame Structure [nn] at [Location] | Portal Frame Structure 01 at Pudding Mill Lane | Yes | At each end of the Portal Frame Structure at Track level | - | - | - | -
Crane System | PFU096 | - | Crane System [nn] at [Location] | Crane System 01 at Victoria Dock Portal | No | - | - | - | - | -
Note on F3: No = No Asset Tag Label Required Yes = Asset Tag Label Required Con = Conditional

## FU Naming Convention
|  | Asset Code (when assigning Cable to Asset) | Asset Tag Naming Information |  | Asset Tag Labelling Information
Class Name | Class Code |  | Asset Tag Naming Convention | Naming Example(s) | Asset Tag Label Required? | Asset Tag Label Instructions | Label Line 1 Convention | Label Line 2 Convention | Label Line 3 Convention | Label Line 4 Convention
Step Plate Junction | FU001 | - | Step Plate Junction [nnn] at [Location] | Step Plate Junction 001 at Bond Street Station | Yes | An Asset Tag Label to be fixed at each end (start and finish) of the Step Plate Junction at a height and position for it to be read from a safe position e.g. adjacent to the walkway at head height | - | - | - | -
BMS Head End Computer | FU002 | - | BMS Head End Computer [nnn] at [Location] | BMS Head End Computer 001 at Bond Street Station | No | - | - | - | - | -
BMS LAN Network | FU003 | - | BMS LAN Network [nnn] at [Location] | BMS LAN Network 001 at Bond Street Station | No | - | - | - | - | -
BMS Outstation | FU005 | - | BMS Outstation [nnn] at [Location] | BMS Outstation 001 at Bond Street Station | No | - | - | - | - | -
Escalator Motor/Drive Controls | FU006 | - | Escalator Motor/Drive Controls [nnn] at [Location] | Escalator Motor/Drive Controls 001 at Bond Street Station | No | - | - | - | - | -
Escalator Balustrade | FU007 | - | Escalator Balustrade [nnn] at [Location] | Escalator Balustrade 001 at Bond Street Station | No | - | - | - | - | -
Escalator Truss Structure | FU008 | - | Escalator Truss [nnn] at [Location] | Escalator Truss 001 at Bond Street Station | No | - | - | - | - | -
Escalator Steps | FU009 | - | Escalator Steps [nnn] at [Location] | Escalator Steps 001 at Bond Street Station | No | - | - | - | - | -
Ventilation System | FU010 | - | Ventilation System [nnn] at [Location] | Ventilation System 001 at Bond Street Station | No | - | - | - | - | -
VRF/DX Heating & Cooling System | FU011 | - | VRF/DX Heating & Cooling System [nnn] at [Location] | VRF/DX Heating & Cooling System 001 at Bond Street Station | No | - | - | - | - | -
Local Heating System | FU012 | - | Local Heating System [nnn] at [Location] | Local Heating System 001 at Bond Street Station | No | - | - | - | - | -
Chilled Water Distribution System | FU013 | - | Chilled Water Distribution System [nnn] at [Location] | Chilled Water Distribution System 001 at Bond Street Station | No | - | - | - | - | -
Lift Roping System | FU015 | - | Lift Roping System [nnn] at [Location] | Lift Roping System 001 at Bond Street Station | No | - | - | - | - | -
Lift Car Assembly | FU016 | - | Lift Car [nnn] at [Location] | Lift Car 001 at Bond Street Station | No | - | - | - | - | -
Lift Communications & Control System | FU017 | - | Lift Communications & Control System [nnn] at [Location] | Lift Communications & Control System 001 at Bond Street Station | No | - | - | - | - | -
Lift Motor/Drive | FU018 | - | Lift Motor/Drive [nnn] at [Location] | Lift Motor/Drive 001 at Bond Street Station | No | - | - | - | - | -
Emergency Lighting | FU019 | - | Emergency Lighting [nnn] at [Location] | Emergency Lighting 001 at Bond Street Station | No | - | - | - | - | -
User Control Subsystem (DALI) | FU020 | - | User Control Subsystem (DALI) [nnn] at [Location] | User Control Subsystem (DALI) 001 at Bond Street Station | No | - | - | - | - | -
Network Devices Subsystem (DALI) | FU021 | - | Network Devices Subsystem (DALI) [nnn] at [Location] | Network Devices Subsystem (DALI) 001 at Bond Street Station | No | - | - | - | - | -
Main Switchboard | FU022 | - | Main Switchboard [nnn] at [Location] | Main Switchboard 001 at Bond Street Station | No | - | - | - | - | -
Distribution Boards | FU023 | - | Distribution Boards [nnn] at [Location] | Distribution Boards 001 at Bond Street Station | No | - | - | - | - | -
Electronic Signage | FU024 | - | Electronic Signage [nnn] at [Location] | Electronic Signage 001 at Bond Street Station | No | - | - | - | - | -
Non-electronic Signage | FU025 | - | Non-electronic Signage [nnn] at [Location] | Non-electronic Signage 001 at Bond Street Station | No | - | - | - | - | -
Primary Control System (RCC/BUCF) | FU027 | - | Primary Control System (RCC/BUCF) [nnn] at [Location] | Primary Control System (RCC/BUCF) 001 at Bond Street Station | No | - | - | - | - | -
Secondary Control System (local control) | FU028 | - | Secondary Control System (local control) [nnn] at [Location] | Secondary Control System (local control) 001 at Bond Street Station | No | - | - | - | - | -
Domestic Water Normal Supply | FU030 | - | Domestic Water Normal Supply [nnn] at [Location] | Domestic Water Normal Supply 001 at Bond Street Station | No | - | - | - | - | -
Domestic Water Boosted Supply | FU031 | - | Domestic Water Boosted Supply [nnn] at [Location] | Domestic Water Boosted Supply 001 at Bond Street Station | No | - | - | - | - | -
Domestic Hot Water Supply | FU032 | - | Domestic Hot Water Supply [nnn] at [Location] | Domestic Hot Water Supply 001 at Bond Street Station | No | - | - | - | - | -
Fire Suppression Water Supply | FU033 | - | Fire Suppression Water Supply [nnn] at [Location] | Fire Suppression Water Supply 001 at Bond Street Station | No | - | - | - | - | -
Amplification Sub-system | FU034 | - | Amplification Sub-system [nnn] at [Location] | Amplification Sub-system 001 at Bond Street Station | No | - | - | - | - | -
Input Subsystem | FU035 | - | Input Subsystem [nnn] at [Location] | Input Subsystem 001 at Bond Street Station | No | - | - | - | - | -
Output Subsystem | FU036 | - | Output Subsystem [nnn] at [Location] | Output Subsystem 001 at Bond Street Station | No | - | - | - | - | -
CIS Control Subsystem | FU037 | - | CIS Control Subsystem [nnn] at [Location] | CIS Control Subsystem 001 at Bond Street Station | No | - | - | - | - | -
CIS Display Subsystem | FU038 | - | CIS Display Subsystem [nnn] at [Location] | CIS Display Subsystem 001 at Bond Street Station | No | - | - | - | - | -
GSM-R Network Subsystem | FU039 | - | GSM-R Network Subsystem [nnn] at [Location] | GSM-R Network Subsystem 001 at Bond Street Station | No | - | - | - | - | -
GSM-R RF Subsystem | FU040 | - | GSM-R RF Subsystem [nnn] at [Location] | GSM-R RF Subsystem 001 at Bond Street Station | No | - | - | - | - | -
GSM-R Trainborne Subsystem | FU041 | - | GSM-R Trainborne Subsystem [nnn] at [Location] | GSM-R Trainborne Subsystem 001 at Bond Street Station | No | - | - | - | - | -
ACRL Network Subsystem | FU042 | - | ACRL Network Subsystem [nnn] at [Location] | ACRL Network Subsystem 001 at Bond Street Station | No | - | - | - | - | -
ACRL RF Subsystem | FU043 | - | ACRL RF Subsystem [nnn] at [Location] | ACRL RF Subsystem 001 at Bond Street Station | No | - | - | - | - | -
LFEPA Network Subsystem | FU044 | - | LFEPA Network Subsystem [nnn] at [Location] | LFEPA Network Subsystem 001 at Bond Street Station | No | - | - | - | - | -
LFEPA RF Subsystem | FU045 | - | LFEPA RF Subsystem [nnn] at [Location] | LFEPA RF Subsystem 001 at Bond Street Station | No | - | - | - | - | -
PCR Network Subsystem | FU046 | - | PCR Network Subsystem [nnn] at [Location] | PCR Network Subsystem 001 at Bond Street Station | No | - | - | - | - | -
PCR RF Subsystem | FU047 | - | PCR RF Subsystem [nnn] at [Location] | PCR RF Subsystem 001 at Bond Street Station | No | - | - | - | - | -
Telephony Network Subsystem | FU048 | - | Telephony Network Subsystem [nnn] at [Location] | Telephony Network Subsystem 001 at Bond Street Station | No | - | - | - | - | -
Help Point Subsystem | FU049 | - | Help Point Subsystem [nnn] at [Location] | Help Point Subsystem 001 at Bond Street Station | No | - | - | - | - | -
Telephony Subsystem | FU050 | - | Telephony Subsystem [nnn] at [Location] | Telephony Subsystem 001 at Bond Street Station | No | - | - | - | - | -
SMS Server Subsystem | FU051 | - | SMS Server Subsystem [nnn] at [Location] | SMS Server Subsystem 001 at Bond Street Station | No | - | - | - | - | -
SMS Workstation Subsystem | FU052 | - | SMS Workstation Subsystem [nnn] at [Location] | SMS Workstation Subsystem 001 at Bond Street Station | No | - | - | - | - | -
SMS RTU Subsystem | FU053 | - | SMS RTU Subsystem [nnn] at [Location] | SMS RTU Subsystem 001 at Bond Street Station | No | - | - | - | - | -
CMS Server Subsystem | FU054 | - | CMS Server Subsystem [nnn] at [Location] | CMS Server Subsystem 001 at Bond Street Station | No | - | - | - | - | -
CMS Workstation Subsystem | FU055 | - | CMS Workstation Subsystem [nnn] at [Location] | CMS Workstation Subsystem 001 at Bond Street Station | No | - | - | - | - | -
CMS RTU Subsystem | FU056 | - | CMS RTU Subsystem [nnn] at [Location] | CMS RTU Subsystem 001 at Bond Street Station | No | - | - | - | - | -
Core Network Subsystem (OFN) | FU057 | - | Core Network Subsystem (OFN) [nnn] at [Location] | Core Network Subsystem (OFN) 001 at Bond Street Station | No | - | - | - | - | -
Access Network Subsystem (OFN) | FU058 | - | Access Network Subsystem (OFN) [nnn] at [Location] | Access Network Subsystem (OFN) 001 at Bond Street Station | No | - | - | - | - | -
Core Network Subsystem (CDN) | FU059 | - | Core Network Subsystem (CDN) [nnn] at [Location] | Core Network Subsystem (CDN) 001 at Bond Street Station | No | - | - | - | - | -
Access Network Subsystem (CDN) | FU060 | - | Access Network Subsystem (CDN) [nnn] at [Location] | Access Network Subsystem (CDN) 001 at Bond Street Station | No | - | - | - | - | -
Master Clock Subsystem | FU061 | - | Master Clock Subsystem [nnn] at [Location] | Master Clock Subsystem 001 at Bond Street Station | No | - | - | - | - | -
PMR Network Subsystem | FU062 | - | PMR Network Subsystem [nnn] at [Location] | PMR Network Subsystem 001 at Bond Street Station | No | - | - | - | - | -
PMR RF Subsystem | FU063 | - | PMR RF Subsystem [nnn] at [Location] | PMR RF Subsystem 001 at Bond Street Station | No | - | - | - | - | -
CCTV Control Sub-system | FU064 | - | CCTV Control Sub-system [nnn] at [Location] | CCTV Control Sub-system 001 at Bond Street Station | No | - | - | - | - | -
CCTV Workstation Subsystem | FU065 | - | CCTV Workstation Subsystem [nnn] at [Location] | CCTV Workstation Subsystem 001 at Bond Street Station | No | - | - | - | - | -
DOO CCTV Imaging Sub-system | FU066 | - | DOO CCTV Imaging Sub-system [nnn] at [Location] | DOO CCTV Imaging Sub-system 001 at Bond Street Station | No | - | - | - | - | -
DOO CCTV Control Sub-system | FU067 | - | DOO CCTV Control Sub-system [nnn] at [Location] | DOO CCTV Control Sub-system 001 at Bond Street Station | No | - | - | - | - | -
DOO CCTV Transmission Sub-system | FU068 | - | DOO CCTV Transmission Sub-system [nnn] at [Location] | DOO CCTV Transmission Sub-system 001 at Bond Street Station | No | - | - | - | - | -
DOO CCTV Local Recording Sub-system | FU070 | - | DOO CCTV Local Recording Sub-system [nnn] at [Location] | DOO CCTV Local Recording Sub-system 001 at Bond Street Station | No | - | - | - | - | -
Rigid bar system (ROC) | FU071 | - | Rigid bar system (ROC) [nnn] at [Location] | Rigid bar system (ROC) 001 at Bond Street Station | No | - | - | - | - | -
Overhead Catenary System (OCS) | FU072 | - | Overhead Catenary System (OCS) [nnn] at [Location] | Overhead Catenary System (OCS) 001 at Bond Street Station | No | - | - | - | - | -
Earth Mat (Substation or station) | FU073 | - | Earth Mat (Substation or station) [nnn] at [Location] | Earth Mat (Substation or station) 001 at Bond Street Station | No | - | - | - | - | -
Trackside Earth System | FU074 | - | Trackside Earth System [nnn] at [Location] | Trackside Earth System 001 at Bond Street Station | No | - | - | - | - | -
Autotransformer Site (ATS) | FU075 | - | Autotransformer Site (ATS) [nnn] at [Location] | Autotransformer Site (ATS) 001 at Bond Street Station | No | - | - | - | - | -
Sectioning Auto Transformer Site (SATS) indoor | FU076 | - | Sectioning Auto Transformer Site (SATS) indoor [nnn] at [Location] | Sectioning Auto Transformer Site (SATS) indoor 001 at Bond Street Station | No | - | - | - | - | -
Autotransformer Feeder Station (ATFS) | FU077 | - | Autotransformer Feeder Station (ATFS) [nnn] at [Location] | Autotransformer Feeder Station (ATFS) 001 at Bond Street Station | No | - | - | - | - | -
Substation | FU078 | - | Station Substation [nnn] at [Location] | Station Substation 001 at Bond Street Station | No | - | - | - | - | -
Fire Alarm System | FU082 | - | Fire Alarm System [nnn] at [Location] | Fire Alarm System 001 at Bond Street Station | No | - | - | - | - | -
Fire Mains | FU083 | - | Fire Mains [nnn] at [Location] | Fire Mains 001 at Bond Street Station | No | - | - | - | - | -
Gaseous Fire Suppression System | FU084 | - | Gaseous Fire Suppression System [nnn] at [Location] | Gaseous Fire Suppression System 001 at Bond Street Station | No | - | - | - | - | -
Water Mist System | FU085 | - | Water Mist System [nnn] at [Location] | Water Mist System 001 at Bond Street Station | No | - | - | - | - | -
Slab Track | FU086 | - | Slab Track [nnn] at [Location] | Slab Track 001 at Bond Street Station | No | - | - | - | - | -
Ballasted Track | FU087 | - | Ballasted Track [nnn] at [Location] | Ballasted Track 001 at Bond Street Station | No | - | - | - | - | -
Switch | FU088 | - | Switch [nnn] at [Location] | Switch 001 at Bond Street Station | Yes | An Asset Tag Label will be fixed in the Cess adjacent to the Switch Half Set | - | - | - | -
Crossing | FU089 | - | Crossing [nnn] at [Location] | Crossing 001 at Bond Street Station | Yes | An Asset Tag Label will be fixed in the Cess adjacent to the Crossing | - | - | - | -
Track Gravity Drainage | FU090 | - | Track Gravity Drainage [nnn] at [Location] | Track Gravity Drainage 001 at Bond Street Station | No | - | - | - | - | -
Track Pumped Drainage | FU091 | - | Track Pumped Drainage [nnn] at [Location] | Track Pumped Drainage 001 at Bond Street Station | No | - | - | - | - | -
Local Foul Gravity Drainage | FU092 | - | Local Foul Gravity Drainage [nnn] at [Location] | Local Foul Gravity Drainage 001 at Bond Street Station | No | - | - | - | - | -
Local Foul Pumped Drainage | FU093 | - | Local Foul Pumped Drainage [nnn] at [Location] | Local Foul Pumped Drainage 001 at Bond Street Station | No | - | - | - | - | -
Local Non-Foul Gravity Drainage | FU094 | - | Local Non-Foul Gravity Drainage [nnn] at [Location] | Local Non-Foul Gravity Drainage 001 at Bond Street Station | No | - | - | - | - | -
Local Non-Foul Pumped Drainage | FU095 | - | Local Non-Foul Pumped Drainage [nnn] at [Location] | Local Non-Foul Pumped Drainage 001 at Bond Street Station | No | - | - | - | - | -
Axle Counter Subsystem | FU096 | - | Axle Counter Subsystem [nnn] at [Location] | Axle Counter Subsystem 001 at Bond Street Station | No | - | - | - | - | -
Points Operating Equipment (POE) | FU097 | - | Points Operating Equipment (POE) [nnn] at [Location] | Points Operating Equipment (POE) 001 at Bond Street Station | No | - | - | - | - | -
Interlocking Subsystem | FU098 | - | Interlocking Subsystem [nnn] at [Location] | Interlocking Subsystem 001 at Bond Street Station | No | - | - | - | - | -
Central System Router (RCS component) | FU099 | - | Central System Router (RCS component) [nnn] at [Location] | Central System Router (RCS component) 001 at Bond Street Station | No | - | - | - | - | -
Network Management System | FU100 | - | Network Management System [nnn] at [Location] | Network Management System 001 at Bond Street Station | No | - | - | - | - | -
Access Point (RCS component) | FU101 | - | Access Point (RCS component) [nnn] at [Location] | Access Point (RCS component) 001 at Bond Street Station | No | - | - | - | - | -
Train Unit (RCS Module) | FU102 | - | Train Unit (RCS Module) [nnn] at [Location] | Train Unit (RCS Module) 001 at Bond Street Station | No | - | - | - | - | -
Platform Screen Doors Control Unit | FU103 | - | Platform Screen Doors Control Unit [nnn] at [Location] | Platform Screen Doors Control Unit 001 at Bond Street Station | No | - | - | - | - | -
Platform Screen Doors Assembly | FU104 | - | Platform Screen Doors Assembly [nnn] at [Location] | Platform Screen Doors Assembly 001 at Bond Street Station | Yes | Each Platform Screen Door assembly shall be numbered consecutively down the platform. See also CRL1-XRL-Z3-GUI-CR001-50071: Public Facing Labelling Guidance where asset is in public accessible area. | - | - | - | -
Roof Coverings | FU105 | - | Roof Coverings [nnn] at [Location] | Roof Coverings 001 at Bond Street Station | Yes | An Asset Tag Label is to be fixed where an access point/hatch exits. Alternatively, where the roof is most commonly access from. | - | - | - | -
Roof Structure | FU106 | - | Roof Structure [nnn] at [Location] | Roof Structure 001 at Bond Street Station | Yes | An Asset Tag Label is to be fixed where an access point/hatch exits. Alternatively, where the roof is most commonly accessed from. | - | - | - | -
Brick Lined Tunnel | FU107 | - | Brick Lined Tunnel [nnn] at [Location] | Brick Lined Tunnel 001 at Bond Street Station | Yes | An Asset Tag Label to be fixed at each end (start and finish) of the Brick Lined Tunnel at a height and position for it to be read from a safe position e.g. adjacent to the walkway at head height. | - | - | - | -
Cut and Cover Tunnel | FU109 | - | Cut and Cover Tunnel [nnn] at [Location] | Cut and Cover Tunnel 001 at Bond Street Station | Yes | An Asset Tag Label to be fixed at each end (start and finish) of the Cut and Cover Tunnel at a height and position for it to be read from a safe position e.g. adjacent to the walkway at head height. | - | - | - | -
Tube Tunnel | FU110 | - | Tube Tunnel [nnn] at [Location] | Tube Tunnel 001 at Bond Street Station | Yes | An Asset Tag Label to be fixed at each end (start and finish) of the Tube Tunnel at a height and position for it to be read from a safe position e.g. adjacent to the walkway at head height. | - | - | - | -
Tube Tunnel Platform Area | FU111 | - | Tube Tunnel Platform Area [nnn] at [Location] | Tube Tunnel Platform Area 001 at Bond Street Station | No | - | - | - | - | -
Above Ground Girdering\Internal Structural System | FU112 | - | Above Ground Girdering\Internal Structural System [nnn] at [Location] | Above Ground Girdering\Internal Structural System 001 at Bond Street Station | No | - | - | - | - | -
Below Ground Girdering\Internal Structural System | FU113 | - | Below Ground Girdering\Internal Structural System [nnn] at [Location] | Below Ground Girdering\Internal Structural System 001 at Bond Street Station | No | - | - | - | - | -
Tunnel Ventilation Attenuators | FU114 | - | Tunnel Ventilation Attenuators [nnn] at [Location] | Tunnel Ventilation Attenuators 001 at Bond Street Station | No | - | - | - | - | -
Tunnel Ventilation Fan Sub System | FU115 | - | Tunnel Ventilation Fan Sub System [nnn] at [Location] | Tunnel Ventilation Fan Sub System 001 at Bond Street Station | No | - | - | - | - | -
Tunnel Ventilation Motorised Damper Group | FU116 | - | Tunnel Ventilation Motorised Damper [nnn] at [Location] | Tunnel Ventilation Motorised Damper 001 at Bond Street Station | No | - | - | - | - | -
Platform Edge Screen (PES) | FU117 | - | Platform Edge Screen (PES) [nnn] at [Location] | Platform Edge Screen (PES) [001] at [Bond Street Station] | Yes | A label should be fixed at both ends of the Platform Edge Screens | - | - | - | -
Shaft Girdering\Internal Structural System | FU118 | - | Shaft Girdering/Internal Structural System [nnn] at [Location] | Shaft Girdering/Internal Structural System 001 at Bond Street Station | No | - | - | - | - | -
Note on F3: No = No Asset Tag Label Required Yes = Asset Tag Label Required Con = Conditional