| 02SL - Stations (LUL) | Cxxx-NCR-002625 | NCR | Fire detection Zone plans |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2021-05-25 | 2021-06-16 13:10 | 22 | 2021-04-27 16:13 | Fire - Detection | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | The issue During the production of and approval for the FAS/SCS interface SAT, an issue was raised regarding the production of a general alarm and specific alarm signal that were indicated on the C&E matrix. The approved DES OPS for the __ system indicated that a single input would be provided for the activation of the stairs pressurisation fans on or off (general alarm) but there was no provision for the receipt of a simultaneous second signal to enable the Air Release fans and Start up the stair pressurisation fans if a detector in the Air Release Zone was activated (specific alarm). It is understood through the workshops that this issue has also been identified at several other stations and CRL/CEG would like to adopt a consistent approach at all stations. Thus, the issue was that the mechanical control system could not interpret the signals in a consistent way. This was overcome by the introduction of an additional zone reference into the config for the specific alarm input but no change was made to the fire alarm zoning drawings. Thus, whereas the fire alarm detection and SCS systems have been tested and are working correctly to the C&E matrix, the zone charts and software zone references in the FAS config do not indicate separate zones which is a breach of BS 5839 and prevents the end user and/or fire brigade from identifying which zone the fire is located in when viewing the FAP and/or zone charts in the SOR. Remedial works proposed Following a number of workshops between CRL/CEG/T1/T2, the options below have been identified as possible solutions to overcome the noncompliance to BS5839: 1. Apply delay timer to the General Alarm to ensure that any specific alarm is received first by the SCS system and latched 2. Create duplicate zones aligned with current zones such allowing Zone charts to pinpoint location of incident 3. Create logic through hardware/software to combine multiple signals to a single signal (not preferred as this would have a single point of failure) 4. Change the SCS general alarm priority to lower than a specific alarm CRL/CEG to advise the option that the T1 contractor is to progress to ensure that there is line wide consistency in the solution for the wider project. NB: the revisions to the zone charts and config will be included in section 7 of the fire detection and alarm AC
| 02SL - Stations (LUL) | Cxxx-NCR-002626 | NCR | Isoclad Shroud |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2021-05-27 | 2021-06-09 10:42 | 13 | 2021-04-29 14:22 | Fire - Compartmentation | 5000 |  | Documentation and Records | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | A permanent installation of __ Isoclad fire shroud and fire door has been fitted within the hoist shaft behind door W-04-139-D01 in Moorgate shaft at Platform +3. CRL approval have been sought for the Isoclad shroud through Cxxx-FCD-003127, Cxxx-FCD-003144 and associated drawing and MCR. To resolve design assurance and progress the SCC to approval the below actions are required and recorded in this NCR: 1. Submit MCR for the door installed within the Isoclad shroud. 2. Update existing __ Isoclad drawing to include for the door details and shroud system fire performance. 3. Submit door GA drawing with door specification details.
| 02SL - Stations (LUL) | Cxxx-NCR-002627 | NCR | __ Quality Assurance Packs – Evidence Required by the Works Information Not Provided |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2021-05-28 | 2021-05-14 15:05 | -14 | 2021-04-30 13:05 | Architectural - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | __ Quality Assurance packs Cxxx-LAO-C-LRC-C101-50748 and Cxxx-LAO-C-LRC-C101-50587 submitted as part of the assurance process for SCC Cxxx-LAO-C-CER-C101-50296 have been returned ‘Code 2’ because they do not reference or include certain evidence required by the works information.
| 02SL - Stations (LUL) | Cxxx-NCR-002628 | NCR | AP2 Sump Pump (SWP 417 & 418) |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2021-07-17 | 2021-06-14 10:00 | -33 | 2021-05-28 14:14 | Mechanical - Public Health Engineering | 5999 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | The seepage water pump control panels have an F2 fire compliance on the MCR submission (CRL-MCR-006013). As such they are limited to a fire compartment no greater than 200m3, the AP2 sump panel for pumps 417 and 418 are in a compartment larger than 200m3 and therefore doesn't comply with this condition.
| 02SL - Stations (LUL) | Cxxx-NCR-002629 | NCR | LBS Quality Assurance Packs – Evidence Required for Assurance of the Works Not Provided |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2021-06-14 | 2021-05-21 15:49 | -24 | 2021-05-17 15:56 | Architectural - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | LBS QA packs Cxxx-LAO-C-LRC-C101_WS099-50579 and Cxxx-LAO-C-LRC-C101_WS099-50584 submitted as part of the assurance process for SCC Cxxx-LAO-C-CER-C101-50297 have been returned ‘Code 2’ because they do not reference or include certain evidence required for assurance of the works.
| 02SL - Stations (LUL) | Cxxx-NCR-002631 | NCR | UPS control cables function code on AIMS |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2021-07-10 | 2021-07-16 15:30 | 6 | 2021-06-24 15:47 | Information Management - Asset Information | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Cxxx have used 'LVD' function codes in tags for L746291- Control Cables for UPS system Tags affected are M135-LVD-09069 C-UPS-004-PTD-001, - M135-LVD-09070 C-UPS-003-PTD-006, - M135-LVD-09071 C-UPS-006-PTD-012, - M135-LVD-09072 C-UPS-005-PTD-014, - M135-LVD-09073 C-UPS-002-PTD-017, - M135-LVD-09074 C-UPS-001-PTD-019, - M135-LVD-09075 C-PTD-019-PTD-020, - M135-LVD-10532 C-UPS-004-TPS-019, - M135-LVD-10533 C-UPS-003-TPS-072, - M135-LVD-10534 C-UPS-006-TPS-099, - M135-LVD-10535 C-UPS-005-TPS-058, - M135-LVD-10536 C-UPS-002-TPS-032, - M135-LVD-10537 C-UPS-001-TPS-029, - M135-LVD-10548 C-PTD-001-PTD-002, - M135-LVD-10549 C-PTD-002-PTD-003, - M135-LVD-10550 C-PTD-003-PTD-004, - M135-LVD-10551 C-PTD-004-PTD-005, - M135-LVD-10552 C-PTD-006-PTD-007, - M135-LVD-10553 C-PTD-012-PTD-013, - M135-LVD-10554 C-PTD-013-PTD-010, - M135-LVD-10555 C-PTD-010-PTD-009, - M135-LVD-10556 C-PTD-009-PTD-008, - M135-LVD-10557 C-PTD-008-PTD-011, - M135-LVD-10558 C-PTD-014-PTD-015, - M135-LVD-10559 C-PTD-015-PTD-016, - M135-LVD-10560 C-PTD-017-PTD-018, - Cxxx would require CRL to approve and 'leave as is'.
| 02SL - Stations (LUL) | Cxxx-NCR-002632 | NCR | Movement joint within Terrazzo Flooring - Broadgate Ticket Hall, AP2, and the Platform level |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2022-11-01 | 2022-08-29 17:55 | -64 | 2021-07-16 10:29 | Architectural - Flooring | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Gaps at control joints within within the terrazzo floor finishes of the public areas at Liverpool St.station have been observed in the Broadgate Ticket Hall, AP2, and the platform level.
| 02SL - Stations (LUL) | Cxxx-NCR-002633 | NCR | __X Louvres Fixing Design |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2021-10-25 | 2021-10-28 08:42 | 3 | 2021-08-16 15:15 | Architectural - General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Fixing design not fully assured.
| 02SL - Stations (LUL) | Cxxx-NCR-002634 | NCR | MTH CIS screen blast tethering required |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2021-11-05 | 2021-10-22 10:13 | -14 | 2021-09-03 15:10 | Architectural - Security | 5000 |  | Incomplete Works | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | It has been identified that the Customer Information Screen supports have not been assessed for blast. This assessment has now been carried out by the Consultant and it has been confirmed CIS screens inset in the MTH cladding require tethering. CIS screens on drop poles and those in BTH have been reviewed and are acceptable in their current fixing arrangement. The remediation has been communicated to the site team for implementation. Details of the assessment can be found in document - Cxxx-LAO-A-RGN-C101-50107.
| 02SL - Stations (LUL) | Cxxx-NCR-002635 | NCR | Incorrect labels fitted to escalator luminaires |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2021-10-06 | 2021-09-09 07:39 | -27 | 2021-09-08 21:03 | Information Management - Asset Information | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During VAP 14 on 27/08/21 CRL Asset Information Coordinator, Ben Osei-Ababio noticed that the asset labels fitted to the escalator luminaires in the Broadgate Ticket Hall were white in colour, as opposed to the stainless steel type specified within the asset labeling in public areas Guidance Document CRL1-XRL-Z3-GUI-CR001-50071, Clause 4.14.2. During the VAP review, LU Project Lead, Mark Dewhirst advised LU did not require the labels to be changed.
| 02SL - Stations (LUL) | Cxxx-NCR-002636 | NCR | Smoke Seal installation to AP2/8/10 and Lift 4 doors |  | Contr | LAO | LIS - Liverpool Street Station (Central) |  | 2021-10-20 | 2021-12-03 16:16 | 44 | 2021-09-22 08:26 | Fire - Fire Systems & General | 6000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | During the close-out of ATU and the Fire Safety Compliance Report, the consultants identified that the smoke seal installations pertaining to the AP fire doors (AP2, AP8, AP10) and Lift 4 door contain gaps, and therefore are unsuitable for use as-is. Development has progressed and the agreed solutions for each door are as-follows:- AP2 - E-04-201-D01 • Top - Type A - Standard brush seal utilising a __ LP2004SS • Bottom – Type B – __ LAS50XX brush seal fixed to the face of the door • Pivot – Type C – Standard brush seal as per __ drawing utilising a __ LP2004SS • Leading Edges - Type D – Zero teardrop seal between central mating faces AP8 - E-02-201-D01 & E-02-201-D02 • Top – Type A - Standard brush seal utilising a __ LP2004SS • Bottom – Type B – __ LAS50XX brush seal fixed to the face of the door • Pivot – Type C – Standard brush seal as per __ drawing utilising a __ LP2004SS • Leading Edges – Type E – __ plain strip intumescent (LP2000) to brush (LP2004SS) AP10 - W-07-201-D02 • Top – Type A - Standard brush seal utilising a __ LP2004SS • Bottom – Type B – __ LAS50XX brush seal fixed to the face of the door • Pivot – Type C – Standard brush seal as per __ drawing utilising a __ LP2004SS • Leading Edges - Type E – __ plain strip intumescent (LP2000) to brush (LP2004SS) Lift 4 - W-01-072-D01 • Top – Type A - Standard brush seal utilising a __ LP2004SS • Bottom – Type B – __ LAS50XX brush seal fixed to the face of the door • Pivot – Type C – Standard brush seal as per __ drawing utilising a __ LP2004SS • Leading Edges - Type E – __ plain strip intumescent (LP2000) to brush (LP2004SS) Please find attached “Smoke Seal Photo Mark Up 100821” covering __’s proposal, and the following design drawings provided by __ to achieve the correct seal widths particularly at the top seal:- (AP8) 1cs - ct - Door Stop Detail – DRAFT.pdf (LU4) 1db - Door Stop Detail – DRAFT.pdf (AP2) 98b - Door Stop Detail – DRAFT.pdf Once installation is complete, the changes will be captured via the redline process.
| 02SL - Stations (LUL) | Cxxx-NCR-002637 | NCR | __ network switches |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2022-01-23 | 2021-12-20 08:57 | -34 | 2021-11-16 14:24 | Communications and Control Systems | 500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Various items of electrical plant equipment are fitted with network switches to allow monitoring by the BMS. A certain number of these switches manufactured by __ have generated fault signals for loss of communication, that is the network communication between the switch and the BMS, these faults last at times for seconds and at others several minutes, these faults have been occurring for a prolonged period. Various endeavours have been made to remedy these faults and the volume has reduced dramatically however there remains 18No (36%) switches still generating faults signals.
| 02SL - Stations (LUL) | Cxxx-NCR-002638 | NCR | escalator skirt lighting |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2022-01-31 | 2021-12-22 12:54 | -40 | 2021-12-06 11:29 | Electrical - Lighting | 13000 |  | Manufacturing Defect | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There are 12 faults identified on the escalator skirt lighting at present we have 5 faults identified as driver faults where the skirt lighting is not working, the reset procedure for a lock out has been carried out and this has not resolved the issue, in addition there are 7 faults on strip lights on the Dali controllers for identified on __ light scape as failures
| 02SL - Stations (LUL) | Cxxx-NCR-002639 | NCR | Defective Pumps |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2022-08-19 | 2022-08-16 07:07 | -3 | 2022-02-16 11:41 | Mechanical - Pumps | 5000 |  | Equipment Breakdown | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Report received from LU on 6th Feb 2022: Moorgate – 80306929 / 55684183 - Blocked toilet - staff toilet 7/440 - Broadgate entrance of Moorgate Attended site and found toilet in room 7/440 overflowing and it had flooded the surrounding lobby areas. Found the pump control panel in adjacent foul pump room 7/911 had no power and one pump disconnected. Reinstated power supply from switch room 7/628 and ran the working pump and it just tripped the power supply again. Meggered both pumps and found the disconnected pump down to earth and the other pump with low resistance readings. Lifted the pump that was connected out of the tank and found no obstructions and impellor spun freely. Tested one more time and it just tripped the power supply again. Both pumps are defective and require replacement. Pump 1 controls are also not working on hand or auto and require further investigation. One pump has been left in the pump room outside the tank ready to be removed. The other pump is still inside the tank. It was then noticed that not only this toilet discharges into this tank as water was overflowing up through the toilet whilst we were testing the pumps. As a result the small submersible in the pump room opposite the foul pumps and the pumps in the cleaners store in the cross passage between the 2 platforms also discharge into this tank and have had to be switched off on the hand/auto switches. The power has been left switched on to indicate any high levels. As a result of these pumps being isolated we have had to take some sinks and toilets out of service as well. Assets out of service Cleaners Store 7/412 through 7/069 off the platform cross passage – Both cleaners sinks isolated and both pumps switch off on hand/auto switches. The panel is showing a HL after we had to dump all the foul water into this tank which is under the floor plates. Do not use notices posted on sinks and panels Pump Room 7/416 – Pump out of service and Do not use notices posted panel Foul Pump room 7/911 – Both pumps defective, out of service and require replacement to get all these assets back into service. Power has been reinstated and OOS notice posted on panel. Toilet and Sink 7/440 – Both out of service and Do not use notices posted. Note that the toilet bowl is still full as we couldn’t dump no more water into the cleaners store tank due to charged inlet pipework Cleaners Tea Point 7/903 – Sink out of service and Do not use notice posted. Both foul pumps need to be replaced before these assets can go back into service. We have removed all the standing flood water with the aqua-vac and dumped it down the sink in the cleaners store. This is why the cleaners store pumps are now at high level. New pumps need to be ordered and replaced ASAP. This can be done on days or nights as there is lift access to this level (-9) from the street via a double door entrance opposite the new Broadgate entrance. Master Key required I have left a list of all the assets out of service with the CSS along with the shift managers auto number. Pump Details New Halden GRP50 SN: 457695 400V 8.7A 2900 RPM 58Kg Plate left on shift managers desk I recommend that we order 3 of these pumps to replace the 2 defective ones and keep a 3rd spare on site in case this happens again. I believe that’s all, see attached photos
| 02SL - Stations (LUL) | Cxxx-NCR-000085 | NCR | Measurement of fibres for SCL |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2011-10-25 | 2011-12-21 22:43 | 57 | 2011-10-11 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | The batching plant had not installed automatic devices for weighing fibre at the time of the shotcrete trials 26/09/2011
| 02SL - Stations (LUL) | Cxxx-NCR-000086 | NCR | Temporary Works design not submitted prior to works commencing |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2011-10-25 | 2011-12-06 08:28 | 42 | 2011-10-11 | Structural Engineering - Structural Engineering - General | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | The temporary works submission for the ramp in 11-12 Blomfield Street was not submitted prior to works commencing. The informal copy passed to CRL did not contain the required Cat 3 check certificate.
| 02SL - Stations (LUL) | Cxxx-NCR-000303 | NCR | Damage to earthing rod E1 |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-02-05 | 2012-01-25 09:53 | -11 | 2012-01-22 | Electrical - Electrical Engineering General | 500 |  | Damaged | Rework |  | Complete |  | Completed |  | On installing the earth rod seal around earthing rod E1 (NW corner of substation), it was found to be unscrewed at a depth of 3.6m. The rod can't be reconnected without damaging its effectiveness.
| 02SL - Stations (LUL) | Cxxx-NCR-000307 | NCR | Submission of Materials Compliance Records & Inspection Request Forms |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-02-08 | 2012-02-20 14:13 | 12 | 2012-01-25 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Material Compliance Records have been completed but not submitted to the Project Manager for acceptance. A Material Proposals Schedule has been completed and submitted to the Project Manager. Inspection Request Forms have not been issued for all witness points on ITPs
| 02SL - Stations (LUL) | Cxxx-NCR-000338 | NCR | Removal of 2No sheet piles from substation pour 1 temporary works |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-02-14 | 2012-02-20 13:40 | 6 | 2012-01-31 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The 2 sheet piles removed/cut down were approximately 3m apart, approx 300mm wide and formed part of the substation base slab/retaining wall support temporary works. The works were undertaken by __ supervision and not considered a risk to the infrastructure.
| 02SL - Stations (LUL) | Cxxx-NCR-000339 | NCR | Earthing rod 6 could not be driven to full design depth |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-02-14 | 2012-02-20 14:17 | 6 | 2012-01-31 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Earth rod 6 was installed in the design location and hit a hard obstruction at a depth of 6m. It was not possible to break beyond this obstruction. The earth rod was tested using the three point test and achieved a resistance of 1.59 ohms at this depth.
| 02SL - Stations (LUL) | Cxxx-NCR-000375 | NCR | Use of incorrect concrete mix |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-02-28 | 2012-02-27 15:43 | -1 | 2012-02-14 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The posts on the switchroom base slab were concreted using 40N concrete (prebagged). The use of 40N concrete has not be approved under a Material Compliance Record nor has it been verified that it satisfies the requirements of a Mix A1 concrete. A pre pour inspection of this section of works was not requested nor completed. Concrete cubes were taken during concreting. The subcontractor had been forewarned against the use of 40N concrete without prior approval.
| 02SL - Stations (LUL) | Cxxx-NCR-000387 | NCR | Stagger coupler construction joint in substation |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-03-02 | 2012-02-23 08:28 | -8 | 2012-02-17 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | The issue of removing the staggered joint with couplers designed across the substation slab construction joint was raised under LIS-CRL-FCD-Cxxx-00129. This issue was raised due to constructability issues. The designer response to the FCD stated in the 'technical requirements' section that "It is not clear why couplers cannot be cast tight to the face of a concrete pour, this is common practice." This was incorrectly interpreted that it was acceptable to amend the detail however the designer would not amend the schedule thus the contractor took the initiative to re-detail the construction joint rebar. It was not noticed that FCD-Cxxx-00129 was ultimately rejected. BM02 was replaced with BM01 throughout. Pour 2 bars were also re-detailed to suit. The straight construction joint is not in accordance with the design drawings but is agreed to be common practice. T1 bars have alternating __ P14 and Griptec couplers in order to be able to install the pour 2 bars.
| 02SL - Stations (LUL) | Cxxx-NCR-000400 | NCR | Lower switchroom manhole 70 incorrectly installed |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-03-07 | 2012-05-02 13:46 | 56 | 2012-02-21 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Manhole 70 in the lower switchroom slab has been partially installed to the incorrect detail due to confusion over various RFI responses. The detail from page 9 of RFI-Cxxx-00116 has been used instead of the correct information in RFI-Cxxx-00186. The base of manhole 70 was constructed using two layers of B1131 mesh and the sides constructed with C40 mass concrete. Rebar detailing has been constructed to drawing P30201-C1M12-C00-D-65425 (and RFI-Cxxx-00118) which is not consistent with the RFI sketches in RFI-Cxxx-00186.
| 02SL - Stations (LUL) | Cxxx-NCR-000410 | NCR | Eldon Street carriageway reinstatement |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-03-09 | 2012-05-01 16:32 | 53 | 2012-02-24 | Civil - Streets & Highways | 500 |  | Material | Rework |  | Complete |  | Completed |  | Hot Rolled Asphalt (HRA) has been used for the carriageway reinstatement whereas the existing reinstatement is Stone Mastic Asphalt (SMA)
| 02SL - Stations (LUL) | Cxxx-NCR-000411 | NCR | Blomfield Street carriageway reinstatement |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-06-30 | 2012-07-02 13:26 | 2 | 2012-02-24 | Civil - Streets & Highways | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | Double yellow lines and white lines have not been reinstated following completion of the works The joints between the tarmac of reinstated excavations and existing carriageway need to be sealed appropriately to prevent deterioration
| 02SL - Stations (LUL) | Cxxx-NCR-000414 | NCR | Old Broad Street carriageway reinstatement (tarmac) |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-03-09 | 2012-05-29 10:58 | 81 | 2012-02-24 | Civil - Streets & Highways | 500 |  | Material | Rework |  | Complete |  | Completed |  | Upon inspection from City of London (__ ), the tarmac reinstatement has been rejected and resurfacing has been requested
| 02SL - Stations (LUL) | Cxxx-NCR-000415 | NCR | Old Broad Street carriageway reinstatement |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-03-09 | 2012-05-01 16:48 | 53 | 2012-02-24 | Civil - Streets & Highways | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | Double yellow lines and white lines have not been reinstated following completion of the works Anti-skid surfacing has not been reinstated following completion of the works
| 02SL - Stations (LUL) | Cxxx-NCR-000452 | NCR | Movement Joint Connection |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-03-17 | 2012-03-15 14:02 | -2 | 2012-03-03 | Civil - Civil Engineering General | 500 |  | Design | Rework |  | Complete |  | Completed |  | 1) FCD-Cxxx-00383 changed the lower switchroom slab design due to a clash with retaining wall W297. The structural concrete was slab was poured up to the wall and a slip membrane layer installed. In order to comply with previous RFI-Cxxx-00296 (which detailed the waterstop sertvitite 150 should be 100mm from the outside face of the slab) the position of the waterstop changed accordingly. To include the waterstop in the substation pour the slab must now increase locally to the waterstop. Attached is the proposal to mass concrete. Please confirm if any steel reinforcement is required in this section. 2) The upstand of the lower switchroom was installed in accordance with FCD-Cxxx-00383 however it has been fixed incorrectly in the proximity of the Movement Joint. The proposal is to drill and fix B16 bars to the correct alignment.
| 02SL - Stations (LUL) | Cxxx-NCR-000490 | NCR | Reinforcement Spacing- Substation Baseslab Pour 2 |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-04-13 | 2012-05-09 10:53 | 26 | 2012-03-22 | Civil - Structural Engineering | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | At the western end of the 1m deep section of substation baseslab, 9no 16mm bars have been fixed without the required spacing as per the stated eurocode. This is the result of local alteration in the designed position of reinforcement to accomodate the installation of a sump pit and holding down bolts in the heavily reinforced slab. Please refer to the attached picture.
| 02SL - Stations (LUL) | Cxxx-NCR-000491 | NCR | Inspection and Test Plan for Switchroom Steel |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-03-28 | 2012-04-04 23:00 | 7 | 2012-03-21 | Civil - Structural Engineering | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Cxxx-VIN-O4-ITP-C101-50002 Rev 1.0 - Inspection Test Plan - Switchroom Superstructure - Steelwork, was submitted to CRL and returned Decal Code 3 on 02/03/2012. Fabrication works for the Switchroom steel commenced without the inspection test plan being accepted by the Supervisor, as per requirements.
| 02SL - Stations (LUL) | Cxxx-NCR-000515 | NCR | Cracking in switchroom substructure |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-04-13 | 2012-05-09 11:01 | 26 | 2012-04-05 | Civil - Civil Engineering General | 500 |  | Material | Repair |  | Complete |  | Completed |  | The following cracking was observed on 03/04/12, the day after the foam concrete pour. Hairline cracks have been observed within the foam concrete. 2No Vertical cracks have been observed at the south west corner of the switchroom. Another crack has been observed through the mortar at the south east corner of the switchroom. No cracking was visible on the night of completion of the foam concrete pour.
| 02SL - Stations (LUL) | Cxxx-NCR-000526 | NCR | Foam concrete bays installed lows |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-04-20 | 2012-04-28 16:51 | 8 | 2012-04-11 | Civil - Civil Engineering General | 500 |  | Equipment Breakdown | Use As-Is |  | Complete |  | Completed |  | 3No bays of foam concrete at the western end of the switchroom substructure have been finished low by 75mm (see attached sketch). This is above the acceptable tolerances.
| 02SL - Stations (LUL) | Cxxx-NCR-000527 | NCR | Earthing plates not cast into upstands |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-06-30 | 2012-06-26 15:38 | -4 | 2012-04-11 | Electrical - Electrical Engineering General | 500 |  | Design | Rework |  | Complete |  | Completed |  | Earth plates connected to rebar prior to pouring. Connecting wires extend above upstands and will clash with the blockwork. Earth plates woudl ideally be cast flush with the face of the upstands.
| 02SL - Stations (LUL) | Cxxx-NCR-000548 | NCR | Holding Down Bolts for Switchroom Platform Slab |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-06-30 | 2012-06-26 15:42 | -4 | 2012-04-25 | Civil - Structural Engineering | 500 |  | System Defect | Rework |  | Complete |  | Completed |  | Holding down bolts at switchroom platform slab level have been installed out of tolerance. It will not be possible to column bases over the cast in bolt positions without re-work
| 02SL - Stations (LUL) | Cxxx-NCR-000552 | NCR | Holding Down Bolts for Substation Baseslab |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-06-30 | 2012-06-26 15:46 | -4 | 2012-04-25 | Civil - Structural Engineering | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Following as bult surveys and checks, 95 holding down bolts have been identified as being low so that the typical holding down bolt detail can't be achieved. The attached spreadsheet identifies these bolts. This has been verified by a survey by the steelwork contractor A positional survey shows that some bolts are outside of the NSSS tolerance also. Summarised in attached spreadsheet. This is compound by the minimal movement of the bolts through the 25mm thick anchor plates.
| 02SL - Stations (LUL) | Cxxx-NCR-000564 | NCR | Batching of Admixtures |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-06-29 | 2012-06-27 09:41 | -2 | 2012-05-04 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | The ad mixtures are being added by hand at the batching plant in Battersea.
| 02SL - Stations (LUL) | Cxxx-NCR-000566 | NCR | Spacing of reinforcement in the substation base slab, near the cable shaft |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-05-31 | 2012-06-01 00:08 | 1 | 2012-05-10 | Civil - Structural Engineering | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | Within the substation base slab, in the area adjacent to the cable shaft, near grid line 15 and in the part of the slab which has been redetailed to take account of the corbel of the adjacent retaining wall W297, the reinforcement bars have been spaced at less than the Eurocode requirements, due to the aforementioned redetail and installation of holding down bolts, in what is a heavily reinforced slab, please refer to the attached picture.
| 02SL - Stations (LUL) | Cxxx-NCR-000567 | NCR | Steel structure level - Substation |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-07-30 | 2012-07-30 16:17 | 0 | 2012-05-09 | Structural Engineering - Structural Engineering - General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Following rework to the holding down bolts as per LIS-CRL NCR-Cxxx-00552, the final level of the M30 couplers installed was such that the packing required to achieve the baseplate design level of +107.050 and +107.350 respectively could not be achieved. The couplers were 90mm long requiring 45mm of threaded bar from both the original bolts and the new threaded rod. Due to the make up of the original holding down bolts and the non-compliant installation it was not possible to achieve 45mm of threaded rod below the design level of the concrete therefore resulting in the couplers extending higher and clashing with the baseplate. In the worst case, the level of the couplers extended a further 66mm above design level of the underside of the baseplate. The level of the steel frame was raised by 70mm along the full length to overcome the clash with the couplers. The __ HF grout specified is only suitable for up to 100mm bedding, however in the worst case 150mm of bedding is required.
| 02SL - Stations (LUL) | Cxxx-NCR-000568 | NCR | Trial Mix Testing |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-05-17 | 2012-05-20 22:56 | 3 | 2012-05-10 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | No evidence has been provided to show that the mix used for the female piles/male piles installed meets the specification for the works.
| 02SL - Stations (LUL) | Cxxx-NCR-000569 | NCR | SCL workability |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-05-25 | 2012-05-15 13:09 | -10 | 2012-05-10 | Tunnelling - Tunnelling General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Slump below lower ITP limit for spraying, concrete used to spray top of shaft and upstand (107.50 to 106.25)
| 02SL - Stations (LUL) | Cxxx-NCR-000576 | NCR | Sequence of sprayed lining installation |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-05-25 | 2012-05-21 09:38 | -4 | 2012-05-11 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | First SCL pass to shaft work not installed before overnight stoppage. This was agreed at the SRG and is detailed on RESS 06 i.e. Minimum requirement for 09/05/12 - Regulating layer +75mm +1hour Penetration test
| 02SL - Stations (LUL) | Cxxx-NCR-000578 | NCR | Lack of __ Representatives at ITP 'hold' points |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-05-21 | 2012-05-21 23:05 | 0 | 2012-05-14 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | No __ representative present at hold points B11 through to B13 as specified in the ITP for SCL shaft works (Cxxx-VIN-C-ITP-C101-50002) on 11/5/12.
| 02SL - Stations (LUL) | Cxxx-NCR-000586 | NCR | Column C77 on Gridline 18/B |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-05-18 | 2012-05-28 22:35 | 10 | 2012-05-16 | Structural Engineering - Steel Member | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Column C77 fabricated for Gridline 18/B was fabricated 300mm too short to match the adjacent column on gridline 17/B which is on a 300mm plinth. The column is therefore 300mm too short and requires rework.
| 02SL - Stations (LUL) | Cxxx-NCR-000588 | NCR | Non-compliance with Infrastructure Protection |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-05-30 | 2012-06-26 17:49 | 27 | 2012-05-16 | Civil - Structural Engineering | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | The approved work documents, as described in the 'Technical Requirements' above were not obtained prior to the breakout of pockets of brick corbel, part of LU wall W297, at Street Level.
| 02SL - Stations (LUL) | Cxxx-NCR-000589 | NCR | Male pile concrete excessive cement content |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-05-25 | 2012-05-21 09:28 | -4 | 2012-05-16 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | The initial male pile mix design submitted to CRL and accepted at Code 2 without specific comment to this mix in document reference Cxxx-VIN-C-CER-C101-500003 rev 1.0 (and the subsequent rev 2.0) states that the cementitious content totals 416 kg/m3, with 266 kg/m3 of CEM I and 150 kg/m3 of GGBS. At the time of writing (16/05/12), 2no male piles have been concreted with this mix. A further 2no are planned to be concreted by 18/05/12.
| 02SL - Stations (LUL) | Cxxx-NCR-000605 | NCR | Sequence of Sprayed Lining installation |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-06-08 | 2012-05-25 16:10 | -14 | 2012-05-25 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | The thickened first pass SCL to shaft work not completed before overnight stoppage on the 17/05/12 at level 101.25 to 100.25. During spraying it was noted by the sprayer that the consistency of the Sprayed concrete had changed and more rebound was evident. Spraying was halted and the thickness of shotcrete applied checked. A minimum of 200mm, consistent with the standard shaft section thickness was noted. Following discussions with Designers representative on site, it was agreed that spraying be halted for the day and the lining over this area of the shaft be completed tthe following day with fresh shotcrete.
| 02SL - Stations (LUL) | Cxxx-NCR-000615 | NCR | Procurement |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-07-11 | 2012-07-09 17:55 | -2 | 2012-06-01 | Electrical - Switchgear | 500 |  | Material | Reject |  | Complete |  | Completed |  | It has come to the Project Manager’s attention that the Contractor has already commenced procuring items of Electrical Equipment without having the necessary approvals in place. It is also stated in the Powerlink Outline Design, 11.0 Design Proposals : that “the replaced and uprated Transformer Rectifiers, Auxiliary Transformers and switchboards will comply with LU Standards and Powerlink Specifications and are subject to Powerlink approval”, to date there is no evidence that the Contractor has procured this equipment with the required approvals in place.
| 02SL - Stations (LUL) | Cxxx-NCR-000625 | NCR | Concrete to reinforced concrete shaft base slab |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-06-27 | 2012-06-27 09:50 | 0 | 2012-06-13 | Tunnelling - Tunnelling General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | C32/40 mix design with 10mm aggregate used, see atttached mix design.
| 02SL - Stations (LUL) | Cxxx-NCR-000633 | NCR | Finsbury Circus sewer lining - manhole opening sizes |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-07-20 | 2012-07-11 09:13 | -9 | 2012-06-20 | Utilities Engineering - Water | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Correct sized manhole openings were installed at 2no locations on Finsbury Circus, however manhole openings have been provided as 600 x 600mm clear opening in 1no shaft on Finsbury Circus (the furthest eastern manhole) and in 1no shaft on Circus Place.
| 02SL - Stations (LUL) | Cxxx-NCR-000634 | NCR | Concrete out of specification on Finsbury Circus |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-07-20 | 2012-07-09 22:59 | -11 | 2012-06-20 | Civil - Concrete Pavement | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | For the surround and concrete backfilling to 2no manholes on Finsbury Circus, dry-lean concrete (ST5, C20/25) was delivered to site at approximately 10.00 and placed and 15.30, thus placing concrete approximately 6 hours after batching.
| 02SL - Stations (LUL) | Cxxx-NCR-000646 | NCR | No tremmie pipe used for concrete placing on B154 |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-07-31 | 2012-08-07 10:31 | 7 | 2012-07-04 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The tremmie was not used to place the concrete, and the concrete was placed directly into the casing through the reinforcement to a depth of approximately 30m.
| 02SL - Stations (LUL) | Cxxx-NCR-000650 | NCR | Probe hole position and depth |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-08-09 | 2012-07-30 16:29 | -10 | 2012-07-06 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Probes drilled as follows: probe hole no. 1 ( approx 15m ) probe hole no. 2 ( approx 8.5m ) probe hole no. 3 ( approx 5m ) All probe holes were drilled on the tunnel axis.
| 02SL - Stations (LUL) | Cxxx-NCR-000665 | NCR | Switchroom Windpost Galvanising |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-08-27 | 2012-07-31 16:28 | -27 | 2012-07-26 | Architectural - Brickworks/Blockworks | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | The windposts provided are stainless steel, and have not been galvanised. The installation of stainless steel windposts instead of galvanised can be considered as betterment and will not adversely affect the structure. There is no issue with dissimilar metals as an isolation strip is installed between the top cleat and the structural steelwork.
| 02SL - Stations (LUL) | Cxxx-NCR-000677 | NCR | Geological Report for SCL works |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-08-31 | 2012-08-18 22:57 | -13 | 2012-08-03 | Tunnelling - Tunnelling General | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | No geological reports have been submitted since construction began on the SCL shaft on 8th May 2012.
| 02SL - Stations (LUL) | Cxxx-NCR-000678 | NCR | Water Management Plan not submitted |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-08-17 | 2012-08-06 22:06 | -11 | 2012-08-03 | Tunnelling - Tunnelling General | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | Water management plan has not been submitted, despite construction beginning on the SCL shaft on 8th May.
| 02SL - Stations (LUL) | Cxxx-NCR-000681 | NCR | Tunnel Convergence Monitoring |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-08-31 | 2012-08-18 23:46 | -13 | 2012-08-06 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | Readings are not stable within the tunnel and daily readings have not been received by CRL since tunneling stopped on 27th July.
| 02SL - Stations (LUL) | Cxxx-NCR-000693 | NCR | Lack of permeability results for SCL shaft and tunnel |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-09-30 | 2012-08-31 17:20 | -30 | 2012-08-10 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | To date (as of 10th August) the Project Manager has received one set of permeability results on 9/7/12 for the shaft only. The construction of the SCL shaft started on 8th May and finished on 11th June, and construction of the SCL tunnel started on the 22nd June and finished on the 27th July - the Project manager should have received multiple sets of permeability results.
| 02SL - Stations (LUL) | Cxxx-NCR-000697 | NCR | Use of Non-Compliant vehicles |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-09-21 | 2012-08-15 10:32 | -37 | 2012-08-13 | Construction Health & Safety - Construction Health & Safety General | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | Defects noted during Period 4 to do with vehicle compliance: Week 1: 1. 27/06 – Blomfield Street site – __ – Van – Not compliant to the following: • Fire Extinguishers • Light & high visibility colours • Reflective warning triangle • Reversing sensors / cameras / alarms • Spare light bulb kit • Rear warning signs for cyclists 2. 29/06 – Blomfield Street site – __ – Rigid Flatbed – Not compliant to the following: • Fresnel lens • Rear warning signs for cyclists Week 2: N/A Week 3: 1. 09/07 – Blomfield Street site – Shotcrete – Van – Not compliant to the following: • Fire Extinguishers • Light & high visibility colours • Reversing sensors / cameras / alarms 2. 11/07 – Blomfield Street site – __ – Pickup – Not compliant to the following: • Flashing beacons • Reversing sensors / cameras / alarms • Side scan detection & warning systems • Spare light bulb kit • Blind spot mirrors • Fresnel lens • Side under run guards 3. 13/07 – Blomfield Street site – BTG – Van – Not compliant to the following: • Fire Extinguishers • Flashing beacons • Light & high visibility colours • Reversing sensors / cameras / alarms • Seat belt; Inspection; & Drug and Alcohol warning decal • Rear warning signs for cyclists Week 4: 1. 16/07 – Blomfield Street site – T. M. Mixer – Van – Not compliant to the following: • Fire Extinguishers • Flashing beacons • Light & high visibility colours • Head, stop, turn, tail & hazard warning lights • Reversing sensors / cameras / alarms • Rear warning signs for cyclists 2. 18/07 – Blomfield Street site – PMA Logistics – Rigid Flatbed – Not compliant to the following: • Fire Extinguishers • Flashing beacons • Light & high visibility colours • Reflective warning triangle • Reversing sensors / cameras / alarms • Side scan detection & warning systems • Spare light bulb kit • Fresnel lens • Rear warning signs for cyclists 3. 20/07 – Blomfield Street site – PMA Logistics – Rigid Flatbed – Not compliant to the following: • Fire Extinguishers • Flashing beacons • Light & high visibility colours • Reflective warning triangle • Reversing sensors / cameras / alarms • Side scan detection & warning systems • Spare light bulb kit • Fresnel lens • Rear warning signs for cyclists
| 02SL - Stations (LUL) | Cxxx-NCR-000700 | NCR | Steet level slab GL16-17 rebate concrete |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-08-20 | 2012-08-27 21:17 | 7 | 2012-08-14 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | During the pouring of the substation street level slab, concrete has not been adequately vibrated so that it fills the northern rebate between GL16-17.
| 02SL - Stations (LUL) | Cxxx-NCR-000701 | NCR | Switchroom floor screed |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-08-24 | 2012-08-17 09:03 | -7 | 2012-08-14 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Further to NCR-648 & RFI-647, the switchroom slab has been installed to FFL i.e. top of concrete is 108.345 and not SSL of 108.320. A screed needs to be applied to the floor level however the required screeds will now produce a FFL starting at 10.375 as per the attached drawing. Lintels have been installed at a level such that door clear openings will not be reduced on installation.
| 02SL - Stations (LUL) | Cxxx-NCR-000712 | NCR | Water ingress |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-02-15 | 2013-01-29 16:26 | -17 | 2012-08-20 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | There is excessive water ingress at several locations, the majority of which coincide with joint locations and we are awaiting the Contractor's urgent investigation into this issue. A submittal from the Contractor regarding methods of removal of defective material and replacement (refer to clause 6.6.9 c) where required is awaited.
| 02SL - Stations (LUL) | Cxxx-NCR-000741 | NCR | Lower switchroom slab flatness |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-02-28 | 2013-01-31 22:47 | -28 | 2012-09-10 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The lower switchroom slab flatness does not meet this 1mm under a 1000mm straight edge tolerance and requires re-work. Slab is outside +/-10mm deviation from target level of 107.000.
| 02SL - Stations (LUL) | Cxxx-NCR-000750 | NCR | Substation Street Level Gridline A Mid Level Brick Ties |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-10-14 | 2012-10-10 10:19 | -4 | 2012-09-14 | Architectural - Brickworks/Blockworks | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | These wall ties were not installed at the east and central sections of the wall.
| 02SL - Stations (LUL) | Cxxx-NCR-000761 | NCR | Lack of convergence readings |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-09-26 | 2012-09-26 23:05 | 0 | 2012-09-19 | Tunnelling - Tunnelling General | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | As of 19/9/12 no readings have been received beyond 7/9/12 due to the Contractor not being able to enter the tunnel.
| 02SL - Stations (LUL) | Cxxx-NCR-000764 | NCR | Insufficiet cover over reinforcement on Substation slab |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-12-28 | 2012-12-19 09:51 | -9 | 2012-09-19 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Reinforcement has been noticed to have less than 10mm of concrete cover at the construction joint adjacent to gridline 17.
| 02SL - Stations (LUL) | Cxxx-NCR-000769 | NCR | Street level columns - out of plumb |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-12-28 | 2012-11-28 17:43 | -30 | 2012-10-11 | Structural Engineering - Steel Member | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Column plumb is out of tolerance as per attached sketch
| 02SL - Stations (LUL) | Cxxx-NCR-000770 | NCR | Louvre support steel - design setting out |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-10-26 | 2012-10-23 15:47 | -3 | 2012-09-20 | Structural Engineering - Steel Member | 500 |  | Design | Rework |  | Complete |  | Completed |  | Setting out on the BSP General Arrangement drawings does not correspond with setting out on the __ drawings. Holding down bolts have been drilled and fixed in accordance with BSP drawings. The columns on Gridline 11 and 17 have been moved inwards by 184mm and 186mm respectively, and the spacing between columns on Gridline 12 – 13, inclusive, have been adjusted from 2917mm specified to dimensions to suit the end bay change. Consequently all base plate locations have been detailed up to 216mm out of position. These baseplate positions cannot be used to achieve the MMD setting out requirements. Steel has been fabricated to the GA drawings and as such Gridline 12 – 13 beams and tie sections are incorrect lengths. All other sections are as per MMD design.
| 02SL - Stations (LUL) | Cxxx-NCR-000786 | NCR | Lack of 28-day test results |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-11-30 | 2012-11-02 08:55 | -28 | 2012-10-03 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | To date Crossrail have only received on set of 28 day results for the tunnel works from chainage 0-48m (which equates to more than 100m3 of concrete sprayed).
| 02SL - Stations (LUL) | Cxxx-NCR-000788 | NCR | Temporary Works Design Installation 1-14 Liverpool Street Bridge Deck |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-10-31 | 2012-10-10 00:05 | -21 | 2012-10-03 | Civil - Civil Engineering General | 500 |  | Design | Repair |  | Complete |  | Completed |  | 1-14 Liverpool Street Bridge deck temporary works installation is not as per VN0001-STW-01-039-001 (eB reference Cxxx-VIN-C-__-C101_WS102-50009 ) The northern side of the deck is not supported by the Secant pile wall, as shown in Section A-A.
| 02SL - Stations (LUL) | Cxxx-NCR-000804 | NCR | Lack of permeability results for second half of SCL tunnel |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-11-22 | 2012-11-22 17:19 | 0 | 2012-10-10 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | We are missing 1 set of permeability tests for the tunnel primary lining.
| 02SL - Stations (LUL) | Cxxx-NCR-000836 | NCR | Works started without MS in place |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-12-21 | 2012-12-12 08:37 | -9 | 2012-10-23 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Works began on installing invert in tunnel (MS Cxxx-VIN-C-GMS-C101-50021) without the MS being approved by CRL and LUL
| 02SL - Stations (LUL) | Cxxx-NCR-000844 | NCR | Switchroom standing seam roof 'missing' penetration |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-02-15 | 2013-01-13 20:41 | -33 | 2012-10-25 | Architectural - Roofing & Exterior Treatment | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | A penetration was not included in the roof above the OLBI. This was not captured during drawing of roof GA drawings, checking and approval. M&E services were co-ordinated but this detail was missed.
| 02SL - Stations (LUL) | Cxxx-NCR-000849 | NCR | Core alignment between UTS room and 2/202 |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-12-24 | 2012-11-09 15:49 | -45 | 2012-10-31 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The cores were set out correctly on the corridor 2/202 side. The core drilling process involved drilling some 3.5m through concrete, steel reinforcement, flint and brickwork. An error within the UTS room over such a distance was inevitable. The result is as follows: - 9no cores within 90mm of their target position - 3no cores between 90mm and 160mm of target position - All ducts have been lined in accordance with the design See attached photo for location of core holes on either side of the wall.
| 02SL - Stations (LUL) | Cxxx-NCR-000859 | NCR | SCL lining test results |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-12-14 | 2012-11-26 22:56 | -18 | 2012-11-06 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | Cores taken for 7 day tests were tested at 9 days. This was because the 7 day ttest was due on thesaturday when the testing laboratory was closed for the weekend. The cores were tested on the next nearest working day.
| 02SL - Stations (LUL) | Cxxx-NCR-000866 | NCR | Damage to concrete upstand at Gridline 18 |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-12-21 | 2012-11-21 15:53 | -30 | 2012-11-08 | Civil - Civil Engineering General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | During installation of the steel windpost at gridline 18, drilling operations have broken out the side of the upstand of which it sits on. Fixings have full embedment and do not require re-work. Installed as per __ updated bolting arangement.
| 02SL - Stations (LUL) | Cxxx-NCR-000873 | NCR | Trial excavation outside Railway Tavern |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-11-26 | 2012-11-13 13:08 | -13 | 2012-11-12 | Civil - Excavation | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | Trench sheets not installed on all sides of excavation as per design drawing.
| 02SL - Stations (LUL) | Cxxx-NCR-000879 | NCR | Damage to Substation roof level plinths and blockwork |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-01-31 | 2012-11-28 17:28 | -64 | 2012-11-13 | Civil - Civil Engineering General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | During delivery and movement of SCS’s flat roof insulation material onto the substation roof on 12/11/12 night shift, damage has occurred to the corner of a concrete plinth. The newly constructed blockwork wall has been knocked out of plumb also (see attached photos)
| 02SL - Stations (LUL) | Cxxx-NCR-000885 | NCR | Cut Rebar with Corridor 2/202 Floor Slab |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-02-28 | 2012-12-14 11:23 | -76 | 2012-11-16 | Civil - Structural Engineering | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | During the installation works, existing rebar was mistakenly cut. The bars that were cut are shown in the attached document. These bars are 8 to 12mm diameter. They appear to be vertical hoops with horizontal bars threaded through the top, running along the southern edge of the floor slab.
| 02SL - Stations (LUL) | Cxxx-NCR-000888 | NCR | Scales calibration and material certification records. |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-01-31 | 2012-12-04 12:04 | -58 | 2012-11-19 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Records were not made available during surveillance QS503-01 of 12/11/12 or thereafter to the date of this NCR to demonstrate compliance with respect to calibration of scales serial number EV0229 or material certification for the fibres added to the SCL production mix.
| 02SL - Stations (LUL) | Cxxx-NCR-000891 | NCR | Commence Excavation with no viable concrete on site |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-11-27 | 2012-11-21 16:06 | -6 | 2012-11-20 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Breaking out of headwall started when concrete arrived on site but before it had been checked. Concrete than sent away because of low slump (120mm, 130mm). Breaking out stopped with lower half of headwall broken out.
| 02SL - Stations (LUL) | Cxxx-NCR-000903 | NCR | Splice Box Access Route Mass Concrete Footing |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-03-15 | 2013-02-28 13:29 | -15 | 2012-11-28 | Civil - Civil Engineering General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | During installation of the Splice Box Access Route structure drilling & fixing operations have broken out the side of one of the concrete footings that support the structure. Fixing has full embedment and does not require re-work.
| 02SL - Stations (LUL) | Cxxx-NCR-000906 | NCR | M&E Support Steelwork Clash |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-02-28 | 2013-01-09 16:54 | -50 | 2012-11-29 | Civil - Civil Engineering General | 500 |  | Design | Rework |  | Complete |  | Completed |  | During the M&E design coordination phase of the works a clash between the support steelwork and the proposed 900mm duct on the original MMD drawing was not identified. The steelwork was fabricated and installed in line with the original MMD design and must now be modified as per the attached detail in order to accommodate the duct.
| 02SL - Stations (LUL) | Cxxx-NCR-000910 | NCR | Finished profile of primary lining not sprayed to specified tolerances |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-01-25 | 2012-12-04 11:49 | -52 | 2012-11-29 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Damaged | Use As-Is |  | Complete |  | Completed |  | Due to overbreak and consequent loss of ground and sprayed concrete at the crown of 51-52, the Primary Lining was sprayed to a safe thickness but could not be completed to the design profile.
| 02SL - Stations (LUL) | Cxxx-NCR-000911 | NCR | Permeability of SCL primary lining |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-04-30 | 2013-04-28 11:37 | -2 | 2012-11-30 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Test results ch 29 to 39 do not comply with this requirement,the results are as the attached certificate
| 02SL - Stations (LUL) | Cxxx-NCR-000912 | NCR | Substation Primary Steelwork - Street Level |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-03-31 | 2013-02-27 12:48 | -32 | 2012-11-30 | Structural Engineering - Steel Member | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The substation primary steelwork at street level is out of position and out of plumb as detailed on the attached sketch
| 02SL - Stations (LUL) | Cxxx-NCR-000920 | NCR | Block work out of alignment tolerance |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-02-28 | 2013-02-27 20:59 | -1 | 2012-12-14 | Architectural - Brickworks/Blockworks | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Though the dimension of 225mm from north gridline has been worked to, the overall blockwork dimension north to south is 7000mm. This is due to an approx 20mm deviation in the concrete slab edging, over which the blockwork cannot overhang - the blockwork has therefore been brought inboard by approx 20mm. In addition, the 225mm dimension shown on the design drawing appears to be incorrect, with both issues leading to a reduced blockwork dimension of 7000mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000923 | NCR | Remedial Works to Doorposts GL 15 & 16 |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-04-30 | 2013-04-25 11:48 | -5 | 2012-12-11 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | The Bracket at the head of the substation door posts at gridline 15 has been fabricated incorrectly and this has resulted in the door opening being reduced by 15mm. This problem is compounded by the main steelwork on gridline 16 being 12mm out of position and this then reduces the available door opening by a further 12mm (25mm in total). See attached drawing
| 02SL - Stations (LUL) | Cxxx-NCR-000926 | NCR | Missing penetration on street level slab |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-02-28 | 2013-02-28 14:34 | 0 | 2012-12-13 | Civil - Civil Engineering General | 500 |  | Design | Rework |  | Complete |  | Completed |  | Penetration not shown on combined service drawing so was not cast into constructed slab.
| 02SL - Stations (LUL) | Cxxx-NCR-000952 | NCR | Twist of IPI keyways to Corridor piles |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-02-28 | 2013-01-31 16:35 | -28 | 2013-01-11 | Surveying - Instrumentation and Monitoring | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Maximum measured spiralling is 13.6° over 1.5m, or 9.1° over 1m.
| 02SL - Stations (LUL) | Cxxx-NCR-000961 | NCR | Permeability of SCL Secondary Lining |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-05-15 | 2013-04-24 21:11 | -21 | 2013-01-24 | Tunnelling - Tunnelling General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Test results from test panels sprayed during spraying of secondary lining to tunnel / escalator junction at ch 56 do not comply with the KT20 requirements stated above. See attached certificate.
| 02SL - Stations (LUL) | Cxxx-NCR-000965 | NCR | Non - compliance with ITP hold points, |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-03-13 | 2013-03-06 15:47 | -7 | 2013-01-30 | Electrical - Cable Management | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | ITP documentation deliverable records and verification documentation not available in ITPs for items installed. IRFs not being issued for required hold points in ITPs
| 02SL - Stations (LUL) | Cxxx-NCR-000969 | NCR | Metal Rainscreen cladding rails |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-03-31 | 2013-02-14 22:44 | -45 | 2013-02-06 | Architectural - Roofing & Exterior Treatment | 500 |  | Design | Rework |  | Complete |  | Completed |  | On delivery of the metal cladding panels it has become apparent that the position of pre-drilled screw holes are not as shown on design GA drawings. Screws are located next to notched corners of the panels and consequently the cladding rails are not wide enough to receive the EJOT JT4-6 5.5x22 fixings. This fixing position is shown close to the panel edge on GA drawings e.g. SPCS-Cxxx-DWG-00050.
| 02SL - Stations (LUL) | Cxxx-NCR-000973 | NCR | Louvre roof screen bolted connections |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-06-30 | 2013-05-07 23:27 | -54 | 2013-02-13 | Architectural - Roofing & Exterior Treatment | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | Bolts between the horizontal roof louvre screen panels and the support steel have been installed. Each connection has 4No bolts however one bolt per connection clashes with the support steel bolts (see attached photo). Although the short bolt is fully through the nut it does not have 3 full threads beyond that is required by the NSSS Section 6.1.4. This occurs at each of the 10 connections along grid line B only
| 02SL - Stations (LUL) | Cxxx-NCR-000974 | NCR | Defects to tunnel secondary lining |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-04-30 | 2013-02-21 09:02 | -68 | 2013-02-14 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | When cleaning the tunnel and the panels sprayed during the night shift of 13/02/13 some rebound was found in the invert joint (LHS) of the panel at approx. ch.4-6m. This is a defect as defined in the specification clause 6.6.9. e), see photos attached.
| 02SL - Stations (LUL) | Cxxx-NCR-000980 | NCR | Paving reinstatement in front of E1, E10, E11 |  | Contr | VIN | LIS - Liverpool Street Station (Central) |  | 2013-12-31 | 2013-11-28 17:47 | -33 | 2013-02-19 | Architectural - Flooring | 5000 |  | Material | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | It was not possible to remove and retain existing paving slabs and new slabs are required to infill the removed sections. Marshalls natural dimpled paving slabs were approved under Cxxx-VIN-O4-ZFM-C101-00364 on 06/02/13 prior to ordering materials. Approval was granted following inspection of a sample of the paving slabs provided by marshalls which closely matches paving slabs by the lower switchroom. Paving slabs are yet to be painted with floor sealer. CRL approval was granted for use of the slabs without LU consultation. The same paving slab is used in various locations in platform 2 however not directly adjacent to where laid. Paving slabs in the public area (& in front of switchroom E1, E10, E11 which will be returned to the public area) are highly polished so dimples have been removed and appear to be a more buff colour. LU has stated that they do not consider these approved slabs to be a suitable match with public area slabs and that these should be replaced. Slabs have been laid in accordance with best practice by minimising the joint widths. New joints on the other side from the straight tide mark do not closely align with the curved platform joints and would require 20-30mm wide birds mouth mortar joints to continue the pattern.
| 02SL - Stations (LUL) | Cxxx-NCR-000987 | NCR | Out of tolerance as-sprayed profiles around chainage 10m |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-04-30 | 2013-03-01 17:46 | -60 | 2013-02-26 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | From as-sprayed surveys taken by SSL it appears that there is a section of tunnel around ch.10m that is out of tolerance by around 30mm, see attahed sketch 'SECTION 10 Initial survey'.
| 02SL - Stations (LUL) | Cxxx-NCR-001002 | NCR | Substation rainscreen window sill |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-04-30 | 2013-03-19 11:22 | -42 | 2013-03-12 | Architectural - Roofing & Exterior Treatment | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | It has been noticed that the sill of the window sits proud of the rainscreen creating a gap below the sill. This could be a potential weakness for water ingress. The profiled steel piece making up the sill seems to be too deep, pushing the sill proud of the rainscreen.
| 02SL - Stations (LUL) | Cxxx-NCR-001005 | NCR | Strength test results to Secondary lining at Junction with Escalator |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-05-15 | 2013-04-24 11:39 | -21 | 2013-03-19 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | 2No. test panels sprayed and cored for testing, 24 hour tests carried out but 7 day and 28 day tests not carried out. From observations carried out by CRL/MMD during spraying it was decicided that hand spraying of the secondary lining in the tunnel would not be allowed, consequently the tests were cancelled by the SCL contractor.
| 02SL - Stations (LUL) | Cxxx-NCR-001008 | NCR | Pile B136 Defect |  | Contr | VIN | LIS - Liverpool Street Station (Central) |  | 2013-08-31 | 2013-07-24 08:38 | -38 | 2013-03-15 | Geotechnical Engineering - Concrete - Bored Pile | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete |  | Completed |  | Gap observed between pile B136 and adjacent female piles over height of corridor currently excavated. Cracks observed on face of pile at approximately 1.5m below cut-off level which expose the skid spacers attached to the reinforcing cages.
| 02SL - Stations (LUL) | Cxxx-NCR-001011 | NCR | Structural base at lvl 97.115 |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-04-30 | 2013-03-21 17:28 | -40 | 2013-03-19 | Tunnelling - Tunnelling General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Structural base at lvl 97.115, concrete as-built level upto 60mm high in footprint of sump tank.
| 02SL - Stations (LUL) | Cxxx-NCR-001026 | NCR | Paint to Switchroom Steelwork |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-04-18 | 2013-04-08 17:44 | -10 | 2013-04-04 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | For the 3rd/top coat of paint to the steelwork an equivalent product __ C237 was used instead of the agreed paint
| 02SL - Stations (LUL) | Cxxx-NCR-001033 | NCR | Non-conformant 28-day cube strength results for piles B129, B131, B144 & B156 |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-05-31 | 2013-04-24 21:37 | -37 | 2013-04-11 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | 28 day cube tests reults on piles B129, B131, B144 & B156 yielded the follwing results; B129 - 10.5N/mm^2 B131 - 9.9N/mm^2 B144 - 41.7N/mm^2 B156 - 42.9N/mm^2
| 02SL - Stations (LUL) | Cxxx-NCR-001046 | NCR | Non conformances identifed in final inspections |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2014-11-30 | 2014-10-22 17:01 | -39 | 2013-04-19 | Civil - Civil Engineering General | 30000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The following items were identified during final inspections with LU and are therefore raised as a non-conformance: 1. E53 - Make good the fire mastic joint seen to be peeling away from the fire boarding at high level on the eastern internal elevation of the E53. 2. E51, E52, E53 - Frame head to double doors displays slight movement when doors slammed / powerfully shaken in shut position. 3. E51, E52, E53 - Threshold strips to doors rattle when stepped upon. 4. E51 - Minor repairs to floor. 5. New switchroom building exterior - no stop beads to external corners. 6. New switchroom roof - the roof vapour barrier appeared not to terminate against the gutter, which consequently would allow moisture to rundown southern exterior wall of the structure. Photographs required to show that the roof vapour barrier is installed as per the design. 7. All fire stopping requires identification stickers against each section (door surrounds, cable penetrations etc.). 8. Generally – It was observed that a number of mortar joints on the external blockwork façade required making good (Example – an area adjacent to the MJ3 mastic joint, approximately 1.5m off the floor on the northern elevation). 9. Generally – __ must not penetrate the fire boarding (Example – __ above the E51 and E52 doors). 10. Generally – All joint greater than 2mm must be filled with approved fire mastic. 11. All switchroom plant to be identified with Traffolyte labels. 12. Insulation to A/C pipe work to be addressed, sections require replacing. 13. Insulation to A/C pipe work to be addressed, sections require replacing. 14. Workmanship of cut ventilation ducts requires addressing. 15. BMS 'Fan run hours' meters missing to mechanical plant. 16. BMS DP switches to be completed to mechanical plant. 17. BMS Lamp Test facility missing to mechanical plant. 18. No circuit Identification Labels in LV distribution boards. 19. PVC cable ties, steel ties to be installed. 20. All conduits/cables to be identified i.e. 'to and from’. 21. All detectors and bases must be identified. 22. Call point signs to be fitted by each call point. 23. Saddle missing on a conduit in OLBI Room (E52). 24. On the emergency lighting there were no emergency discs on any fitting.
| 02SL - Stations (LUL) | Cxxx-NCR-001076 | NCR | Compressible filler installation for 450mm sewer |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-06-30 | 2013-05-16 16:06 | -45 | 2013-05-09 | Civil - Utilities Engineering | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Compressible filler installed at the joint of the first pipe but not across the full width of the concrete surround.
| 02SL - Stations (LUL) | Cxxx-NCR-001080 | NCR | Door seals to new Switchroom doors, E51, E52, E53 |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2013-09-30 | 2013-07-30 22:41 | -62 | 2013-05-15 | Fire - Compartmentation | 1000 |  | Material | Rework | 4 (0.5-3k) | Complete |  | Completed |  | No evidence of compliance has been provided for the Norsound Nor710 doorseals and the mass of material appears to be above the limit for minor use items.
| 02SL - Stations (LUL) | Cxxx-NCR-001091 | NCR | 28 day cube results |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-07-31 | 2013-06-11 22:52 | -50 | 2013-05-22 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Results not available for 28 days cube tests for two sample sets relating to the first pour of the substation base slab and the substation base slab upstands.
| 02SL - Stations (LUL) | Cxxx-NCR-001112 | NCR | New stairs within QVT Room 2/736 |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-07-31 | 2013-07-04 11:44 | -27 | 2013-06-17 | Architectural - General | 500 |  | Design | Rework |  | Complete |  | Completed |  | The gap between the door and edge of top riser, on the landing, is less than 400mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001113 | NCR | Design of fixings to the new cable tunnel CMS |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-07-31 | 2013-07-04 11:54 | -27 | 2013-06-17 | Electrical - Cable Management | 500 |  | Design | Repair |  | Complete |  | Completed |  | No design or design check have been formally submitted for acceptance to the Project Manager. Only informal calculations have been viewed.
| 02SL - Stations (LUL) | Cxxx-NCR-001118 | NCR | Dripshield fabricated without an accepted ITP |  | Contr | VIN | LIS - Liverpool Street Station (Central) |  | 2014-04-30 | 2014-03-06 09:43 | -55 | 2013-06-21 | Architectural - Ceilings & Soffits | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Dripshield fabricated off site before ITP accepted
| 02SL - Stations (LUL) | Cxxx-NCR-001141 | NCR | Render to soffit closing detail |  | Contr | VIN | LIS - Liverpool Street Station (Central) |  | 2013-10-31 | 2013-07-24 09:54 | -99 | 2013-07-04 | Architectural - Brickworks/Blockworks | 3000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete |  | Completed |  | Due to limited space, as the blockwork is out of alignment, render has had to be stopped short of the soffit closing piece creating a possible weak point for waterproofing.
| 02SL - Stations (LUL) | Cxxx-NCR-001154 | NCR | Lack of IRF Notification for Gas Main diversion work |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2013-09-08 | 2013-07-11 23:09 | -59 | 2013-07-10 13:51 | Utilities Engineering - Gas | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | No IRFs have been submitted for the gas diversions in teh above ground work site
| 02SL - Stations (LUL) | Cxxx-NCR-001155 | NCR | Lower Switchroom roof flashings |  | Contr | VIN | LIS - Liverpool Street Station (Central) |  | 2014-03-30 | 2013-11-21 10:16 | -129 | 2013-07-30 10:50 | Architectural - Roofing & Exterior Treatment | 4000 |  | Design | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | P30201-C1M12-A00-65830 shows roof flashing are to be installed to the edge of the lower switchroom roof. On early inspection of the installation, it has been noticed that the minimum 50mm overlap onto the blockwork has not been achieved. Since the design drawings have been issued, a PMI to add render to the outside of the lower switchroom has been actioned, so in the current layout, the flashing finishes at the top of the waterproof render with no overlap. Concerns have been raised regarding the performance of the system without an overlap.
| 02SL - Stations (LUL) | Cxxx-NCR-001156 | NCR | Damage to roof louvre sections |  | Contr | VIN | LIS - Liverpool Street Station (Central) |  | 2014-09-30 | 2014-08-20 10:14 | -41 | 2013-07-30 14:14 | Architectural - Roofing & Exterior Treatment | 2000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following installation of monitoring prisms to the south side of the substation roof, it has been noticed that the bolts clamping the prisms to the structure have damaged the coating to the uprights of the louvre. 8 no. damaged areas are present consisting of 10mm round marks where the paint has been removed.
| 02SL - Stations (LUL) | Cxxx-NCR-001157 | NCR | Blockage of __ Re-Groutable Hose at Shaft Top |  | Contr | VIN | LIS - Liverpool Street Station (Central) |  | 2013-10-31 | 2013-08-14 23:06 | -78 | 2013-08-06 18:41 | Civil - Tunnelling | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Two __ regroutable hoses were installed at the top of the shaft in the opening formed in the substation base slab. A third hose was installed under the base slab - see sketch attached. Following the re-grouting of the hose under slab it was noted that grout was present in the termination box for the two hoses fixed in the slab opening. The hoses were subject to water testing with the following results. The upper hose is open and available for use. The lower of the two tubes is blocked by resin from previous grouting of the tube under the slab.
| 02SL - Stations (LUL) | Cxxx-NCR-001158 | NCR | Substation rainscreen external window |  | Contr | VIN | LIS - Liverpool Street Station (Central) |  | 2014-03-31 | 2014-01-07 15:36 | -83 | 2013-08-07 09:21 | Architectural - Glazing | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | P30201-C1M12-A00-D-65881 shows details for the fire rated windows. The external window, which ties into the rainscreen cladding, was to be installed 50mm within the building leaving an edge for the plasterboard and insulation to terminate at. The as found condition is similar to the detail for the internal window and has been installed flush with the inside of the blockwork. This leaves an open detail for plasterboard and insulation.
| 02SL - Stations (LUL) | Cxxx-NCR-001159 | NCR | Office Columns enclosed with Fire-Boarding without insulation |  | Contr | VIN | LIS - Liverpool Street Station (Central) |  | 2013-12-31 | 2013-12-06 12:13 | -25 | 2013-08-13 09:02 | Architectural - Finishes | 1500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Supervision - Supervisor not familiar with the work | Completed |  | i) Office columns have been fully enclosed with fire-boarding without insulation product installed between the back of the columns & inside face of the external blockwork walls. Cxxx drawings 65823, 65881, 65913 & 65912 show this requirement (though noted that in several cases, the insulation detailed is part of the dry-lining, which will not fit) ii) Drawings generally show fireboarding butting up to dry lining, however installation of fireboarding was undertaken directly up to blockwork walls (i.e. fireboarding installed before dry lining). Noted however, that there is some ambiguity in the Cxxx design, which though shows majority of fireboarding butting up to dry lining, some fireboarding is shown taken right up to the wall. Further noted, that it has now been confirmed that all fireboarding is to butt directly up to the blockwork walls, to avoid a fire bridge via the back of the dry lining. To be formerly covered on FCD
| 02SL - Stations (LUL) | Cxxx-NCR-001160 | NCR | Substation External Render Joints - Poor Quality Mastic |  | Contr | VIN | LIS - Liverpool Street Station (Central) |  | 2013-12-31 | 2013-11-25 13:37 | -36 | 2013-08-13 09:01 | Architectural - Finishes | 5000 |  | Workmanship | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Mastic applied to 10mm gap between render joint beads in top 2/3 of facade is of poor quality, as it has not be applied between the straight metal edges of the bead. Rather the mastic sits between the render itself, which as it has an aggregate finish, provides an uneven line.
| 02SL - Stations (LUL) | Cxxx-NCR-001161 | NCR | Substation External Render Joints - Incorrect Mastic |  | Contr | VIN | LIS - Liverpool Street Station (Central) |  | 2013-12-31 | 2013-11-25 12:47 | -36 | 2013-08-13 09:00 | Architectural - Finishes | 1000 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Mastic applied to bottom 1/3 of substation façade by mastic contractor (in response to above NCR-001160) is incorrect product, and not LUL approved.
| 02SL - Stations (LUL) | Cxxx-NCR-001162 | NCR | Louvre Door Hinges |  | Contr | VIN | LIS - Liverpool Street Station (Central) |  | 2013-12-31 | 2013-12-12 13:56 | -19 | 2013-08-13 08:59 | Architectural - Doors | 1000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Doors designed without sufficiently strong hinges to support weight of doors. Consequently the hinges buckled on the factory test rig.
| 02SL - Stations (LUL) | Cxxx-NCR-001163 | NCR | Substation Main Stairs - Break out of Slab Pockets for Stringers @ Mezz Level |  | Contr | VIN | LIS - Liverpool Street Station (Central) |  | 2013-10-31 | 2013-10-31 16:14 | 0 | 2013-08-14 17:47 | Structural Engineering - Structural Engineering - General | 1000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The main stair stringers at mezz level are designed to bear directly onto the mezz steelwork beam along the edge of the stair opening. With the mezz slab being cast ahead of stair installation, pockets should have been cast to accommodate the stringers, however were not.
| 02SL - Stations (LUL) | Cxxx-NCR-001164 | NCR | Mess Room - Use of Floor Screed Ahead of Approval |  | Contr | VIN | LIS - Liverpool Street Station (Central) |  | 2013-10-31 | 2013-10-31 16:35 | 0 | 2013-08-16 18:15 | Architectural - Flooring | 1500 |  | Material | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Other | Completed |  | __ screed is the approved product for use in the Substation mess room. __ AM35 has instead been installed, ahead of MCR being submitted or approved.
| 02SL - Stations (LUL) | Cxxx-NCR-001165 | NCR | Defects to concrete wall in Utilities Corridor |  | Contr | VIN | LIS - Liverpool Street Station (Central) |  | 2013-10-31 | 2013-09-10 16:02 | -51 | 2013-08-20 10:35 | Structural Engineering - Concrete Member | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following the striking of the formwork to the top of the walls and roof to the Utilities Corridor between GL3 and 7, 2no defects became apparent (see attached photos) in the northern section at the top of the wall.
| 02SL - Stations (LUL) | Cxxx-NCR-001166 | NCR | 750/750 piles lacking interlock at high level |  | Contr | VIN | LIS - Liverpool Street Station (Central) |  | 2014-03-30 | 2013-12-18 15:41 | -102 | 2013-08-20 18:03 | Geotechnical Engineering - Concrete - Bored Pile | 10000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | During the excavation for the Utilities Corridor between GL8 and the QVT, it has become apparrent that a number of the 750mm male piles are not interlocked with the female piles, as required by the specification. To date, this issue has been identified in approximately 5no piles to the east of GL8. the gaps vary in size but are generally approximately 30-50mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001167 | NCR | Damage to __ waterproofing membrane on balustrades |  | Contr | VIN | LIS - Liverpool Street Station (Central) |  | 2013-11-30 | 2013-11-25 11:59 | -5 | 2013-08-28 15:53 | Architectural - Roofing & Exterior Treatment | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The __ waterproofing system has been damaged in several locations on the louvre balustrades at approx mid height of the balustrade. At approx the same height mastic has been allowed to run down the __ r
| 02SL - Stations (LUL) | Cxxx-NCR-001168 | NCR | Lower Switchroom finished floor level Flattness |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2013-12-31 | 2013-11-21 09:57 | -40 | 2013-08-20 18:52 | Architectural - Flooring | 10000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | Further to Cxxx-NCR-00741, During the HV equipment installation it has been noted that chims were installed to achieve the correct equipment level tolerance as per the manufaturer's specification. The chims were never part of the HV Switchboard installation as the desired floor tolerance were supposed to be achieved via a scread finish to the floor as per above referenced NCR.
| 02SL - Stations (LUL) | Cxxx-NCR-001169 | NCR | Substation Mess Room Render Quality |  | Contr | VIN | LIS - Liverpool Street Station (Central) |  | 2013-11-30 | 2013-10-31 16:45 | -30 | 2013-08-23 18:58 | Architectural - Walls | 3000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Mess room render is not in accordance with spec, with regards to following: 1) Beads around doorway are missing (spec states beads required to all external corners) 2) Render displays trowel marks, hollows & is generally uneven (spec states coatings shall be finished with a trowel or float to produce tight, matt, smooth surface with no hollows, abrupt changes of level or trowel marks) 3) Internal angles in corner are rounded and not plumb (spec states surfaces shall be finished with all angles & corners to a right angle / walls & reveals shall be plumb & square).
| 02SL - Stations (LUL) | Cxxx-NCR-001170 | NCR | Missing Surveys regarding the utilities diversion excavation works |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2014-10-26 | 2014-09-29 09:25 | -27 | 2013-09-16 17:25 | Civil - Utilities Engineering | 1500 |  | Design | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | The contractor failed to provide the surveys shown in the attached pdf
| 02SL - Stations (LUL) | Cxxx-NCR-001171 | NCR | Breakout of QVT supoprt column outside of permit |  | Contr | VIN | LIS - Liverpool Street Station (Central) |  | 2013-11-30 | 2013-09-30 12:09 | -61 | 2013-09-11 15:56 | Civil - Construction Health & Safety | 3500 |  | Supervision/Management | Rework | 3 (3-6k) | Complete | Management Problem - Other | Completed |  | A column in the QVT was demolished outside the limits of the permit to demolish. This column supports a beam spannig across the QVT and a roof slab to the redundant CER room. The exact nature of the beam and column were unknown at the time of demolition. A RIVO report and investigation were carried out, concluding that better communication and supervision could have prevented this incident.
| 02SL - Stations (LUL) | Cxxx-NCR-001172 | NCR | Substation Transformer Room - Out of Tolerance Floor Slab |  | Contr | VIN | LIS - Liverpool Street Station (Central) |  | 2013-12-31 | 2013-11-08 09:32 | -53 | 2013-09-13 13:17 | Architectural - Flooring | 5000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | The substation street level slab has been found to be out of tolerance with regards to British Standards (specifically BS8204, which is refered to in BS5606, which itself is referred to in the Crossrail Civil & Structural specification). BS tolerance is a max allowable 5mm departure from a 2m straight edge resting on the floor, and a max allowable 15mm departure from datum level across the whole area. Further, the requested tolerance for the street level equipment (max deviation of 3mm in 1m) has not been achieved. A survey of the street level slab is attached
| 02SL - Stations (LUL) | Cxxx-NCR-001173 | NCR | Construction records of the demountable Cladding |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2014-10-31 | 2014-10-31 11:42 | 0 | 2013-09-30 11:53 | Architectural - General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | There were no verifying records for pull out test on the fixings that hold the support frame work for the demountable cladding, Substation Architectural Specification Cxxx-MMD-A-RSP-C101-00006, H43.2101 All fixings to brick retaining wall will be required to be load and pull out tested to comply with LU standard 1-050 A2: Civil Engineering – Common Requirements: Section 3.10.
| 02SL - Stations (LUL) | Cxxx-NCR-001174 | NCR | Substation Corium Brick Cladding - Mortar Colour Variance |  | Contr | VIN | LIS - Liverpool Street Station (Central) |  | 2014-09-30 | 2014-09-08 17:35 | -22 | 2013-09-30 12:01 | Architectural - Finishes | 1000 |  | Material | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Though the overal brick slip cladding mortar application is still work in progress, there are several completed localised areas where the colour does not match that of the sample panel (areas in question display a lighter shade than the sample).
| 02SL - Stations (LUL) | Cxxx-NCR-001175 | NCR | Substation Patio Area - Additional Service Holes Cored |  | Contr | VIN | LIS - Liverpool Street Station (Central) |  | 2013-12-20 | 2013-12-06 13:17 | -14 | 2013-09-30 12:14 | Structural Engineering - Structural Engineering - General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | RFI 1187 confirmed 3no allowable areas for individual core holes to be put through. Due to a misunderstanding, 5no holes have been put through, with 2no pairs of 2no holes 50mm apart, as shown in the attached sketch.
| 02SL - Stations (LUL) | Cxxx-NCR-001176 | NCR | Low Handraill Sections on the Substation Main Stairs |  | Contr | VIN | LIS - Liverpool Street Station (Central) |  | 2014-03-31 | 2014-02-26 23:07 | -33 | 2013-09-30 16:30 | Architectural - Handrail | 3000 |  | System Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Where the substation main stairs meet the Mezzanine and Street level slabs the handrail does not meet the 900mm minimum height
| 02SL - Stations (LUL) | Cxxx-NCR-001178 | NCR | Method of drilling into Eldon Street sewer |  | Contr | VIN | LIS - Liverpool Street Station (Central) |  | 2013-12-31 | 2013-11-07 10:52 | -54 | 2013-10-11 16:09 | Utilities Engineering - Water | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The break-through into the TWUL Eldon Street sewer for the 450mm sewer diversion to 100 Liverpool Street was planned to be done using a single 700mm core. The hole was actually created by stitch-drilling, which was against the method set out in the Method Statament and contrary to the Works Information (following the issue of PMI-00281).
| 02SL - Stations (LUL) | Cxxx-NCR-001179 | NCR | 100 Liverpool Street Water Connections |  | Contr | VIN | LIS - Liverpool Street Station (Central) |  | 2014-06-30 | 2014-05-19 10:53 | -42 | 2013-11-05 08:01 | Civil - Utilities Engineering | 3000 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | During the 100 Liverpool Street water main connection works the incorrect couplers were installed on one of the 225mm water mains. The design for the main detailed that thrust reistant couplers should be used on the rocker pipe,instead non-thrust resistant couplers were installedl on one of the 225mm water mains. The combination of the wrong couplers and the outstanding thrust block design meant the connection failed.
| 02SL - Stations (LUL) | Cxxx-NCR-001180 | NCR | Substation Toilet & Washroom Walls - Tile Preparation Render Out of Tolerance |  | Contr | VIN | LIS - Liverpool Street Station (Central) |  | 2014-04-30 | 2014-02-17 08:20 | -72 | 2013-11-13 17:31 | Architectural - Walls | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Render applied to the walls of the toilet & washroom in preparation for tiling, was not installed to tolerance (3mm under a 2m straight edge)
| 02SL - Stations (LUL) | Cxxx-NCR-001181 | NCR | QVT South Wall Vertical Dowels |  | Contr | VIN | LIS - Liverpool Street Station (Central) |  | 2014-01-31 | 2013-11-21 10:42 | -71 | 2013-11-18 09:15 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 41no 40mm vertical dowels are required to be installed between the QVT roof and the new South Retaining Wall. At the final inspection prior to the concrete pour, it was noticed that one of the dowels was replaced by a 32mm rebar section. The 32mm rebar was cut to the correct length and was installed in the correct position.
| 02SL - Stations (LUL) | Cxxx-NCR-001182 | NCR | 11kV Cable wound wrongly on cable drum delivered to site |  | Contr | VIN | LIS - Liverpool Street Station (Central) |  | 2014-03-31 | 2014-02-17 08:28 | -42 | 2013-11-27 14:59 | Electrical - Power Distribution | 3000 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | 11kV Cable wound wrongly on cable drum delivered to site by __ and caused problems and possible damage to the cable whilst being installed.
| 02SL - Stations (LUL) | Cxxx-NCR-001183 | NCR | Poorly wound cable onto drum |  | Contr | VIN | LIS - Liverpool Street Station (Central) |  | 2014-04-30 | 2014-02-12 16:42 | -77 | 2013-11-27 15:13 | Electrical - Power Distribution | 3000 |  | Material | Reject | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After the previous drum of 11kV 3 core cable came to site poorly wound onto the drum, the next was inspected prior to unloading. This drum was found to be similary poorly wound and was subsequently sent away from site.
| 02SL - Stations (LUL) | Cxxx-NCR-001184 | NCR | M&E Frame Headroom Clearance Issue |  | Contr | VIN | LIS - Liverpool Street Station (Central) |  | 2014-09-30 | 2014-07-14 16:00 | -78 | 2013-11-29 14:55 | Archaeology - General | 1000 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The M&E Service frame was erected lower than originally planned to enable the setting of the Busbars on the frame. This caused the head height from the top landing of the AM02 stairs to a cantilever section of the Frame to diminish to 1930mm (the frame design did not allow for any level adjustment). Part k of the Building Regulation in LU standard 1-133 refers to a minimum of 2m Head height requirement.
| 02SL - Stations (LUL) | Cxxx-NCR-001185 | NCR | Utilities Corridor South Wall Rebar Concrete Cover GL8-9 |  | Contr | VIN | LIS - Liverpool Street Station (Central) |  | 2014-06-30 | 2014-03-30 10:26 | -92 | 2013-12-02 18:54 | Civil - Civil Engineering General | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Specification for the Utilities Corridor reinforced concrete works, requires minimum 45mm concrete cover to the rebar. Between GL8-9 South Wall lower level concrete poured on 29/11, the cover to the rebar at a number of locations is less than the specified 45mm. The cover is as low as 20mm to some locations.
| 02SL - Stations (LUL) | Cxxx-NCR-001186 | NCR | Utilities Corridor South Wall Waterproofing GL8-9 |  | Contr | VIN | LIS - Liverpool Street Station (Central) |  | 2014-03-31 | 2013-12-11 13:47 | -110 | 2013-12-04 11:26 | Civil - Civil Engineering General | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Specification for the Utilities Corridor waterproofing (Cxxx-MMD-C-DDB-C101_Z-89022), requires 75mm lap (typical) at the waterproof membrane joints. Between GL8-9 South Wall lower level concrete poured on 29/11, the exposed waterproofing is limited to 30mm at some locations.
| 02SL - Stations (LUL) | Cxxx-NCR-001187 | NCR | AM12 Ships Ladder - Clash With Existing HV Cable Route & Protection |  | Contr | VIN | LIS - Liverpool Street Station (Central) |  | 2014-03-31 | 2014-02-17 13:19 | -42 | 2013-12-08 10:56 | Architectural - General | 3000 |  | Design | Reject | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The northern 2no columns of the AM12 ships ladder, which support the intermediate landing, clash with the HV cable route and protection running along the Platform 2/3 boundary in the region of 350mm. This was only picked up once the components had been manufactured & delivered to site for installation.
| 02SL - Stations (LUL) | Cxxx-NCR-001188 | NCR | Substation Louver Door Western Leaf - Slightly Warped |  | Contr | VIN | LIS - Liverpool Street Station (Central) |  | 2014-03-31 | 2014-01-08 15:00 | -82 | 2013-12-09 18:03 | Architectural - Doors | 5000 |  | Material | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | The active leaf of the western louver doors is slightly warped along the bottom, which has the effect of prevent the door pulling to without the use of excessive force over the final 15-20mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001189 | NCR | Manhole MHS1 base slab concrete grade |  | Contr | VIN | LIS - Liverpool Street Station (Central) |  | 2014-03-31 | 2014-02-25 10:44 | -34 | 2013-12-10 17:55 | Civil - Civil Engineering General | 1500 |  | Material | Repair | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | The concrete used for the manhole MHS1 base slab is grade C35/45 and not C40/50 as required by the drawing Cxxx-MMD-U-DDL-C101-50050. Use of C40/50 would not have been compliant with specification Cxxx-MMD-C-RSP-C101-00007 cl. KF10.1309 with regards to the cement content.
| 02SL - Stations (LUL) | Cxxx-NCR-001190 | NCR | Galvanising of Architectural Metalwork |  | Contr | VIN | LIS - Liverpool Street Station (Central) |  | 2014-05-31 | 2014-03-10 09:51 | -82 | 2013-12-13 08:33 | Architectural - Finishes | 500 |  | System Defect | Repair | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | ITP Cxxx-VIN-C-ITP-C101-50033 requires that a DFT Certificate is provided for all items of galvanised metalwork. For several items, listed below, the DFT certificate was not requested by __ from the galvaniser. Items without DFT Certs - AM01 Cat Ladders, AM02 Stairs, AM10 Stairs, AM10a Stairs, AM11 Companionway Ladder, Cable Shaft Stairs, Security Grills (Splice Box), Splice Box Access Route, Wind Posts
| 02SL - Stations (LUL) | Cxxx-NCR-001191 | NCR | Utility Corridor Roof Rebar Cover GL8-GL9 |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2014-03-31 | 2014-01-07 10:10 | -83 | 2013-12-20 15:41 | Civil - Civil Engineering General | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | During a final pre pour inspection by CRL (__ ) in the morning of 20th December following a Pre Pour Inspection by CRL (__ ) of the Utility Corridor Roof between GL8-9, it was apparent that the minimum cover requirements of 45mm, had still not been met despite the issue being raised by Crossrail during previous visits. In some areas rebar was touching the formwork meaning there was no concrete cover at all. CRL were sent the IRF by Cxxx on the 19th December which includes checking of these items. A photo from 19th December of some offending section of rebar has been attached.
| 02SL - Stations (LUL) | Cxxx-NCR-001192 | NCR | Broad Street Avenue - Section of Retaining Wall Demolished In Error |  | Contr | VIN | LIS - Liverpool Street Station (Central) |  | 2014-10-26 | 2014-10-14 14:54 | -12 | 2013-12-24 11:53 | Civil - Excavation | 1000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | An operative demolished a section of W297 retaining wall as part of the BSA streetworks, that we neither had approval for nor any requirement to undertake as can be seen in IMG_1991.jpg. The operative in question was told to dig down the rear of the retaining wall, to prove the space available, after finding services on the line of the original east end inspection chamber. This was alas not done on Saturday as intended, instead they left & did it on Sunday. There was no reason for them to break down the retaining wall - Galldris had previously put a core hole through the wall for the drainage, and it was simply a case of digging down to find the hole in the back of the retaining wall.
| 02SL - Stations (LUL) | Cxxx-NCR-001193 | NCR | GL1-2 Water Pockets beneath Waterproof layer |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2014-04-30 | 2014-03-03 23:18 | -58 | 2014-01-07 13:07 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During the final CRL inspection of the GL1-2 Utility Corridor Base slab it was noted that there were large pockets of water beneath the waterproofing layer below the rebar. This was is a result of recent downpours of rain over the Xmas period. It was decided on site with Cxxx (__ ) and CRL (__ and __ ) that the concrete would be poured from GL2 (base slab already completed) to force the water out of waterproofing layer at GL1 using the weight of the concrete. During the concrete pour CRL inspected the pour and found that the concrete was being poured from GL1 and a large water bubble has been built up below the waterproofing layer. See Cxxx-MMD-C-DDD-C101_Z-89031 drawing for waterproofing details. Note the 20mm compressible material was omitted below the base slab in Cxxx-FCD-1136.
| 02SL - Stations (LUL) | Cxxx-NCR-001196 | NCR | Damaged LVAC cable |  | Contr | TWC | LIS - Liverpool Street Station (Central) |  | 2014-04-30 | 2014-03-03 17:53 | -58 | 2014-01-13 10:44 | Electrical - Switchgear | 3000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 1 of the 8 1000mm cable form auxiliary transformer No 1 to the LVAC switch board has been damaged during installation. Possible replacement required.
| 02SL - Stations (LUL) | Cxxx-NCR-001197 | NCR | Non-compliant security doors in the new substation |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2014-08-31 | 2014-08-28 14:44 | -3 | 2014-01-13 18:15 | Architectural - Doors | 25000 |  | Material | Rework | 2 (6-60k) | Complete | External Phenomenon - Other | Completed |  | The 3 High Security Doors at street level in the Substation (doors DR-13, 15 and 21) are not certifed to LPS level 3 and will have to be replaced.
| 02SL - Stations (LUL) | Cxxx-NCR-001198 | NCR | MHS1 Walls - Missing Rebate |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2014-04-30 | 2014-02-18 22:45 | -71 | 2014-01-14 09:32 | Civil - Civil Engineering General | 2000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During the inspection of the MHS1 Roof slab with __ , it was found that the 25x25mm rebate required on both the roof slab and manhole walls had not been installed on the roof despite it being present when the final CRL wall inspection took place (photo to show rebate present on 20th December 2013) It appears that the contractor took the decision not to install this following the final inspection the 20th December. Refer to Cxxx-mmd-u-ddl-c101-50050 c03 - typical joint seal detail This is of even more inportance after the contractor requested a pre cast design for the roof slab and the rebate insures the joint is waterproof
| 02SL - Stations (LUL) | Cxxx-NCR-001199 | NCR | E Series Piles Survey |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2014-04-30 | 2014-03-04 17:42 | -57 | 2014-01-14 09:46 | Civil - Excavation | 1500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Following a revision of the Broadgate E Series Pile Line (Cxxx-PMI-00423) the contractor was instructed to carry out an excavation on the pile line down to 2m and install sheet piles on the north of the excavation to protect the utilities installed by Cxxx. Further to this as part of Stage 1 (point 1.4) defined in the works information on drawing Cxxx-MMD-C-DDB-C101_Z-42950, 1.4 - Contractor to survey and provide Crossrail Project Manager with as built sheet locations and verticality (all sections) for acceptance prior to back filling pre-dig trench. The Contrator has provided a survey to the Project Manager but this does not include information about the verticality of the sheet piles, nor was it issued for acceptance prior to backfilling the trench As part of the
| 02SL - Stations (LUL) | Cxxx-NCR-001200 | NCR | Combustible Materials left in LU operational station during traffic hours |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2014-04-30 | 2014-02-19 23:20 | -70 | 2014-01-20 18:02 | Architectural - General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | A number of combustible materials are being stored adjacent to the new LU Switchrooms on Platform 3 during traffic hours, also not in accordance with the storage licence
| 02SL - Stations (LUL) | Cxxx-NCR-001202 | NCR | Pile E124 reinforcement level |  | Contr | VIN | LIS - Liverpool Street Station (Central) |  | 2014-04-30 | 2014-04-28 10:20 | -2 | 2014-01-27 11:54 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Pile 124 was drilled between 23/01/14 - 24/01/14. The pile was drilled to the required depth and the top of cage was to the required design level. The pile was then concreted and the process of case extraction took longer than expected (2.5) hours which led to the cage coming up with the casings. The top of cage as built level is 113.820mm (the projecting steel was cut off) which is +170mm out of tolerance.
| 02SL - Stations (LUL) | Cxxx-NCR-001203 | NCR | Pile E126 reinforcement cage level |  | Contr | VIN | LIS - Liverpool Street Station (Central) |  | 2014-04-30 | 2014-04-28 10:51 | -2 | 2014-01-27 16:57 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Pile E126 was concreted on 27/01/2014. The pile was initially drilled approx. 200mm lower than the cut-off level. The cage was installed to design level by hanging on casing using chains. When the casing was removed, the cage dropped by approx. 190mm which means that it is 150mm out of tolerance.
| 02SL - Stations (LUL) | Cxxx-NCR-001204 | NCR | Water seepage through invert collecting on walkway |  | Contr | VIN | LIS - Liverpool Street Station (Central) |  | 2014-04-30 | 2014-03-30 10:52 | -31 | 2014-01-28 11:00 | Tunnelling - Walkways | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Design Problem - Not Defined | Completed |  | Water seeping through concrete walkway in invert of cable tunnel and collecting on the surface of walkway before running off into side channels. Concrete at seepage point has been finished to incorrect falls
| 02SL - Stations (LUL) | Cxxx-NCR-001205 | NCR | Surface Cracks to Substation Base slab |  | Contr | VIN | LIS - Liverpool Street Station (Central) |  | 2014-03-29 | 2014-03-27 13:53 | -2 | 2014-01-28 14:10 | Structural Engineering - Concrete Member | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Cracks noted in top surface of substation base slab,above and parallel to reinforcement see sketch and photo attached. Crack widths vary both along cracks and in different cracks and are difficult to measure accurately because of previous grinding operation. Maximum width is approximately 1.0 mm
| 02SL - Stations (LUL) | Cxxx-NCR-001206 | NCR | Pile E125 verticality |  | Contr | VIN | LIS - Liverpool Street Station (Central) |  | 2014-05-31 | 2014-03-18 23:19 | -74 | 2014-01-30 16:04 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Pile E125 was drilled to full depth, 11.5m, and the verticality test completed shows that the verticality of the pile is slightly out of tolerance. The 1:150 tolerance at depth of 11.5m allows for up to 77mm of deviation but the actual deviation was 90mm as can be seen from the attached graph. An obstruction, 100mm steel pipe, was encountered at approx. 3.7m deep going through the footprint of the pile which the rig had to drill through and which resulted in the casings being kicked out of position.
| 02SL - Stations (LUL) | Cxxx-NCR-001207 | NCR | Pile E125 final level of cage reinforcement |  | Contr | VIN | LIS - Liverpool Street Station (Central) |  | 2014-05-31 | 2014-04-29 14:46 | -32 | 2014-01-30 18:22 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Pile E125 was concreted on 29/01/2014. The pile was initially drilled approx. 200mm lower than the cut-off level. The cage was installed to design level by hanging on casing using chains. When the casing was removed, the cage dropped by approx. 100mm which means that it is 50mm out of tolerance.Top level of reinforcement cage for pile E125 is 113.400 mOD.
| 02SL - Stations (LUL) | Cxxx-NCR-001208 | NCR | Pile E123 final level of reinforcement |  | Contr | VIN | LIS - Liverpool Street Station (Central) |  | 2014-05-31 | 2014-05-02 16:11 | -29 | 2014-01-31 18:21 | Civil - Civil Engineering General | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Pile E123 was concreted on 31/01/2014. Pile E125 was concreted on 29/01/2014. The pile was initially overdrilled to mitigate the ongoing risks we are having with concrete and cages being lifted up. The cage was installed to design level by by installing 2no cage feet. When the casing was removed, the feet collapsed and the cage dropped by approx. 470mm which means that it is 420mm out of tolerance.Top level of reinforcement cage for pile E123 is 113.030 mOD.
| 02SL - Stations (LUL) | Cxxx-NCR-001209 | NCR | Feeder cables F657, F655 & F658 |  | Contr | TWC | LIS - Liverpool Street Station (Central) |  | 2014-08-31 | 2014-08-11 09:10 | -20 | 2014-02-11 07:41 | Electrical - Cable Management | 5000 |  | Material | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Issued and approved cable schedule indicates that the 11kV 3 core 185mm feeder cables would be XLPE/SWA/LSF where as the installed cables are XPLE/SWA/MDPE. Please confirm that the installed cables are fully compliant with LUL standards.
| 02SL - Stations (LUL) | Cxxx-NCR-001210 | NCR | Pile E124 28-day concrete strength |  | Contr | VIN | LIS - Liverpool Street Station (Central) |  | 2014-05-31 | 2014-04-28 15:04 | -33 | 2014-03-03 17:34 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | We have received the concrete test cube report for the 28-day strength for pile E124 and is lower than the specification. On average, the compressive strength developed is 41.6 N/mm2 which is lower than the 45 N/mm2 specified.
| 02SL - Stations (LUL) | Cxxx-NCR-001211 | NCR | Neutral Link in Isolator on E30 Class A DB within switchroom E51 not reconnected prior to energisation |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2014-08-31 | 2014-06-08 22:45 | -84 | 2014-03-06 16:08 | Electrical - Electrical Engineering General | 3000 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | Following a report by LU Staff of faulty electrical equipment within the Liverpool Street SOR, at around 5am on Thursday 6th 2014, it was discocovered that the neutral Link in the Isolator on the E30 Class A DB within switchroom E51 had not been reconnected prior to energisation. The link had been disconnected to carry out testing, but was not reconnected, in breach of __'s procedure.
| 02SL - Stations (LUL) | Cxxx-NCR-001212 | NCR | Asphalt to footpath in Broad Street avenue |  | Contr | VIN | LIS - Liverpool Street Station (Central) |  | 2014-07-31 | 2014-06-09 15:08 | -52 | 2014-03-07 11:28 | Civil - Wearing Course | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | At small sections of footpath asphalt along the rear of the kerb the surface lacks fines causing holes in the finish.
| 02SL - Stations (LUL) | Cxxx-NCR-001215 | NCR | Defective Installation of __s in Utilities Corridor |  | Contr | VIN | LIS - Liverpool Street Station (Central) |  | 2014-09-30 | 2014-07-17 14:44 | -75 | 2014-03-10 08:23 | Civil - Civil Engineering General | 0 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | We raise an NCR over the defective installation in term of verticality, alignment and overlapping of some __s along the south and north walls of the Utilities Corridor and more specifically between GL5 - GL9. This may have implications over the installation of the cantilever brackets. Photos attached.
| 02SL - Stations (LUL) | Cxxx-NCR-001216 | NCR | Utilities Corridor West - North Wall Duct Cast in sockets |  | Contr | VIN | LIS - Liverpool Street Station (Central) |  | 2014-06-30 | 2014-06-16 11:41 | -14 | 2014-03-11 10:59 | Civil - Utilities Engineering | 0 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | 12no Cast in Duct Sockets in the Northern Wall of the Utilities Corridor on the West between GL 0 - 1 have been installed to the incorrect size. The cast in sockets have an internal dimension of 106mm and the ducts to connect from externally into the sockets are 96mm external dimension.The sockets cast into the wall should have been 96mm instead of the 110mm sockets installed.
| 02SL - Stations (LUL) | Cxxx-NCR-001217 | NCR | Permeation Grouting |  | Contr | VIN | LIS - Liverpool Street Station (Central) |  | 2014-06-30 | 2014-05-09 08:07 | -52 | 2014-03-14 15:28 | Civil - Civil Engineering General | 20000 |  | Material | Repair | 2 (6-60k) | Complete | External Phenomenon - Not Defined | Completed |  | Permeation grouting was undertaken to improve the ground condition in the location of the proposed heading for the new 1400mm sewer. After the heading excavation started, it was identified that the ground was not improved by permeation grouting as the grout had not covered the area to be excavated.
| 02SL - Stations (LUL) | Cxxx-NCR-001218 | NCR | Water Seepage from Substation Base Slab expansion joint |  | Contr | VIN | LIS - Liverpool Street Station (Central) |  | 2014-09-30 | 2014-08-20 11:42 | -41 | 2014-03-21 15:21 | Structural Engineering - Joints | 3000 |  | System Defect | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Water is seeping from the joints in the mastic sealant to the expansion joint at the junction of the slab and the upstand.
| 02SL - Stations (LUL) | Cxxx-NCR-001219 | NCR | Pile E105 Final Level of Reinforcement |  | Contr | VIN | LIS - Liverpool Street Station (Central) |  | 2014-06-30 | 2014-04-29 17:18 | -62 | 2014-03-24 08:53 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Final level of reinforcement cage for pile E105 is 45mm lower than the tolerance allowed. Top level of cage is 113.405.
| 02SL - Stations (LUL) | Cxxx-NCR-001220 | NCR | Pile E103 No Concrete Cubes Taken |  | Contr | VIN | LIS - Liverpool Street Station (Central) |  | 2014-05-31 | 2014-04-29 17:08 | -32 | 2014-03-25 16:28 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | During the concreting of pile E103, __ operatives did not take a set of concrete cubes as required by the specification.
| 02SL - Stations (LUL) | Cxxx-NCR-001221 | NCR | Utilities Corridor GL9-10 Plinths |  | Contr | VIN | LIS - Liverpool Street Station (Central) |  | 2014-06-30 | 2014-04-07 00:23 | -84 | 2014-03-27 11:10 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Supervisor not available on jobsite | Completed |  | On the Utilities Corridor roof, 6no plinths starter bars between GL9 – GL10 have been cast in the wrong position. The starter bars are 150mm further north from their design location.
| 02SL - Stations (LUL) | Cxxx-NCR-001222 | NCR | External Dry Riser Cabinet - Installed @ Incorrect Height (GL 18) |  | Contr | VIN | LIS - Liverpool Street Station (Central) |  | 2014-11-30 | 2014-09-11 14:03 | -80 | 2014-05-02 11:36 | Architectural - Walls | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The external dry riser cabinet at GL18 was built into the yellow brick wall at the incorrect level (base of cabinet was 750mm above SSL), causing the connection point to be too high by 120mm relative to standards. As the cabinet had been built into the wall, the brickwork around it was broken out to release it (without damage to the cabinet). Due to this being undertaken on the day of substation sign-off (17/02/14), the cabinet had to be repositioned & connected up prior to the brickwork being repaired. The 50mm flange around the cabinet did not enable a tidy reconstruction of the wall around the cabinet (photo attached for reference)
| 02SL - Stations (LUL) | Cxxx-NCR-001224 | NCR | MSH2 100 |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2014-08-31 | 2014-07-14 15:13 | -48 | 2014-05-02 16:38 | Civil - Utilities Engineering | 0 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The high level connection for the backdrop in MHS2-100 was not installed according to the __'s manhole installation guide, which says the rodding pipe must be isnerted into cored holes in the walls of the Man hole.
| 02SL - Stations (LUL) | Cxxx-NCR-001225 | NCR | Manhole MHS2 Lower Reducer Slab Rebar |  | Contr | VIN | LIS - Liverpool Street Station (Central) |  | 2014-07-31 | 2014-06-10 11:41 | -51 | 2014-05-03 12:07 | Civil - Civil Engineering General | 0 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | The walls from the MHS2 base slab to the lower reducer slab have been cast approx. 600mm too high therefore the “L” bars (bar mark 61,50, 62,44, 40,46) cannot be installed on top of the lower reducer slab and tie to the walls.
| 02SL - Stations (LUL) | Cxxx-NCR-001226 | NCR | Level discrepency between existing floor and escalator barrel stairs platform |  | Contr | VIN | LIS - Liverpool Street Station (Central) |  | 2014-11-30 | 2014-09-16 16:25 | -75 | 2014-05-07 11:26 | Archaeology - General | 3000 |  | Planning | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As shown on the attached photographs a level difference of up to 60mm exists between the existing floor level in 4/237 and the new platform at the base of the disused escalator barrel stairs in 4/792.
| 02SL - Stations (LUL) | Cxxx-NCR-001229 | NCR | Mess Room Internal Render - Fixing Penetrations |  | Contr | VIN | LIS - Liverpool Street Station (Central) |  | 2014-09-30 | 2014-08-21 12:08 | -40 | 2014-06-20 17:31 | Architectural - Finishes | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A number of penetrations made in the __ waterproof render for installing surface mounted services & accessories, were not sealed with the specified __ Anchorfix-1 during installation. (Anchorfix-1 requirement advised by specialist __ installation contractor __, who installed the render).
| 02SL - Stations (LUL) | Cxxx-NCR-001230 | NCR | __ Duct Route |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2014-11-30 | 2014-11-03 14:25 | -27 | 2014-07-30 11:04 | Civil - Utilities Engineering | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | External Phenomenon - Other | Completed |  | The Contractor attempted to test the __ duct route on 8th July, by passing a mandrel through the ducts from chamber to chamber. The Contractor failed to pull the mandrel through all 4 of the __ ducts - see EWN 0900. From camera surveys, the __ duct route was found to have a large number of additional bends that are not in the Works Information or agreed via an RFI/FCD. These additional bends result in a build of friction on the rope that prevents the rope, brush and mandrel from being pulled through the ducts. At areas where the mandrell was getting stuck at the east and west of the Utility Corridor, two excavations were opened, exposing some of the additional bends which were subsequently cut out to form two temporary pits from which to re-attempt to mandrell the duct route in six separate sections as opposed to the two chamber to chamber sections originally attempted. The mandrelling of these six separate sections was completed on 24th July 2014 , however __/Crossrail voiced concerns over the remaining additional bends and that a fully representative chamber to chamber mandrel test was still not possible. __ stated that they would attempt the subducting of the system on 29th July. On 29th July the subducts could not be pulled into the duct route (see attached email from __ dated Wed 30/07/2014 11:01) due to the cumulative friction from the numerous additional bends installed within the duct route.
| 02SL - Stations (LUL) | Cxxx-NCR-001231 | NCR | Leak in the Utility Corridor GL1 to 3 |  | Contr | VIN | LIS - Liverpool Street Station (Central) |  | 2014-11-30 | 2014-11-12 15:51 | -18 | 2014-07-30 15:08 | Civil - Civil Engineering General | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | With refernce to EWN 00912 Following the completion of the waterproofing membrane on top of Utility Corridor GL1 to 3, the water ingress on GL1 and GL3 has not stop (refer to attachment). We therefore did investigated the integrity of the waterproofing membrane on top of the roof slab.
| 02SL - Stations (LUL) | Cxxx-NCR-001232 | NCR | Installation of electrical services within the utilities corridor, East and West walls, not as per approved drawings |  | Contr | TWC | LIS - Liverpool Street Station (Central) |  | 2014-11-30 | 2014-09-25 14:47 | -66 | 2014-08-04 11:16 | Electrical - Electrical Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Installation of the electrical services including containment, cable tray, distribution boards (DBA and D__), 110v distribution board c/w integral TX, electric meters, 100 amp TP&N supply and Fan Control Panels to the East and West walls of the utilities corridor has not been completed as per the approved drawings Cxxx-VIN-DDE-C101-Z_00421 and Cxxx-VIN-DDE-C101-Z_00422. In particular, the new arrangement on the West wall has raised concerns due to the height in which the 110v distribution board c/w integral TX has been fixed, creating the potential risk of water damage.
| 02SL - Stations (LUL) | Cxxx-NCR-001233 | NCR | Installation of 2no security doors to AP Power substation |  | Contr | VIN | LIS - Liverpool Street Station (Central) |  | 2014-11-30 | 2014-10-03 15:02 | -58 | 2014-08-04 13:38 | Architectural - Doors | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the installation of replacement doors DR13 and DR15 in the new AP Power substation on the night of Friday 1st August, a number of non-conformances were identified. These include: - the fixings for the door closer to DR13 broke during installation and no spares were available. These are being brought to site to replace and the door closer will be installed at the earliest opportunity. - the final fire stopping was not able to be installed as the approved firs stopping installer was not available for that shift. However, rock wool was installed as a temporary measure, although there was not sufficient material to complete the stopping around door DR15. The mastic is due to be completed on Monday 4th August for both doors. - the door contact for DR15 was not able to be reconnected but will be done on Monday 4th August.
| 02SL - Stations (LUL) | Cxxx-NCR-001234 | NCR | Waterproofing |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2014-12-15 | 2014-11-14 13:46 | -31 | 2014-08-26 16:59 | Architectural - General | 1000 |  | System Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Further to NCR 1175 and RFI 1238 the water seal around the cables running through the patio area Located between GL 17 & 18 failed (Existing Seal pic attached). This lead to water ingress in the substation as shown in the attached photos
| 02SL - Stations (LUL) | Cxxx-NCR-001235 | NCR | Concrete cube results (utilities corridor) |  | Contr | VIN | LIS - Liverpool Street Station (Central) |  | 2014-09-16 | 2014-09-18 15:12 | 2 | 2014-09-02 14:13 | Civil - Civil Engineering General | 0 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | After checking out the ITP records for the RC Utilities Corridor package, __ Quality Department noticed that one of the cube test results was not reaching the specification strength of 45 N/mm2 after 56 days. The strength obtained was 44.3 N/mm2. The mentioned results belong to the pour for the base slab between GL0-GL01.
| 02SL - Stations (LUL) | Cxxx-NCR-001236 | NCR | Incorrect revision number used on as-builts |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2015-03-31 | 2015-04-15 12:00 | 15 | 2014-09-09 13:45 | Electrical - Electrical Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | During review of the HV Package Listing it has been noted that revision 'Zx' has been used for as-built status, which was the requirement in the original Works Information, however this requirement was superseded by PMI 177, which states in Part 13.3.6.3: '...the contractor shall electronically re-draft at Revision C (Contractual) and Status Code at AB (As-Built)...'
| 02SL - Stations (LUL) | Cxxx-NCR-001237 | NCR | Substation Fan - Mezz level |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2014-11-28 | 2014-11-14 15:05 | -14 | 2014-09-12 10:06 | Mechanical - Heating Ventilation & Air Conditioning | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The fan that has been installed within the sub station at the mezzanine level is non complaint with the works information. The fan does not match the fan that was detailed as part of the accepted design, refer to drawing Cxxx-VIN-E-XPA-C101-50001.
| 02SL - Stations (LUL) | Cxxx-NCR-001238 | NCR | Defective Screed in Upper Switch room area |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2014-10-27 | 2014-10-27 14:30 | 0 | 2014-09-15 14:23 | Architectural - Flooring | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A protion of the screed applied to the Area between the South wall of the upper switchrooms and the retaining wall was applied incorrectly leading to a defective screed as shown in the attached photo.
| 02SL - Stations (LUL) | Cxxx-NCR-001239 | NCR | Incorrect OTX Cladding support fixings used |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2014-10-27 | 2014-10-21 10:13 | -6 | 2014-09-15 17:43 | Architectural - Ceilings & Soffits | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Normal washers were used instead of Spring washers to fix the OTX cladding support
| 02SL - Stations (LUL) | Cxxx-NCR-001241 | NCR | Multi-Pro Board Used Instead of __ |  | Contr | VIN | LIS - Liverpool Street Station (Central) |  | 2014-11-03 | 2014-10-24 15:37 | -10 | 2014-09-17 10:39 | Architectural - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other management problem | Completed |  | During an inspection of the works on 11th September 2014 it became apparent that __ and __ had substituted the agreed __ backing board for the VE works with a different product. It has now been confirmed that the product used is Resistant Multi-Pro board, __ provided a __ report (attached) to confirm that the board has been tested and is rated as A1. The Crossrail Fire Engineer (__) has confirmed that the materials is suitable for use as a backing material (see attached email)
| 02SL - Stations (LUL) | Cxxx-NCR-001242 | NCR | Inseption Request Forms for the OTX Cladding works |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2014-11-04 | 2014-10-29 22:53 | -6 | 2014-09-23 19:20 | Architectural - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | CRL did not receive any Inspection Request Form for the works associated with the installation of Secondary Steelwork first fix (item 4.04 in ITP Cxxx-VIN-C-ITP-C101-50066).
| 02SL - Stations (LUL) | Cxxx-NCR-001243 | NCR | Utilities Corridor - Cable Anchors |  | Contr | TWC | LIS - Liverpool Street Station (Central) |  | 2014-12-15 | 2014-11-11 17:09 | -34 | 2014-09-25 11:40 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | The 7No. steel plates detailed on Cxxx-MMD-U-DDL-C101_Z-89067 were incorrectly installed without the 20mm threaded core hole in the centre. As a result, the Haklift Grade 8 screw lifting eye (or equivalent) cannot be fixed into place for future works.
| 02SL - Stations (LUL) | Cxxx-NCR-001244 | NCR | Abandonment of 200mm Water Main |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2014-11-30 | 2014-11-13 20:37 | -17 | 2014-10-14 10:13 | Civil - Utilities Engineering | 3000 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Cxxx have not completed the abandonment of the 200mm water main in accordance with TWUL procedures or the Works Information. The 200mm is currently dead, but still physically connected to a shut valve in the junction of Old Broad Street and Liverpool Street. In accordance with __ Best Operating Practice AM-PRO-WN&T-WN45-SEC1 - As soon as practicable after ceasing to be service structures, abandoned mains should be completely physically separated from any pipework remaining in use. Cxxx-MMD-U-DDA-C101-50011 and the Works Information clearly identify the 200mm main as to be fully abandoned by the Contractor. The 200mm main ceased to be a service structure in May 2014 , however, the incomplete abandonment was identified by Crossrail on 17th September 2014 and again via EWN-940. In accordance with Volume 2B this constitutes a defect - "Where a specified work activity has not been carried out in accordance with agreed procedural requirements, a NCR is raised."
| 02SL - Stations (LUL) | Cxxx-NCR-001246 | NCR | UTS Room Concrete base slab cube testing |  | Contr | VIN | LIS - Liverpool Street Station (Central) |  | 2014-10-28 | 2014-10-23 15:15 | -5 | 2014-10-14 08:25 | Civil - Civil Engineering General | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient surveillance of subcontractors | Completed |  | The Inspection and Test Plan for the UTS Concrete base slab, Cxxx-VIN-C-ITP-C101-50013 Rev 2.0 requires concrete cubes to be taken and tested at 7 and 28 days. We are unable to provide these cube test results.
| 02SL - Stations (LUL) | Cxxx-NCR-001247 | NCR | VE Panel installation defect |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2014-11-16 | 2014-11-19 12:08 | 3 | 2014-10-17 10:47 | Archaeology - General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Inadequate/insufficient tooling. | Completed |  | Upon visual inspection of the VE Panels installed along the Switchrooms E51 E52 and E53 North Elevation it was observed that the VE fixings installed damaged the edges of some of the panels beyond repair as shown in attached pics
| 02SL - Stations (LUL) | Cxxx-NCR-001248 | NCR | noise levels of roof fans above requirement set out in Works Information |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2015-01-31 | 2015-02-06 14:55 | 6 | 2014-10-30 10:38 | Environmental - Noise and Vibration | 5000 |  | Testing and Commissioning | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | a requirement within the specification for mechanical systems Cxxx-MMD-M-RSP-C101-00003 is that 63dB @ 1m should be met, results from latest test state that 69-70dB was measured which does not meet the specification requirements.
| 02SL - Stations (LUL) | Cxxx-NCR-001250 | NCR | Illegible Mill Certificates |  | Contr | VIN | LIS - Liverpool Street Station (Central) |  | 2014-11-21 | 2014-11-10 19:40 | -11 | 2014-11-07 16:05 | Architectural - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Upon review it was discovered that 3No. Mill Certificates from the records document - Shaft and Tunnel - Architectural Metalwork Records (CRL Document Number: Cxxx-VIN-O4-LRC-C101-50077) were not legible. A request was made to the supplier (__) for clear copies of the documents but __ have been unable to deliver these. This is because the metal suppliers only hold the documents for 1-2 years (dependent on the quantity of material) and the Mill Certs in question had already been disposed of.
| 02SL - Stations (LUL) | Cxxx-NCR-001252 | NCR | OTX 2 Cladding Finishes |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2015-01-31 | 2014-12-19 15:48 | -43 | 2014-11-26 19:52 | Architectural - Ceilings & Soffits | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The OTX 2 Cladding finishes installed onsite were supposed to match OTX 1 Cladding (Asbuilts attached) however, upon closer observation onsite it was clear that the OTX2 Folded chanels (supporting the cladding panels) at the edges were of a different colour.
| 02SL - Stations (LUL) | Cxxx-NCR-001253 | NCR | 2/201 Corridor Ceiling |  | Contr | VIN | LIS - Liverpool Street Station (Central) |  | 2015-03-31 | 2015-04-16 09:23 | 16 | 2014-11-27 12:22 | Architectural - Ceilings & Soffits | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | An error has been made in original ceiling survey resulting in very small perimeter sections being used to fill-in the ceiling on the outer radius. The use of such small infill panels is not acceptable.
| 02SL - Stations (LUL) | Cxxx-NCR-001254 | NCR | Old Broad Street Sewer Lining |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2015-03-31 | 2015-02-27 09:39 | -32 | 2014-12-11 09:59 | Civil - Drainage | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | The CCTV report generated for the CIPP liner install from MHS2 to 30m downstream has highlighted a wormanship defect. At the junction with the Sun Street Passage (Chainage 59.8m on the CCTV survey) the liner has been cut out in such a way that it is causing debris to snag/accumulate within the junction. At Chainage 46.1m the liner has rippled sufficiently to provide a large intrusion in the soffit of the sewer, providing an increased risk of head injury in an already confined space.
| 02SL - Stations (LUL) | Cxxx-NCR-001255 | NCR | E series piles Pile E125 void |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2015-04-30 | 2015-03-25 15:09 | -36 | 2015-01-22 15:25 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the excavation for the northern capping beam of Broadgate Ticket Hall a void was found within pile E125 at a level of 112.6 to 111.9m. The void appears to have been created by the bore of the pile collapsing during the removalm of the casing. The top section of the pile has been concrete to the design level but the area where the void is positioned clashes with the design cut off level of 112.295 as per attached Cxxx pile schedule and overlay. The extent of the void appears to stop at a level of 111.900m but on visual inspection this cannot be confirmed. It appears that the final design cut off level id to retain the ground to the west of the entrance to the escalators only and is not incorperated within the lining walls or slabs.
| 02SL - Stations (LUL) | Cxxx-NCR-001258 | NCR | water ingress into utilities corridor lighting system |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2016-07-31 | 2016-11-14 11:07 | 106 | 2015-11-09 11:34 | Electrical - Electrical Engineering General | 10000 |  | System Defect | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | During regular inspection within the utilities corridor it was noted that a number of light fittings were not working, on further investigation it is clear that there is water within the IP55 adaptable boxes feeding the light fitting and also evidence of water within the light fittings.
| 02SL - Stations (LUL) | Cxxx-NCR-001259 | NCR | Utilities clash with corridor AP8 |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2016-06-30 | 2016-04-12 16:45 | -79 | 2016-01-20 09:46 | Utilities Engineering - Utilities General | 35000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | External Phenomenon - Other | Completed |  | During the excavation of the AP8 passageway currently being undertaken by Cxxx a number of utilities were discovered within the footprint of AP8 structure. As per attached photos of the excavated footprint of AP8 Cxxx have exposed the following Utilities 4no 100mm Cable and Wireless Communication Ducts 4no 100mm Virgin Media Communication Ducts 4no 150mm __ Rigid ducts. A detailed survey of the Utilities has been carried out by Cxxx and the results imposed on the 3D model of the AP8 structure outline as per below sections. The snapshots below clearly show the clash with the AP8 structure, the result of the clash will result in the possibility of either redesign of the AP8 structure , diversion of the assets to clear the footprint or both of the previous due to logistical restriction within the area.
| 02SL - Stations (LUL) | Cxxx-NCR-001260 | NCR | Water heater installation within LUL substation Liverpool street |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2016-05-31 | 2016-04-07 12:56 | -54 | 2016-02-18 09:42 | Mechanical - Hot & Cold Water Supplies | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 2 number water heaters installed with the new LUL substation at liverpool street have been installed incorrectly, this had resulted with one of the water heaters blowing a gasket and now needs replacing.
| 02SL - Stations (LUL) | Cxxx-NCR-001261 | NCR | Bus-bar cable burn-out within connection panel |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2016-09-30 | 2016-12-05 11:53 | 66 | 2016-04-21 12:54 | Electrical - Power Distribution | 50000 |  | Damaged | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Other | Completed |  | Report received from LU Works Controller, 21st April 5:22am: We were called out to an emergency last night at Liverpool St where the report was of an exposed 400V bus bar cable- plate has melted away. On investigation we found that it was part of a new Cross rail install that feeds a new switch room on the disused platform 3. The containment system that has been used is something that we have not seen before so would have no way of carrying out a temp fix. It looks like the cable has burnt out in one of the connection panels you can see in the photos. The supply is still live coming into the connection box but is no longer going away into the switch room. We have spoken to the SSE who is sending a couple of power link guys down there to see if they can find where to isolate it from and __ is still down there to lend assistance if needed. Further update at 5:34: The room is switch room E51 which Crossrail have built to replace E1 and it houses the SEPS supplies. It is fed from a bus- bar system and it is one of these connections that have burnt out. __ are on site now with the intention of isolating the burnt out supply. Also see attached photographs.
| 02SL - Stations (LUL) | Cxxx-NCR-000013-L | NCR | Review of __ Documentation |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2011-11-30 | 2012-04-02 13:01 | 124 | 2011-08-15 | Communications and Control Systems - General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | Failure to reply to __ Documents within the 14 day Period
| 02SL - Stations (LUL) | Cxxx-NCR-000037-L | NCR | Penetration of __ sewer during core drilling within the LU Hammersmith and City Line Tunnel |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-11-24 | 2012-09-03 11:06 | -82 | 2011-11-17 | Civil - Sewage/Water services | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | On the 06/11/11 at 9:00 am the __ S.P.i.C. contacted his supervisor to confirm the chainages (m) of the core sample locations. The chainages supplied for sample locations 7, 8, 9 and 10 (chainages 120, 125, 155 and 160m) by the __ supervisor, were used by the __ representative to locate the sample positions using track chainage markers for reference, as advised. The chainages supplied originated from the TL79 tunnel portal and not the track chainage markers. It was not bought to attention that there were multiple chainage references. The method statement supplied on site by __ was not the latest revision of the document and did not contain the required chainage information of the cores. As a result of the incorrect chainage the core sample at location 7 on the westbound side of the site possibly breached a thames water sewer asset at the other side of the tunnel lining. Preventive Measures Taken: Prior to any safety critical works, a pre-commencement/review meeting is required, with attendance from all parties involved in the work (sub-contractors, supervisors etc.), in order to ensure that the correct information is compiled, mutually understood and available throughout the works.
| 02SL - Stations (LUL) | Cxxx-NCR-000039-L | NCR | Cracked segment on ring no 2 |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-01-31 | 2012-07-30 12:11 | 181 | 2012-01-10 | Civil - Civil Engineering General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | An ordinary type segment no. 2BT158078 cracked down the middle of the plate during installation. The segment was part of the ring no 2 (where ring no 1 is build on the cutting edge).
| 02SL - Stations (LUL) | Cxxx-NCR-000042-L | NCR | Liverpool Street - Damages Segment on ring 6 |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-02-19 | 2012-07-30 12:33 | 162 | 2012-01-18 | Tunnelling - Tunnelling General | 500 |  | Damaged | Use As-Is |  | Complete |  | Completed |  | Following the installation of the segments, it was noted that there was damage to a segment in ring 6. Inspection were carried out as per the ITP (item 9.1). The cause of this defect is unknown. This may have been damaged during the installation of grout lines / ventilation.
| 02SL - Stations (LUL) | Cxxx-NCR-000043-L | NCR | Excavation of Shaft under Archaelogical Watching Brief |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-01-15 | 2012-02-19 15:18 | 35 | 2011-11-28 | Environmental - Archaeology | 500 |  | Damaged | Use As-Is |  | Complete |  | Completed |  | The excavator driver continued to level the ground at the pit bottom, when requested to stop by the attending Archaeologist who was at the top of the shaft. This resulted in possible disturbance to wat was later identified as potentially Holocene Paleochannel. The driver halted works when requested to do so by the site engineer, following communication from the site Agent.
| 02SL - Stations (LUL) | Cxxx-NCR-000044-L | NCR | Liverpool Street - Bags of grout utilised for shaft back grouting not as specified in Work Method Statement |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-05-15 | 2012-04-23 09:56 | -22 | 2011-12-02 | Tunnelling - Grouting | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | The shaft back grouting was undertaken utilising a combination of dry, bagged cement products including OPC, G10 and G20. The G20 grout has a specified 28 day strength of 1.5N/mm2. No evidence of cubes being taken in grouting records.
| 02SL - Stations (LUL) | Cxxx-NCR-000045-L | NCR | Liverpool Street - Borehole drilling for an extensonmeter that damaged a basement |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-03-29 | 2013-03-13 09:16 | -16 | 2011-12-02 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | Whilst digging the trial pit, __ found a layer of bitumen which they thought to be an old road and hence, carried on digging the pit. Below this bitumen layer two courses of brick were found which make up the cellar roof. The extent of the cellar in question is not on the drawings there is a sketch which shows the approx position on a pdf. Root cause : As built information not up to date
| 02SL - Stations (LUL) | Cxxx-NCR-000046-L | NCR | Liverpool Street - Borehole Drilling for an inclinometer Damaging an extensometer sensor |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2011-01-15 | 2012-05-31 20:31 | 502 | 2011-12-02 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Damaged | Rework |  | Complete |  | Completed |  | When drilling Borehole Cxxx-IM10505 at depth of 30m the drill hit an obstruction. The obstruction was the extensometer Cxxx-XR10505. The holes had combined. Both boreholes have been abandoned and new positions for both boreholes are set out.
| 02SL - Stations (LUL) | Cxxx-NCR-000047-L | NCR | Liverpool Street - Access Shaft - Bentonite testing for shaft jacking |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-01-20 | 2012-05-31 10:31 | 132 | 2011-12-05 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The bentonite was in use between the 10/11/2011 - 25/11/2011. Testing requirement as per listed ITP was not carried out.
| 02SL - Stations (LUL) | Cxxx-NCR-000048-L | NCR | Cutting of 24mm Diameter Bosworth Bolts used in Ring Plates |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-02-19 | 2012-05-25 11:05 | 96 | 2012-01-18 | Tunnelling - Tunnelling General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | The bolt should finish flush with the top ring to prevent interference with the following segment. In the case of approximately 1/3 of the bolts, the top of the bolt needed to be trimmed by a maximum of a 40mm as tehy were too long. Bolt holes were thoroughly cleaned out before the next ring is placed, and the bolts were greased. This still resulted in the cutting of the protruding bolts.
| 02SL - Stations (LUL) | Cxxx-NCR-000050-L | NCR | Flow test too high for shotcrete sprayed in section 4/4 at LIV AS 1 excavation from (102.6 to 101.4) |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-09-29 | 2012-08-20 17:16 | -40 | 2012-01-10 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Approx 2m3 of shotcrete used to spray shaft advance had flow 690/700mm, exceeding ITP specification. When recognise, the shotcrete mix was adjusted appropriately. Root cause: Problems with CPI silos dosing system generates intermittent fluctuations in the workability of the mix.
| 02SL - Stations (LUL) | Cxxx-NCR-000052-L | NCR | Sprayed Concrete applied with fibres when RESS stated No fibres |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-06-29 | 2012-04-23 10:21 | -67 | 2012-01-09 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | First 100mm Layer of Primary Lining, area annotated on attached drawing. Sprayed concrete was applied with fibres, Mix P1 when RESS stated No Fibre mix used, Mix P2.
| 02SL - Stations (LUL) | Cxxx-NCR-000053-L | NCR | Incorrect dig level reached for advance with proposed dig level of 99.0mAOD |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-01-15 | 2012-09-06 11:47 | 235 | 2012-01-10 | Tunnelling - Excavation - Hand | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The excavation of the first half of the advance with a proposed finished level of 99.0mAOD was exceeded. This level is governed by RESS sheet AS1/07, and was exceeded by 0.7m. As a result an average dig level of 98.3m was reached. This RESS was part of the daily briefing to the crew.
| 02SL - Stations (LUL) | Cxxx-NCR-000055-L | NCR | Misplaced reinforcement at first stage of Thickening execution |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-02-29 | 2012-05-25 11:01 | 86 | 2012-01-20 | Tunnelling - Tunnelling General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | 2 No. Vertical bar couplers were misplaced in the initial stage resulting in 2 No. Bars requiring to be placed inside the eye. These bars were removed upon consultation with the designers. Reinforcement not held securely during first stage spraying operation
| 02SL - Stations (LUL) | Cxxx-NCR-000056-L | NCR | Low flow test results out of specification 6 GAD1 |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-09-05 | 2012-09-06 16:04 | 1 | 2012-02-06 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Flow test were carried out on advance 6 for GAD 1 on the 21/01/2012. 5 of the 7 flow test results done were <530mm and 1 of the test result was > 660mm. Initial Lining Test: Low results 480mm, 515mm and high result 680mm. Primary Lining Test: Low results: 495mm, 510mm, 520mm. Root cause : Control of water for concrete production batch from CPI silos can be difficult to adjust. With regard to high results, engineer should allow for dry aggregates to absorb the water. Engineers have not been briefed sufficiently on this issue.
| 02SL - Stations (LUL) | Cxxx-NCR-000057-L | NCR | 75mm sealing layer not sprayed to full depth on advance 3 GAD1 |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-03-16 | 2012-09-06 15:34 | 174 | 2012-02-06 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Face was not sprayed with 75mm of SCL. The beamer system was not working with blue tooth transmission issue. Pins could not be installed in face as it had not been sprayed. Gang sprayed face but in places only 10mm/20mm had been applied. Root cause : Beamer system was not working; thickness was being controlled by pins for primary lining. Pins cannot be installed until initial layer is sprayed.
| 02SL - Stations (LUL) | Cxxx-NCR-000058-L | NCR | Temporary invert in advance 2 and 3 GAD1 not sprayed. |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-03-16 | 2012-09-06 16:12 | 174 | 2012-02-06 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | Temporary invert was not sprayed with 75mm of SCL. Root cause: Confusion of requirement by gangs. Miss-understanding of RESS sheet. Failure to question when unsure.
| 02SL - Stations (LUL) | Cxxx-NCR-000059-L | NCR | Over dig on advance 6 GAD1 |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-08-30 | 2012-09-07 11:26 | 8 | 2012-02-06 | Tunnelling - Tunnelling General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Advance 6 was over excavated by 200mm in the top of the face and 550mm in the bottom. Over excavated by 575mm in the crown and right shoulder, 500mm in the knee position. Root cause : Miss communication between engineer and machine driver on advance length. Profile over dig on knee as beamer could not see in to knee position.
| 02SL - Stations (LUL) | Cxxx-NCR-000060-L | NCR | Out of excavation sequence advance 4 GAD1 |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-09-27 | 2012-09-07 11:41 | -20 | 2012-02-06 | Tunnelling - Tunnelling General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Excavation sequence not followed RESS GAD1/03 advance 5 was started before temporary bench was removed. One bucket load was taken from the face. Root cause: Once excavation and spraying had been completed, the gang were confused which advance they were on. The depth to the face did not appear to reflect what was on the RESS.
| 02SL - Stations (LUL) | Cxxx-NCR-000061-L | NCR | SCL Monitoring array installed in incorrect advance (GAD2) |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-03-20 | 2012-08-20 10:19 | 153 | 2012-02-20 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Monitoring array was scheduled to be installed in Advance 26. Because of availability of surveyor it was decided to install in Adv 27. We are allowed to install +/- one advance as defined in the RESS. After completing Adv 27, thearray was installed in Adv 26. This was incorrect, resulting in loss of approximately 6hrs of convergence data. Root Cause: Importance and relevance of monitoring array location was not understood fully by the site team
| 02SL - Stations (LUL) | Cxxx-NCR-000065-L | NCR | Incomplete SCL Profile sheets for GAD1 |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-03-18 | 2012-09-06 16:33 | 172 | 2012-02-01 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Incomplete SCL profile sheets as per ITP : Cxxx-__M-C4-ITP-CR092-50001 Rev 4 found in surveillance of profile sheets over Advances 1 to 45, GAD 1. Root cause : Engineering & operative learning curve.
| 02SL - Stations (LUL) | Cxxx-NCR-000066-L | NCR | Profile report submitted showing an overall lining thickness of less than 250mm |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-12-21 | 2012-10-15 18:00 | -67 | 2012-02-01 | Tunnelling - Linings - Sprayed Concrete | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | Activity :Mining and Spraying SCL Advance #33 A profile report was produced for advance number 33 that showed the lining thickness as less than 250mmin several places. After proof drilling we noted that only one area gave a thickness result of < 250mm (central invert = 240mm) Root cause: Incorrect data used for the advance profile report. First of all, the engineer on shift was queried as to the results. He stated that the tunnel Beamer guidance system had lost orientation during the mining cycle and was reading incorrect figures. He reoriented the Beamer and continued on with the mining cycle. Unfortunately when the data was processed, all points were stored and reproduced including those from when the machine was out of orientation.
| 02SL - Stations (LUL) | Cxxx-NCR-000067-L | NCR | P1 Mix Flow Test Outside Tolerance |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-09-12 | 2012-08-13 08:14 | -30 | 2012-02-06 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | One of the initial lining flow result 10mm below tolerance - 520mm. one of the primary lining flow results 20mm above tolerance 680mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000068-L | NCR | Shotcrete Temperature Below Tolerance |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-09-24 | 2012-08-20 17:51 | -35 | 2012-02-06 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | During grout adit construction adv 53 the Workability of mix test recorded temperature 10.5C Root Cause: low ambient air temperature
| 02SL - Stations (LUL) | Cxxx-NCR-000069-L | NCR | Incorrect profile to invert of advance 2 GAD 2 East |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-09-30 | 2012-08-09 10:28 | -52 | 2012-02-14 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The invert of advance 2 was constructed flat accross. Root cause: Operator was not given correct instruction or failed to follow instruction from Shift Engineer.
| 02SL - Stations (LUL) | Cxxx-NCR-000071-L | NCR | Profile report submitted showing an overall lining thickness of less than 250mm |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-12-21 | 2012-10-15 18:11 | -67 | 2012-02-20 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Profile reports from Adv 27 & 28 indicate a couple of areas where the overall lining thickness was less than 250mm and some areas where the profile was tight and within the design intrados. Root Cause: - Localised thin area of shotcrete, poor workmanship in setting out the primary lining profile. - First shift of new operator, still familiarising himself with spraying machine and beamer technique.
| 02SL - Stations (LUL) | Cxxx-NCR-000073-L | NCR | Core taken inidcating an overall lining thickness of less than 250mm |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-12-14 | 2012-10-15 18:07 | -60 | 2012-02-20 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | A set of core was taken from Adv 17 for strength testing purposes. One of those cores taken indicated an overal lining thickness of less than 250mm (Actual 200mm). The profile report from the tunnel beamer indicated all thickness were above 250mm. Root Cause: Localised thin area of shotcrete, poor workmanship in excavation profile
| 02SL - Stations (LUL) | Cxxx-NCR-000074-L | NCR | Profile reports submitted showing an overall lining thickness of less than 250 mm |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-12-14 | 2012-10-15 18:16 | -60 | 2012-02-21 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Profile reports of Adv 36, 38 & 40 indicate a couple of areas where the overall lining thickness was less than 250 mm. Root Cause: Localised thin area of shotcrete, poor workmanship in setting out the excavation profile and/or the primary lining profile
| 02SL - Stations (LUL) | Cxxx-NCR-000075-L | NCR | Out of Tolerance P1 Flow Test Result |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-09-29 | 2012-08-16 16:22 | -44 | 2012-02-21 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | During construction of grout adit 1 adv 50 Flow test record between 690-700. Root Cause: Dry Silo fluctuation in consistency / workability.
| 02SL - Stations (LUL) | Cxxx-NCR-000076-L | NCR | P1 Mix Flow Test Outside Tolerance (GAD 2 Adv 27) |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-10-12 | 2012-08-20 17:31 | -53 | 2012-02-21 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Flow test for initial lining GAD 2 Adv 27 was above required tolerance: Flow value 700mm. Root Cause: Water fluctuation on CPI silo causes inconsitency in the mix.
| 02SL - Stations (LUL) | Cxxx-NCR-000077-L | NCR | CRL sign off of ITP hold, witness and inspection points |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-03-30 | 2012-04-30 11:50 | 31 | 2012-02-22 | Tunnelling - Tunnelling General | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | Due to the works being carried out 24/7 and the current level of CRL staff coverage on site does not mirror this (i.e. CRL staff 7 days a week only, no nightshift cover) several hold and witness points can not be attended to nor signed off by CRL staff. This leaves records unsigned with no wrong doing of the contractor.
| 02SL - Stations (LUL) | Cxxx-NCR-000078-W | NCR | Swanlea School Mini Piles – Pile P05 |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2011-06-20 | 2012-02-19 16:12 | 244 | 2011-06-17 | Civil - Civil Engineering General | 500 |  | Material | Repair |  | Complete |  | Completed |  | The 12 hour time period for the construction of piles as stated in the ICE Specification for Piling and Retaining Walls (2007) was exceeded in the construction of Pile POS.
| 02SL - Stations (LUL) | Cxxx-NCR-000079-W | NCR | Swanlea School Mini Piles – Pile P06 |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2011-06-20 | 2012-02-19 16:10 | 244 | 2011-06-17 | Civil - Civil Engineering General | 500 |  | Material | Repair |  | Complete |  | Completed |  | The 12 hour time period for the construction of piles as stated in the ICE Specification for Piling and Embedded Retaining Walls (2007) was exceeded in the construction of Pile P06.
| 02SL - Stations (LUL) | Cxxx-NCR-000080-W | NCR | Welds to the steel cutting edge for the Whitechapel Grout Shaft |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2011-06-20 | 2012-03-11 18:10 | 265 | 2011-06-17 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | The ITP called for a visual inspection to be carried out on the site welds to ensure conformity with the DWG UnPS-CFT-WCH-GS1-D0004. The site welds were to have convex, totally filled profiles. Many did not have a convex shape and most areas showed poor visual quality with under filled profiles. Ref: Report By Mr Nicholas Cook, 26/05/11. Upon inspection and subsequent non conformance of the site welds, further investigation was carried out on the fabrication shop welding which was also found to differ from the design. Where 20mm butt welds were specified along the top edge of the horizontal flange, 12mm fillet welds were present. It was possible that these could have been reinforcing an underlying butt weld but there was certainly no evidence to show that 20mm butt weld was present. Where 20mm fillet welds were specified along the underside of the horizontal flange, unequal and insufficient leg length fillet welds were present. . Ref: Report By Mr Nicholas Cook, 26/05/11.
| 02SL - Stations (LUL) | Cxxx-NCR-000091-L | NCR | Records of temperature with flow test absent |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-06-21 | 2012-08-20 17:44 | 60 | 2012-05-16 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Thermometer not present at time of testing and so temperature not recorded as required in the ITP
| 02SL - Stations (LUL) | Cxxx-NCR-000092-L | NCR | Underbreak at Excavation Profile at Adv 14(from level 89.3 to 88.1), South East |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-07-26 | 2012-09-27 08:16 | 63 | 2012-05-03 | Shafts -Sprayed Concrete | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | Proof drilling done before spraying Primary Lining 2nd layer showing locally a surface smaller than 2m2 where the thickness (initial layer + primary 1st layer) has been measured 200mm (against min 275mm)
| 02SL - Stations (LUL) | Cxxx-NCR-000093-L | NCR | Primary 2 lining thickness of Advance 13 AS1 |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-09-03 | 2012-08-01 20:05 | -33 | 2012-05-30 | Shafts -Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | In a number of sections, the P2 layer is less than 125mm thick. Observed by __ Staff and CRL Inspectors. Root Cause Analysis: Control of the primary 1 spray was not adequately checked to ensure total layer thickness.
| 02SL - Stations (LUL) | Cxxx-NCR-000094-L | NCR | Final sprayed concrete profile at Adv 14 (From level 89.776 to 88.7), circumferential. |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-07-25 | 2012-09-27 08:27 | 64 | 2012-05-03 | Shafts -Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Setting into shaft profile radial bar for the primary lining 2ng layer and overspraying when spraying, therefore generating underbreaks.
| 02SL - Stations (LUL) | Cxxx-NCR-000095-L | NCR | Excavation not in accordance to process outlined in the RESS |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-07-25 | 2012-05-31 11:35 | -55 | 2012-05-03 | Shafts -Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The last quarter was excavated in a manor deviated from that outlined in the RESS. The final quarter was excavated in thirds working anti-clockwise, from east to west instead of west to east (As specified in the RESS).
| 02SL - Stations (LUL) | Cxxx-NCR-000098-W | NCR | Whitechapel Grout Shaft - Out of Plumbness |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2011-08-15 | 2011-08-24 14:37 | 9 | 2011-08-05 | Civil - Tunnelling | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | The grout shaft construction (caisson method) has been completed, the final checks on the shaft show that the shaft is out of plumb.The out of plumb exceeds the requirements set out in the Specification for Tunnelling Works.Plumb checks had been carried out during the sinking process. Whilst this operation was ongoing an uncharted well was found within the shaft. All personal were stopped from entering the shaft base until the extent of the opening/well was ascertained; this meant that 4 rings had been jacked without the plumb readings being taken. By this time the out of plumb was difficult to bring back as we only had 3 rings left to jack.
| 02SL - Stations (LUL) | Cxxx-NCR-000101-L | NCR | Partial shotcrete thickness issue at base shaft AS1 |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-08-22 | 2012-08-16 16:18 | -6 | 2012-05-15 | Shafts -Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Area of shaft base, left of the staircase, where the shotcrete thickness surveyed only 260mm
| 02SL - Stations (LUL) | Cxxx-NCR-000102-L | NCR | Post office tunnel No Monitoring Data Received daily as required |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-11-09 | 2012-09-14 09:59 | -56 | 2012-09-10 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | Delays in installing, commissioning, and providing an automated monitoring system within the Post Office Tunnel to provide consistant daily automated monitoring measurements. Root cause: Installation problems occured due to not recognising the lack of telephone network coverage at the top of the Post Office Tunnel access shaft which lead to delays in arranging for a permanent telephone line to be installed within the tunnel.
| 02SL - Stations (LUL) | Cxxx-NCR-000102-W | NCR | Failed notification of Amber Trigger Level |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2011-07-25 | 2011-12-22 19:12 | 150 | 2011-08-11 | Civil - Tunnelling | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | History: 2 readings done per day and a daily review. Tuesday review 26/07/2011: OKWednesday review 27/07/2011 @ 13:00: Tendency of heave of building (Possible rainy season)Thursday review 28/07/2011: First reading @ 17:00 above amber trigger value, SRG-RES Meeting carried out with Senior SCL Engineer, TW Coordinator and Deputy Monitoring Eng. (See Minutes of Meeting), Second reading @18:00 stabilized. __ team did not informed CRL Project Manager immediately.Friday review 29/07/2011 @ 16:40: Reading stabilized and information issued to CRL via email from __ on 29/07/2011 @ 17:45 to detail situation of 28/07 and 29/07.
| 02SL - Stations (LUL) | Cxxx-NCR-000103-L | NCR | Probehole: No monitoring probehole (05 April 2012) |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-01-10 | 2012-10-15 18:22 | -87 | 2012-10-05 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Within the cross section of Access Shaft AS1 at LIV four vertical probeholes have been drilled 10 m below the final excavation level of the shaft and standpipes have been installed. Probehole numbers are 5, 6, 7, and 8. Drilling time was 01.04. and 02.04.2012. The following two days, 03.04. and 04.04.2012, no measurement could be taken because the probe was not on site at Finsbury Circus. Measurements of groundwater were taken form 05. April 2012 to 13. April 2012. The results of these readings were sufficient to finally design the required excavation and support of AS1. Root cause : Delay of monitoring due to probe not available on site.
| 02SL - Stations (LUL) | Cxxx-NCR-000103-W | NCR | Whitechapel - Incorrect excavation for batching plant slab |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2011-08-16 | 2011-10-06 12:51 | 51 | 2011-08-15 | Civil - Civil Engineering General | 500 |  |  | Rework |  | Complete |  | Completed |  | Excavation was blinded before it was noted it was too small.
| 02SL - Stations (LUL) | Cxxx-NCR-000104-L | NCR | Loss of data during TAM Drilling |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-08-29 | 2012-05-31 20:45 | -90 | 2012-05-15 | Geotechnical Engineering - Compensation Grouting | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | During drilling of boreholes GAD1S05, GAD1S11, GAD1S15, GAD1S17 drilling parameters have been displayed on __ screen mounted on the rig, but they haven’t been properly recorded in the memory of the computer. Incomplete drilling records have been delivered at SRG meeting.
| 02SL - Stations (LUL) | Cxxx-NCR-000104-W | NCR | Whitechapel - Batching plant temporary works started without accepted ITP |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2011-08-16 | 2011-10-06 13:04 | 51 | 2011-08-15 | Civil - Civil Engineering General | 500 |  | System Defect | Rework |  | Complete |  | Completed |  | Batching Plant Temporary works have started (Excavation and Blinding Concrete) without an accepted ITP, which is not conformed to Contract Clause. Comments on ITP relate to the Concrete works.
| 02SL - Stations (LUL) | Cxxx-NCR-000105-L | NCR | TAM positions outside specified tolerance |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-04-26 | 2013-02-07 14:54 | -78 | 2013-01-23 | Geotechnical Engineering - Compensation Grouting | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The following boreholes were surveyed using a Maxibor and were found to be outside the agreed tolerances: Geotechnical Adit 1 S09 was outside the tolerance envelope on plan. S12 was outside the tolerance envelope on plan. N03 was outside the tolerance envelope on plan. N05 was outside the tolerance envelope on plan. N07 was outside the tolerance envelope on plan. N09 was outside the tolerance envelope on plan. N10 was outside the tolerance envelope on plan. N15 was outside the tolerance envelope on plan. N16 was outside the tolerance envelope on plan. N19 was outside the tolerance envelope on plan. N20 was outside the tolerance envelope on plan. CH01 was outside the tolerance envelope on plan and in elevation. CH03 was outside the tolerance envelope on plan. CH08 was outside the tolerance envelope on plan. CH09 was outside the tolerance envelope in elevation. CH11 was outside the tolerance envelope on plan. CH12 was outside the tolerance envelope in elevation. CH13 was outside the tolerance envelope in elevation. CH15 was outside the tolerance envelope on plan and in elevation. CH16 was outside the tolerance envelope on plan. CH18 was outside the tolerance envelope on plan. CH21 was outside the tolerance envelope in elevation. 1.90m of TAM inside the Northern Line Grouting Exclusion Zone (see LIS-CRL-NCR-Cxxx-00163). CH22 was outside the tolerance envelope on plan. CH23 was outside the tolerance envelope on plan. CH25 was outside the tolerance envelope in elevation. CH27 was outside the tolerance envelope on plan. CH29 was outside the tolerance envelope in elevation. 0.91m of TAM inside the Northern Line Grouting Exclusion Zone (see LIS-CRL-NCR-Cxxx-00154). CH31 was outside the tolerance envelope on plan. CH32 was outside the tolerance envelope on plan and in elevation. CH36 was outside the tolerance envelope on plan. CH37 was outside the tolerance envelope in elevation. 15m of TAM inside the Northern Line Grouting Exclusion Zone (See LIS-CRL-NCR-Cxxx-00183). CH38, CH39 and CH40, see LIS-CRL-NCR-Cxxx-00207. CH38r, CH39r and CH40r, see LIS-CRL-NCR-Cxxx-00218. CH43 was outside the tolerance envelope in elevation. CH44 was outside the tolerance envelope on plan. CH45 was outside the tolerance envelope on plan. CH49 was overdrilled 3.0m longer than design length. See LIS-CRL-NCR-Cxxx-00184. CH51 was outside the tolerance envelope in elevation. CH53 was outside the tolerance envelope on plan. CH54 was outside the tolerance envelope in elevation. CH58 was outside the tolerance envelope on plan. CH59 was outside the tolerance envelope on plan. CH60 was outside the tolerance envelope on plan. CH65 was outside the tolerance envelope on plan and in elevation. Geotechnical Adit 2 S01 was outside the tolerance envelope on plan. S02 was outside the tolerance envelope on plan. S07 was outside the tolerance envelope in elevation. S09 was outside the tolerance envelope in elevation. S12 was outside the tolerance envelope on plan. N09 was outside the tolerance envelope in elevation. N10 was outside the tolerance envelope in elevation. N13 was outside the tolerance envelope on plan. N17 was outside the tolerance envelope in elevation. N22 was outside the tolerance envelope on plan. CH04 was outside the tolerance envelope in elevation. CH05 was short of design length by 9m due to obstruction. CH15 was outside the tolerance envelope on plan. CH22 was outside the tolerance envelope in elevation. CH27 was outside the tolerance envelope on plan. CH29 was outside the tolerance envelope on plan. CH35 was outside the tolerance envelope in elevation. CH49 was outside the tolerance envelope on plan. CH64 was outside the tolerance envelope on plan. CH66 was outside the tolerance envelope in elevation. CH67 was outside the tolerance envelope on plan. CH68 was outside the tolerance envelope on plan. CH69 was outside the tolerance envelope on plan and in elevation. Root cause : Drilling accuracy was not within specification possibly due to workmanship but a definitive root cause cannot be positively determined.
| 02SL - Stations (LUL) | Cxxx-NCR-000105-W | NCR | Swanlea School Mini Piles – Integrity Testing |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2011-09-02 | 2012-02-19 16:14 | 170 | 2011-08-18 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | Specification clause KP10.2201 states that “integrity testing shall be carried out between 7 days and 21 days after piles have been cast”. Piles have not been tested in accordance with the above. Piles cannot be tested until they are adequately broken down to cut-off level.Programme of pile cap construction prohibits the piles to be tested between 7 days and 21 days after being cast.
| 02SL - Stations (LUL) | Cxxx-NCR-000106-W | NCR | Swanlea School Mini Piles - Verticality |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2011-09-02 | 2011-10-06 12:59 | 34 | 2011-08-18 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | Specification clause KP10.3210(c) states that “the maximum permitted deviation of the finished concrete pile from the vertical is 1 in 100”. Pile verticality measured as 1 in 70. Pile casing installed vertical through the void between drilling platform and the existing strata approximately 3m below the level of the drilling platform. During the drilling of the pile the casing moved out of vertical.
| 02SL - Stations (LUL) | Cxxx-NCR-000107-L | NCR | Fluid flow not recorded properly during TAM Drilling |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-08-31 | 2012-08-01 20:11 | -30 | 2012-05-24 | Geotechnical Engineering - Compensation Grouting | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | During drilling of boreholes GAD2S02, GAD2S06, GAD2S01 (up to 32m) the flow rate has not been recorded properly in the __ computer mounted on the rig. Drilling records without flow rate curves have been delivered at SRG meeting. Root cause: Wrong configuration of the new drilling parameters data logger. Flow rate calculated instead of being read directly from the flow meter.
| 02SL - Stations (LUL) | Cxxx-NCR-000108-L | NCR | Grouting in Post Office Tunnel Exclusion Zone |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-11-24 | 2012-09-27 08:40 | -58 | 2012-08-24 | Geotechnical Engineering - Compensation Grouting | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | Between 16/07/2012 and 21/08/2012, 18 No sleeves were grouted within __ Exclusion Zone. The exclusion zone has been defined as 5m radially on __ drawings (Cxxx-__M-C2-DWG-C101-50003 Rev C01). Root Cause: Grouting instructions released to operational team did not show the __ exclusion zone.
| 02SL - Stations (LUL) | Cxxx-NCR-000109-L | NCR | Excavation adjacent to Post Office Tunnel not in line with RESS (Out of Quadrant) |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-08-31 | 2012-07-30 11:56 | -32 | 2012-05-29 | Shafts -Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The excavation for step 8 excavated out by one quadrant ie the 1/2 of the circumference is infringing into step 09 which is adjacent to the __ Root cause: Unclear instruction on the RESS document and change of shaft centre lines.
| 02SL - Stations (LUL) | Cxxx-NCR-000111-L | NCR | Loss of data during TAM Drilling |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-10-25 | 2012-08-01 20:15 | -85 | 2012-07-25 | Geotechnical Engineering - Compensation Grouting | 500 |  | Equipment Breakdown | Use As-Is |  | Complete |  | Completed |  | During drilling of boreholes GAD1S09 drilling parameters have been displayed on __ screen mounted on the rig, but they haven’t been properly recorded in the memory of the computer. Incomplete drilling records have been delivered at SRG meeting (see Minutes attached). Root cause : Drilling parameters data logger fault
| 02SL - Stations (LUL) | Cxxx-NCR-000114-L | NCR | Insufficient __ Quality Control Personnel on site for Inspection |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-09-17 | 2012-07-12 10:36 | -67 | 2012-06-12 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Witness site inspections from __ Quality Control personnel are insufficient for the period from March 2012 to May 2012 and as a result Quality Control Sheets are not signed by __ Quality Control Personnel. Root cause: While an increase of the work load occurred with both sites starting working 24/24 and 7/7, we encountered: - Reduction in personnel (1 SCL Inspector still absent today for Health), - Insufficient planning of the resources to cover all activities to be inspected, - Difficulty to recruit new personnel.
| 02SL - Stations (LUL) | Cxxx-NCR-000115-L | NCR | Surface Level of the mass pour concrete slab incorrect |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-07-20 | 2012-07-16 10:14 | -4 | 2012-06-20 | Shafts - Shafts General | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | Area of shaft base concreted to a higher level than specified on the drawing by average of 42mm. The highest point exceeded design level by 63mm. Root cause: Insufficient level checking points and insufficient access provide to place concrete.
| 02SL - Stations (LUL) | Cxxx-NCR-000115-W | NCR | Pile reinforcement drawings have no approval or revision status |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2011-09-22 | 2011-12-22 20:08 | 91 | 2011-09-01 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | Reinforcement drawings used for construction of for minipiles have no evidence of approval and have no revision status. An example is the cage type D drawing. Note: lack of revision status and approval also shows failure to implement a procedure to approve documents for adequacy prior to issue and to ensure the current revision status of documents are identified as required by ISO 9001:2000 Clause 4.2.3
| 02SL - Stations (LUL) | Cxxx-NCR-000116-L | NCR | Muck Conveyor Belt - No IRFs provided to the Project Manager to notify Hold and Witness Points |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-06-14 | 2013-05-30 13:38 | -15 | 2012-11-07 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Further ITP for the muck conveyor belt (document Cxxx-__M-CITP-C101-50016 ITP LIV Conveyor Installation), the Project Manager's and Supervisor's team have not been invited to witness the following events: - Installation of Conveyor - Ground anchors: 1.Setting out of Conveyor anchor - Not witnessed 2.Installation of ground anchors – cleanliness - Not witnessed 3.Installation of __ HST stud anchors – depth and protrusion – Not witnessed 4.Installation of __ HST stud anchors – bolt diameter - Not witnessed 5.Installation of ground anchors – torque - Not witnessed - Installation of Conveyor – Frame bolts 1.Installation of bolts in frame – bolt diameter - Not witnessed 2.Installation of bolts in frame – protrusion - Not witnessed 3.Installation of bolts in frame – torque - Not witnessed Root cause: •Cxxx-__M-CITP-C101-50016 ITP LIV Conveyor Installation not followed.
| 02SL - Stations (LUL) | Cxxx-NCR-000116-W | NCR | Minipile Position and Vertical Tolerances |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2011-09-22 | 2011-12-22 20:14 | 91 | 2011-09-01 | Civil - Civil Engineering General | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | ITP Cxxx-__M-C-STP-D061-50003B Rev 2.0 Inspection number 1.3 specificies acceptance criteria of 1 in 75 for verticality and +/- 75mm positional tolerance.
| 02SL - Stations (LUL) | Cxxx-NCR-000117-W | NCR | Pile cap D1 in Durward Street has been poured without any IFC drawing nor proper accepted FCD |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2011-09-15 | 2011-12-22 20:17 | 98 | 2011-09-02 | Structural Engineering - Reinforcement | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | Work has been prepared according to Swanlea School protection design works Reinforcement Design Intent Cxxx-OVE-S-DDD-CR0001_Z23436 P02.2 S0 received unofficially 08/08/11. On the 16/08/11, we received a PMI with a drawing and a bending schedule. We implemented the reinforcement as far as possible according to the PMI drawing and our bending schedule, and added some bars that were missing in our bending schedule according to PMI bending schedule.( See final bending schedule).No final design was issuedThe links in __ bending schedule have hooks at each end and couldn’t be implemented as per PMI drawing. We placed all the links shown in PMI drawing in addition to our links. ( see picture)The bottom bars are installed on 75 mm thick concrete spacers. As the PMI drawing shows that they have a link with the top bar, then the bottom cover resulting is 75 mm – 12 mm = 63 mmDue to the constraint of the reopening of Swanlea school, __ needed to proceed as per information given. CRL representative on site have been informed of the situation. Formal FCD was not issue in due time to validate officially agreements.
| 02SL - Stations (LUL) | Cxxx-NCR-000119-L | NCR | Contractor’s surveillance findings |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-07-11 | 2012-07-26 18:53 | 15 | 2012-06-27 | Geotechnical Engineering - Compensation Grouting | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | Contractor’s surveillance of 07/06/2012 documented findings on material that did not meet specified requirements and omission of specified test from the ITP, yet these were not reported as NCRs (RU)
| 02SL - Stations (LUL) | Cxxx-NCR-000120-L | NCR | progressive assurance |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-07-31 | 2012-07-12 11:16 | -19 | 2012-06-27 | Geotechnical Engineering - Compensation Grouting | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | Records were not made available for CRL surveillance of 07/06/12 do demonstrate compliance with the requirements set out in the contract for calibration schedule for all measurement and monitoring equipment, measurement of settlement during TAM drilling and the test standard together with the acceptable test result parameters for grout testing. (RU)
| 02SL - Stations (LUL) | Cxxx-NCR-000121-L | NCR | Batching Plant – __ Anchor done with insufficient anchorage of threaded bar |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-10-17 | 2012-10-15 11:56 | -2 | 2012-07-17 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | __ Anchor done with insufficient anchorage of threaded bar length for holding down bolt of admixture structural frame to affixe temporary works structure to concrete foundation Root cause: Improper workmanship and supervision as to the correct lengths of threaded Bars to be cut and inserted into existing anchorage holes on the structural frame.
| 02SL - Stations (LUL) | Cxxx-NCR-000122-L | NCR | Batching Plant – Coordination issue between services concrete opening and position of batching plant footing and anchors |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-12-21 | 2012-11-14 12:13 | -37 | 2012-07-25 | Civil - Civil Engineering General | 500 |  | Material | Repair |  | Complete |  | Completed |  | Incorrect location of service ducts as per DWG: UnPS-CFT-LIV-SIT-D-62270 Rev 12, because the flexibility of the ducts did not permit ease of bending into correct location and hence some of the duct was underneath base plate 26. Root Cause: The Material of Ducts was inappropriate for the required measurements of the duct location and hence clashed with one of the Batcher plant footings. See attached drawing of as built Duct after concrete of Batching Plant Foundation
| 02SL - Stations (LUL) | Cxxx-NCR-000123-L | NCR | Shaft Backfilling Temporary Phase Quality Control Not Detailed |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-01-30 | 2013-01-11 16:38 | -19 | 2012-10-29 | Tunnelling - Tunnelling General | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | Activity was covered by SCL Construction Access Passages CP5 & CP6’, Cxxx-__M-C-GMS-C101-50021 Rev 4.0, Page 15, Section 5.3.4 and by Cxxx-__M-C4-ITP-CR092-50001 Rev 6.0 ITP SCL Tunnelling Methodology but did not reference to ITP: Cxxx-__M-C-ITP-C101-50030 Rev 1.0 ITP AS1 Shaft Concrete Repair Works Primary Lining LIV to detail the quality control for the intermediate temporary phase of backfilling. Root cause: Reference to Cxxx-__M-C-ITP-C101-50030 not included in Cxxx-__M-C-GMS-C101-50021 to coordinate the HOLD POINT of Concrete Repair Inspection prior to commencing backfilling operation.
| 02SL - Stations (LUL) | Cxxx-NCR-000124-L | NCR | TAM drilling parameters not recorded (CRL Observation 50) |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-10-25 | 2012-08-01 20:20 | -85 | 2012-07-25 | Geotechnical Engineering - Compensation Grouting | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | S11 driller wasn't recording parameters for 2m as the driller forgot to press the recording button after adding new drilling rod before drilling again. (CRL Observation 50) During drilling of boreholes GAD2S11 and GAD2N14 drilling parameters have not been recorded properly in the __ computer mounted on the rig. 2m (from 11 to 13m) are not displayed on the final drilling record for GAD2S11 and 1m (from 2 to 3m) is not displayed on the final drilling record for GAD2N14. Root cause: __ recorder has been left in Pause Mode during drilling.
| 02SL - Stations (LUL) | Cxxx-NCR-000125-L | NCR | Insufficient Shotcrete on site to complete the 2nd Prinary Layer of the AS1 Shaft Base (Supply Shortage). |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-10-25 | 2012-09-07 11:44 | -48 | 2012-08-16 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | This NCR addresses the causes of other NCR LIS-CRL NCR-Cxxx-00101 and to ensure the issue of shortage of concrete is duly address. Issue was that site ran out of shotcrete in dry silo and no further delivery were foreseen as SCL activities were ending. It was therefore decided to complete works with what was left in silo, based on assessment by Engineers that the volume contained in Dry Silo was sufficient. Root cause : Main root cause was the change of activity and production mode shotcrete lining. Also, there should have been a safety factor in the quantity assessed for the whole final volume to be sprayed.
| 02SL - Stations (LUL) | Cxxx-NCR-000126-W | NCR | Swanlea School Mini Piles : As built location of piles out of tolerance |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2011-10-13 | 2012-01-25 09:06 | 104 | 2011-10-03 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | a) Survey as built of the pile locations once they had been cut down at finished level gave the locations out of tolerance for 3 out of the 6 piles. b) The as built record is attached. c) The margin is as built location as follows: Pile 3.1: 117mm, Pile 3.2: 90mm, Pile 3.4:144mm, Pile 3.5: 48mm, Pile 3.6: 34mm See file attached.
| 02SL - Stations (LUL) | Cxxx-NCR-000127-L | NCR | Blockage of standpipes (during excavation) in shaft AS1 necessary for determination of water levels/water pressure in water bearing strata under base of shaft (CRL Observation 38). |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-12-06 | 2012-11-30 12:35 | -6 | 2012-09-06 | Geotechnical Engineering - Ground Investigation | 500 |  | Damaged | Use As-Is |  | Complete |  | Completed |  | Within the cross section of Access Shaft AS1 at LIV four vertical probeholes have been drilled 10 m below the final excavation level of the shaft and standpipes have been installed. Probehole numbers are 5, 6, 7, and 8. Measurements of groundwater were taken form 05. April 2012 to 13. April 2012. During excavation of shaft AS1 blockage of standpipes occurred. No more readings could be taken. The results of these readings were sufficient to finally design the required excavation and support of AS1. From the beginning it was expected that the standpipes could not be preserved during the excavation and that they most likely would be damaged. Nevertheless, the standpipes could be recovered at a later stage of AS1 excavation and could act as passive relief wells for the rest of the excavation. Root cause : Damage due to excavation works as expected.
| 02SL - Stations (LUL) | Cxxx-NCR-000128-L | NCR | Works for Liverpool Street Batching Erection done without an ITP |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-10-30 | 2012-08-02 16:50 | -89 | 2012-07-30 | Civil - Civil Engineering General | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | Batching Plant Temporary works have started (Excavation and Blinding Concrete) without an accepted ITP, which is not conformed to Contract Clause. Comments on ITP relate to the Concrete works. Root cause: It was assumed that the ITP for the commissioning of the Batching Plant was going to be sufficient for this activity since __ main goal was to ensure a properly operational batching. This would have given sufficient satisfaction to __ that the Batching Plant was erected adequately.
| 02SL - Stations (LUL) | Cxxx-NCR-000128-W | NCR | Swanlea School Mini Piles : As built location of piles out of tolerance |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2011-10-24 | 2012-02-19 16:16 | 118 | 2011-10-12 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | a) Survey as built of the pile locations once they had been cut down at finished level gave the locations out of tolerance for 4 out of the 6 piles.b) The as built record is attached.c) The margin is as built location as follows: Pile 2.1: 89mm, Pile 1.2: 69mm, Pile 1.3: 85mm, Pile 1.4: 84mm, Pile 1.5: 85mm, Pile 1.6 41mm See file attached.
| 02SL - Stations (LUL) | Cxxx-NCR-000129-L | NCR | Muck Hoist Installation works started without Approved ITP |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-09-10 | 2012-08-20 17:55 | -21 | 2012-07-25 | Tunnelling - Tunnelling General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Works undertaken on site to method statement Cxxx-__M-C-GMS-C101-50030 Rev 1 before ITP : Cxxx-__M-C-ITP-50015 Rev 1.0 accepted by CRL with Code 1 or 2 status. Root Cause Insufficient follow up of approval of documentation ITP and WMS
| 02SL - Stations (LUL) | Cxxx-NCR-000129-W | NCR | Batching Plant: Bolt dimensions and specification not in conformance with design |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2011-11-15 | 2012-08-09 13:14 | 268 | 2011-11-01 | Civil - Civil Engineering General | 500 |  |  | Repair |  | Complete |  | Completed |  | a) Diameter of bolts (28mm instead of 30mm because of thread on all length) b) Bending process of bars (Cold bending)
| 02SL - Stations (LUL) | Cxxx-NCR-000131-L | NCR | Slump test of one load was reported as 150mm (N.SZPIN 19/07/2012) |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-10-19 | 2012-09-07 11:55 | -42 | 2012-07-20 | Civil - Concrete Pavement | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Slump test results 50mm above required tolerance. Recorded value – 150mm. Root cause : Concrete mixed by the operator in training
| 02SL - Stations (LUL) | Cxxx-NCR-000132-L | NCR | Temporary Works welding |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-07-25 | 2013-07-18 12:46 | -7 | 2012-07-25 | Civil - Civil Engineering General | 500 |  | System Defect | Rework |  | Complete |  | Completed |  | Temporary works items have been welded on site without the all required assurance documentation for welding. The works currently without assurance include: -Gallows brackets supporting draw bridge in access shaft (LIS) -CPI silo podium (LIS) -Muck hoist base plate extensions (LIS) -Conveyor (LIS) -Access shaft stairs brackets and footings (WHI) -Other minor areas Root cause: __ have to date failed to put in place all required assurance documentation for welding: -No mention of site welding on the method statement, -No ITP for the welding, -No weld specification or standards on the sub-contractors drawing used to carry out the works, -There was no welding procedure produced by __, -The __ welder who has undertaken the works does not have any welder qualifications, -There were no pre works inspections for the weld set up and preparation.
| 02SL - Stations (LUL) | Cxxx-NCR-000135-L | NCR | Shotcrete used in location not approved by MCR |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-10-31 | 2012-09-07 12:00 | -54 | 2012-07-26 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Shotcrete used to concrete underpinning slab at Finsbury Circus Root cause: Material used to construct underpinning slab in order to accelerate process of certification of batching plant – requirement to produce 50m3 of mix
| 02SL - Stations (LUL) | Cxxx-NCR-000136-L | NCR | Steel manufactured out of tolerance and insufficient cover for shaft reinforcement |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-11-16 | 2012-09-06 12:19 | -71 | 2012-08-16 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Dimensions of steel links BM#155 & BM#116 for NW & SW columns were manufactured out of tolerance, by 50 to 70mm. In trying to fix the oversized links the SCL wall of the shaft had been scabbled/broken back in 2 places in order to allow for more room to fix the steel. this area had then been proof drilled and found to have compromised the minimum SCL thickness of 400mm by max 60mm. there is also the chance that with the uneven SCL surface and tolerance of fixing steel going up on the shaft walls the required cover of 45mm may be compromised. Root Cause: Bar marks detailed on schedule as shape code 99, supplier stated preference to call a 'special' as it could not be detailed in dimensions on columns A-E on the bar schedule. BS 8666:2005 gives no guidance on tolerances for any shapes other than those listed in the shape code shart.
| 02SL - Stations (LUL) | Cxxx-NCR-000137-L | NCR | Water added to fresh concrete in Base Slab |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-12-03 | 2012-11-30 12:32 | -3 | 2012-09-03 | Shafts - Shafts General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Delivered concrete slump S3. Water added to mix in situ. The quantity of water varies from 10 to 80 litre per 8m3 batch. Root cause : On the attached concrete pour record there appears to be on three occasions where the initial slump was not recorded prior to the addition of water. As can be seen from the attached concrete pour record sheet either a second slump was recorded as a retest or entered into the second slump column.
| 02SL - Stations (LUL) | Cxxx-NCR-000138-L | NCR | Loss of data during TAM drilling on 02/08/2012 |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-09-03 | 2012-08-08 18:24 | -26 | 2012-08-07 | Geotechnical Engineering - Compensation Grouting | 500 |  | Equipment Breakdown | Use As-Is |  | Complete |  | Completed |  | During drilling of borehole GAD2N17 (02/08/2012) drilling parameters have been displayed on __ screen mounted on the rig, but they haven't been properly recorded in the memory of the computer. Incomplete drilling records have been delivered at SRG meeting (see Minutes attached) Root Cause: Isolation of drilling rig during maintenance operation causing __ system to reboot after maintenance has been completed. As a result, __ configuration was not correct anymore.
| 02SL - Stations (LUL) | Cxxx-NCR-000138-W | NCR | Wrong XY Positioning for box out 24 |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2011-11-15 | 2012-04-23 10:15 | 160 | 2011-11-01 | Civil - Civil Engineering General | 500 |  |  | Repair |  | Complete |  | Completed |  | The box is away from its design position. Dimensions to theoretical position are reported on attached picture.
| 02SL - Stations (LUL) | Cxxx-NCR-000139-W | NCR | Whitechapel - Swanlea School: As Built location of piles out of tolerance |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2011-11-15 | 2012-03-19 17:49 | 125 | 2011-11-01 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | - A survey as built of the pile location once they had been cut down at finished level gave the locations out of tolerance for 4 out of 6 piles, as follow: Pile 2.1: 89mm, Pile 1.2: 69mm, Pile 1.3: 85mm, Pile 1.4: 84mm, Pile 1.5: 85mm, Pile 1.6: 41mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000140-W | NCR | Whitechapel - Main Access Shaft works started without accepted ITP |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2011-11-24 | 2012-04-23 09:47 | 151 | 2011-11-10 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Works Information Part 20.8 Inspection and Testing. “The Contractor Shall not start the works until the Supervisor (Crossrail) has accepted the ITP”.
| 02SL - Stations (LUL) | Cxxx-NCR-000141-L | NCR | AS1 base slap reinforcement issues |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-12-17 | 2012-08-20 17:59 | -119 | 2012-08-13 | Shafts - Shafts General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | 1. Issue 1: Base slab Bottom reinforcement splicing, 2. Issue 2: Rebars bar mark 28 and 25, 3. Issue 3: Incorrect number of bars installed in T2 layer of AS1 reinforcement, 4. Issue 4: Installation of shear links, 5. Issue 5: Top mat reinforcement bar mark 23 (a-d). 6. Issue 6: Position of lacers in base slab Non-Conformance: 1. Due to the length of the rebar specified in the design it was not possible to achieve the desired overlap outlined in the design. 2. 3# bars bar mark 25 (a-o) missing 3. The T2 layer of the top matt, the correct number of bars is in the matt (89) but under the SE column they are 6 B32 bars installed not 4 so there are 2 less B40 bars. This drops the area of steel provide. However there are 2 B20 bars which were installed as guide bars running about 100mm under the area. See the pdf attachment (Sketch Issue 3) 4. In order to install the sheared link the length A must be shortened by approx. 150mm leaving 165mm length to section A of the rebar. 5. U shapped Rebars not available and replaced by L shaped bars (32mm dia) that have been cut and spliced 6. Lacers rebars clashes with the vertical starters bar for the columns. Vertical starter bars to remain in position and lacers to be moved against starter bars.
| 02SL - Stations (LUL) | Cxxx-NCR-000141-W | NCR | Whitechapel - Shear bolt connection left out on bottom rings for main access shaft |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2011-11-24 | 2012-05-31 13:54 | 189 | 2011-11-10 | Civil - Civil Engineering General | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | The second ring built or ring 9, on one of the segments. One of the vertical shear bolts has not been tightened up.
| 02SL - Stations (LUL) | Cxxx-NCR-000142-W | NCR | Whitechapel - Access shaft acoustic shed foundation works started without accepted ITP |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2011-11-18 | 2012-04-23 09:44 | 157 | 2011-11-03 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | • Shallow excavations (<500mm), concrete blinding and some sorting and tying of the steel for the foundations commenced on site 28/10/2011. These works were covered under an approved Code 1 method statement and risk assessment. • The ITP was not approved Code 1 until 02/11/11.
| 02SL - Stations (LUL) | Cxxx-NCR-000146-L | NCR | Reinforcement issues in the columms AS1 |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-12-05 | 2012-09-06 10:47 | -90 | 2012-09-04 | Shafts - Shafts General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Non-Conformance: Issue 1: A total of 2No. Vertical rebar B40 coupled bar (BM 102 a), 1No. on each of the NW and SW columns, intrude 50mm on the tunnel eye intrados AP7 west and CP5. This does not give the required concrete cover (as per attached drawing). Issue 2: In North-East column, 4# links BM14 were found missing and have been replaced by using links BM28 as per the attached drawing. Issue 3: 1# link n. 26 has also been replaced by a link bar mark 27 (Dimension and shape of link are very similar). Issue 4: Links BM116 and 117 on the left hand side (looking from the centre of the shaft) do not share vertical bars passing through the lap of the links. This occurs at each layer of links in the SW column as per the attached drawing. Issue 5: Column lacers BM 13 (a-p), 35 (a-d), 113 (a-p), 135 (a-d) and 134 (a-e) respectively intrude on the CP5/6 and AP7 eye intrados requiring adjustments ranging from 180mm – 20mm to achieve cover (see attached drawings). Issue 6: Vertical B40 bars are on occasions spaced over/under designed 150mm centres ranging from 235mm – 80mm. See attached drawing. Note for issue with regard Reinforcement cover against shotcrete face refer to LIS-CRL NCR-Cxxx-00136 Root cause: Issue 1: Marking out the tunnel eye AP7 was not possible because of the obstructing haki stair tower. No access was indeed possible (using the cherry picker). The beamer survey system wasn’t available/functional at the time of the reinforcement installation for both AP7and CP5. Issue 2 & 3: Extra Links in bar mark 28 were remaining when some links of barmark 14 were missing – Error in delivery is probable Issue 4: Workmanship and supervision. Issue 5: Lacers fabricated are too long and hence intrude into both eyes on either side of the column Issue 6 : Difficulty to achieve correct spacing.
| 02SL - Stations (LUL) | Cxxx-NCR-000147-L | NCR | Gantry crane resin anchor installation |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-01-25 | 2012-12-17 15:50 | -39 | 2012-09-05 | Tunnelling - Tunnelling General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Column base A4 & B7 • 7 No M27 Anchors in A4 and 5 No M27 Anchors in B7 were installed instead of M30, 300mm deep with __ RE500 resin (see sketch attached). Column base B5 & B6 • 8No M30 Anchors were installed instead of 12No M24. • Protrusion not achieved in 9 out of 12 bolts in B5 and in 8 out of 12 bolts in B6. Column base B8 • 24 No M30 Anchors out of 25 total installed. Column Base A3, A4, B5, B6, B7, B8 • Torque witnessed to be 300Nm instead of 320Nm for M30 anchors Root cause : Column base A4 & B7 •M27 and M30 threaded haven’t been segregated properly in fitters shed, resulting in a mistake by workforce during installation. Column base B5 & B6 • UnPS-CFT-LIV-SIT-D-62273 _Rev11.0 indicates 8NO Ø33 Grade 4.6 whereas Manufacturer drawing 2011-069-003 Rev D shows 12NO Ø24 Grade 10.9. • Bolts cast in to Batching Plant Foundation without details for bolt protrusion. Column Base A3, A4, B5, B6, B7, B8 • Resin used is __ Hit-Re 500. ITP based on originally specified Rawl R-Cas Resin. As per attached manufacturers specification, torque value for __=300Nm and Rawl=320Nm.
| 02SL - Stations (LUL) | Cxxx-NCR-000148-L | NCR | Documentation to cover Welding of reinforcement, __ hose installation, preparation of concrete joint |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-12-04 | 2012-09-06 10:58 | -89 | 2012-09-04 | Shafts - Shafts General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Tack welding of reinforcement undertaken as per drawing, UnPS-CFT-LIV-AS1-D-50551 rev C4, __ hose installation & preparation of concrete joint but not detailed in method statement & ITPs listed above.
| 02SL - Stations (LUL) | Cxxx-NCR-000149-L | NCR | Reinforcement issues in the columms AS1 (issue 7 to 12) |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-09-30 | 2012-09-06 11:55 | -24 | 2012-09-05 | Tunnelling - Tunnelling General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Issue 7: With regard to radial rebars not passing through the correct link. Issue 8: Cover at opening. Issue 9: Cover at slipform. Issue 10: Cover between reinforcement and shotcrete under 20mm in few location. Issue 11: No issue. Issue 12: Problem with the dimension of the polystyrene
| 02SL - Stations (LUL) | Cxxx-NCR-000149-W | NCR | Interface between CPI silo and Europ Equipment structure |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-05-21 | 2012-04-30 11:57 | -21 | 2012-04-19 | Civil - Civil Engineering General | 500 |  |  | Rework |  | Complete |  | Completed |  | The drawing of the silo from CPI (ref SF12271.01) is different to the delivered silo. So when the silo was installed, it could not be connected to the structure because the silo had a wider external flange and a different top cover (see photos) which prevented the base to align square to the frame. Root cause : Incorrect design issued by CPI in respect to the actual silo delivered to site.
| 02SL - Stations (LUL) | Cxxx-NCR-000151-L | NCR | Absence of monitoring during Correcting Grouting under Hammersmith&City Line |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-02-15 | 2013-02-14 10:37 | -1 | 2012-09-18 | Geotechnical Engineering - Compensation Grouting | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | On the 10th September 2012, grout injections recommenced on corrective grouting phase GJ10 at the start of shift. An injection commenced at 08:44 and by 09:51 219 litres of grout was injected in A2, 96L in A1, 139L in B1 and 160L in B2 underneath the Hammersmith and City Line. During these injections, real time monitoring was not visible on Geoscope Web. Root cause: The monitoring department did not advise the Ground Engineering Team that the real time monitoring system was not operational.
| 02SL - Stations (LUL) | Cxxx-NCR-000153-L | NCR | Voids and honeycombing on the concrete surface of the AS1 Shaft Lining |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-12-26 | 2012-12-22 10:46 | -4 | 2012-09-27 | Shafts - Linings | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Reinforcement bars are exposed in without any cover. See attached photos and mapping of all the areas that need repairing. Root cause: The voids are mainly caused by poor vibration at the time of concrete pouring.
| 02SL - Stations (LUL) | Cxxx-NCR-000154-L | NCR | GAD1CH29 TAM position outside specified tolerance intruding Northern Line grouting exclusion zone |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-01-18 | 2012-12-17 16:41 | -32 | 2012-10-15 | Geotechnical Engineering - Compensation Grouting | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Borehole GAD1CH29 drilled on the 12th September 2012 and was surveyed on the 18th September 2012 using Maxibor. The borehole was found to be outside the agreed tolerances in elevation. The borehole is 0.8m outside the tolerance envelope in elevation, making it entering the Northern Line Grouting Exclusion zone by 0.91m. Root cause: Drilling accuracy was not within specification possibly due to workmanship but a definitive root cause cannot be positively determined.
| 02SL - Stations (LUL) | Cxxx-NCR-000156-L | NCR | __ Gantry Crane - No IRFs provided to the Project Manager to notify Hold and Witness Points |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-04-26 | 2013-04-12 16:09 | -14 | 2012-11-07 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Further to ITP for the __ Gantry Crane(document Cxxx-__M-CITP-C101-50028 ITP __ Crane Installation), __ has not invited the Project Manager'sand Supervisor's teams to witness the following events or issues has arisen after the inspection: - Installation of Gantry Crane - Ground anchors 1.Setting out of Gantry anchor - Witnessed, no action 2.Installation of ground anchors – cleanliness - Not witnessed 3.Installation of ground anchors – depth and protrusion - Witnessed bolt protrusion post installation (inspection on 25/08/12). Problems with B5 and B6. Designers still need to verify whether B5 and B6 are acceptable. 4.Installation of ground anchors – diameter - Witnessed and checked bolt diameter post installation (inspection on 25/08/12). Problems with A4,B5, B6 and B7. 5.Installation of ground anchors – curing - Not witnessed 6.Installation of ground anchors – torque - Witnessed, issues below with incorrect torque value now rectified and witnessed by the Inspector for M30 bolt. However, M27 bolts were installed in A4 and B7 instead of M30 bolts. M30 bolts were installed in B5, B6 instead of M24. Designers still need to verify whether M27 instead of M30 bolts are acceptable - Installation of Gantry Crane – Frame bolts 1.Installation of bolts in frame – diameter - Not witnessed 2.Installation of bolts in frame – protrusion - Not witnessed 3.Installation of bolts in frame – torque - Not witnessed Root cause : •Cxxx-__M-CITP-C101-50028 ITP __ Crane Installation not followed
| 02SL - Stations (LUL) | Cxxx-NCR-000158-L | NCR | Muck Hoist - No IRFs provided to the Project Manager to notify Hold and Witness Points |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-04-26 | 2013-04-17 13:18 | -9 | 2012-11-07 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Further to __'s ITP for the muck hoist (document Cxxx-__M-C-ITP-C101-50015 ITP Shaft AS1 Temporary Muck hoist Installation), B__ has not invited the Project Manager's and Supervisor's teams to witness the following events: - Installation of Muck hoist- Ground anchors 1.Setting out of muck hoist anchors - Not witnessed 2.Installation of ground anchors – cleanliness - Not witnessed 3.Installation of ground anchors – depth and protrusion - Not witnessed 4.Installation of ground anchors – bolt diameter - Not witnessed 5.Installation of ground anchors – curing - Not witnessed 6.Installation of ground anchors – torque - Not witnessed - Installation of Muck hoist – Frame bolts 1.Installation of bolts in frame – bolt diameter - Not witnessed 2.Installation of bolts in frame – protrusion - Not witnessed 3.Installation of bolts in frame – torque - Not witnessed Root cause : •Cxxx-__M-C-ITP-C101-50015 ITP Shaft AS1 Temporary Muck hoist Installation not followed.
| 02SL - Stations (LUL) | Cxxx-NCR-000160-L | NCR | Work without an approved ITP: Crane Base Foundation |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-12-12 | 2012-12-03 11:28 | -9 | 2012-10-08 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Crane Base foundation works started without an approved ITP (Refer to ITP – __ Crane Installation Cxxx-__M-C-ITP-C101-50028.) ITP was submitted by __ 20.07.12 and accepted by CRL 26/07/12, however works had started with excavations for the foundations on 16/07/12 and the first concrete pour on 20.07.12. Root cause : Insufficient follow up of approval of documentation ITP and WMS
| 02SL - Stations (LUL) | Cxxx-NCR-000161-L | NCR | Underpinning and installation of sheeted frames during excavation |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-03-15 | 2012-12-17 16:45 | -88 | 2012-11-27 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Sheet piles driven to full depth without installation of frame. Root cause : Groundforce drawings drawings and __ method statement not followed and adhered to.
| 02SL - Stations (LUL) | Cxxx-NCR-000162-L | NCR | Exceeding Temperature of the Laboratory cabin |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-01-31 | 2013-01-25 11:53 | -6 | 2012-10-16 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | The cube moulds of the grout samples have to be cured at a temperature of (20 ± 5) °C . The room temperature of the laboratory cabin was found to be 27 °C (exceeded 25°C ) which can cause dehydration of the cubes. The issue was raised by CRL Inspector Raymond Urbaniak during the CRL Surveillance on 11 October 2012. Root Cause: Not completion of the Air Condition unit installation. The order though has been placed since April 2012. (Requisition attached) Insufficient monitoring of the curing room temperature.
| 02SL - Stations (LUL) | Cxxx-NCR-000162-W | NCR | Waste Transfer Notes Incomplete: SIC Code Missing |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-03-22 | 2012-05-16 21:22 | 55 | 2012-02-22 | Environmental - Waste & Material Management | 500 |  | System Defect | Reject |  | Complete |  | Completed |  | During a random check of Waste Transfer Notes on SmartWaste, of the 15No checked, the SIC Code was noted to be missing from the following: 19/01/2012: WTN 319816 11/01/2012: WTNs 319129, 319131, 319130 and 319132. Lack of SIC Codes on WTNs has previously been identified during the Waste Audit on 31 October although closed out.
| 02SL - Stations (LUL) | Cxxx-NCR-000163-L | NCR | GAD1CH21 TAM position outside specified tolerance intruding Northern Line grouting exclusion zone |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-01-18 | 2012-12-17 17:15 | -32 | 2012-10-15 | Geotechnical Engineering - Compensation Grouting | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Borehole GAD1CH21 drilled on the 26th September 2012 and was surveyed on the 28th September 2012 using Maxibor. The borehole was found to be outside the agreed tolerances in elevation. The borehole is 1.14m outside the tolerance envelope in elevation, making it entering the Northern Line Grouting Exclusion zone by 1.90m. Root cause: Drilling accuracy was not within specification possibly due to workmanship but a definitive root cause cannot be positively determined.
| 02SL - Stations (LUL) | Cxxx-NCR-000164-L | NCR | Shotcrete base mix used with some batches not containing Micro Silica |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-01-30 | 2012-11-19 17:11 | -72 | 2012-10-29 | Civil - Civil Engineering General | 500 |  | Equipment Breakdown | Use As-Is |  | Complete |  | Completed |  | Date of Occurance: early August 2012. Some loads of shotcrete did not contain micro silica Root cause: An intermittent computer malfunction occurred
| 02SL - Stations (LUL) | Cxxx-NCR-000165-L | NCR | Early strength testing Adv 29 significantly lower than the modified J2 Curve |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-02-22 | 2013-02-18 16:11 | -4 | 2012-11-05 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Compliance with Early Strength requirements advances 29 and using Accelerator dosage of 3.5% for invert of advance 29 Initial Lining. Root cause : J2 curve – Use more accelerator dosage which caused non-compliance with the J2 Curve as per KT 20 Specs. The sprayer miss-tabulated the accelerator dosage with a reading dosage of 3.5% instead of the actual range from 4% to 8%.
| 02SL - Stations (LUL) | Cxxx-NCR-000167-L | NCR | Concrete defects on the surface of the AS1 Shaft lining (higher than +1m of the backfilling level). |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-01-31 | 2013-01-08 19:11 | -23 | 2012-10-17 | Shafts - Shafts General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Defects on the primary AS1 Shaft Lining: •Reinforcement bars are exposed without any cover, •Uneven surface, small voiding without rebar, crack, potential cold joint, spalling. This NCR refers to all the concrete defects that are higher than +1m of the backfilling level according to the attached list (12-10-2012) and have to be repaired even after the break-out of the tunnel eyes. Please refer to NCR-0153 for the rest of the defects. See attached photos and mapping of all the areas that need repairing. Root cause : The voids are mainly caused by poor vibration at the time of concrete pouring.
| 02SL - Stations (LUL) | Cxxx-NCR-000168-L | NCR | Kwikastrip Reinforcement damage in AP7-E Adv. 2 during excavation of Adv.6. |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-12-14 | 2012-12-12 13:50 | -2 | 2012-10-26 | Civil - Tunnelling | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | The Damage and Consequential removal of section of KWIKASTRIP Reinforcement of Adv. 2 during the excavation of Advance 6. Root cause : Accidental Breaking out (damage) of Kwikastrip by Terex Breaker at advance 6.
| 02SL - Stations (LUL) | Cxxx-NCR-000169-L | NCR | Possible deviation against RESS |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-01-29 | 2013-01-17 12:57 | -12 | 2012-10-29 | Tunnelling - Tunnelling General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Issue 1: The top heading of LIS AP7-East Advance 10 (pilot tunnel) has been undermined by c.a. 500mm and the associated invert has not been profiled. Issue 2: The top heading excavation line of LIS AP7-East Advance 12 (pilot tunnel) is below the indicative invert line; invert profile not achieved. Root cause : Lack of set level for the invert (= full meaning of “indicative “ with regard to level 77.80).
| 02SL - Stations (LUL) | Cxxx-NCR-000169-W | NCR | Non-Conformity of aggregate - Sample E0035 & E0056 |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-03-22 | 2012-06-28 11:59 | 98 | 2012-02-22 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | One sample taken from each of 's batching plants have shown a marginal grading failure on the 2.0 sieve on sample Nos E053 and E056. Root Cause: Material marginally too fine or segregation of material.
| 02SL - Stations (LUL) | Cxxx-NCR-000170-L | NCR | Excavation Advance Length |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-01-29 | 2013-01-17 12:59 | -12 | 2012-10-29 | Tunnelling - Tunnelling General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Advance length, measured by tape, of 1.4m at top heading bottom excavation line of Advance 12. Root cause : New graduated Shift Engineer on training. Overbreak caused by excavator bucket and confinement at invert and sidewalls.
| 02SL - Stations (LUL) | Cxxx-NCR-000171-L | NCR | Joint Detail for Adv 16 not constructed as per Detail |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-01-29 | 2013-01-17 13:11 | -12 | 2012-10-29 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Joint at Primary Lining Spray not constructed as per Detail. ROOT CAUSE: New graduated Shift Engineer on training. New Shift Engineers have not been suitably informed, instructed, trained or supervised by the experienced members of the ‘Shift Team’. Primary Lining sprayed closer to the inclined face by the Operator. The ‘Nozzleman’ should be fully aware of the quality requirements on the placement of shotcrete.
| 02SL - Stations (LUL) | Cxxx-NCR-000172-L | NCR | Early Strength Sprayed Concrete Test Results |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-01-30 | 2013-01-29 17:21 | -1 | 2012-10-29 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Issue 1) Low concrete temperature at flow test: •Adv 10: air temperature=8 / shotcrete temperature=12 •Adv 11: air temperature=6 / shotcrete temperature=10 •Adv 12: air temperature=4.7 / shotcrete temperature=12.6 Issue 2) Missing tests therefore readings at 3hrs and 6hrs Adv 11. Test results at 9hrs not complying with requirements: Stenght average at 9h: 2.53 N/mm2 (see Early Strength Hilt Gun Test record at 9h Adv. 11 attached) Root cause : Issue 1) Sudden drop of weather temperatures therefore Air Temperature and Concrete Temperature slowing down the early strength raising. Issue 2) Availability of Shift Engineer to perform tests.
| 02SL - Stations (LUL) | Cxxx-NCR-000173-L | NCR | Shotcrete Batching Plant not ready for emergency production of shotcrete |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-02-28 | 2013-02-08 09:33 | -20 | 2012-11-06 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | • 25/10/2012 Nightshift while spraying the 75mm initial on the invert of AP7 East Adv 7, the concrete pump broke down and the second one was not connected • 3/11/2012 Dayshift Adv. 2 of AP7-W was full excavated and the batcher operator was under to start the batcher due to an electric problem. The problem was not rectified on this shift, when the NS finally got the batcher working it was after 2000. The CPI pre-blended mix was not used to seal the face on the DS. In both cases the face has been exposed for many hours which is not in accordance with KT20.3204 (b) .
| 02SL - Stations (LUL) | Cxxx-NCR-000173-W | NCR | Window film installation at Swanlea School done without an approved ITP |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-04-20 | 2012-04-23 09:35 | 3 | 2012-03-06 | Architectural - Glazing | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | Works started and completed in August 2011, ITP was issued on 25th July 2011 abd CRL comments received on 09th November (Code 3). Therefore, Works were carried out without an accepted ITP. Root Cause: This has happened in August 2011 (8 Months from now) the project was in the learning curve for the submission of ITPs and dealing with the delayed response by CRL. Engineers were not informed adequately on how to manage the issue.
| 02SL - Stations (LUL) | Cxxx-NCR-000174-L | NCR | Construction of Adv 2 of Pilot Tunnel |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-12-21 | 2012-12-13 11:59 | -8 | 2012-11-05 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Equipment Breakdown | Use As-Is |  | Complete |  | Completed |  | a)Insufficient number of readings for the thickness of the initial layer and blind spot on the bottom left side for the primary lining thickness check b)The staggering of joint initial/primary is not as detailed in RESS AP7-E/02 (below 300mm) Root cause : •Lack of readings and a “blind spots” of Beamer vision due to its technical limitations •Profile sprayed tight (-3 to -22 mm) •The shortness of the advance prevented from constructing the requested size of joint
| 02SL - Stations (LUL) | Cxxx-NCR-000175-L | NCR | Batching Plant weigh scale accuracy |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-04-05 | 2012-12-17 16:48 | -109 | 2012-12-03 | Tunnelling - Tunnelling General | 500 |  | Equipment Breakdown | Use As-Is |  | Complete |  | Completed |  | From a review of the autographic record print outs this has not been achieved in all cases. Root cause : The overrun was identified once the batcher printer came on line and coincided with a software upgrade in the plant whereby, the computer should have self-learnt and adjusted itself for in flight material that is, the material free falling onto the weigh belt after the aggregate hopper gate has closed. At the same time for whatever reason it adjusted itself from a 3% weigh tolerance to 5%.
| 02SL - Stations (LUL) | Cxxx-NCR-000176-L | NCR | Fall of shotcrete AP7-E Adv 12 |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-01-31 | 2013-01-17 13:18 | -14 | 2012-10-30 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Rework |  | Complete |  | Completed |  | On Saturday 27.10.2012 at 06:00 a section approximately 1x0.6x0.1 m3 of shotcrete on initial lining of top heading, right hand side shoulder fell out. Root cause : Running short of shotcrete accelerator: shotcrete has been sprayed without accelerator because the tank onto POCA sprayer has not been refilled by shotcrete operators.
| 02SL - Stations (LUL) | Cxxx-NCR-000177-L | NCR | Completeness of shotcrete checksheet |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-03-15 | 2013-02-08 11:08 | -35 | 2012-11-06 | Tunnelling - Linings - Sprayed Concrete | 500 |  | System Defect | Rework |  | Complete |  | Completed |  | The shocrete checkseet is not completed properly according to the ITP. Many fields remain empty where ‘N/A’ should be stated instead. Root cause : The engineers are not trained enough and sometimes they do not know how to fill in the checkseet properly.
| 02SL - Stations (LUL) | Cxxx-NCR-000177-W | NCR | TAM - Drilling - Maxi Bore out of Tolerance |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-12-14 | 2012-09-28 15:36 | -77 | 2012-09-06 | Geotechnical Engineering - Compensation Grouting | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The following boreholes were surveyed using a Maxibore and were found to be outside the agreed tolerances: TAM02 which commenced drilling on the 5th March 2012 and completed on the 6th March 2012 was outside the tolerance envelope in elevation. TAM05 which commenced drilling on the 7th March 2012 and completed on the 8th March 2012 was outside the tolerance envelope in elevation. TAM10 which commenced drilling on the 28th March 2012 and completed on the 29th March 2012 was outside the tolerance envelope on plan. TAM11 which commenced drilling on the 26th March 2012 and completed on the 26th March 2012 was outside the tolerance envelope on plan. TAM15 which commenced drilling on the 19th March 2012 and completed on the 19th March 2012 the TAM was short of design length by 1m. TAM16 which commenced drilling on the 15th March 2012 and completed on the 15th March 2012 the TAM was short of design length by 1.5m. TAM50 which commenced drilling on the 23rd April 2012 and completed on the 23rd April 2012 was outside the tolerance envelope on plan. TAM52 which commenced drilling on the 29th March 2012 and completed on the 30th March 2012 was outside the tolerance envelope in elevation. TAM55 which commenced drilling on the 17th May 2012 and completed on the 17th May 2012 the TAM was short of design length by 0.5m. TAM56 which commenced drilling on the 17th May 2012 and completed on the 17th May 2012 was outside the tolerance envelope in elevation. TAM58 which commenced drilling on the 29th February 2012 and completed on the 29th February 2012 was outside the tolerance envelope in elevation I06 which commenced drilling on the 6th March 2012 and completed on the 6th March 2012 was outside the tolerance envelope in elevation Root cause: Drilling accuracy was not within specification possibly due to workmanship but a definitive root cause cannot be positively determined
| 02SL - Stations (LUL) | Cxxx-NCR-000178-L | NCR | Insufficient Thickness of Shotcrete on AP7-E Advance 17 |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-01-31 | 2013-01-17 12:23 | -14 | 2012-10-30 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The Total Thickness profile (Tunnel Beamer record) showed insufficient shotcrete thickness at Adv 17. Proof drilling has taken place on 30/10/2012 (see attached sheet). Root cause: New graduated Shift Engineer on training.
| 02SL - Stations (LUL) | Cxxx-NCR-000179-L | NCR | Shotcrete cores have not been taken according to the required frequency (1 set every 50m3) |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-12-21 | 2012-12-13 12:21 | -8 | 2012-11-07 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | Cores for AP-7 E have not been taken according with the ITP (1 set every 50m3). Root cause : Misunderstanding on the ITP requirement of 1 set every 50m3. The requirement is for the designed quantities and not on the batched quantities.
| 02SL - Stations (LUL) | Cxxx-NCR-000180-L | NCR | Shaft AS1 SCL - No measurement of estimated fibre & aggregate rebound |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-12-14 | 2012-12-10 18:04 | -4 | 2012-11-05 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | No measurement of estimated fibre & aggregate rebound recorded for Shaft AS1 Primary SCL. (1 test every month, during spraying operation) Root cause: Checksheet not in place to record rebound.
| 02SL - Stations (LUL) | Cxxx-NCR-000181-L | NCR | Insuficient thickness adv 13 |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-02-15 | 2013-01-17 12:33 | -29 | 2012-11-01 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Repair |  | Complete |  | Completed |  | Core samples have been taken from adv 13. Depth of cores varies from 180mm to 230mm. It is insufficient thickness of the advance (min 250mm),( see Core Hole Depth Record Adv 13 attached). The records of the excavation and primary lining shows correct profiles (see Thickness Profile for Adv 13 attached). Root cause: Discrepancy between Beamer profiles and Depth of cores. Using a single (instead of 2 No) Beamer, without an extension arm, is causing blind areas on the left hand side of the advance causing selective coverage of the excavation profiles and shotcrete thickness. There is no written procedure on the minimum number of ‘shots’ required both in the radial and longitudinal directions to give a representative sample of the profile and thicknesses.
| 02SL - Stations (LUL) | Cxxx-NCR-000182-L | NCR | No steel fibres in the shotcrete primary lining of AP7-W Adv. 6 |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-02-07 | 2013-02-05 12:50 | -2 | 2012-11-06 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Equipment Breakdown | Rework |  | Complete |  | Completed |  | No fibres were mixed in the shotcrete forAP7-W ADV6 primary layer. Blockage on the Fibre dosing belt prevented fibres being added to the mix. Camera that monitors fibre dosing belt was not working at that time.
| 02SL - Stations (LUL) | Cxxx-NCR-000183-L | NCR | GAD1 CH37 - TAM position outside specified tolerance intruding Northern Line Grouting Exclusion Zone |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-01-18 | 2013-01-15 14:11 | -3 | 2012-11-07 | Geotechnical Engineering - Compensation Grouting | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Borehole GAD1CH37 has been drilled on 18/10/12 and surveyed on 27/10/12 using Maxibor. The borehole was found to be outside the agreed tolerances in elevation. The borehole is 0.28m outside the tolerance envelope in elevation, making it entering the Northern Line Grouting Exclusion zone by 15.3m. Root cause: Drilling accuracy was not within specification possibly due to wormanship but a defenitive root cause cannot be positively determined.
| 02SL - Stations (LUL) | Cxxx-NCR-000184-L | NCR | TAM Drilling GAD1 CH49 - Overdrilled 3m |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-02-19 | 2013-01-17 12:44 | -33 | 2012-11-16 | Geotechnical Engineering - Compensation Grouting | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Borehole GAD1CH49 has been drilled to 53.0m as per drawing Cxxx-__M-C2-DWG-C101-50001 rev C01. 52.0m of TAM have been installed, 3.0m more than the final design. Root cause: Start of shift briefing has been correctly given to operatives on site. However, recent update of drawing revision has not been reflected on site (Geotechnical Adits), causing confusion for operatives.
| 02SL - Stations (LUL) | Cxxx-NCR-000185-L | NCR | Working without an ITP |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-01-31 | 2012-12-17 16:54 | -45 | 2012-10-31 | Civil - Tunnelling | 500 |  | System Defect | Rework |  | Complete |  | Completed |  | On Tuesday, 16.10.12, Nightshift, 2 No Piezometers were installed by __/__ without a suitable Inspection and Test Plan in place. the SNC ‘Method for Installing Vibrating Wire Piezometers Below Ground Water Table’ Cxxx-__M-C-CCN-C101-50049 was in place. This document refers to WMS Cxxx-__M-C-GMS-C101-50038 which references the ITP Cxxx-__M-C-ITP-D061-50014 which is not relevant to the Installation Activity. The SNC in the list of attachments refers to another SNC, Cxxx-__M-C-CCN-D061-50040, which refers to MS, Cxxx-__M-C-GMS-D061-50076, which in turn references ITP Cxxx-__M-C-ITP-D061-50052. The only reference to the piezometer in this ITP is found in section 3.2 which only states the ‘Piezometer is installed to the Geologists Satisfaction’ which does not cover the installation works suitably nor does the trail of documents present a workable identification of relevant test requirements. Root cause: In the first instance, the cause was due to administrative error and lack of responsability during issuing/signing of the above mentioned SNC. However this document was signed off by both __ and Crossrail reprensentatives.
| 02SL - Stations (LUL) | Cxxx-NCR-000187-L | NCR | Damage to Advance 33 Crown Primary layer 1.5m2 area |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-12-20 | 2012-12-17 17:18 | -3 | 2012-11-06 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The primary layer of shotcrete in AP7-E - pilot Adv. 33 has been knocked to the extend that an area of fairly green shotcrete on the previous advance fell down leaving the lining damaged by the Schaeff arm. This relates to Crown Lining while excavating Adv. 34. Root cause: Driver of Schaeff hit Crown area in advance 33 with Arm of excavator damaged the primary lining of Shotcrete in one uncareful move.
| 02SL - Stations (LUL) | Cxxx-NCR-000187-W | NCR | Drilling of Ground Investigation Boreholes CS1/1 & CS1/2 in CS1 |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-10-05 | 2012-09-28 07:59 | -7 | 2012-05-08 | Geotechnical Engineering - Ground Investigation | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | On the 6th & 7th March 2012 the drilling of BH CS1/1 & BH CS1/2 was undertaken in accordance with the Rev.2 WMS attached. The method of work used was not in accordance with Material and Workmanship Specification Sprayed Concrete Linings - clause KT20.3211.
| 02SL - Stations (LUL) | Cxxx-NCR-000188-L | NCR | Recording flow tests |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-04-12 | 2013-01-25 12:00 | -77 | 2012-11-27 | Tunnelling - Tunnelling General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | From the pour record sheet it could be taken that a technician has falsified testing records as, a flow test was carried at a given time but he was not actually on site. Root cause : It appears that a rogue individual may have breached company procedures and this is being dealt with through company disciplinary procedures.
| 02SL - Stations (LUL) | Cxxx-NCR-000188-W | NCR | Backfilling of the Albion Brewery Well - ITP item 2.1 not respected (Logger missing) |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-04-30 | 2012-08-09 13:18 | 101 | 2012-05-10 | Tunnelling - Grouting | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | From the commencement of grouting of the Albion Brewery Well until the 28thMarch 2012 the logger was not operational on-site while grouting continued.
| 02SL - Stations (LUL) | Cxxx-NCR-000190-L | NCR | Pins installation are installed in order to achieve the correct thickness |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-02-21 | 2013-01-25 12:27 | -27 | 2012-11-14 | Tunnelling - Linings - Sprayed Concrete | 500 |  | System Defect | Repair |  | Complete |  | Completed |  | Pins are installed sometimes to help achieve the right thickness because the automated Tunnel Beamer System cannot work due to interference with dust and being unsighted due to plant. The Tunnel Beamer System was developed along with the LaserShell process but like all automated systems is sometimes fallible. The pins installation is not described in the Method Statement or the relevant Risk Assessment. Root cause : The common practice of pins installation has not been described in the Risk Assessment and the Method Statement.
| 02SL - Stations (LUL) | Cxxx-NCR-000191-L | NCR | CP5 S Adv 6: Insufficient thickness of shotcrete |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-02-28 | 2012-12-12 14:05 | -78 | 2012-11-14 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | The thickness of the initial layer of Adv. 6 was 20mm instead of 75mm. Root Cause: - Nozzleman mistakenly sprayed less shotcrete on this area. - Insufficient measurements taken with the Beamer.
| 02SL - Stations (LUL) | Cxxx-NCR-000192-L | NCR | Toolbox items as per RESS are missing |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-01-18 | 2012-12-17 17:00 | -32 | 2012-11-14 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | The above toolbox items were not available on site as per RESS. Root cause : Relevant Toolbox items were not available on site and have been forgotten to be in place.
| 02SL - Stations (LUL) | Cxxx-NCR-000192-W | NCR | Shotcrete Sprayed not within mix design when sprayed (Temperature) |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-07-25 | 2012-08-20 15:54 | 26 | 2012-05-02 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Shotcrete that was batched and sprayed was 13 degrees Celsius and not the required minimum of 15 degrees Celsius as per specification KT20 3205
| 02SL - Stations (LUL) | Cxxx-NCR-000193-W | NCR | The berm en vertical wall was not sprayed as per RESS CS1/04 |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-07-25 | 2012-06-27 08:50 | -28 | 2012-05-02 | Shafts -Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | During the spraying of the initial layer problems were experienced with the batching plant therefore only enough shotcrete to finish the spraying of the initial layer was available. Further shotcrete was batched with required properties and operatives commenced spraying the primary layer without sealing of the exposed berm end vertical wall.
| 02SL - Stations (LUL) | Cxxx-NCR-000194-L | NCR | Missed flow Test CP5 - Advance 15 start of batch of Initial Layer |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-02-27 | 2012-12-14 16:17 | -75 | 2012-11-14 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | Missed flow Test Advance 15 Initial layer Batch # 466- 09.56am Root cause : No Lab technician available – so we were using our trainee engineer to test who had multiple jobs and we are one Shift engineer down, it was a communication problem as well a time issue that the engineer was not able to make the test which resulted in miss test results.
| 02SL - Stations (LUL) | Cxxx-NCR-000194-W | NCR | One FUKO hose has been installed instead of 2 required as per RESS CS1/04 |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-06-29 | 2012-05-16 21:28 | -44 | 2012-05-02 | Shafts -Sprayed Concrete | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | Due to running out of the FUKO hose only one line has been installed in the 5.0 m long section within the cutting edge in the last third of the advance 1
| 02SL - Stations (LUL) | Cxxx-NCR-000195-L | NCR | CP5 S adv 14: Invert over excavated by 950mm |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-02-15 | 2013-02-08 12:16 | -7 | 2012-11-15 | Tunnelling - Excavation - Hand | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Over excavation of CP5 - Advance 14 invert (910mm) into Advance 15. Adv. 15 invert over excavation into 16 (400mm). Leading edge line regained at advance 16 when mucking out ADV 17. Root cause : Beamer configuration and Uploading data Problems with the result of over excavation on Adv 14 & Adv 15. Lack of care and due diligence by all present at the working face. (Advance length of 1 m can be approximately estimated by all personnel, before the fine tune of profile with the Beamer is required).
| 02SL - Stations (LUL) | Cxxx-NCR-000196-L | NCR | Undermining Advance 14 Access Passage 7 - West (pilot tunnel) |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2012-12-14 | 2012-12-10 18:11 | -4 | 2012-11-16 | Tunnelling - Excavation - Hand | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The joint between the top heading/invert in Advance 14 during night shift on 7/11/2012 was constructed at a level of c.a. 77.3m (measured by Nathan), this constitutes undermining in level of c.a. 1.2m. This is in violation on the requirements of RESS AP7-W/03.
| 02SL - Stations (LUL) | Cxxx-NCR-000197-L | NCR | Time intervals for Early Strength Tests are not in accordance with the ITP requirements (1hr, 3hr, 6hr, 12 hrs) |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-02-20 | 2012-12-14 16:34 | -68 | 2012-11-20 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | In many cases, the Early Strength Test (Penetrometer and HILTI) is not performed on the specified intervals at 1hrs, 3hrs, 6hrs, 12hrs as required by the ITP for every 3rd Advance and the KT20 Spec. For evidence see sample J2 Curves attached hereby. Root cause : Lack of due care of engineers and lack of planning of on-going activities had caused the miss of some tests or performing the tests in different intervals than the specified ones.
| 02SL - Stations (LUL) | Cxxx-NCR-000197-W | NCR | Overspray to Bottleneck of Shaft CS1 |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-07-31 | 2012-09-27 09:25 | 58 | 2012-05-10 | Shafts -Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | At level 97.95m shaft primary lining is out of tolerance varying from -20mm to -40mm. At level 97.45m shaft primary lining is out of tolerance at -20mm. At level 96.66m shaft primary lining is out of tolerance varying from -10mm to -90mm. See attached as built surveys at above levels.
| 02SL - Stations (LUL) | Cxxx-NCR-000198-L | NCR | Incorrect revision of the Shotcrete placement Checksheet has been used for CP6-Adv.11,12,13 and 14 |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-02-22 | 2012-12-14 16:23 | -70 | 2012-11-22 | Tunnelling - Linings - Sprayed Concrete | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | Mistakenly the Shift Engineers have used Rev.2 of the Shotcrete Placement Checksheet D3-37 for Adv. 11,12,13 AND 14 of CP6. Root cause : Mistake on the print-outs by the Shift Engineers.
| 02SL - Stations (LUL) | Cxxx-NCR-000199-L | NCR | AP7-E Adv 37: Low Early Strength of shotcrete of invert primary |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-02-25 | 2012-12-17 17:08 | -70 | 2012-11-23 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | During the excavation of Adv 38 the excavator pulled up the primary of Adv 37 due to the lack of early strength. There are no panels tested for early strength because it has been agreed that only the initial layer will be tested (which is now changed and the primary is tested). Root cause: Not possible to identify the root cause at this case. There were no early strength results from this spraying. There has been no discrepancy on the relevant shotcrete tickets. Accelerator was at 6%. All of the J2 Curves before and after this spraying were ok (see J2 Curves attached).
| 02SL - Stations (LUL) | Cxxx-NCR-000199-W | NCR | Shotcrete Testing Shaft CS1 Adv 6 and 7 not complete and compliant |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-09-24 | 2012-08-22 13:06 | -33 | 2012-07-26 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Advance 6: - 1st primary lining (1 of 2) full record sheet not present. (Shotcrete test panel lost in the muck away) - 2nd primary penetrometer testing only completed to 30 minutes Advance 7: - 1st primary linings (both) penetrometer tests average taken over 5 instead of ten readings - 2nd primary lining 6 hour pull out test not conducted Root cause: Lack of understanding on the importance of the early strength shotcrete testing records being taken and safely kept by the engineers. Lack of information checking by the section engineers/shift team leaders on site allowing information to be omitted from the report sheets The lost panel was something which should not have occurred. It was viewed that safety would be improved by removing the panel from the shaft in the skip as opposed to using strops but the tipping of the skip at the top was something that was overseen until after the incident, when the panel could then no longer be re-located in the muck bin. Lack of communication between pit bottom and pit top.
| 02SL - Stations (LUL) | Cxxx-NCR-000200-L | NCR | LIS Early Strengths Issue: strength not reached |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-04-05 | 2013-02-04 15:58 | -60 | 2012-12-07 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | • CP6 Adv 9, 10, 13,16: Failure in achieving early strength J2 Curve. Panels sprayed for early strength testing showed that after 1 hour strengths had not reached 0.5N/mm2 or after 2 hours strengths had not reached 1N/mm² or after 6 hours strengths had not reached 3N/mm² . Root cause : •Awaiting issue of report from SCL Coordinator
| 02SL - Stations (LUL) | Cxxx-NCR-000200-W | NCR | Backfilling material not in accordance with MCR: Type 1 Material used to backfill utility trench not submitted for approval. |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-10-05 | 2012-09-28 15:25 | -7 | 2012-05-23 | Utilities Engineering - Water | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | A type 1 material has been submitted and approved in MCR :Cxxx-__M-C-RGN-CR092-50044. The type 1 material used to backfill the trench is not the same as the one approved in MCR :Cxxx-__M-C-RGN-CR092-50044 Root cause The sub contractor in charge of the work has not informed __ that they were using a different type 1 material to the approved one. The site engineer in charge of checking the material conformity failed to do so. The section manager in charge of the work hasn’t provided the site engineers with enough informations with regards to the implementation of inspections for the material.
| 02SL - Stations (LUL) | Cxxx-NCR-000201-L | NCR | Weighing Scales of microsilica showing incorrect values |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-03-08 | 2013-01-14 12:24 | -53 | 2012-11-29 | Civil - Civil Engineering General | 500 |  | Equipment Breakdown | Use As-Is |  | Complete |  | Completed |  | On 17/11/12, it has been observed that there was a big difference between the microsilica quantity value shown on the computer in the batching plant and the value that was in the silo. The automated weighing system has been calibrated. Root cause : The scale is calibrated through and the issue has not occurred again. A definitive root cause cannot be positively determined.
| 02SL - Stations (LUL) | Cxxx-NCR-000201-W | NCR | Not sufficient sealing 75 mm on top heading Adv.11 CP2 north enlargement. |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-12-05 | 2012-11-09 09:18 | -26 | 2012-09-05 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Face sprayed with only 30-40mm of shotcrete. Root cause: Shotcrete that was held in the remixer ran out and it was decided that to mix another 2 cubic meters to spray a further 30mm on the face was deemed a waste as the face would be mined forward after the invert (advance of 12) was completed. This was planned to be before the end of the shift.
| 02SL - Stations (LUL) | Cxxx-NCR-000202-L | NCR | RESS issued without accepted MS and ITP |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-01-31 | 2012-12-14 16:39 | -48 | 2012-11-28 | Tunnelling - Tunnelling General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | -The MS LIV WMS: LIV TUNNEL WELLPOINT INSTALLATION AND COMMISSIONING was submitted to Crossrail on 15/11/2012. -Required Excavation Support Sheet number CP5-S/06 (RESS) was issued on 16/11/2012. -MS was returned to __ as Code 2 with a caveat on 20/11/2012. -The caveat stated:- ''The MS and ITP 50032 is ONLY approved for the installation of well points. It requires a more fundamental revision to cover installation of the piezometers, protection of the piezometers and well points, decommissioning, recording of ground conditions including sampling requirements and auguring to determine those ground conditions.'' -On day shift 23/11/2012 shift 3 followed the RESS CP5-S/06 for the depressurisation boreholes and installed the piezometers.
| 02SL - Stations (LUL) | Cxxx-NCR-000202-W | NCR | Night Shift RESS Meeting did not take place |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-08-15 | 2012-05-31 11:34 | -76 | 2012-05-15 | Shafts -Sprayed Concrete | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | The night shift did not hold a SRG meeting that satisfied the points laid down in document clause - KT20.2108.
| 02SL - Stations (LUL) | Cxxx-NCR-000203-L | NCR | Calibration of waterfowl meter |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-01-31 | 2013-01-25 11:23 | -6 | 2012-11-29 | Civil - Tunnelling | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Calibration records were not made available for the waterfowl meter installed at the CPI silo. The meter is used to measure the amount of water added to the premix back up supply for sprayed concrete
| 02SL - Stations (LUL) | Cxxx-NCR-000203-W | NCR | Access Shaft - RESS CS1/09 - No Staggered Joint |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-07-25 | 2012-09-05 08:16 | 42 | 2012-05-15 | Shafts -Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | At level 94.64m the step in from the primary thickening 2nd layer to the Primary lining 2nd layer is sloped in at 45 degrees rather than stepped as detailed in the RESS No. 9. Root cause : RESS No.9 had been briefed to the sprayers but not in as much detail as was required. There was no discussion about the joint detail from the Primary lining thickening second layer to the primary lining second layer. As a result, the joint was sprayed in at a 45 degree angle to the face. The radial profile bar for the primary lining thickening second layer was set too low to get the step detailing as per the RESS and this was only picked up subsequently.
| 02SL - Stations (LUL) | Cxxx-NCR-000204-L | NCR | EuroMix product number |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-01-31 | 2013-01-09 09:45 | -22 | 2012-11-29 | Civil - Tunnelling | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | EuroMix delivery note dated 20/11/2012 product reference number is SPCONCROSSLPH with hand written addition “ 405__”
| 02SL - Stations (LUL) | Cxxx-NCR-000204-W | NCR | Access Shaft - RESS CS1/08 – Handspray carried without approval |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-11-30 | 2012-11-05 09:58 | -25 | 2012-08-30 | Shafts -Sprayed Concrete | 500 |  | Equipment Breakdown | Use As-Is |  | Complete |  | Completed |  | Both of the robotic spraying __’s were down with mechanical issues and mining for advance 8 commenced. This resulted in the need to hand spray the initial layer on the first half excavation. Slew broken on __ 1 (terminal) and so oscillating head from __ 1 was being exchanged with that on __ 2 to enable __ 2 to spray with the same head arrangement/accuracy. Oscillation on the head of the 2 robots was different. This exchange was not completed in time for spraying the initial layer to the first half. Root cause: Mechanical failure of the spraying robot. Delay in exchanging the oscillating heads of the robots lead to the requirement to hand spray.
| 02SL - Stations (LUL) | Cxxx-NCR-000205-L | NCR | Control of storage life SCL back up plant |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-01-31 | 2013-01-17 17:16 | -14 | 2012-11-29 | Civil - Tunnelling | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Contractor could not demonstrate that planned arrangements were in place to ensure material was used within two months from delivery date shown on the delivery ticket
| 02SL - Stations (LUL) | Cxxx-NCR-000205-W | NCR | Sainsbury Car Park Column Jacking - 5mm lift deviation on column A3 |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-08-31 | 2012-08-14 10:48 | -17 | 2012-05-22 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Column A3 has been lifted at 11:45 pm on Wednesday 17th May. The records of the dial gauges shows a 15.47 mm lift The day after the jacking was done, the survey of the column showed a 10.2 mm lift which is not compliant with the 15mm requested
| 02SL - Stations (LUL) | Cxxx-NCR-000206-L | NCR | Calibration of stud pull out measurement equipment |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-01-31 | 2013-01-25 11:29 | -6 | 2012-11-29 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Hilt pull out measuring device HAT 28 serial number 010319 was not included in the calibration schedule and current calibration record was not made available for inspection during CRL surveillance of 28th November 2012.
| 02SL - Stations (LUL) | Cxxx-NCR-000207-L | NCR | TAM Drilling: GAD1 CH38, 39, 40 out of tolerance |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-03-29 | 2013-01-15 14:14 | -73 | 2012-12-03 | Geotechnical Engineering - Compensation Grouting | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Boreholes GAD1CH38, GAD1CH39 and GAD1CH40 are out of tolerance after 55 meters of drilling. Root cause: Boreholes out of tolerance on elevation.
| 02SL - Stations (LUL) | Cxxx-NCR-000209-L | NCR | CP6 advance 16 insufficient thickness of shotcrete |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-01-31 | 2013-01-17 12:36 | -14 | 2012-12-04 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Thickness survey report documents significant area where the minimum thickness was not achieved - measurement were 215, 222, 213 and 245 mm
| 02SL - Stations (LUL) | Cxxx-NCR-000211-L | NCR | Drilling and installing of inclinometer casing |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-03-29 | 2013-02-08 12:32 | -49 | 2012-12-19 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Planning | Reject |  | Complete |  | Completed |  | Casing was installed to a depth less than 50m (actual depth 47m). Root cause : Due to a rig break down and co-ordination the borehole was left with rods inside longer than would be desirable. This could have caused collapse or sediment build up creating problems with installing inclinometer casing..
| 02SL - Stations (LUL) | Cxxx-NCR-000211-W | NCR | Bore Hole Methodology Issue: BH905, 906, 905A, 906A, 907 & 908. |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-08-31 | 2012-08-15 10:25 | -16 | 2012-05-23 | Civil - Geotechnical Engineering | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | Several issues occurred during drilling of boreholes in CS1. - BH905, 906 were abandoned and backfilled. - BH905A was drilled to 25m then re-drilled. - BH906A & BH907 were drilled and water ingress made further drilling problematic. - BH906A & BH907 were back grouted then drilled to full depth.
| 02SL - Stations (LUL) | Cxxx-NCR-000213-L | NCR | Insufficient Thickness of Shotcrete on Adv 1 Pilot Tunnel CP5-South |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-04-30 | 2013-04-25 17:02 | -5 | 2012-12-20 | Tunnelling - Linings - Sprayed Concrete | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | During the construction of CP5 Adv.1 – Enlargement the pilot tunnel was found out to have significantly less thickness than 250mm. The issue was reported by both __ SCL Inspector and CRL Inspector Denis McElroy. Due to Safety reasons it was not possible to take a picture at that moment. CRL inspector’s email describes the situation quite clear. The records of the profile did not show any non-conformity at the moment of spraying. Root cause : The root cause cannot be specified now. The most important issue is to identify why the Beamer Profile showed that the thickness was ok.
| 02SL - Stations (LUL) | Cxxx-NCR-000214-L | NCR | Face Support Safe Stop (additional 75mm SCL) Adv 11 on CP5 not carried out at backfill level |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-03-22 | 2013-01-25 11:07 | -56 | 2012-12-18 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | The safe stop was carried out only on above backfill level. The invert did not get 75mm extra face support for the safe stop as backfill was done prior to this.
| 02SL - Stations (LUL) | Cxxx-NCR-000215-L | NCR | Shotcrete Batching Plant not ready for emergency production of shotcrete |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-03-22 | 2013-02-08 12:58 | -42 | 2012-12-18 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Equipment Breakdown | Use As-Is |  | Complete |  | Completed |  | During the night shift Friday 14/12/12 the concrete pump in the batching plant stopped working. The second pump could also not be started. Both pumps had been working at the start of the shift. The third pump was waiting for parts. To seal the face the CPI mix was used. This was sent down the shaft ins skips to be sprayed on the face. Root cause : First pump was down to earth on the cable and the timer on the delta had to be replaced. The second pump had had an emergency stop activated. This is an additional emergency stop that the electricians and the operators were unaware off and is located in such a position that it has not been noticed before This emergency stop was not included in the training provided by Schwing concrete pumps.
| 02SL - Stations (LUL) | Cxxx-NCR-000216-L | NCR | Shotcrete cube strenghts |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-03-07 | 2013-01-17 12:42 | -49 | 2012-12-19 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The observation was that the cubes no C0846 were not covered with hessian cloth or polyethylene sheet in order to keep them moist and wet. Root Cause: Technician did not cover the cubes at the time as they were recently made and didn't want to damage to surface of the samples.
| 02SL - Stations (LUL) | Cxxx-NCR-000217-L | NCR | CP5 Enlargement Adv. 3: Shotcrete did not achieve the required early strength |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-05-03 | 2013-05-03 06:16 | 0 | 2012-12-20 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | • The primary layer of shotcrete in CP5 Enlargement - Adv. 3 did not achieve the required early strength at 3 and 4 hours. • The result was not recorded on the J2 Curve diagram Root cause : • The root cause cannot be identified specifically for this batch. All the records that have been checked seemed ok (batching tickets, flow test etc). The issue of not achieving the required early strength is part of another investigation, as well (and other NCRs). • The result was not recorded because of negligence by the Engineer.
| 02SL - Stations (LUL) | Cxxx-NCR-000218-L | NCR | Drilling of boreholes GAD1CH38r, 39r and 40r |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2013-10-25 | 2013-08-23 14:59 | -63 | 2013-01-17 | Human Factors - Human Factors General | 5000 |  | Workmanship | Use As-Is | 3 (3-6k) | Complete | External Phenomenon - Other | Completed |  | Boreholes GAD1CH38r has been drilled to 72m and is within Moorgate Floodgate Chamber grouting exclusion zone after 55m Boreholes GAD1CH40r has been drilled to 61m and is within Moorgate Floodgate Chamber grouting exclusion zone after 55m Borehole GAD1CH39r has been drilled to 55m, but was found to be too far out of tolerance at that point and so has been backfilled and TAMs have not been installed. Root cause: Boreholes out of tolerance on elevation/plan view.
| 02SL - Stations (LUL) | Cxxx-NCR-000219-L | NCR | Damage on the conveyor belt steel structure by the excavator |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-04-05 | 2013-01-29 12:53 | -66 | 2012-12-20 | Civil - Civil Engineering General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | Operative was slewing with 20t excavator in the muck bin area when he hit the brace linking GTU and Conveyor belt. 2 muck skips were unloaded on the belt after that incident. Visual damage can be seen on the brace. The issue has been reported in RIVO as a property damage (see attached). The issue also reported as an NCR because of the rectification works that need to be done on the Conveyor Structure. Root cause : Inattention of the driver – misjudgement of excavator arm position.
| 02SL - Stations (LUL) | Cxxx-NCR-000219-W | NCR | Borehole WH57 issue |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-09-06 | 2012-08-20 09:17 | -17 | 2012-05-31 | Geotechnical Engineering - Ground Investigation | 500 |  | Equipment Breakdown | Rework |  | Complete |  | Completed |  | Borehole WH57 was not drilled to required depth. Drilling stopped at 35.8 mbgl due to a pump breakdown (see __ WH57 driller's log). Piezometer has been installed, but drill barrel disturbed standpipe on removal of casing. After the pump has been repaired the borehole has been redrilled in the same place to required depth at 40 mblg and piezometer reinstalled as foreseen. See final borehole log of __ (WH57_2012_05_15 Log __ (TA6285)). Root cause : Pump breakdown.
| 02SL - Stations (LUL) | Cxxx-NCR-000220-W | NCR | Shotcrete sprayed not within mix design when sprayed (Flow & Temperature) |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-10-04 | 2012-09-04 16:01 | -30 | 2012-05-31 | Shafts -Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Shotcrete that was batched and sprayed on 25/04/12 for use in WHI CS1 advance 1 had a flow of 490mm Shotcrete that was batched and sprayed was 14.1 degrees Celsius and not the required minimum of 15 degrees Celsius as per specification KT20 3205 Root cause : Inconsistent flows achieved as it batchers getting used to the new system. Hot water was not used in the mix as it was seen to take longer and there was no perceived issue with the temperature (ambient). Engineers not checking the mix prior to its use allowed the “cold” mix to be used.
| 02SL - Stations (LUL) | Cxxx-NCR-000221-W | NCR | Thrust block to restrain 15” water main in Whitechapel road footpath not constructed as per design |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-09-09 | 2012-08-14 10:55 | -26 | 2012-05-31 | Utilities Engineering - Gas | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | The thrust block hasn’t been poured according to the drawing dimensions. Thrust block not compliant with design. Root cause: The construction team has assessed the available space to cast the thrust block The information has been passed onto the design team and they have issued a design taking into consideration all available space. When the construction team started to build the thrust block, it has been found that a collar of the 15” water main was restricting the area more than expected as it had to remain accessible for the future works. The main cause for this NCR is that the available space to construct the thrust block and then replace the pipe hasn’t been assessed properly.
| 02SL - Stations (LUL) | Cxxx-NCR-000223-L | NCR | Contaminated Compensating Grouting Mix |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-04-26 | 2013-04-25 15:22 | -1 | 2012-12-21 | Geotechnical Engineering - Compensation Grouting | 500 |  | Material | Reject |  | Complete |  | Completed |  | Delivery of contaminated (with gravel) G20 grouting material has been delivered on site on Wednesday 19/12/2012. The material has been loaded form the truck to the silo, the fresh grout tests were ok but the issue has been identified because the gravel has blocked the pipes, the pumps and the equipment of __. The incident has occurred one time in WHI in the past. Root cause : Supplier delivered on site contaminated material. Insufficient Quality Control of the supplier upon loading the trucks.
| 02SL - Stations (LUL) | Cxxx-NCR-000226-W | NCR | Injection of Grout without Sufficient Bentonite Content in TAM 13 & 59 During Pre-Conditioning Grouting Works |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-09-28 | 2012-08-07 19:12 | -52 | 2012-06-14 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The first batch of grout to be injected for the pre-conditioning works was mixed with the following proportions: Water 575L Pre-blended Portland cement/Bentonite 1150kg. TAM 13 Sleeves 30 & 35 and TAM 59 Sleeves 04, 08 & 12 were injected using this non-conforming grout mix. Root cause : The site management did not communicate instructions clearly to site operatives.
| 02SL - Stations (LUL) | Cxxx-NCR-000227-W | NCR | No early strength tested of the shotcrete of the advance 15 of CS1 |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-09-24 | 2012-08-08 19:15 | -47 | 2012-06-14 | Shafts -Sprayed Concrete | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | No early strength tested (penetrometer test) for advance 15. Root cause: The reason for not carrying the penetrometer test was that the engineering team could not find available penetrometer needle. There were 2no needles on site but in the place they are not usually stored and at that time unknown to the engineering team.
| 02SL - Stations (LUL) | Cxxx-NCR-000228-W | NCR | Insufficient amount of A393 mesh on site for slab construction |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-09-27 | 2012-08-30 15:41 | -28 | 2012-06-14 | Shafts -Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | During the installation of the mesh it was realised that there was insufficient amount of A393 mesh on site. Root cause: The additional mass infill and mesh detail was shown on revision C7 of the latest reinforcement drawings, this revision stated the required overlap being 950mm whereas on previous issues (C6) there was no mention of required overlap. Revision C7 was officially issued on the 12/06/12 one day before the concrete pour. The A393 mesh was ordered before this drawing was issued and the quantity ordered was assumed using the standard 400mm overlap on the mesh.
| 02SL - Stations (LUL) | Cxxx-NCR-000230-W | NCR | Shotcrete fall out above the Eye in the shaft CS1 |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-07-25 | 2012-08-10 17:40 | 16 | 2012-07-18 | Shafts -Sprayed Concrete | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | On Saturday 26.05.2012 at 05:38 a small area of fresh sprayed shotcrete fell out after a minute, then slowly a section approximately 2x3x0.1 = 0.6m3 with an approximate weight 1.4Tonnes came away from the lining falling to the ground. Before and during the spraying the face was jet washed and inspected. The spraying was done per hand, 2 certificated nozzleman were doing the work. The accelerator line was flushed at the start of the spraying and the accelerator tank was full. For the spraying a rate of 4.5%-5% accelerator was used. All Tests and checks according the ITP was done and passed. (early strength, flow table etc). Root cause: Possible lack of accelerator to the mix, but cannot be confirmed with evidence.
| 02SL - Stations (LUL) | Cxxx-NCR-000231-W | NCR | Temporary Invert to top heading Adv 2 not ‘dished’ |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-12-10 | 2012-11-09 09:21 | -31 | 2012-09-10 | Tunnelling - Excavation - TBM | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The temporary invert was excavated flat due to the constraints of constructing the transition and breaking the Pilot Tunnel South. Root cause: When excavating the top heading the pilot tunnel was being broken down at the same time. The breaking process created an over excavation down in the vertical plane on the knees of the heading.
| 02SL - Stations (LUL) | Cxxx-NCR-000232-W | NCR | Breakout of Advance 1 CP2 N Enlargement was not excavated to a min of 75mm |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-11-09 | 2012-09-06 11:18 | -64 | 2012-08-09 | Tunnelling - Tunnelling General | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | During the breakout of the enlargement eye one of the thickening reinforcement bars was damaged on the left hand axis of the eye. (See report showing damage to Rebar) From this point on we instructed the team to only excavate +50mm not +75mm as stated in the RESS Root cause: The steel for the eye was installed with a cover of 50mm. There over excavation of the tunnel eye was specified as +75mm minimum. This created the clash.
| 02SL - Stations (LUL) | Cxxx-NCR-000234-W | NCR | Underspray thickness of the primary thickening Layer |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-08-31 | 2012-08-03 17:23 | -28 | 2012-07-06 | Shafts -Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | At level 85.67m shaft primary lining thickening is partially only 370 / 380 mm sprayed. At level 84.86m shaft primary lining thickening is partially only 380mm sprayed. At level 83.97m shaft primary lining thickening is partially only 360 – 390 mm sprayed. At level 82.85m shaft primary lining thickening is partially only 330-390 mm sprayed. Root cause: The horizontal profile bars had been set out and checked by the shift engineers. The nozzleman / leadminer sprayed too less shotcrete between the profile bars. It appears to be a miss understanding.
| 02SL - Stations (LUL) | Cxxx-NCR-000235-W | NCR | Works without IFC TW design - supporting frame to secatol tanks under mixer |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-10-31 | 2012-09-03 10:06 | -58 | 2012-08-15 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Works being carried out despite no IFC drawing was issued. In addition to that, changes were agreed verbally only between TW Dpt and Site Engineering Team but never formulated in time by a clear sketch or drawing. 1-When concrete was being poured, no drawing clearly approved by TW had been issued. 2-Changes to steel reinforcement were only agreed verbally but not formally stated between TW and Site teams at moment of concrete pour 3-The sketch related to construction changes drawn and approved by TWC, have been issued too late and didn’t let the Quality Inspection Team go on site check details in time because the concrete was already being poured. In parallel, CRL as witness in ITP has not been informed. Root cause : Changes were agreed several days before concrete pour between TW Dpt and Site Engineers, but never formalized, and no new drawing / sketch have been issued and approved accordingly. This concern has been dealt with too late considering the urgency of this construction works and it did not give any time for an inspection by the Quality Team. Decision then made to provide an as-built drawing approved by TWC.
| 02SL - Stations (LUL) | Cxxx-NCR-000236-W | NCR | Installation of Peri staircase and bracket installation without ITP |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-11-14 | 2012-08-17 16:28 | -89 | 2012-08-16 | Civil - Civil Engineering General | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | Works on the installation of the brackets and subsequent peri staircase into the shaft for access started before a signed code 1 ITP had been received from the client (Cxxx-__M-C-ITP-D061-50055 ITP Shaft Stair Installation Rev 2.0). Root cause: Planning for the installation of the staircase in the shaft had been on going and the ITP had been over looked. Works progressed with the installation of the staircase into the shaft whilst a modification to the batching plant was being carried out, so there was no mining being undertaken.
| 02SL - Stations (LUL) | Cxxx-NCR-000240-W | NCR | Primary lining to CP2 North enlargement Adv 1 not sprayed in two stages. |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-11-09 | 2012-10-05 13:13 | -35 | 2012-08-09 | Tunnelling - Tunnelling General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | During the installation of Primary 1 on Adv 1, the entire Primary Lining Thickness of 225mm (150mm Primary 1 and 75mm Primary 2)was sprayed in one go. Root cause : •There should have been 4 beamer profile files generated for CP2 N Enlargement: Excavation, Initial, Primary 1 and Primary 2. •There was only 3 beamer profiles produced: Excavation, Initial and Primary. Which failed to identify the split of the Primary Lining into 2 stages. •When the engineers were setting out the primary lining profile they set out with the only profile in the beamer which resulted in the full thickness being sprayed.
| 02SL - Stations (LUL) | Cxxx-NCR-000241-W | NCR | Rebound exposed in joint of Adv 21/24 |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-11-19 | 2012-11-09 09:12 | -10 | 2012-09-03 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The leading edge of Adv 21, which was the lower section of the ‘cods mouth’ enlargement, was exposed and broken back when continuing forward with Adv 24, the next lower section. Once exposed, layers of rebound were found in the knees on both sides. This was broken back to solid lining approximately 400mm in the knee sections and the next advance continued. (See extract of drawing attached) Root cause : •This was the first section of the large ‘elephants foot’ profile in the knees and as such large amounts of rebound were generated and collected at the face. Whilst the operatives were observed to be cleaning as they sprayed, not enough was being done to prevent this in these two localised areas. •The rebound built up and was caught in the SCL at the leading edge of the advance.
| 02SL - Stations (LUL) | Cxxx-NCR-000242-L | NCR | Contaminated bags of Reader Grout G20 |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-04-20 | 2013-04-17 16:49 | -3 | 2013-01-10 | Geotechnical Engineering - Compensation Grouting | 500 |  | Material | Reject |  | Complete |  | Completed |  | The bags of G20 Reader Grout that were delivered on both sites (WHI and LIV) on 9th of January 2013 , did not have dry powder form and but more like sand form. As a result the material blocked the equipment of __. Root cause : The supplier provided nonconforming Grout
| 02SL - Stations (LUL) | Cxxx-NCR-000242-W | NCR | Shotcrete placement checksheet incorrectly completed |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-11-30 | 2012-09-27 11:13 | -64 | 2012-09-03 | Shafts -Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | First layer thickening on the east and west side of CS1 completed without correctly filling in the shotcrete placement checksheet. Root cause: Engineers were under the impression that the onsite lab taking shotcrete flows/temperatures and cubes was sufficient for the reporting process. Lab tickets were being stapled to the reverse of the shotcrete placement checksheets.
| 02SL - Stations (LUL) | Cxxx-NCR-000243-L | NCR | Installation of kwikastrip reinforcement continuity strip type M15s, Double Rebar 12mm/150 |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-04-19 | 2013-02-18 16:20 | -60 | 2013-01-17 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Horizontal gap between sets of kwikastrip (in Advance 1 referring to RESS No. CP5 - S / 12) Kwikastrip at incorrect position (Advance 1, left hand side, kwikastrip near by the face), interior pullout bars when bended would not have been embedded in the Primary Lining of the permanent Invert. Root cause : Not installed properly and mistake
| 02SL - Stations (LUL) | Cxxx-NCR-000243-W | NCR | CRL Observation 30: backfilling to shaft CS1 undertaken without signed off SNC. Cxxx-__M-C-CCN-50032 |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-07-25 | 2012-09-05 08:36 | 42 | 2012-07-11 | Shafts - Shafts General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Start of the Work without signed SNC Cxxx-__M-C-CCN-D061-50032 After a chat with the Site Management and the Crossrail representative, I got the Information the SNC is approved and only the formal Sign and the back sending to __ is missing. The Backfill is only a temporary construction help, so we started the backfill to push the work forward and save Costs for standstill. Root cause: For the backfilling of the shaft the responsible PIC (Peter Punzengruber) give the order to start the backfilling of the shaft without signed SNC
| 02SL - Stations (LUL) | Cxxx-NCR-000244-L | NCR | Compliance to RESS – CP5-05/12 – Adv. 2 Stage 2 not done (Excavation was done at one stage and not at 2 stages) |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-04-19 | 2013-02-18 17:04 | -60 | 2013-01-18 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | RESS – CP5-05/12 Advance 2 stage 2 not completed / overlooked. instead of excavating in 2 stages (firstly 1.5m deep and then the rest as it is stated in the RESS) the excavation was done at one stage. Advance 2 was excavated at once and then sprayed initial and primary. Root cause : The site team judged there was no danger from the excavated trench because the depth of the trench is less on the first 2 advances as it can be seen from the RESS sketch because of the inclination. It was decided on the spot to continue like that.
| 02SL - Stations (LUL) | Cxxx-NCR-000244-W | NCR | New welfare / office construction commenced without authorised ITP |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-07-27 | 2012-09-07 11:09 | 42 | 2012-07-08 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | Work to install new welfare and office 3 units at Whitechapel had commenced before revision one of Cxxx-__M-C-ITP-D061-50053 associated with this activity had been reviewed by CRL. Subsequent review of ITP classified it at code 3.
| 02SL - Stations (LUL) | Cxxx-NCR-000245-L | NCR | CP5-e: The SCL profile was remediated without prior acceptance of the remediation proposal |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-07-12 | 2013-06-14 14:27 | -28 | 2013-01-21 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | On Monday 14th of January, the ‘tight’ or oversprayed areas of CP5 Enlargement have been trimmed (advances trimmed of CP5 are: 11, 13, 14, 16, 19, 28, 29 and the headwall) in order to meet the tolerances specified in the specs. Apart from the SRG Meeting agreement there hasn’t been any record of identifying the non-conforming situation and consequently there was no notification for the remedial works (trimming) that took place. Root cause : The decision has been taken quickly in the SRG (see attached) and the trimming has been carried out by the Shift Production Team almost immediately. This didn’t give enough time to the Quality Teams to record the issue. However, it should have been recorded properly if there was proper coordination of all the teams on this case.
| 02SL - Stations (LUL) | Cxxx-NCR-000246-L | NCR | __ do not hold ISO 9001:2008 certification |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-04-26 | 2013-04-26 12:01 | 0 | 2013-01-21 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | __ are the 2nd tier subcontractor (via __) responsible for the structure, i.e. excluding all M&E, for the Finsbury Circus muck conveyor. __ and their associates have acted as Designer, Checker, Fabricator, and Installer for the conveyor structure. __ are a subcontractor of __. __ do not hold ISO 9001:2008 certification. Root cause : • System failure: __ did not comply with this requirement. It is probably due to miss coordination between several departments (Engineering, Temporary Works, Commercial and Quality). __ was assessed as competent but no dispensation was requested to Crossrail (RFI).
| 02SL - Stations (LUL) | Cxxx-NCR-000246-W | NCR | SCL insufficient thickness on CP North Adv 7/8/9 as per core taken |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-10-31 | 2012-10-18 12:11 | -13 | 2012-07-26 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Cored samples taken from the CP2 North Pilot Tunnel show an area on the left hand axis of Adv 8 was less than 250mm. The beamer profile reports had data missing from this area. Root cause : •Localised thin area of SCL, poor workmanship in setting out the excavation and primary lining profiles. •Learning curve for new tunnel and workforce.
| 02SL - Stations (LUL) | Cxxx-NCR-000247-L | NCR | Conveyor: No ITPs to cover the off site manufacturing process |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-04-26 | 2013-04-26 12:08 | 0 | 2013-01-22 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | There were no ITPs to cover the off-site manufacturing process of the conveyor at Liverpool Street. Root cause : • It was not believed to be necessary for the conveyor manufacture to have an ITP. With hindsight this may have been incorrect.
| 02SL - Stations (LUL) | Cxxx-NCR-000247-W | NCR | Material Compliance Records (MCR) not Submitted for water mains strengthening |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-12-10 | 2012-10-23 12:57 | -48 | 2012-09-10 | Utilities Engineering - Water | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | Part of material used in the water strengthening works hasn't been submitted as MCR. Root cause: In most of the cases, the exact type of material to be used can only be determined once the configuration of the existing pipe is assessed, which is only feasible once the trench is open. When the original design cannot be implemented, the type of material used is defined in RFI. Submit MCR and wait for them to be approved prior to carry out the works would have a considerable impact on the programme and delay the over all project.
| 02SL - Stations (LUL) | Cxxx-NCR-000248-L | NCR | Excavation started before water level reaches specified point |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-04-24 | 2013-03-05 16:32 | -50 | 2013-01-25 | Tunnelling - Excavation - Hand | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Invert broken out (advance 5 CP5 Enlargement) before water level reached 72.5m as agreed in the SRG Meeting of 23.01.2013. Root cause : Water level was dropping very quickly at the start of the shift and it was believed that the required level would be reached before breaking out had gone further than locating the kwikastrip. Water level failed to go below 72.2m but break out of invert was completed.
| 02SL - Stations (LUL) | Cxxx-NCR-000248-W | NCR | Hold point to inspect the bolt torque of the fittings missed |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-10-25 | 2012-08-20 09:26 | -66 | 2012-07-25 | Utilities Engineering - Water | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | On Sunday 22nd July, the pipe flange connecting the 180 mm in Durward Street to the 90 mm in Winthrope Street has not been inspected by CRL and the pipe has been backfilled to allow Cxxxaccess to their site the Monday after. No IRF was issued to CRL to announce this inspecion was due. Root cause: Friday morning , CRL has been made aware verbally of this hold point for Sunday morning and a meeting was arranged Sunday morning with CRL field engineer. The field engineer finally didn’t work on Sunday, and the CRL representative who replaced him hasn’t been able to contact __ utility engineer who was not working on Saturday to fix the appointment. Being conscious that this was a hold point, but also that the road had to be reinstated for Monday, the team has decided to video the tightening of the bolts and present it to Thames water Representative The root cause is a defect in the communication between __ and CRL and a lack of communication with regards to the availability of all persons involved in the inspection process.
| 02SL - Stations (LUL) | Cxxx-NCR-000249-L | NCR | Initial Shotcrete Profile of CP6-Adv.17 Enlargement did not achieve 75mm thickness |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-04-30 | 2013-04-18 16:23 | -12 | 2013-01-29 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Thickness of the shotcrete profile of Adv. 17 on CP6 was less than 75mm (see attached beamer profile). Root Cause: Mistake during spraying.
| 02SL - Stations (LUL) | Cxxx-NCR-000250-L | NCR | CP6-e Adv 30: More than 700mm of kwikastrip was left for construction joint continuity purposes |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-04-30 | 2013-04-29 17:06 | -1 | 2013-01-30 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | There has been more than 700mm kwikastrip left on the left side of Adv.30, leaving the Adv. 29 with insufficient support below. See beamer measurement, photos and sketch. Root cause : Usually the site teams leave ~300mm for continuity of the joint. On this case, there has been a misjudgement of the mining gang and more than 700mm was left.
| 02SL - Stations (LUL) | Cxxx-NCR-000251-L | NCR | Installation of piezometers started without approved WMS and ITP |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-05-03 | 2013-04-24 15:13 | -9 | 2013-01-30 | Tunnelling - Tunnelling General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | The set-up of the installation of piezometers on CP6 started on the 13th of January without having approval from Project Manager. __ and WJ proceeded on the preparatory works (setting out- drilling) before the ITP being approved. See attached Documents Log extract. Root cause : Bad planning and coordination from the Site teams.
| 02SL - Stations (LUL) | Cxxx-NCR-000254-L | NCR | Batching Plant Automatic weighing system showing incorrect values |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-05-10 | 2013-05-07 16:10 | -3 | 2013-02-04 | Tunnelling - Tunnelling General | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | The scale of the weighing system of microsilica of the Batching Plant at LIV was showing incorrect measurement of approx. 14 tons while the tank was almost empty. The production stopped and an additional order of microsilica had to be placed. Root cause : The scale of microsilica is showing incorrect measurements due to some build-up in the storage tanks. The scales are all calibrated.
| 02SL - Stations (LUL) | Cxxx-NCR-000255-L | NCR | Failure to take results at 1, 3 & 6 hours on AP7-East Pilot - Adv 62 & to conform to the required testing frequency (every 3 advance) |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-06-21 | 2013-06-14 14:44 | -7 | 2013-03-15 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | - As it can be seen from the attached J2 Curve, the Site Teams missed to perform the Early Strength Test on the 1st ,and on the 6th hour (the test on the 3rd hour was actually performed on the 4th hour ). - The previous Early Strength testing was performed on Advance 58 (not complying with the requirement of one test every third Advance as per ITP). Advance 61 should have been tested instead. Root cause : Bad coordination and communication between the different shifts.
| 02SL - Stations (LUL) | Cxxx-NCR-000255-W | NCR | Gas mitigation work commeneced without accepted ITP |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-08-31 | 2012-09-13 10:14 | 13 | 2012-07-26 | Utilities Engineering - Gas | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | ITP Cxxx-__M-C-ITP-D061-50038 was accepted by CRL on 28.03.12, by which point gas mitigation work had already commenecd.
| 02SL - Stations (LUL) | Cxxx-NCR-000256-L | NCR | AP7-West Pilot: Non Adherence To RESS |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-04-16 | 2013-03-05 16:48 | -42 | 2013-02-11 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Whilst constructing adv 26 of AP7 pilot west on nightshift 09-10/02/13 the 75mm Initial and the 175mm Primary were sprayed in the Invert prior to applying the 75mm Initial Lining spray to all exposed surfaces (the face and the crown were not sprayed). This does not adhere to the stages outlined in the RESS (stages 01-05). Root cause: Sprayers and Shift Engineers deviated from the discipline of the RESS thus shortcutting the stages.
| 02SL - Stations (LUL) | Cxxx-NCR-000256-W | NCR | Local over-excavation of Adv 22 Cross Passage 2 South |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-10-29 | 2012-08-28 16:17 | -62 | 2012-07-27 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The face was excavated in places between 300mm and 500mm big (over excavated). Root cause: • Human error. Engineer got the +/- on the tunnel beamer the wrong way around and instructed further excavation believing a further 3000mm to be excavated. When taking the next shot he noticed that the value had increased and not decreased and realised his error.
| 02SL - Stations (LUL) | Cxxx-NCR-000257-W | NCR | Reinforcement installation on the headwall of CP2 North as not pre drawing |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-01-07 | 2012-12-17 12:47 | -21 | 2012-10-05 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | •Extra vertical 16mm NF1 lap bars have been added and spliced to the 8mm NF1 bars, BM 410a to t. This was done to ensure there was enough bar available to achieve a 350mm lap (as specified on the design) after spraying phase 3 of RESS CP2 – N/14a. These bars have been added onsite and not as part of the FCD process. Root cause: •Phasing of the steel layers (near face and far face) and the phasing of the spray areas on RESS sheets do not match up accurately enough. Additional bars were needed to comply with the 350mm lap length specified on the design after spraying phase 3.
| 02SL - Stations (LUL) | Cxxx-NCR-000258-L | NCR | GAD1&2: Early strength curves below J2 Curve or not recorded on proper timings |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-05-31 | 2013-03-10 16:40 | -82 | 2013-02-19 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Early strength Curves in many cases were below J2 Curve or not recorded at all on proper timings during the SCL activities of GAD1 & 2. See attached summary table and sample nonconforming J2 Curves. This NCR summarizes all of these cases and it is issued after the works completion in order to record the issue for the Certification Packages L068 and L069 at LIV. Root cause : Early stages of Project. Production and Quality Control Teams were not familiar with the relevant ITP requirements and in many cases, tests were missed. Root cause of low early strength of CPI Silo mix is difficult to be traced now. However, preventive measures such as regular follow-up of expiry dates of CPI Mix (discussion in weekly progress meetings), frequent surveillances by __ and finally the use of CPI Mix only as an emergency sealing-face measure , have reduced the risk of facing strength problems during the permanent works. Any other issues for the P1 or P2 Mix have been addressed and followed up with other NCRs.
| 02SL - Stations (LUL) | Cxxx-NCR-000258-W | NCR | start works without accepted ITP (Albion Brew) |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-08-31 | 2012-09-27 08:04 | 27 | 2012-07-27 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | The ITP to support the asbestos removal activities in the Albion Brewery basement to facilitate I&M installation was accepted by CRL on 06.12.11, by which point the works had already commenecd (25.11.11).
| 02SL - Stations (LUL) | Cxxx-NCR-000259-L | NCR | Flow was out of specs during the SCL activities of GAD 1 & 2 |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-05-31 | 2013-03-05 16:10 | -87 | 2013-02-19 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | In many cases (as it can be seen from the attached summary table) the flow of the CPI Silo Mix that was used during the GAD1 & 2 Construction was out of the range of 530-660mm. This NCR summarizes all of these cases and it is issued after the works completion in order to record the issue for the Certification Packages L068 and L069 at LIV. Root cause : Early stages of Project. Production and Quality Control Teams were not familiar with the relevant ITP requirements.
| 02SL - Stations (LUL) | Cxxx-NCR-000260-L | NCR | Curing concrete compressive test specimens |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-03-29 | 2013-03-06 09:14 | -23 | 2013-02-13 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | During surveillance of 30th January 2013 Cubes and cores were stored in the site laboratory without protection form dehydration.
| 02SL - Stations (LUL) | Cxxx-NCR-000260-W | NCR | silica fume manufacturer approvals and periodic on site monitoring |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-08-21 | 2012-08-17 16:25 | -4 | 2012-08-07 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | above not implemented
| 02SL - Stations (LUL) | Cxxx-NCR-000261-L | NCR | Cores stored in the site laboratory were not marked |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-03-29 | 2013-03-06 09:51 | -23 | 2013-02-13 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Cores stored in the site laboratory seen during surveillance of 30 January 2013 were not marked
| 02SL - Stations (LUL) | Cxxx-NCR-000262-L | NCR | Early Strength Gain Values / Needle Test for up to 1h |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-05-24 | 2013-05-07 16:39 | -17 | 2013-02-15 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | CP5 and CP6 (Pilot + Enlargement), AP7 Pilot (Until 15/02/13): Early Strength Curve (Penetrometer) for CPI Silomix (Blue Line) was used for site batched mix (Red Line). Root cause : • Early strength curve calculation tested & modified for CPI dry silo mix was used for self-batched wet mix after batching plant went to work (start from pilot tunnel CP5).
| 02SL - Stations (LUL) | Cxxx-NCR-000262-W | NCR | Change to specified requirements |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-10-31 | 2012-10-05 12:50 | -26 | 2012-08-08 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | During surveillance of 31/07/2012 the Contractor undertook to implement the above requirement with respect to the maximum storage temperature for silica fume. The undertaking was not implemented by the 8/08/2012
| 02SL - Stations (LUL) | Cxxx-NCR-000263-L | NCR | Installation of kwikastrip reinforcement continuity strip type M15s, Double Rebar 12mm/150 |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-05-24 | 2013-04-29 09:41 | -25 | 2013-02-18 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Kwikastrip at incorrect position (Advances 1 & 2, both hand sides, kwikastrip near by the Shaft), interior pullout bars when bended would not have been embedded in the Primary Lining of the Invert. Root cause : There was probably an incorrect profile used for the Beamer during the setting out and installation of the Kwikastrip.
| 02SL - Stations (LUL) | Cxxx-NCR-000264-L | NCR | CP6 Headwall: Cover of the steel reinforcement more than 100mm |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-07-26 | 2013-06-12 09:07 | -44 | 2013-02-20 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The concrete cover of the reinforcement on the headwall of CP6 was in many areas more than 100mm. Root cause : Bad coordination of the teams on site.
| 02SL - Stations (LUL) | Cxxx-NCR-000265-L | NCR | Core holes on CP5 and CP6 enlargement are not backfilled |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-05-30 | 2013-05-30 15:39 | 0 | 2013-02-18 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The core holes from CP5 and CP6 sampling have not been backfilled as they should have. The issue has been recorded many times in Surveillance Reports and Observations from the Quality Department on both sites (WHI and LIV). (see attachments). Root cause : Negligence of Production Team
| 02SL - Stations (LUL) | Cxxx-NCR-000266-L | NCR | Grout Mix S (Sleeve Grout) - Samples out of agreed tolerance from 23/04/12 to 21/12/12 |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-06-07 | 2013-05-01 10:04 | -37 | 2013-03-06 | Geotechnical Engineering - Compensation Grouting | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | After submittal of Grout samples for Sleeve grout, related to TAM drilling activities from 23/04/2012 to 21/12/2012, it has been found that: • 3224 set of samples (density, viscosity and bleed test) have been taken • 3131 set of samples out of the 3224 mentioned above are relevant (93 samples are internal checks and are not to be take into account) • 0 density tests have been found out of agreed tolerance • 3 viscosity tests have been found under agreed tolerance • 2036 viscosity tests have been found above agreed tolerance, and 1989 samples are still under 45 seconds • 586 bleed tests have been carried out, where 626 were required to meet agreed tolerance. The 586 bleed tests are within agreed tolerances. Root cause : Good workability of material despite parameters above range specified in ITP.
| 02SL - Stations (LUL) | Cxxx-NCR-000267-L | NCR | Incorrect Cheek Plates Dimension for the PO Tunnel propping - Design omission |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-07-12 | 2013-06-12 10:11 | -30 | 2013-04-08 | Civil - Civil Engineering General | 500 |  | Design | Rework |  | Complete |  | Completed |  | The cheek plates for the propping of PO Tunnel were 55mm as per the design but it was later found on site that they couldn’t fit into the existing PO Tunnel rings which ranged from 62mm to 75mm. Root cause : • The input for the design of the PO Tunnel was incorrectly showing that the flanges were 55mm instead of 65-72mm. Inconsistent archive information/drawings. • The dimensions of the rings were not measured during the trial erection.
| 02SL - Stations (LUL) | Cxxx-NCR-000268-L | NCR | Missing signatures on GAD1&2 Records |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-05-31 | 2013-03-10 16:34 | -82 | 2013-02-19 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | In many cases, the SCL Checksheets for the GAD1 and GAD2 Construction have not been signed by either the __ Construction Responsible person, __ QC or CRL Representative. The full list of these cases is shown in the attached summary table (red cross=missing signatures) This NCR summarizes all of these cases and it is issued after the works completion in order to record the issue for the Certification Packages L068 and L069 at LIV.
| 02SL - Stations (LUL) | Cxxx-NCR-000269-W | NCR | CP2 Enlargement South Adv 1-6: Discrepancy in overall thickness of transition |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-12-10 | 2012-11-23 12:02 | -17 | 2012-09-10 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Design | Rework |  | Complete |  | Completed |  | During the spraying of Advance 6 the engineers noted that the overall thickness of the beamer profiles Advance 1 to 6 was 300mm, 100mm short of the required 400mm as shown in the RESS. Root cause : •There was a discrepancy and some ambiguity in the design drawings in the transition zone between CP2 Enlargement to Cods Mouth Enlargement. •The Surveying team who provide the Beamer profiles understood that the overall thickness in the transition was 300mm. •Therefore, the site team sprayed Adv 1 to 6 as 300mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000270-L | NCR | Missing Records from the Green Folders of GAD1 and GAD2 |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-05-31 | 2013-05-09 11:28 | -22 | 2013-02-27 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | In many cases, the required deliverable records have not been produced on site during the Construction of GAD1 and GAD2. Please see attached summary table for more details. This NCR summarizes all of these cases and it is issued after the works completion in order to record the issue for the Certification Packages L068 and L069 at LIV. Root Cause: Early stages of Project. Production and Quality Control Teams were not familiar with the relevant ITP requirements and in many cases, records (like production of required profiles, J2 Curves or others) were missed.
| 02SL - Stations (LUL) | Cxxx-NCR-000270-W | NCR | Missing utilities works records: Concrete thrust blocks in Brady Street |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-12-18 | 2012-10-09 16:21 | -70 | 2012-09-18 | Utilities Engineering - Water | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Records of the thrust block poured at the north end of Brady Street missing as per 1-2 (technical requirements) Root cause : It was assumed that the approved ‘’Material and compliance Record: Approval of backfilling material’’ reference Cxxx-__M-C-RGN-CR092-50044 Rev1 applied to this operation. This concrete has been used for the thrust block. Subsequently attention to detail of ITP was lacking.
| 02SL - Stations (LUL) | Cxxx-NCR-000271-L | NCR | CP6: Transport of the regulating layer to the pump using the excavator bucket instead of the pipe |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-06-28 | 2013-05-14 13:16 | -45 | 2013-03-01 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The transport of the regulating layer to the pump in CP6 was conducted using the excavator bucket instead of the pipe. Root Cause: The concrete transport pipes were all disconnected on CP6 because of the steel fixing and the site teams preferred to use this quicker method to transport that short quantity of shotcrete.
| 02SL - Stations (LUL) | Cxxx-NCR-000271-W | NCR | Setting out, Excavation and Pipe laying in Brady Street |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-12-18 | 2012-10-09 16:24 | -70 | 2012-09-18 | Utilities Engineering - Water | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Records of Setting out, Excavation and Pipe laying in Brady Street missing as per 1-2.
| 02SL - Stations (LUL) | Cxxx-NCR-000272-L | NCR | CP6: Accelerator dosage for the regulating area set at 1% |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-06-28 | 2013-04-29 10:06 | -60 | 2013-03-01 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The accelerator dosage for the regulating area of CP6 on 23rd of February 2013 was set at 1% instead of 2% that it is agreed in the Method Statement. Root cause : The operator set up the dosage on 1% instead of 2% because he wasn’t informed about the proper dosage and judged the case on his experienced.
| 02SL - Stations (LUL) | Cxxx-NCR-000273-L | NCR | Cores from Adv. 49 of AP7-E Pilot in the left shoulder with less than 250mm |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-06-21 | 2013-04-29 10:11 | -53 | 2013-03-15 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Cores from Adv. 49 of AP7-E Pilot in the left shoulder were less than 250mm (around 190mm). Root cause : Localized less shotcrete. Probably the Engineer has not “scanned” the area properly with the Beamer during spraying.
| 02SL - Stations (LUL) | Cxxx-NCR-000273-W | NCR | CP2S Enlargement Adv 10 over spray primary 1 |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-12-11 | 2012-11-23 12:59 | -18 | 2012-09-11 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | During the spraying of Advance 10 the engineer made a mistake and started spraying to the Primary 2 profile, making the Primary 1 layer too thick. He corrected himself after spraying the sides and informed the Shift Team Leader immediately. The roots: An error was made by the engineer. He raised the error himself and reported it immediately.
| 02SL - Stations (LUL) | Cxxx-NCR-000274-L | NCR | Low Early Strength on shotcrete of AP7-W Adv.18 which has not been reported to the PIC/Crossrail in sufficient time allowed to react to testing results. The excavtion was allowed to proceed even though J2 curve results had failed. |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-06-21 | 2013-05-14 13:24 | -38 | 2013-03-15 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The Early Strength Curve for the shotcrete of AP7-W Adv.18 was significantly low than the J2 Curve. The issue has not been reported to the PIC/CRL. Root cause : Negligence by the Production Team. The issue had to be reported.
| 02SL - Stations (LUL) | Cxxx-NCR-000274-W | NCR | CP2N Enlargement Invert Adv 4 over excavate face |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-12-11 | 2012-11-23 15:04 | -18 | 2012-09-11 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Excavation of Adv 4, the face was not inclined and because of this excavation line was ahead of the design profile by up to 1.5m in the invert. Root cause: -During the transition from Advance 2 to 3 the face was mucked vertically. This was to be adjusted in Adv 4 but instead of adjusting it the error was carried forward onto this excavation. -The corrective measure was not communicated to the shift team well. -The beamer profile on the face was not followed.
| 02SL - Stations (LUL) | Cxxx-NCR-000275-W | NCR | Jacking the school without WMS and ITP |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-12-20 | 2012-12-14 17:01 | -6 | 2012-09-20 | Utilities Engineering - Utilities General | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | On Wednesday 5th September at 15:00, the site team has made the decision to insert a shim plate and to jack the school deviating from WMS and ITP in place. This has created minor cracks in the school façade and internal finishes and caused a door to get stuck. Root cause: Lack of communication between the site engineer and the section manager. Site engineer taking important decision without assessing the works to be done and verifying that he was allowed to do so.
| 02SL - Stations (LUL) | Cxxx-NCR-000276-L | NCR | Concrete flow test |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-06-28 | 2013-05-20 08:30 | -39 | 2013-03-18 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | During a flow test conducted at approximately 12:00pm 14th March, 2013 the technician omitted the EN 12350 -5 clause 6 requirement for waiting 30 seconds from striking off the concrete before proceeding. The Contractor was informed prior to the striking off the cone, that the test would be timed, notwithstanding this the cone was removed approximately after 5 seconds and then the test was paused for approximately 30 seconds before proceeding with the flow table drops. The 30 second wait was out of sequence and was done after the cone was removed, not before. With reference to SCL Inspector's Daily Site Report it appears that the batch of shotcrete was used to spray AP7 East (Pilot) tunnel Advance 65.
| 02SL - Stations (LUL) | Cxxx-NCR-000276-W | NCR | Marginal Grading Failures |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-12-17 | 2012-12-14 16:45 | -3 | 2012-09-17 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Sample numbers E0191 & E0194 taken from the 6mm Limestone aggregate delivered on the 17th & 20th August respectively fail to comply with the specification E0191 being 2% to fine on 1mm sieve & E0194 3% to fine also on the 1mm sieve. Sample numbers E0154 & E0196 taken from the 0/4mm Limestone Sand delivered on the 16th July & 21th August respectively fail to comply with the specification E0154 being 0.2% to fine on 0.063mm sieve & E0196 0.3% to fine also on the 0.063mm sieve. Root cause: Material marginally to fine due to segregation occured during discharge to hopper. Sampling only possible from hopper.
| 02SL - Stations (LUL) | Cxxx-NCR-000277-L | NCR | The core holes at AP7 W and E were backfilled with not approved grout material |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-07-12 | 2013-06-03 16:51 | -39 | 2013-04-08 | Tunnelling - Grouting | 500 |  | Material | Repair |  | Complete |  | Completed |  | The core holes at AP7 W and E were backfilled with not approved grout material (Lafarge Cement) Root cause : Production Team was not informed about the requirement and they proceed with the easiest solution at that moment.
| 02SL - Stations (LUL) | Cxxx-NCR-000277-W | NCR | Head Wall Joint Issue on CP2 North |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-12-18 | 2012-10-18 10:21 | -61 | 2012-09-18 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | There was a build up of rebound found around the layer of Kwikastrip in the headwall. Root cause : •Insufficient cleaning during the spraying of Adv 45 on the CP2 N Enlargement led to build up of rebound at the face and into the ‘corner’ of the SCL.
| 02SL - Stations (LUL) | Cxxx-NCR-000278-W | NCR | Grouting while No ATS Operational |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-02-15 | 2013-02-14 10:57 | -1 | 2012-09-17 | Geotechnical Engineering - Compensation Grouting | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | On the 10th September 2012, grout injections recommenced on corrective grouting phase GJ06 at the start of shift. An injection commenced at 07:46 and by 08:09 318 litres of grout was injected underneath the Albion Brewery. During these injections, real time monitoring was not visible on Geoscope Web. Root cause : The monitoring department did not advise the Ground Engineering Team that the real time monitoring system was not operational.
| 02SL - Stations (LUL) | Cxxx-NCR-000281-L | NCR | L - AP7-E CH2 Enl. : Voids and shadowing behing kwikastrip (adv 3 and 7) |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-08-29 | 2014-06-20 09:21 | -70 | 2013-04-15 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • On 13/04/13, in AP7-E Ch2 Enlargement Adv 4, voids and shadowing have been found below kwikastrip. • SRG instructed on 14/04/13 voids proof drilling. Result: No void was found following the proof drilling completed for the joint between Advance 4 and Advance 6 within Kwikastrip area. (see att03d – CH2 Primary Prodd Drilling) • Further investigations have been agreed in Materials Meeting on 15/04/2013 and more cores were taken in AP7 East Enlargement Chamber 2 Advance 3 and 7 on the right hand side. These cores show the followings imperfections: o Laminations between layers o Cracks and voids around kwikastrip See Core Report attached (att02)
| 02SL - Stations (LUL) | Cxxx-NCR-000281-W | NCR | Extensometers Installation Issue at WHI and LIV |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-02-28 | 2013-12-10 16:24 | -80 | 2012-09-25 | Geotechnical Engineering - Geotechnical Monitoring | 46943.36 |  | Workmanship | Repair | 2 (6-60k) | Complete | Management Problem - Inadequate supervision | Completed |  | Measuring rod extensometer failure. (See report attached for Liverpool Street issue) Root cause : Device not set to a correct working range. No proper supervision and commissioning of the instrumentation was carried out by __ and __ Inappropriate briefing and training was provided to the surveyors carrying out the readings __ was not reviewing and taking responsibility for the data
| 02SL - Stations (LUL) | Cxxx-NCR-000282-L | NCR | AP7 E CHAMBER 2 ADV 19: Incorrect Installation of kwikastrip reinforcement |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-07-26 | 2013-07-03 14:34 | -23 | 2013-04-23 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | • Gap between the kwikastrip of Advance 18 and the kwikastrip of Advance 19 on the right hand sidewall • Kwikastrip of Advance 18 much shorter than the 1m Advance step on the left hand sidewall Root cause : • Poor Workmanship • Kwikistrip installed towards the end of the initial spray before the face had been fully finished.
| 02SL - Stations (LUL) | Cxxx-NCR-000282-W | NCR | Undermining of top heading |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-06-28 | 2013-06-14 10:22 | -14 | 2012-09-25 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | •Top Heading Advances 4 and 5 in CP2 S were undermined up to a depth of 600mm. Following the application of Primary layer 1 the lower excavation of 600mm is being solely supported by the initial layer of 75mm only. •This has occurred also on few occasion following this event and in particular: oAdv.10 was undermining on left side in the zone around axis and knee. (10/09/2012) oAdv.11 was undermining on right side in the zone around axis and knee. (11/09/2012) Root cause : RESS sheet did not specified the designer's intent.
| 02SL - Stations (LUL) | Cxxx-NCR-000283-L | NCR | Over excavation of ADV 76 in AP7 West Pilot Tunnel |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-07-26 | 2013-07-02 13:57 | -24 | 2013-04-23 | Tunnelling - Excavation - Hand | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Advance Length of face over excavated approximately 700mm in the invert. Root Cause: Lack of care of the Construction Team and excavation not fully supervised by Engineers
| 02SL - Stations (LUL) | Cxxx-NCR-000284-L | NCR | AP7 E Enlargement, Adv 5: Missing Monitoring Pins |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-07-26 | 2013-07-18 08:30 | -8 | 2013-04-23 | Tunnelling - Tunnelling General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | The Invert Monitoring Pins were not installed in Advance 4 as required in RESS AP7-E/15. See attached a photograph showing the positioning of the monitoring points which have been installed above the kwikastrip in Advance 4. Root cause : Construction Team only refer to the RESS and didn’t follow the requirements of the drawing.
| 02SL - Stations (LUL) | Cxxx-NCR-000285-L | NCR | Designer of the Muck Hoist not accepted by CRL |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2013-10-18 | 2013-10-24 16:16 | 6 | 2013-05-01 | Civil - Civil Engineering General | 500 |  | System Defect | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | __ has not submitted for approval the Designer “Tunnel Services UK” for the design that they performed for the Muck Hoist. Root cause : It was not clear in the early stages of the Project that such a requirement applies for structures like Muck Hoist.
| 02SL - Stations (LUL) | Cxxx-NCR-000285-W | NCR | Inclinometer annulus fill |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-08-09 | 2013-07-23 12:39 | -17 | 2012-09-27 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | To confirm the discussion at the weekly __/CRL meeting on 21st September 2012, we believe that during installation of the inclinometers at both at WHI and LIV our sub-contractor used a sand / bentonite grout in contravention of the Specification. Having identified this potential deviation from the specification we don’t necessarily believe that such a change will materially affect the performance of the inclinometers and we therefore respectfully reserve the right to demonstrate this and / or request a concession if we believe this to be justified. Root cause: Misunderstanding specification.
| 02SL - Stations (LUL) | Cxxx-NCR-000286-L | NCR | CP6 Wraparound: NF1 __ Couplers |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-08-02 | 2013-06-07 13:30 | -56 | 2013-05-02 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The coupler staggering in quadrants 3 & 4 were opposite to that described on the above mentioned drawing. In addition to this the number of couplers installed is fewer than described on the drawing – please find attached marked up photographs. The exclusion of couplers has been made on the basis that the coupled bar would be too short to warrant disrupting its continuity. Levels and position remain unchanged. Root cause: Cut measurements given from reference level. Each individual bar cut position was not marked – Drawing given to operatives and explained.
| 02SL - Stations (LUL) | Cxxx-NCR-000286-W | NCR | Slight local over excavation in CP2 N Advance 5 |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-01-25 | 2012-12-18 13:56 | -38 | 2012-10-16 | Tunnelling - Excavation - TBM | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | A slight local over excavation has occurred as shown on sketch attached. Root cause : This is a minor local over exaction, no specific root cause. the required excavation length of adv 5 was specified as very short and was hard and difficult to achieve as specified on the RES and corresponding drawing
| 02SL - Stations (LUL) | Cxxx-NCR-000287-L | NCR | Contaminated bulk load of Grout G20 on 16/05/2013 and 21/05/2013 |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-10-11 | 2013-07-03 08:08 | -100 | 2013-06-21 | Geotechnical Engineering - Compensation Grouting | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | The bulk load of G20 Grout that was delivered in LIV on 16th of May 2013 and 21st of May 2013, was containing sand. As a result the material blocked the equipment and the lines of the ground engineering team. Root cause : The supplier provided nonconforming Grout.
| 02SL - Stations (LUL) | Cxxx-NCR-000287-W | NCR | Valve installed with incorrect spindle adaptor |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-04-19 | 2013-03-19 11:33 | -31 | 2012-12-17 | Utilities Engineering - Water | 500 |  | Material | Repair |  | Complete |  | Completed |  | 4 Nb valves Serie 756 AVK double Eccentric Butterfly have been installed. This type of valve is operated with a wheel. Spindle adaptor have been installed, but __ was still unable to manoeuvre the valves. Root Cause: Because of the very short leading time to procure the valve, it has been decided to install 4 Nb valves Serie 756 AVK double Eccentric Butterfly operated with wheel and to provide an adaptor to allow it to be operated with key valve spindle.
| 02SL - Stations (LUL) | Cxxx-NCR-000288-L | NCR | AP7W pilot, adv 108: Thickness less than 250mmbetween 9 and 10 o’clock position |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-08-09 | 2013-06-07 13:17 | -63 | 2013-05-03 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Core drilling was done in Advance 108 left side (between 9 and 10 o’clock position). One core sample drilled showed a length of only 170mm, which is well below the minimum 250mm. Root cause : • Mistake during spraying – underspray of local area.
| 02SL - Stations (LUL) | Cxxx-NCR-000288-W | NCR | No flow test Primary Lining Adv.8 CP2 North |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-01-04 | 2012-11-05 10:02 | -60 | 2012-10-04 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | •Spraying of primary lining Adv 8 CP2 North completed with no flow test carried out prior to spray Root cause : •Lack of communication between Engineering and Lab department’s on site
| 02SL - Stations (LUL) | Cxxx-NCR-000289-L | NCR | Voids found behind the Kwikastrip after the spray in CP6 |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-08-09 | 2013-05-15 08:08 | -86 | 2013-05-07 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | After the spray of the NF2 steel below the level 75.200, two voids were found behind the Kwikastrip around the eyes. One void was found on Q3 and one void was found on Q4 (see attached drawing ). The size of the voids was 20x10x40mm. See the attached document for the position of the voids. Root cause: Inadequate supervision of the spraying activity.
| 02SL - Stations (LUL) | Cxxx-NCR-000289-W | NCR | Insufficient Micro-silica for design Adv. 24 CP2 South |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-02-15 | 2013-01-04 13:47 | -42 | 2012-10-04 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Rework |  | Complete |  | Completed |  | •Excavation commenced without checking whether there was a sufficient amount of wet mix concrete available for immediate use to support the excavated profile of Advance 24 CP2 South •Shotcrete sprayed onto the temporary invert of Advance 24 with a believed lower quantity of microsilica compared with that of the design specification (6%). Root cause: •No checks were done at the onsite batching plant prior to commencing the excavation •There was a perceived ‘run out’ of microsilica in the batching plant. The decision was made to seal up advance 24 (double invert) and wait until the day shift and a delivery of microsilica before continuing
| 02SL - Stations (LUL) | Cxxx-NCR-000290-L | NCR | Reinforcement bars diameter in the headwall of CP6 below the axis not as per drawing |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-08-16 | 2013-07-10 07:45 | -37 | 2013-05-15 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Rework |  | Complete |  | Completed |  | On 11/05/2013 reinforcement bars for Headwall in CP6 have been installed following drawing revision C01 instead of the current revision C02 agreed by CRL. DIA.32mm horizontal reinforcement bars have been installed instead of DIA.25mm bars. Also __ __ robot was used instead of __ which was the specified robot in the Method Statement (Cxxx-__M-C-GMS-C101-50021 Rev.10 page 22). An agreement with __ Designer which allowed Construction Team to keep the 32mm bars in place (for constructability reason) had been fixed previously as per Revision C01 but not communicated to Crossrail.
| 02SL - Stations (LUL) | Cxxx-NCR-000290-W | NCR | Over excavation of advance 6 of CP2 South Pilot |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-01-11 | 2012-11-15 13:32 | -57 | 2012-11-06 | Tunnelling - Excavation - TBM | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | on 11.07.12 the top heading was over-excavated by 200mm in the face of the top heading (approximately from shoulder to shoulder). Root Cause: First full face advance of CP2 South Pilot excavated without full profile control from engineers.
| 02SL - Stations (LUL) | Cxxx-NCR-000291-W | NCR | Adv. 24 CP2 South 2nd Primary Lining not sprayed in one go |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-12-31 | 2012-11-23 12:52 | -38 | 2012-10-01 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Equipment Breakdown | Use As-Is |  | Complete |  | Completed |  | •The full Advance 24 Primary Lining Stage 2 was not completed in one go. •Stopped at 15:00, 90% complete with small area in crown to complete, on the 17/09/12 because we had run out of micro silica. •Recommenced and completed Primary Lining Stage 2 at 19:00 on the 17/09/12. Root cause : •There was a miscalculation in the ordering of materials. The Batching plant computer was also showing that we had sufficient materials remaining in the storage tank. The sensors were either not calibrated correctly or were faulty.
| 02SL - Stations (LUL) | Cxxx-NCR-000292-W | NCR | No Estimated Fibre & Aggregate Rebound |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-01-18 | 2012-12-11 12:52 | -38 | 2012-10-17 | Shafts -Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | No test on the fibre and aggregate rebound was carried out for the duration of shaft CS1 construction. Root cause : It has not been cascaded as being an important test and site has overlooked the carrying out of the test.
| 02SL - Stations (LUL) | Cxxx-NCR-000293-L | NCR | CP6 Wraparound: Spray of 250mm shotcrete behind 25mm reinforcement |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-08-23 | 2013-06-17 17:13 | -67 | 2013-05-17 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | During spraying of Stage 4 between the top heading of pilot tunnel and enlargement, __ sprayed 250 mm behind 25mm rebars, within the PT enlargement opening area, where sacrificial reinforcement is installed. Root cause : As it has been recorded on reinforcement checksheet dated 12/02/13, the cover is not as per Design (> 100 mm). However, it has been agreed with SCL Inspector to spray behind rebar and oversprayed the 200mm in one go as this area will be broken during construction of enlargement
| 02SL - Stations (LUL) | Cxxx-NCR-000294-L | NCR | L - Access Shaft AS1: Some Welds on temporary works have failed the N__ Test |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-07-25 | 2014-06-26 15:59 | -29 | 2013-05-31 | Structural Engineering - Welding | 4000 |  | Testing and Commissioning | Rework | 3 (3-6k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Welds on several locations failed the N__ Test during the inspection made by __ on 25/02/2103 and 28/03/2013, (see attachment 1: summary table): 1. Access Shaft Gallows Bracket for the Haki – W9: welds were seen to be 4mm fillet welds (see attachment 2a: __ Report 47512J SR 16 KB) 2. Grout Adit Folding Platform Support Brackets – W9: 1No of the 16No fin plates had variable leg length ranging from 4mm to 10mm. (see attachment 4a: __ Report 47512J SR 22 KB)
| 02SL - Stations (LUL) | Cxxx-NCR-000296-W | NCR | CP2 S Enlarg. Invert, Adv. 3: Face of excavation being vertical and not inclined as required |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-01-11 | 2012-12-17 12:53 | -25 | 2012-10-11 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Excavation of Adv 3, the face was not inclined and because of this the excavation line was ahead of the design profile by up to 1.5m in the invert. Root cause : •During the transition from Advance 2 to 3 the face was mucked vertically. •The beamer profile on the face was not followed.
| 02SL - Stations (LUL) | Cxxx-NCR-000297-W | NCR | Jacks not installed as per RFI WHI-CRL-RFI-Cxxx-00171 |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-04-19 | 2013-04-16 11:06 | -3 | 2012-10-04 | Utilities Engineering - Utilities General | 500 |  | Supervision/Management | Reject |  | Complete |  | Completed |  | The jacks in pile cap D1 and SW2 are not located as per guidance sketch issued with RFI WHI-CRL –RFI-Cxxx-00171 The position of the jacks hasn’t been confirmed to the designer prior to pile cutting. Root cause: The section manager has instructed the site engineer to install the jacks as per RFI WHI-CRL –RFI-Cxxx-00171 and then to produce the as-built as per the RFI and submit it to Crossrail via an RFI to check with designer. Because the ground beam was uneven at this location and the installation of the jacks would have required a lot of hardly achievable concrete scabbling, the site engineer installed the jacks where he thought it was suitable but did not produce as built and checked the jacks location prior to cut the pile. There was no hold point indicated for this on the check sheet and ITP.
| 02SL - Stations (LUL) | Cxxx-NCR-000298-L | NCR | Voids in shotcrete during the spray of the CP6 North Wraparound |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-09-20 | 2013-07-02 14:12 | -80 | 2013-06-03 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | • Repeated voids have been formed during the spray of the shoulders and crowns in CP6. Root Cause: • Design was not clear enough: Reinforcement layer on drawing Cxxx-__M-C4-DDB-C101-00070 rev P04 is not sufficiently detailed, no dimensions are mentioned.
| 02SL - Stations (LUL) | Cxxx-NCR-000299-L | NCR | AP7W-e Adv. 51 Early strength testing of Shotcrete Panel Advance 51 incomplete & lower than the modified J2 curve |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-09-13 | 2013-07-18 13:16 | -57 | 2013-06-03 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | • Compliance with Early Strength requirements stated in the specifications KT20 is not reached, early strength is below the J2 curve modified. • Many fields remain empty and none of the hilti gun test have been done Root cause : • Engineers forgot to do the hilti tests and fill properly the sheets due their busy working days.
| 02SL - Stations (LUL) | Cxxx-NCR-000300-L | NCR | Incomplete SCL Placement Checksheets and wrong version used |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-09-27 | 2013-07-18 13:20 | -71 | 2013-06-05 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | • Incomplete placement check sheets whereby a spot check of the placement check sheet for advance 71 had neither thumb test( ITP section C3 ) or joint cleanliness ( ITP section 3.1 ) acceptance signed. • Site has used rev 6 of placement check sheet __ Form D3-37 which was still under review. Rev 5 was the current check sheet. Root cause : • Thumb Test have been done on site but not recorded on checksheet: lack of awareness of the Lead Miner and the Nozzleman on the importance of recording results and the requirements for them to be part of the deliverable information. Supervision and management didn’t checked results and didn’t notified missing information. • Checksheet rev 6.0 has been sent for review and comments to the Site, they didn’t understand and start to use it before official approval.
| 02SL - Stations (LUL) | Cxxx-NCR-000301-L | NCR | CP5 Headwall: insufficient spraying of the previous layer |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-09-27 | 2013-07-02 14:47 | -87 | 2013-06-10 | Structural Engineering - Reinforcement | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | • On CP5, 1st layer of the headwall has not been sprayed enough and no sufficient bulk out has been done before the second row of steel got implemented. The cover is approximately of 200mm behind the bars on the headwall area in some areas. Root Cause: • No correct survey of the 1st layer of the headwall has been undertaken before to implement the rebar.
| 02SL - Stations (LUL) | Cxxx-NCR-000301-W | NCR | Shotcrete Fall Record Process |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-01-18 | 2012-12-11 12:42 | -38 | 2012-10-16 | Tunnelling - Linings - Sprayed Concrete | 500 |  | System Defect | Repair |  | Complete |  | Completed |  | Follow the issue of shotcrete fall that occurred on 14/07/2012 on CP2 Advance 17, shotcrete fall was recorded in the RIVO register and in the Tunnel Unusual Occurrence Register. This process did not seem to be sufficient to record investigation required for Quality purpose. Root cause : No specific requirement for Shotcrete fall records.
| 02SL - Stations (LUL) | Cxxx-NCR-000302-L | NCR | Damage to 32mm NF bars CP5 around the platform tunnel eye |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-09-20 | 2013-06-18 16:05 | -94 | 2013-06-14 | Structural Engineering - Reinforcement | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | Bars around the platform tunnel eye, on the west side, to ensure the stability during the excavation and construction of the platform tunnels have been damaged. • The bars in CP5 around the platform tunnel PTW-W eye were damaged while removing backfill with the __ 944 in the invert area.
| 02SL - Stations (LUL) | Cxxx-NCR-000302-W | NCR | Bending of kwikastrip bars carried out prior to installation of initial lining |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-01-18 | 2012-11-23 15:08 | -56 | 2012-10-18 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Bending of Kwikastrip done prior to spraying of initial lining. This issue was reported on 12/07/2012 and has occurred on few occasion since. Root cause : This is a workmanship issue.
| 02SL - Stations (LUL) | Cxxx-NCR-000303-L | NCR | PTE-West Pilot: Non Adherence To RESS |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-09-13 | 2013-07-08 08:24 | -67 | 2013-06-14 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The 75mm Initial and the 175mm Primary were sprayed in the Invert prior (the face and the crown were not sprayed). This does not adhere to the stages outlined in the RESS (stages 02-03-04). Root cause: Sprayers and Shift Engineers deviated from the discipline of the RESS. Due to the beginning of the Platform Tunnel – pilot, there has been a miscommunication between the sprayers and shift engineers and misunderstood of the RESS.
| 02SL - Stations (LUL) | Cxxx-NCR-000303-W | NCR | Insufficient as-built profiles presented on night shift SRG meeting for Adv.12-13 & 15-16 in CP2 S. |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-01-11 | 2012-11-23 12:49 | -49 | 2012-10-19 | Tunnelling - Tunnelling General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | For Adv.12-13 and 15-16 for south pilot CP2 in sufficient measurements were taken to provide the requirements stated in 1-2. Root cause : Insufficient points being measured on the same advance between layers.
| 02SL - Stations (LUL) | Cxxx-NCR-000304-L | NCR | PTE-E Breakout (Advance 1) |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-09-13 | 2013-07-10 07:52 | -65 | 2013-06-17 | Tunnelling - Excavation - Hand | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | Breakout of Advance 1 done to level believed to be indicated by the RESS but actually below specified level on RESS sheet. Root cause: • Clarity of RESS Sheet. Poor quality of text makes for hard reading, ambiguous text and arrows allows for misinterpretation. No additional or clarifying information or levels on page 3 of the RESS.
| 02SL - Stations (LUL) | Cxxx-NCR-000304-W | NCR | Incorrect shape of profile across CodsMouth/Invert Enlargement Advances 1,2 & 3 in CP2 North. |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-01-11 | 2012-12-17 15:16 | -25 | 2012-10-18 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | An extra volume is left when after breaking out the enlargement and left in place after spraying enlargement invert. This volume is removed at a further stage prior to placing reinforcement. This occurred on 09/09/2012 on advance 1, 2 & 3 in CP2 N and has probably occurred at several other location where same detail applies. Root cause : This is a snag left during the construction process in order to progress with the work and profile is corrected at later stage.
| 02SL - Stations (LUL) | Cxxx-NCR-000305-L | NCR | Missing points in Primary profile in AP7-E Enlargement CH2 Adv 47+48 |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-09-13 | 2013-08-02 10:49 | -42 | 2013-06-17 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | During the record of the primary ( Advance 47+48 in CH2 ) some points in the bottom right part are missing. Root Cause: • Lack of awareness of the engineers of the importance of results and the requirement for them to be part of the deliverable information • Supervision and management not checking results and notifying of missing information
| 02SL - Stations (LUL) | Cxxx-NCR-000305-W | NCR | Stage 1 in CP2 N - Primary finished profile |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-06-14 | 2013-06-11 12:41 | -3 | 2012-12-05 | Tunnelling - Linings - Sprayed Concrete | 500 |  | System Defect | Repair |  | Complete |  | Completed |  | Areas of CP2 – North West side wall Bottom half of wall in excess of 75mm (>400mm) noticed behind far face reinforcement of CP2 thickening on 04.10.12 Root cause : The Beamer programming only projects simple shapes – a “tube” for the enlargement and a “dish” for the headwall. Where these two elements meet there is no rounded corner as required on the drawings (see attached Beamer “view”). The Primary lining was installed to the beamer profile and in areas either side of the junction the profile was greater than the allowable tolerance.
| 02SL - Stations (LUL) | Cxxx-NCR-000306-L | NCR | PTW-E Pilot: Under excavation in advance 55 and 56 |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-09-06 | 2013-07-02 14:50 | -66 | 2013-06-19 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | • Excavation line was recorded as 0.000 to – 0.011 which is below required excavation line (see excavation profiles attached) Root cause : • Confusion with beamer programme mechanics by shift engineer. Wrong button was pressed during excavation so values do not represent true finished excavation line
| 02SL - Stations (LUL) | Cxxx-NCR-000306-W | NCR | Marginal Grading Failures (30th August, 20, 21st and 29th September, 3rd, 4th, 9th, and 10th October) |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-12-20 | 2012-12-14 17:07 | -6 | 2012-10-31 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Sample numbers E0204, E238, E0240, E247, E249, E253, E257, E260 taken from the 0/4mm Limestone Sand delivered on the 30th August, 20, 21st and 29th September, 3rd, 4th, 9th, and 10th October respectively fail to comply with the specification on 0.063mm sieve. All samples are to fine on 0.063mm sieve exceeding limits as per attached summary between 0.1% to 0.9%. Root cause : Material marginally to fine due to segregation occurred during discharge to hopper. Sampling only possible from hopper.
| 02SL - Stations (LUL) | Cxxx-NCR-000307-W | NCR | Calibration schedule |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-01-31 | 2013-01-30 16:26 | -1 | 2012-10-19 | Tunnelling - Tunnelling General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | During a CRL lead surveillance on 17.10.2012 the Contractor could not demonstarte that the specified calibration schedule was in place. In addition the calibration records for the pentrometers employed at the SCL works were not available.
| 02SL - Stations (LUL) | Cxxx-NCR-000309-W | NCR | Non-compliance of face logs with BS5930 |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-03-01 | 2013-03-01 11:06 | 0 | 2012-10-24 | Geotechnical Engineering - Geotechnical Engineering - General | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | Some of the SCL face log soil descriptions fall some way short of BS5930 descriptions, and as not all logs are provided, unable to confirm that 25% of all logs witness and that *all* logs are reviewed by a competent geologist (a requirement of the ITP Cxxx-__M-C4-ITP-CR092-50001). Greasybacks & fissures. More info is needed on the face logs on discontinuity orientation (in general & with ref to greasy backs). An attempt at guesstimating orientation for bigger joints should always be made & they should be sketched on the face logs. The example SCL face logs in the report mostly make statements about fissure frequency but rarely about the orientation of these fissures (other than to occasionally say they are random – which doesn’t sound very credible). Greasybacks – a statement about whether they fell out or not should be consistently made & some estimate of their dimensions (& shape) should be consistently made.
| 02SL - Stations (LUL) | Cxxx-NCR-000311-L | NCR | Remedial work to CP5 lining, possible voids |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2013-10-04 | 2013-09-09 11:01 | -25 | 2013-07-01 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete |  | Completed |  | • Lining subject to voiding, due to delamination of finishing layer Root Cause: • Bad workmanship
| 02SL - Stations (LUL) | Cxxx-NCR-000311-W | NCR | Starting work on the breakout PTE-E without a signed RESS. |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-04-05 | 2013-02-05 13:56 | -59 | 2012-11-29 | Tunnelling - Tunnelling General | 500 |  | System Defect | Repair |  | Complete |  | Completed |  | • Started breakout without a signed RESS Root cause : • Confusion with information transfer, with what was and wasn’t the programme of works for the weekend was slightly misleading which lead to the breakout starting without signed RESS
| 02SL - Stations (LUL) | Cxxx-NCR-000312-L | NCR | CP5 Fiberless Shotcrete encroaching into Transition |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2013-09-20 | 2013-09-05 16:24 | -15 | 2013-06-28 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | As a regulating layer in the Crown near the Transition for the installation of NF2 & NF1, so where rebar is present, some fibreless shotcrete was sprayed. The spray is encroaching about 500mm into the Transition over an average thickness of 250mm. Root cause: The spray was chamfered and it is encroaching into the Transition
| 02SL - Stations (LUL) | Cxxx-NCR-000313-L | NCR | Rebar encroaching toe eye for PT enlargement |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-10-11 | 2013-07-09 15:55 | -94 | 2013-07-04 | Structural Engineering - Reinforcement | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | • There are bars protruding into the eye of the enlargement. Root Cause: • Detailing error in design drawing
| 02SL - Stations (LUL) | Cxxx-NCR-000314-L | NCR | Contaminated accelerator used for the spray of CP5 – Stage 6 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2013-09-06 | 2013-09-06 09:07 | 0 | 2013-07-02 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete |  | Completed |  | Accelerator used for the spray of bulking layer, stage6 was contaminated. Root Cause: Top of accelerator cube left open after re-filling of the tank.
| 02SL - Stations (LUL) | Cxxx-NCR-000314-W | NCR | Cross contamination of shotcrete aggregates |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-02-22 | 2013-02-21 10:32 | -1 | 2012-11-07 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Equipment Breakdown | Use As-Is |  | Complete |  | Completed |  | During batching operations it was noted that the mix became very course with a reduced amount of sand. Root cause: Initially it was thought that the aggregate had overrun from the 6mm bin into the sand bin however, once the level of the material in the bin had been lowered it was apparent that a hole had formed in the partition wall allowing 6mm to enter the sand bin.
| 02SL - Stations (LUL) | Cxxx-NCR-000315-L | NCR | Aggregate grading failure |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-10-04 | 2013-07-29 11:03 | -67 | 2013-07-02 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | On the 15th June a load of 6mm was delivered to the LIV site batching plant and a sample (E0855) was taken that, was later found to fail the grading limits being 21% to fine on the 2mm sieve and 6.4% to fine on the 63µ sieve. Root Cause: Noncompliant material being delivered.
| 02SL - Stations (LUL) | Cxxx-NCR-000315-W | NCR | Laboratory Air temperature outside the specification limits |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-01-31 | 2013-01-28 11:32 | -3 | 2012-11-08 | Civil - Civil Engineering General | 500 |  | Equipment Breakdown | Rework |  | Complete |  | Completed |  | Laboratory Air Temperature found 11.5°C which is outside spec limits. Also temperature was not recorded on daily check sheets for 1st and 2nd November. The issue was raised by Site Quality Engineer during his lab visit on 02 November 2012. Root Cause: - Lab container doors won't shut flush due physical damage. - Not completion of the Air Condition unit installation. The order though has been placed since April 2012. (Requisition attached) - Insufficient monitoring of the curing room temperature.
| 02SL - Stations (LUL) | Cxxx-NCR-000316-W | NCR | No 30mm “window” left for installation of the Type 1 and Type 2 reinforcement between wraparound structure and Enlargement tunnels. |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-03-29 | 2013-03-19 11:44 | -10 | 2012-11-16 | Tunnelling - Tunnelling General | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | •No shotcrete “windows” left for L-bar installation Root cause : •RESS WHI CP2-N-14c for stages 6 & 7 does not state requirement for shotcrete “window” or recess. It does refer to dwg UnPS-CFT-WCH-CP2-D-01023 which is only the overview of all stages and detail stages 1 & 2. The continuation of the stages drawings starts at dwg UnPS-CFT-WCH-CP2-D-01047 for stages 3, 4 & 5 and for stages 6, 7 & complete on dwg UnPS-CFT-WCH-CP2-D-01048. None of these drawings shows a “window” or recess. •GA drawings UnPS-CFT-WCH-CP2-D-26002, UnPS-CFT-WCH-CP2-D-26003 do not show a “window” or recess at the stage of CP2 completion. Enlargement thickening GA drawing UnPS-CFT-WCH-CP2-D-26015 also shows no “window” or recess at the stage of CP2 completion. •“Window” or recess shown only on UNPS-CFT-WCH-CP2-D-01017 which has not been noticed by the site team or the SCL Engineer for the production of the RESS. •The site team using the RESS provided and drawings available completed the CP2 thickening without the formation of a “window” or recess.
| 02SL - Stations (LUL) | Cxxx-NCR-000317-L | NCR | PTE-E pilot, adv 15&16: delay to support sequence |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2013-10-18 | 2013-10-02 07:57 | -16 | 2013-07-05 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | On 27/06/13, the excavation of PTE-East Pilot Tunnel : • Adv 15 was completed at 13:00 whilst the placement of the initial lining did not begin until 14:45 causing a delay to support of 105 minutes. • Adv 16 was completed at 17:45 whilst the placement of the initial lining did not begin until 19:30 causing a delay to support of 105 minutes. (see attached shift report) Root Cause: • Lack of care of the operatives and bad organization.
| 02SL - Stations (LUL) | Cxxx-NCR-000317-W | NCR | PTE-W, Adv. 28 SCL Cores Less than Min. Required Length |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-02-08 | 2012-12-18 12:00 | -52 | 2012-11-08 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Cored samples taken from the PTE - W Pilot Tunnel show an area on the right hand shoulder of Adv 28 was less than 250mm. The beamer profile reports show that the area had sufficient thickness. Root cause : • Localised thin area of SCL, poor workmanship in setting out the excavation and primary lining profiles.
| 02SL - Stations (LUL) | Cxxx-NCR-000318-L | NCR | PTW-W-adv12, pilot: Over-excavation of the face |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2013-11-22 | 2013-09-14 08:52 | -69 | 2013-07-08 | Tunnelling - Excavation - Hand | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Supervision - Supervisor not familiar with the work | Completed |  | Face of the advance over excavated by approx. 500mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000318-W | NCR | Marginal Grading Failures (17, 18, 20, 22, 25 and 26th October) |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-02-11 | 2013-01-02 08:04 | -40 | 2012-11-09 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Sample numbers E0267, E268, E 274, E277, E282, E285 taken from the 0/4mm Limestone Sand delivered on the 17, 18, 20, 22, 25 and 26th October respectively fail to comply with the specification on 0.063mm sieve. All samples are to fine on 0.063mm sieve exceeding limits as per attached summaries between 0.1% to 1.4%. Root cause : Material marginally too fine due to possible segregation occurring during discharge into hopper (sampling on site is only possible from the hopper), or material is delivered too fine.
| 02SL - Stations (LUL) | Cxxx-NCR-000319-L | NCR | Non-compliance with RESS for adv 80&81, PTE-W pilot |  | Contr |  | LIS - Liverpool Street Station (Central) |  | 2013-10-11 | 2013-07-09 16:00 | -94 | 2013-07-08 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The requirements of Stages 2, 3 and 4 (spraying the initial and primary as an homogeneous layer in the invert) as stated in RESS PTE-W/06 were not followed for advances 80 and 81. Root Cause: Sprayers deviated from the discipline of the RESS due to Failure to instruct and supervise the personnel.
| 02SL - Stations (LUL) | Cxxx-NCR-000320-W | NCR | PTE-W, Adv 14 excavated in one go which is not as per RESS |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-03-29 | 2013-01-04 14:16 | -84 | 2012-11-27 | Tunnelling - Excavation - Hand | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Adv. 34 in PTE West has been excavated in one go (top heading and inclined invert) which is not as per RESS PTE W/04. Invert level has been confirmed by __ Engineer at 85.2, whilst the theoretical excavation level for the invert is 85.05. Level 85.2 been shot on loose material which means that possible excavation is up to the full pilot invert 85.0 and not 86.14 as prescribed in the RESS. Root cause : • Step for temporary invert was not respected. • Level 85.2 been shot on loose material which means that possible excavation is up to the full pilot invert 85.0 and not 86.14 as prescribed in the RESS.
| 02SL - Stations (LUL) | Cxxx-NCR-000321-W | NCR | Under spray the primary lining of Advance 46 of PTE East Pilot. |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-02-20 | 2013-01-17 13:10 | -34 | 2012-11-20 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The primary lining was left approximately 500mm short of the excavation face. Operator and engineering error is to blame. In one location (LHS axis) they made a misjudgement of 200mm when spraying the joint. Probably due to an uneven excavation on the face. Root cause : Primary lining was not brought forward far enough with the advance sequence.
| 02SL - Stations (LUL) | Cxxx-NCR-000322-L | NCR | Accuracy of monitoring data at CP6 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-02-21 | 2013-09-04 12:16 | -170 | 2013-07-18 | Surveying - Tunnels/Portal/Shafts surveys | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | • There are big “jumps” on the measurements of SCL settlement of some dates which are obviously not correct and out of tolerances (see attached graphs). Root Cause: • Difficulties in obtaining such readings because all invert points are ~3m deep in 300mm safety pipe. Very often the pipe is full water, so that survey team try to set the levelling staff blind on the invert point.
| 02SL - Stations (LUL) | Cxxx-NCR-000322-W | NCR | Overexcavation of Adv.9 PTW East |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-02-15 | 2013-01-17 13:06 | -29 | 2012-11-15 | Tunnelling - Excavation - Hand | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The top heading was over-excavated by ~600mm in the face of the top heading (approximately from shoulder to shoulder). Root cause : • Full face excavation of adv 9 of PTW East pilot tunnel carried out without full profile control from engineers. • Lack of due care of Excavator driver.
| 02SL - Stations (LUL) | Cxxx-NCR-000324-W | NCR | Earth Strengths Beneath J2 |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-03-14 | 2013-02-25 10:14 | -17 | 2012-12-05 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | PTW-E 21, 22, 25, 27. PTE-W 46, 48. PTE-E 53, 54, 55. Tests showed that after 1 hour strengths had not reached 0.5N/mm2. Root cause: Awaiting issue of report from SCL Coordinator
| 02SL - Stations (LUL) | Cxxx-NCR-000325-L | NCR | AP7E Pilot Adv 100: Minimum thickness not reached and laminations showed |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2013-11-01 | 2013-09-16 11:05 | -46 | 2013-07-23 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During excavation of AP1 (Adv. 16, enlarge.), RHS thickness of AP7E Pilot Adv. 100 has been found below the 250 mm required and lining has showed pronounced lamination. Beamer profiles show thickness above 300mm within that area and insufficient readings in the invert. Primary profile looks also ok.
| 02SL - Stations (LUL) | Cxxx-NCR-000326-L | NCR | Overspray of CH 1 ( I ) in AP7-W Enlargement |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2013-10-31 | 2013-09-06 11:10 | -55 | 2013-07-23 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete |  | Completed |  | Profile of primary lining in some locations in CH1 ( I ) is tight form the required profile Root Cause: The overspray spot is a human error. We assume that the as built measurements of the primary layer P2 were taken but due to the nature of the measurement, these small sections were not originally highlighted, therefore these overspray spots were not picked up during reviewing of these profiles. The reason for over spraying of this area is unknown although there is a visible offset between over sprayed area and rest of the tunnel wall.
| 02SL - Stations (LUL) | Cxxx-NCR-000326-W | NCR | Over excavation of PTW-E Advance 25 RHS |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-02-28 | 2012-12-18 12:07 | -72 | 2012-11-26 | Tunnelling - Excavation - Hand | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The top heading was over-excavated by ~350mm from crown round the RHS knee Root cause : Some issues with the Beamer during the excavation, it seemed as if the excavation shifted to the LHS. Whilst engineers trying to sort the problem giving intermittent information to the excavator driver. This unfortunately was the cause of the over dig as full engineering control was not given throughout.
| 02SL - Stations (LUL) | Cxxx-NCR-000328-L | NCR | AP1,adv 27 Non Adherence To RESS |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2013-12-08 | 2013-11-07 10:06 | -31 | 2013-07-26 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Primary Lining in the invert & sidewalls sprayed partially: L bars together with lower rebar have been sprayed in a continuity system covered but the total thickness has not been fully achieved. For a better understanding: Full ring was not complete during dayshift (grey area on sketch attached). The blue area (see area on sketch attached) was sprayed in nightshift.
| 02SL - Stations (LUL) | Cxxx-NCR-000329-L | NCR | PTW-W Pilot: Incorrect revision of the SCL Placement Checksheet |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2013-11-23 | 2013-09-24 13:58 | -60 | 2013-07-31 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | - During surveillance of 18/07/13, a wrong version of __ Form D3-37, Revision 6 has been found. Although the revision 6.0 is the relevant one, the form found was different: The line “Are there any panels for Early Strength tests taken?” was deleted and the box “RESS” has been replaced by “Chainage “on the top left of the sheet. - The wrong version has been used for advance 48 to 46 in PTW-W Pilot. (see Checksheets attached)
| 02SL - Stations (LUL) | Cxxx-NCR-000329-W | NCR | Fibre Content Failure |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-03-29 | 2012-12-18 12:18 | -101 | 2012-11-29 | Tunnelling - Tunnelling General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Sample number CR236 taken during spraying for advance PTE East Pilot Adv 28 at Whitechapel site fail to comply with min 28kg of fibre content for mix P1 35kg. Root cause : It's not possible to establish root cause from available data.
| 02SL - Stations (LUL) | Cxxx-NCR-000330-L | NCR | Hold Point not completed - SCL Placement Checksheet Section D - not signed/dated |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2013-11-22 | 2013-09-09 11:43 | -74 | 2013-07-31 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | • While looking to the green folders during the surveillance of the 18/07 it has been spotted that the Section D of the __-Form-D3-37 Shotcrete Placement Check sheet of PTW-W Pilot Adv 48 to 44 have not been signed by the __ Construction Responsible person, the __ QC and the CRL representative. Root Cause: • Lack of awareness
| 02SL - Stations (LUL) | Cxxx-NCR-000331-L | NCR | Core holes in PTE-E Pilot are not backfilled |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2013-11-22 | 2013-09-09 07:51 | -74 | 2013-07-31 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Reject | 4 (0.5-3k) | Complete |  | Completed |  | • The core holes from PTE-E Pilot have not been backfilled as they should have. Root Cause: • Negligence of Production Team
| 02SL - Stations (LUL) | Cxxx-NCR-000331-W | NCR | Lack of logging of depressurisation boreholes in PTE-East Pilot Tunnel |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-04-19 | 2013-04-18 12:58 | -1 | 2012-12-07 | Geotechnical Engineering - Geotechnical Engineering - General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | During drilling of depressurisation boreholes v1, v2 and v3 between advances 29 and 41 in PTE-E logging has not been done or has not been done with the required accuracy of 1m, respectively. Samples have not been taken for subsequent logging by the geologist/trained engineer. Root cause: No supervision by WJ/__ geologist. No proper instruction to drillers on logging and sampling in absence of geologist/engineer. No specification on RESS with respect to logging and sampling, see attached RESS PTE-E/06.
| 02SL - Stations (LUL) | Cxxx-NCR-000332-W | NCR | Damage to reinforcement during remedial works of CP2 thickening layers |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-06-21 | 2013-06-19 18:09 | -2 | 2012-12-21 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | Damage to reinforcement during remedial works of CP2 thickening layers. Remedial works to remove SCL to allow correct installation of reinforcement (refer to NCR WHI 316) has damaged reinforcement bars and lining considerably (See pictures attached) Root cause: Remedial work methodology was not validated, not documented and probably not adequate or was lacking some control measures to avoid the occurred result. CP2 North: • Photo 1: 2 x 32mm bars damaged , Bar Mark 33 a to g • Photo 2: 3 x 16mm bars missing, Bar Mark 70 / 71 • Photo 3: 3 x 16mm bars missing, Bar Mark 70 / 71 • Photo 4: 1 x 25mm bar missing, Bar Mark 90 a to x • Photo 4: 1 x 25mm bar damaged, Bar Mark 90 a to x • Photo 5: 2 x 16mm bars missing, Bar Mark 70 / 71 CP2 South: Photo 6: 2 x 25mm bars missing, Bar Mark 90 a to x Photo 6: 1 x 25mm bar damaged, Bar Mark 90 b to x Photo 7: 2 x 25mm bars damaged, Bar Mark 93 / 94 Sketch showing location of photos.
| 02SL - Stations (LUL) | Cxxx-NCR-000333-W | NCR | PTE East adv 68 - No flow test carried out and temperature recorded |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-04-12 | 2013-01-04 14:22 | -98 | 2012-12-13 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | • Spraying of Adv 68 completed with no flow test carried out. Root cause : • Lack of communication between Engineering and Lab department’s on site
| 02SL - Stations (LUL) | Cxxx-NCR-000334-W | NCR | CP2-S and PTW tunnels: Tunnel monitoring points used to support cables. |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-04-12 | 2013-01-30 12:55 | -72 | 2012-12-11 | Tunnelling - Tunnelling General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | • Cables and services on convergence monitoring targets. Root cause : • Lack of awareness of operatives on the importance and sensitivity of the targets and also of the requirements of the specification to not support tunnel services on the monitoring targets. Also that if for any reason a target has been damaged it must be reported and replaced as soon as possible to ensure monitoring of convergence can be maintained.
| 02SL - Stations (LUL) | Cxxx-NCR-000335-W | NCR | Information missing from early strength test sheets. |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-03-21 | 2013-01-28 11:56 | -52 | 2012-12-21 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Non-Conformance (10) : • PTW-E Advance 69, Delivery ticket number, flow, accelerator dosing and temperature missing from D3-33. • PTW-W Advance 56, penetrometer results missing from curve (0-3hr) Root cause (15) : • Due to a lack of time and personnel available to record results or a lack of care taken when completing the check sheets.
| 02SL - Stations (LUL) | Cxxx-NCR-000336-W | NCR | CP2 Nth Enlarg Adv 32 & 41: Shotcrete core strengths |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-08-02 | 2013-07-10 16:49 | -23 | 2012-12-07 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Core sample number CR0170 taken from advance 32 in CP2 Nth enlargement complied with the 28 day requirement as did the core results from sample number CR0173 attaining strengths of 39.8 & 47.4N/mm² respectively however, the 90 day results attained strengths of 34.8 & 38.5N/mm² respectively. CR0170 fails to comply with the minimum strength of 36N/mm² but CR0173 is compliant in this respect, these two results have increased the standard deviation that has caused failures on the running mean results. Root cause : There is no real apparent reason for this reduction in strength from 28 day’s to 90 day’s as there is no evidence of reduced density or excess voids in the core samples taken.
| 02SL - Stations (LUL) | Cxxx-NCR-000340-W | NCR | Lack of cores being taken in accordance with KT 20 |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-03-22 | 2013-02-06 15:06 | -44 | 2012-12-19 | Shafts - Shafts General | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | After advance 4 no cores have been taken for 3 day strength testing. Root cause : Unable to access shaft to carry out coring due to works being undertaken
| 02SL - Stations (LUL) | Cxxx-NCR-000341-W | NCR | Flow test taken 15 minutes after spraying had commenced gave flow test result of 660mm. |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-03-29 | 2013-03-19 11:50 | -10 | 2012-12-20 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | • Flow not taken prior to start. • Subsequent testing for flow variation monitoring not completed and therefore Flow Variation Form not completed. Root cause : • Laboratory technician distracted by coring duties in tunnel and did not communicate with Engineers the need for assistance.
| 02SL - Stations (LUL) | Cxxx-NCR-000344-W | NCR | No Estimated Fibre & Aggregate Rebound CP2 |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-05-03 | 2013-02-08 11:00 | -84 | 2013-02-05 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | No test on the fibre and aggregate rebound was carried out for the duration of CP2 construction. Root cause : • It has not been cascaded as being an important test and site has overlooked the carrying out of the test.
| 02SL - Stations (LUL) | Cxxx-NCR-000349-W | NCR | Lack of cores being taken in accordance with KT 20 (WHI - PTE East & LIV – CP5) |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-04-15 | 2013-02-15 10:43 | -59 | 2013-01-15 | Tunnelling - Tunnelling General | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | Lack of cores being taken in accordance with KT 20. Approximate affected locations: - WHI - PTE East Advance 108, PTW West Advance’s 66 & 76. - LIV – CP5 Advance 24. Root cause : Unable to access shaft to carry out coring due to works being undertaken and several sickness days in material team.
| 02SL - Stations (LUL) | Cxxx-NCR-000350-W | NCR | Insufficient welds to Sainsbury Carpark Column Shear Key (Temporary Works) |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-04-26 | 2013-02-07 11:51 | -78 | 2013-01-24 | Utilities Engineering - Utilities General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | The initial welds to the shear key clamps for columns A7, A8, A9, A10, A11, A13 and A14 were less than the specified 12mm filet weld Root cause: Welder did not follow design drawings.
| 02SL - Stations (LUL) | Cxxx-NCR-000351-W | NCR | Fan Support Steel Frame South: On site welding’ checked and some failed |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2013-10-25 | 2013-09-18 14:38 | -37 | 2013-02-21 | Structural Engineering - Welding | 2000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Welds on the items inspected were not all as per the drawing in terms of weld thickness and length. (4mm fillet weld had been used instead of the stated 6mm or 8mm). Root cause : • Fitter foreman/charge hand fitter not inspecting work that has been undertaken by site welders against the drawings • Site management have not inspected items welded against drawings.
| 02SL - Stations (LUL) | Cxxx-NCR-000354-W | NCR | Drilling and installing of inclinometer casing – Spiral Test out of specification criteria. |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-08-09 | 2013-07-31 16:31 | -9 | 2013-03-13 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Reject |  | Complete |  | Completed |  | Borehole Cxxx-IM50501; Borehole Cxxx-IM50502; Borehole Cxxx-IM50503; The installed casing was over the maximum spiralling threshold of 0.75o per metre as specified in Cxxx – M&W Specification KX10 – Instrumentation & Monitoring Cxxx-OVE-Z4-RSP-CR001-00007 Section KX10.3212 (e). Root Cause: It is unclear why spiralling was outside of specified limits as correct installation procedure was followed by experienced staff, and the installation have been witness by __ management and CRL.
| 02SL - Stations (LUL) | Cxxx-NCR-000355-W | NCR | Lack of readings and clarity on profile checks of CS1 |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-04-19 | 2013-02-25 10:24 | -53 | 2013-01-25 | Shafts - Alignment | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | All advances profile results unclear, incomplete, un signed, no diagram for layout of check positions. Root cause : • Lack of awareness of the engineers of the importance of results and the requirement for them to be part of the deliverable information. • Supervision and management not checking results and notifying of missing information.
| 02SL - Stations (LUL) | Cxxx-NCR-000360-W | NCR | Grouting of probe hole not carried out before next Advance. |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-05-17 | 2013-05-16 17:08 | -1 | 2013-02-07 | Tunnelling - Grouting | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Probe hole in Advance 112 was not grouted before moving on to Advance 113. Root cause : • Mis-communication between shift teams as to completion of grouting procedure.
| 02SL - Stations (LUL) | Cxxx-NCR-000362-W | NCR | Form D3-05 not used - CS1 |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-04-26 | 2013-02-14 15:43 | -71 | 2013-02-04 | Shafts - Shafts General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | For CS1 shaft form D3-05 form was not used. Deliverable item column on ITP not selected as either deliverable or not. Root cause : • Seen as a form that was not required as all information was being captured on the form D3-37 Shotcrete Placement Checksheet • Not selected as either deliverable or not, and so with above comment not used
| 02SL - Stations (LUL) | Cxxx-NCR-000363-W | NCR | CS1: Form D3-37 Pre shotcrete checksheet not completed fully |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-05-24 | 2013-02-25 10:44 | -88 | 2013-02-14 | Shafts - Shafts General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Advances 1- 17 and Thickening C5 – Some forms with no reference to flow/temp/air temp 2.1 – Differing checks carried out, some vault profile checks checked while some state N/A and others nothing marked up 3.3 – Advance numbers/stages incomplete or unclear 4.1 – Advance numbers/stages incomplete or unclear, signature boxes not filled by CRL/QA, 4.2 – Signature/initialling not completed, 4.3 – No checks on __ carried out or referenced for first stages Root cause : • Lack of awareness of the engineers of the importance of results and the requirement for them to be part of the deliverable information. • Supervision and management not checking results and notifying of missing information.
| 02SL - Stations (LUL) | Cxxx-NCR-000364-W | NCR | Voids behind CP2 reinforcement |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-06-07 | 2013-06-07 15:37 | 0 | 2013-02-04 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | • Voids behind reinforcement discovered on tests carried out in various locations of CP2 wraparound thickening. Root cause : • Density of reinforcement in wraparound making it difficult to achieve full encapsulation. • Nozzleman not operating spraying robot from a suitable location to see if full encapsulation is achieved.
| 02SL - Stations (LUL) | Cxxx-NCR-000367-W | NCR | Failure of R28 Modulus of Elasticity |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-04-19 | 2013-02-18 13:07 | -60 | 2013-02-05 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Modulus of Elasticity failure on cores taken from WHI site PTW West Pilot Adv 6 (see attached results ) limits given in KT20 rev 13 are 31.9 N/mm2 and we get average 31.66 N/mm2. Root cause : It’s difficult to point out any particular reason for such marginal failure of 0.23 GPa. This may be related to workmanship – quality of cores.
| 02SL - Stations (LUL) | Cxxx-NCR-000368-W | NCR | The temperature of the mix |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-04-05 | 2013-02-14 11:14 | -50 | 2013-02-06 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The concrete temperatures are not measured at the point of placing
| 02SL - Stations (LUL) | Cxxx-NCR-000373-W | NCR | CS1 Early Strength Result Sheets |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-05-10 | 2013-04-16 11:54 | -24 | 2013-02-11 | Shafts - Shafts General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | For CS1 shaft form D3-33 form not completed fully. Root Cause: Engineers not aware of the importance of completing the forms fully.
| 02SL - Stations (LUL) | Cxxx-NCR-000376-W | NCR | Vallance Gardens : Data from Piezometers in WH60 seems to be unreliable. |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-05-30 | 2013-03-22 14:03 | -69 | 2013-02-22 | Geotechnical Engineering - Geotechnical Engineering - General | 500 |  | Equipment Breakdown | Use As-Is |  | Complete |  | Completed |  | Data obtained from 3 No vibrating wire piezometers installed in borehole Piezometers in WH60 seems to be unreliable, see pages 2 to 4 of this NCR. Root cause : Root cause cannot be identified definitively. Possible root causes are listed below: • Lack of supervision during installation of piezometer. • Interference with power cables.
| 02SL - Stations (LUL) | Cxxx-NCR-000379-W | NCR | Lack of monitoring for Total Suspended Solids (TST) |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-05-24 | 2013-04-18 13:21 | -36 | 2013-02-08 | Geotechnical Engineering - Geotechnical Engineering - General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | Lack of monitoring for Total Suspended Solids (TSS) during pumping for depressurisation. __ are not carrying out this test since the beginning of the project and therefore are not compliant. Root cause : During a meeting with CRL on 15th January 2013, __ discussed the issue of monitoring TSS. It has been agreed by all parties that the requirements and trigger given in clause KT22.3301 are too tight. Proposals were discussed but no relaxation to the specification has been agreed through an RFI yet. The RFI is in progress under WHI-CRL RFI-Cxxx-00388.
| 02SL - Stations (LUL) | Cxxx-NCR-000382-W | NCR | PTE/W Pilot Adv 108 &109: Not following correct RESS |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-07-31 | 2013-05-30 13:43 | -62 | 2013-02-12 | Tunnelling - Excavation - Hand | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | The enlargement should have started at Adv 108, but Adv 108 & 109 was constructed to +30mm. Root cause : Misunderstanding and lack of communication, RESS PTE-W/10 covered pilot advances up to and including 110 and RESS PTE-W/12 started at 108 so there was an overlap in “live” documentation The SRG minutes from DS 10/02/13 which stated ‘Next RESS starts at advance 108’ was not distributed until DS 11/02/13 which unfortunately was after 108 & 109 had been excavated.
| 02SL - Stations (LUL) | Cxxx-NCR-000391-W | NCR | Flow test not done for Adv.123 PTE-W |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-05-31 | 2013-04-16 12:27 | -45 | 2013-02-21 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Initial Flow test not done as required per ITP Cxxx-__M-C4-ITP-CR092-50001 & ref Cxxx-__M-C-ASD-50021. Root cause : • The technician was unaware that batching had started when he became aware, he did the first flow for batch 4684 with a result of 570mm flow.
| 02SL - Stations (LUL) | Cxxx-NCR-000392-W | NCR | Adv. 115 PTE-W Right Knee, SCL Cores less than min. required length |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-06-28 | 2013-06-19 19:15 | -9 | 2013-02-21 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Cored samples taken from the PTE - W Pilot Tunnel show an area on the right hand knee of Adv 115 was less than 250mm. The beamer profile reports show that the area had sufficient thickness. Root cause : • Localised thin area of SCL, poor workmanship in setting out the excavation and primary lining profiles.
| 02SL - Stations (LUL) | Cxxx-NCR-000394-W | NCR | Grout Strength did not conform to ITP specified value. |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-04-30 | 2013-02-27 15:29 | -62 | 2013-02-21 | Geotechnical Engineering - Compensation Grouting | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | The following grout mixes were found not to achieve the ITP stated value of 1.5MPa for average 28 day compressive strength: Cube NoC0374 which was sampled on the 13th July 2012. Average strength @ 28 days 2.0MPa. Cube NoC0387 which was sampled on the 17th July 2012. Average strength @ 28 days 1.0MPa. Cube NoC0388 which was sampled on the 18th July 2012. Average strength @ 28 days 1.0MPa. Cube NoC0403 which was sampled on the 19th July 2012. Average strength @ 28 days 1.0MPa. Cube NoC0404 which was sampled on the 20th July 2012. Average strength @ 28 days 1.0MPa. Cube NoC0405 which was sampled on the 23rd July 2012. Average strength @ 28 days 1.0MPa. Cube NoC0414 which was sampled on the 24th July 2012. Average strength @ 28 days 2.0MPa. Cube NoC0415 which was sampled on the 25th July 2012. Average strength @ 28 days 2.0MPa Cube NoC0416 which was sampled on the 26th July 2012. Average strength @ 28 days 2.0MPa Cube NoC0418 which was sampled on the 2nd August 2012. Average strength @ 28 days 2.0MPa Cube NoC0439 which was sampled on the 3rd August 2012. Average strength @ 28 days 1.0MPa. Cube NoC0453 which was sampled on the 7th August 2012. Average strength @ 28 days 1.0MPa. Cube NoC0470 which was sampled on the 16th August 2012. Average strength @ 28 days 1.4MPa. Cube NoC0759 which was sampled on the 15th November 2012. Average strength @ 28 days 0.6MPa. Cube NoC0760 which was sampled on the 16th November 2012. Average strength @ 28 days 1.1MPa.
| 02SL - Stations (LUL) | Cxxx-NCR-000395-W | NCR | Grout viscosity did not conform to ITP specified range. |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-04-30 | 2013-02-27 15:33 | -62 | 2013-02-21 | Geotechnical Engineering - Compensation Grouting | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Grout viscosity was not within the ITP specified tolerance range. Root cause : The cement bentonite grout is designed to be a low viscosity grout with good pumpable qualities. The specified range of viscosity given in the ITP is 38-40 seconds, but achieving the specific target range given in the ITP was impractical. A larger range of viscosities should have been specified in the ITP.
| 02SL - Stations (LUL) | Cxxx-NCR-000399-W | NCR | Shotcrete Early strength results failed |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-08-30 | 2013-08-09 16:24 | -21 | 2013-03-12 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | PTW-W 138, 137, 158, PTE-W 118, 115, 112. Tests showed that after 1hour strenghts had not reached 0.5 N/mm2. Root Cause: See report from SCL Coordinator - Delayed Early Strength Gain - November 2012 - Cxxx-__M-C4-RGN-CR092-50004.
| 02SL - Stations (LUL) | Cxxx-NCR-000401-W | NCR | W - CP2 North Walkway: welding checked and some failed |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-07-25 | 2014-03-17 14:33 | -130 | 2013-02-27 | Structural Engineering - Welding | 3000 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Site welds on CP2 North walkaway were inspected on 04/02/2013 and some welds were not as per the drawing in terms of weld thickness and length. See attached __ Report 47512J SR 04 KB (see att 1) for all details: 1. Triangular decking extension – W9 and N5 2. End plate extensions Location 1 – W9 3. End plate extensions Location 2 – W9 4. End plate extensions Location 3 – W9 5. End plate extensions Location 4 – W9
| 02SL - Stations (LUL) | Cxxx-NCR-000402-W | NCR | Ventilation Support Brackets: welding checked and some failed |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-06-03 | 2013-05-31 14:21 | -3 | 2013-02-27 | Structural Engineering - Welding | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Site welding on the ventilation support brackets were inspected and some welds (East Bracket, Centre Bracket, West Bracket) were not conformed in terms of weld thickness, length and surface breaking defects. (See __ Report attached). Root cause : • Welder did not follow design on drawings • Fitter foreman/charge hand fitter not inspecting work that has been undertaken by site welders against the drawings • Site management have not inspected items welded against drawings.
| 02SL - Stations (LUL) | Cxxx-NCR-000403-W | NCR | PTE West adv 117 - No flow test carried out and temperature recorded |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-05-31 | 2013-04-16 12:42 | -45 | 2013-02-26 | Tunnelling - Tunnelling General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | • Spraying of Adv 117 completed with no flow test carried out. Root cause : • Lack of communication between Engineering and Lab department’s on site
| 02SL - Stations (LUL) | Cxxx-NCR-000404-W | NCR | Calibration of the pumps has not been performed annually as per the relevant instructions |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-02-28 | 2014-02-03 10:02 | -25 | 2013-03-05 | Geotechnical Engineering - Compensation Grouting | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Last third-party calibration of the flowmeters and pressure gauges of the pumps was in March 2011. The calibration should be performed annually by an external certified organization.
| 02SL - Stations (LUL) | Cxxx-NCR-000406-W | NCR | Poor Encapsulation of rebar |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-08-16 | 2013-06-19 18:32 | -58 | 2013-03-06 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Reinforcement bars were not fully encapsulated as voids were shown on core log CR0398B taken from the thickening Right Crown& CR0398E from the thickening Right Shoulder. Root cause : Investigation are under progress. See Spraying Reinforcement Report (Cxxx-__M-C4-RGN-CR092-50003 rev 3.0).
| 02SL - Stations (LUL) | Cxxx-NCR-000415-W | NCR | 2 additional cores at CP1a drilled without approved RESS |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-06-27 | 2013-06-06 12:33 | -21 | 2013-03-28 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | No RESS has been issued for the 2 additional core holes at CP1a Pilot. • RESS has been issued for 4 cores only. • On 25.02.13, location for 4 cores has been defined by RESS WHI PTE-W14. On 26.02.13 additional cores have been discussed and agreed in the SRG (see attached extract of SRG Minutes) but no new RESS has been issued.
| 02SL - Stations (LUL) | Cxxx-NCR-000416-W | NCR | PTW – W Pilot, Adv. 202 excavated with +150mm enlargement instead of +30mm |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-08-30 | 2013-06-14 12:35 | -77 | 2013-03-15 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | • Adv. 202 in PTW – W excavated with +150mm enlargement instead of +30mm excavation. There was a late design change showing local enlargement of the pilot tunnel for the opening of the Bypass Tunnel (refer to Cxxx-__M-C4-DDB-D061-00193 rev C02) , this change came into effect at the end of what RESS PTW-W covered (RESS PTW-W/13, adv 183 to 202). It was so instructed to excavate +150mm to allow for the local enlargement (as agreed by RESS PTW/14, adv 202 to 211) but actually the beamer was already programmed to the enlarged cross section, adv 202 to 211. Therefore we over-excavate +150mm instead of +30mm. Root cause : • Late design change • Miscommunication between SCL Engineer/Design and Survey team • This was then changed next day with new RESS and survey control
| 02SL - Stations (LUL) | Cxxx-NCR-000421-W | NCR | Sewer Manhole Concrete Base Slab strength |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-07-12 | 2013-04-12 11:59 | -91 | 2013-04-10 | Utilities Engineering - Utilities General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The actual achieved strength at 28 days was 28.5N/mm2 as shown on the attached cube test results. Root cause: There was a typo on the ITP parameter and it should have read GEN3-C16/20 (16/20N/mm2 instead of 40N/mm2).
| 02SL - Stations (LUL) | Cxxx-NCR-000423-W | NCR | Nails’ distance on shotcrete test panels is less than 80mm |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-06-14 | 2013-06-06 13:54 | -8 | 2013-03-15 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | It was observed during a regular Surveillance at WHI on 12/03/2013 of PTE-E adv T3, that the distance between the __ nails on the panel was less than 80mm which is the minimum required distance between the nails according to BS EN 14488-2:2006 . See attached picture for evidence. A similar occurrence had been observed on an existing test panel during an equivalent surveillance at LIV site on 13/03/13. Root cause : Sometimes there is not enough space on the panel to shoot the nails with the proper distance and the Engineers prefer to shoot it closer to each others (which is wrong).
| 02SL - Stations (LUL) | Cxxx-NCR-000425-W | NCR | PTW East adv 71 pilot: No flow tests carried out and recorded |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-06-21 | 2013-04-17 09:34 | -65 | 2013-03-20 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | • Spraying of Adv 71 completed with no flow test carried out on 15/01/13. Root cause : • Lack of communication between Engineering and Lab department’s on site.
| 02SL - Stations (LUL) | Cxxx-NCR-000428-W | NCR | PTW East adv 98 - No flow test carried out |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-06-28 | 2013-06-06 12:22 | -22 | 2013-03-26 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | • Spraying of Adv 98 completed with no flow test carried out. Root cause : • Lack of communication between departments
| 02SL - Stations (LUL) | Cxxx-NCR-000431-W | NCR | Incorrect reinstatement of Granite edging Blind Beggar compound |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-07-12 | 2013-06-06 12:15 | -36 | 2013-04-10 | Utilities Engineering - Utilities General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Following completion of works outside the Blind Beggar pub (undertaken by __), the reinstated granite edging was replaced. However these granite edgings were not installed square. Root cause : • Operatives not following straight line.
| 02SL - Stations (LUL) | Cxxx-NCR-000432-W | NCR | 3 day strength testing not being taken |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-07-19 | 2013-06-14 12:50 | -35 | 2013-04-12 | Tunnelling - Tunnelling General | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | There are instances where cores for 3 day strength testing have not been taken. (see summary sheets attached) Root cause : There have been a number of factors such as access, site activities and staff issues that have prevented the cores from being taken.
| 02SL - Stations (LUL) | Cxxx-NCR-000433-W | NCR | No flow tests 1hr after initial test - PTE East adv 90 and PTW West 51 |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-07-19 | 2013-06-14 13:12 | -35 | 2013-04-16 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | • Simultaneous spraying of PTE-East Adv 90 & PTW-West Adv 51 completed with no follow-up flow tests carried out 1 hour after initial test. Root cause : • No lab technician on site – one day holiday no cover arranged. • Lack of availability of engineers to cover flow tests.
| 02SL - Stations (LUL) | Cxxx-NCR-000439-W | NCR | PTW-W enlargement, adv 68: Missed Flow Test |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-07-26 | 2013-06-14 13:41 | -42 | 2013-04-24 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | Flow test missed prior to start of spraying PTW-W Advance 68. Root cause : Lab technician not available at time.
| 02SL - Stations (LUL) | Cxxx-NCR-000440-W | NCR | PTW-E enlargement, adv 77: Over-excavation |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-07-26 | 2013-07-10 16:57 | -16 | 2013-04-24 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | PTW-E Advance 77 face profile observed to be over-excavated by up to 500mm. Root cause : • Beamer system program irregularly shutting down requiring re-setup during excavation. • Lack of engineering control. • Visual inspection would have revealed an overexcavation. • Visual judgement not used by any of the tunneling operatives or the engineers
| 02SL - Stations (LUL) | Cxxx-NCR-000441-W | NCR | PTE-E enlargement, adv 122: Over excavation |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-07-26 | 2013-06-06 14:21 | -50 | 2013-04-24 | Tunnelling - Excavation - Hand | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | • The top heading was over-excavated by ~600mm in the face of the top heading on the right and left side; approximately from access down to the eazistrip level (approximately 2.0m). Root cause : • The excavation of the adv 122 was more challenging due to small enlargement commencement in this advance. (Excavation from +100 to +225mm). Whilst excavator driver was trying to achieve the correct excavation tunnel wall profile with no intention to do so he over excavated the face of this advance ~600mm on the both sides of the face in approximately 2.0m of height.
| 02SL - Stations (LUL) | Cxxx-NCR-000448-W | NCR | Batched Materials Out of Tolerances |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-08-02 | 2013-06-14 14:08 | -49 | 2013-05-01 | Tunnelling - Tunnelling General | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | As it has been observed during the __ Surveillance No.10 (Cxxx-__M-O4-RGN-CR092-50021) the batched materials of the shotcrete exceeded the 3% tolerance. Root cause : Problem of the settings of the Batching Plant computer
| 02SL - Stations (LUL) | Cxxx-NCR-000449-W | NCR | Overexcavation of the lower part of the Adv. 90 on WHI – PTW-E enlargement |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-07-26 | 2013-07-10 17:01 | -16 | 2013-04-26 | Tunnelling - Excavation - Hand | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | The excavation of the lower part of the Adv. 90 on WHI – PTW-E is more than 1 m (see attachment). The gap between the Eazistrip and the face is circa of 0.5 m on the LHS. Root Cause: Mistake of the Operator and the Engineer
| 02SL - Stations (LUL) | Cxxx-NCR-000450-W | NCR | Sequence of works not followed in PTW – W: Adv. 80 (top heading) started instead of Adv. 79 |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-07-26 | 2013-06-19 18:22 | -37 | 2013-04-26 | Tunnelling - Excavation - Hand | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The sequence of works was not followed in PTW – W and therefore Adv. 80 (top heading) was started instead of Adv. 79 which is a double invert. Once the mistake was identified the top heading excavation was stopped and the invert was excavated however the opened top heading was not resealed with 75mm of shotcrete prior to invert excavation. Root cause : • Mistake by the mining gang and the supervision teams. • Misunderstanding and lack of communication between shift engineer and 944 operator: during few minutes at the beginning of the shift, the 944 operator start to excavate while the shift engineer was busy to install his beamer and was not ready to supervise. They saw the mistake few minutes after, they stopped and started again following the RESS.
| 02SL - Stations (LUL) | Cxxx-NCR-000457-W | NCR | CP2 South Knee and invert near the headwall no cured as per ITP |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-09-27 | 2013-07-23 13:04 | -66 | 2013-06-11 | Tunnelling - Tunnelling General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | • The CP2 South knee and invert near the headwall was not cured due to the invert backfilling after spraying. Root Cause: • It was assumed that the clay backfill allowed a proper cure preventing excessive water loss.
| 02SL - Stations (LUL) | Cxxx-NCR-000464-W | NCR | PTE-E Enlarg, Adv T1: Over excavation and Lack of inclination of the face |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-08-30 | 2013-07-08 15:59 | -53 | 2013-05-15 | Tunnelling - Excavation - Hand | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | • The excavation of adv. T1-PTE E enlargement transition was more than 2000 mm on the Right hand side and 1800 mm on the Left hand side. • The top was broken out by 600 mm and a straight face has been created instead of an inclined face as per RESS PTE E / 14. Root cause : • Workmanship mistake but considering the special geometry and the need to use a powerful/big excavator (944) the work is understandable.
| 02SL - Stations (LUL) | Cxxx-NCR-000465-W | NCR | PTE-E Enlarg, Adv.T4: No eazistrip on the RHS of T5 |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-08-16 | 2013-07-23 13:10 | -24 | 2013-05-15 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Due to over excavation on adv.T4 PTE E transition enlargement which included adv.T5 on the RHS on dayshift and spraying of initial lining and primary lining, a correction has been made on night shift. The remaining section of Adv.T5 has been sprayed (75 mm + 250 mm primary) on night shift where the eazistrip has been included on the LHS of T5, however there is no eazistrip on the RHS of T5. Root cause : • Mistake during construction
| 02SL - Stations (LUL) | Cxxx-NCR-000467-W | NCR | W - Welfare Unit and Shed Door Hoist Brackets: welding checked and some failed |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-08-26 | 2016-07-27 08:22 | -30 | 2013-05-31 | Structural Engineering - Welding | 2500 |  | System Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Welds on several locations failed the N__ Test during the inspection made by __ on 15/03/2103 and 03/04/2013, (see attachment 1: summary table): 1. Welfare Unit Sliding Prevention Plates x6 – N7: lack of root penetration in the centre of the weld of up to 4mm. (see attachment 2b: __ Report 47512J SR 20 KB) 2. Shed Door Modifications NE&NW (see attachment 3: __ Report 47512J SR 23 KB) a. NE door West Hoist Brackets – W9 b. NW door West Hoist Brackets – W9 c. NW door East Hoist Brackets – W9 e. NW door West stiffener – W9 Please note that RSA Brace connection brackets welds have been raised as a separate NCR: Cxxx-NCR-000725.
| 02SL - Stations (LUL) | Cxxx-NCR-000469-W | NCR | Site survey and setting out data traceability |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-08-09 | 2013-06-19 18:44 | -51 | 2013-05-23 | Tunnelling - Linings - Sprayed Concrete | 500 |  | System Defect | Rework |  | Complete |  | Completed |  | The Contractor provided a copy of his PTE-E Enlargement-Advance 117 – Excavation printout to demonstrate compliance , however review of the print out failed to find any details with respect to traceability as listed in the Technical Requirements.
| 02SL - Stations (LUL) | Cxxx-NCR-000473-W | NCR | PTE-E, enlargement: Missing Profiles for Adv 143 |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-09-20 | 2013-07-10 16:33 | -72 | 2013-06-11 | Tunnelling - Tunnelling General | 500 |  | Equipment Breakdown | Use As-Is |  | Complete |  | Completed |  | No Beamer Record available for Adv 13 of PTE-E, enlargement. Root cause : • Profile has been checked by the shift engineer but a data saving problem has occurred.
| 02SL - Stations (LUL) | Cxxx-NCR-000474-W | NCR | CP2 South: Defective cores results |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-07-13 | 2013-06-06 12:56 | -37 | 2013-06-04 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | • Remedial works to the thickening layers in the portals and headwalls of the CP2 South&North Wraparound have been carried out and defective core results have been found (see attached pictures of cores). Evidence of incomplete encapsulation has been observed particularly where bars cross. Root cause : • Under Investigation
| 02SL - Stations (LUL) | Cxxx-NCR-000475-W | NCR | PTE-W Enlargement Adv1, Overexcavation of the break out |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-09-20 | 2013-07-23 13:21 | -59 | 2013-06-03 | Tunnelling - Excavation - Hand | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The crown was overexcavated radially by 800mm to locally +1m. Root cause : • The excavator needs an attack angle to precede the excavation. This angle produce an over excavation due to the technical impossibility to follow break out excavation line
| 02SL - Stations (LUL) | Cxxx-NCR-000476-W | NCR | W - Compensation Grouting for Blind Beggar |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-04-11 | 2014-04-11 14:34 | 0 | 2013-05-31 | Tunnelling - Linings - Sprayed Concrete | 10000 |  | Supervision/Management | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Other | Completed |  | The following breaches of triggers and compensation grouting requirements (KC21/SCOGMS) were identified on the Blind Beggar (__): 1) A breach of amber slope trigger on east façade of Blind Beggar between LB50420 to LB50422 on 30/04/13 2)A breach of amber slope trigger on north façade of Blind Beggar between LB50420 to LB50446 on 05/05/13 Please note that the breaches above are i) based on __ data only (ie. does not include prisms data) ii) does not include amber slope triggers where the distance between __’s is generally less than approximately 10m. __ have failed to control the effect of the works on the Blind Beggar building, a very sensitive structure, where mitigation measures were proposed. This NCR has been raised to capture these trigger breaches and the following non-conformance with the specification:- 1) Failure to concurrently grout during the enlargement beneath the Blind Beggar, despite arrangements being made between CRL (EM) and __ to allow grouting within the SCL Exclusion Zones during PTW enlargement. 2) We understand that __ have not always been continuously on site when excavations requiring concurrent grouting are required (eg. when tunnelling beneath Blind Beggar), which is in contradiction to KC21.1201(d). If __ were present on site it appears that no effort was made to undertake concurrent grouting over the weekend of 27/04/13 (see chronology below). 3) The Contract requires the Contractor to “limit ground settlements as far as practicable” and ensure settlement does not produce “i) a slope between any adjacent monitoring points in excess of 1/1000 and ii) a deflection ratio …. in excess of 1/2000.” Failure to limit settlements at the extreme edge of the compensation grouting array (ie. NE corner of __) has resulted in excessive differential settlements breaching amber slope triggers. 4) It should be noted that __ did not amend their standard 50 litre injection despite not being able to halt settlement and control differential movements. KC21.3222 h) and i) provide guidance on this issue. We understand that the property owners/representatives have reported additional cracking to their buildings which appear to be coincident with these breaches of slope triggers. Chronology: On Friday 26/04/13, PTW east enlargement had just passed beneath the north west corner of the Blind Beggar. At the Shift Review Group (SRG) meeting, it was agreed that compensation grouting (CG) above the tunnel (ie. above fresh concrete) would continue provided the agreed 5mm in-tunnel alert was not breached. In addition, __ presented a programme of compensation grouting which included the __ building; however the CG daily report provided in the SRG minutes of 27/04/13 does not indicate that any grouting took place beneath the __ on 26/04/13. On Saturday 27/04/13, the SRG minutes record that CG will continue above the ”young concrete” and that monitoring data will be checked before and after each grouting episode. However, there is no programme included in the minutes to suggest that __ were proposing to grout below the __ despite tunnelling underneath. In addition, the daily report for grouting on Saturday was not presented at the SRG until Monday, which showed no grouting beneath the __. On Sunday 28/04/13, the SRG minutes record that grouting was stopped at ~15:30 due to a computer problem; however tunnelling continued. On 29/04/13 an amber slope trigger (over 7m distance) was noted on the east façade. The slope worsened over the next few days with an amber slope trigger breached (on 30/04/13) along the full length of the east façade and along the north façade on 05/05/13. Crossrail Asset Protection team raised the issue of a lack of CG beneath the __ at the SRG on 29/04/13, and __ presented a programme for extensive grouting beneath the __. The grouting undertaken was not sufficient to arrest settlement especially beneath the NE corner of the building. A Contract Technical Committee (CTC) was held and __ presented proposals to improve the differential settlement occurring to the __. It took until 7 May before differential slopes started to improve, when a reaction at the NE corner started to occur. During the intervening period we suggested that __ consider increasing the volume of grout per injection and consider doing more injections depending upon reaction, which was eventually taken on board. In summary, the monitoring data indicated that settlement to the __ from the enlargement approximately commenced on 26/04/13. The lack of concurrent grouting between 26-28 April and subsequent lack of reaction to grouting (especially at NE corner) has resulted in a maximum settlement of 25mm and slopes of less than 1 in 600. We understand that the __ reported additional damage to their building in and around the dates of these trigger breaches.
| 02SL - Stations (LUL) | Cxxx-NCR-000478-W | NCR | Removal of rebound layer from Invert of Advance 7, PTW East Platform Tunnel Enlargement |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-09-27 | 2013-07-23 13:30 | -66 | 2013-06-07 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | • Advance 7, an invert was completed on 03/06/13. Upon excavation of the subsequent invert, Advance 10, a layer of encapsulated rebound was found between the initial and primary lining of the previous invert advance. This was noted by the shift engineer and miner and reported to the PIC and Inspectors who witnessed the removal of the rebound and SCL back to solid concrete. Root cause : • The primary lining was sprayed without adequate attention to cleanliness or removal of rebound material before or during the spraying process.
| 02SL - Stations (LUL) | Cxxx-NCR-000484-W | NCR | No Backboards in MON1 Telemetry Bollards |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-07-26 | 2013-07-08 10:03 | -18 | 2013-06-11 | Utilities Engineering - Water | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Backboards have not been installed in MON1 Telemetry Bollards as detailed in PMI 351. This has resulted in aborted visits from UK Power Networks who require backboards in order to complete the connection works. Cancellation fees will apply.
| 02SL - Stations (LUL) | Cxxx-NCR-000485-W | NCR | No flow tests carried out for Adv. 27 in PTE - W and Adv. 18 in PTW – W |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-10-25 | 2013-08-16 15:47 | -70 | 2013-06-14 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Flow test missed prior to start of spraying WHI PTE-W Enlargement Adv 27 (2nd top heading) and WHI PTW-W Enlargement Adv 18 (invert) during the night shift of 11/06/2013. Root cause : •Lack of availability of Lab technician & shifts engineers at time of the flow. •Lack of people trained to carry out the flow tests when lab technicians and shifts engineers not available.
| 02SL - Stations (LUL) | Cxxx-NCR-000486-W | NCR | Reprofiling of the primary shotcrete lining |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-10-04 | 2013-08-16 15:56 | -49 | 2013-06-19 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | Trimming of WHI PTW-E adv 36 without prior notification from SRG. The result is a that some areas of re-profiling now have a residual thickness less that the designed primary lining. Root Cause: • Mix-up in beamer profiles between two shifts. • Decision taken quickly with a lack of communication.
| 02SL - Stations (LUL) | Cxxx-NCR-000491-W | NCR | No initial flow test conducted PTE East Advance 62 |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-09-06 | 2013-07-10 16:36 | -58 | 2013-06-18 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Flow test missed prior to start of spraying PTE-EAST Advance 62. Root cause : • Lab technician not available at time.
| 02SL - Stations (LUL) | Cxxx-NCR-000492-W | NCR | No flow tests carried out for Adv. TB in PTE - E and Adv. 35 in PTW – W |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-10-04 | 2013-07-23 13:35 | -73 | 2013-06-19 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Flow test missed prior to start of spraying WHI PTE-E Enlargement Adv TB (Transition) and WHI PTW-W Enlargement Adv 35 (2nd Top Heading) during the night shift of 15/06/2013. Root Cause: • Lab technician was not available at time because he was coring and the engineer was not informed.
| 02SL - Stations (LUL) | Cxxx-NCR-000494-W | NCR | Low Residual Flexural strength |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2013-09-27 | 2013-09-11 18:46 | -16 | 2013-06-21 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | WHI beam set CR0582 for May has achieved a D3 result of S1.3 at 28 days that is marginally below the specification limit. Root cause : The actual root cause has not yet been identified it could have been the method of spraying, fibre distribution or damage in transit but, as required in the specification we have beam samples for 90 day testing that could close this out.
| 02SL - Stations (LUL) | Cxxx-NCR-000495-W | NCR | Inclinometers functionality |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-08-30 | 2013-07-31 16:48 | -30 | 2013-06-21 | Surveying - Instrumentation and Monitoring | 500 |  | System Defect | Reject |  | Complete |  | Completed |  | Management of installations and data review failure in relation to inclinometers. In addition the inclinometes are not providing reliable data. Non compliance issues: 1)Cxxx-OVE-C2-DDJ-CR001_Z-31521 & Cxxx-OVE-C2-DDA-CR001_Z-31521 The inclinoemters are providing unreliable data. CRL is expecting to obtain reliable data from the inclinometers installed at the frequencies specified in the drawings. 2)KX10.2101i i) “The Contractor will also be responsible for the collection, processing, storage, interpretation and reporting of the data” – and SCOGM 2.1.1.8 and 2.1.1.17. There is a lack of interpretation of the inclinometer data. 3)KX10.2101 “The Contractor is responsible for the design, procurement, calibration, quality assurance, installation, commissioning, maintenance, monitoring and removal of the instrumentation and monitoring equipment”. Evidence to date suggests that the commissioning (supposed to be undertaken immediately after installation (KX10.1202) and maintenance (as defined in KX10.1202) has not been undertaken “to ensure that instrumentation is kept in good working order, to guarantee the constant operation and availability of accurate and precise monitoring data.” 4)KX10.1203 “Monitoring shall then continue throughout construction and for a period thereafter until the rate of change reduces to an acceptable threshold” – and SCOGM 2.1.1.7. __ have not undertaken monitoring at the required frequency as detailed in the I&M Schedule (Cxxx-OVE-C2-DDJ-CR001_Z-31521). An example of this is at IM50502A (Brady Street), where the manual monitoring ceased on 04/04/13 and we are still yet to receive any further data. 5)KX10.2101e – “.. procedures for validation including testing, auditing of the accuracy, reliability and frequency of monitoring, data processing and reporting and for the review of performance” – and SCOGM 1.1.2.2. There is no quality control from __ to validate and audit the accuracy and the reliability of the data. The CMP states that “actions on corrupt readings / monitoring points” will be passed onto the monitoring team. The recent meetings held between CRL and __ to resolve the issues identified with the inclinometer results presented have not been addressed despite unexplained movements. 6)KX10.1201m – “Contractor responsibilities include “maintenance and repair or replacement of damaged instrumentation.” – and KX10.3202 g) After automation the instruments are providing unreliable data. __ has not put in place any proposal to rectify the issue (eg. carry out manual readings of the instruments in question), CRL is not being informed of non-functioning instruments 7)KX10.2112d ii) – “The contractor shall include in his weekly report “Assessment of the cause of anomalous readings such as reading or data reduction errors” – and KX10.3202 d) This is not being undertaken. 8)KX10.2201b – “adequate precautions shall be taken to protect the instrumentation from harmful effects of groundwater. Instrumentation found to be malfunctioning at any time shall be replaced at the earliest opportunity”. __ is not complying with this requirement (eg. IM50502A). 9)KX10.3201 e) “The Contractor shall provide the Project Manager with 24 hours notice of his intention to install instrumentation”. No notice was provided to the CRL PM in relation to the automation of the inclinometers at WHI.
| 02SL - Stations (LUL) | Cxxx-NCR-000496-W | NCR | Incorrect triggers used for Albion water cells |  | Contr | OVE | WHI - Whitechapel Station (Central) |  | 2014-02-15 | 2013-12-03 13:44 | -74 | 2013-06-26 | Surveying - Instrumentation and Monitoring | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Incorrect slope triggers have been applied to the water cells in the Albion basement and as such a number of amber triggers have been breached:- G: 1 in 1250 A: 1 in 1000 R: 1 in 500 We understand that these slope triggers were implemented on the graphs supplied by __ and relied upon by __ for compensation grouting purposes. It also appears that the automated data (water cells) has not been checked against the manual retro data, as some slopes have also breached amber triggers. These slope trigger breaches occurred in mid to late April 2013. One water cell has currently breached the amber slope trigger by 40%. The amber trigger breaches range from 1 in 753 to 1 in 965. A query was initially raised in early May 2013 for __ to investigate why there were differences between manual and water cell data for Albion basement. This was undertaken by __ survey team who explained the issue in the SRG some weeks back. One of the actions was for __ to correct these triggers but this has yet to be undertaken. Please also note that __ stated they rely (at least partially) on the triggers shown by __.
| 02SL - Stations (LUL) | Cxxx-NCR-000499-W | NCR | Missing ITP documentation in Asbestos removal deliverables |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-09-20 | 2013-07-10 16:40 | -72 | 2013-06-28 | Civil - Demolition/Site Clearance | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | • Several sections that have been stated as deliverable information does not have any supporting documents available. (See attached ITP checksheet for information not available). Root cause : • The information that was not gathered was part of a very extensive list of documents that were proposed as deliverable. The ITP was an “early” ITP and the deliverable section was not fully understood. All were marked as “Y” deliverable. • Subcontractor did not assemble all required information at the time of the works.
| 02SL - Stations (LUL) | Cxxx-NCR-000501-W | NCR | Flow Test out of tolerance |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-09-27 | 2013-07-23 13:42 | -66 | 2013-07-03 | Tunnelling - Linings - Sprayed Concrete | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | • Result for flow test carried out on 24/05/13 for spraying in CP2 North is 540mm which is out of the range allowed by the approved ITP. • Batch has not been rejected. Root Cause: • Misunderstanding of batcher and construction team caused by the numerous revisions of the ITP, MSTs and discrepancy before the different documents.
| 02SL - Stations (LUL) | Cxxx-NCR-000502-W | NCR | Overspray PTE-E CH 50.0 -52.0m |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2013-10-11 | 2013-09-03 17:38 | -38 | 2013-07-03 | Tunnelling - Linings - Sprayed Concrete | 1898.04 |  | Workmanship | Repair | 4 (0.5-3k) | Complete |  | Completed |  | • Profile of primary lining at CH50.7 area is max -79mm from required profile. Root Cause: • This explanation is the only best guess due to amount of time elapsed from the time we sprayed this advances. The most likely explanation for overspray spots is a human error. We assume that the as built measurements of the primary layer P2 were taken before and after the CH 50.7m therefore these overspray spots were not picked up during reviewing of these profiles. The reason for over spraying of this area is unknown although there is a visible offset between over sprayed area and rest of the tunnel wall.
| 02SL - Stations (LUL) | Cxxx-NCR-000505-W | NCR | Overspray to chambers VA2 & VA4 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2013-10-25 | 2013-08-29 18:49 | -57 | 2013-07-10 | Tunnelling - Linings - Sprayed Concrete | 1656.78 |  | Workmanship | Repair | 4 (0.5-3k) | Complete |  | Completed |  | • Profile of primary lining in some locations between CH91 & CH101 in both headings is tight by around 50 mm from the required profile. Root Cause: • This explanation is the only best guess due to amount of time elapsed from the time we sprayed this advances. The most likely explanation for overspray spots is a human error. We assume that the as built measurements of the primary layer P2 were taken but due to the nature of the measurement, these small sections were not originally highlighted, therefore these overspray spots were not picked up during reviewing of these profiles. The reason for over spraying of this area is unknown although there is a visible offset between over sprayed area and rest of the tunnel wall.
| 02SL - Stations (LUL) | Cxxx-NCR-000506-W | NCR | Fall of SCL during spraying of thickening on the south eye of CP3. |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-10-18 | 2013-08-16 16:11 | -63 | 2013-07-08 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Repair |  | Complete |  | Completed |  | • A fall of SCL occurred during the spraying of the first layer of CP3 Primary Lining Thickening South. Root Cause: • Inconclusive, all of the parameters for spraying were as per the agreed procedure.
| 02SL - Stations (LUL) | Cxxx-NCR-000507-W | NCR | Nonconforming Cores of week ending 05/07/2013 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2013-10-25 | 2013-09-11 18:19 | -44 | 2013-07-08 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | PTW-W-Adv176-LK-WHI-CR0726 and PTW-W-Adv182-RK-WHI-CR0727: • Cores are shorter than required in the design. • There are cracks in the cores. • There are some laminations in the cores. • There are significant voids and/or honey combing in the cores. Root Cause: Bad workmanship
| 02SL - Stations (LUL) | Cxxx-NCR-000510-W | NCR | PTW-W, enlarg, Adv 244: Thin areas in the invert profile |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2013-09-20 | 2013-09-12 15:30 | -8 | 2013-07-12 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete |  | Completed |  | There were some areas identified with thickness less than required as per Whitechapel SCL Design Package 3 in the invert and left side profile. ROOT CAUSE: The most possible reason for short spray in this area is that the adv 244 is positioned in the transition from PTW West into CP1a thickening and change of tunnel alignment in this area. As experienced before under specific circumstances using of the Beamer in the transition areas can cause that readings may be slightly deteriorated. Also a human error may be another possibility for this short spray.
| 02SL - Stations (LUL) | Cxxx-NCR-000512-W | NCR | PTW-E Adv 89: Missing 1h early strength test |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2013-11-08 | 2013-09-02 19:33 | -67 | 2013-07-25 | Tunnelling - Tunnelling General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | On 23/04/13, night shift, 1h early strength test is missing. Root Cause: Lack of organisation and planning on site.
| 02SL - Stations (LUL) | Cxxx-NCR-000514-W | NCR | The provision of contemporaneous records |  | Crossrail | PDP | WHI - Whitechapel Station (Central) |  | 2013-11-29 | 2013-09-23 16:54 | -67 | 2013-07-17 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Quality Surveillance QS510-18 found Cxxx-__M-04-STP-CR092-50007 rev 3 was at code decal 2 since 29/02/2012 and Cxxx-__M-O4-TSC-CR092-50003 rev 6 was code decal 2 since 22/02/2013. The code decal 2 status stands for ” Not accepted, revise and resubmit work may proceed subject to incorporation of changes indicated” The concrete batching quality management system was therefore not current at the time of this surveillance as the required changes were not incorporated
| 02SL - Stations (LUL) | Cxxx-NCR-000515-W | NCR | Localised thin area in the shoulder of PTW-W Enlargement Advance 243 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2013-10-31 | 2013-09-12 15:25 | -49 | 2013-07-22 | Tunnelling - Linings - Sprayed Concrete | 2000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete |  | Completed |  | • The SCL primary lining on this advance, in this area, RH Shoulder, was to be a minimum thickness of 325mm as per the RESS PTW-W/25. • After a set of cores was taken from the RH shoulder it was found that the thickness was less than 325mm in this area. • A set of proof drilling was carried out on a 3.0m x 3.0m grid every 500mm to determine the extent of the thin area. • A survey was also taken using the tunnel beamer to see if the areas had been under sprayed.
| 02SL - Stations (LUL) | Cxxx-NCR-000518-W | NCR | Missing Lab 3 day tests |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2013-11-29 | 2013-09-02 19:09 | -88 | 2013-07-18 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate resources | Completed |  | There are instances where cores for 3 day strength testing have not been taken. Root Cause: There have been a number of factors such as access, site activities and staff issues that have prevented the cores from being taken.
| 02SL - Stations (LUL) | Cxxx-NCR-000519-W | NCR | Removal of pocket of rebound in primary lining before spraying CP3 North Thickening Eye |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-11-08 | 2013-07-31 12:22 | -100 | 2013-07-23 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | • During the preparation works for the first layer of thickening around CP3 north eye an area of incorporated rebound was found in the primary lining of PTE-E. • The area, which was approximately 0.5m x 0.5m square and 250mm deep, was removed by mechanical means. Root Cause: • During the spraying of the primary lining this area was not sprayed properly and a pocket of rebound was encapsulated into the primary lining.
| 02SL - Stations (LUL) | Cxxx-NCR-000520-W | NCR | Overspray in invert areas between advance 70 and advance 88 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2013-10-31 | 2013-09-03 16:20 | -58 | 2013-07-24 | Tunnelling - Linings - Sprayed Concrete | 1898.04 |  | Workmanship | Rework | 4 (0.5-3k) | Complete |  | Completed |  | • Profile of primary lining between the above mentioned advances varies up to +150mm from required profile. The worst area is around a monitoring point that has been installed in the invert.
| 02SL - Stations (LUL) | Cxxx-NCR-000521-W | NCR | Construction sequence of CP3 south thickening not as per Cxxx-__M-C4-DDB-D061-00120 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2013-10-31 | 2013-09-02 18:59 | -59 | 2013-07-25 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | •The spraying sequence was changed on site to suit previous design, as the batching plant is only able to batch P1 mix or P2 mix. As tunnelling work continues in the other drives, P1 is the main mix used. •Steel was sprayed in using the P2 mix as all previous steel work within the tunnels. •Once the steel had been sprayed in P2 mix, P1 mix was used for the remaining bulking required for the thickening. Root Cause: •Design sequence of construction is in contradiction to previous designs •Spraying P2 mix for bulking prevents mining in other headings from continuing •No structural change caused by the alternative mix use. Decision therefore made on site to follow this route.
| 02SL - Stations (LUL) | Cxxx-NCR-000524-W | NCR | W - Nonconforming Cores CR0654, CR0655, CR0660, CR0692, CR0704 – PTW-W, PTE-W, PTW-W |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-04-25 | 2013-12-13 16:37 | -133 | 2013-07-25 | Tunnelling - Linings - Sprayed Concrete | 2500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Nonconforming Cores of week ending 05/07/2013: •Cores CR0654 - PTW-E-Adv19-LK, •Cores CR0655 - PTE-W-Adv12-LK, •Cores CR0660 - PTW-W-Adv18-RK, •Cores CR0692 - PTW-W-Adv 36-LK, •Cores CR0704 – PTE-W-Adv 70 LH. Cores are shorter than required in the design. There are cracks in the cores. There are some laminations in the cores. There are significant voids and/or honey combing in the cores.
| 02SL - Stations (LUL) | Cxxx-NCR-000526-W | NCR | Nonconforming Cores of week ending 26/07/2013 (CR0793) |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-02-28 | 2014-01-06 17:04 | -53 | 2013-07-29 | Tunnelling - Tunnelling General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | • Cores CR0793 (PTW-W-Ext-Adv25-Shoulder) are shorter than required in the design (<325 mm)
| 02SL - Stations (LUL) | Cxxx-NCR-000528-W | NCR | PTW-W adv 27 & PTE-W adv 193 invert - incorrect spraying of invert |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2013-11-22 | 2013-08-22 11:39 | -92 | 2013-07-31 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete |  | Completed |  | • The inverts have been sprayed in 2 halves commencing solely on the left or right side of the invert with a longitudinal joint in the centre of the invert. This way of spraying can potentially introduce joints and additional requirements for trimming of joint surfaces. (See picture attached). Root Cause: • Construction Team intended to reduce rebound / over sprayed material.
| 02SL - Stations (LUL) | Cxxx-NCR-000530-W | NCR | W- Insufficient thickness of the thickening PTE-E CP3 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-07-04 | 2014-07-08 11:20 | 4 | 2013-08-05 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | PTE-E ch. 56-60m was sprayed between 10-04-2013 and 14-04-2013. There were some areas that seemed with insufficient thicknesses. Newer scans proved that the area has sufficient thickness. The NCR actual refers to two different issues: a. Insufficient thickness of HeadWall b. Insufficient thickness of PTE-E ch. 56-60
| 02SL - Stations (LUL) | Cxxx-NCR-000532-W | NCR | Marking up of chainages every 10m is not done at WHI |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2013-12-05 | 2013-09-03 15:01 | -93 | 2013-08-05 | Tunnelling - Tunnelling General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete |  | Completed |  | Marking up of chainages every 10m is not done at WHI Tunnels. ROOT CAUSE: Negligence of construction teams. The issue has been identified in __ Surveillance Cxxx-__M-O4-RGN-CR092-50076.
| 02SL - Stations (LUL) | Cxxx-NCR-000535-W | NCR | W - Core in primary lining, PTE-E enlargement adv 106 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-02-28 | 2014-01-07 16:45 | -52 | 2013-08-09 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | core set CR0542 taken at PTE-E enlargement adv 106 bottom of invert on 01.05.13 (sprayed 18.04.13) shows signs of voids withlamination and broken off at primary lining interface, therefore being non complianty with KT 20 requirements.
| 02SL - Stations (LUL) | Cxxx-NCR-000536-W | NCR | Core in Primary Lining CR0570 PTE-E enlargement adv 147 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-02-28 | 2014-02-05 13:58 | -23 | 2013-08-14 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | set of cores CR0570 taken in PTE-E enlaragement adv 141 on the left knee position on 10.05.13 sprayed 07.05.13 shows breakage at joint with dust/rebound incapsulation
| 02SL - Stations (LUL) | Cxxx-NCR-000537-W | NCR | Core CR0498 - PTW-E enlargement adv 64 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2013-10-25 | 2013-09-05 12:40 | -50 | 2013-08-14 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | the set of cores CR0498 taken in the left knee position on 20.04.13 sprayed on 14.04.13 are broken at the joints with possibly less fibres in the joint and dust encapsulation
| 02SL - Stations (LUL) | Cxxx-NCR-000538-W | NCR | W - Core in Primary Lining CR0519 PTW-E enlargement adv 89 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-02-28 | 2013-12-13 17:15 | -77 | 2013-08-14 | Tunnelling - Linings - Sprayed Concrete | 2000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | set CR0519 taken in PTW-E enlaragement adv 89 on 26.04.13 sprayed 22.04.13 shows insufficient thickness and laminations
| 02SL - Stations (LUL) | Cxxx-NCR-000539-W | NCR | W - Core in Primary Lining CR0523 PTW-E enlargement adv 97 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-02-28 | 2013-12-13 17:11 | -77 | 2013-08-14 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | set of cores CR0523 taken in PTW-E enlargement adv 97 on 27.04.13 sprayed 24.04.13 shows cores are broken off and show insufficient length
| 02SL - Stations (LUL) | Cxxx-NCR-000540-W | NCR | Core in Primary Lining CR0565 PTW-E enlargement adv 147 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-02-24 | 2016-04-06 16:13 | -324 | 2013-08-14 | Tunnelling - Linings - Sprayed Concrete | 50000 |  | Workmanship | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Set of cores CR0565 taken in PTW-E enlargement adv 147 right knee on 07.05.13 sprayed on 05.05.13 show voids and laminations with rebound encapsulations.
| 02SL - Stations (LUL) | Cxxx-NCR-000541-W | NCR | Core in Primary Lining CR0537 PTW-W enlargement adv 102 |  | Contr | __M |  |  | 2014-01-31 | 2014-01-29 14:37 | -2 | 2013-08-15 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | set of cores CR0537 taken at PTW-W enlargement adv 102 left knee level on 01.05.13 sprayed 27.04.13 shows rebound, voids and joints
| 02SL - Stations (LUL) | Cxxx-NCR-000542-W | NCR | Core in Primary Lining CR0538 PTW-W enlargement adv 107 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-01-31 | 2014-01-29 14:40 | -2 | 2013-08-15 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | set of cores CR0538 taken at PTW-W enlargement adv 107 invert on 01.05.13 sprayed on 28.04.13 shows laminations with voids and rebound
| 02SL - Stations (LUL) | Cxxx-NCR-000543-W | NCR | Core in Primary Lining CR0550 PTW-W enlargement adv 120 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-02-28 | 2014-02-05 13:55 | -23 | 2013-08-15 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | set of cores CR0550 taken at PTW-W enlargement adv 120 left knee level on 03.05.13 sprayed 30.04.13 shows broekn cores with voids and shadowing
| 02SL - Stations (LUL) | Cxxx-NCR-000544-W | NCR | Core CR0552 PTW-W enlargement adv 130 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-02-28 | 2014-02-05 14:00 | -23 | 2013-08-15 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | set of cores CR0552 taken at PTW-W enlargement adv 130 left knee level on 03.05.13 sprayed on 01.05.13 show broken cores with voids and shadowing
| 02SL - Stations (LUL) | Cxxx-NCR-000545-W | NCR | Core CR0578 PTW-W enlargement adv 141 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-01-31 | 2013-12-11 16:31 | -51 | 2013-08-15 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | set of cores CR0578 taken PTW-W enlargement adv 141 in left knee position on 13.05.13 sprayed on 05.05.13 showsinsufficient length with voids, lamination and rebound
| 02SL - Stations (LUL) | Cxxx-NCR-000548-W | NCR | primary lining insufficient thickness invert PTE-W at CP1a North |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-08-30 | 2013-08-16 14:00 | -14 | 2013-08-15 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | proof drilling undertaken by __ 05.08.13 identifiying localised spots of insufficient thicknesses for example 360, 320, 270, 230 (absolute min), details see survey record attached
| 02SL - Stations (LUL) | Cxxx-NCR-000549-W | NCR | Damaged reinforcement whilst trimming tight spots in the shotcrete window |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2013-09-15 | 2013-08-29 18:20 | -17 | 2013-08-16 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete |  | Completed |  | Non-conformance: - The SCL primary lining thickening 2nd layer not sprayed to profile as per Cxxx-__M-C4-DDB-D061-00101 P07 - As built survey showed the area of the shotcrete window had been over sprayed (tight) by 30/90mm - During controlled trimming works, a small number of reinforcing bars damaged. Root cause: - Initial investigation shows that some areas of reinforcement have been installed in the incorrect position, this combined with some overspray resulted in as-built survey showing tight areas within the window. The window is to allow continuity bars (L Bars) between the PTE-E and the CP3 Cross Passage. So not to encroach into the secondary lining profile, with an over sprayed primary lining. Instruction was given to re-profile the area before being allowed to continue. - On average 50mm needed to be removed from the profile. - With reinforcement being installed in some areas 30mm tight, and our target of 50mm trim. We hit reinforcement unexpectedly after 20/30mm of trimming.
| 02SL - Stations (LUL) | Cxxx-NCR-000550-W | NCR | Localised thin areas of PTW-W Enlargement & EPTW Enlargement |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2013-09-15 | 2013-09-12 15:10 | -3 | 2013-08-16 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete |  | Completed |  | Non-conformace: - The SCL primary lining in these areas was to be a minimum thickness of 325mm as per the RESS PTW-W/27 & PTW-W/28. - As built survey using ‘Dibit’ 3D showed localised areas that did not theoretically meet minimum thickness. - Proof drilling was carried out in the areas on a 1mx1m grid. - A survey was also taken using the tunnel beamer to see if the areas had been under sprayed Root cause: - Excavation in this area should have been +170mm so to avoid any trimming in the area of VA5, EP1 after thickening had been completed. There could have been some localised under excavation in these areas, which when put through the ‘Dibit’ software caused some errors as the beamer information does not show the same errors. - Dibit software may create a different triangulation to that of the beamer software which would show a different result to that of the beamer profiles - However, this does not take away the fact, that there has been some under spray in relation to that set out in the RESS (picked up on the beamer profiles) which has resulted in thickness issues.
| 02SL - Stations (LUL) | Cxxx-NCR-000551 | NCR | L - Missing thicknesses, face logs and lab data for AS1 shaft |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2013-09-30 | 2013-09-04 12:32 | -26 | 2013-08-21 10:37 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete |  | Completed |  | - Issue 1: Lab data for advance 23 step 61 Primary has not been recorded on 01/05/2012. However a flow test was undertaken and recorded during the Initial Layer and was within tolerance. Unchanged for this revision. - Issue 2:Thickness profiles for the advances 1,2,3,4,5,10 are missing from the deliverables package. The SRG minutes reference pins that were set to ensure profile for advances 2,3,5; however records are missing. The profiles for excavation, initial and primary have been submitted to the SRG during the tunnelling process and have been accepted as within tolerance. - Issue 3: Face logs for advances 3-8 are not included in the deliverables package. The open face has been inspected by CRL and __ during tunnelling and accepted by the SRG daily. Unchanged for this revision.
| 02SL - Stations (LUL) | Cxxx-NCR-000553 | NCR | W - PTW-E Thickening VA4 Chainage 88: High profile of primary lining of a local area of invert profile ( <1m x 1m) |  | Contr | __M |  |  | 2014-02-21 | 2014-01-22 09:05 | -30 | 2013-10-28 17:53 | Structural Engineering - Reinforcement | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | On July 2013, a local area of invert profile (<1m x 1m) of PTW-E Thickening VA4 Chainage 88 has been built high in respect to the adjacent area. The lining has been built ‘big’ (for TBM reception). As a consequence of the lining being locally high (in the invert) such the mesh reinforcement will locally not be in alignment with the main reinforcement profile.
| 02SL - Stations (LUL) | Cxxx-NCR-000554 | NCR | L - CP5 damaged rebar invert concrete |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-01-24 | 2013-12-09 10:10 | -46 | 2013-09-02 19:07 | Structural Engineering - Reinforcement | 30000 |  | Supervision/Management | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | - During enlargement PTW-W breakout for Adv. 6 (invert), some rebars (radial B32 for the most of them) were exposed in the invert due to positioning of the bars within the breakout profile. At that time, it has been thought that only the end of it was exposed and, with the agreement of __ designers, rebars could be cut and excavation could proceed. - However, few days later, this area has been cleaned out highlighting rebars exposed in a much longer proportion.
| 02SL - Stations (LUL) | Cxxx-NCR-000555 | NCR | PTW-W Opening Enl.: construction sequence did not follow the RESS |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-01-31 | 2013-12-09 10:19 | -53 | 2013-08-22 14:57 | Tunnelling - Excavation - Hand | 500 |  | System Defect | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | The excavation sequence did not start by the top heading as shown in the RESS.
| 02SL - Stations (LUL) | Cxxx-NCR-000556 | NCR | W - Storage of chemicals unsafe |  | Contr | __M |  |  | 2014-02-28 | 2013-12-03 14:12 | -87 | 2013-08-27 16:03 | Environmental - Waste & Material Management | 500 |  | Equipment Breakdown | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | - The hydraulic oil intermediate bulk container (IBC) which can contain up to 1000 litres is situated on a metal stand above a Garic interceptor drip tray with a containment of less than 1100 litres. Therefore the current arrangement of the hydraulic oil IBC does not comply with the Control of Pollution (oil storage) regulations requiring 110% of the containers total storage capacity. - The tap on the hydraulic oil IBC has been identified as leaking since May. This raises the issue of whether the IBC and associated fitting comply with the regulation ‘sufficient structural integrity to ensure that in normal circumstances it is unlikely to leak or burst’.
| 02SL - Stations (LUL) | Cxxx-NCR-000557 | NCR | L - AP7-W CH1 ( ii ) primary lining sprayed using the wrong mix |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2013-11-15 | 2013-10-07 12:17 | -39 | 2013-08-28 16:47 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | The second layer (85 mm thickening) was sprayed using P2 mix. This layer contains no reinforcement according to drawings Cxxx-__M-C4-DDB-C101-00180 – 182. Refer to placement check sheet attached for evidence.
| 02SL - Stations (LUL) | Cxxx-NCR-000558 | NCR | L - Damaged of extensometer |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-03-28 | 2013-12-19 08:05 | -99 | 2013-09-09 17:12 | Surveying - Instrumentation and Monitoring | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | The drilling for the shallow datum at the corner of Eldon Street struck a HV cable. Following the repairs undertaken by __ in the area it was reported that the extensometer has been damaged and cannot be recovered.
| 02SL - Stations (LUL) | Cxxx-NCR-000559 | NCR | W - Nonconforming Cores of period ending 23/08/2013 CR0781 CR0851 |  | Contr | __M |  |  | 2014-02-07 | 2014-01-15 15:37 | -23 | 2013-08-27 10:31 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Nonconforming Cores of week ending 05/07/2013: • Cores CR0781 - PTE-W-Adv155-RK (see attachment 1), • Cores CR0851 – VA4-Adv5-RK (see attachment 2). Cores are shorter than required in the design. There are cracks in the cores. There are some laminations in the cores. There are significant voids and/or honey combing in the cores.
| 02SL - Stations (LUL) | Cxxx-NCR-000560 | NCR | W - Damaged reinforcement whilst breaking out invert advance 6 as per RESS CP3/06 |  | Contr | __M |  |  | 2013-11-29 | 2013-11-04 12:07 | -25 | 2013-08-27 15:18 | Tunnelling - Excavation - Hand | 2243 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | • During breakout works using heavy breaker on 944, as per RESS CP3/06. Some over break happened, which caused damage to the reinforcement in the invert area of CP3 • Bars too damage to straighten and pin back into position • Bars cut out, leaving the reinforced area not per design.
| 02SL - Stations (LUL) | Cxxx-NCR-000561 | NCR | W - Permeation Grouting: No notification given to CRL to undertake inspection witness points as specified in the ITP |  | Contr | __M |  |  | 2014-03-28 | 2013-12-20 14:46 | -98 | 2013-09-09 17:43 | Geotechnical Engineering - Compensation Grouting | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | No CRL inspection requested during Permeation Grouting.
| 02SL - Stations (LUL) | Cxxx-NCR-000562 | NCR | W - Overspraying of window to rebar CP3 S, N, VA2 & 4 |  | Contr | __M |  |  | 2013-09-13 | 2013-09-04 13:55 | -9 | 2013-09-03 17:56 | Tunnelling - Linings - Sprayed Concrete | 2000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete |  | Completed |  | The windows (location of the L bars in the thickening) are not +100mm as required. (see survey attached for CP3 N&S and VA2&VA4)
| 02SL - Stations (LUL) | Cxxx-NCR-000563 | NCR | L - AP7-W Advance 18: Missing points in Excavation, Initial and Primary profiles |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2013-11-08 | 2013-10-02 08:04 | -37 | 2013-08-29 09:17 | Tunnelling - Excavation - Hand | 1500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During the record of the excavation, initial and primary of AP7 W Adv 18 some points in the left invert part are missing. (See attached LIV AP7E W Adv 18 - SCL Profiles)
| 02SL - Stations (LUL) | Cxxx-NCR-000564 | NCR | W - Shotcrete produced through un-calibrated batching plant. |  | Contr | __M |  |  | 2013-11-29 | 2013-09-30 13:15 | -60 | 2013-08-27 10:44 | Tunnelling - Tunnelling General | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | A slight gap between when calibration was due on the batching plant, and when it was undertaken.
| 02SL - Stations (LUL) | Cxxx-NCR-000565 | NCR | L - AP7-W Enlarg: Non conforming profiles for Adv 37, 39, 41, 42, 43, 45, 46, 47 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2013-11-29 | 2013-09-24 13:48 | -66 | 2013-08-30 11:37 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The primary profiles of the advances 37, 39, 41, 42, 43, 45, 46, 47 show that some points are out of tolerance( between 1mm to 36mm ).
| 02SL - Stations (LUL) | Cxxx-NCR-000566 | NCR | AP7-W( Ch1 ), Enl.: Tests Missing in advances 8 & 50 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2013-11-22 | 2013-09-24 11:40 | -59 | 2013-08-27 17:47 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | • In Advance 8 of AP7 W ( Ch1 ) the 12hr pull out test is missing. • In Advance 50 of AP7 W ( Ch1 ) the 6hr and 12hr pull out tests are missing. See J2 Curves attached
| 02SL - Stations (LUL) | Cxxx-NCR-000567 | NCR | L - AP7-W Ch1-2 Enl. Adv 60 and 63: Minimum thickness not reached in some points |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-08-29 | 2014-06-28 10:01 | -62 | 2013-08-27 18:08 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | • In Advance 61-62-63, the Overall thickness profile shows 6 points less than 400mm ( 380, 355, 395, 351, 374 and 371 ) • In Advance 58-59-60, the Overall thickness profile shows 5 points less than 400mm ( 388, 349, 357, 392, 371 mm) Refer to the attached profiles (att01 & att02)
| 02SL - Stations (LUL) | Cxxx-NCR-000568 | NCR | L - PTE-W Pilot: Over excavation of face in invert of Adv 112 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2013-11-15 | 2013-09-23 14:40 | -53 | 2013-08-27 18:34 | Tunnelling - Excavation - Hand | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The face of Adv 112 was over excavated by 0.8m in the lower invert part of the advance.
| 02SL - Stations (LUL) | Cxxx-NCR-000569 | NCR | L - Missing Check Sheets for the Shaft AS1 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2013-09-13 | 2013-09-11 18:55 | -2 | 2013-08-28 09:19 | Tunnelling - Tunnelling General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete |  | Completed |  | Missing Check Sheets for: reinforcement delivery, cutting edge delivery, reinforcement placement, Bentonite placement
| 02SL - Stations (LUL) | Cxxx-NCR-000570 | NCR | L - Breaking out of PTW-W enlargement eye causing further implications to exposed steel |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2013-11-22 | 2013-09-19 14:23 | -64 | 2013-08-28 09:47 | Tunnelling - Excavation - Hand | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Having previously been uncovered upon trimming the ‘L’ bar shotcrete window, these bars had a lack of cover sufficient enough to allow the bars to be agitated out of the lining by the breaking activities.
| 02SL - Stations (LUL) | Cxxx-NCR-000571 | NCR | L - AP1 Enl Adv 66: Incorrect Installation of kwikastrip reinforcement |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2013-11-08 | 2013-11-08 08:54 | 0 | 2013-08-28 10:05 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Supervision - Supervisor does not have sufficient experience | Completed |  | Kwikastrip for Advance 66 double invert lower level (77.37mATD) varies from previous advance in level by approx. 200mm (77.17mATD). The previous advance Kwikastrip installed In invert enlargement layer but 200mm lower than design, causing a step in the Kwikastrip level. The continuity joint is now at correct level.
| 02SL - Stations (LUL) | Cxxx-NCR-000572 | NCR | W - CP3 Enlarg: Over-excavation of Top Heading Advance 16 |  | Contr | __M |  |  | 2013-12-06 | 2013-11-08 15:16 | -28 | 2013-09-10 09:43 | Tunnelling - Excavation - Hand | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | •Advance 16 (top heading 1) was excavated to the face profile of Advance 17 (top heading 2), resulting in a 2m top heading advance. •The engineer controlling the excavation noticed unusual readings during the face excavation, re-set the beamer which consequently displayed a reduced offset to the correct face profile as a result of a coincidentally separate beamer shift, so therefore continued having not noticed the actual programming error. •During the wall profile trimming the over-excavation became clear to the engineer however the face excavation was at this point complete. •The top heading advance was therefore 2m in length as a result.
| 02SL - Stations (LUL) | Cxxx-NCR-000573 | NCR | L - AP7-W, Ch1 Enlarg: Non conforming profiles for Adv 73, 69, 51, 36, 33, 30, 27, 3. |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2013-11-29 | 2013-09-26 12:43 | -64 | 2013-08-30 12:03 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | The primary profiles of the advances 73, 69, 51, 36, 33, 30, 27, 3 shows that some points are out of tolerance (between 1mm to 47mm ).
| 02SL - Stations (LUL) | Cxxx-NCR-000574 | NCR | L - AP1 Enl Adv 5, 13 & 27: Nonconforming Cores CR0807, CR0810, CR0808, CR0809 of week ending 02/08/13 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-10-17 | 2014-08-21 08:58 | -57 | 2013-09-02 10:34 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Nonconforming Cores of week ending 02/08/2013: - Cores CR0807 – AP1 Enl Adv 5, (see att01) - Cores CR0810 – AP1 Enl Adv 13, (see att02) - Cores CR0808&809 – AP1 Enl Adv 27, (see att03) Cores are shorter than required in the design. A number of cores displayed a shear failure circa 200mm in from the clay. There are voids and/or honey combing in the cores.
| 02SL - Stations (LUL) | Cxxx-NCR-000575 | NCR | L - Cores of week ending 09/08/2013 AP1 Enl Adv 28 & 36, PTE-W Pilot Adv 110 (CR0838, CR0840, CR0844) |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-03-21 | 2014-01-07 14:45 | -73 | 2013-09-02 11:01 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Nonconforming Cores of week ending 09/08/2013: - Cores CR0838 – AP1 Enl Adv 28, - Cores CR0840 – AP1 Enl Adv 36, - Cores CR0844 – PTE-W Pilot Adv 110 Cores are shorter than required in the design. There are small voids, cracks or lamination in the cores.
| 02SL - Stations (LUL) | Cxxx-NCR-000576 | NCR | W - CP2N Enlarg: Early Strength Testing not carried out as per ITP |  | Contr | __M |  |  | 2013-12-20 | 2013-11-04 12:21 | -46 | 2013-09-17 14:12 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | - Early strength testing missed on several advances at times required as per ITP - Advance 15 – Only 1 and 7 hour testing taken - Invert Advance 1 – Testing missed between ½ and 6 hours - Invert Advance 3 – Testing missed up to 6 hours
| 02SL - Stations (LUL) | Cxxx-NCR-000577 | NCR | W - Nonconforming Cores of week ending 30/08/2013 CR0874 (CP1a-p-35) |  | Contr | __M |  |  | 2013-12-13 | 2013-12-03 15:54 | -10 | 2013-09-03 08:55 | Tunnelling - Linings - In-situ Concrete | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Nonconforming Cores of week ending 30/08/2013: - Cores CR0874 - CP1a pilot Advance 35 LK, There are significant voids and/or honey combing in the cores.
| 02SL - Stations (LUL) | Cxxx-NCR-000578 | NCR | L - No curing of the final thickening layer in Chamber 1-2 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2013-12-20 | 2013-10-23 08:20 | -58 | 2013-09-11 09:17 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | The final layer of the primary lining thickening for the top half of Chamber 1-2 4 was sprayed on the night shift starting 22/08/2013. However no curing was carried out of this thickening layer.
| 02SL - Stations (LUL) | Cxxx-NCR-000579 | NCR | L - LCE (PTE-W) pilot adv 59: face sealed under 75mm |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2013-12-06 | 2013-10-14 13:26 | -53 | 2013-09-06 11:34 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Shotcrete thickness at the face was between 50 and 100mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000580 | NCR | L - AP7-W CH1 (ii) Enlarg: joint not as per design |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2013-12-13 | 2013-11-06 08:23 | -37 | 2013-09-09 10:39 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Half top sprayed with joint not staggered, refer to the 4 photos attached for evidence.
| 02SL - Stations (LUL) | Cxxx-NCR-000581 | NCR | L - PTE-E pilot: adv 93 over-excavated |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2013-12-13 | 2013-10-14 10:40 | -60 | 2013-09-09 10:43 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | PTE-East pilot tunnel advance 93 was over-excavated by 900mm max and 400mm in invert and previous invert was broken out.
| 02SL - Stations (LUL) | Cxxx-NCR-000582 | NCR | WHI - Nonconforming Cores of period ending 06/09/2013 CR0882, CR0898, CR0900, CR0896 (CP3e Adv 19/40/48 and PTW-E thickening Area CP3) |  | Contr | __M |  |  | 2013-10-01 | 2013-09-23 15:24 | -8 | 2013-09-10 11:50 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Nonconforming Cores of week ending 06/09/2013: • Cores CR0882 – CP3 Enlargement Advance 19 RK, • Cores CR0898 – CP3 Enlargement Advance 40 LK (2 reports), • Cores CR0900 – CP3 Enlargement Advance 48 RK, • Cores CR0896 – PTW-E Thickening CP3 south area There are cracks in the cores. There are some laminations in the cores. There are significant voids and/or honey combing in the cores.
| 02SL - Stations (LUL) | Cxxx-NCR-000583 | NCR | L - AP7-W,Enlarg: Minimum Thickness not achieved in advance 38 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2013-12-13 | 2013-10-31 13:57 | -43 | 2013-09-09 10:47 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • Issue 1: Highly localised thicknesses show a total of 280mm and 277mm. • Issue2: One point 0.002mm inside primary design profile, at right axis.
| 02SL - Stations (LUL) | Cxxx-NCR-000584 | NCR | L - AP7 (iii) Layer thickness and profile checks issues |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-10-30 | 2015-08-10 14:04 | -81 | 2013-09-09 11:05 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | - Issue 1: Thickness data is missing for the initial lining of advance 29 between 4 to 6 o clock and 7 to 8 o clock as shown in attached profile. - Issue 2: Minimum thickness not achieved in advances 4, 9, 13, 14, 15, 19, 20, 31, 37, 38, 39 by varying amounts as shown in attached profiles. - Issue 3: Primary profile tolerance exceeded in advances 1/2, 4, 7, 8, 9, 12, 12, 18, 19, 20, 22, 24, 25, 31, 34, 37, 38, 39, 40 by varying amounts as shown in attached profiles
| 02SL - Stations (LUL) | Cxxx-NCR-000585 | NCR | L - Cover behind reinforcement higher than expected |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-03-28 | 2013-12-09 14:43 | -109 | 2013-09-11 16:04 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • In some areas of AP7W/Ch1a Invert, small voids local de-lamination (failed hammer test) were identified, causing steel cover exceeded 100mm (between 102 and 267mm). Very localised area show an important steel back cover (approx 260mm). See attached survey sketch (attachment A)
| 02SL - Stations (LUL) | Cxxx-NCR-000586 | NCR | W - Grout Viscosity did not conform to ITP specified range |  | Contr | __M |  |  | 2013-12-20 | 2013-09-30 13:43 | -81 | 2013-09-10 18:19 | Geotechnical Engineering - Compensation Grouting | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Grout viscosity was not within the ITP specified tolerance range.
| 02SL - Stations (LUL) | Cxxx-NCR-000587 | NCR | W - Grout 28 day compressive strength did not conform to ITP specific Range |  | Contr | __M |  |  | 2013-12-20 | 2013-09-30 14:00 | -81 | 2013-09-12 11:45 | Geotechnical Engineering - Compensation Grouting | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Not Defined | Completed |  | The following grout mixes were found not to achieve the ITP stated value of less than 1.5MPa for average 28 day compressive strength: Cube NoC0247 which was sampled on the 10th May 2012: Strength 2.0MPa.
| 02SL - Stations (LUL) | Cxxx-NCR-000588 | NCR | L - AP7-W Enlarg: Missing Early Strength adv 37-47 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2013-12-12 | 2013-09-17 14:15 | -86 | 2013-09-12 15:26 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | - Missing testing frequency – not every 3 advances as per ITP. Test panels undertaken at advances 38, 40, 43, 47. Test should have been conducted at advance 46. - Advance 47 – 1 hour result missing. See attached. - Advance 47 – observed strength below J2mod between 6 and 12hours. See attached.
| 02SL - Stations (LUL) | Cxxx-NCR-000589 | NCR | L -AP7(ii): Primary profile tolerances breached and minimum overall thickness not achieved. |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-10-30 | 2015-05-21 14:36 | -162 | 2013-09-16 12:17 | Tunnelling - Linings - In-situ Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Inadequate/insufficient tooling. | Completed |  | • Issue 1: Minimum thickness not achieved in advances 9 and 15 by varying amounts as shown in attached profiles • Issue 2: Primary profile tolerance exceeded in advances 14, 15, 16, 17, 18, 21, 24, 25 by varying amounts as shown in attached profiles.
| 02SL - Stations (LUL) | Cxxx-NCR-000590 | NCR | W - Incorrect Tunnel Geometry and shape of zone “CP1a Wraparound” |  | Contr | __M |  |  | 2013-11-20 | 2013-11-08 14:30 | -12 | 2013-09-23 14:50 | Tunnelling - Linings - Sprayed Concrete | 49656.7 |  | System Defect | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | Between the 13/09/13 DS and the 15/09/13 DS, geometry of the tunnel CP1a Wraparound enlargement was built different than the approved design from advance 14 to 27, ie from chainage 12.45 to 21.04. (Please refer to RESS CP1a/09). The difference is shown evidently on the attached scanned profiles (more than 200mm in the chainages shown) in the areas around the transition (scanning has been produced after some of the “wrong” areas have already been broken out in order to be re-sprayed according to the RESS CP1a/09, so they do not appear).
| 02SL - Stations (LUL) | Cxxx-NCR-000592 | NCR | L - PTW-W enlarg., adv 24: Sub-Drain Geotextile overlapping 100mm surrounding shotcrete initial lining. |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2013-12-20 | 2013-10-02 07:54 | -79 | 2013-09-16 17:49 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | Geotextile of sub-drainage was connected to the initial lining (approx. 100mm overlap).
| 02SL - Stations (LUL) | Cxxx-NCR-000593 | NCR | W - Nonconforming Cores of period ending 20/09/2013 CR0911, CR0924 (CP3 Enlargement in the eye of EP2 and Adv4) |  | Contr | __M |  |  | 2013-12-13 | 2013-12-11 16:36 | -2 | 2013-09-24 09:33 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Nonconforming Cores of week ending 20/09/2013: • Cores CR0911 – CP3 Enlargement in the eye of EP2 • Cores CR0924 – CP3 Enlargement Advance 4 There are some laminations in the cores. There are significant voids and/or honey combing in the cores especially around the steel plate of the eazistrip.
| 02SL - Stations (LUL) | Cxxx-NCR-000595 | NCR | L-Uncalibrated Equipment flow meters |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2014-02-28 | 2014-02-13 11:57 | -15 | 2013-09-18 11:12 | Geotechnical Engineering - Compensation Grouting | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | A contractor led surviellance on 16.05.2013 of Equipment Calibration and the material for the injection of grout for compensation (Compensation Grouting) identified a number of flow meters that were in use or identified as availble spares whose annual calibration had lapsed.
| 02SL - Stations (LUL) | Cxxx-NCR-000596 | NCR | L - Nonconforming Cores of week ending 20/09/2013: PTW-W Enl, Adv 5 and 14 (CR0929 and CR0932) |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-09-26 | 2014-08-20 14:33 | -37 | 2013-10-01 15:19 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Nonconforming Cores of week ending 20/09/2013: • Cores CR0929 - PTW-W Enlargement-Adv5-LK (actually taken from Adv. 7 and not 5, the advances are inclined), • Cores CR0932 - PTW-W-Enlargement Adv14-LK, There is one crack in the first core. There are significant voids and/or honey combing in the cores. Rebars are not well captured in the shotcrete. Cores broken.
| 02SL - Stations (LUL) | Cxxx-NCR-000597 | NCR | W - Bypass Pilot Advance 27: Incorrect finished SCL profile |  | Contr | __M |  |  | 2014-01-17 | 2013-12-20 13:58 | -28 | 2013-10-01 08:52 | Tunnelling - Linings - Sprayed Concrete | 1426.54 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | On 28/09/13, DS, Advance 27 of the Bypass Pilot was excavated with a section on the left hand side being significantly tighter than the “+100mm” target. The problem was reported post-completion of the advance.
| 02SL - Stations (LUL) | Cxxx-NCR-000598 | NCR | W - Albion Brewery: Grout Viscosity and bleed did not conform to ITP specified range. |  | Contr | __M |  |  | 2013-11-29 | 2013-09-24 15:53 | -66 | 2013-09-24 09:41 | Geotechnical Engineering - Geotechnical Engineering - General | 500 |  | System Defect | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Grout viscosity was not within the ITP specified tolerance range. The following grout mixes were found to be over the ITP stated value of 5% for one hour bleed: Cube tested on site by VG dated 08/03/2012. Bleed 7%. Cube tested on site by VG dated 09/03/2012. Bleed 8%. Three cubes tested on site by VG dated 12/03/2012. Bleeds 7%, 9% and 10% respectively.
| 02SL - Stations (LUL) | Cxxx-NCR-000599 | NCR | W - Backfilling of boreholes for ground investigation in CS1: Grout 28 day compressive strength did not conform to ITP specified range |  | Contr | __M |  |  | 2013-11-22 | 2013-09-30 16:19 | -53 | 2013-09-24 18:36 | Geotechnical Engineering - Ground Investigation | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The following grout mixes were found not to achieve the ITP stated value of less than 1.5MPa for average 28 day compressive strength: Cube NoC0161 which was sampled on the 3rd March 2012. Strength 2.0MPa. Cube NoC0196 which was sampled on the 29th March 2012. Strength 3.0MPa. Cube NoC0200 which was sampled on the 4th April 2012. Strength 2.5MPa.
| 02SL - Stations (LUL) | Cxxx-NCR-000600 | NCR | W - Bypass excavation without depressurisation check sheet |  | Contr | __M |  |  | 2014-03-21 | 2013-12-09 15:08 | -102 | 2013-09-25 15:54 | Tunnelling - Tunnelling General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | On 23/09/13, DS, advances 17 & 18 of Bypass tunnel were constructed beyond the extent of at that time valid depressurisation check sheet – BYP-pilot-Adv 1 to 16 and so without a valid depressurisation check sheet as required by the RESS. The site was informed that after drilling of the two bottom probe holes can proceed with further excavation (two or three advances) with note that probing will be completed on next day. This information was confirmed by production manager, senior member of SRG team and works superintendant. Also this matter was discussed on D/S SRG on Monday 23/09/2013 with no other objection. Therefore site has decided to carry out the excavation without signed off depressurisation check sheet as it was deemed safe to do so.
| 02SL - Stations (LUL) | Cxxx-NCR-000601 | NCR | W - PTW-E, Invert, Adv.104 -106: Step across one of the joints |  | Contr | __M |  |  | 2014-03-14 | 2014-01-15 14:56 | -58 | 2013-12-06 14:03 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | On 13/11/13, during the preparation works for invert regulating layer of PTW-W, a step across one of the joints of approximately 100 to 130mm was identified in Advance 104 to 106 (Chainage 72 to 74). The profile of Advance 106 was sprayed to profile at the leading edge but the back edge of the Advance was over sprayed by approximately 130mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000602 | NCR | W - EP2 invert: Exposed and damaged steel reinforcement in the break out |  | Contr | __M |  |  | 2014-03-28 | 2014-02-11 11:28 | -45 | 2013-09-26 17:12 | Structural Engineering - Reinforcement | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Personnel Error - Other human error | Completed |  | • On 25/09/13 DS, during EP2 Breakout, reinforcement installed and sprayed as part of the permanent thickening work for EP2 was exposed and damaged. • Excavation/Breakout in excess of that stated on the RESS
| 02SL - Stations (LUL) | Cxxx-NCR-000603 | NCR | W - CS1 Ground Investigation: ITP items not recorded |  | Contr | __M |  |  | 2013-11-22 | 2013-09-30 17:33 | -53 | 2013-09-26 15:43 | Geotechnical Engineering - Ground Investigation | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | ITP Items 4.2, 4.6 & 4.11 are recorded on shift reports but not all have been recorded. ITP Items 4.3, 4.7 & 4.12 was completed as a visual check and recorded in shift reports. ITP Items 4.4, 4.8 & 4.13 was completed as a visual check. ITP Items 4.5 & 4.10 full installation recorded on shift reports & form D3-14. Details of installation as implied in ITP but not recorded in detail. Sign off from D3-14 implies all installation was carried out as required.
| 02SL - Stations (LUL) | Cxxx-NCR-000604 | NCR | L - AP1 Temporary Invert Enlarg, adv 1: Break-out started 500-600mm backwards from the correct position |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-03-21 | 2014-01-22 09:54 | -58 | 2013-10-01 17:38 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | On NS 15/09/2013, the break-out of temporary invert lining, advance 1 in AP1, has started 500-600 mm backward from the original position. (see sketch attached).
| 02SL - Stations (LUL) | Cxxx-NCR-000605 | NCR | L - AP1 Enlarg, Adv 3: Incorrect position of Kwikastrip |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-01-10 | 2013-11-28 07:53 | -43 | 2013-10-01 16:57 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | On 20/09/13, NS, kwikastrip in AP1 Invert Enlargement, advance 3 has been installed at the wrong level. There is around 1m vertical discontinuity between end of Adv 3 lower level kwikastrip and start of Adv 4 lower level kwikastrip. After investigation it seems that the level of the Adv 3 was wrong.
| 02SL - Stations (LUL) | Cxxx-NCR-000606 | NCR | L - Moorgate Box: While drilling Bore hole BO1 the drill went through the sewer |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-01-31 | 2014-01-02 09:14 | -29 | 2013-10-22 17:09 | Geotechnical Engineering - Supported Excavations | 20000 |  | Workmanship | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | • Tam hole B01 was drilled into the Goswell street sewer exclusion zone and drilled into the sewer at the shoulder position during the night shift of 21st September 2013.
| 02SL - Stations (LUL) | Cxxx-NCR-000607 | NCR | L - Nonconforming Cores of week ending 27/09/2013: PTW-W Enl Adv 17 and 30 (CR0937 and CR0941 ) |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-01-31 | 2013-12-11 16:42 | -51 | 2013-10-01 15:48 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Nonconforming Cores of week ending 20/09/2013: • Cores CR0937 - PTW-W Enlargement-Adv17-RK, • Cores CR0941 - PTW-W-Enlargement Adv30-RK, There is shadowing in the first core. There are significant voids and/or honey combing in the cores. Rebars are not well captured in the shotcrete Cores are broken.
| 02SL - Stations (LUL) | Cxxx-NCR-000608 | NCR | L - PTW-W Enl Adv 54 ( invert ) - Primary lining not completed in one go |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-01-17 | 2013-12-02 10:58 | -46 | 2013-10-04 15:35 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • On DS 30/09/13, Initial lining and partial primary 1 lining has been stopped at 4.15 pm due to water ingress in the invert. • The spray has been resumed at 5.45 pm and has been finished by night shift after 10pm. (Refer to the attached Shift Report of PTW-W Enl on 30/09/13) • Some bars form kwikastrip were sprayed in the initial. ( Refer to the attached photo for evidence) • During the spray some water was remaining in the invert ( Refer to the attached photo for evidence)
| 02SL - Stations (LUL) | Cxxx-NCR-000609 | NCR | W - Nonconforming Cores CR0955 (PTE-E Adv121, enlargement) |  | Contr | __M |  |  | 2014-02-28 | 2014-02-28 09:14 | 0 | 2013-10-09 14:40 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • Nonconforming Cores CR0955 – PTE-E Enlargement Advance 121 Central Invert (date of spray: 22/04/13, date of core: 27/09/13): o Cores are shorter than required (average 345.5mm instead of 375mm). See attachment 2: cores report, o This thin area can be seen in the beamer profile too. See attachment 3: beamer profile.
| 02SL - Stations (LUL) | Cxxx-NCR-000610 | NCR | W - Nonconforming Cores CR0703 – PTW-W-Adv 166 RH |  | Contr | __M |  |  | 2013-10-17 | 2013-10-07 15:26 | -10 | 2013-10-03 18:08 | Tunnelling - Linings - In-situ Concrete | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Nonconforming Cores : Cores CR0703 – PTW-W-Adv 166 RH (see attachment 1): • Cores are broken and shorter than required in the design. • There are some laminations, voids and cracks, rebound
| 02SL - Stations (LUL) | Cxxx-NCR-000611 | NCR | W - Poor bar steel encapsulation on L-Bar window in an area (Approx 1.0m x 2.0m) above axis on the right hand side of portal. |  | Contr | __M |  |  | 2014-02-14 | 2013-12-16 16:34 | -60 | 2013-10-31 08:47 | Tunnelling - Linings - Sprayed Concrete | 1756 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • The L-Bars that span the junction between PTW-W platform tunnel and CP1A cross passage were being sprayed. This essentially creates two surfaces at 90 degrees to each other that need to be sprayed concurrently. • Sufficient care needs to be taken when spraying this location to ensure that when you are spraying one surface you do not allow spray to build up on the perpendicular surface. • In this instance, the nozzleman allowed spray to build up on the PTW-W tunnel eye when he was spraying the shoulder of CP1A (See Photos). This led to voiding and over spray. It has been found on 10/10/2013.
| 02SL - Stations (LUL) | Cxxx-NCR-000612 | NCR | W - Beamer Verification - lack schedule of calibration, inspection, measuring and testing equirment |  | Crossrail | XRL |  |  | 2013-12-09 | 2013-12-06 15:50 | -3 | 2013-10-10 11:50 | Surveying - Tunnels/Portal/Shafts surveys | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | On 11/09/2013 during a Crossrail led surveillance held at Whitechapel offices on the Beamer verification process the Contractor was requested to provide evidence of calibration for all beamers identified on the __ Calibration Schedule tabled during the surveillance. Calibration record for one instrument __ TS15 1615319 was made available and the rest were requested by 18/09/2013. None were provided by 25/08/2013. Also during the surveillance it was noted that the tabled calibration schedule was no longer current. The above referenced __ TS15 was identified as under repair with a next calibration date of “before use on site” whilst the calibration certificate was dated as current until 20/02/2014. It may be that the calibration schedule was current and the certificate was not, as the instrument may have suffered damage following its calibration on 20/02/2013.
| 02SL - Stations (LUL) | Cxxx-NCR-000613 | NCR | W - Beamer Verification - No planned arranagements for physical checks undertaken during transfer of data from drawings to Beamer user software |  | Crossrail | XRL |  |  | 2014-02-28 | 2013-12-13 14:30 | -77 | 2013-10-10 14:16 | Surveying - Tunnels/Portal/Shafts surveys | 500 |  | System Defect | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | On 11/09/2013 during a Crossrail led surveillance held at Whitechapel offices on the Beamer verification process the Contractor demonstrated with reference to records that the following physical checks are undertaken during transfer of data from drawings to Beamer user software:- (1) Each setting out area has a unique reference number, (2) The take off from drawings is initially self checked, (3) An independent check of the take off from drawings then follows, and (4) An independent check of Drawing currency is included There were no planned arrangnments for the above physical checks. Physical checking is a verification activity and as such must be included in an inspection and test plan, a requirement of Works Information Clause 20.2.
| 02SL - Stations (LUL) | Cxxx-NCR-000614 | NCR | L - PTW-W Enlarg: Core holes backfilled with not approved grout material |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-03-28 | 2014-01-10 10:27 | -77 | 2013-10-25 15:55 | Geotechnical Engineering - Geotechnical Engineering - General | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | - On NS 19/10/2013 cores holes in first advances on left were backfilled improperly by a lab technician and with non-compliant mix. - On NS 20/10/2013 the same Lab Technician re-drilled it and backfill it again. But grout was not properly mixed and core holes not properly filled. See attachment 1 for evidence.
| 02SL - Stations (LUL) | Cxxx-NCR-000615 | NCR | L - PTW-W Enl Adv 5 and 6 - Frequency of flow tests not done as per ITP |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-01-17 | 2013-11-07 11:42 | -71 | 2013-10-23 14:12 | Geotechnical Engineering - Geotechnical Engineering - General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | On NS 21/10/13, PTW-W Adv 5 spray started at 21:00 whereas the first test flow was done at 21:30 PTW-W Adv 6 spray started at 00:00 whereas the first test flow was done at 00:22 Refer to flow tests record and placement checksheet for evidence
| 02SL - Stations (LUL) | Cxxx-NCR-000616 | NCR | L - AP1 Enlarg, Adv 13-14: Problem with profile in the transition |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-09-05 | 2014-09-05 13:28 | 0 | 2013-11-01 16:29 | Geotechnical Engineering - Geotechnical Engineering - General | 1500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On DS, 28/09/2013, AP1 Enlarg, Adv 13, deep invert, started but on the right hand side the initial was found tight due to clay under excavated. Refer to the proof drilling checksheet for evidence (1 spot is 100mm thin and 2 thin by 50mm ). On the left hand side there has been a gap of 300mm between the two lengths of kwikastrip.
| 02SL - Stations (LUL) | Cxxx-NCR-000617 | NCR | L - CP5 Enlarg: No curing carried out for final thickening layer, stages 3 and 5 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-01-10 | 2013-11-18 14:52 | -53 | 2013-10-25 16:44 | Geotechnical Engineering - Geotechnical Engineering - General | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Stage 3 (Final layer) of the primary lining thickening for CP5-reinforced areas was sprayed on day shift 09/06/2013. Stage 5 (Final layer) of the primary lining thickening for CP5-reinforced areas was sprayed on night shift 16/06/2013. However no curing was carried out of this thickening layer.
| 02SL - Stations (LUL) | Cxxx-NCR-000618 | NCR | W - CP1a Enlarg, adv 53-55 & 54-56: Variation from specified RESS sequence |  | Contr | __M |  |  | 2014-02-14 | 2013-12-13 11:49 | -63 | 2013-10-11 16:04 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | On 05/10/13 DS, during CP1a Enlargement: • Advance 53 (Second Top) was excavated and sprayed together with advance 55 (Partial Top). • Then advance 54 (2m Invert) was excavated and sprayed together with advance 56 (1m Invert), which is not accordance with the RESS CP1a/10 attached (att 1)
| 02SL - Stations (LUL) | Cxxx-NCR-000619 | NCR | W - Geotechnical Inclinometer instrumentation data processing calculation error |  | Contr | __M |  |  | 2015-07-30 | 2015-02-19 11:05 | -161 | 2013-10-11 15:43 | Geotechnical Engineering - Geotechnical Monitoring | 2000 |  | System Defect | Rework | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | Reporting incorrect inclinometer displacement magnitudes. The data was incorrectly calculated for the manual inclinometers for all inclinometers at Whitechapel and Liverpool Street. The error was a generic calculation error within the Microsoft Excel spreadsheet used for all instruments. Magnitudes of the recorded movements were reported as only half the actual movement. The first re-drilled inclinometer to be initially measured was on the 09th November 2012, and the generic calculation error was noticed and verbally reported to Crossrail in March 2013. The possible consequence of the error and the magnitude of the error to be confirmed as anticipated was explained and verbal recognition with Crossrail was agreed. __ had to confirm that the suspected error was correct, and then implement the correction to each of the instruments individual spreadsheet. The previous calculated data had to also be reprocessed for every measurement taken, for every instrument.
| 02SL - Stations (LUL) | Cxxx-NCR-000620 | NCR | L - PTW-E and W, pilot: Regular Monitoring Survey not read properly |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-07-11 | 2014-06-28 10:08 | -13 | 2013-10-14 16:19 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Tunnel monitoring results shown in SRG were incomplete at different locations, especially in the pilot PTW-E and PTW-W. Several Regular Monitoring Survey (RMS) cannot be read properly because some of the targets are not reinstalled after been damaged or are blocked and unreadable. Refer to attachement 1- Extract of the results shown in the SRG of the 8th of October 2013 for evidence.
| 02SL - Stations (LUL) | Cxxx-NCR-000621 | NCR | L - PTW-W Enlarg: Core holes not backfilled in several advances |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-02-28 | 2014-01-10 13:42 | -49 | 2013-10-14 16:44 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Planning | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Cores taken from the lining PTW-W Enlargement is not always backfilled and not distributed around the lining according to KT20-2202. See pictures attached as evidence.
| 02SL - Stations (LUL) | Cxxx-NCR-000623 | NCR | W - PTE-W, PTE-E, VA4 & VA2 Enlargement: Missing Flow Tests |  | Contr | __M |  |  | 2014-02-15 | 2013-12-03 13:45 | -74 | 2013-10-18 15:07 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate resources | Completed |  | Missing Flow Tests of the shotcrete at the following locations: - PTE-W adv. 27, enlargement on NS 11/06/2013 - PTE-E adv.158, enlargement on DS 25/06/2013 - VA4 adv.3, enlargement on NS 04/08/2013 - VA2, adv. 15, enlargement on NS 13/08/2013
| 02SL - Stations (LUL) | Cxxx-NCR-000624 | NCR | Permeation Grouting verification Documents |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2013-12-03 | 2013-11-18 12:41 | -15 | 2013-10-22 11:56 | Civil - Tunnelling | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | On the 02/10/2013 during a Crossrail led surveillance, held at the Finsbury Circus office, on permeation grouting verification records. The contractor was asked to provide evidence of inspection notification; the contractor was unable to provide this.
| 02SL - Stations (LUL) | Cxxx-NCR-000625 | NCR | Permeation grouting verification documents |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2014-01-31 | 2014-01-24 14:21 | -7 | 2013-10-22 12:05 | Civil - Tunnelling | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | On the 02/10/2013 during a Crossrail led surveillance, held at the Finsbury Circus office, on permeation grouting verification records. When reviewing the TAM drilling record sheets it was evident that the hold points on the ITP were not being signed off prior to the work commencing.
| 02SL - Stations (LUL) | Cxxx-NCR-000626 | NCR | Permeation grouting verification documents |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2014-02-07 | 2013-12-02 12:11 | -67 | 2013-10-22 12:11 | Civil - Tunnelling | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | On the 02/10/2013 during a Crossrail led surveillance, held at the Finsbury Circus office, on permeation grouting verification records. The contractor was asked to provide evidence of ITP interventions hold and witness points by QC contractor; the contractor was unable to provide this.
| 02SL - Stations (LUL) | Cxxx-NCR-000627 | NCR | Permeation grouting verification records |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2014-01-31 | 2014-01-23 12:18 | -8 | 2013-10-22 12:18 | Civil - Tunnelling | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | On the 02/10/2013 during a Crossrail led surveillance, held at the Finsbury Circus office, on permeation grouting verification records. . When reviewing the TAM drilling record sheets it was found that they were incomplete with important information missing.
| 02SL - Stations (LUL) | Cxxx-NCR-000628 | NCR | L - CP6/PTE-W: Damaged rebar from invert |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-03-07 | 2014-01-07 14:03 | -59 | 2013-10-22 14:09 | Tunnelling - Linings - Sprayed Concrete | 30000 |  | Design | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On the 10/10/13 during the break out of the enlargement PTE-W ( CP6 ) Adv6, some NF1 rebars B32 were exposed ( 4 in the right and 1 in the left of the invert ), this area has been over broken just under 100mm on both sides.
| 02SL - Stations (LUL) | Cxxx-NCR-000629 | NCR | W - PTW-W, CAV SWD top left drift: Incorrect starting excavation sequence of adv 1 of CAV SW top left |  | Contr | __M |  |  | 2014-01-24 | 2013-12-20 14:39 | -35 | 2013-10-28 18:23 | Tunnelling - Linings - Sprayed Concrete | 3817.11 |  | Supervision/Management | Rework | 3 (3-6k) | Complete | Supervision - Insufficient supervision | Completed |  | On DS 16/10/13, The bottom part of the side wall drift south top (upper part of advance 4) was started before Advance 1 which is not in accordance with RESS CAV-WB/01 sequences.
| 02SL - Stations (LUL) | Cxxx-NCR-000630 | NCR | L - Marking up of chainages every 10m is not done |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-07-29 | 2016-06-10 10:22 | -49 | 2013-10-30 16:10 | Tunnelling - Tunnelling General | 1000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Marking up of chainages every 10m is not done everywhere in LIV Tunnels
| 02SL - Stations (LUL) | Cxxx-NCR-000631 | NCR | L - CP6/PTE-E: Damaged rebart at invert level during breakout |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-01-31 | 2013-12-12 11:08 | -50 | 2013-11-06 17:47 | Tunnelling - Linings - Sprayed Concrete | 30000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | On the NS 24/10/13 during the break out of the enlargement PTE-E ( CP6 ) 30 NF1 rebars B32 (radial and horizontal) have been exposed. Refer to attachment 2 - “CP6- PTE-E Invert opening - Bars exposed” for detail of the number and location of the rebars exposed
| 02SL - Stations (LUL) | Cxxx-NCR-000632 | NCR | W - CR0911 - Water Penetration Test Results non-compliant |  | Contr | __M |  |  | 2014-02-14 | 2013-12-03 13:47 | -73 | 2013-10-29 14:17 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Sample CR0911 has been cored on 10/09/2013 (date of spray 28/08/13) in CP3 wall area to be excavated to create EP2 CL in order to carry out the water penetration test of August. Results are showing non-compliance to the KT20-06: one individual results 39mm and average of 27mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000634 | NCR | Permeation Grouting verification Documents |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2014-03-28 | 2014-02-03 10:38 | -53 | 2013-10-30 09:43 | Civil - Tunnelling | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | On the 02/10/2013 during a Crossrail led surveillance, held at the Finsbury Circus office, on permeation grouting verification records,whilst reviewing theITP for Permeation Grouting Cxxx‐__M‐C‐ITP‐C101‐50043 rev 0.2 inspection number 2.1 States that the Verifying document as being the Survey Record, the Contractor was unable to supply this on request.
| 02SL - Stations (LUL) | Cxxx-NCR-000635 | NCR | Permeation Grouting verification Documents |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2014-02-07 | 2014-01-23 12:25 | -15 | 2013-10-30 09:58 | Civil - Tunnelling | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | On the 02/10/2013 during a Crossrail led surveillance, held at the Finsbury Circus office, on permeation grouting verification records. The contractor was asked to provide evidence of training and competence of all key personnel carrying out the permeation grouting. The Contractor was unable to supply this information.
| 02SL - Stations (LUL) | Cxxx-NCR-000636 | NCR | W - PTE-E Ch30 Significant Cracking in crown |  | Contr | __M |  |  | 2014-07-18 | 2014-06-25 17:33 | -23 | 2014-04-07 14:02 | Tunnelling - Linings - Sprayed Concrete | 2598 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | On 18/02/14, a significant crack was found during the process of snagging identification in WHI – PTE-E around chainage 30 in the crown between approximately 9’ to 1’.
| 02SL - Stations (LUL) | Cxxx-NCR-000637 | NCR | W - Bypass Enlargement advance 4 LHS was constructed under profile |  | Contr | __M |  |  | 2014-04-25 | 2014-03-03 11:56 | -53 | 2013-11-26 09:27 | Tunnelling - Linings - Sprayed Concrete | 1555 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | On 17/10/13 NS, during excavation of Bypass Enlargement advance 4, the left hand side was too thin leading to the removal of a previously installed section of Kwikastrip.
| 02SL - Stations (LUL) | Cxxx-NCR-000638 | NCR | L - AP7W Pilot Adv 112 & 113 defect on primary lining in the invert |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-02-07 | 2013-11-07 12:06 | -92 | 2013-10-31 16:13 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On DS 30/10/2013 a hole in the invert of AP7-W pilot, advances 112 & 113, has been found. The area has been cleaned and survey done. - Adv 112: Area is approximately 1600x1900mm and 150mm depth. - Adv 113: Area is approximately 1800x1600mm and 350mm depth. You will find attached the dimensions, the survey and photos of the hole in attachment 1.
| 02SL - Stations (LUL) | Cxxx-NCR-000639 | NCR | L - AP7-W CH1-2 Joint preparation not suitable |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-02-21 | 2014-01-23 07:49 | -29 | 2013-11-08 11:50 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | On DS 16/10/13, the 8t excavator c/w road headerhas been used to prepare joint. This did not provide a suitable ‘square joint’ in the staggering between sprayed stages.
| 02SL - Stations (LUL) | Cxxx-NCR-000640 | NCR | L - CH1-1 Steps in primary lining thickening |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-03-07 | 2014-01-09 12:04 | -57 | 2013-11-08 12:09 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Rework | 2 (6-60k) | Complete | Management Problem - Inadequate supervision | Completed |  | • On 22/10/13 NS, Area around joint between top heading and invert section of thickening has been found out of tolerance. Approx 1m height area alongside the joint where the top part of it is locally over sprayed and the invert side under sprayed locally. Worst case is a step of 200mm • Refer to the sketch and survey attached for a better understanding.
| 02SL - Stations (LUL) | Cxxx-NCR-000641 | NCR | W -PTW-W Enlarg Adv 139: Missing 1h early strength test |  | Contr | __M |  |  | 2014-01-24 | 2013-12-03 13:49 | -52 | 2013-11-08 13:56 | Tunnelling - Linings - In-situ Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate resources | Completed |  | On 05/05/13, all early strength testing up to 6 hours is missing. See Early Strength Checksheet attached.
| 02SL - Stations (LUL) | Cxxx-NCR-000642 | NCR | W - Bypass Wraparound: Thickening Stage 1 & 2 sprayed in a different sequence that on design drawings |  | Contr | __M |  |  | 2014-02-28 | 2013-12-10 15:08 | -80 | 2013-11-11 14:35 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • Due to the limit of reach of the spray robot, the invert sections could not be sprayed in one go. The Stage 1 steel was fixed in entirety and the first half sprayed from outside of the wraparound. Not only would we have to wait 24hrs to drive on this section to spray the second half but the backfill ramp would have to be placed and then removed and the layer cleaned to place and spray Stage 2 steel. On DS 07/11/13, it was decided to tie the first half of Stage 2 and spray this in. Once cured the ramp could be built and the second half of Stage 1 sprayed, followed by the steel fixing and spraying the second half of Stage 2. This took out one sequence of backfill removal and cleaning as well as one 24hr waiting period. • The reinforcement steel for Stage 1 & 2 was fixed and sprayed to DWG Cxxx-__M-C4-DDB-D061-00445, Rev P01. During this time, Revision P02 of this DWG was released showing a different location for the splice of the invert radial B16 bars. Rev P01 showed the splice offset to the left of the centre line, whilst P02 showed the splice offset to the right of the centreline. The bars were fixed and sprayed as per Revision P01.
| 02SL - Stations (LUL) | Cxxx-NCR-000643 | NCR | W - PTE-E enl. Adv 106: Area of 0.5*0.5m of Primary lining sprayed with Regulating Layer |  | Contr | __M |  |  | 2014-03-28 | 2014-01-16 17:34 | -71 | 2014-01-10 11:10 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | On 05/11/13, after cleaning the primary lining, an area of 0.5m * 0.5m of primary lining was re-sprayed with Mix Regulating Layer instead of mix P1 in PTE-E Ch75.
| 02SL - Stations (LUL) | Cxxx-NCR-000644 | NCR | L - PTE-W Advance 18: Thickness of the Safe stop not compliant |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-02-21 | 2014-02-12 09:02 | -9 | 2013-11-15 12:03 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | • On 19/10/13 DS, a 200mm safe stop has been sprayed in the PTE-W Enlargement face for less than 3 days. (see att. 1 - SRG 19/10/13). • On 23/10/13 DS and because the stop was going for more than 3 days, it has been agreed by SRG that 200 mm were considered as appropriate even if it's not in accordance with the drawing and RESS. (see att. 2 – SRG 23/10/13)
| 02SL - Stations (LUL) | Cxxx-NCR-000645 | NCR | L - AP1 Invert Enl Adv 26 & 27 - Kwikastrip partially sprayed in with the initial |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-02-21 | 2014-02-13 14:36 | -8 | 2013-11-25 09:17 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | • On 05/11/13 NS, 8 No. bars partially encapsulated by initial lining spray - refer to photo attached for evidence
| 02SL - Stations (LUL) | Cxxx-NCR-000646 | NCR | L - AP1 Invert Enl Adv 21: Excavated sand used for the backfill of the drain/trench |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-03-07 | 2014-01-08 10:06 | -58 | 2013-11-25 09:48 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Insufficient quantity of material to do the job | Completed |  | • On NS 27/10/13 in AP1 Deep Invert Enlargement Advance 21 __ used excavated sand instead of 6mm aggregate to backfill the drain.
| 02SL - Stations (LUL) | Cxxx-NCR-000647 | NCR | W - VA4 Enlarg, adv. 1-19: Missing early strength tests |  | Contr | __M |  |  | 2014-02-28 | 2013-12-13 11:53 | -77 | 2013-11-25 16:52 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | • In VA4 adv. 1-19, Early Strength Tests should have been performed every third advance, or at advances 1&2, 5, 8, 11, 14, and 17, 18 & 19. Instead, Early Strength Tests were undertaken at advances 7, 12, 16, and 17, 18 & 19. This resulted in too large of a gap between testing between advances 1&2 and 7 and again between advances 7 and 12. • For Advance 7, 06.08.2013 (night shift), the 1h early strength penetrometer test is missing. An early strength penetrometer test was performed at 30 minutes, which exceeds the requirement.
| 02SL - Stations (LUL) | Cxxx-NCR-000648 | NCR | W - Side Wall Drift Invert: Design Review Process Failure |  | Contr | __M |  |  | 2014-03-21 | 2014-01-07 16:20 | -73 | 2013-12-16 12:39 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | During WHI Westbound crossover, Side Wall Drift Invert design check • A__ has produced calcs and drawings and issued them to UnPS. These calcs were not matching with the drawings: o The calcs assumed that the thickening of the Side Wall Drift Invert (in red on the sketch attached) had to be installed as we excavate, every 1m. o The drawing Cxxx-__M-C4-DDB-D061-00315 was indicating that this thickening had to be installed after the whole full length invert is excavated, which is contradictory to the calcs. There is also the drawing Cxxx-__M-C4-DDB-D061-00306 which leaves the level of detail of this sequence ambiguous. • UnPS CAT II showed that the sequences detailed in the drawings (ie, thickening to be installed only once the full length invert is excavated) were in line with their calcs. • Constructability Review was held and reviewed the drawings for this section of work but it has not picked up any inconsistency (see attached MoM). • This issue has been discovered during late discussions between __ and A__ on an unrelated question of sequence to the sidewall drift. This caused A__ to revisit the initial calcs and of course discover the difference in the assumption.
| 02SL - Stations (LUL) | Cxxx-NCR-000649 | NCR | L - PTW-E Enl Adv 5: Face support thickness required not achieved for up to 24 hours |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-08-29 | 2014-06-05 09:46 | -85 | 2013-11-25 13:47 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | • On the 17/11/13 NS, face support has been sprayed as a sealing for 24 hours. This face support was with only 50mm and 40mm thick in some areas. Refer to the proof drilling checksheet attached done the 19/11/13 for evidence
| 02SL - Stations (LUL) | Cxxx-NCR-000650 | NCR | L - PTE-W Enlarg Adv 23: bad quality of square joint |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-07-25 | 2014-07-28 12:43 | 3 | 2013-11-27 17:49 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | • On 27/10/13 NS, while excavating double invert, the joint has been jigger and square joint hasn’t be achieved properly. Refer to the photo attached for evidence.
| 02SL - Stations (LUL) | Cxxx-NCR-000651 | NCR | L - AP7-E CH2: Minor thickness from permanent invert lining |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-03-07 | 2014-02-21 12:55 | -14 | 2013-11-28 15:52 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • On 19/11/13 DS, shotcrete thickness check has been done. One point with a thickness of 340mm has been found. Refer to the proof drilling check sheet attached for evidence.
| 02SL - Stations (LUL) | Cxxx-NCR-000652 | NCR | W - EP2 Enlarg adv 14: Cores showing an area with insufficient thickness in the primary lining |  | Contr | __M |  |  | 2014-03-21 | 2014-02-07 10:06 | -42 | 2013-11-26 09:47 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Cores taken on 25/11/13 and subsequent proof drilling revealed an area (800mm x 250mm, LHS Axis) in EP2 enlargement adv 14, that was of insufficient thickness in the primary lining. • Out of 4 cores taken in this area, two were shown to be insufficiently thick. • The first was marginally thin with an overall thickness of 270mm to 290mm. • The second showed a localised thin area. One side of the core being correct at 300mm and the other only 190mm. • Subsequent proof drilling defined an area of approximately 800mm x 250mm that was thinner than design by 10mm to 50mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000653 | NCR | W - PTW-W Enlarg. Adv 46: Radial invert crack formed in the joint between Adv T13 and Adv 46 |  | Contr | __M |  |  | 2014-03-07 | 2014-03-10 09:45 | 3 | 2013-12-19 11:39 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Material | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | On 20/11/13, during inspection of exposed invert joit, a radial invert crack formed in Advance 46, more specifically in the joint between Advance T13 and 46. Radial Crack on the left side of invert with width between 3mm and 15mm. (see sketch attached for clarity)
| 02SL - Stations (LUL) | Cxxx-NCR-000654 | NCR | W - EP2 adv 15&21 invert: Cleanness of the joints between the top advances and invert |  | Contr | __M |  |  | 2014-03-21 | 2014-01-07 12:48 | -73 | 2013-12-17 09:53 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | On 22/11/13 DS and 24/11/13 DS, in EP2 adv 15 and 21 Invert, there was a possibility that preparation of the joint between top and invert primary layer did not fully comply with the KT.20.3214 and drawing requirements due to the cleanness of the joint.
| 02SL - Stations (LUL) | Cxxx-NCR-000655 | NCR | L - CP6 Enlarg, adv 2, 4, 11, 12, 36: Incomplete Early Strength Testing sheets and inadequate strengths on J2 curves |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-03-28 | 2013-12-09 14:52 | -109 | 2013-12-05 14:15 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | • Issue 1: On 20/01/13 and 22/01/13, Incomplete J2 curve for Adv 4(3hr and 12hr test points missing) and Adv 12 (3hr test point missing). • Issue 2: On 31/01/13, __ test sheet missing for Adv 36 • Issue 3: On 22/01/13 and 03/02/13 Inadequate strengths for J2 curves for Adv 11, Adv 12 and Adv 2 Invert.
| 02SL - Stations (LUL) | Cxxx-NCR-000656 | NCR | W - EP2 adv 15 double invert: interruption in spraying |  | Contr | __M |  |  | 2014-03-28 | 2014-02-07 10:10 | -49 | 2013-12-17 15:13 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Equipment Breakdown | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Not Defined | Completed |  | On 22/11/13 DS, EP2 Adv 15, double invert has been sprayed at 11:00am, stopped and restart at 15:00 afternoon. There was an interruption in spraying operation, which caused the loss of quality of the SCL lining. Invert has been sprayed at 11:00am, stopped and restart at 15:00 afternoon.
| 02SL - Stations (LUL) | Cxxx-NCR-000657 | NCR | W - PTW-E/CP3: Theoretical profile thickness secondary lining or specified profile limits of at PTW-E window to CP3 (ch 47 to 58) cannot be maintained due to L-bar placement in primary lining |  | Contr | __M |  |  | 2014-06-20 | 2014-05-15 16:33 | -36 | 2013-12-19 11:51 | Tunnelling - Linings - Sprayed Concrete | 10000 |  | Design | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The theoretical profile thickness of the secondary lining of PTW-E at CP3 cannot be maintained due to design and integration of L-bar reinforcement in primary previous lining. Scans reveal that the primary lining was built ‘big’ in areas around the opening of CP3 in PTW-E. Due to the placement of the L-bar reinforcement, the area out of tolerance in the primary lining cannot be trimmed. Result of this would be an overprofile of the secondary lining or a reduced secondary lining thickness.
| 02SL - Stations (LUL) | Cxxx-NCR-000658 | NCR | L - PTE-E adv 63 and PTE-W adv 40 enlarg: Start of excavation with having just one __ working |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-04-18 | 2014-02-17 12:31 | -60 | 2013-12-12 14:43 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Equipment Breakdown | Rework | 4 (0.5-3k) | Complete | Management Problem - Improper resource allocation | Completed |  | On 20/11/2013 DS: Excavation in PTE-E Advance 63 have started. On 21/11/2013 NS : Excavation in PTE-W Advance 40 have started. In both cases only one __ was ready to be used. 2nd __ was trapped in PTW-W due to the breakout of the invert
| 02SL - Stations (LUL) | Cxxx-NCR-000659 | NCR | L - PTW-W/CP3a enlarg, Stage 1 thickening spray (FF1): Rebar badly encapsulated |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-03-28 | 2014-01-09 11:51 | -78 | 2014-01-06 13:09 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | On 03/12/2013 NS, thicknening layer (FF1) has been sprayed. On 04/12/2013 NS, voiding/delamination have been found between previous primary lining and newly applied P2 shotcrete. Refer to the shift report attached for evidence
| 02SL - Stations (LUL) | Cxxx-NCR-000660 | NCR | L - PTW-E adv 39 enlarg: Low strength gain |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-03-14 | 2014-01-27 10:53 | -46 | 2013-12-12 14:19 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | On 02/12/2013 NS: Panel for the Advance 39 has been sprayed at 22:25 and the penetrometer results are following: at 15 min: 0.28N/mm2; at 30 min: 0.29N/mm2 and at 1hr: 0.37N/mm2. Refer to the PTW-E Adv 39 Early strength test results attached.
| 02SL - Stations (LUL) | Cxxx-NCR-000661 | NCR | L - PTE-W adv 74 LS enlarg: Core 1146 show insufficient thickness |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-06-01 | 2014-11-07 12:37 | -206 | 2013-12-13 11:15 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On 06/12/2013 NS, one set of 5 cores has been done and one of the cores had a length of 350mm. Refer to Photo attached and Cores Report. On 07/12/2013 DS, minor thickness has been confirmed by proof drilling. Refer to the Checksheet attached for results.
| 02SL - Stations (LUL) | Cxxx-NCR-000662 | NCR | L - PTW-W Enlarg: Early Strength Tests Missing & Profile within tolerance |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-03-28 | 2014-01-07 14:41 | -80 | 2013-12-12 15:32 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | • Early Strength Testing A. Advance 12 – 1 hour test missing, failure at 40mins, achieved J2mod at 90mins. B. Advance 15 – 3hr test missing, achieved J2mod prior to 5hour test C. Advance 18 – no Early strength record (missed third advance for testing, test performed on advance 19). D. Advances 24, 28, 39 – 1 hour test missing E. Advance 42 - no Early strength record (missed third advance for testing, test performed on advance 43) • Profiles A. Advance 36 Primary profile – some invert points are within the tunnel design profile.
| 02SL - Stations (LUL) | Cxxx-NCR-000663 | NCR | L - Nonconforming Cores of week ending the 06/12/2013 - CR1097 PTE E Enl Adv 40 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-05-30 | 2014-03-25 12:20 | -66 | 2013-12-13 10:11 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Nonconforming Cores of week ending 06/12/2013: Cores CR1097 - PTE-E Enlargement-Adv 40-LK, • Core 1: Ok • Core 2: Core broken and shadowing • Core 3: Trap rebound behind steel • Core 4: Good rebar encapsulation and slight voiding See attached Cores Report.
| 02SL - Stations (LUL) | Cxxx-NCR-000664 | NCR | L - CH1-2: No sumps installed |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-07-29 | 2015-09-24 12:48 | -309 | 2013-12-20 12:44 | Tunnelling - Linings - Sprayed Concrete | 3500 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | • The thickenings in CH1 have been completed in the invert without the indicated sumps installed as per IFC drawings. • Cxxx requirement for these sump have not been taken into consideration in the Cxxx design.
| 02SL - Stations (LUL) | Cxxx-NCR-000665 | NCR | L - PTW-W CP3a stage 4: No curing applied |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-04-04 | 2014-01-13 07:56 | -81 | 2014-01-06 14:31 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Stage 4 (Final layer) of the primary lining thickening for PTW-W / CP3a-reinforced areas was sprayed on day shift 09/12/2013 but no curing has been applied.
| 02SL - Stations (LUL) | Cxxx-NCR-000666 | NCR | L - PTW-W / CP3a Thickening - Over-scabbling |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-04-04 | 2014-01-13 10:02 | -81 | 2013-12-20 12:35 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | On 02/12/2013 NS and 03/12/2013 DS, Scabbling has been done prior to the installation of the thickening. Post Proof drilling done the 03/12/2013 DS show one spot with a total thickness of 370mm. Refer proof drilling check sheet attached
| 02SL - Stations (LUL) | Cxxx-NCR-000667 | NCR | L - Lack of traceability of calibration measuring equipment |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-07-31 | 2016-07-19 10:17 | -12 | 2014-01-30 14:59 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | SCL surveillance carried out 20.09.2013 identified lack of traceability of calibration measuring equipment: 1. Lapsed calibration of one thermometer, 2. No traceability or proof of calibration of penetrometer needles, 3. Flow table appeared outside of tolerances (40+/-1mm as per BS EN 12350-5)
| 02SL - Stations (LUL) | Cxxx-NCR-000668 | NCR | L - Electra House: Drilling of TAMs with revised azimuth and or dip from the detailed drawing and schedules |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-09-19 | 2014-07-25 16:02 | -56 | 2014-07-18 13:52 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | During the TAM drilling operations boreholes were identified which were not possible to drill at the set-out position due to various site constraints. (see Att A. and B.)
| 02SL - Stations (LUL) | Cxxx-NCR-000669 | NCR | W - RCE Foam Concrete: Higher strengths and densities than suggested |  | Contr | __M |  |  | 2014-05-30 | 2014-04-24 15:07 | -36 | 2014-02-19 15:30 | Tunnelling - Linings - Sprayed Concrete | 4160.52 |  | Workmanship | Rework | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | On 9th, 11th and 12th January 2014 whilst undertaking Foam Concrete Plug pours in Reception Chamber East (RCE) the following non-conformances were observed with regards to the density and strength requirements. See also attached summary of the results for more details (att 1):- Density - Pour 2: 1-day 1390 kg/m3 - Pour 3: 1-day 1940 kg/m3 Strength (cube results) - Pour 3: 1-day 9.7 and 7-day 31.2 N/mm2 Strength (Core results) - Pour 1: 5-day 13.3 N/mm2 No tests done for Pour 4
| 02SL - Stations (LUL) | Cxxx-NCR-000670 | NCR | W - CP2 Enlarg, Adv 27 Non-conforming Early strength testing |  | Contr | __M |  |  | 2014-03-04 | 2014-01-07 13:59 | -56 | 2014-01-06 13:51 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | On 25/082012, Early strength test results non-compliant each time the panel was tested by both penetrometer needle and the __ pull out test. (see J2 Curve attached) Penetrometer testing, which is carried out several times within 60 minutes of the panel being sprayed, was below the required J2 strength at all test points. After 3-24 hours of the panel being sprayed, the __ pull out test results were also non-compliant by not meeting the J2 specifications.
| 02SL - Stations (LUL) | Cxxx-NCR-000671 | NCR | W - CP2N Enlarg Adv 39: No flow test carried out and recorded |  | Contr | __M |  |  | 2014-04-04 | 2014-01-07 14:00 | -87 | 2014-01-07 09:08 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | On 30/08/2012, Spraying of CP2N Enl Adv 39 (Initial lining) completed with no records for pre-shotcrete check or inspection of wet shotcrete.
| 02SL - Stations (LUL) | Cxxx-NCR-000672 | NCR | L - CP5 and 6 Thickenning: Miscellaneous items |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-04-25 | 2014-02-19 17:43 | -65 | 2014-02-19 17:35 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | During CP5 thickening work in June 2013: o Early strength tests is missing before 90min for Stage 3. (see attached) During CP6 thickening work in May 2013: o Early age strength curve for stage 6: flow and temperature data missing (see attached) o Wrong proforma used for spraying thickening for Stage 6 (see attached)
| 02SL - Stations (LUL) | Cxxx-NCR-000673 | NCR | L - PTE-W Enl. Adv 90 RS - CR1180 and Adv 100 RK - CR1208: Insufficient Lining Thickness |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-06-01 | 2015-01-15 11:56 | -137 | 2014-01-27 14:12 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | - On 17/12/2013 NS, one set of 4 cores has been done in PTE-W Enlargement Adv 90 RS and 3 cores where less than 400mm (350mm). Refer to the cores review attached for evidence - On 12/01/2014 NS, one set of 5 cores has been done in PTE-W Enlargement Adv 100 RK and 1 core was 320mm long (instead of 400mm). Refer to the cores review attached for evidence
| 02SL - Stations (LUL) | Cxxx-NCR-000674 | NCR | L - PTE-W Enl. Adv 99: Early Strength Failed |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-04-25 | 2014-02-03 09:54 | -81 | 2014-01-20 15:06 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | On 17/12/2013 NS: Panel for the Advance 99 has been sprayed at 17:15 and the results were under the J2 modified even after the age of 12 hours. Refer to the PTW-W Enl Adv 99 Early strength test results attached.
| 02SL - Stations (LUL) | Cxxx-NCR-000675 | NCR | L - PTE-E Enl. Adv 95: Over excavation in the crown |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-04-25 | 2014-03-11 13:44 | -45 | 2014-01-20 15:41 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | On 08/01/2014 DS and NS , the advance PTE-E Enl Adv 95 has been significantly over-excavated in the crown - refer to the excavation profile attached.
| 02SL - Stations (LUL) | Cxxx-NCR-000676 | NCR | L - PTE-E Enl Adv 97: Discontinuation from the excavation (unsupported for roughly 25 min) |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-05-23 | 2014-03-11 13:39 | -73 | 2014-02-05 17:24 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | On 08/01/2014 between the NS and DS, the excavation from Adv 97 was on hold and unsupported for roughly 20 min without any labourer at the face.
| 02SL - Stations (LUL) | Cxxx-NCR-000677 | NCR | W - CP1a: Insufficient preparation of joints and potential damage to encapsulated rebar during remedial works |  | Contr | __M |  |  | 2014-03-28 | 2014-01-22 11:27 | -65 | 2014-01-17 09:49 | Tunnelling - Linings - Sprayed Concrete | 2000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | On 15 & 16/01/14, at CP1A thichening: • Whilst inspecting the first layer of crown steelwork the inspector noted that there was no clear and square joint for the first and final layers between the invert and crown thickening. • The second, intermediate layer did have a clean square joint. • It was agreed to cut and chisel a joint out of the feathered section to create a better key (and hence better load transfer) between invert and crown. • Whilst placing the cut line, using the hydraulic chainsaw, two mistakes were made. The cut line was lower than that marked out and the chiselling commenced under the line, not above the line. The chiselling was stopped when the operator exposed some of the FF3 steel under the eye. (see photo 490 attached). The engineer and PIC were notified.
| 02SL - Stations (LUL) | Cxxx-NCR-000678 | NCR | L - Nonconforming Cores of week ending the 17/01/2014: PTE W Enl Adv 110 LK |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-09-19 | 2014-09-01 13:04 | -18 | 2014-01-23 11:58 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Nonconforming Cores of week ending 17/01/2014:- PTE-W Enlargement-Adv 110-LK, • Core 1: Broken and with 15mm voids • Core 2: Broken and with 15mm voids • Core 3: Broken, 50mm voids and rebars not properly encapsulated • Core 4: Broken and with voids • Core 5: Broken and with voids (see attached Cores Report)
| 02SL - Stations (LUL) | Cxxx-NCR-000679 | NCR | L - Cores holes not/incorrectly backfilled |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-08-28 | 2015-07-17 09:30 | -42 | 2014-01-30 16:21 | Tunnelling - Linings - Sprayed Concrete | 2000 |  | Planning | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | • Cores taken from the Enlargements are not always backfilled • In AP1, PTE-W and AP7 W, some core holes are not correctly backfilled. They are filled with muck.
| 02SL - Stations (LUL) | Cxxx-NCR-000680 | NCR | L - PTE E Enl: start of adv.142 despite low early strength result on adv. 141 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-08-22 | 2014-06-02 09:57 | -81 | 2014-01-23 11:31 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | On 20/01/2014 NS: Panel for PTE-E Enl., Adv. 141 has been sprayed at 04:30am. The penetrometer results were below J2 curve. (see attached Early strength test results for evidence) On 21/01/2014 DS: The excavation of the following advance (Adv 142) started at 7.15am whereas the results were still below J2 curve.
| 02SL - Stations (LUL) | Cxxx-NCR-000681 | NCR | L - PTE-E Enl Adv 155, PTE-W Enl Adv 164, PTW-W Enl Adv 92: faces left open, waiting for shotcrete |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-08-08 | 2014-06-20 09:27 | -49 | 2014-02-06 14:09 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Equipment Breakdown | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | • On 26/01/14 NS, between 10pm and 12pm re-mixer broke down while three faces were opened. One face has been left open for almost four hours. • In case of emergency, access to the pumps were nevertheless still possible.
| 02SL - Stations (LUL) | Cxxx-NCR-000682 | NCR | W - CP3 Enl Adv 9: Lack of early strength testing before 3 hrs |  | Contr | __M |  |  | 2014-04-04 | 2014-02-07 10:01 | -56 | 2014-01-28 17:14 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | On 26/08/2013 DS, 1 hour early strength test is missing for CP3 Enlargement Advance 9.
| 02SL - Stations (LUL) | Cxxx-NCR-000683 | NCR | L - Cores not taken as per schedule requirement |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-09-26 | 2014-07-04 08:28 | -84 | 2014-02-06 13:29 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | •At the end of January 2014, it has been noticed that 10 cores were not taken on time. Refer to the Sampling Requirements 30-01-2014 for evidence.
| 02SL - Stations (LUL) | Cxxx-NCR-000684 | NCR | L - PTE-E Enl Adv 75: Non compliant Water Penetration Result |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-04-18 | 2014-03-25 11:19 | -24 | 2014-02-04 15:13 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Sample CR01159 Taken in PTE-E Enlargement Adv 75 showing non-compliance for Water Penetration Test: one individual results 46mm and average of 36mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000685 | NCR | L - AP7 East TP Adv 96 and 99 – Early Strength tests results below J2 curve |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-06-27 | 2014-03-31 16:19 | -88 | 2014-03-31 11:24 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | • On 05/05/13, AP7 East Adv 96 has been sprayed: The Penetometer test results (at 3, 6, 10, 15, 30, 45, 60, 120 min) are below the requirements. see att 1 • On 06/05/13, AP7 East Adv 99 has been sprayed: The Penetometer test results (at 3, 6, 10, 15, 30, 45, 60, 120, 180 min) are below the requirements. see att 1
| 02SL - Stations (LUL) | Cxxx-NCR-000686 | NCR | L - PTE-W LCE Enl Adv 48: Invert completed before to seal the face |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-06-13 | 2014-02-27 13:37 | -106 | 2014-02-25 09:36 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | • On 15/02/14 DS, during Advance 48 ( double-invert ) construction, primary, lining for invert section was completed prior to seal the front face. (Refer to the photo attached for evidence)
| 02SL - Stations (LUL) | Cxxx-NCR-000687 | NCR | W - PTW-E Blocks 7 and 9: Joint between invert concrete slab and side wall not formed as per design |  | Contr | __M |  |  | 2014-05-16 | 2014-03-24 09:50 | -53 | 2014-02-10 14:28 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The shape of the joint between the cast in-situ invert and cast in-situ sidewall was not formed radial according the secondary Lining design and or the RFI 596 which allows a step in the joint an a slight reorientation of the radial angel in the secondary lining.
| 02SL - Stations (LUL) | Cxxx-NCR-000688 | NCR | W - PTW-East Invert Slab Blocks 6 and 8: Damaged Waterproofing Membrane |  | Contr | __M |  |  | 2014-05-16 | 2014-04-04 17:42 | -42 | 2014-02-11 14:26 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | • Begining of Feb. 14, whilst the installation and assembly of the invert shutter at blocks No 6 and 8 the waterproofing membrane was damaged. • Damage to the waterproofing membrane was in the vicinity of the side shutter (radial joint): Adjacent to invert shutter Block 6 and adjacent to Block 8 at a higher level approximately 2-3m from the edge of the invert block. See pictures attached
| 02SL - Stations (LUL) | Cxxx-NCR-000689 | NCR | W - PTW-E: MCRs for secondary Lining were not submitted/approved prior to pouring the first blocks |  | Contr | __M |  |  | 2014-10-17 | 2014-09-22 12:02 | -25 | 2014-02-14 16:08 | Tunnelling - Linings - Sprayed Concrete | 500 |  | System Defect | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | In PTW-E, the submission for the MCR approval of the invert concrete was submitted late, alongside other materials involved in secondary lining invert works which have been used prior to acceptance: o MCR 50148 shutter spirals remaining in invert concrete o MCR 50149 curing agent for secondary lining o MCR 50151 concrete spacer bars o MCR 50152 invert concrete mix o MCR 50156 retarder
| 02SL - Stations (LUL) | Cxxx-NCR-000690 | NCR | W - PTW-W Enl Adv 169: No early strength records available |  | Contr | __M |  |  | 2014-05-16 | 2014-03-10 17:45 | -67 | 2014-02-10 15:33 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | On 24/06/13 (Day shift), there are no results for required early strength panel of Adv. 169.
| 02SL - Stations (LUL) | Cxxx-NCR-000691 | NCR | W - RCE Foam Concrete: no cubes taken on the last pour |  | Contr | __M |  |  | 2014-05-23 | 2014-04-04 17:28 | -49 | 2014-02-14 14:06 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | On the last foam concrete pour at RCE, no cubes were taken.
| 02SL - Stations (LUL) | Cxxx-NCR-000692 | NCR | W - PTW-E Blocks 1 to 9 - Insufficient finish on the sides of the invert concrete slab |  | Contr | __M |  |  | 2014-05-16 | 2014-05-16 09:17 | 0 | 2014-02-11 14:14 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • In PTW-E Blocks 1 to 9: Side shutter forming the radial joint not completely filled underneath the horizontal formwork. See pictures attached for a better understanding.
| 02SL - Stations (LUL) | Cxxx-NCR-000693 | NCR | EBRT W (Pilot) Advance 10 SCL Early Strength Requirement Not Achieved |  | Crossrail | XRL |  |  | 2014-05-30 | 2014-05-30 13:42 | 0 | 2014-02-14 11:11 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | On 8/12/2013 dayshift whilst spraying the pilot Eastbound Running Tunnel West Advance 10 early strength testing using the penetrometer and __ methods was carried out and the following results were gained:- 1 Hour 0.23 MPa (Penetrometer) 3 Hours 0.63 MPa (Penetrometer) 4 Hours 2.19 MPa (__ Test) The minimum early strength requirements according to the Specification (Figure KT20-01) are:- 1 Hour 0.5 MPa 3 Hours 1.0 MPa (1) These strengths were not achieved. The minimum strength requirement as per Whitechapel General SCL Tunnelling Methodology Revision 10 states ''no personnel to enter under the vault until it is sure that all sprayed concrete has attained minimum strength of 0.25MPa” (2) This minimum strength for safety was not achieved but despite this work commenced on advance 11.
| 02SL - Stations (LUL) | Cxxx-NCR-000694 | NCR | L - PTE and PTW: Missing early strength tests, some profiles not within tolerance |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-06-13 | 2014-06-09 11:42 | -4 | 2014-03-06 08:32 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | • Early Strength Testing A. PTE-W Advance 2 – 3 hr test missed, early strength failing to reach J2 until 5hrs. B. PTE-E Advance 6 – 3 hr test missing C. PTW W Advance 9-11 – No panel taken D. PTW-W Advance 52 – 3 hr test missed E. PTW-W Advance 54 – 6 hr test missed • Profiles A. PTE-E Advance 6 – Two Points within the tunnel envelope. B. PTW-W Advances 9, 27 – Two/One Points within the tunnel envelope. C. PTW-W Advances 24, 39 – Two/Three points show insufficient thickness.
| 02SL - Stations (LUL) | Cxxx-NCR-000695 | NCR | L -Britannic House Tilt Meters: Full installation not complete |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-05-30 | 2014-03-12 09:33 | -79 | 2014-02-20 15:09 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | • Failed to connect the instrument to the power supply and install a communication box.
| 02SL - Stations (LUL) | Cxxx-NCR-000696 | NCR | W - PTW-E Blocks 1 and 3: Radial Joint repaired without approved documentation |  | Contr | __M |  |  | 2014-08-22 | 2014-07-30 18:02 | -23 | 2014-04-08 12:46 | Tunnelling - Linings - Sprayed Concrete | 8294.33 |  | Supervision/Management | Repair | 2 (6-60k) | Complete | Management Problem - Inadequate supervision | Completed |  | The radial joint at the top of the sidewalls have been poorly formed and is unacceptable to use. In order to be able to use these joints they must be repaired. The radial joints on the sidewalls for PTW-E Blocks 1 and 3 have been repaired without an approved repair procedure and using unapproved material for that location (__dur 41-CF which do not meet the fire requirements).
| 02SL - Stations (LUL) | Cxxx-NCR-000697 | NCR | W - PTW-E Block 1,3,4,5 and 6: Poor joint on top of side walls |  | Contr | __M |  |  | 2014-07-11 | 2014-07-01 15:31 | -10 | 2014-04-04 16:23 | Tunnelling - Linings - Sprayed Concrete | 1571 |  | System Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The radial joint at the top of the sidewalls have been poorly formed and is unacceptable to use. Different methods were used to help achieve the radial joint: • Block 1 - cast horizontally and the top of the sidewall joint was formed by building up the concrete. • Block 3 - cast to horizontal and then cut back after an hour to try and achieve a radial joint • Block 4 - cast with Expamet Hy-rib to help form the joint and was unsuccessful • Block 5 - cast with new additional design on top of the shutter, the joint was formed better but the edge of the sidewalls was broken off. • Block 6 - cast with the new shutter, but the concrete was not packed effectively and hence formed an inadequate joint.
| 02SL - Stations (LUL) | Cxxx-NCR-000698 | NCR | W and L - I and M installation: Anchor type used for rod extensometer |  | Contr | __M |  |  | 2016-12-16 | 2016-10-18 16:01 | -59 | 2014-02-24 10:10 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The Non Conformance happened due to the correct paperwork not being formally submitted and agreed with Crossrail. The Works Method Statement Cxxx __M C GMS CR092 50009 Installation of Monitoring Sensors was altered specifically after agreement with the Crossrail Cxxx monitoring representatives was approved to change the anchor type of the extensometer from the contract specified pronged type to the proposed packer anchor type. The effected extensometers were all the extensometers that were installed from the start of the contract which were prior to installation extensometer Cxxx-XR50304 on 09th January 2013. A total of 20 at Liverpool street and 14 at Whitechapel were successfully installed using the packer type anchor.
| 02SL - Stations (LUL) | Cxxx-NCR-000699 | NCR | W - CP3: Insufficient thickness in invert of CP3 thickening layer at the EP2 eye |  | Contr | __M |  |  | 2014-05-16 | 2014-04-22 14:36 | -24 | 2014-02-28 13:57 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Post-thickening scans of the invert of CP3 reveal a localised thin section, approximetaly 2mx8m, of thickening layer between chainages 27 and 27.5. Scans of the primary lining reveal that it was built to the specification of 350 mm thickness. Thickness scans taken after the spraying of the thickening layer reveal that the thickening is between 50mm to 200mm short of the required 350mm thickness. (see CP3 Scan annoted attached)
| 02SL - Stations (LUL) | Cxxx-NCR-000700 | NCR | W - CP3N: Removal of L-Bars in PTE-E around CP3 Window |  | Contr | __M |  |  | 2014-06-06 | 2014-05-15 15:38 | -22 | 2014-03-06 09:02 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On 16/02/14, the end parts of damaged L-Bars, in approx. 10 locations, were cut out and removed. (see attached sketch of L-Bar removed area) No thickening reinforcement was damaged in the process. Then the regulating layer was sprayed.
| 02SL - Stations (LUL) | Cxxx-NCR-000701 | NCR | L - CH2: Early Strength Tests Missed in several advances |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-05-30 | 2014-04-08 13:36 | -52 | 2014-02-27 13:18 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | During CH2 Primary Lining work in April 2013, Early Strength Tests have been missed in the following advances: • Advance 3, 17, 19, 23, 28 and 41: Panel missed • Advance 4: Early strength testing between 30min and 3 hr missed • Advance 8: Early strength testing between 30min and 1hr missed • Advance 14: Early strength testing at 3hr missed. • Advance 20: Early strength testing at 1 hr and 3 hr missed • Advance 38: Early strength testing at 1hr missed
| 02SL - Stations (LUL) | Cxxx-NCR-000702 | NCR | W - CP3: Early Strength Test Missed and Low J2 Curve |  | Contr | __M |  |  | 2014-05-16 | 2014-04-04 17:17 | -42 | 2014-03-05 10:27 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During CP3 works which occured between August and September 2013: • At Advance 6, early strength test measurements are missing at 1 hr and 3 hrs. Measurements were taken at 30 minutes and 5 hours. • At Advance 18, early strength test measurement missing at 3 hours. Measurements were taken at 1 hour and 6 hours. • At Advance 21, early strength test measurement missing at 1 hour. Measurement was taken at 30 minutes, which exceeds the requirement. • At Advance 24, early strength test measurement missing at 1 hour and 3 hours. Measurements were taken at 30 minutes (exceeding requirement) and 4.5 hours. • At Advance 27, early strength test measurement missing at 1 hour. Measurement was taken at 30 minutes, which exceeds the requirement. • On the 3rd Thickening Layer (P1), early strength testing is low at 1 hr.
| 02SL - Stations (LUL) | Cxxx-NCR-000703 | NCR | W - EBRT-W-Enl Adv 83 RK: Nonconforming Cores CR1367 |  | Contr | __M |  |  | 2014-07-25 | 2014-07-28 12:50 | 3 | 2014-03-05 09:52 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Nonconforming Cores : Cores CR1367 – EBRT-W-Adv 83 RK cored on 21/02/14 DS (see attachment 1): • Cores are broken, non-homogeneous and show lamination. One of the broken cores displays rebound and bad compaction at the bottom.
| 02SL - Stations (LUL) | Cxxx-NCR-000704 | NCR | W - PTE-E Ch99: Hollow area in the crown |  | Contr | __M |  |  | 2014-08-01 | 2014-06-25 15:01 | -37 | 2014-04-07 15:29 | Tunnelling - Linings - Sprayed Concrete | 2346 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | On 02/02/14, a significant hollow area was found during the process of snagging identification in WHI – PTE-E around chainage 99 in the crown between approximately 11’ to 1’. (See att 1: Snagging Documentation)
| 02SL - Stations (LUL) | Cxxx-NCR-000705 | NCR | W - PTW-E Block 8 cast in-situ invert Movement Joint constructed with unapproved Flexcell Material |  | Contr | __M |  |  | 2014-09-12 | 2014-09-05 14:33 | -7 | 2014-05-29 17:26 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | •In January 2014, in the permanent works PTW-E Block 8, the cast in-situ invert Movement Joint was constructed with unapproved material, Flexcell.
| 02SL - Stations (LUL) | Cxxx-NCR-000706 | NCR | W - PTW-E and EPTW-W Enl: Early Strength Test Missed |  | Contr | __M |  |  | 2014-06-27 | 2014-04-04 17:19 | -84 | 2014-03-17 17:49 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During PTW-E works which occured in April 2013: • At Advance 70, early strength test measurements are missing at 3 hrs. Measurements were taken at 60 minutes and 6 hours. • At Advance 73, early strength test measurement missing at 3 and 6 hours. Measurements were taken at 1 hour and 12 hours. • At Advance 76, early strength test measurement missing at 3 hours. Measurement was taken at 1 hour and 6 hours. • At Advance 79, early strength test measurement missing at 6 hours and 12 hours. Measurements were taken at 3.5 and 24 hours. • At Advance 82, early strength test measurement missing at 3 hours. Measurement was taken at 60 minutes and 6.5 hours. During PTW-W Extension works: • Early strength for PTW-W Extension advance 3 Invert has been missed. The Advance was completed on the 15/07/13.
| 02SL - Stations (LUL) | Cxxx-NCR-000707 | NCR | L - PTWW thickening: Cores show minor shadowing around the steel |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-07-25 | 2014-07-16 09:07 | -9 | 2014-03-21 14:12 | Tunnelling - Linings - Sprayed Concrete | 50000 |  | Workmanship | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Nonconforming Cores • CR1444 - CP3A Location Left in PTW-W cored on 13/03/14 (see attachment 1) • CR1445 - CP3A Location Right in PTW-W cored on 13/03/14 (see attachment 2) show laminations, voids and minor shadowing around the steel, and one longitudinal crack.
| 02SL - Stations (LUL) | Cxxx-NCR-000708 | NCR | secondary lining works without IFC drawings |  | Crossrail | PDP |  |  | 2014-04-13 | 2014-03-20 18:43 | -24 | 2014-03-14 14:54 | Tunnelling - Tunnelling General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | Secondary lining works had commenced in Cxxx WHI PTE and PTW tunnels in December 2013 without IFC drawings for these permanent works being issued (sikatape strip 15.-16.12.14, sheet waterproofing membrane 17.-18.12.13, invert concrete block 8 25.01.14). The works commenced and continued throughout January and February prior to issue of IFC drawings for the works.
| 02SL - Stations (LUL) | Cxxx-NCR-000709 | NCR | W - PTE-W Enl: Early Strength Test Missed |  | Contr | __M |  |  | 2014-06-13 | 2014-04-04 17:15 | -70 | 2014-03-18 17:02 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During certification package process of WHI PTE-W Adv 170-199, it was noticed than: • Adv 175: J2 curve: missing 12 hours test • Adv 178: J2 curve: missing 1 and 3 hours test. • Adv 187 & 193: J2 curve: missing 3 hours test. • Adv 199: J2 curve: missing 3 and 6 hours test.
| 02SL - Stations (LUL) | Cxxx-NCR-000710 | NCR | W - PTW-W Enl. Adv 174: Missing Flow Test prior spraying |  | Contr | __M |  |  | 2014-06-13 | 2014-04-22 15:27 | -52 | 2014-03-31 17:11 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | • On 25/06/13 DS, flow test has been missed prior to start of spraying PTW-W Enlargement Adv. 174.
| 02SL - Stations (LUL) | Cxxx-NCR-000711 | NCR | W - PTE-E Block 9 cast in-situ invert incomplete pour |  | Contr | __M |  |  | 2014-07-04 | 2014-07-01 15:16 | -3 | 2014-04-09 09:11 | Tunnelling - Linings - Sprayed Concrete | 8733 |  | Equipment Breakdown | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | On 18/03/14 NS, Permanent works PTE-E Block 9 pour was incomplete and could not be finished. A blockage was encountered in the line causing problems during pouring of PTE-E Block 9. The pour could not be completed and poured in one and therefore would not be suitable as permanent works.
| 02SL - Stations (LUL) | Cxxx-NCR-000712 | NCR | L - PTE-W LCE Enl Adv 14 RS: Non conforming Cores CR1354 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-07-25 | 2014-07-23 09:08 | -2 | 2014-04-04 11:17 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | PTE-W LCE Enl Adv 14 has been sprayed on 04/02/14 and cored (RS) on 19/02/14. The cores CR1354 were reviewed by __ and Cxxx and noted as a ACI grade of 3 due to some voids and laminations (see att 1 cores report): - Cores 1 and 5: Voids (50/75 mm) - Core 3: Voids (50 mm) and length <350mm - Cores 2 and 4: 1 lamination and voids (75/100 mm)
| 02SL - Stations (LUL) | Cxxx-NCR-000713 | NCR | L - PTW-W/CP3 thickenning: 1 void found in far face 3 spray |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-07-18 | 2014-04-25 12:12 | -84 | 2014-04-23 17:03 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • On 15/03/14 DS during the hammer tests, a void has been found in PTW-W / CP3 Thickening area sprayed the 14/03/2014
| 02SL - Stations (LUL) | Cxxx-NCR-000714 | NCR | L - CH5-AP5 Adv 8: Over excavation forward of approx 900mm |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-09-12 | 2014-06-20 09:36 | -84 | 2014-05-12 08:27 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | On 23/03/2014 DS , the advance CH5-AP5 Enl Adv 8 has been over excavated of approx. 900 mm. Refer to the excavation photo attached for evidence
| 02SL - Stations (LUL) | Cxxx-NCR-000715 | NCR | L - AP5 Enl Adv 11 RK: Non conforming Cores CR1494 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-07-25 | 2014-07-28 12:52 | 3 | 2014-04-25 14:51 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | AP5 Enl Adv 11 has been sprayed on 24/03/14 and cored (RK) on 31/03/14. The cores CR1494 were reviewed by __ and Cxxx and the followings imperfections were found: • Core 1: Trap rebound at the end of the core • Cores 3: Major voids behind kwikastrip rebars. See attachment 1 During the SRG meeting on the 01/04/14 it has been agreed that a NCR should be raised.
| 02SL - Stations (LUL) | Cxxx-NCR-000716 | NCR | W - Fallout repair forms D3-54: not signed by Crossrail |  | Contr | __M |  |  | 2014-07-11 | 2014-06-12 08:57 | -29 | 2014-04-07 13:33 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | During Platform Tunnels work in 2013, few Sections B- Pre shotcrete repair & inspection and C- Shotcrete spraying and post shotcrete repair & inspection of the Shotcrete repair form (D3-54) have not been signed by Crossrail Inspectors. (see forms attached for location details)
| 02SL - Stations (LUL) | Cxxx-NCR-000717 | NCR | W - PTW-E Block 4 Sidewall: Long time for concrete to cure |  | Contr | __M |  |  | 2014-06-27 | 2014-06-24 12:28 | -3 | 2014-04-23 14:20 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | On 24/02/14, permanent works PTW-E Block 4 was poured. Curing time was longer than expected (3 days). Too much retarder (Delvo. Stabilizer) was used within the mix causing the concrete to wait a long time before the curing process began. This longer curing time occurred in the side (wing) walls causing a delay in striking the shutter.
| 02SL - Stations (LUL) | Cxxx-NCR-000718 | NCR | L - London Wall Buildings: Watercell system 11 incorrectly labelled during configuration |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-06-01 | 2015-05-18 13:43 | -14 | 2014-04-07 16:05 | Surveying - Instrumentation and Monitoring | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | It has been identified that the internal monitoring system within London Wall Building - Water Cell System 11, sensor cells 13 & 15 - was incorrectly labelled during the configuration.
| 02SL - Stations (LUL) | Cxxx-NCR-000719 | NCR | W - RHS SWD invert thickening phase: Spraying P2 in the sides of the invert thickening instead of P1 |  | Contr | __M |  |  | 2014-07-18 | 2014-07-17 15:53 | -1 | 2014-04-17 12:12 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Not Defined | Completed |  | • On 18/02/14, during the RHS SWD invert thickening phase: area with no rebar sprayed with mix P2 instead of mix P1 in the invert thickening around the Section 2 (3m out from headwall) as shown on the sketch attached for better understanding (attachment 5). Please also refer to the statements made in FCD-581.
| 02SL - Stations (LUL) | Cxxx-NCR-000720 | NCR | W - EP2: Early Strength Tests Missing |  | Contr | __M |  |  | 2014-08-08 | 2014-04-22 15:24 | -108 | 2014-04-10 17:32 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | During EP2 tunneling, between September and November 2013: • At Advance 6, early strength test measurements are missing at 1 hr. Measurements taken at 30 minutes were below the J2 curve. Measurements taken at 3 hrs. were above the J2 curve. • At Advance 12, early strength test measurements are missing at 1 hr. and 12 hrs. Measurements taken at 30 minutes were below the J2 curve; measurements taken at 4 hrs. and 24 hrs. were above the J2 curve. • At Advance 15, early strength test measurements are missing at 3 hrs. Measurements taken at 1 hr. and 7 hrs. were above the J2 curve. • At Advance 21, early strength test measurements are missing at 3 hrs. Measurements were taken at 1 hr. and 4.5 hrs. and were above the J2 curve. • At Advance 24, early strength test measurements are missing at 3 hrs. Measurements were taken at 1 hr. and 6 hrs. and were above the J2 curve.
| 02SL - Stations (LUL) | Cxxx-NCR-000721 | NCR | L - PTE-W Enl Adv 161 Insufficient thickness around the kwikastrip |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-08-30 | 2014-08-21 09:11 | -9 | 2014-04-14 08:52 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | • On 24/01/14 NS, PTE-W Enlargement Adv 161 (top heading) seems to have been mucked tight around the continuity reinforcement level. Proof drilling have been done following this observation. Proof Drilling show local Insufficient thickness around the kwikastrip (see att 2 proof drilling)
| 02SL - Stations (LUL) | Cxxx-NCR-000722 | NCR | L - CH5-AP5 Enl Adv 46: Insufficient thickness between 10 to 11 o'clock |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-08-15 | 2014-05-06 12:23 | -101 | 2014-04-25 10:23 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Equipment Breakdown | Rework | 4 (0.5-3k) | Complete | Verification Problems - Unavailability or inadequate M&TE | Completed |  | On 07/04/14 DS, CH5-AP5 adv 46 has been sprayed. On NS, proof drilling have been undertaken on left side due to insufficient survey being taken. It was found out that the required shotcrete thickness was less than 100mm in the 10 o clock to 11 o clock position.
| 02SL - Stations (LUL) | Cxxx-NCR-000723 | NCR | L - CP3 Enl Adv 3: Low J2 curve |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-07-18 | 2014-07-03 10:08 | -15 | 2014-06-30 11:03 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | • On 01/05/14, CP3 Primary Lining Enlargement – Advance 3 (P1): early strength tests are lower than J2 Curve until 3 hours. (see att01.)
| 02SL - Stations (LUL) | Cxxx-NCR-000724 | NCR | L - PTE-E and W Enl: Low early strength during the first hour and missing tests |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-07-25 | 2014-06-28 10:19 | -27 | 2014-04-29 10:59 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Issue1 During __ Surveillance carried out the 05/12/13, at LIS on SCL Activities it has been found that: • At PTE-E Enlargement Advance 66, sprayed on 21/11/13, measurements taken before and at 1 hour were below the J2 curve (0.4N/mm2 instead of 0.5 at 1h); measurements taken at 3 hrs. were above the J2 curve. See attached Extract of Surveillance Report No.61 - SCL Activities - Cxxx-__M-O4-RGN-CR092-50093 Rev 1.0 (att01) During Certification Process, it has also been found that during: Issue2 PTE-E Enlargement work in November 2013: • Adv 12, early strength test measurements are missing at 3hr, • Adv 18, early strength test measurements are missing at 1hr, • Adv 48, early strength test measurements are missing at 3hr, • Adv 60, early strength test measurements are missing at 1hr, • Adv 63, early strength test measurements are missing at 1hr, (see att 04) • Adv 51, Flow test not done due to a spillage in the batching plant and a variety of issues with plant, see att 05 notes from daily shift report attached. Issue 3 PTE-W Enlargement work, in October 2013: • Adv 12, early strength interval was missed due to panel broken • Adv 30, early strength test measurement are missing before and at 1hr, • Adv 36, early strength test measurements are missing before 30min and at 12hrs. (see att 06)
| 02SL - Stations (LUL) | Cxxx-NCR-000725 | NCR | W - Shed Door Modifications NE&NW RSA brace connection brackets: welding checked and some failed |  | Contr | __M |  |  | 2016-08-12 | 2016-07-29 13:40 | -14 | 2014-04-17 09:08 | Structural Engineering - Welding | 2500 |  | System Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Shed Door Modifications NE&NW RSA brace connection brackets Welds failed the N__ Test during the inspection made by __ on 03/04/2013, (see attachment 1: __ Report 47512J SR 23 KB) a. NE door West RSA brace connection brackets – W9 b. NE door East RSA brace connection brackets – W9 c. NW door West RSA brace connection brackets – W9 d. NW door East RSA brace connection brackets – W9 Please note that the other failed welds of Sheed Door have been raised as a separate NCR: Cxxx-NCR-000467.
| 02SL - Stations (LUL) | Cxxx-NCR-000726 | NCR | W - CAV WB: Central Drift Excavation: Lack of space preventing progress of plants |  | Contr | __M |  |  | 2014-08-08 | 2014-07-22 10:24 | -17 | 2014-04-17 11:21 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | • During Centre Drift Top excavation, it has been found that the space was too narrow to allow plant/equipment's manoeuvre such as Schaeff ITC 112 and __. (see sketch attached)
| 02SL - Stations (LUL) | Cxxx-NCR-000727 | NCR | Contractor not implemented the requirements of his BS EN ISO 9001:2008 certified quality management system clause 4.2.3 |  | Crossrail | XRL |  |  | 2014-06-25 | 2014-07-04 11:19 | 9 | 2014-04-10 08:13 | Civil - Tunnelling | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | During the surveillance a request was made to review the Contractors documented Materials Approval Procedure. The Snr Materials Engineer was not aware of any procedure being in place. ‘Materials Approval Request Procedure’ updated 13/03/2014 was made available by CRL post surveillance, Cxxx-__M-O4-GPD-CR092-50012 Rev 2 refers. Works Information vol 2B clause 20.4 states “The Contract Quality Plan shall be supported by comprehensive QSPs…...The primary activities addressed by QSPs and to be implemented by the Contractor are to include: verification of Equipment, Plant and Materials”. Although a procedure was in place and accepted by Crossrail, the Snr Materials Engineer who is responsible for raising Materials Compliance Record (MCR) documents as part of the verification of materials for the works was not aware of this procedure. The Contractor had therefore not implemented the requirements of his BS EN ISO 9001:2008 certified quality management system clause 4.2.3 which requires the Contractor to “ensure that relevant versions of applicable documents are available at points of use”.
| 02SL - Stations (LUL) | Cxxx-NCR-000728 | NCR | Failure with self certification as defined in the Works Information volume 2B part 20.9 |  | Crossrail | XRL |  |  | 2014-06-25 | 2014-07-01 15:15 | 6 | 2014-04-10 10:11 | Civil - Tunnelling | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Non Conformance Report Cxxx-NCR-000689 was raised by Crossrail on 14/02/2014 for 5 materials which had been used in the permanent works in January before approved MCR’s were in place. No evidence could be provided to demonstrate that corrective actions had been put in place to ensure non-reoccurrence. Subsequently 2 materials were used in the permanent works in February without an approved MCR in place. This is highlighted on the Contractors minor NCR database and is awaiting __ to raise an additional NCR, which re-confirms that no corrective actions were put in place following NCR 689. Furthermore, the Contractor produces a 5 week look-ahead programme which contains a section for identifying the requirement for material approvals during that 5 week period. On review of the 5 week look-ahead covering the period of January, the 5 materials which relate to NCR 689 were not incorporated on the programme. Works Information vol 2B clause 13.3.8 states “The Contractor shall utilise the template attached in Appendix 13J (MCR) for the purpose of recording material and product acceptances for the works and submit such records to the Project Manager for acceptance.” The Contractor has failed to implement corrective actions as a result of NCR 689 and materials have been incorporated in the works without Project Managers acceptance. NCR was raised to document that there was a failure with Self Certification as defined in the Works Information volume 2B part 20.9, namely “ Defects and Non –conformities not resolved in a timely manner “and “failure to prevent recurring Non conformities”
| 02SL - Stations (LUL) | Cxxx-NCR-000729 | NCR | Contractor not implementing the Materials Proposal Schedule requirements as defined in the Works Information vol 2B clause 20.7 |  | Crossrail | XRL |  |  | 2014-06-25 | 2014-07-15 12:37 | 20 | 2014-04-10 08:26 | Civil - Tunnelling | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | The requirements of the Works Information vol 2B clause 20.7 state “The Contractor shall develop a Materials Proposal Schedule (MPS) listing all proposed permanent works materials and products and indicating any variances from the specified materials ... The MPS shall identify .,target dates (approval, delivery, over dues)”. On review of the Contractors Materials Proposal Schedule (MPS) Rev 11, Cxxx-__M-C-TSC-CR092-50007, it was highlighted that the document was not being used for forward planning all proposed permanent works materials, this was also confirmed by the Contractor verbally during the surveillance. The Contractor however does produce a 5 week look-ahead programme which incorporates a requirement for detailing all materials needing approval during that 5 week period, however this programme is not being completed by the Contractors teams for forward planning of proposed materials with target dates limited to a 5 week look ahead.
| 02SL - Stations (LUL) | Cxxx-NCR-000730 | NCR | Review of the Contractors Materials Prposal Schedule showed that 9 MCR’s were identified as being at a Code 2 status for periods between 3-10 months, therefore not current |  | Crossrail | XRL |  |  | 2014-07-04 | 2014-07-08 13:32 | 4 | 2014-04-10 08:31 | Civil - Tunnelling | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Review of the MPS during the surveillance showed that 9 MCR’s were identified as being at a Code 2 status for periods between 3-10 months. The Contractor confirmed that it is the responsibility of the person, who has issued the MCR to reply within the contractual time frames; however the 9 MCR’s still remain at Code 2 decal status. Under Document management Procedure Rev 2, CRL1-XRL-Z3-GPD-CR001-50001, a Code 2 decal stands for “Not accepted, revise and resubmit work may proceed subject to incorporation of changes indicated”. The 9 MCR’s were therefore not current at the time of the surveillance as the required changes were not incorporated. Works Information vol 2B clause 13.2 details the provision of contemporaneous records. NCR raised to ensure compliance. Cxxx-__M-C-RGN-CR092-50035 Code 2 17/06/2013 Cxxx-__M-C-RGN-CR092-50108 Code 2 20/09/2013 Cxxx-__M-C-RGN-CR092-50072 Code 2 27/03/2013 Cxxx-__M-C-RGN-CR092-50115 Code 2 05/12/2013 Cxxx-__M-C-RGN-CR092-50093 Code 2 07/06/2013 Cxxx-__M-C-RGN-CR092-50116 Code 2 26/09/2013 Cxxx-__M-C-RGN-CR092-50105 Code 2 20/09/2013 Cxxx-__M-C-RGN-CR092-50122 Code 2 20/11/2013 Cxxx-__M-C-RGN-CR092-50107 Code 2 20/09/2013
| 02SL - Stations (LUL) | Cxxx-NCR-000731 | NCR | Non compliance to PMI 00519 Quality Decals and Templates |  | Crossrail | XRL |  |  | 2014-07-04 | 2014-07-15 12:41 | 11 | 2014-04-10 08:35 | Civil - Tunnelling | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | The Construction Products Regulations 2011 came into force in the UK in July 2013 which requires Manufacturers to draw up a Declaration of Performance for all products that are covered by a harmonised European Standard or European Technical Assessment. This is a mandatory requirement and is law under the regulations. To ensure materials being used on CRL conform to these CE Marking requirements, a Project Managers Instruction was sent to all CRL contracts for issue, PMI 00519 was instructed to the Contractor at Cxxx in November 2013. The PMI states: ‘It is the Contractors responsibility to ensure that all documentation is in place to support the new regulations. Any MCR’s which have been submitted to date, including those submitted pre July 2013 still being sourced post July 2013 are not required to be re-submitted at this time, but supporting documentation must be obtained by the Contractor and kept on record and available upon CRL’s request or for auditing purposes’. The Contractor’s Snr Materials Engineer emailed the site team on 29/01/14 and after no reply again on the 11/03/14 to request information on which materials pre July 2013 are still being used in the works to allow internal update to meet the requirements of PMI 00519. The Snr Materials Engineer at the time of the surveillance had yet to receive a response from the site team and as such MCR’s still being sourced past July 2013 have not been updated. The Contractor also confirmed that materials submitted between the period of July 13 and Nov 13 had also not undergone internal update as required. NCR raised against the requirements of PMI 519.
| 02SL - Stations (LUL) | Cxxx-NCR-000732 | NCR | MCR P1 SCL Primary Lining Concrete Mix non compliance to the requirements of PMI 00519 |  | Crossrail | XRL |  |  | 2014-07-04 | 2014-07-04 11:35 | 0 | 2014-04-10 08:39 | Civil - Tunnelling | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | A review of the Contractors MPS was undertaken and MCR Cxxx-__M-C-RGN-CR092-50057 P1 SCL Primary Lining Concrete Mix was reviewed for its content to demonstrate compliance against the requirements of PMI 00519 and CE Marking. The MCR was first submitted to Crossrail for acceptance in July 2012 and has to date been used as the sole mix design for all SCL Primary Lining works. The PMI states: “In accordance with Works Information vol 2B part 13 the Contractor is required to complete a Materials Compliance Records for the purpose of recording material and product acceptances. The existing Materials Compliance Record – Appendix 13J has been revised to accommodate the aforementioned supplier decal and also the necessary Declaration of Performance and requirements for CE marking to comply with the Construction product Regulation effective July 2013.” On review of the documentation the Contractor was using the updated Materials Compliance Record, CRL1-XRL-C-ZTM-CR001-50002 Rev 4, however could not provide all the required Declaration of Performance’s for the aggregates, additives, cement and steel fibres, or referenced traceability to the Declaration of Performances as required by the respective PMI to demonstrate compliance to the Construction Products Regulations 2011.
| 02SL - Stations (LUL) | Cxxx-NCR-000733 | NCR | Contractor failed to implement the requirements of their BS EN ISO 9001:2008 certified quality management system clause 7.4.3 |  | Crossrail | XRL |  |  | 2014-10-03 | 2014-08-30 16:23 | -34 | 2014-04-10 08:43 | Civil - Tunnelling | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During the surveillance the Contractor was asked whether they carry out intermittent reviews of the materials CE Marking Declaration of Performance for its content and relevance before submitting to CRL for approval. The contractor confirmed they do not carry out intermittent review of the Declaration of Performance’s content to the construction products Regulations 2011 and associated harmonised European Standards. The Contractor has therefore not implemented the requirements of his BS EN ISO 9001:2008 certified quality management system clause 7.4.3 which states “The organization shall establish and implement the inspection or other activities necessary for ensuring that purchased product meets specified purchase requirements.”
| 02SL - Stations (LUL) | Cxxx-NCR-000734 | NCR | Materials Proposal Schedule not current and being updated to represent MCR decal statuses |  | Crossrail | XRL |  |  | 2014-07-04 | 2014-07-04 12:54 | 0 | 2014-04-10 08:48 | Civil - Tunnelling | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | A review of the Contractors MPS Rev 11 was undertaken and 3 MCR’s were identified as being at a Code 3 decal as highlighted below: Cxxx-__M-C-RGN-CR092-50012 Non Shrink grout Code 3 Submitted 13/12/2012 Cxxx-__M-C-RGN-CR092-50071 DYWIDAG Drill hollow Bar System Code 3 Submitted 03/12/2012 Cxxx-__M-C-RGN-CR092-50106 __ __ VT1 Re-injectable Tube Code 3 Submitted 04/09/2013 On post surveillance review of the documentation it was confirmed that Cxxx-__M-C-RGN-CR092-50071 DYWIDAG Drill hollow Bar System and Cxxx-__M-C-RGN-CR092-50106 __ __ VT1 Re-injectable Tube were actually at a Code 1 decal. Works Information vol 2B clause 13 states “The Contractor shall regularly submit the Material Proposal Schedule and a matrix of approvers for all materials and products, commencing within 6 weeks of the starting date”. The Contractors MPS undergoes periodic updates however the information contained within the document does not represent the acceptance status of the two MCR’s. NCR raised to ensure the Contractor implements appropriate corrective action to maintain contemporaneous records as required by Works Information volume 2B clause 13.2.
| 02SL - Stations (LUL) | Cxxx-NCR-000735 | NCR | Contractor could not provide records to demonstrate that a Code 3 decal MCR had not been used in the works |  | Crossrail | XRL |  |  | 2014-07-04 | 2014-06-26 15:56 | -8 | 2014-04-10 08:51 | Civil - Tunnelling | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Cxxx-__M-C-RGN-CR092-50012 Non Shrink grout was confirmed by the Contractor as still being at a Code 3 decal. Under Document management Procedure Rev 2, CRL1-XRL-Z3-GPD-CR001-50001, a Code 3 decal stands for “Not Accepted. Revise and resubmit. Work may not proceed”. The Contractor could not confirm post surveillance whether the material had or had not been used in the permanent works, due to the poor quality/ traceability of records and the lack of Method Statements and Inspection Test Plans for the works this MCR is related to. NCR was raised as the Contractor could not demonstrate that the Code 3 Non Shrink Grout had not been used in the works.
| 02SL - Stations (LUL) | Cxxx-NCR-000737 | NCR | W - ES1 Permeation: Not enough cubes tested and one set did not conform the ITP Compressive Strength Value |  | Contr | __M |  |  | 2014-08-29 | 2014-08-13 17:44 | -16 | 2014-04-16 14:54 | Structural Engineering - Grouting | 2000 |  | Material | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | During ground treatment at ES1, cubes of mix P were taken but only 3 sets out of 96 were tested . One set did not conform to ITP specified value. Three sets of cubes were tested for the duration of the permeation grouting works. Six cubes were sampled per day, however no results are available. Cube Cxxx3 was out of tolerance, with an average compressive strength of 0.1N/mm2 at 28 days. No other cube results are available.
| 02SL - Stations (LUL) | Cxxx-NCR-000738 | NCR | L - PTW-E Enl Adv 138 Inv: Cores CR1523 show insufficient thickness |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-09-12 | 2014-08-18 13:02 | -25 | 2014-04-30 17:14 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | PTW-E Enl Adv 138, Invert has been sprayed on 04/04/14 and cored on 10/04/14 NS. The cores CR1523 were reviewed by __ and Cxxx and it has been found that: - Four cores were taken and all four cores have lesser than 400mm required length – shortest is 340mm and longest is 370mm. - Core holes have been checked and it looks all cores have hit the clay. See Cores Reports attached (att 1)
| 02SL - Stations (LUL) | Cxxx-NCR-000739 | NCR | L - AP5-CH5 Enl Adv 40 LS and 46 RS: Non conforming Cores CR1538 and CR1539 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-08-08 | 2014-07-28 13:17 | -11 | 2014-04-28 15:29 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | AP5-CH5 Enl Adv 40LS & 46RS have been sprayed on 06/04/14 and 09/04/14 and cored on 13/04/14. The cores CR1538 and CR1539 were reviewed by __ and Cxxx and the followings imperfections were found: • CR1538: Broken, Major Laminations, Major Voids (> 3 and 5 mm). Mean ACI: 2.6 • CR1539: Lamination, Major Voids (>10mm) and Honeycombing. Mean ACI: 3 During the SRG meeting on the 15/04/14 it has been agreed that a NCR should be raised. See Cores Reports attached (att 1 and 2)
| 02SL - Stations (LUL) | Cxxx-NCR-000740 | NCR | L - LCE/VD4 Thickening Top Right: Non conforming Cores CR1527 - bad encapsulation of rebar |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-06-01 | 2014-11-20 12:28 | -193 | 2014-04-29 16:05 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | VD4 from LCE Thickening has been cored the 11/04/14. The core CR1527 was reviewed by __ and Cxxx and major voids behind rebars have been found. ACI grade: 3. During the SRG meeting on the 15/04/14 it has been agreed that a NCR should be raised. See Cores Reports attached (att 1)
| 02SL - Stations (LUL) | Cxxx-NCR-000741 | NCR | L - LCE/VD5 Thickening Top Right: Non conforming Cores CR1528 - bad encapsulation of rebar |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-02-01 | 2014-11-24 11:39 | -69 | 2014-04-29 17:01 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | LCE Thickening for VD5 break out has been cored the 11/04/14. The core CR1528 was reviewed and the followings imperfections were found: • Major voids >10mm around rebar • Poor encapsulation around rebar • Core broken • Average ACI grade: 2.6 During the SRG meeting on the 15/04/14 it has been agreed that a NCR should be raised. See Core Report attached (att 1)
| 02SL - Stations (LUL) | Cxxx-NCR-000742 | NCR | L - LCE/AP6 Thickening Top Right: Non conforming Cores CR1530 - bad encapsulation of rebar |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-02-28 | 2015-02-18 13:53 | -10 | 2014-04-29 16:46 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | LCE/AP6 thickening Top Right has been cored on 12/04/14 DS. The core CR1530 was reviewed and the followings imperfections were found: • Major voids behind reinforcement • Poor encapsulation around rebar • ACI grade: 3 See Core Report attached (att 1)
| 02SL - Stations (LUL) | Cxxx-NCR-000743 | NCR | L - RCE Block 4: Regulating layer contaminated with fibres in crown |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-02-01 | 2014-11-26 12:41 | -67 | 2014-07-31 11:26 | Geotechnical Engineering - Compensation Grouting | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | - On 16/07/14 NS : During spray of the Regulating Layer in the crown of RCE Block 4,the mix has been slightly contaminated with fibres. Refer to the Placement shotcrete Checksheet attached for more detail of the spray (Att01.)
| 02SL - Stations (LUL) | Cxxx-NCR-000744 | NCR | L - PTW-W/CP3 Thickening Right Shoulder: Non-conforming Cores CR1548 - bad encapsulation of rebar |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-09-05 | 2014-09-01 12:49 | -4 | 2014-04-29 09:12 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | PTW-W/CP3 thickening Right Shoulder has been cored on 16/04/14 NS. The core CR1548 was reviewed and the followings imperfections were found: • Major voids >10mm around rebar • Poor encapsulation around rebar • Average ACI grade: 3 See Core Report attached (att 1)
| 02SL - Stations (LUL) | Cxxx-NCR-000745 | NCR | L - CP8 Enl Adv 6 Inv: CR1565: Insufficient Lining Thickness |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-09-12 | 2014-07-28 13:18 | -46 | 2014-04-30 17:27 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | CP8 Enl Adv 6, Invert has been sprayed on 17/04/14 and cored on 26/04/14 NS. The cores CR1565 were reviewed by __ and Cxxx and it has been found that: 1 core out of 5 (core number 5) has lesser than 250mm required length (50 mm shy). See Cores Reports attached (att 1)
| 02SL - Stations (LUL) | Cxxx-NCR-000746 | NCR | L - LCE thickening: Defects in the invert |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-09-05 | 2014-05-16 12:23 | -112 | 2014-05-07 17:07 | Tunnelling - Linings - Sprayed Concrete | 10000 |  | Workmanship | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • On 27/04/14 NS, CRL Inspectores carried out hammer test on LCE Invert Thickening and raised issue regarding shotcrete integrity. After discussion, 3 No. 77mm diameter cores were taken in the invert of LCE thickening ( zone with 2nd bulking layer done) Cores were inspected and show good quality of shotcrete spray – Refer to the Attachment 1 • On 28/04/14 DS, between 10am and 11am, 3 additional No. 77mm diameter cores were taken in the zone with 1st layer bulking done Cores have been inspected and imperfections have been found ( broken cores, laminations, major voids, rebound encapsulation…) – Refer to the Attachment 2 • Location and photos of the cores ( Attachment 3) and 27 & 28th April Shift reports ( Attachment 4) have been attached for a better understanding
| 02SL - Stations (LUL) | Cxxx-NCR-000747 | NCR | L - AP5 Enl Adv 54: Over-excavation in length (2m) in the invert |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-08-29 | 2014-06-28 10:22 | -62 | 2014-04-30 14:43 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | On 10/04/2014 DS, it has been found that AP5 Enl Advance 54 was 2m in length excavated in the invert. After investigation it seems that the previous advance was left shy. The rest of the advance - the top heading area - was fine. Refer to the excavation photo attached for evidence
| 02SL - Stations (LUL) | Cxxx-NCR-000748 | NCR | L - CH5-AP5 Adv 33: Invert left short |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-09-12 | 2014-07-25 15:41 | -49 | 2014-05-12 08:42 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | On 03/04/2014 NS , the advance CH5-AP5 Enl Adv 33 excavation has been done and was left short. It does not meet the top heading of advance 32 for full ring closure, therefore not in compliance with the RESS. Refer to the photos attached for a better understanding ( Attachment 1 and Attachment 2 )
| 02SL - Stations (LUL) | Cxxx-NCR-000749 | NCR | L - RCE/VD2 Thickening Hammer test failed ( voids ) |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-08-22 | 2014-05-16 12:09 | -98 | 2014-05-07 17:28 | Tunnelling - Linings - Sprayed Concrete | 6000 |  | Workmanship | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • On 29/04/14 DS during hammer tests, void have been found in the FF2 layer of REC Thickening around VD2.
| 02SL - Stations (LUL) | Cxxx-NCR-000750 | NCR | L - AP7-W CH1-2/CP4 Thickening Left Top: Non conforming Cores CR1596 - bad encapsulation of rebar, voids |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-08-29 | 2014-07-28 13:22 | -32 | 2014-05-06 16:08 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | AP7-W CH1-2 Thickening, Left Top, for CP4 break out has been sprayed between August and October 2013 and cored the 03/05/14. The cores CR1596 were reviewed and the followings imperfections were found on 1 core: • Honeycombing • Major voids >5mm • Poor encapsulation • Core broken • ACI grade: 3 During the SRG meeting on the 06/05/14 it has been agreed that a NCR should be raised. See Core Report attached (att 1)
| 02SL - Stations (LUL) | Cxxx-NCR-000751 | NCR | L - AP7-E/CP7 Thickening Right Top: Non conforming Cores CR1599 - voids, shadowing |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-10-30 | 2015-06-19 14:18 | -133 | 2014-05-06 14:57 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | AP7-E CH2 Thickening, Right Top, for CP7 break out has been sprayed in November 2013 and cored the 03/05/14 . The core CR1599 was reviewed and the followings imperfections were found: • Major voids >10mm • Shadowing • ACI grade: 3 See Core Report attached (att01)
| 02SL - Stations (LUL) | Cxxx-NCR-000752 | NCR | W - EPW1-W Adv 26: Left hand side sprayed under minimum thickness |  | Contr | __M |  |  | 2014-08-29 | 2014-09-09 11:59 | 11 | 2014-05-30 17:59 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • In EPW1-W Advance 26 LHS Axis level, sprayed on 11/04/14 DS, it appeared that 4 cores (CR1571) were too short (260, 260, 280, 290, requirement 300). • Proof drilling was carried out and showed an area of 1500 * 700 was thinner than required. • These results suggest that the primary lining of Adv 26 was sprayed under thickness in an area on the left hand side at axis level of no greater than 1m². See attachments.
| 02SL - Stations (LUL) | Cxxx-NCR-000753 | NCR | W and L - LIS and WHI: No photographs of Face Excavations |  | Contr | __M |  |  | 2014-09-05 | 2014-06-04 16:03 | -93 | 2014-05-22 13:39 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | • Not all advances have had a photograph taken of the face excavation for submission to Crossrail within the factual geological reports. • List of missing photographs of attached. (see att01)
| 02SL - Stations (LUL) | Cxxx-NCR-000754 | NCR | W - PTE and PTW Enl: Early strength tests performed incorrectly |  | Contr | __M |  |  | 2014-09-12 | 2014-06-20 16:07 | -84 | 2014-05-22 10:16 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | • PTE-E Thickening at VA2 (Second layer primary thickening (crown), P1, 14.07.2013) – all early strength test measurements before 4.5 hours are missing. Measurements taken at 4.5 hours and later were above the J2 curve. • PTE-E Thickening at VA2 (Third layer primary thickening (crown), P1, 15.07.2013) – early strength tests are missing at 1 hr and 3 hrs. Measurements taken at 15 minutes were below the J2 curve; measurements taken at 4 hrs were above the J2 curve. • PTE-E Thickening at CP3-N (Second layer primary thickening (crown), P1, 21.07.2013) – early strength testing at 6 hrs delayed and performed at 8 hrs. Measurements taken at 1, 3, 8 and 12 hrs were above the J2 curve. • PTE-W Thickening at CP1-a-N (Third layer primary thickening (crown), P1, 03.08.2013) – all early strength test measurements before 3 hrs are missing. Measurements taken at 3 hours and later were above the J2 curve. • PTE-W Thickening at CP1-a-N (Second layer primary thickening (invert), P1, 10.08.2013) – early strength measurement at 3 hrs is missing. Measurements taken at 60 minutes and 6 hours were above the J2 curve. • PTE-W Thickening at CP1-a-N (Third layer primary thickening (invert), P1, 11.08.2013) – early strength measurement at 1 hour is below the J2 curve and is missing at 3 hours. Measurements taken at 6 hours and later were above the J2 curve. • PTW-E Enlargement, Advance 97 – early strength measurement at 12 hours is missing. Measurements taken at 1, 3, 6 and 24 hours were above the J2 curve. • PTW-E Enlargement, Advance 103 – early strength measurements at 1 and 3 hours are missing. Measurements taken at 5.5 hours and later were above the J2 curve. • PTW-W Enlargement, Advance 12 – an early strength measurement should have been done at this advance, as it was previously performed at advance 9. This was not done, but an early strength test was done at advance 13. • PTW-W Enlargement, Advance 13 – early strength measurement at 3 hours is missing. Measurements taken at 1 hour and 6 hours are above the J2 curve. • PTW-W Enlargement, Advance 18 – early strength measurement at 3 hours is missing. Measurements taken at 1 hour and 6 hour are above the J2 curve.
| 02SL - Stations (LUL) | Cxxx-NCR-000756 | NCR | L - CP4 Pilot Adv 6 LK: Non-conforming Cores - CR1632 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-08-29 | 2014-07-21 13:06 | -39 | 2014-05-20 09:31 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | CP4 Pilot Adv 6 LK has been sprayed on 08/05/14 and cored on 11/05/14. The cores CR1632 was reviewed by __ and Cxxx and the followings imperfections were found: • Major Laminations (cores 1 and 3 broken) • Major Voids (> 5 mm). • Mean ACI: 2.6 During the SRG meeting on the 13/05/14 it has been agreed that a NCR should be raised. See Cores Report attached (att 1)
| 02SL - Stations (LUL) | Cxxx-NCR-000757 | NCR | L - CP7 Pilot Adv 13 Inv: Insufficient Lining Thickness - CR1624 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-08-22 | 2014-07-17 11:10 | -36 | 2014-05-20 10:03 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | CP7 Pilot Adv 13 Invert has been sprayed on 09/05/14 and cored on 10/05/14. The cores CR1624 were reviewed by __ and Cxxx and it has been found that: 1 core out of 5 (core number 5) has lesser than 250mm required length (200 instead of 250mm). See Cores Reports attached (att 1)
| 02SL - Stations (LUL) | Cxxx-NCR-000758 | NCR | L - RCE/VD2 Thickening : spraying of FF2 without CRL notification for inspection |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-07-25 | 2014-07-08 12:38 | -17 | 2014-05-16 10:48 | Tunnelling - Linings - In-situ Concrete | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | • On 10/05/14 DS, FF2 layer on RHS below axis in VD2 Thickening has been sprayed without been inspected by CRL (Hold Point). Refer to the VD2 FF2 Placement checksheet attached
| 02SL - Stations (LUL) | Cxxx-NCR-000759 | NCR | L - RCE/VD2 Thickening: Non-conforming cores CR1641 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-08-22 | 2014-07-16 09:09 | -37 | 2014-05-16 14:07 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | RCE Thickening, Left Bottom, for VD2 break out has been sprayed between April and May 2014 and cored the NS 14/05/14. The core CR1641 was reviewed and the followings imperfections were found: • Laminations • Core broken twice • ACI grade: 3 It has been agreed with __ Designer Coordinator that NCR should be raised. See Core Report attached (att01) and __ Design CoordinatorEmail (att02)
| 02SL - Stations (LUL) | Cxxx-NCR-000760 | NCR | L - VD5 Enl: Breaking and Excavation not in accordance to process outlined in RESS |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-09-05 | 2014-07-25 16:05 | -42 | 2014-05-20 11:09 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | On 16/05/14 DS and NS, Breaking A1+A2 and A3 in one go without spraying 75 mm initial lining on exposed faces. Refer to the shift report attached ( Att02.) for the exact sequence of works.
| 02SL - Stations (LUL) | Cxxx-NCR-000761 | NCR | L - VD5 Enl: 1 rebar damaged at crown and invert level |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-08-29 | 2014-09-04 08:24 | 6 | 2014-05-20 16:28 | Tunnelling - Linings - Sprayed Concrete | 2000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Thickening works have done from March to May 2014, • On 16/05/14 NS, during excavation of Adv A3, one NF2 rebar in the crown was exposed ( 20mm diameter and 750 mm length ) • On 18/05/14 DS, during excavation of Adv 6, one NF2 rebar in the invert was exposed Refer to the shifts reports ( att01 and att02 ) for the exact times of excavation and the photos of the rebars exposed ( att03 and att04)
| 02SL - Stations (LUL) | Cxxx-NCR-000762 | NCR | W - PTE-E Ch 70: Sprayed waterproofing membrane incorrect repair |  | Contr | __M |  |  | 2014-10-31 | 2014-09-26 16:58 | -35 | 2014-05-20 17:20 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | • During repair work on a damp area on the regulating layer in PTE East (CH 70, left side) above the invert wing the incorrect repair material was used. •The area of visible surface moisture was repaired with non-shrink grout to act as a seal as there was no __ Top Seal 107 available at the time. The area has since been sprayed over with Masterseal due to increased waterproofing layer thickness requirements. • This material repair does not conform to WMS Cxxx-__M-C4-GMS-50020.
| 02SL - Stations (LUL) | Cxxx-NCR-000763 | NCR | L - CP4a Enl Adv 5 Invert: 1 rebar damage during excavation |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-05-29 | 2015-04-14 10:30 | -45 | 2014-05-22 11:16 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | • Thickening works have been done from Aug to Dec 2013, • On 14/05/14 DS, during excavation of Adv 5, thickening bar underneath CP4a Invert Profile was exposed and damaged. Refer to the shifts reports (att01) for the exact times of excavation and the photos of the rebar exposed (att02).
| 02SL - Stations (LUL) | Cxxx-NCR-000764 | NCR | L - VD2 Adv 3 and 3a: mucked tight on the left and right |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-09-19 | 2014-06-20 11:20 | -91 | 2014-05-21 12:04 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | • On 17/05/14 DS, VD2 Adv 3 and 3a have been mucked tight on both sides. • The Advance 3 on the LHS and RHS has been under excavated, then spayed and kwikastrip installed in the wrong position See Beamer Profile as evidences (att01) and Photo attached of the kwikastrip in the wrong position (att02)
| 02SL - Stations (LUL) | Cxxx-NCR-000765 | NCR | L - CP7 Enl: Bar hit on breakout of CP7 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-06-01 | 2015-04-29 11:11 | -33 | 2014-05-22 12:01 | Tunnelling - Linings - Sprayed Concrete | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | • Thickening works have done from Nov to Dec 2013, • On 10/05/14 end of NS, during breakout of CP7 Enlargement, a near face 2bar in the crown was hit and damaged with the road-header. Refer to the shifts reports ( att01) for the exact times of breakout and the photos of the rebar exposed ( att02 )
| 02SL - Stations (LUL) | Cxxx-NCR-000766 | NCR | L - VD5 Pilot: Unable to obtain cores |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-09-26 | 2014-06-05 09:40 | -113 | 2014-05-23 15:40 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | VD5 Pilot has been built between the 10th and 15th of May. VD5 Enlargement stared on the 16th of May. During this period, lab Techniciens have been unable to obtain cores from VD5 pilot on time.
| 02SL - Stations (LUL) | Cxxx-NCR-000767 | NCR | L - RCW/VD1 Thickening: U bar damaged |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-08-29 | 2014-07-08 12:35 | -52 | 2014-05-23 15:15 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • On 21/05/14 NS, U bar in VD1 (Bar mark BM4x) has been exposed and broken. The upper leg is intact (see Pictures attached). • This happened during joint preparation when cleaning the SCL surface for the invert application of the thickening. • The cover was between 10mm and 30mm. The rock wheel was used to remove all the snots and loose SCL.
| 02SL - Stations (LUL) | Cxxx-NCR-000768 | NCR | W - MON1: Missing concrete pre-pour checksheets and concrete testing result certificates for cast concrete bases and chambers |  | Contr | __M |  |  | 2014-07-11 | 2014-07-08 12:48 | -3 | 2014-05-29 14:04 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | In February 2013, • Pre-pour checksheets for cast concrete bases (ITP item 3.1) are missing. • Pre-pour checksheets for concrete chambers (ITP item 3.3) are missing. • Test certificates for concrete cubes (ITP item 3.6) are missing.
| 02SL - Stations (LUL) | Cxxx-NCR-000769 | NCR | L - RCW/VD1 Thickening: Non-conforming Cores CR1665 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-09-19 | 2014-07-23 08:20 | -58 | 2014-05-28 09:51 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | RCW Thickening for VD1 Breakout has been sprayed in May 2014 and cored the NS 26/05/14. The core CR1665 was reviewed and the followings imperfections were found: • Planes of separation between layers in build up of lining • Laminations • Voids • Core broken • Encapsulation of rebar appears satisfactory except of one bar which is entirely loose. Cores have been presented during SRG meeting on the 27/05/14 and it has been agreed that the core should be sent to __ Design Coordinator for review. It has been decided that NCR should be raised. See Core Report attached (core number 1 of att01) and __ Design Coordinator Email (att02)
| 02SL - Stations (LUL) | Cxxx-NCR-000770 | NCR | W - PTW-E LHS Ch.8.5 and 30, RHS Ch.18 and 43.5: Installation of Monitoring bolts deeper than 60mm |  | Contr | __M |  |  | 2014-09-05 | 2014-09-05 14:19 | 0 | 2014-06-03 14:43 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | On 01/06/14, in PTW-E chainages: LHS 8.5 & 30, RHS 18 & 43.5, Monitoring Bolts have been installed deeper than 60mm without permit in the first Layer of the sprayed Final lining. See photo att1.
| 02SL - Stations (LUL) | Cxxx-NCR-000771 | NCR | W - CAV WB: Voids in final layer of the crown |  | Contr | __M |  |  | 2015-10-31 | 2014-12-04 11:34 | -331 | 2014-06-02 15:25 | Tunnelling - Linings - Sprayed Concrete | 15000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • During inspection of the crown of WB cavern before regulating it was discovered that there are some voids within the lining between the final layer and primary layer. • During hammer testing of the cavern in order to obtain the permit to cover for regulating layer several areas were identified as potentially hollow. Further drilling investigations confirmed 4no areas have voids between the primary lining installed during the sidewall and crown drifts and the final layer that was installed during with the B12 reinforcement. (WB Cavern approx. ch. +200m and +250m) • The void is not around the reinforcement but appears to be between the layers which indicate a “slump” away from the primary lining that did not fall as was held in place by the reinforcement. See attached: - a presentation that compiles all proof drilling records of the hollow areas. “Hollow area CAV-W Summary. (Att01.) - a Beamer Profile with proofdrill up to Headwall (Att02.) - Initial Cores CR1643, CR1644, CR1645 (Att06A, 06B, 06C).
| 02SL - Stations (LUL) | Cxxx-NCR-000772 | NCR | L - AP1: underthickness lining found in the crown when proof drilling after Scabbling |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-08-22 | 2014-07-30 09:55 | -23 | 2014-06-03 16:48 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | • On 31/05/14 DS, area of AP1 was scabbled back with the rock wheel before installation of FF1. • The area was proof drilled before scabbling started (see att02) and then again after (see att01 and att03). This uncovered an area of under thickness 400mm total lining (500mm required thickness) in the crown. • The extent of the area is approximately 2.2m x 1m. Please refer to proof drilling indicating that the area of the proof drilling in over 100mm tight on excavation.
| 02SL - Stations (LUL) | Cxxx-NCR-000773 | NCR | W - PTW-E Block 1: Radial Joint repaired without approved documentation and Poor joint on top of side walls |  | Contr | __M |  |  | 2016-02-19 | 2016-01-22 14:24 | -28 | 2014-06-03 16:27 | Tunnelling - Linings - Sprayed Concrete | 4000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • The radial joint at the top of the sidewall have been poorly formed and is unacceptable to use. In order to be able to use these joints they must be repaired. The radial joint on the sidewalls for PTW-E Blocks 1 has been repaired without an approved repair procedure and using unapproved material for that location (__dur 41-CF which do not meet the fire requirements). The method used to help achieve the radial joint was: • Block 1 - cast horizontally and the top of the sidewall joint was formed by building up the concrete. • By trying solving the problem different problem was caused: Block 1 - Material formed incompetent joints.
| 02SL - Stations (LUL) | Cxxx-NCR-000774 | NCR | W - PTW/EPTW: Missing Early Strength Tests |  | Contr | __M |  |  | 2014-09-26 | 2014-07-01 14:28 | -87 | 2014-06-11 14:25 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During works in PTW-W and EPTW Enlagement, in July 2013, few early strenght have been missed (see attachments 01 to 16): • PTW-W Enlargement, Advance 235 – early strength test is missing at 12 hrs. Measurements taken prior to and after 12 hrs are above the J2 curve. • PTW-W Enlargement, Advance 238 – early strength tests should be performed at every 3rd advance and thus should have been performed at this advance. Instead, the early strength tests were performed at advance 239, which resulted in a larger than permitted gap in early strength testing. Measurements after Advance 239 were taken every third advance. • PTW-W Enlargement, Advance 244 – early strength test is missing at 12 hrs. Measurements taken prior to and after 12 hrs are above the J2 curve. • PTW-W Enlargement, Advance 247 – early strength test is missing at 3 hrs. Measurements taken prior to and after 3 hrs are above the J2 curve. • PTW-W Enlargement, Advance 253 – early strength test is missing measurements taken before 3 hrs. Measurements taken at 3 hrs and after are above the J2 curve. • PTW-W Enlargement, Advance 259 – early strength tests are missing at 3 and 6 hrs. Measurements taken before 3 hrs and after 6 hrs are above the J2 curve. • PTW-W Enlargement, Advance 262 – early strength test is missing at 3 hrs. Measurements taken before and after 3 hrs are above the J2 curve. • EPTW Enlargement, Advances 1-5 – early strength tests should be performed every 3rd advance, and thus should have been performed at Advance 2 or Advance 3. Instead, the first early strength test was performed at Advance 5, which resulted in a larger than permitted gap in early strength testing. Measurements taken after Advance 5 were taken at at least every 3rd advance. • EPTW Enlargement, Advance 6 – early strength test is missing at 12 hrs. Measurements taken before and after 12 hrs are above the J2 curve. • EPTW Enlargement, Advance 12 – early strength test is missing at 3 hrs. Measurements taken before and after 3 hrs are above the J2 curve. • EPTW Enlargement, Advance 30 – early strength test is low at 1 hr and missing at 12 hrs. All strength tests after 1 hr exceed the J2 curve. • EPTW Enlargement, Advance 36 – early strength test is missing at 6 hrs. Measurements taken before and after 6 hrs are above the J2 curve. • EPTW Enlargement, Advance 39 – early strength tests are missing prior to 3 hrs. All strength tests taken at and after 3 hrs exceed the J2 curve. • EPTW Enlargement, Advance 42 – early strength test is missing at 1 hr. All strength tests taken after 1 hr are above the J2 curve. • EPTW Enlargement, Advance 67 – early strength test is missing at 1 hr. All strength tests taken after 1 hr are above the J2 curve. • EPTW Enlargement, Codsmouth Invert 2 – early strength tests are missing at 1 hr, 3 hrs and 12 hrs. Strength tests taken at 6 hrs and 24 hrs are above the J2 curve. • PTW-E Thickening at CP3 South – early strength test missing at 12 hrs. Early strength tests taken at 8 hrs exceed the strength needed for 12 hrs, and 24 hrs is also above the J2 curve. • PTW-E Thickening at VA4 (2nd layer primary thickening, 12.07.13, P1 mix) – early strength test missing at 12 hrs. Tests taken at 15 and 24 hrs exceed the J2 curve. • PTW-E Thickening at VA4 (2nd layer primary thickening, 16.07.13, P1 mix)– early strength test missing at 12 hrs. Tests taken at 3 hrs and 24 hrs exceed the J2 curve.
| 02SL - Stations (LUL) | Cxxx-NCR-000775 | NCR | W - PTW-E and PTE-E: Waterproofing details between the invert and the sidewalls not included in the installation of the secondary lining |  | Contr | __M |  |  | 2016-10-28 | 2016-11-17 09:19 | 20 | 2014-06-16 15:52 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | • There was no waterproofing detail or water barrier between the tunnels invert and sidewalls (both sides) for blocks PTW 9 – 1 and PTE 9 – 3 as suggested on the drawings and in the specifications.
| 02SL - Stations (LUL) | Cxxx-NCR-000776 | NCR | W - CP2-N: 13mm Crack |  | Contr | __M |  |  | 2014-11-17 | 2014-11-07 14:45 | -10 | 2014-07-11 17:42 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Material | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | • A 13mm crack is present within CP2-N at advance 13 in the enlargement, due to the size of the crack this is considered excessive.
| 02SL - Stations (LUL) | Cxxx-NCR-000777 | NCR | W - CP3-S: Rebars exposed due to trimming back of Secondary Lining profile |  | Contr | __M |  |  | 2016-07-22 | 2016-01-26 13:23 | -178 | 2014-06-17 08:41 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | • Looking South to North the left hand side was sprayed to the correct profile, however the right hand side was significantly over-sprayed. • Re-profiling was immediately requested, first of all attempted with handheld jiggers then with the 8T road-header. • During re-profiling works some of the profile bars in the area were damaged and/or removed, and some of the structural reinforcement in the area was exposed, bent out of position, but not damaged.
| 02SL - Stations (LUL) | Cxxx-NCR-000778 | NCR | L - PTE-E /CP10 Thickening: FF1 reinforcement damage |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-07-25 | 2014-07-16 09:18 | -9 | 2014-06-13 13:53 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Thickening works have been done from May to June 2014: • On 10/06/14 NS, during scabbling, two FF1 bars in the invert were exposed Refer to the photos of the bars exposed ( att01) for evidences
| 02SL - Stations (LUL) | Cxxx-NCR-000779 | NCR | L - VD1: Clay hit while scabbling |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-07-31 | 2014-07-17 08:29 | -14 | 2014-06-18 15:33 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | • On 17/06/14 DS, scablling to enable steel installation was on-going but unfortunately clay was discovered Refer to the photos attached (att01) for evidence • After investigation it seems that the joint in advance 26 was under excavated – some points were at -0.011 instead of +0.100
| 02SL - Stations (LUL) | Cxxx-NCR-000780 | NCR | W - PTE-E Ch.76 LS: Spray Waterproof Membrane failed to cure due to water ingress |  | Contr | __M |  |  | 2014-11-28 | 2014-11-24 16:39 | -4 | 2014-08-21 15:50 | Tunnelling - Linings - Sprayed Concrete | 2000 |  | System Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In PTE East (CH 76, left side) above the invert wing the Spray Applied Waterproof Membrane has failed to cure due to water ingress coming through the substrate. The __ Masterseal 345 did not cure as the waterproof membrane was still wet and soft due to the water ingress from the substrate. Therefore the integrity of the waterproofing is impaired and fails to meet the specification.
| 02SL - Stations (LUL) | Cxxx-NCR-000781 | NCR | L - NLL: Length of fabricated reinforcement bars with couplers |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-08-29 | 2014-08-27 11:30 | -2 | 2014-06-12 13:54 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Northern Line Link - Opening Set in Cross Passage 4/203, Construction of R.C. underpinning bays: BMK 14 (section 2A and 2B) is too short, which is then resulting in BMK 15 in section 3 (LHS and RHS) coming up short by 35mm i.e. greater than 50mm cover to the end of the 32mm diameter longditudinal main reinforcing bars.(att02 and 3)
| 02SL - Stations (LUL) | Cxxx-NCR-000782 | NCR | W - Manual Monitoring of LO assets |  | Contr | __M |  |  | 2015-07-30 | 2015-03-19 15:26 | -133 | 2014-09-09 09:57 | Tunnelling - Linings - Sprayed Concrete | 500 |  | System Defect | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | On May 2014, manual monitoring has not been carried out due to the black listing of the COSS required to provide protection for the survey teams. Track access is not permitted unless protected by a COSS. In order to work on the LO tacks the COSS must be in possession of a valid ELL Induction. The supplier who provides the COSS did not have any available COSS with this induction and as a consequence track access was denied until one of their COSS was inducted.
| 02SL - Stations (LUL) | Cxxx-NCR-000783 | NCR | L - VD1 Enl Adv 37: Missing Early Strength testing of 1hr |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-07-18 | 2014-07-10 15:42 | -8 | 2014-06-26 09:58 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate resources | Completed |  | • During __ Surveillance carried out on 12/06/14, it has been found that the Early Strength Test of 1h has been missed in VD1 Enlargement Advance 37 and that 3h, 6h, 12h tests have been delayed of 1h – please refer to Surveillance Report Cxxx – __M –O4 – RGN –CR092 – 50103 REV 1.0, item 14, photo 23. (att01.)
| 02SL - Stations (LUL) | Cxxx-NCR-000784 | NCR | L & W - No photographs of Face Excavations during May 2014 |  | Contr | __M |  |  | 2014-07-10 | 2014-07-01 14:33 | -9 | 2014-06-16 16:13 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During May and June 2014, on both site: • 10 advances have not had a photograph taken of the face excavation for submission to Crossrail within the factual geological reports. The 10 advances are: • LIV CP3 Enlargement ADV 14/15 • LIV VD2 Enlargement ADV1 • LIV VD5 Enlargement ADV 15 Top Heading • WHI Crossover Advances 14 • WHI Crossover Advances 16 • WHI Crossover Advances 17 • WHI CAV CD Bench Invert ADV 28 • WHI EBRT – W Enlargement 159 Invert, • WHI EBRT – W Enlargement 176 • WHI EBRT – W Enlargement 184 • As the face is then sprayed, no other opportunity to take a photograph is possible. • List of advances is attached
| 02SL - Stations (LUL) | Cxxx-NCR-000785 | NCR | W - PTW and CP1a: Missing Early Strength Tests |  | Contr | __M |  |  | 2014-07-11 | 2014-07-01 14:30 | -10 | 2014-06-24 18:45 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During works in PTW and CP1a Enlagement, between August and October 2013, few early strenght have been missed (see attachments 01 to 15): • PTW-W Primary Lining – 1st Thickening (crown) at EP1 (P1): early strength test is missing at 1 hr and 3 hrs. Measurements taken after 3 hrs are above the J2 curve. • PTW-W Primary Lining – 2nd Thickening (crown) at EP1 (P1): early strength test is missing at 1 hr. Measurements taken after 1 hr are above the J2 curve. • PTW-W Primary Lining – 3rd Thickening (crown) at EP1 (P1): early strength tests are missing at and prior to 1 hr. Measurements taken after 1 hr are above theJ2 curve. • EPTW Primary Lining – 2nd Thickening (crown) at VA5 (P1): early strength tests are missing at and prior to 1 hr. Measurements taken after 1 hr are above the J2 curve. • EPTW Primary Lining – 2nd Thickening (invert) at VA5 (P1): early strength test is missing at 1 hr and taken at 4 / 8 hrs instead of 3 / 6 hrs respectively. Measurements taken at 4 hrs onwards are above the J2 curve. • EPTW Primary Lining – 3rd Thickening (crown) at VA5 (P1): early strength tests are missing at and prior to 1 hr. Measurements taken after 1 hr are above the J2 curve. • EPTW Primary Lining – 3rd Thickening (crown) at Bypass (P1): early strength tests are missing at 1 hr and 3 hrs and were taken at 7 hrs instead of 6 hrs. Measurements taken at 7 hrs onwards are above the J2 curve. • CP1a Primary Lining – Advance 25 (P1): early strength tests are missing at 1 hr (low at 45 min), 3 hrs, 6 hrs, and 12 hrs. Measurements taken at 24 hrs were above the J2 curve. • CP1a Primary Lining – Advance 27 (P1): early strength test is low at 1 hr. Measurements taken at 3 hrs and later were above the J2 curve. • CP1a Primary Lining – Advance 20 Rework (P1): early strength test at 6 hrs taken at 8 hrs. Measurements taken before and after 6 hrs exceed J2 curve. • CP1a Primary Lining – Advance 23 Rework (P1): early strength test for 1 hr is missing. Measurements taken after 1 hr exceeds the J2 curve. • CP1a Primary Lining – Advance 30 (P1): early strength test for 3 hrs was performed at 4 hrs. Measurements before and after 3 hrs exceed the J2 curve. • CP1a Primary Lining – Advance 33 (P1): early strength test is missing at 1 hr. Measurements after 1 hr exceed the J2 curve. • CP1a Primary Lining – Advance 36 (P1): early strength test is missing at 1 hr. Measurements after 1 hr exceed the J2 curve. • CP1a Primary Lining – Advacne 54 (P1): early strength test is low at 1 hr. Measurements taken after 1 hr exceed the J2 curve. CP1a Primary Lining Enlargement, advance 5, 24, 19 Rework, and 57 – early strength tests should be performed at every 3rd advance and thus should have been performed at this advance. Instead, the early strength tests were performed at advances 6, 25 and 20 Rework, which resulted in a larger than permitted gap in early strength testing.
| 02SL - Stations (LUL) | Cxxx-NCR-000786 | NCR | L - CH5/CP2: Start of Breakout without Checksheet signed off by CRL/__ |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-07-25 | 2014-06-30 10:42 | -25 | 2014-06-25 15:13 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | • On 08/06/14 DS, breakout of CP2 from CH5 thickening has started at 7.30 am • At that time the breakout checksheet was fully filled, ok to go and signed by Cxxx but not by __ Designer and CRL
| 02SL - Stations (LUL) | Cxxx-NCR-000788 | NCR | W - CP3-N Crown: Overspray of the 1st Layer Secondary Lining |  | Contr | __M |  |  | 2015-12-31 | 2015-03-05 15:26 | -301 | 2014-08-22 17:58 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In PTE East above the eye of CP3-N the 1st layer of secondary lining was sprayed tight. The first layer of secondary lining was sprayed and reinforcement was installed around the eye. After surveying the reinforcement it was clear to see that above the eye in the centre that the lining was sprayed tight meaning that the reinforcement could not be sprayed in with fireproofing also sprayed on top to the final profile. See detailed survey and tolerances sketch in attachments.
| 02SL - Stations (LUL) | Cxxx-NCR-000789 | NCR | W - PTE-W Blocks 13 and 14: Cable Trench not as per design |  | Contr | __M |  |  | 2014-10-10 | 2014-09-22 11:58 | -18 | 2014-07-14 08:48 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Planning | Repair | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | • On 16/6/14, during works of Block 13 Cable Trench/Duct, the level was dropped down correctly for the cable trench, but the radial joint was not created as designed, therefore leaving a smaller radial joint which would be inadequate. See sketches in attachment 02 for all details.
| 02SL - Stations (LUL) | Cxxx-NCR-000790 | NCR | W - PTE-W between Blocks 14 and 15 RHS: Transversal Joint not in the middle of the water bar |  | Contr | __M |  |  | 2014-10-17 | 2014-09-22 12:16 | -25 | 2014-07-11 17:29 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | • On 15/06/14, location of transversal joint between block 15 and 16 was not formed in the middle of the water bar • The stop –end was placed past too far along and hence the joint was located past the centre of the water bar and out of the acceptable tolerance. See sketch attached for Location (att01.)
| 02SL - Stations (LUL) | Cxxx-NCR-000791 | NCR | L - AP1/CP10: FF2 one U bar damaged during cleaning of bulk-out layer |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-08-01 | 2014-07-16 12:16 | -16 | 2014-06-25 14:52 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Thickening works have been done in June 2014: • On 15/06/14 NS, during cleaning of bulk-out layer with road header one U bar was damaged Refer to the photo of the U bar damaged ( att01) for evidences
| 02SL - Stations (LUL) | Cxxx-NCR-000792 | NCR | L - PTW-W/CP1 Thickening: Non-conforming Cores CR1773 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-09-26 | 2014-07-30 10:05 | -58 | 2014-06-26 13:48 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | PTW-W/CP1 Thickening, for CP1break out has been sprayed beginning of June 2014 and cored the 21/06/14. The core CR1773 (Right Knee ) was reviewed and the followings imperfections were found on core #2: • voids >10mm • voids behind rebar • ACI grade: 4 See Core Report attached (att01)
| 02SL - Stations (LUL) | Cxxx-NCR-000793 | NCR | W EP1 Pilot and L CP3 Pilot: Unable to obtain cores |  | Contr | __M |  |  | 2014-07-18 | 2014-07-17 16:02 | -1 | 2014-06-24 10:04 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | EP1 Pilot in WHI has been built at the end of 2013. CP3 Pilot in LIS has been built in April 2014. During this period, lab Techniciens have been unable to obtain cores from these pilots on time.
| 02SL - Stations (LUL) | Cxxx-NCR-000794 | NCR | W - ES1 Pipe Arch: As-built survey of installed pipes not conforming to the designed array |  | Contr | __M |  |  | 2015-02-27 | 2015-01-29 13:05 | -29 | 2014-06-24 12:30 | Tunnelling - Linings - Sprayed Concrete | 50000 |  | Equipment Breakdown | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As-built survey of installed pipes not conforming to the designed array referenced by drawing UnPS-CFT-WCH-PAS-D-32382. See att Att03. 16-06-14 ES1 Pipe Arch As-built section and plan view for more details.
| 02SL - Stations (LUL) | Cxxx-NCR-000795 | NCR | W - Crossover Pilot Adv 15 and 25: Current margin strength failure |  | Contr | __M |  |  | 2014-09-19 | 2014-09-17 17:40 | -2 | 2014-06-24 12:04 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Cores have been taken in Crossover Pilot Adv 15 and 25. Even though the strengths of sample numbers CR 1659 & CR 1660 exceed the design strength at, 38.3N/mm² & 42.0N/mm² respectively but they have both failed to meet the target mean strength of 41.9N/mm² by 0.2N/mm². See lab result attached (att01)
| 02SL - Stations (LUL) | Cxxx-NCR-000796 | NCR | L - VD5: OSD pile encountered during drilling of two ejectors |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-12-12 | 2014-09-24 10:06 | -79 | 2014-06-30 09:49 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Not Defined | Completed |  | An obstruction was encountered at 3m (73.9 mATD) during drilling of EJ12 and at 3.2m (74.4 mATD) during drilling of EJ14. Detailed log describing geological strata encountered is attached to this document. (att01.) A small piece of black plastic material, looking like an impermeable membrane, was found on tip of rod in EJ12. During pulling out of rods in EJ14, the last rods snapped and circa 30cm of last rod got stuck inside the holes.
| 02SL - Stations (LUL) | Cxxx-NCR-000797 | NCR | L - RCE: Incorrect size of TBM Rail Plinth Detail |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-09-26 | 2014-09-22 11:43 | -4 | 2014-07-04 14:20 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | • On 20/06/14, during installation of reinforcement and dowels in Reception Chamber RCE, Site Team found discrepancy between size of reception chamber and size of reinforcement meshes allowed for. • On 24/06/14, after site inspection by __ Temporary Works Coordinator of the structural slab & haunch pour (supporting foam concrete plug formwork and TBM rail), it appears that the embedment of the dowels into the haunch structure is not acceptable. (Refer to attached photo, att01).
| 02SL - Stations (LUL) | Cxxx-NCR-000798 | NCR | L - CP1 Enl Adv 10 and 11: Tight excavation on the right hand side behind the kwikastrip |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-08-22 | 2014-07-16 12:19 | -37 | 2014-07-02 08:46 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | • On 27/06/14 DS, CP1 Enl Adv 10 and 11 has not been cleaned / roadheaded sufficiently, the excavation was mucked tight on the right hand side behind the kwikastrip (+20mm as opposed to +100mm). This was found during the excavation of the invert advances 12 & 13.
| 02SL - Stations (LUL) | Cxxx-NCR-000799 | NCR | L - AP1/CP9 and PTW-E/CP7: exposed rebar and poor joints in the invert thickening |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-09-12 | 2014-07-04 12:26 | -70 | 2014-07-02 12:22 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • On 28/06/14 NS, rebars have been partially exposed in AP1/CP9 and CP7/PTW-E both of FF2 RF invert (att01: AP1/CP9 exposed rebar of FF2 below the eye and att02: PTW-W/CP7 exposed rebar of FF2 top right corner) and poor joints in the invert of the thickening in CP7 have been spotted (att03).
| 02SL - Stations (LUL) | Cxxx-NCR-000800 | NCR | L - AP7W-e CH1 (i) Adv 50 and 66: Missing early strength |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-08-29 | 2014-07-21 14:57 | -39 | 2014-07-09 16:37 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | • During package L048 review it has been found that the Early Strength Test of 6hr and 12hr has been missed in AP7 West Enlargement Ch1 (i) Advance 50 and that 6hr test has been also missed in AP7 West Enlargement Ch1 (i) Advance 66 Please refer to the Early Strength Test Checksheets attached for evidence (att01.)
| 02SL - Stations (LUL) | Cxxx-NCR-000801 | NCR | L - LCE Thickening Final Layer: Defects in the invert |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-08-31 | 2015-01-29 11:08 | -214 | 2014-07-28 11:01 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following closure of NCR 746, related only to delimation of LCE first layer thickenning, it has been found that some areas at the far end (furthest from AP6) of the 2nd (and final) layer of LCE also failed the hammer test. Specific failed areas will be defined at later stage as there is no record of failure at the moment. Hammer testing will be repeated on the area during snagging process before regulating layer. The 06/12/14: Hammer testing have been done in PTE Block 31 and 32 and no hollow spots have been found. Refer to the Permit ot cover and Hammer Testing Checksheet of Block 31 and 32.(Att01. and Att02. )
| 02SL - Stations (LUL) | Cxxx-NCR-000802 | NCR | W - PTE-Block 10: Installation reinforcement in invert slab of Block 10 not in accordance with the design |  | Contr | __M |  |  | 2015-10-31 | 2015-04-14 11:23 | -200 | 2014-07-08 17:09 | Tunnelling - Linings - Sprayed Concrete | 7000 |  | Design | Repair | 2 (6-60k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | • During PTE-Block 10 installation, not all reinforcement stated on the latest design was installed accordantly. • The following bar marks have been not or differently installed: - BM 45: Not installed 6 bars each side effected - BM 24/27: Not installed but will be post drilled into the invert slab - BM 18:Not installed but will be post drilled into the invert slab - BM 28: Not installed but will be post drilled into the invert slab - BM 20/21: Not installed but will be post drilled into the invert slab - BM 30/36: Not installed but B25 all 150 mm along the entire slab installed. Post drilled 30/36 towards the wings possible. - A393 Mesh FF. Not installed in invert - Support chairs B16 installed in the invert. See attached picture. (see att05)
| 02SL - Stations (LUL) | Cxxx-NCR-000803 | NCR | L - AP1 thickening: 1 NF2 rear end exposed and damaged |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-09-19 | 2014-07-23 07:53 | -58 | 2014-07-09 17:31 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On 04/07/2014 DS, in the invert thickening of CP10 from AP1, roadheadering at the surrounding was on going to prepare the support for the next stage of spray and top NF2 rebar got exposed, caught and damaged. Refer to the photo (att01) and drawing (att02) attached
| 02SL - Stations (LUL) | Cxxx-NCR-000804 | NCR | W - Malfunction of beam press machine - No results for the 28day beam testing |  | Contr | __M |  |  | 2014-08-22 | 2014-07-28 13:30 | -25 | 2014-07-09 17:14 | Tunnelling - Tunnelling General | 500 |  | Equipment Breakdown | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | On 29/05/14, whilst carrying out the 28 day flex beam testing for sample number CR1588 (April 14 beams), the machine did not register any results.
| 02SL - Stations (LUL) | Cxxx-NCR-000805 | NCR | L - AP1/CP9 Thickening: Non-conforming Cores CR1824 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-09-19 | 2014-07-28 13:32 | -53 | 2014-07-17 17:08 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Core CP9 From AP1 Thickening in the Right Top has been sprayed between June and July 2014 and cored the 10/07/14. The core CR1824 was reviewed and the followings imperfections were found: • Major voids >5mm • Poor encapsulation • Core broken • ACI grade: 3 During the SRG meeting on the 10/07/14 it has been agreed that a NCR should be raised. See Core Report attached (att 1)
| 02SL - Stations (LUL) | Cxxx-NCR-000806 | NCR | W - PTE-W: Areas above on Spray Waterproof Membrane wet and failing to cure due to water ingress coming |  | Contr | __M |  |  | 2016-09-30 | 2016-10-10 10:33 | 10 | 2014-08-21 15:20 | Tunnelling - Linings - Sprayed Concrete | 8000 |  | System Defect | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • In PTE West several areas have been identified above on the Spray Applied Waterproof Membrane as wet and failing to cure due to water ingress coming through the substrate. • The __ Masterseal 345 did not cure as the waterproof membrane was still wet and soft due to the water ingress from the substrate. Therefore the integrity of the waterproofing is impaired and fails to meet the specification. • A list of locations can be found in the attachments - The Email was the first initial finding with 11 wet patches (27/06/14 - att01) - After further inspection from __ this was increased to 16 wet patches (30/06/14 - att02) - Currently (21/08/2014) we have a longer list consisting of 26 wet patches (att03 and 04) • Suspected total number of wet patches appears to be about 32 (due to some being renamed)
| 02SL - Stations (LUL) | Cxxx-NCR-000807 | NCR | W - PTE-W Block 14: Sidewing Central Crack |  | Contr | __M |  |  | 2017-01-31 | 2017-01-18 08:30 | -13 | 2014-08-21 18:01 | Tunnelling - Linings - Sprayed Concrete | 10000 |  | Material | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | In PTE West block 14 sidewing has a crack running down the centre of the block throughout the middle of the block. This appears to go throughout the whole block. See Photos of crack through block 14
| 02SL - Stations (LUL) | Cxxx-NCR-000808 | NCR | W - PTW-E, PTW-W, EPTW: Missing Early Strength |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-08-22 | 2014-07-29 13:53 | -24 | 2014-07-18 12:08 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | • PTW-E Thickening at VA4 (First layer primary thickening (crown), P1, 11.07.2013) –early strength test measurements at 1 hour missing. • PTW-E Thickening at VA4 (Second layer primary thickening (crown), P1, 12.07.2013) – early strength tests are missing at 1 hr and 3 hrs. • PTW-E Thickening at VA4 (First layer primary thickening (Invert), P2, 16.07.2013) – early strength tests are missed at 1 and 3 hrs • PTW-E Thickening at VA4 (Second layer primary thickening (Invert), P1, 16.07.2013) – early strength test measurements missed at 6 and 12 hours. • PTW-W Thickening at CP1-a-S (First layer primary thickening (invert), P1, 14.08.2013) – early strength measurement at 12 hrs is missing • PTW-W Thickening at CP1-a-S (Second layer primary thickening (invert), P2, 14.08.2013) – early strength measurement at 1 and 3 hours are missing. • PTW-E Thickening at CP3-S (First layer primary thickening (Invert), P2, 21.07.2013) –early strength requirement at 1hr below J2 curve. • PTW-E Thickening at CP3-S (Final layer primary thickening (Invert), P1, 11.07.2013) –early strength test measurements at 1,3 and 12 hours missing. • EPTW Enlargement, Advance 5, P1 18/09/13 – early strength measurement at 1 hour below required J2 curve. • EPTW Enlargement, Headwall Thickening, P2 19/09/13 – early strength test measurement below required modified J2 curve. • PTW-E Enlargement at ADV 89, P1 23/04/14 – early strength test measurements at 1 hour missing
| 02SL - Stations (LUL) | Cxxx-NCR-000809 | NCR | L - VD5 Enl Adv 19 and VD1 Enl Adv 20: Strength failure on the running mean strength |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-06-01 | 2014-11-20 13:15 | -193 | 2014-07-14 12:29 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | Even though all the 28 day results comply with criterion 1 given in technical requirements, two lower than normal 28 day results on sample numbers CR1687 (VD5 Enl Adv 19 sprayed on 22/05/14 and cored on 31/05/14) & CR1719 both (VD1 Enl Adv 20 sprayed on 10/06/14 and cored on 10/06/14) at 33.7N/mm² has resulted in seven subsequent results failing criterion 2 from between 0.1 & 0.8N/mm². See lab report attached (att01.)
| 02SL - Stations (LUL) | Cxxx-NCR-000810 | NCR | W - XOV Enl Adv 5 and 6 - Side bars incorrectly installed AND Adv 9 - wrong mix used |  | Contr | __M |  |  | 2014-10-03 | 2014-09-29 12:08 | -4 | 2014-07-25 12:11 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | 1. On 14/07/14 DS, Reinforcement in XOV Enlargement adv 5&6 has been installed as NF instead of FF. 2. On 15/07/14 DS, when spraying XOV Enlargement adv 9 Top Heading, shotcrete mix used to spray was wrong. Mix P1 (fibre mix) has been used for side wall reinforcement instead of the mix P2.
| 02SL - Stations (LUL) | Cxxx-NCR-000811 | NCR | L - CP3 Enl Adv 11: No face log completed or photograph taken |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-08-22 | 2014-07-22 16:04 | -31 | 2014-07-16 17:27 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | • On 05/05/14 DS, no facelog completed for last advance 11 of CP3 Enlargement.
| 02SL - Stations (LUL) | Cxxx-NCR-000812 | NCR | W - EPW1: Core Hole backfilled with muck |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-06-30 | 2015-03-27 10:32 | -95 | 2014-07-25 15:28 | Tunnelling - Linings - Sprayed Concrete | 4000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On 14/07/14, it has been found that in EPW1 Enlargement RHS about axis level, some core holes have been backfilled with muck. (see photo att01)
| 02SL - Stations (LUL) | Cxxx-NCR-000813 | NCR | W - Malfunction of beam press machine |  | Contr | __M |  |  | 2015-03-27 | 2015-03-05 10:19 | -22 | 2014-07-18 14:27 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Equipment Breakdown | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Whilst carrying out the 28 day beam testing for sample number CR1656B, CR1654B, CR1724A, CR1740C the machine register unusual graph line. (see att01). Account samples: CR1724A, CR1740C fall below individual sample limit D3 1.26N/mm2.
| 02SL - Stations (LUL) | Cxxx-NCR-000814 | NCR | L - AP7-E CH2 Enl: Early Strength Testing and Sampling not carried out as per ITP |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-08-29 | 2014-08-04 13:56 | -25 | 2014-07-30 11:04 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | - On 11/04/13 DS in AP7E Enl CH2: Adv 2 Spray started without flow test carried out. Start of spray 8h45, first sample (Ticket No. 3012 ) tested at 14h40. - On 22/04/13 DS in AP7E Enl CH2: Adv 26 ( invert ), no Early Strength tests have been done - On 23/04/13 DS in AP7E Enl CH2: Adv 27 No flow tests were done Refer to the placement checksheets attached for evidence (att01)
| 02SL - Stations (LUL) | Cxxx-NCR-000815 | NCR | W - EB Cav, Sidewall Enl.: B16 steel continuity bars installed in the Primary 3 layer of Advance 1 & 2 |  | Contr | __M |  |  | 2015-09-30 | 2014-12-16 10:19 | -288 | 2014-08-05 17:54 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | B16 steel continuity bars installed in the Primary 3 layer of Advance 1 & 2. The bar was installed and sprayed in on Advance 1 & 2 where DWG Cxxx-__M-C4-DDB-D061-00614 indicates this should start at approximately Advance 3.
| 02SL - Stations (LUL) | Cxxx-NCR-000816 | NCR | L - RCE Block 1 and 2: damp marked areas sprayed |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-10-31 | 2014-10-15 15:54 | -16 | 2014-07-30 15:06 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | - On 13/07/14 DS, areas of water seepage have been spotted in RCE block 1 & 2 and recorded on the forms D3-93 Permits to Cover Primary Lining. Installation of water management system has been requested and recorded on the Checksheet. Refer to att01 for evidence - Unfortunately the following shifts (13/07/14 NS and 14/07/14 DS) the areas with water seepage have been sprayed despite the clear instructions written in the checksheet to not spray the wet areas Refer to att02 attached
| 02SL - Stations (LUL) | Cxxx-NCR-000817 | NCR | W - ES1 Permeation: None compliance of the permeability tests on treated ground |  | Contr | __M |  |  | 2014-08-29 | 2014-08-20 17:21 | -9 | 2014-07-23 15:59 | Geotechnical Engineering - Geotechnical Engineering - General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | The measured permeability results did not achieve the above technical requirement. The results are as follows: • BH No C1: - Top Depth (m): 5.5 - Bottom Depth (m): 6.5 - Coefficient of Permeability k (m/s): 1.5E-07 (Piezometer) - Date Tested: 25/06/14 • BH No C1 - Top Depth (m): 6.5 - Bottom Depth (m): 7.3 - Coefficient of Permeability k (m/s): 9.8E-07 - Date Tested: 05/12/13 • BH No C2 - Top Depth (m): 4 - Bottom Depth (m): 5 - Coefficient of Permeability k (m/s): 1.3E-06 - Date Tested: 01/12/13 • BH No C3 - Top Depth (m): 6 - Bottom Depth (m): 7 - Coefficient of Permeability k (m/s): 1.8E-06 - Date Tested: 29/11/13 From the above results and in accordance with the RFI requirement 100% of the permeability results achieved less than 5x10-6m/s, 50% of the tests did not achieve the specified requirement of less than 1x10-7m/s.
| 02SL - Stations (LUL) | Cxxx-NCR-000818 | NCR | W - PTE-W Adv. 200-248: Missing some Early Strength |  | Contr | __M |  |  | 2014-08-22 | 2014-08-13 17:18 | -9 | 2014-07-28 15:01 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Between 28/03/14 and 04/04/14, the following advances have been sprayed in PTE-W Enl and tests have been missed: • PTE-W Primary Lining Enlargement – Advance 208 (P1): Early strength test is low at 1 hr and missing at 3 hrs. Measurements taken after 3 hrs are above the J2 curve. • PTE-W Primary Lining Enlargement – Advance 214 (P1): Early strength test is missing at 6 hrs. Measurements taken before and after 6 hrs are above the J2 curve. • PTE-W Primary Lining Enlargement – Advance 217 (P1): Early strength test missing at 1 hr. Measurements taken before and after 1 hr are above the J2 curve. • PTE-W Primary Lining Enlargement – Advance 220 (P1): Early strength tests missing at 6 and 12 hrs. Measurements taken before 6 hrs and after 12 hrs are above the J2 curve. • PTE-W Primary Lining Enlargement – Advance 223 (P1): Early strength test is missing at 3 hrs. Measurements taken before and after 3 hrs exceed the J2 curve. • PTE-W Primary Lining Enlargement – Advance 229 (P1): Early strength test is missing at 1 hr. Measurements taken after 1 hr exceed the J2 curve. • PTE-W Primary Lining Enlargement – Advance 232 (P1): Early strength test is low at 1 hr. Measurements taken after 1 hr exceed the J2 curve. • PTE-W Primary Lining Enlargement – Advance 235 (P1): Early strength test is low at 1 hr and missing at 3 hrs. Measurements taken after 3 hrs exceed the J2 curve. • PTE-W Primary Lining Enlargement – Advance 241 (P1): Early strength test is missing at 1 hr. Measurements taken after 1 hr exceed the J2 curve. • PTE-W Primary Lining Enlargement – Advance 244 (P1): Early strength test is missing at 6 hrs. Measurements taken before and after 6 hrs exceed the J2 curve.
| 02SL - Stations (LUL) | Cxxx-NCR-000819 | NCR | L - Blomfield Box: TAM positions outside specified tolerance |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-09-26 | 2014-07-29 15:59 | -59 | 2014-07-23 18:19 | Geotechnical Engineering - Geotechnical Engineering - General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | The following boreholes were surveyed using a Gyrosmart instrument and were found to be outside the agreed tolerances: - TAM__03 which commenced drilling on the 10th July 2014 and completed on the 10th July 2014 was outside the tolerance envelope in elevation by 280mm at 15m (see att01). - TAM__12 which commenced drilling on the 16th June 2014 and completed on the 17th June 2014 was outside the tolerance envelope in elevation by 330mm at 30m(see att02). - TAM__13 which commenced drilling on the 18th June 2014 and completed on the 18th June 2014 was outside the tolerance envelope on elevation and plan by 250mm and 240mm respectively at 33m (see att03). - TAM__14 which commenced drilling on the 5th June 2014 and completed on the 7th June 2014 was outside the tolerance envelope on elevation and plan by 20mm and 140mm at 51m respectively. (see att04) - TAM__15 which commenced drilling on the 30th June 2014 and completed on the 1st July 2014 was outside the tolerance envelope in elevation by 530mm at 45m. (see att05) - TAM__16 which commenced drilling on the 2nd July 2014 and completed on the 2nd July 2014 the TAM was short of design length by 19.4m and was outside the tolerance envelope in elevation by 90mm at 9m and 12m. (see att06) - TAM__17 which commenced drilling on the 18rd June 2014 and completed on the 21st June 2014 was outside the tolerance envelope on plan by 820mm at 66m. (see att07) - TAM__18 which commenced drilling on the 3rd July 2014 and completed on the 3rd July 2014 was outside the tolerance envelope in elevation by 70mm at 60m. (see att08)
| 02SL - Stations (LUL) | Cxxx-NCR-000820 | NCR | L and W: Use of Mix S for Active Compensation Grouting and Corrective Grouting |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-05-31 | 2014-12-17 11:17 | -165 | 2014-07-24 15:31 | Geotechnical Engineering - Geotechnical Engineering - General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | __ did not submit Mix S to the Project Manager for acceptance as a grouting material for Active Compensation Grouting or Corrective Grouting.
| 02SL - Stations (LUL) | Cxxx-NCR-000821 | NCR | L - CP9 Pilot Adv 27: Under-excavation |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-11-28 | 2014-11-20 13:24 | -8 | 2014-07-30 15:20 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | - On 22/07/14 DS: CP9 Pilot Adv 27 has been mucked tight on the trailing edge to -20mm from 6 o’clock to 9o’clock. Refer to attached Shotcrete placement Checksheet (Att01) and Beamer excavation profile (Att02).
| 02SL - Stations (LUL) | Cxxx-NCR-000822 | NCR | W - EBRT W Enl Adv 159: 1st Layer sprayed with Mix P2 only |  | Contr | __M |  |  | 2014-09-05 | 2014-09-09 17:16 | 4 | 2014-07-24 17:06 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | • On 13/05/14 DS, EBRT W Adv.159 1st layer was sprayed with mix P2 only.
| 02SL - Stations (LUL) | Cxxx-NCR-000823 | NCR | W - PTE-W & EBRT-W- Missing Early Strength Test |  | Contr | __M |  |  | 2014-12-12 | 2014-09-15 09:46 | -88 | 2014-09-08 14:44 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | Between 19/03/13 and 11/02/14, the following advances have been sprayed and tests have been missed: • PTE-W Enlargement, Adv 205, early strength test at 3 hrs missing, later tests above J2 curve. • EBRT-W Enlargement, Adv 3, early strength test at 1 hrs missing, later tests above J2 curve. • EBRT-W Enlargement, Adv 38, early strength test at 1 hrs missing, later tests above J2 curve. • EBRT-W Enlargement, Adv 50, early strength test missing at 1 hrs, later tests above J2 curve. • EBRT-W Enlargement, Adv 54, early strength test missing at 6 hrs, later tests above J2 curve . • EBRT-W Enlargement, Adv 56, early strength test at 6 hrs missing, later tests above J2 curve. • EBRT-W Enlargement, Adv 59, early strength test at 1 hrs missing, later tests above J2 curve. • EBRT-W Enlargement, Adv 62, early strength test at 3 & 6 hrs missing, later tests above J2 curve
| 02SL - Stations (LUL) | Cxxx-NCR-000824 | NCR | W - PTE-E/VA2 Headwall Enl: area of voided concrete to the east side of the junction |  | Contr | __M |  |  | 2014-09-26 | 2014-09-26 17:09 | 0 | 2014-07-30 09:23 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | - On 31/10/13, an area of voided concrete has been detected by hammer tapping under the thickening in the east side of the VA2/PTE-E junction. See attached picture (att01.) - The area about 2m x 1m has been proof drilled and the void is at an approximate depth of 50mm below the surface of the thickening layer. See attached sketch of approx. dimensions to be treated (att02.).
| 02SL - Stations (LUL) | Cxxx-NCR-000825 | NCR | L - PTE Block 2: Incorrect Shotcrete Placement Checksheet used for regulating layer |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-08-15 | 2014-08-04 13:58 | -11 | 2014-07-30 17:28 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | - During __ Surveillance carried out on 24/07/14 (Scope: Application of Regulation Layer / Permit to Cover Process at LIV), it has been found that on 14/07/14 DS, a wrong Shotcrete placement Checksheet (D3-37 instead of D3-86) has been used for the regulating layer spray of PTE Block 2. Refer to the photo attached (Att01.)
| 02SL - Stations (LUL) | Cxxx-NCR-000826 | NCR | W - PTW-W/EP1 Third thickening layer (Invert): 1 hr. test missing |  | Contr | __M |  |  | 2014-09-05 | 2014-08-27 12:32 | -9 | 2014-07-31 09:29 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | PTW-W Thickening at EP1 (Third Layer primary thickening (Invert), P1, 08.09.2013) –early strength test measurements at 1 hour missing. See att01.
| 02SL - Stations (LUL) | Cxxx-NCR-000827 | NCR | W - Bypass and VA5 Invert 2nd thickening layer: missing reinforcement checksheets |  | Contr | __M |  |  | 2014-11-30 | 2014-12-01 15:32 | 1 | 2014-07-31 13:53 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | - PTW-W Thickening at VA5 (Second Layer primary thickening (Invert), 05.09.2013 –Reinforcement check sheet D3-26 missing - PTW-W Thickening at Bypass (Second Layer primary thickening (Invert) 04.09.2013 - Reinforcement check sheet D3-26 missing
| 02SL - Stations (LUL) | Cxxx-NCR-000828 | NCR | L - AP1/CH7: 2 rebars exposed during breakout of the invert |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-10-10 | 2014-09-08 16:19 | -32 | 2014-08-01 09:19 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Thickening works have done in June 2014 • On 31/07/14 DS, during breakout of CH7 two rebars in the invert have been exposed Refer to the photos for evidence ( att01 and att02 )
| 02SL - Stations (LUL) | Cxxx-NCR-000829 | NCR | L - PTE-E and AP5 Enl: Missing Early Strength and late flow tests |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-10-24 | 2014-08-10 13:35 | -75 | 2014-08-04 15:31 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Issue1 On 11/04/14, during AP5: Early strength tests have been missed for adv 59. Issue 2 PTE-E work in November 2014: (see att01.) - On 07/11/13, in PTE-E Adv 11: spraying commenced at 14:15 but sampling regime was only done at 14:52 (result compliant) - On 14/11/13, in PTE-E Adv 36: spraying commenced at 01:15 but sampling regime was only done at 01:15 (result compliant) - On 17/11/13, in PTE-E Adv 49: spraying commenced at 04:00 but sampling regime was only done at 04:01 (result compliant) - On 17/11/13, in PTE-E Adv 52: spraying commenced at 23:30 but sampling regime was only done at 23:40 (result compliant) - On 19/11/13, in PTE-E Adv 58: spraying commenced at 03:00 but sampling regime was only done at 03:31 (result compliant) - On 20/11/13, in PTE-E Adv 64: spraying commenced at 22:00 but sampling regime was only done at 22:04 (result compliant) AP5 work in April 2014: (see att02.) - On 10/04/14, in AP5 Adv 53: spraying commenced at 03:15 but sampling regime was only done at 03:20 (result compliant) - On 10/04/14, in AP5 Adv 56: spraying commenced at 22:00 but sampling regime was only done at 22:18 (result compliant) - On 13/04/14, in AP5 Adv 64: spraying commenced at 00:15 but sampling regime was only done at 00:30 (result compliant)
| 02SL - Stations (LUL) | Cxxx-NCR-000830 | NCR | L - PTW-E Enl Adv 6: Total thickness not achieved on Beamer Profile |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-04-23 | 2014-12-03 16:54 | -141 | 2014-08-04 17:25 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Equipment Breakdown | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During Certification process of PTW-E, it has been decided to raise a NCR due to potential lack of thickness of PTW-E Enl Adv 6 Invert as recorded on Beamer Profile Thickness (see att02.Beamer Profile). Indeed, Beamer Profile shows thickness between 289 and 398mm (instead of 400mm). However, comments have been made by Shift Engineers explaining that thickness has been achieved. (see att02 SCL checksheet)
| 02SL - Stations (LUL) | Cxxx-NCR-000831 | NCR | L - VD2: L-bars hit when scabbling |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-09-26 | 2014-09-05 13:29 | -21 | 2014-08-04 18:24 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On 01/08/14 NS, during re-profiling in the ‘L’ bar window area, up to 50 mm on VD2 eye, 3 No. ‘L’ bars were exposed (see photos attached).
| 02SL - Stations (LUL) | Cxxx-NCR-000832 | NCR | L - CP10 Pilot Adv 4: Non conforming Cores CR1886 - major void, honeycombing |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-09-19 | 2014-09-17 13:27 | -2 | 2014-08-05 15:34 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | CP10 Pilot Adv 4 has been sprayed on 17/07/14 and cored the 02/08/14 DS. The core CR1886 was reviewed and the followings imperfections were found: • Major voids >50mm • Honeycombing • Core broken • ACI grade 4 for core #3 See Core Report attached (Att 1)
| 02SL - Stations (LUL) | Cxxx-NCR-000833 | NCR | L - PTE-W/CP2 Thickening RK and LS: Non-conforming Cores CR1895 and CR1896: bad encapsulation of rebar |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-11-28 | 2014-10-11 10:45 | -48 | 2014-08-08 17:23 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | PTE-W/CP2 thickening Right Knee and Left Shoulder have been cored on 04/08/14 DS. - The cores CR1895 and CR1896 were reviewed and the followings imperfections were found: • Major voids >10mm around rebar • Poor encapsulation around rebar • ACI grade for core #4 is 4 See Cores Report attached (Att 1) - Additional cores have been cored on 07/08/14 DS. The cores CR1913 (LH and RK) were reviewed and confirmed imperfections found in the first sets of cores: • Major voids >>10mm around rebar • Poor encapsulation around rebar • ACI grade for core #1 is 4 and for #2 is 3 See Cores Report attached (Att 3) PTE-W/CP2 thickening has been sprayed between the 16/07/14 and the 03/08/14 It has been sprayed during 15 different shifts (5 time by Shift 1, 6 time by Shift 2 and 4 time by Shift 3 during 5 days shifts and 10 nights shifts) At least 6 different Nozzlemen did the spraying of the thickening. They are all qualified and have lot of experience to do the work as we can see in Cxxx-__M-C4-CER-C101-50001 “Liverpool Street Nozzleman Certification “ During the spray, Nozzlemen are supervised by shift engineers and often by Nozzleman supervisors or SCL Inspectors when they are present on site (DS).
| 02SL - Stations (LUL) | Cxxx-NCR-000834 | NCR | W - WHI April: Non-compliance result on one of 90 day remaining beam (CR1564F) |  | Contr | __M |  |  | 2016-02-29 | 2016-01-27 13:32 | -33 | 2014-08-05 15:01 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | 90 day beam sample CR1564F (sprayed on 23/04/14) does not comply with specification limit for individual test result which leads to overall failure for whole 90 day beam set. See Att01.
| 02SL - Stations (LUL) | Cxxx-NCR-000835 | NCR | W - EP1,CP1a, EBRT-E, Bypass and VA5 Enl: Missing some Early Strength Tests |  | Contr | __M |  |  | 2014-10-24 | 2014-08-27 19:32 | -58 | 2014-08-12 12:38 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | Between 15/09/13 and 15/05/14, the following advances have been sprayed in EP1, Bypass and VA5 Enl and tests have been missed: • EP1 Enlargement, Adv 6, early strength test at 3 hrs missing, later tests above J2 curve. • EP1 Enlargement Adv 8, early strength test at 1 hr. missing, later tests above J2 curve. • EP1 Enlargement Adv 12, early strength test at 1 hr. missing, later tests above J2 curve. • EP1 Enlargement Adv 21, early strength test missed. • Bypass Tunnel Adv 6, early strength test at 3 hrs missing, later tests above J2 curve. • Bypass Enlargement Adv 26, early strength test at 12 hrs missing, later tests above J2 curve. • Bypass Enlargement Adv 35, early strength test at 3 hrs missing, later tests above J2 curve. • Bypass Enlargement Adv 42, early strength test at 12 hrs missing, later tests above J2 curve. • Bypass Enlargement Adv 50, early strength test at 12 hrs missing, later tests above J2 curve. • Bypass Enlargement Adv 5, early strength test missed. • Bypass Enlargement Adv 32, early strength test missed. • Bypass Enlargement Adv 41, early strength test missed. • Bypass wraparound Stage 4/6, early strength test at 12 hrs missed, later tests above J2 curve. • Bypass Wraparound Stage 13, early strength test at 1,3 and 12 hrs missed. • VA5 Enlargement Adv 3, early strength test missed. • VA5 Enlargement Adv 24, early strength test missed. • VA5 Enlargement Adv 39, early strength test missed. • VA5 Enlargement Adv 45, early strength test missed. • VA5 Enlargement Adv 56, early strength test missed. • CP1a Enlargement Adv. 15, early strength test at 1 hr is missing, later tests are above the J2 curve. • EBRT-E Enlargement Adv. 20, early strength test missing at 1 hr, later tests are above the J2 curve. • EBRT-E Enlargement Adv. 26, early strength test missing at 12 hr, previous and later tests are above the J2 curve. • EBRT –E Enlargement Adv. 32, early strength test missed. • EBRT-E Enlargement Adv. 47, early strength test missed.
| 02SL - Stations (LUL) | Cxxx-NCR-000836 | NCR | W - EP1, Bypass and VA5: Missing Shotcrete placement check sheet __-Form D3-37 |  | Contr | __M |  |  | 2014-10-24 | 2014-08-27 19:34 | -58 | 2014-08-12 14:15 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | Between the 29/09/13 and the 04/05/14, the following information are missing: • Bypass Enlargement Tunnel Adv. 3, missing Shotcrete placement check sheet __ form D3-37. • Bypass Tunnel Adv. 35, missing section A of Shotcrete placement check sheet __ form D3-37. • EP1 Enlargement Adv 6, missing section A of Shotcrete placement check sheet __ form D3-37. • VA5 Enlargement Adv 21, missing section B, C and D of Shotcrete Placement checksheet __ form D3-37 • VA5 Enlargement Adv 45, missing section B, C and D of Shorcrete Placement check sheet __ form D3-37 (see att01 to att04)
| 02SL - Stations (LUL) | Cxxx-NCR-000837 | NCR | W - WHI July Cast test beams: Low Residual Flexural strength |  | Contr | __M |  |  | 2016-02-29 | 2016-01-27 13:34 | -33 | 2014-08-07 16:48 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | WHI cast beam set CR1792 for July has achieved a D3 result of S1.5 at 28 days on average but two beams of this set get lower individual result than specified S1.26 – CR1792A – S0.9, CR1792B – S1.1 respectively.
| 02SL - Stations (LUL) | Cxxx-NCR-000838 | NCR | W - PTE-E CH 32-25 S/L test panel: Current margin strength failure |  | Contr | __M |  |  | 2015-04-30 | 2015-02-05 07:48 | -84 | 2014-08-07 17:04 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | Even though the strengths of sample number CR1757 exceed the design strength at 28 days with 41.4N/mm². It have failed to meet the target mean strength of 41.6N/mm² by 0.2N/mm².
| 02SL - Stations (LUL) | Cxxx-NCR-000839 | NCR | L - LCE Enl: No samples retained from depressurisation hole EJ5 for geological logging |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-10-31 | 2014-10-02 12:22 | -29 | 2014-08-12 09:56 | Geotechnical Engineering - Geotechnical Engineering - General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | No log completed for drilling of depressurisation well EJ5 in Launch Chamber East (LCE).
| 02SL - Stations (LUL) | Cxxx-NCR-000840 | NCR | W - LCW Enl Adv 16: Invert sprayed short by approximately 1m. |  | Contr | __M |  |  | 2014-09-12 | 2014-09-01 14:27 | -11 | 2014-08-14 14:21 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | On 12/08/14 DS, LCW Enlargement Adv 16, 2.0m, double invert was excavated but the Primary Lining II left about 1.0m short of the second top heading.
| 02SL - Stations (LUL) | Cxxx-NCR-000841 | NCR | W - PTE-E: Hollow areas in Secondary Lining |  | Contr | __M |  |  | 2016-06-30 | 2016-06-13 13:38 | -17 | 2014-08-22 09:07 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • On 24/07/14 during hammer tapping of the secondary lining in WHI PTE-East chainage 12-70m - crown some areas produced a consistent hollow sound suggesting that the secondary lining may be heterogeneous on these areas Ch 15 at 1 o'clock ( Will be dealt in Cxxx-NCR-001302 ) Ch 17.5 at 9 o'clock Ch 17.5 at 3 o'clock Ch 46 at 3 o'clock Refer to Att01. WHI PTE-East chainage 12-70m Hammer Testing Checksheet for a detailed sketch • On this basis and as requested by CRL formally through Cxxx-SVI-00004, __ took 3 sample cores, CR1923 at ch.15, ch.1924 at ch.30 and CR1925 at ch.67, as indicated on the attached checklist (see att01). The core CR1923 (PTE-E, CH15, crown) taken in the hammer-tapped area which sounded hollow, confirmed a defect in this area (see exact location of the hollow sound in the detailed photo/survey - att04). Core description: o Core drilled up to 220mm. Recovered length 130-140mm (the rest remains at the hole) o Core broken between the 1st and 2nd layer of secondary lining due to delamination between the layers (void of approx.. 3-4mm), o A longitudinal crack of 2-3mm width goes through the whole thickness of the core but it was not visible from the intrados surface. o ACI Grading = 4. • Other cores taken at PTE-E Secondary Lining showed good compaction and no imperfections or lamination between the two different layers of secondary lining. CR1924 (PTE-E, CH30) and CR 1925 (PTE-E, CH67) were taken from PTE-E, they had a length of ~200mm (ACI = 1) confirming the good and reliable test results of the hammer tapping • On 04/02/16 during hammer tapping of the secondary lining in WHI PTE-East chainage 45-70m, three hollow areas have been found: Ch 42 - 1.3m x 0.8m - 2 o'clock Ch 58 - 1.1m x 0.4m - 8 o'clock Ch 67 - 1.0m x 0.8m - 10 o'clock Refer to Att05. WHI PTE-East chainage 45-70m Hammer Testing Checksheet for a detailed sketch • On 06/02/16 during hammer tapping of the secondary lining in WHI PTE-East chainage 25-45m, one hollow area has been found ( Ch 37 at 10 o'clock ) Refer to Att06. WHI PTE-East chainage 25-45m Hammer Testing Checksheet for a detailed sketch
| 02SL - Stations (LUL) | Cxxx-NCR-000842 | NCR | W - XOV Enl: Non conforming core CR1902 at Adv.75 LK |  | Contr | __M |  |  | 2015-07-23 | 2015-04-13 16:36 | -101 | 2014-08-22 17:46 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | XOV Enlargement Adv 75 have been respectively been sprayed at 30/07/14. It has been cored on 06/08/14. Cores have been reviewed and showed lamination and cracks (see attached report).
| 02SL - Stations (LUL) | Cxxx-NCR-000843 | NCR | L - LIS July Sprayed test beams: Low Residual Flexural strength - CR1837 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-02-29 | 2015-12-14 20:17 | -77 | 2014-08-14 14:35 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | LIV Sprayed beam set, CR1837, has been taken on 15/07/14 (6 Beams Sprayed; Mix P1 C32/40 35kg, no particular area) for July monthly test. CR1837 has achieved a D3 result of S1.5 at 28 days on average, but one beam of this set got lower individual result than specified S1.26 – CR1837B – S1.1
| 02SL - Stations (LUL) | Cxxx-NCR-000844 | NCR | W - PTE-W, PTW-E and PTW-W: No samples retained from depressurisation holes |  | Contr | __M |  |  | 2014-10-31 | 2014-09-11 15:00 | -50 | 2014-08-14 14:51 | Geotechnical Engineering - Geotechnical Engineering - General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | • No Engineers logs completed for drilling of depressurisation wells in PTE – W, PTW – E and PTW – W as samples were not retained for logging. List of Missing Depressurisation Wells: PTE West: Wells ch 109v2, 113v1, 117v3, 121v1, 125v2, 125v3, 129v1. PTW East: Wells ch.10v1, 61v2, 61v3, 53v2, 53v3, 18v1, 26v1, 34v1, 46v2, 46v3, 38v3, 14v2, 14v3, 22v2, 22v3, 49v1, 57v1, 65v1, 41v1, 30v2, 30v3, 38v2. These holes were redrilled holes PTW West: Wells 13v2, 13v3, 17v1, 21v3, 25v1, 29v2, 29v3, 33v1, 37v3, 145v1. • Drillers logs are included in Geological Factual Report Cxxx-__M-C2-RGN-D061-50083.
| 02SL - Stations (LUL) | Cxxx-NCR-000845 | NCR | L-No photograph for the face excavation of Adv 71 CH1(i), Adv 14 CP3a Enl and Adv 71 and 86 PTE-E Enl (RCE) |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-10-31 | 2014-09-05 13:35 | -56 | 2014-08-21 13:28 | Civil - Tunnelling | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | • In May 2013, no photograph of the face excavation of Advance 71 of Chamber CH1 (i) has been taken. Face log completed and photographs taken of advances 70 & 72 • In March and April 2014, no photograph of face excavation of Advance 14 in CP3a Enlargement and Advances 71 & 86 of PTE East Enlargement (RCE) have been taken.
| 02SL - Stations (LUL) | Cxxx-NCR-000846 | NCR | L - Water Flooding into Primary Lining RCW-Adv.54 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-11-28 | 2014-10-02 12:12 | -57 | 2014-08-26 14:55 | Civil - Tunnelling | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During the night shift of 03/05/2014 the team sprayed 2m section of the bottom invert of Primary Lining RCW-Adv.54 but they didn't complete the operation. This has led to water flooding into the primary lining and caused it disintegrate part of the primary lining with no leading edge. Please see photos attached (Att.01)
| 02SL - Stations (LUL) | Cxxx-NCR-000847 | NCR | L - Cores from RCW Adv. 6 Inv. are less than 400mm |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-12-12 | 2014-11-24 11:41 | -18 | 2014-09-02 13:46 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Not Defined | Completed |  | On 14/05/2014 NS, one set of 4 cores has been done and all cores have been broken short. Refer to the report and photos attached ( Att01.)
| 02SL - Stations (LUL) | Cxxx-NCR-000848 | NCR | L - Sealing Layer of LCE/VD4 enlargement Adv.33 was only 20mm instead of 75mm |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-11-16 | 2014-09-08 13:47 | -69 | 2014-08-18 14:04 | Civil - Tunnelling | 2000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | On 17/08/2014, at approx.1400 hrs yesterday the face at the axis approx.4mx 2m x0.4m of Adv.33 of LCE/VD4 collapsed while cleaning the invert. The sealing layer which was sprayed the night before was only 20mm instead of 75mm which is the RESS. The issue was also discussed and agreed in the SRG 17/08/2014 (see attached).
| 02SL - Stations (LUL) | Cxxx-NCR-000849 | NCR | W - EBRT-W: Missing early strength tests |  | Contr | __M |  |  | 2014-10-31 | 2014-09-01 14:30 | -60 | 2014-08-22 16:05 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | Between 12/01/14 and 23/02/14, the following advances have been sprayed in EBRT-W and tests have been missed: • EBRT-W Enlargement, Adv 8, early strength test at 1 hrs missing, later tests above J2 curve. Att01 • EBRT-W Enlargement, Adv 20, early strength test at 3 hrs missing, later tests above J2 curve. Att02 • EBRT-W Enlargement, Adv 53, early strength test missing. • EBRT-W Enlargement, Adv 74, early strength test missing. • EBRT-W Enlargement, Adv 83, early strength test at 1 & 3 hrs missing, later tests above J2 curve. Att03 • EBRT-W Enlargement, Adv 104, early strength test at 1 hrs missing, later tests above J2 curve. Att04 • EBRT-W Enlargement, Adv 107, early strength test at 1 hrs missing, later tests above J2 curve. Att05 • EBRT-W Enlargement, Adv 113, early strength test at 1 hrs missing, later tests above J2 curve. Att06 • EBRT-W Enlargement, Adv 116, early strength test at 1 hrs missing, later tests above J2 curve. Att07 • EBRT-W Enlargement, Adv 119, early strength test missing. • EBRT-W Enlargement, Adv 128, early strength test at 1 & 12 hrs missing, later tests above J2 curve. Att08
| 02SL - Stations (LUL) | Cxxx-NCR-000850 | NCR | W and L - Rebound Tests Records missing |  | Contr | __M |  |  | 2015-03-10 | 2015-01-28 16:50 | -41 | 2014-08-22 15:02 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | There was no Rebound Test carried out at - Whitechapel between the 19/10/2013 and 30/01/2014 (circa 3.5 months instead of 2 months) - Liverpool Street between the 15/11/13 and 31/03/14 (circa 4.5 months instead of 2 months) - Liverpool Street between the 31/03/14 and 21/08/14 (circa 5 months instead of 2 months)
| 02SL - Stations (LUL) | Cxxx-NCR-000851 | NCR | W - X-over EB Cavern: Regulating Layer applied before invert thickening |  | Contr | __M |  |  | 2015-10-29 | 2014-12-16 10:16 | -317 | 2014-09-09 10:18 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | • On 01/08/14 DS, in EB Cavern adv. 28, regulating layer had been placed on the primary lining where thickening layer had yet to be applied. • The existing part of the SWD consists of several layer (of P1 and P2 mix – depending if they contain rebars or not). Finally a regulating layer of P2 was sprayed on top, approx. 30mm thick.
| 02SL - Stations (LUL) | Cxxx-NCR-000852 | NCR | W - CP2 Block 10 Noth Side Wall: exposed reinforcement |  | Contr | __M |  |  | 2016-12-23 | 2017-02-21 11:07 | 60 | 2014-08-22 18:06 | Tunnelling - Linings - Sprayed Concrete | 4000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | - In PTE block 10 the sidewing reinforcement was exposed after casting (see attached photo) - When PTE Block 10 was repaired due to a bad surface it came to fruition that the cover was lower than the required 70mm as requested by the drawings.
| 02SL - Stations (LUL) | Cxxx-NCR-000853 | NCR | W - PTE-W: hollow spots and 3 different cracks found in the first layer on the secondary lining |  | Contr | __M |  |  | 2017-04-30 | 2017-03-11 13:18 | -50 | 2014-09-02 15:14 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • In PTE-W, Cracks and hollow spots in the secondary lining question the integrity of the lining and need to be recorded and repaired. • Hollow spots in SL 1st layer can be seen on the checksheet Att.03: Ch25 - Size 0.6m x 0.3m - 9 o'clock • Cracks were identified at: - CH. 22 – 35 - CH. 144 – 147.5 - Radially at CH. 122 • Hollow spot in SL 1st layer can be seen on the checksheet Att.09: Ch82 - Size 0.5m x 0.3m - 9 o'clock Ch83 - Size 2.1m x 1.5m - 2 o'clock • Two Hollow spots in SL 1st layer can be seen on the checksheet Att.10: Ch134 - 9 o'clock Ch134 - 3 o'clock • Three Hollow spots in SL 2nd layer can be seen on the checksheet Att.11: Ch140 - 3 o'clock Ch130 - 9 o'clock Ch130 - 3 o'clock
| 02SL - Stations (LUL) | Cxxx-NCR-000854 | NCR | W - EP1: Water barrier damage and protection layer crack |  | Contr | __M |  |  | 2016-07-29 | 2015-12-23 12:38 | -219 | 2014-10-13 18:07 | Tunnelling - Linings - Sprayed Concrete | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | As it can also been seen from the picture attached, the water barrier at EP1 was damaged by workmanship during the installation of the membrane. Defect has been found all along the 3m concrete block. Refer to photo EP1.jpg. Area damaged have been marked in the photo attached Barrier has been found damaged and not to be used anymore. See also email chain attached.
| 02SL - Stations (LUL) | Cxxx-NCR-000855 | NCR | W - VA5 Block 4 Invert: 2 holes at the membrane |  | Contr | __M |  |  | 2016-01-31 | 2016-01-26 13:39 | -5 | 2014-08-22 18:18 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | On 01/08/14 DS, it has been noted that 2 holes have been put in the waterproof sheet membrane of Block 4 Invert at VA5, therefore compromising the integrity of the waterproof membrane system and not meeting the 100% coverage required. See photo, att01.
| 02SL - Stations (LUL) | Cxxx-NCR-000856 | NCR | W - VA4: damaged contact grout tube |  | Contr | __M |  |  | 2016-07-29 | 2015-12-23 12:30 | -219 | 2014-08-21 18:19 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | The contact grouting tubes in VA4 Invert Block 1 were damaged; this was severed near to the lining leaving very little pipe making them unusable for contact grouting. This occured between the 17/07/14 (date of protection concrete pouring) and the 30/07/14 (date when it was discovered). See att01. picture
| 02SL - Stations (LUL) | Cxxx-NCR-000857 | NCR | W - ES1: Pipe Arch Horizontal Inclinometer damaged |  | Contr | __M |  |  | 2014-12-12 | 2014-11-21 17:11 | -21 | 2014-09-09 10:24 | Tunnelling - Linings - Sprayed Concrete | 1100 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | • On 02/08/14, it has been noted that the Pipe Arch Horizontal Inclinometer IPI installed in ES1 was not fully functioning. Data cables of the sensors Cxxx-IE501201a and Cxxx-IE501201f have been damaged. (see att01. and att02.) • Construction team commencing the breakout work despite defective instrument.
| 02SL - Stations (LUL) | Cxxx-NCR-000858 | NCR | L - VD1: Fibres not covered by regulating layer |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-11-28 | 2014-10-11 10:59 | -48 | 2014-08-22 14:26 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • On 19/07/14 NS, Regulating layer in VD1 Ch 0.00 to 36.00 has been sprayed. Refer to the checksheet attached ( Att01 ) • The 30/07/14, 01/08/14 and the 03/08/14 the two waterproofing layers have been applied (Att02) • After application of the waterproofing water ingress and steel fibres were found • Failure at bond between Dolly and Masterseal has been spotted Refer to the Waterproofing QA Checksheet attached for evidences ( Att03)
| 02SL - Stations (LUL) | Cxxx-NCR-000859 | NCR | W - PTE-E 1st layer Secondary Lining Ch16-23: Interruption of the spray |  | Contr | __M |  |  | 2016-05-27 | 2016-05-11 16:09 | -16 | 2014-08-22 14:07 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Equipment Breakdown | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | On 28/05 DS, interruption at the start of the spraying at PTE-E, 1st Layer of Secondary Lining Ch16-23, resulted in an incomplete build-up of that section of lining. Only 3m above side walls(right and left side) and not along the hole circumferential. See pictures in att01 and 02.
| 02SL - Stations (LUL) | Cxxx-NCR-000860 | NCR | W - Incorrect levels of concrete invert at CP2 north invert slab block 1 |  | Contr | __M |  |  | 2014-10-31 | 2014-09-22 12:44 | -39 | 2014-08-28 15:18 | Tunnelling - Linings - In-situ Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | On 25/08/14 NS, at CP2 north invert slab block 1, the design level was specified as 84.929, the pour has been measured to be above this level between the levels of 85.01298 up to 85.04289. Therefore these levels are on average over 100mm above the required level. See att01.photos identifying the levels marked out by the beamer and att02. as-built of CP2-North
| 02SL - Stations (LUL) | Cxxx-NCR-000861 | NCR | W - Installation of wooden boxes to cover wet patches damaged waterproofing membrane at PTE-W |  | Contr | __M |  |  | 2016-09-30 | 2016-10-10 10:42 | 10 | 2014-08-26 17:35 | Tunnelling - Tunnelling General | 4000 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | On 22/08/14 DS, 2 boxes have been installed to cover wet patches in PTE-W, at ch.57 (repairs a2/a3). To put these boxes in place bolts have been used (4 bolts d20 and 100 mm long), drilling throught the MasterSeal Membrane and potentially damaged it.(See attached photos)
| 02SL - Stations (LUL) | Cxxx-NCR-000862 | NCR | L - NLL Opening Set in CP 4/203: Short bars in the lintel beam |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-01-17 | 2014-12-09 15:19 | -39 | 2014-11-18 10:09 | Tunnelling - Tunnelling General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Other | Completed |  | Length of fabricated reinforcement bars with couplers are to be in accordance with the schedule on the design drawing
| 02SL - Stations (LUL) | Cxxx-NCR-000863 | NCR | L - PTE-E/CP10 Enl. and PTE-W/CP2: Breakout process not as per RESS |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-10-31 | 2014-09-08 13:51 | -53 | 2014-09-02 17:10 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | 1. On 18/08/14 NS, PTE-E/CP10 breakthrough enlargement work was carried out with a diversion from the RESS. The Break-out was completed in one single stage. ‘L’ bars were not installed until Adv. 10 was completed. 2. On 28/08/14 NS, PTE-W/CP2 breakthrough enlargement work was carried out with a diversion from the RESS. Adv. 10 and 11 were broken out in one go and L-bars were installed after Adv. 13.
| 02SL - Stations (LUL) | Cxxx-NCR-000864 | NCR | L - CH5/CP2: poor quality of Adv 4 and exposure of 5 L-bars |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-10-24 | 2014-10-08 15:58 | -16 | 2014-08-29 11:58 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Supervision - Insufficient supervision | Completed |  | • On 24/08/14 DS, Advance 4 of CH5/CP2 Enlargement has been sprayed. • After the spray, hammer testing has been done on the left hand side and voids have been found. • On 25/08/14 NS, during the remedial works of Advance 4, 5 L-bars were exposed on the right hand side.
| 02SL - Stations (LUL) | Cxxx-NCR-000865 | NCR | L - PTW-E/CP9 Enl: Over breaking and rebar exposed |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-02-02 | 2015-01-12 15:50 | -21 | 2014-08-28 11:54 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Supervision - Other | Completed |  | Thickening works have been done between June and July 2014 1) - On 25/08/14 NS, during the breakout of CP9 Enlargement from PTW-East some over breaking occurred. - The road header caught one of the reinforcement bars and exposed two others. Refer also to the photos for evidence of rebar exposed (Att02 ) 2) - The over-trimming also caused some of the thickening final bulkout to be broken away which has now caused a void in the thickening and hollow sounds can be heard when hammer-tapping. - The location of this hollow area is shown in the attached sketch (Att01) between the three points
| 02SL - Stations (LUL) | Cxxx-NCR-000866 | NCR | L - VD4 Enl Adv 30 RK: Non conforming Cores CR1943 - major voids |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-12-19 | 2014-10-15 12:37 | -65 | 2014-08-29 09:53 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | VD4 Enlargement Adv 30 has been sprayed on 12/08/14 NS and cored on 23/08/14 DS. The Cores CR1943 were reviewed and the followings imperfections were found: o Major voids for cores #1 and #4 o Core broken o ACI grade 4 for cores #1 and #4 See cores report attached (att01.)
| 02SL - Stations (LUL) | Cxxx-NCR-000867 | NCR | W - ES1-EPW1 profiles: insufficient thicknesses on the installation of ES1 excavator location/crown |  | Contr | __M |  |  | 2015-05-01 | 2014-12-17 15:58 | -135 | 2014-10-13 19:11 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Because of interface between SCL reality and designed temporary works, the far face reinforcement was installed to +0mm (i.e. to design) to coincide with the set-out hanging tubes in EPW1. The sprayed layers of SCL and the near face reinforcement were then installed to +70mm which reduced the depth between reinforcement layers to 150mm. In addition the thickened lining was sprayed thin in a number of areas giving the thickness of 250mm instead of 300mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000868 | NCR | L - RCE: Water bar installed at the wrong level |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-05-29 | 2015-01-23 17:07 | -126 | 2014-09-02 14:14 | Tunnelling - Linings - Sprayed Concrete | 4000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | On 27/08/14 NS, water bars have been found in the wrong location in RCE Refer to the photo attached for evidence ( Att01)
| 02SL - Stations (LUL) | Cxxx-NCR-000869 | NCR | W - PTW-E: Hollow spot the second layer on the secondary lining |  | Contr | __M |  |  | 2016-12-16 | 2015-12-23 12:25 | -359 | 2014-08-29 14:46 | Tunnelling - Linings - Sprayed Concrete | 6000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • In PTW-E, Hollow spots have been found during hammer tapping, in the second layer on the secondary lining. Hollow spots question the integrity of the lining and need to be recorded and repaired. Chainage, location and date when hollow spots has been found can be seen in Att.02 • Hollow spots checksheets are in Att.01
| 02SL - Stations (LUL) | Cxxx-NCR-000870 | NCR | L - VD2: Waterproofing sheet membrane installed wrongly |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-02-27 | 2015-01-23 17:02 | -35 | 2014-09-22 13:25 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | 1) VD2 requires a fully sprayed waterproof lining, including in the invert. __ have installed a sheet membrane in the invert and in the sidewalls of VD2 instead of a spray applied membrane. 2) IFC drawing issued after the works
| 02SL - Stations (LUL) | Cxxx-NCR-000871 | NCR | L - VD1 CH18-36 Inv: Masterseal application without required supervision |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-03-01 | 2015-01-23 17:12 | -37 | 2014-09-02 13:40 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not trained for the work being performed | Completed |  | • On 29/08/14 DS, the Masterseal application in the invert from VD1 (36 to 18 ) has been done without any engineer supervision. • The required tests before and during the application are missing
| 02SL - Stations (LUL) | Cxxx-NCR-000872 | NCR | L - May 2014: Strength failure on the running mean strength |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-12-19 | 2014-09-18 12:24 | -92 | 2014-09-10 11:30 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | 90 days samples taken between 01/05 and 14/05 comply with criterion 1 but failed to comply with criterion 2 due to increase of standard deviation that has caused failures on the running mean results with failure range between 0.2 - 1.0N/mm². Effected samples are highlighted on attached summary.
| 02SL - Stations (LUL) | Cxxx-NCR-000873 | NCR | L - VD1 Inv: Masterseal 345 damaged during repair works |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-05-15 | 2015-04-27 15:14 | -18 | 2014-09-02 14:02 | Tunnelling - Linings - Sprayed Concrete | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | On 01/09/14 DS, the MS 345 in the invert of VD1 has been found damaged during the on-going repair works Refer to the photo attached ( Att01. ) for evidence
| 02SL - Stations (LUL) | Cxxx-NCR-000874 | NCR | L - CH5/CP2 Breakout Enlarg: U-bars exposed on RHS and adv2 over-excavated |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-10-31 | 2014-09-23 13:44 | -38 | 2014-09-03 17:27 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On 23/08/14 NS, during CH5/CP2 Enlargement: • U bars on right hand side were exposed, • Advance 2 has been over-excavated into advance 3.
| 02SL - Stations (LUL) | Cxxx-NCR-000875 | NCR | L - CH5/CP2 Breakout Enlarg Adv 3: No continuity reinforcement installed |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-10-31 | 2014-09-19 12:45 | -42 | 2014-09-03 17:32 | Tunnelling - Linings - Sprayed Concrete | 2000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | On 23/08/14 NS, During CP2 Adv 3 works, continuity reinforcement had not been installed in top heading
| 02SL - Stations (LUL) | Cxxx-NCR-000876 | NCR | L - PTE-E: over trimming of hollow areas |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-10-30 | 2015-07-17 09:46 | -105 | 2014-09-02 16:35 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On 28/08/14 NS, in PTE-E, trimming was undertaken after identification of hollow areas. 3 proof drillings after trimming have been done and they all show under thickness in the crown • 350mm in Ch42.3, • 300mm in Ch35.7, • 330mm in Ch35.7 and • 350mm in Ch37.5 Refer to the proof drillings attached (Att01.) • The 3d scan attached ( Att02.) shown that the thickness was enough before the trimming
| 02SL - Stations (LUL) | Cxxx-NCR-000877 | NCR | L - PTE-W/CP4a Thickening: overspray of 1st bulking out layer |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-12-12 | 2014-10-31 08:43 | -42 | 2014-09-15 10:36 | Tunnelling - Linings - Sprayed Concrete | 2000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | • On 29/08/14 NS: First layer of the PTE-W/CP4a Thicknening has been partially sprayed - approximately 3 /4 of the layer. • During following shift (30/08/14 DS), entire 150 mm layer has been sprayed in addition to already sprayed layer.
| 02SL - Stations (LUL) | Cxxx-NCR-000878 | NCR | L - AP7-W Enl. Adv 12 Inv, AP7-E Adv65(pilot), Adv6 Enl and PTW-W Adv. 8 Enl.: No face log completed |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-10-31 | 2014-10-03 10:14 | -28 | 2014-09-03 12:04 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | • On 20/02/13, in AP7-W Enl., no facelog has been completed for Advance 12 Invert of AP7 West Enlargement. Face logs & photos for Advance 12 Top Heading, Adv 11 , Adv 13 all present showing London Clay or Lambeth Group. Photo of Adv 11 Invert has also been produced. • On 03/13, in AP7-E Enl. Advance 6 and Pilot Advance 65, no facelog have been completed and photos taken. Face logs & photos for previous and after advances are all present showing London Clay or Lambeth Group. • On 10/09/13, in PTW-W Enl., no facelog has been completed for Advance 8. Face logs & photos for Advances 7 and 9 all present showing London Clay or Lambeth Group.
| 02SL - Stations (LUL) | Cxxx-NCR-000879 | NCR | W - SWD North & South: Missing early strength tests |  | Contr | __M |  |  | 2014-10-31 | 2014-09-11 14:51 | -50 | 2014-09-03 18:13 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | Between 12/11/13 and 15/01/14, the following advances have been sprayed in Side Wall Drift Top Headings Norht & South and tests have been missed: • SWD North TH, Adv 5, early strength test at 3 hrs missing, later tests above J2 curve. • SWD North TH, Adv 10, early strength test at 3 hrs missing, later tests above J2 curve. • SWD North TH, Adv 15, early strength test at 1 hrs missing, later tests above J2 curve. • SWD North TH, Adv 20, early strength test at 3 hrs missing, later tests above J2 curve. • SWD North TH, Adv 23, early strength test at 1 hrs missing, later tests above J2 curve. • SWD North TH, Adv 25, early strength test missed. Panel taken at adv 26. • SWD North TH, Adv 30, early strength test at 3 hrs missing, later tests above J2 curve. • SWD South TH, Adv 5, early strength test at 3 hrs missing, later tests above J2 curve. • SWD South TH, Adv 10, early strength test at 1 hrs missing, later tests above J2 curve. • SWD South TH, Adv 25, early strength test at 3 hrs missing, later tests above J2 curve. • SWD South TH, Adv 30, early strength test at 6 hrs missing, later tests above J2 curve. • SWD North Invert Adv 10, early strength test at 1 hrs missing, later tests above J2 curve. • SWD North Invert Adv 15, early strength test at 3 hrs missing, later tests above J2 curve. • SWD North Invert Adv 20, early strength test at 1 hrs missing, later tests above J2 curve. • SWD North Invert Adv 25, early strength test missing, panel taken on Adv 26 • SWD North Invert Adv 33, early strength test at 1 hrs missing, later tests above J2 curve. • SWD South Invert Adv 5, early strength test at 1,3,6 & 12 hrs missing. • SWD South Invert Adv 10, early strength test at 12 hrs missing, later tests above J2 curve. • SWD South Invert Adv 19, early strength test at 1 hrs missing, later tests above J2 curve. • SWD South Invert Adv 20, early strength test missing. Panel taken on Adv 19 • SWD South Invert Adv 33, early strength test at 1 & 3 hrs missing, later tests above J2 curve.
| 02SL - Stations (LUL) | Cxxx-NCR-000880 | NCR | L - PTW Block 10: Underthickness lining found after scabbling |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-01-31 | 2015-01-19 13:04 | -12 | 2014-09-15 11:04 | Tunnelling - Linings - Sprayed Concrete | 2000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Verification Problems - Not Defined | Completed |  | • On 03/09/14 DS, in PTW Block 10 not all the proof dillings have been carried out pre-scabbling • Proof drilling post-scabbling in Block 10/11 show underthickness lining in the crown (260mm instead of 400mm). Refer to the attached proof drilling post-scabbling (Att01.) and the location of the proof drillings (Photo Att02.).
| 02SL - Stations (LUL) | Cxxx-NCR-000881 | NCR | L - PTE-WCP4 : U-bars exposed and damaged |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-06-01 | 2014-12-11 13:03 | -172 | 2014-09-09 09:21 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On 05/09/14 NS, during preparation of joint in CP4 around the eye U-bars in the left and right side have been exposed. • On the left hand side, bottom of U-bar reinforcement were knocked out. • On the right hand side, surface of U-bar has been exposed but not damaged. • U-bars concerned are 4c of FF2. Refer to the Attachment 1 for photos of the exposed rebars in RHS and Attachment 2 for the LHS ones
| 02SL - Stations (LUL) | Cxxx-NCR-000882 | NCR | L - VD1 Enl adv 17, 19, 23 and 24: Missing Tests and Beamer Records |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-10-31 | 2014-10-14 10:48 | -17 | 2014-09-09 08:54 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | - On 01/06/14 and 02/06/14, no Beamer Lining Profiles have been recorded for VD1 Adv 17 and Adv 19, however Excavation Profiles have been recoreded and show conforming excavation (see att05 and 06). - On 04/06/14 DS, no flow tests have been done for VD1 Adv 23 and Adv 24. - On 04/06/14 DS, early strength test at 6 hrs is missing for Adv 23, later tests are above J2 curve.
| 02SL - Stations (LUL) | Cxxx-NCR-000883 | NCR | W - WHI July Sprayed test beams: Low Residual Flexural strength |  | Contr | __M |  |  | 2016-02-29 | 2016-01-27 13:36 | -33 | 2014-09-09 15:10 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | WHI July sprayed beam set, CR1872, has been sprayed on 30/07/14 (6 Beams of Mix P1 C32/40 35kg) for July Monthly Test. Sprayed beam CR1872C has achieved a D3 result of S1.1 at 28 days (lower than specified individual result S1.26). Average result for whole set fall out of specified level S1.4 to S1.3.
| 02SL - Stations (LUL) | Cxxx-NCR-000884 | NCR | W - May and June 2014: Strength failure on the running mean strength |  | Contr | __M |  |  | 2015-02-26 | 2015-02-12 10:38 | -14 | 2014-09-10 11:17 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | 90 days samples CR1610 (date of spray 05/05/14, VA5 Enlargement Left Shoulder) with result of 35 N/mm2 and CR1705 (date of spray 02/06/14, LCW Adv 5 Left Invert) with result of 34.7 N/mm2 failed to comply with criterion 1 which leads to increase the standard deviation that has caused failures on the running mean results with failure range between 0.2 - 3.0N/mm². Effected samples are highlighted on attached summary.
| 02SL - Stations (LUL) | Cxxx-NCR-000885 | NCR | W - July and August 2014: Strength failure on the running mean strength |  | Contr | __M |  |  | 2015-02-26 | 2015-02-03 08:16 | -23 | 2014-09-10 11:23 | Tunnelling - Linings - In-situ Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Even though all the 28 day results comply with criterion 1 given above, few lower than normal 28 day results for samples taken between 21/07 till 02/08 has resulted in fifteen results failing criterion 2 in range between 0.1 - 1.3N/mm².
| 02SL - Stations (LUL) | Cxxx-NCR-000886 | NCR | L - PTW-W/CP3a: L-Bars damaged during scabbling works |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-12-12 | 2014-11-24 11:43 | -18 | 2014-09-16 09:48 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • Between 10/09 NS and 12/09/14 DS, during scabbling works in PTW-W/CP3a thickening L-bars were damaged. Refer to the drawing attached (Att01) for the location of the L-bars damaged. • After investigation: it has been spotted that 40 to 50 L-bars were damaged. 3 in the 9o’clock and the rest between 11 and 3o’clock and some of the legs were salvaged Refer to the photo attached (Att02) • The 14/09/14 NS: During scabbling works at the junction Ch1-1-CP3a L-bars have been exposed and damaged. 10 to 15 L-bars in the crown have been hit - Refer to the photo Att2a for evidence
| 02SL - Stations (LUL) | Cxxx-NCR-000887 | NCR | W and L - No face log completed or photograph taken (July, September and October 2013) |  | Contr | __M |  |  | 2014-11-28 | 2014-10-29 13:48 | -30 | 2014-09-15 09:54 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | On compiling and submitting Geological Factual Reports, it has become evident that some face log photographs have been duplicated and missing face logs. Liverpool Street – Works Completed in September 2013 • PTE W (LCE) Pilot tunnel Advance 79 – Missing photograph • PTW – W Enlargement Advance 13 – Missing Photograph Whitechapel Works Completed in July 2013 • PTE – W Enlargement Advance 181 – Missing photograph. • PTW – W Enlargement Advance 241 – Missing photograph. Works Completed in October 2013 • EP1 Enlargement Advance 8 – Missing log and photograph. • Bypass Tunnel Enlargement Advance 36 – Missing photograph.
| 02SL - Stations (LUL) | Cxxx-NCR-000888 | NCR | W - PTE-W Ch 10-30: shadowing behind profile bars on second layer of secondary lining |  | Contr | __M |  |  | 2016-07-29 | 2016-06-28 14:47 | -31 | 2014-12-09 10:19 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | As it can be seen from the attached pictures, there is possible shadowing behind the profile bars of the two layers of the secondary lining at PTE-W Ch.10-30.
| 02SL - Stations (LUL) | Cxxx-NCR-000889 | NCR | W - EPW1: Mild shadowing behind hanging threaded tubes |  | Contr | __M |  |  | 2015-01-03 | 2014-12-18 16:39 | -16 | 2014-09-25 17:22 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Some slight shadowing (maximum depth 30mm) behind 4 of the sprayed in hangers on the left hand side of ES1 was found as a result of spraying. The lining in this area (the upwards section of the “working area”) is considered to be to full design thickness with the reinforcement installed as design. Load tests were carried out on such hangers as per the testing plan with all hangers passing the full test loading of 6No. Tonnes. Nonetheless after the load testing it was deemed beneficial to fill these small areas to ensure lining continuity.See attached Photos and Permit to Load.
| 02SL - Stations (LUL) | Cxxx-NCR-000890 | NCR | L - VD4: Coring through waterproofing membrane |  | Contr | __M |  |  | 2016-06-24 | 2016-05-09 10:44 | -46 | 2014-10-03 11:29 | Tunnelling - Linings - Sprayed Concrete | 50000 |  | Damaged | Repair | 2 (6-60k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Under PMI-00702 and PMI-00708 __ has been instructed to core from VD4 and breakthrough into the Moorhouse Shaft on the coordinates attached. The cores taken, perforated the waterproofing membrane installed by Cxxx.
| 02SL - Stations (LUL) | Cxxx-NCR-000891 | NCR | W - X-over EB Cavern: NF LHS bars damaged during enlargement from EB Cavern |  | Contr | __M |  |  | 2015-05-01 | 2014-12-16 10:58 | -136 | 2014-10-13 19:18 | Tunnelling - Linings - Sprayed Concrete | 3500 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | XOV Connection - NF LHS bars damaged during enlargement from EB cavern as shown in the pictures attached.
| 02SL - Stations (LUL) | Cxxx-NCR-000892 | NCR | L - Some areas of the Sprayed Waterproofing Membrane at VD1 will be left exposed for more than 3 Weeks |  | Contr | __M |  |  | 2015-10-30 | 2015-02-09 13:58 | -263 | 2014-09-25 12:09 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | At the connection detail of the end of VD1 (about 1m inside VD1 - connection with RCW2), the sprayed waterproofing membrane will be left exposed for more than 3 weeks. As per RFI-00699 the issue is currently unavoidable.
| 02SL - Stations (LUL) | Cxxx-NCR-000893 | NCR | L - CP4 and CP4a From PTE-W Thickening: Non conforming Cores CR1980, CR1982 and CR1984 – bad encapsulation and voids |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-12-04 | 2014-10-20 10:56 | -45 | 2014-09-18 10:31 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Thickening in PTE-W/CP4a has been sprayed between the 15/08/14 and the 11/09/14. Thickening in PTE-W/CP4 has been sprayed between the 09/08/14 and the 12/09/14. The 13/09/14 NS: one core has been taken in the RK ( CR1980) of the CP4a eye from PTE-W Thickening. Core has been review the 16/09/14 and a 20mm voids has been spotted. During the 16/09/14 SRG meeting it has been decided that a NCR will be raised and the core report sent to __ Designer ( UnPS ) for review. See core report attached (att01.) The 13/09/14 NS: two cores have been taken, one in the LK ( CR1982 )and the other in the RS ( CR1984) of the CP4 eye from PTE-W Thickening. Cores have been review the 16/09/14 and voids / honeycombing have been spotted. During the 16/09/14 SRG meeting it has been decided that a NCR will be raised and the core reports sent to __ Designer ( UnPS ) for review. See cores report attached (att02.)
| 02SL - Stations (LUL) | Cxxx-NCR-000894 | NCR | W - EPW1 PL: Missing Test and documentation |  | Contr | __M |  |  | 2017-04-29 | 2017-03-02 14:05 | -58 | 2016-11-15 17:05 | Architectural - Landscape Architectural | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | • Cxxx-__M-C4-LLG-D061-50182 Deliverable Records for EPW1-W Primary Lining Thickening: 1) Crown Thickening - ITP Items C5, C6, 1.3, 5.1, 5.2, 5.3, 5.5, 5.6, 5.7 and 5.11. - Crown Thickening Mix P2 1st layer Ch. 16m to 22m – No Shotcrete Placement Checksheet (__ Form D3-72) - Crown Thickening Mix P2 2nd layer Ch. 11m to 16m – No Shotcrete Placement Checksheet (__ Form D3-72) 2) Invert Thickening - ITP Items C3, C5, C6, 1.3, 5.1, 5.2, 5.5, 5.6 and 5.7 - Invert Thickening Mix P1 Ch. 11m to 19m – No Shotcrete Placement Checksheet (__ Form D3-37)
| 02SL - Stations (LUL) | Cxxx-NCR-000895 | NCR | L - VD2: Incorrect installation of Waterproofing |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-03-27 | 2015-02-01 16:58 | -54 | 2014-09-17 15:29 | Tunnelling - Tunnelling General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | The 18/08/2014: Installation of the sheet waterproofing membrane in VD2 invert has started using the approved IFC drawing C02. In this drawing (Att02.) the limit between the sheet membrane and the sprayed waterproofing was uncleared and the sheet membrane has been installed all through the VD2 invert instead of a mix spray applied membrane / sheet membrane.
| 02SL - Stations (LUL) | Cxxx-NCR-000896 | NCR | W - NonConforming Cores CR1992 and CR1988 of EB Cavern HeadWalls |  | Contr | __M |  |  | 2015-10-01 | 2015-04-13 16:02 | -171 | 2014-09-17 17:11 | Tunnelling - Tunnelling General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Cores CR1992, CR1988 and CR1975 of EB Cavern HeadWalls have been graded with ACI = 3 > 2.5 and thus are nonconforming.
| 02SL - Stations (LUL) | Cxxx-NCR-000897 | NCR | L - CH7 Damaged L-Bars |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-01-01 | 2014-11-24 11:34 | -38 | 2014-09-19 09:28 | Tunnelling - Tunnelling General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | 17/09/14 DS: during scabbling works in CH7, L-bars were damaged Refer to the photos attached ( Att01 and Att02 ) 04/10/14 DS: Additional L-bars in the RHS have been exposed ( Att04)
| 02SL - Stations (LUL) | Cxxx-NCR-000898 | NCR | L - VD7: Missing flows and early tests |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-01-04 | 2014-10-08 15:53 | -88 | 2014-09-22 11:35 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Issue 1 - Missed early strength tests • Adv1 & 2 – 1 & 3 hour tests missed • Adv6 – 1 hour test missed • Adv8 & 9 – 30min and 1 hour tests missed Refer to Att01. LIV - VD7 Missing early strengths Issue 2 - Missed flows: • Adv1, Adv3, Adv5, Adv6
| 02SL - Stations (LUL) | Cxxx-NCR-000899 | NCR | L - Low Residual Flexural strength of beam set CR1930 for August 2014 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-02-29 | 2015-12-14 20:22 | -77 | 2014-09-19 14:05 | Tunnelling - Tunnelling General | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | LIV Sprayed beam set CR1930 for August has achieved D3 result of S0.9 at 28 days on average. See results attached.
| 02SL - Stations (LUL) | Cxxx-NCR-000900 | NCR | W - Incorrect Mix Poured at Block CP2-N |  | Contr | __M |  |  | 2016-11-30 | 2016-11-28 14:42 | -2 | 2014-09-22 16:38 | Tunnelling - Tunnelling General | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | During the pouring of the side walls of Block 10 at CP2 - N at Whitechapel on 14/09/2014 DS the concrete that was poured was mistakenly Mix PL instead of Mix Mix Invert C32/40 35kg. Please see attached the related batched tickets for the exact quantity that was poured.
| 02SL - Stations (LUL) | Cxxx-NCR-000901 | NCR | W - East Bound Cavern XOV - Under Spray of Adv.124 |  | Contr | __M |  |  | 2015-01-18 | 2015-01-19 14:39 | 1 | 2014-10-10 17:04 | Tunnelling - Tunnelling General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | On the 05/09/2014 Adv.124 of XOV EB was undersprayed for approx. 50mm. See email chain attached. The issue was resolved by spraying additional shotcrete while spraying Adv.127 and the overall thickness is now conforming to the required 300mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000902 | NCR | W - Missed Early strength testing in Bypass tunnel. |  | Contr | __M |  |  | 2015-01-07 | 2014-10-10 13:48 | -89 | 2014-09-25 16:18 | Tunnelling - Tunnelling General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Counterfeit Items | Completed |  | • Bypass pilot tunnel, Adv 9, early strength missed • Bypass pilot tunnel, Adv 12, early strength missed • Bypass pilot tunnel, Adv 15, early strength missed • Bypass pilot tunnel, Adv 29, early strength missed • Bypass pilot tunnel, Adv 31, early strength missed • Bypass pilot tunnel, Adv 33, early strength missed • Bypass pilot tunnel, Adv 36, early strength missed
| 02SL - Stations (LUL) | Cxxx-NCR-000903 | NCR | W - Missing Primary 1 thickness ‘as-built’ records for EBRT-W Enlargement Adv 132 & 133 & 51 |  | Contr | __M |  |  | 2015-01-03 | 2014-10-16 16:25 | -79 | 2014-09-25 16:31 | Tunnelling - Tunnelling General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | • EBRT-W, adv. 132, Primary lining profiles and thicknesses not available. • EBRT-W, adv. 133, Primary lining profiles and thicknesses not available. • EBRT-W, adv. 51, Primary lining profiles and thicknesses not available.
| 02SL - Stations (LUL) | Cxxx-NCR-000904 | NCR | L - PTE-E & RCE Water bars not installed properly |  | Contr | __M |  |  | 2015-04-16 | 2015-04-08 16:55 | -8 | 2014-10-23 09:58 | Tunnelling - Tunnelling General | 2000 |  | Planning | Repair | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Water bars undertrack crossing in PTE-E Block 11 LHS and RHS and in RCE have been wrongly installed. Area concerned by the defects are all of the UTX in PTE-E Block 11 and RCE. See attached drawing with mark-ups (Att02.) It occurred throughout the installation of the waterproofing dates from: 01/09/2014 – 10/10/2014
| 02SL - Stations (LUL) | Cxxx-NCR-000905 | NCR | Low Residual Flexural strength Cast beam set CR1950 for August |  | Contr | __M |  |  | 2016-02-29 | 2016-02-02 15:35 | -27 | 2014-09-26 12:01 | Tunnelling - Tunnelling General | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | WHI Cast beam set CR1950 for August has achieved D3 result of beam A - S1.1 at 28 days with average for whole set S1.4 instead of class D1 S1.8 D3 S1.4 at 28 days. See attached results.
| 02SL - Stations (LUL) | Cxxx-NCR-000906 | NCR | L - CP4/CH1-2 rebars exposed during Enl. breakout |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-01-16 | 2014-12-15 10:50 | -32 | 2014-09-30 14:25 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | • The 27/09/14 NS: During CP4 Enlargement breakout 1 horizontal bar NF (B20-12-150 ) has been broken at coupler level and 12 vertical bars FF ( B20-10-150-FF1) bent at the bottom Refer to the drawing Att01, photos Att02 and beamer profiles Att03 for more details.
| 02SL - Stations (LUL) | Cxxx-NCR-000907 | NCR | L - LCWb: Application of TSL 865 without paperwork and prior inspection |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-06-01 | 2015-01-19 17:39 | -133 | 2014-09-30 16:24 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The 22/09/14 DS and NS: application of TSL 865 in LCWb has been done prior inspection and without paperwork.
| 02SL - Stations (LUL) | Cxxx-NCR-000908 | NCR | L - VD1: Repair works done with heater/dryer |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-06-01 | 2015-01-23 17:06 | -129 | 2014-10-01 10:31 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not trained for the work being performed | Completed |  | The 30/09/14 DS: Two layers of MS 345 repair works were cured with the help from heater / dryer which causes the MS 345 to cure quicker. Refer to the photo attached (Att01.)
| 02SL - Stations (LUL) | Cxxx-NCR-000909 | NCR | L - VD1 Hollow spots in secondary lining 1st layer |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-10-04 | 2015-01-23 17:03 | -254 | 2014-10-02 09:13 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The 30/09/14 DS: During hammer tests in VD1, 4 areas with bonding layers have been spotted in the invert. A=0.32m2 B=0.18m2 C=0.30m2 D=0.24m2 Refer to the Hamer testing Checksheet (Att01) and Photos (Att02) for evidence.
| 02SL - Stations (LUL) | Cxxx-NCR-000910 | NCR | L - VD1: Over-drilling and wrong bolts used |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-06-01 | 2015-01-22 13:49 | -130 | 2014-10-02 10:21 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The 22/09/14 DS: Normal drill bit with marking has been used. These holes were drilled to a maximum of 70mm. (Att01) The 29/09/14 DS: During the visit in VD1 it came apparent that the drills being used for fixing the bagging are much longer then the ones mentioned in the WMS.
| 02SL - Stations (LUL) | Cxxx-NCR-000911 | NCR | Face Logs, Photographs and probe logs not completed during excavation |  | Contr | __M |  |  | 2015-04-28 | 2014-11-03 09:19 | -176 | 2014-10-10 15:47 | Tunnelling - Tunnelling General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | - During excavation of Tunnels at both sites Engineers have no completed a either a face or probe log, nor taken a photograph of the face. - This has happened during the excavation of the works from initial excavation - The list is significant as all factual reports have been reviewed and missing information identified. For a complete list of what is missing please see attachment.
| 02SL - Stations (LUL) | Cxxx-NCR-000912 | NCR | L - AP1: Voids in primary lining thickening |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-01-30 | 2014-12-04 15:53 | -57 | 2014-10-03 14:05 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The 26/09/14 DS: During snagging works in AP1 Thickening, construction team found two vvoids above CH7 eye. Voids are located at 120 mm depth in NF2 reinforcement area and are 20mm thick. Refer to the Photo (Att01) and Survey (Att02) for more information
| 02SL - Stations (LUL) | Cxxx-NCR-000913 | NCR | L - Low Residual Flexural strength of beam set CR1976 for September 2014 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-02-29 | 2015-12-14 20:23 | -77 | 2014-10-09 12:09 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | LIV spray beam set CR1976 from September has achieved too low individual D3 result of beam A - S1.1 at 28 days with average for set of three beams - S1.6, Additional beam D tested - with D3 - S2.0 whole set average S1.7 Refer to the tests results attached ( Att01)
| 02SL - Stations (LUL) | Cxxx-NCR-000914 | NCR | L - VD1 stop end: Non-conforming rib |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-10-30 | 2015-10-27 14:36 | -3 | 2014-10-09 11:39 | Tunnelling - Linings - Sprayed Concrete | 7000 |  | Supervision/Management | Repair | 2 (6-60k) | Complete | Supervision - Insufficient supervision | Completed |  | The 30/09/14 DS: The rib stop end was meant to be sprayed in VD1 at CH 34.341 (blomfield boxside) completely around the circumference of the tunnel in order to create a connection for the next contractor to connect the secondary lining to. The rib stop end hasn't been sprayed as agreed with CRL/Cxxx and was not cut back and also covered with masterseal therefore losing the overlap connection for the waterproofing. Location of the NCR can be seen in Att.13
| 02SL - Stations (LUL) | Cxxx-NCR-000915 | NCR | W - Nonconforming Beamer Thickness Profile of Adv. 23 of Bypass Tunnel |  | Contr | __M |  |  | 2016-05-31 | 2016-05-05 10:13 | -26 | 2014-10-13 18:45 | Tunnelling - Tunnelling General | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | As it can be seen from the attached Beamer print-out, the thickness of Adv. 23 of the Bypass Tunnel Enlargement is less than 400mm as required by the RESS.
| 02SL - Stations (LUL) | Cxxx-NCR-000916 | NCR | W - PTE-E ch70-100 __ Sprayed Waterproofing Membrane Areas will be left exposed for more than 3 Weeks |  | Contr | __M |  |  | 2016-05-27 | 2016-05-05 10:09 | -22 | 2014-10-13 19:01 | Tunnelling - Tunnelling General | 36000 |  | Incomplete Works | Repair | 2 (6-60k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | There are some areas on PTE-W where the __ sprayed membrane have been left exposed for more than 3 weeks. See attached sketch and photos. Area concerned are between chainage 70-100. Spraying occured in March/April 2014
| 02SL - Stations (LUL) | Cxxx-NCR-000917 | NCR | L - VD1 Profile bars not fully covered |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-12-18 | 2015-10-27 14:18 | -52 | 2014-10-14 10:01 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The 06/10/14 NS: During spray of the secondary lining layer 2 in VD1. Profile bars were not fully covered. Refer to the photos attached.
| 02SL - Stations (LUL) | Cxxx-NCR-000918 | NCR | L - VD1 Hollow spots in Secondary lining |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-06-26 | 2015-02-16 10:47 | -130 | 2014-10-14 10:23 | Tunnelling - Linings - Sprayed Concrete | 3500 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | The 09/10/14 DS: During trimming works in VD1 an hollow spot area of 600x900mm at Chainage 11m has been spotted. Refer to the photo (Att01) and SL placement checksheet (Att02.) for evidence.
| 02SL - Stations (LUL) | Cxxx-NCR-000919 | NCR | L - RCE: Water bars not installed properly |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-03-03 | 2015-02-12 14:12 | -19 | 2014-10-16 12:39 | Tunnelling - Tunnelling General | 4000 |  | Supervision/Management | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | The 09/10/14 DS: Water bars have been wrongly installed in Block 4 RCE
| 02SL - Stations (LUL) | Cxxx-NCR-000920 | NCR | W - EBCAV: Hollow spots in primary lining |  | Contr | __M |  |  | 2016-09-23 | 2016-06-13 11:12 | -102 | 2014-10-15 10:39 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After hammer tapping the SCL primary lining areas with hollow sound and possible voids have been identified ( Refer to Att.01 for the EBCAV hollow spots tracker ) • On 28/01/16: Two hollow spots have been found in EBCAV Ch 126-127 crown ( max 0.9 x 0.4 m ) - Refer to Att.02 for the hammer tapping checksheet • On 28/01/16: Three hollow spots have been found in Ch 113 ( max 1.5 x. 0.8 m ) - Refer to Att.03 for the hammer tapping checksheet • On 24/01/16: Five hollow spots have been found in EBCAV Ch 175-178 crown, max 2.0 x 1.0 m - Refer to Att.04 for the hammer tapping checksheet • On 18/02/16: One hollow spot has been found in the EBCAV Ch 176 invert - Refer to Att.05 for the hammer tapping checksheet • On 25/01/16: Three hollow spots have been found in EBCAV Ch 143-146 crown, max 1.8 x 1.1 m - Refer to Att.06 for the hammer tapping checksheet
| 02SL - Stations (LUL) | Cxxx-NCR-000921 | NCR | L - LCWb: Waterproofing termination raised without agreement |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-04-16 | 2015-04-14 14:47 | -2 | 2014-10-16 14:10 | Tunnelling - Linings - In-situ Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | The 13/10/14 DS: Locally raised termination in LCWb has been done without any agreement. ( Att01) Refer to the excat location of the addtional waterprooifing (Att02) After investigation this solution has been decided to cover a damp area (Att02)
| 02SL - Stations (LUL) | Cxxx-NCR-000922 | NCR | W - LCE & VA5 - Missing Early Strength Tests |  | Contr | __M |  |  | 2015-01-24 | 2014-10-22 14:34 | -94 | 2014-10-16 14:13 | Tunnelling - Tunnelling General | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | • LCE Enlargement, Adv 233, early strength test at 12 hrs missing, later tests above J2 curve (Also 30mins test taken at 40mins and becasue there was a spreadhseet error at 30mins) • LCE Enlargement, Adv 236, early strength test at 1, 6 & 12 hrs missing, later tests above J2 curve. • LCE Enlargement, Adv 239, early strength test missing at 1, 3 & 6 hrs, later tests above J2 curve. • LCE Enlargement, Adv 269, 0.5 N/mm2 early strength requirements at 1hr was not met. Later tests above J2 curve. • LCE Enlargement, Adv 272/273, early strength test at 1 & 6 hrs missing, later tests above J2 curve. • LCE Enlargement, Adv 242 early strength test missed. • LCE Enlargement, Adv 260 1hr early strength test missed.Later Tests ok. • VA5 Adv.18 Missing tests at 1hr and 6hr but later tests and long term strength all conforming.
| 02SL - Stations (LUL) | Cxxx-NCR-000923 | NCR | L - VD1 Enl adv 11, 22, 23, 24: Missing Tests and Beamer Records |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-12-19 | 2014-12-11 10:58 | -8 | 2014-10-16 15:08 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | - On 30/05/14 DS, early strength test at 1 hrs is missing for Adv 11 - On 04/06/14: Beamer Lining Profiles show missing RHS datas for VD1 Enl Adv 22 (Att02). - On 05/06/14: Beamer Lining Profiles show missing crown datas for VD1 Enl Adv 23 (Att03). - On 05/06/14: Beamer Lining Profiles show missing crown datas for VD1 Enl Adv 24 (Att04).
| 02SL - Stations (LUL) | Cxxx-NCR-000924 | NCR | W - September: Low Residual Flexural strength - CR1994 |  | Contr | __M |  |  | 2016-02-29 | 2016-01-27 13:56 | -33 | 2014-10-23 17:25 | Tunnelling - Tunnelling General | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | WHI spray beam set CR1994 from September has achieved too low individual D3 results of beam A - S1.0, B – S1.3, C – S0.9 at 28 days with average for set of three beams - S1.1
| 02SL - Stations (LUL) | Cxxx-NCR-000925 | NCR | W - LCW missed early strengths |  | Contr | __M |  |  | 2015-01-25 | 2014-10-30 12:53 | -87 | 2014-10-17 11:22 | Tunnelling - Tunnelling General | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | Missed Early strength tests as per attached (self explanatory) checksheets at LCW primary lining.
| 02SL - Stations (LUL) | Cxxx-NCR-000926 | NCR | W - LCE Enl. Adv 264: Missing Excavation Beamer Profile |  | Contr | __M |  |  | 2015-01-11 | 2014-10-23 17:39 | -80 | 2014-10-23 11:11 | Tunnelling - Tunnelling General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The Beamer Excavation Profiles for LCE Enl. Adv 264 are missing. The issue was identified during the preparation of the certification package of LCE Primary Lining W003.
| 02SL - Stations (LUL) | Cxxx-NCR-000927 | NCR | L - VD1: Secondary lining underthickness |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-12-18 | 2015-09-15 17:40 | -94 | 2014-10-23 11:19 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The 12/10/14: Profiles thickness ( Att01 and Att02 ) have been gernerate and show in Chainage 30, 31, 32 some areas are 180mm instead of 200 mm and in Chainage 33.5 the thickness is in some areas 170 mm. Since the occurrence on the 17/10/2014 additional shotcrete was sprayed to remediate the underthickness, see placement check sheet attached (Att.04). It can be seen that there are still areas of under thickness, but only 10mm shy (190mm thick) on the required 200mm. These 10mm shy areas should be made up in the fireproofing. See new scans (Att.05+Att.06)
| 02SL - Stations (LUL) | Cxxx-NCR-000928 | NCR | W - TBM Rails installation out of tolerances in many locations |  | Contr | __M |  |  | 2015-06-20 | 2015-03-30 18:53 | -82 | 2014-12-02 10:14 | Tunnelling - Tunnelling General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | As it can be seen from the As-Built Survey attahed, in many areas the setting out tolerncaes of the TBM Rails have exceeded the design tolerances (
| 02SL - Stations (LUL) | Cxxx-NCR-000929 | NCR | W - VA5 Flow test carried out after spraying has started |  | Contr | __M |  |  | 2015-02-01 | 2014-12-09 14:41 | -54 | 2014-10-24 12:29 | Tunnelling - Tunnelling General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | During the spraying of Adv.6 and Adv. 33 of enlargement of VA5 at WHI the flow tests have been carried out after the spraying has started. VA5 Adv.6: Spraying started at 09:15 and flow test carried out at 10:00 VA5 Adv.33: Spraying started at 20:45 and flow test carried out at 21:10
| 02SL - Stations (LUL) | Cxxx-NCR-000930 | NCR | W - LCW Enl.: Flow test missed or carried out after spraying has started |  | Contr | __M |  |  | 2014-11-10 | 2014-10-30 12:54 | -11 | 2014-10-27 11:24 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | During the spraying of LCW Enlargement, in August 2014, few flow tests have been missed or carried out after the start of the spray: - LCW Adv 5: Spraying started at (I) 16:00 and (P) 16:40 and flow test carried out at (I) 16:25 and (P) 16:55 - LCW Adv 14: Spraying started at 11:55 and flow test carried out at 12:10 - LCW Adv 15: Spraying started at 15:30 and flow test carried out at 16:00 - LCW Adv 16: Spraying started at 01:15 and flow test carried out at 01:29 - LCW Adv 18: Spraying started at (I) 14:00 and (P) 15:30 and flow test carried out at (I) 14:58 and (P) 16:00 - LCW Adv 19: Spraying started at (I) 00:30 and (P) 01:00 and flow test carried out at (I) 00:35 and (P) 01:33 - LCW Adv 20: Spraying started at (I) 10:00 and (P) 10:40 and flow test carried out at (I) 10:07 and (P) 11:17 - LCW Adv 31: Spraying started at (I) 16:15 and (P) 16:45 and only one flow test carried out at 16:20 - LCW Adv 35-36: Spraying started at (I) 13:30 and (P) 15:15 and only one flow test carried out at 15:07 for Primary Lining See attached SCL checksheets for evidences
| 02SL - Stations (LUL) | Cxxx-NCR-000931 | NCR | L - PTE-E Shutter removed before 6 hours |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-05-28 | 2015-03-30 18:57 | -59 | 2014-10-29 09:41 | Tunnelling - Linings - In-situ Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | The 21/10/14 NS: PTE Block 8 has been poured between 20h00 and 23h30. Workers have used the "Schmit Hammer " and as the strength was above the 10 N> mm2 they started to remove the shutter. The shutter has been striked and removed between 3h00 and 5h20. Time between the end of the pour and the start of the shutter removal: 3h30. Refer to the PTE-E SL shift report attached ( Att01. )
| 02SL - Stations (LUL) | Cxxx-NCR-000932 | NCR | W - PTW-W: Hollow spots in the primary lining |  | Contr | __M |  |  | 2016-10-07 | 2016-09-23 11:09 | -14 | 2014-10-29 10:19 | Tunnelling - Tunnelling General | 15000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Management Problem - Inadequate supervision | Completed |  | After hammer tapping the SCL primary lining areas in PTW-W some hollow sound and possible voids have been identified ( Refer to Att.20 for the PTW-W PL hollow spots tracker ) • On 24/10/15: One hollow spot has been found in PTW-W crown Ch 28.5 ( 1.0 x 1.8 m ) - Refer to Att.01 for the hammer tapping checksheet • On 28/10/14: Three hollow spots have been found in PTW-W crown Ch 30 ( Max 5.0 x 1.0 m ) - Refer to Att.02 for the hammer tapping checksheet • On 26/10/14: Eight hollow spots have been found in PTW-W crown Ch 80-98 ( Max 1.2 x 0.5 m ) - Refer to Att.03 for the hammer tapping checksheet • On 26/10/14: Five hollow spots have been found in PTW-W crown Ch 100-143 ( Max 0.7 x 0.5 m ) - Refer to Att.04 for the hammer tapping checksheet • On 06/12/15: Two hollow spots have been found in PTW-W crown Ch 116 ( Max 1.5 x 1.0 m ) - Refer to Att.05 for the hammer tapping checksheet • On 26/10/14: Two hollow spots have been found in PTW-W crown Ch 165-170 ( Max 2.5 x 1.0 m ) - Refer to Att.06 for the hammer tapping checksheet • On 25/10/14: Four hollow spots have been found in PTW-W crown Ch 183-187 ( Max 1.5 x 0.5 m ) - Refer to Att.07 for the hammer tapping checksheet and Att.08 for the proof drilling checksheet • On 25/10/14: Four hollow spots have been found in PTW-W crown Ch 183-203 ( Max 2.2 x 1.6 m ) - Refer to Att.07 for the hammer tapping checksheet • On 25/10/14: Twenty hollow spots have been found in PTW-W crown Ch 208-228 ( Max 5.0 x 1.0 m ) - Refer to Att.09 for the hammer tapping checksheet • On 26/01/16: Three hollow spots have been found in PTW-W invert Ch 104-109 ( Max 1.5 x 0.6 m ) - Refer to Att.10 for the hammer tapping checksheet • On 09/11/15: One hollow spot has been found in PTW-W invert Ch 105 - Refer to Att.11 for the hammer tapping checksheet • On 25/01/16: One hollow spot has been found in PTW-W invert Ch 107 ( 0.4 x 0.2 ) - Refer to Att.12 for the hammer tapping checksheet • On 16/11/15: Two hollow spots have been found in PTW-W invert Ch 115-160 - Refer to Att.13 for the hammer tapping checksheet
| 02SL - Stations (LUL) | Cxxx-NCR-000933 | NCR | L - LCE Localised underthickness lining |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-05-29 | 2015-03-11 12:49 | -79 | 2014-10-29 11:38 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | LCE primary lining scan show two extremely localised areas Ch 196 ( Page 3 ) and Ch 202.5 ( Page 16 ) with underthickness lining. Refer to the attachement (Att01.) for evidence.
| 02SL - Stations (LUL) | Cxxx-NCR-000934 | NCR | L - VD4 Adv 34-35 Exposed clay |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-03-18 | 2014-12-02 08:18 | -106 | 2014-10-29 16:38 | Tunnelling - Linings - Sprayed Concrete | 4000 |  | Supervision/Management | Rework | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | The 20/10/14 DS: Trimming works of hollow spots in VD4 headwall were on-going. Prior start of the trimming proof drillings have been done and have shown more than 400mm thickness everywhere ( Att02.) During the trimming works some clay has been exposed. Refer to the photos attached (Att01), proof drilling (Att02) and excavation profiles (Att03) for more details.
| 02SL - Stations (LUL) | Cxxx-NCR-000935 | NCR | W - Thrust block at LCW at WHI out of tolerances |  | Contr | __M |  |  | 2015-02-07 | 2015-01-29 14:31 | -9 | 2014-10-30 12:21 | Tunnelling - Tunnelling General | 28000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Management Problem - Inadequate supervision | Completed |  | The thrust block at WHI - LCW has exceeded the 15mm tolerance (in some areas 30mm or 40mm) as it can be seen from the attached 3d-scan. This is violating the given tolerance of -15mm that was specified in the drawing Cxxx-__M-C4-DDB-D061-00545 and later clarified with Cxxx-FCD-000642.
| 02SL - Stations (LUL) | Cxxx-NCR-000936 | NCR | L - Violation of the Permit to Cover Process (remaining open NCRs) at Block 4 &5 at PTW-E |  | Contr | __M |  |  | 2015-05-18 | 2015-01-23 17:10 | -115 | 2014-10-30 17:20 | Tunnelling - Tunnelling General | 500 |  | System Defect | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During the Permit to Cover Process for spraying Regulation Layer at Block 4 and Block 5 at PTW-E at LIV on 30/11/2014 the open NCR-865 and NCR-847 haven't been closed properly before the sign-off. This is a major violation of a Hold Point of the SCL ITP which hasn'e been released properly. See attached Permits to Cover.
| 02SL - Stations (LUL) | Cxxx-NCR-000937 | NCR | SCL thickness in LCE headwall |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2015-09-30 | 2015-07-17 09:38 | -75 | 2014-10-31 13:42 | Tunnelling - Linings - Sprayed Concrete | 6000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | Proof drilling carried out after the construction of the headwall to LCE enlargement on 22.03.2014 indicates headwall thickness beyond the minimum design thickness and in excess of the prescribed tolerance.
| 02SL - Stations (LUL) | Cxxx-NCR-000938 | NCR | L - Foreign object in the secondary lining of Block 15 of PTE-E |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-04-08 | 2015-03-11 14:49 | -28 | 2014-10-31 15:04 | Tunnelling - Tunnelling General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Personnel Error - Not Defined | Completed |  | Foreign object in the secondary lining of Block 15 of PTE-E (see attached picture and email by CRL/Cxxx Engineer).
| 02SL - Stations (LUL) | Cxxx-NCR-000939 | NCR | L - VD7 SL: Missing Test and Documentation |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-07-18 | 2017-07-21 12:55 | 3 | 2017-07-04 08:17 | Tunnelling - Tunnelling General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | • Cxxx-__M-C4-LLG-C101-50232 Deliverable Records for VD7 Regulating Layer, Secondary Lining & Fireproofing Layer - Package L046: 1) Regulation Layer: ITP item 2.6 Missing hammer tapping check sheet (__ Form D3-80) for VD7 Box connection, Ch. 11 to 11.391. 2) Secondary 1st Layer: ITP item 5.12 Missing hammer tapping check sheet (__ Form D3-80) for VD7 Secondary 1st , Ch. 5.558 to 9.491. • Cxxx-__M-C4-LLG-C101-50233 Deliverable Records for VD7 __ Membrane – Package L046: __ Membrane – ITP Item 2.7, 2.9, 2.11 Missing QA Checksheet (__ Form D3-100) for VD7 Crown, Ch. 4 to 9. __ Membrane – ITP Item 4.1 Missing Permit to Cover __ Membrane (__ Form D3-131) for VD7 Box Connection, Ch.10 to 11.391. • Cxxx-__M-C4-LLG-C101-50235 Deliverable Records for VD7 Portal Opening – Package L046: Portal Opening – ITP Item 4.2 Missing Verification of cover from Reinforcement Check Sheets (__ Form D2-26). See Att01. Portal Opening – ITP Item 6.3 Missing strike time on Concrete Pour Check Sheet (__ Form D3-05) for both Pour 1 and 2. See Att02.
| 02SL - Stations (LUL) | Cxxx-NCR-000940 | NCR | L - VD7 Enl Adv 5: Localised insufficient thickness |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-09-30 | 2016-10-20 14:08 | 20 | 2014-11-03 15:40 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | On 05/06/14, VD7 Enlargement Advance 5 has been built however beamer profile for this advance show missing information/data on 2 areas (2 o'clock and 6 o'clock). (see att01.) A proof drilling has been carried out at these 2 locations to check the final thickness. This proof drilling shows localised insufficient thickness ( see att02 - location 4 and 5) with 180 and 190 instead of the 250mm required.
| 02SL - Stations (LUL) | Cxxx-NCR-000941 | NCR | L - VD1 Enl Adv 36 and 38: Tight Spot and Insufficient Thickness |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-05-31 | 2015-01-23 10:15 | -128 | 2014-11-07 14:03 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | On 07/06/14, VD1 Enlargement Advances 36 and 38 have been built however beamer profile show : - a tight spot on the excavation of Advance 36 (-0.008) - insufficient thickness for this point on Advance 38 (237mm instead of the 250mm required) See attachement 01 for full details.
| 02SL - Stations (LUL) | Cxxx-NCR-000942 | NCR | W - VA4: __ Waterproofing membrane damaged |  | Contr | __M |  |  | 2016-02-29 | 2016-02-02 15:00 | -27 | 2015-10-16 15:24 | Tunnelling - Tunnelling General | 3000 |  | Planning | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | • On 29/09/15 During breakthrough works from Cambridge Heath Shaft (CHS), Stitch drilling via cores were taken across the top profile of the opening. This resulted in the __ membrane to be cut and damaged around the profile inside the opening of VA4 chainage 190 in the crown.
| 02SL - Stations (LUL) | Cxxx-NCR-000943 | NCR | L - Sidewings in the PTE-E have been cast encroaching the required space proofing |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-12-14 | 2015-11-18 16:14 | -26 | 2014-11-06 17:30 | Tunnelling - Tunnelling General | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Sidewings in the PTE-E blocks 15, 14, 13, 11, 10, 9, 5, 4, 3 and 1 have been cast encroaching the required space proofing: The final profile of the secondary lining has encroached the required space proofing and is out of tolerance. Therefore possibly affecting the next contractors. See attached scanned profiles and plan view ( PTE Block 15 to 1 ) and the summary table. For a better understanding a plan view with the affected areas can be seen in Att.01
| 02SL - Stations (LUL) | Cxxx-NCR-000944 | NCR | W - Nonconforming Early Strengths for Centre Drift Top heading, bench and invert |  | Contr | __M |  |  | 2015-06-20 | 2014-12-05 10:10 | -197 | 2014-12-02 11:35 | Tunnelling - Tunnelling General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | W - Missing early strength testing frequencies and below J2 Curve early strengths
| 02SL - Stations (LUL) | Cxxx-NCR-000945 | NCR | AP1 SL: Missing tests and documentation |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-07-20 | 2017-07-21 13:47 | 1 | 2017-07-06 09:20 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Cxxx-__M-C4-LLG-C101-50111 Deliverable Records for AP1 Regulation Layer – Package L020 1) Regulation Layer: ITP item C.3, 1.1, 2.1, 2.3, 2.5 Missing Shotcrete Placement Checksheet (__ Form D3-86) for AP1 Regulation Layer Crown, Ch. 91.67 to 102 and Ch.141 to 141.256. Missing Shotcrete Placement Checksheet (__ Form D3-86) for AP1 Regulation Layer Invert, Ch. 101 to 124. 2) Regulation Layer: ITP item 2.6 Missing Hammer Testing Checksheet (__ Form D3-80) for AP1 Regulation Layer Crown, Ch. 91.67 to 99. Missing Hammer Testing Checksheet (__ Form D3-80) for AP1 Regulation Layer Invert, Ch. 114 to 124. Cxxx-__M-C4-LLG-C101-50124 Deliverable Records for AP1 __ Sprayed Waterproofing Membrane - Package No. L020 3) __ Membrane – ITP item 1.2, 1.5 Missing Acceptance of Substrate for Waterproofing Sprayed Membrane (__ Form D3-81) for AP1 Crown, Ch. 121 to 124. Cxxx-__M-C4-LLG-C101-50127 Deliverable Records for AP1 Secondary Lining - Package No. L020 4) Secondary 1st Layer – ITP item C4 Missing Hammer Testing Checksheet (__ Form D3-80) for AP1 Second 1st Layer, Ch. 91 to 100 and 139 to 139.5. 5) Secondary 1st Layer and 2nd Layer – ITP item 5.1 Missing Packer Injection Checksheet (__ Form D3-133) for AP1 Second 1st Layer, Ch. 115 to 128 and AP1 Second 2nd Layer, Ch. 120 to 124. Cxxx-__M-C4-LLG-C101-50128 Deliverable Records for AP1 Fireproofing - Package No. L020 6) Fireproofing – ITP item 6.1 Contact grouting tubes #8 and #9 damaged for AP1, Ch. 108 to 111. See Att06. Cxxx-__M-C4-LLG-C101-50126 Deliverable Records for AP1 Cast In-Situ Invert and Wingwalls - Package No. L020 7) Protection Layer – ITP item 2.1, 2.2, 2.3 Missing Secondary Lining Concrete Pre-Pour Checksheet (__ Form D3-85) for AP1 Protection Layer, Block 2 to 4, Ch. 113.5 to 126.7 8) Invert– ITP item 3.1, 3.2, 3.4, 3.5 Missing Secondary Lining Concrete Pre-Pour Checksheet (__ Form D3-85) for AP1 Invert, Block 4, Ch. 125.3 to 126.7 9) Invert– ITP item 3.6, 3.7 Missing Secondary Lining Concrete Pour Checksheet (__ Form D3-84) for AP1 Invert, Block 4, Ch. 125.3 to 126.7 10) Invert– ITP item 3.3 Missing Reinforcement Check Sheet (__ Form D3-26)for AP1 Invert, Block 4, Ch. 125.3 to 126.7 11) Invert– ITP item C1 Cube not taken for AP1 Invert, Block 1, 2, 5 and 7 12) Wingwall– ITP item C1 Cube not taken for AP1d Wingwalls (18/6/2015), AP1-4 North (LHS), AP1-5 (North & South sides), AP1-6 (North & South sides). 13) Wingwall– ITP item 4.1 Post concrete inspection section not completed for AP1 Block 1 North (LHS) 14) Invert and Wingwall– ITP item 4.1 Defects identified on Concrete Post Pour Checksheet (__ Form D3-88) for AP1 Block 6 and 7. However no subsequent check is present to show repairs signed off. See Att11.
| 02SL - Stations (LUL) | Cxxx-NCR-000947 | NCR | L - PTE-W/CP2: Hollow Spot in primary lining thickening |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-12-19 | 2014-12-15 15:27 | -4 | 2014-11-10 11:20 | Tunnelling - Linings - Sprayed Concrete | 9000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | On 07/11/14 DS: During snagging works in PTE-W/CP2 Thickening, construction team found an hollow spot in the primary lining thickening of CP2. - Dimension 2mx1.3m - Depth 150-200mm - Thickness of void: 10-60mm - Position : Chainage 121 Left Shoulder Refer to the Photo (Att01), Survey (Att02) and Proof Drilling (Att03) for more information
| 02SL - Stations (LUL) | Cxxx-NCR-000948 | NCR | L - LCE/VD4: Hollow Spot in primary lining thickening |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2014-12-19 | 2014-12-16 09:35 | -3 | 2014-11-10 11:20 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On 09/11/14 DS: During snagging works in LCE/VD4 Thickening, construction team found an hollow spot in the primary lining thickening of VD4. - Dimension 0.5mx1.3m - Depth 180-200mm - Thickness of void: <10mm - Position : Chainage 205 Left Shoulder Refer to the Survey (Att01) and Proof Drilling (Att02) for more information Same issue than for NCR 948: voids in PTE-W/CP2
| 02SL - Stations (LUL) | Cxxx-NCR-000949 | NCR | L - VD7 Adv 8/9 Underthickness in the invert |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-05-29 | 2015-02-09 13:34 | -109 | 2014-11-18 08:17 | Tunnelling - Linings - Sprayed Concrete | 2500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The 05/06/14 DS: Only initial lining has been sprayed in VD7 Adv 8/9, which has lead to underthickness in the invert (Att01.)
| 02SL - Stations (LUL) | Cxxx-NCR-000950 | NCR | LIV - TAM positions outside specified tolerance. |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-07-19 | 2015-06-11 15:34 | -38 | 2015-04-10 09:57 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | The 08/04/2015 -The boreholes were surveyed and plotted against tolerance lines. They were all within tolerance in plan; however 2 out of 136 were out of tolerance vertically (A04 and F02). Boreholes which are not drilled to absolute accuracy can be due to poor workmanship but are commonly as a result of unforeseen ground conditions, natural or manmade obstructions in the ground or a combination of both. In the context of the drilling at Moorgate box, 157 boreholes were drilled in two phases of works through strata including Made Ground of unclassified constituents, granular River Terrace Deposits/ Treated River Terrace Deposits with unquantifiable and varying lithology, and cohesive London Clay. Such a variation of strata provides challenging conditions for the design of a suitable drilling system to successfully drill and install the TAMs required for ground treatment. It should be noted that of a total of 157 boreholes drilled in the strata described above, two were out of tolerance equating to 1.3% of the entire array with a worst case deviation of 300mm at 9m. Refer to the Att03. for the location of the out of tolerances boreholes
| 02SL - Stations (LUL) | Cxxx-NCR-000951 | NCR | W - EB Cav Enl- Missing Early Strength Test |  | Contr | __M |  |  | 2015-06-27 | 2014-12-15 15:43 | -194 | 2014-12-09 10:31 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | -EB Cav Invert, Adv’s 7, 14, 21, 24, 28, 32, 35 early strength test missing -EB Cav Invert, Adv 1, 1 hr requirement of 0.5 Nmm2 was not met, later tests above J2 curve. -EB Cav Sidewall: Adv’s 16, 22, 28, 32, 38, 43, 50, 54, 56, 63 early strength test missing -EB Cav Sidewall: Adv 8 – 3 hour, Adv 13 – 12 hour, Adv 19 – 3 hour, Adv 47 - 3 hour, Adv 52 – 3 hour, Adv 57 – 12 Hour, Adv 60 - 3 hour (Missing early strength tests) -EBRT-W Enlargement, Adv 153, early strength test at 1 hr missing, later tests above J2 curve. -EBRT-W Enlargement, Adv 159, 162, 171 early strength test missing. -EBRT-W Enlargement, Adv 200, early strength test at 6 hrs missing, later tests above J2 curve. -EBRT-W Enlargement, Adv 203, early strength test at 12 hrs missing, later tests above J2 curve. -EBRT-W Enlargement, Adv 206, 1 hr requirement of 0.5 Nmm2 was not met, later tests above J2 curve. -EBRT-W Enlargement, Adv 209, early strength test at 1 hr missing, later tests above J2 curve. -EBRT-W Enlargement, Adv 221, early strength test at 1 hr missing, later tests above J2 curve. -EBRT-W Enlargement, Adv 224, early strength test missed. Performed on Adv 225. -EPW1-W Adv 14, Adv 32, Adv 38 – early strength test missing -EPW1-W Adv 23 – 12hr early strength test missing
| 02SL - Stations (LUL) | Cxxx-NCR-000952 | NCR | PTE-W, PTE-E, LCE and RCE: Missing or Failed Early Strength Tests and Flow Tests, missing record |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-06-11 | 2015-03-04 12:34 | -99 | 2015-03-03 09:32 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Cxxx LIS PTE-E, PTE-W, LCE and RCE PTE-W: • Adv 45, early strength test missed. Performed on Adv 46 • Adv 51, early strength test missed. Performed on Adv 52 • Adv 54, 3 hr requirement of 1 Nmm2 was not met, later tests above J2 curve. • Adv 57, early strength test missing • Adv 66, early strength test at 1 hr missing, later tests above J2 curve • Adv 69, early strength test at 12 hrs missing, later tests above J2 curve • Adv 84, early strength test at 1 hr missing, later tests above J2 curve • Adv 90, early strength test missed. Performed on Adv 91 • Adv 91, early strength test at 12 hrs missing, later tests above J2 curve • Adv 96, early strength test missed. Performed on Adv 97 • Adv105, early strength test at 1 hr missing, later tests above J2 curve • Adv 126, early strength test missing • Adv 141, early strength test at 12 hrs missing, later tests above J2 curve • Adv 153, early strength test missed. Performed on Adv 154 • Adv 159, early strength test missing • Adv 165, early strength test missing • Adv 168, 1 hr requirement of 0.5 Nmm2 was not met, later tests above J2 curve. • Adv 177, early strength test missed before 3 hrs, later tests above J2 curve • Adv 180, early strength test missing • Adv 183 headwall, early strength test at 1 hr missing, later tests above J2 curve PTE-E • Adv 81, early strength test at 1 hr missing, later tests above J2 curve • Adv 144, early strength test missed. Performed on Adv 146 • Adv 150, early strength test missed. Performed on Adv 151 • Adv 165, early strength test at 12 hrs missing • Adv 168, early strength test at 12 hrs missing LCE • Adv 6, early strength test at 1 hr missing, later tests above J2 curve • Adv 12, early strength test at 12 hrs missing, later tests above J2 curve • Adv 45, early strength test at 6 hrs missing, later tests above J2 curve • Adv 63, early strength test missing • Adv 75, early strength test missed. Performed on Adv 76 • Adv 87, early strength test at 3 hrs missing, later tests above J2 curve • Adv 114, early strength test at 3 hrs missing, later tests above J2 curve • Adv 123, early strength test at 1 hr missing, later tests above J2 curve • Adv 126, early strength test at 1 hr missing, later tests above J2 curve • Adv 132, early strength test at 3 hrs missing, later tests above J2 curve • Adv 138, early strength test at 1 hr missing, later tests above J2 curve PTE-W/CP4 Thickening • CP4 Thickening, Near Face 1, early strength test at 12 hrs missing • CP4 Thickening, early strength test at 1 hr and 12 hr missing • CP4 Thickening, early strength test at 3 hr missing, later tests above J2 curve • CP4 Thickening, 1st Bulking Layer – Missing 1, 3, 6 & 12 hour tests • CP4 Thickening, 1st Bulking Layer – Missing 1, 3, 6 & 12 hour tests PTE-W/CP4a Thickening • CP4a Thickening, Far Face 1/2 – Missing 1, 3, 6 & 12 hour tests • CP4a Thickening, Bulking – Missing 6 & 12 hour tests • CP4a Thickening, Final Bulk – Missing 3, 6 & 12 hour tests PTE-W/CP2 Thickening • CP2 Thickening, Bulk Spray – Missing 1hr test Flow Tests: PTE-W: • Adv 46, spray commenced before sampling for Initial and Primary Lining • Adv 54, spray commenced before sampling for Initial Lining • Adv 58, missed Flow Tests • Adv 59, missed Flow Tests • Adv 71, missed Flow Tests for Initial Lining • Adv 93, missed Flow Tests • Adv 94, missed Flow Test for Initial Lining • Adv 101, spray commenced before sampling for Initial Lining • Adv 103, missed Flow Tests • Adv 106, missed Flow Tests • Adv 107, missed Flow Tests • Adv 124, spray commenced before sampling for Initial and Primary Lining • Adv 129, spray commenced before sampling for Initial and Primary Lining • Adv 132, spray commenced before sampling for Initial and Primary Lining • Adv 135, spray commenced before sampling for Initial and Primary Lining • Adv 137, spray commenced before sampling for Initial and Primary Lining • Adv 143, spray commenced before sampling for Initial and Primary Lining • Adv 166, spray commenced before sampling for Initial Lining • Adv 169, spray commenced before sampling for Initial Lining PTE-E • Adv 83, spray commenced before sampling for Initial and Primary Lining • Adv 88, spray commenced before sampling for Initial and Primary Lining • Adv 98, spray commenced before sampling for Initial and Primary Lining • Adv 118, spray commenced before sampling for Initial and Primary Lining • Adv 119, spray commenced before sampling for Initial and Primary Lining • Adv 124, spray commenced before sampling for Initial and Primary Lining • Adv 128, spray commenced before sampling for Initial and Primary Lining • Adv 129, spray commenced before sampling for Initial and Primary Lining • Adv 133, spray commenced before sampling for Initial and Primary Lining • Adv 134, spray commenced before sampling for Initial and Primary Lining • Adv 140, spray commenced before sampling for Initial and Primary Lining • Adv 141, spray commenced before sampling for Initial and Primary Lining • Adv 145, no sampling recorded past 18:00 (NS) • Adv 150, spray commenced before sampling for Initial and Primary Lining • Adv 156, missed Flow Test for Initial Lining and Primary Lining • Adv 159, spray commenced before sampling for Initial Lining • Adv 160, spray commenced before sampling for Initial Lining • Adv 179, spray commenced before sampling for Initial and Primary Lining LCE • Adv 15, spray commenced before sampling for Initial and Primary Lining • Adv 22, spray commenced before sampling for Initial and Primary Lining • Adv 26, spray commenced before sampling for Initial and Primary Lining • Adv 29, missed Flow Test for Initial Lining and Primary Lining • Adv 56, missed Flow Test for Primary Lining • Adv 81, spray commenced before sampling for Initial and Primary Lining • Adv 96, missed Flow Test for Primary Lining • Adv 101, missed Flow Test for Initial Lining and Primary Lining • Adv 120, spray commenced before sampling for Initial and Primary Lining • Adv 138, missed Flow Test for Primary Lining • Adv 140, spray commenced before sampling for Initial and Primary Lining • Adv 144, spray commenced before sampling for Initial and Primary Lining • RESS No. PTE-W/28 • PTE West (LCE) Enlargement Remedial Works: missing specific record as evidence of remedial works completion. Refer to Permit to Cover attached as evidence of remedial works completion Shotcrete Fall and Repair: • PTE-W Adv 50: 1 shotcrete fall during the initial spray & 1 shotcrete fall during the primary lining spray between 12 ‐ 1 o'clock. Area re-sprayed but no form done to record the repair.
| 02SL - Stations (LUL) | Cxxx-NCR-000953 | NCR | L - Operating temporary works without completed __ internal documentation |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-08-19 | 2015-03-19 15:18 | -153 | 2014-12-01 14:58 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The 26/11/14 DS: Site commenced lifting off jetty without approval in place
| 02SL - Stations (LUL) | Cxxx-NCR-000954 | NCR | L - RCE Block 7: Wing wall final thickness not achieved |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-08-26 | 2016-02-12 14:47 | -196 | 2014-11-27 15:39 | Tunnelling - Linings - In-situ Concrete | 1000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | The 21/11/14: Thickness in the left hand side of the wing wall in RCE Block 7 has been spotted at roughly 270-290 mm instead of 300mm. The total area of this varying under thickness (270-290mm) is approximately 0.2m2. See Att01 and Att02 for full details and scans.
| 02SL - Stations (LUL) | Cxxx-NCR-000955 | NCR | L - PTW Bloc 10: Hollow spots in primary lining |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-04-16 | 2015-01-15 09:56 | -91 | 2015-01-06 15:31 | Tunnelling - Linings - Sprayed Concrete | 2500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The 08/09/14 DS: 4 hollow areas have been spotted in PTW Bloc 10 crown: Area 1: 700 mm x 300 mm Area 2: 300 mm x 900 mm Area 3: 300 mm x 200 mm Area 4: 300 mm x 700 mm Refer to the email (Att01), beamer profile ( Att02) and photo ( Att03 ) for more information.
| 02SL - Stations (LUL) | Cxxx-NCR-000956 | NCR | L - IAT leave extra material welded loosely |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-03-07 | 2015-02-09 13:53 | -26 | 2014-11-27 16:16 | Tunnelling - Linings - In-situ Concrete | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | The 23/10/14: PTE-E waterproofing not cleaned and free of debris Refer to the photos (Att01.) for examples
| 02SL - Stations (LUL) | Cxxx-NCR-000957 | NCR | L - PTE: Joint not in the correct locations of the waterbars |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-06-30 | 2016-03-11 14:17 | -111 | 2014-12-01 10:06 | Tunnelling - Linings - In-situ Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The 03/11/14 DS: Parts of the fins from the waterbar are not cast properly. Refer to the photo (Att01) for waterbar not cast in properly in PTE Block 11.
| 02SL - Stations (LUL) | Cxxx-NCR-000958 | NCR | L - LCW Block 23/24: Dywidag bars installed without concrete cover |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-09-09 | 2016-07-01 08:49 | -70 | 2014-12-01 10:26 | Tunnelling - Linings - In-situ Concrete | 2000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | The 03/11/14 DS ( Shift 3) : Dywidag bars though invert and cut to flush therefore no concrete cover. Refer to photo (Att01) for evidence of no concrete cover in LCW block 23.
| 02SL - Stations (LUL) | Cxxx-NCR-000959 | NCR | L-Grout compressive strength did not conform to ITP specified range. |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-06-17 | 2015-03-27 10:28 | -82 | 2015-03-09 10:10 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The 27/10/14 DS: Compressive strength was outside of specified range for 37no sets of cubes. Refer to the Att01
| 02SL - Stations (LUL) | Cxxx-NCR-000960 | NCR | L - PTE Block 8/11/22: Cold joint in the wing walls |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-12-16 | 2016-07-01 08:42 | -168 | 2014-12-02 09:58 | Tunnelling - Linings - In-situ Concrete | 3000 |  | Material | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The 30/11/14 NS: Defect runs horizontal all the way across the block 22. Refer to the photos Att01 for evidence. -> During a routine site visit cold joint has been seen in the block 11 north-side and south-side wing walls. -> Potential NCR 348: Possible cold joint in Block 8 ( north-side and/or south-side not clear ). Due to Cxxx services on north side and spraying on CP10 on south side it was impossible to inspect the cold joint before handover.
| 02SL - Stations (LUL) | Cxxx-NCR-000961 | NCR | W - EP1: Injection tubes and __ damaged |  | Contr | __M |  |  | 2016-10-07 | 2016-06-28 15:05 | -101 | 2014-12-09 10:42 | Tunnelling - Tunnelling General | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Where temporary ramps have been constructed, there has been damage to the grout injection tubes and some parts of the sheet membrane system. Potential locations of damages are: DSS PTE-W junction, EP1, VA5, CP1A – junction with PTE-W. Further inspection of all the tubes and the membranes will take place after the tunnels will be handed over back to Cxxx in order to record and capture all the damages in detail. On 08/10/2014 __ has been found damaged in EP1 near the Dwall - Refer to photo PA070053.pdf After TBM transit, in Mid-February, a site visit has been organised with __ ( S. Lakis ) and CRL/Cxxx ( A Bein / M Tallis ) to inspect the waterproofing system after TBM transit. Except in EP1 tunnel that is already captured in NCR 961, there were no other grout injection tubes found damaged. Refer to Att.02 for the site visit report.
| 02SL - Stations (LUL) | Cxxx-NCR-000962 | NCR | L - PTE-E: Curing agent used instead of approved Retarder |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-03-12 | 2015-02-03 11:13 | -37 | 2014-12-02 11:35 | Tunnelling - Linings - In-situ Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | The 23/10/14 DS: Before the pour of PTE-E SL invert blocks, curing agent has been sprayed instead of retarder.
| 02SL - Stations (LUL) | Cxxx-NCR-000963 | NCR | W - Shotcrete out of workability tolerances (flow) |  | Contr | __M |  |  | 2015-06-20 | 2014-12-05 10:15 | -197 | 2014-12-02 12:16 | Tunnelling - Tunnelling General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | Shotcrete flow values were above the upper limit of 620mm (see attached SCL Placement checksheets
| 02SL - Stations (LUL) | Cxxx-NCR-000964 | NCR | W - Reinforcement Checksheets for some of the rebars of the Invert SideWall WB Cavern were not complete |  | Contr | __M |  |  | 2015-06-21 | 2014-12-05 10:50 | -198 | 2014-12-03 17:44 | Tunnelling - Tunnelling General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Reinforcement Checksheets for some of the rebars of the Invert SideWall WB Cavern were not complete: Bars 21,49,50 & 51 were not recorded in any reinforcement checksheets as they should have been, as requested by the design drawing Cxxx-__M-C4-DDB-D061-00351 Rev. C02. The issue was discovered during the certification process of Package W034.
| 02SL - Stations (LUL) | Cxxx-NCR-000965 | NCR | L - TAM lengths outside specified tolerance |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-05-29 | 2015-02-13 10:00 | -105 | 2014-12-04 09:04 | Tunnelling - Grouting | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Previous Construction - Not Defined | Completed |  | The following boreholes were found to be outside the agreed tolerances: -> TAM__16 which commenced drilling on the 2nd July 2014 and completed on the 2nd July 2014 was outside the tolerance envelope in length, short by 18m due to encountering an obstruction at 44m. 2 other attempts were carried out but encountered same obstruction at similar depth. Refer to the attachment Att01. -> TAM__33 which commenced drilling on the 03rd September 2014 and completed on the 04th September 2014 was outside the tolerance envelope in length, short by 4m due to encountering an obstruction at 32m. Refer to the attachment Att02. -> TAM__40 which commenced drilling on the 11th September 2014 and completed on the 12th September 2014 was outside the tolerance envelope in length, short by 6m due to encountering an obstruction (possibly a pile) at 34m. Refer to the attachment Att03. -> TAM__41 which commenced drilling on the 29th September 2014 and completed on the 29th September 2014 was outside the tolerance envelope in length, short by 6m due to encountering an obstruction (possibly a pile) at 39m. Refer to the attachment Att04. -> TAM__43 which commenced drilling on the 26th September 2014 and completed on the 26th September 2014 was outside the tolerance envelope in length, short by 4m due to encountering an obstruction (possibly a pile) at 45m. Refer to the attachment Att05. -> TAM__45 which commenced drilling on the 23rd September 2014 and completed on the 23rd September 2014 was outside the tolerance envelope in length, short by 5m due to encountering an obstruction at 50m. Refer to the attachment Att06. -> TAM__48 which commenced drilling on the 29th September 2014 and completed on the 30th September 2014 was outside the tolerance envelope in length, short by 8m due to encountering an obstruction at 46m. Refer to the attachment Att07.
| 02SL - Stations (LUL) | Cxxx-NCR-000966 | NCR | L - Inclinometer damaged during coring stage |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-03-14 | 2015-02-02 15:42 | -40 | 2014-12-04 11:06 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | • Inclinometer damaged during coring stage. One of the plunge cores has penetrated the inclinometer
| 02SL - Stations (LUL) | Cxxx-NCR-000967 | NCR | L - PTW-E, PTW-E, LCWb, RCW and Thickening: Missing or Failed Early Strength and Flow Tests, missing records |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-05-21 | 2015-05-07 17:43 | -14 | 2015-05-07 16:14 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Primary Lining o RCWa Advance 39 – Early strength test missed at 12 hour o RCWa Advance 48 – Early strength test missed at 6 & 12 hour o RCWa Advance 60 – No sprayed concrete early strength tests conducted o RCWb Advance 12 – 1hr requirement of 0.5 Nmm2 not met, later tests above J2 curve. o PTW-E (vii) Advance 1 – Early strength test at 1 and 3 hr missing, later tests above J2 curve o PTW-E (vii) Advance 5 – Early strength test at 3 hr missing, later tests above J2 curve o PTW-E (viii) Advance 9 – Missing 3, 6 & 12 hour tests o PTW-E (viii) Advance 12 – Early strength test at 1, 3 and 12 hr missing o PTW-E (viii) Advance 15 – Missing 12 hour test o PTW-E (viii) Advance 18 – Missing 12 hour test o PTW-E (viii) Advance 20 – Flow test information missing o PTW-E (viii) Advance 22 – Flow test information missing o PTW-E (viii) Advance 23 – Flow test information missing o PTW-E (viii) Advance 26 – Flow test information missing o PTW-E (viii) Advance 30 – No sprayed concrete early strength tests conducted o PTW-E (viii) Advance 39 – 1 hour J2 failed to reach strength, later tests above J2 curve o PTW-E (viii) Advance 59 – Flow test information missing o PTW-E (viii) Advance 60 – Missing 1, 3, 6 & 12 hour tests o PTW-E (viii) Advance 63 – Missing 3 & 12 hour tests o PTW-E (viii) Advance 66 – Flow test information missing o PTW-E (ix) Advance 78 – Early strength test at 1 hr missing, later tests above J2 curve o PTW-E (ix) Advance 85 – Flow test information missing o PTW-E (ix) Advance 86 – Spraying of primary 2 commenced before sampling o PTW-E (ix) Advance 87 – Spraying of initial and primary commenced before sampling o PTW-E (x) Advance 96 – Early strength test missed at 3 hrs, later tests above J2 curve o PTW-E (x) Advance 102 – Spray commenced before sampling for initial and primary lining o PTW-E (x) Advance 103 – Spray commenced before sampling for initial and primary lining o PTW-E (x) Advance 104 – Flow test information missing o PTW-E (x) Advance 120 – Early strength test missed at 12 hour o PTW-E (x) Advance 126 – Early strength test missed at 12 hour o PTW-E (x) Advance 132 – Early strength test missed at 1, 3, 6 & 12 hour o PTW-E (x) Advance 133 – Early strength test missed at 1 hr and 3 hr, later tests above J2 curve o PTW-E (x) Advance 134 – Early strength test missed at 3, 6 & 12 hour o PTW-E (x) Advance 144 – Early strength test missed at 1 hr, later tests above J2 curve o PTW-E (xi) Advance 152 – Early strength tests for shotcrete fall done but not recorded on J2 curve checksheet o PTW-E (xi) Advance 153 – Early strength test missed at 1 hr, later tests above J2 curve o PTW-E (xi) Advance 156 – Early strength test missed at 3 hr, later tests above J2 curve o PTW-E (xi) Advance 157 – Early strength tests after shotcrete fall not performed o PTW-E (xi) Advance 165 – Early strength test missed at 1 hr, later tests above J2 curve o PTW-E (xi) Advance 166 – No sprayed concrete early strength tests conducted o PTW-E (xi) Advance 168 – Early strength test missed. Performed on Adv 169 o PTW-W (ii) Advance 147 – No sprayed concrete early strength tests conducted o PTW-W (ii) Advance 140 – Missed Flow Test for Initial Lining o PTW-W (iii) Advance 126 – 1 hour J2 failed to reach strength, 3 hour test missing, later tests above J2 curve o PTW-W (iii) Advance 123 – Flow tests missed for initial and primary lining o PTW-W (iii) Advance 123 – 1 hour J2 failed to reach strength, later tests above J2 curve o PTW-W (iii) Advance 120 – 1 hour J2 failed to reach strength, later tests above J2 curve o PTW-W (iii) Advance 108 – Early strength test at 1 hr missing, later tests above J2 curve o PTW-W (iii) Advance 105 – 1 hour J2 failed to reach strength, later tests above J2 curve o PTW-W (iii) Advance 102 – Early strength tests at 6 hr and 12 hr missing o PTW-W (iii) Advance 99 – Early strength tests at 1 hr and 3 hr missing, later tests above J2 curve o PTW-W (iii) Advance 96 – Early strength test at 1 hr missing, later tests above J2 curve o PTW-W (iv) Advance 67 – No sprayed concrete early strength tests conducted o PTW-W (iv) Advance 65 – Spray commenced before sampling for initial and primary lining o PTW-W (v) Advance 62 – Spray commenced before sampling for initial and primary lining o PTW-W (v) Advance 59 – Spray commenced before sampling for initial and primary lining o PTW-W (v) Advance 54 – Early strength test missed at 6 hr, later tests above J2 curve o PTW-W (v) Advance 52 – Early strength test missed at 1 and 3 hr, later tests above J2 curve o PTW-W (v) Advance 52 – Shotcrete fall and repair checksheet missing, recorded in Tunnel Unusual Occurrence Register o PTW-W (v) Advance 45 – Early strength test missed at 6 hr, later tests above J2 curve o PTW-W (vi) Advance 27 – Low early strength before 2hour. Above J2 curve after o PTW-W (vi) Advance 9 – No sprayed concrete early strength tests conducted o LCWb Advance 35 – Early strength test missed at 12 hour o LCWb Advance 34 – Early strength tests missed, carried out at advance 35 o LCWb Advance 33 – Excavation profile beamer records incomplete between 2 and 4 o’clock due to software issue, info recorded o LCWb Advance 32 – No sprayed concrete early strength tests conducted o LCWb Advance 28 – Early strength test missed at 1 hr, later tests above J2 curve o LCWb Advance 27 – Spray commenced before sampling for initial and primary lining o LCWb Advance 26 – no flow test carried out for Initial and Primary Lining o LCWb Advance 25 – Early strength test missed at 6 and 12 hr. o LCWb Advance 23 – Spray commenced before sampling for initial and primary lining o LCWb Advance 22 – early strength test missed at 6 hr, later test above J2 curve o LCWb Advance 19 – Early strength test missed at 1 hr, later tests above J2 curve o LCWb Advance 19 – Spray commenced before sampling for initial lining o LCWb Advance 18 – Spray commenced before sampling for initial and primary lining o LCWb Advance 16 – 1 localised point with under-thickness (389mm should be 400mm) compensated with following layer o LCWb Advance 15 – Early strength test missed at 3 hr and 6 hr, later tests above J2 curve o LCWb Advance 15 – Spray commenced before sampling for initial lining & no flow test carried out for Primary Lining o LCWb Advance 13 – Early strength test missed at 1, 3, 6 and 12 hr. o LCWb Advance 11 – Spray commenced before sampling for initial and primary lining o LCWb Advance 6 – No flow test carried out for Initial and Primary Lining o LCWb Advance 5 – No flow test carried out for Initial and Primary Lining o LCWb Advance 4 – Early strength test missed at 12 hr. o LCWb Advance 2 – Spray commenced before sampling for initial lining Thickening o VD1 FF1 – Missing 3 hour test o VD1 Invert Bulk Out for FF2 – Missing 3 hour test o VD1 Stage 7 – Missing 6 & 12 hour tests o VD1 Final Bulk – Missing 3 hour test o CP9 FF1 – Missing 3, 6 and 12 hour tests o CP9 NF1 – Missing 1, 3 and 6 hour tests o CP9 NF1 Invert – Steel reinforcement survey beamer profile missing o CP1 First Bulk – Missing 1 and 6 hour tests o CP1 FF2 Steel Spray – Missing 1, 3, 6 and 12 hour tests o CP1 Bulk Spray – Missing 1 and 3 hour tests o CP1 Final Bulk Spray – Missing 1, 3, 6 and 12 hour tests o CP1 FF2 Steel Spray – Missing 1, 3, 6 and 12 hour tests o CP7 FF1 Spray – 1 and 12 hour tests missing o CP7 FF2 Bulk – Missing 3, 6 and 12 hour tests o CP7 NF1 – Missing 1, 3 and 12 hour tests (see documents attached for every issue)
| 02SL - Stations (LUL) | Cxxx-NCR-000968 | NCR | L - PTW: Cold joint in the wing wall |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-07-22 | 2016-04-29 09:33 | -84 | 2014-12-05 12:31 | Tunnelling - Linings - In-situ Concrete | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | L- 10/12/14 DS - 1.After removal of the shutter, a cold joint Defect runs horizontal all the way across the PTW-E block 6 RHS/LHS.(This can be seen in Att.01) 2.There has been also been another cold joint spotted in PTW-E Block 11 wing wall LHS and RHS. (Please refer to Att.02 and Att.03) L- The 12/12/14 DS: 3.After removal of the shutter in the PTW-E RHS wingwall defects have been spotted. Refer to the photos of the poor quality wingwall in B12 (Att04) for evidence. 4. The 27/01/15 DS: It was noticed during the set up of the invert in RCWa Block 1 that the damaged wingwalls in block 2 extended further than just the surface of the bottom of the wing walls. The damage (Att.05 and Att.06) is located at the bottom of the wingwalls next to the longitudinal joint to the invert slab. It appears that the cracks could extend further in to the rest of the block and is not just on the surface.
| 02SL - Stations (LUL) | Cxxx-NCR-000969 | NCR | W - Non-compliant 90days core results |  | Contr | __M |  |  | 2015-10-04 | 2015-02-03 12:11 | -243 | 2014-12-08 15:55 | Tunnelling - Tunnelling General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | 90 days samples taken between 12/06/14 and 16/08/14 comply with criterion 1 (apart from one sample CR1878) but failed to comply with criterion 2 due to increase of standard deviation that has caused failures on the running mean results with failure range between 0.1 - 4.6N/mm². Effected samples are highlighted on attached summary.
| 02SL - Stations (LUL) | Cxxx-NCR-000970 | NCR | W - EBRT-W and EB Cav: Missing checksheet |  | Contr | __M |  |  | 2015-02-27 | 2014-12-16 10:14 | -73 | 2014-12-12 17:35 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | Missing Shotcrete placement check sheets (D3-37 & D3-72) and reinforcement placement check sheets (D3-26) for EB Cav Sidewall Adv 18, EB Cav Invert Adv 36 and EBRT-W Adv 172 and 173.
| 02SL - Stations (LUL) | Cxxx-NCR-000971 | NCR | L - PTE E __ MS Violation of permit to cover |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-05-14 | 2015-02-01 16:54 | -102 | 2014-12-15 09:56 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | The 9/12/14: PTE E Ch54 to 74 Permit to cover has been signed and indicating that no NCRs were open in the area. Cxxx-NCR-000957 in PTE Block 11 was unfortunately still open at that time
| 02SL - Stations (LUL) | Cxxx-NCR-000972 | NCR | L - Electra House: Grout Bleed did not conform to ITP specified range |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-05-14 | 2015-03-05 12:59 | -70 | 2014-12-15 10:13 | Tunnelling - Grouting | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Bleed tests frequency of 1 test every 5th mix was not respected during 57 of the 178 shifts. Bleed tests frequency was not within the ITP specified tolerance range.
| 02SL - Stations (LUL) | Cxxx-NCR-000973 | NCR | L - Electra House: Grout Density did not conform to ITP specified range. |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-05-14 | 2015-02-06 08:27 | -97 | 2014-12-15 11:18 | Tunnelling - Grouting | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Inadequate/insufficient tooling. | Completed |  | The 5/12/14: The following grout mixes were found to be outside the ITP range of values: 1.20 – 1.40 g/cm3. Cube tested on site dated 16/01/2014 (NS). Density: 1.41 g/cm3. Cube tested on site dated 16/01/2014 (NS). Density: 1.41 g/cm3. Refer to the Att01.
| 02SL - Stations (LUL) | Cxxx-NCR-000974 | NCR | L - Electra House: TAM positions outside specified tolerance |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-06-26 | 2015-06-11 13:21 | -15 | 2015-01-06 09:30 | Tunnelling - Grouting | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Weather or ambient condition | Completed |  | The boreholes were surveyed and plotted against tolerance lines. They were all within tolerance in plan; however 75 out of 444 were out of tolerance vertically. Refer to the Att01. for evidence
| 02SL - Stations (LUL) | Cxxx-NCR-000975 | NCR | L - VD1: No checksheets for the repairs works |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-07-29 | 2015-09-24 12:41 | -309 | 2014-12-16 10:07 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The 27/10/14: repairs works in VD1 were done witout records ie checksheets and done incorrectly. Cutting back has been done without enought for overlap and thickness was insufficient
| 02SL - Stations (LUL) | Cxxx-NCR-000976 | NCR | L - October spray test beams: Low Residual Flexural strength - CR2023 & CR2030 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-02-29 | 2015-12-12 00:35 | -79 | 2015-01-05 11:04 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | 1) LIV spray beam set CR2023 from October has achieved too low individual D3 results of beam B – S0.7, C – S1.0, E – S0.9, F – S0.9 at 28 days with average for set of six beams - S1.0 2) Second sprayed set for October CR2030 has achieved too low individual D3 results of beam C – S1.0 at 28 days with average for set of three beams - S1.6 Refer to the Att01 for the tests results
| 02SL - Stations (LUL) | Cxxx-NCR-000977 | NCR | L - Strength failure on the running mean strength |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-04-18 | 2015-02-05 08:02 | -72 | 2015-01-08 09:44 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | 90 days samples taken between 03/06/14 and 18/09/14 comply with criterion 1 but failed to comply with criterion 2 due to increase of standard deviation that has caused failures on the running mean results with failure range between 0.1 - 2.3N/mm². Effected samples are highlighted on attached summary (Att01.)
| 02SL - Stations (LUL) | Cxxx-NCR-000978 | NCR | L - Blomfield Box: Grout Viscosity did not conform to ITP specified range. |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-04-16 | 2015-01-20 14:23 | -86 | 2015-01-06 09:42 | Tunnelling - Grouting | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Grout viscosity was not within the ITP specified tolerance range. The following grout mixes were found to be outside the ITP range of values: 35-40 seconds. Cube tested on site by DP dated 16/07/2014. Viscosity: 41 seconds. Cube tested on site by DP dated 17/07/2014. Viscosity: 41 seconds. Refer to the Att01 for evidence
| 02SL - Stations (LUL) | Cxxx-NCR-000979 | NCR | W - XOV Enl: Missing early strength shotcrete testing |  | Contr | __M |  |  | 2015-02-27 | 2015-01-20 11:48 | -38 | 2014-12-19 08:30 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | • Crossover Enlargement Adv’s 10, 15, 46, 55, 58, 68, 85, 88, 103, 118, 124, 130, 3 (Connection): J2 Curve Tests Missed • Crossover Enlargement Adv 7: 1 hour test missed • Crossover Enlargement Adv 56: 12 hour test missed • Crossover Enlargement Adv 97: 12 hour test too high: mistake during the test.
| 02SL - Stations (LUL) | Cxxx-NCR-000980 | NCR | L - Moorgate Shaft Platform fabrication started without an approved ITP |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-10-30 | 2015-08-11 15:43 | -80 | 2015-01-06 15:30 | Tunnelling - Tunnelling General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | As per Cxxx-PMI-0076 __ had to install the platforms within Moorgate Shaft during Christmas. The platforms were manufactured by __ during December 2014. THe ITP covering the fabrication of these platforms is Cxxx-__M-C-ITP-C101-50048 Rev.2 which got a Code 2 on 19/12/2014 only a few days before the installation started and the fabrication was almost completed.
| 02SL - Stations (LUL) | Cxxx-NCR-000981 | NCR | L - CE Marking of the fabricator of Moorgate Shaft Platform hasn't been submitted before the fabrication of the platforms started |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-04-20 | 2015-03-05 17:13 | -46 | 2015-01-06 15:36 | Tunnelling - Tunnelling General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | As per Cxxx-PMI-0076 __ had to install the platforms within Moorgate Shaft during Christmas. The platforms were manufactured by __ during December 2014. It is a legal requirement of Construction Products Regulations 2013 (CPR 2013) that the fabricator should provide the CE Marking Conformity Statement before the fabrication of any structure starts. __ failed to provide the CE Marking Statement before the fabrication started in December 2014.
| 02SL - Stations (LUL) | Cxxx-NCR-000982 | NCR | L - October and November Cast test beam: Low Residual Flexural strength |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-02-29 | 2015-12-12 00:46 | -79 | 2015-01-13 08:46 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | LIV cast beam set CR2029 from October has achieved too low individual D3 results of beam B – S0.9, C – S0.8, at 28 days with average for set of seven beams - S1.7, LIV cast beam set CR2035 from November has achieved too low individual D3 results of beam F – S1.0, at 28 days with average for set of seven beams - S1.8 Second sprayed set for November CR2040 has achieved too low individual D3 results of beam A – S0.6, C – S0.9, E – S1.0 at 28 days with average for set of six beams - S1.3 Refer to the Att01 for evidence
| 02SL - Stations (LUL) | Cxxx-NCR-000983 | NCR | L - No photographs of Face Excavations |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-06-07 | 2015-01-21 13:35 | -137 | 2015-01-08 11:04 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During May 2014: • 1 advance have not had a photograph taken of the face excavation for submission to Crossrail within the factual geological reports. The advance is: • VD4 break out B
| 02SL - Stations (LUL) | Cxxx-NCR-000984 | NCR | L - PTE-W/CP4a Block 19: Radial joint not big enough |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-12-16 | 2017-01-30 11:17 | 45 | 2015-01-13 10:07 | Tunnelling - Linings - In-situ Concrete | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The 26/11/14: The joint of the wing wall from PTE-W Block 19 towards CP4a opening as been spotted with a thickness below the requirements ( thickness of 50mm at the joint ). Refer to the photos attached (Att01.) for evidence The location of the NCR can be seen in Att.04. The location is on in invert as it comes in to CP4a from the platform tunnel on the west side (it does not go past the contraction joint). The location is on in invert as it comes in to CP4a from the platform tunnel on the west side (it does not go past the contraction joint
| 02SL - Stations (LUL) | Cxxx-NCR-000985 | NCR | L - Moorgate Station: Waterproofing system __ __ Hose VT2 installed incorrectly |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-08-28 | 2015-07-29 12:09 | -30 | 2015-03-13 14:36 | Tunnelling - Linings - In-situ Concrete | 4000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The 30/11/14 DS: 1. Termination of __ Hose type V2 was not installed as per manufacturer's installation guide (Att01.) 2. Joint between __ VT2 and reinforced hose was outside the wall 3.This occurred at both terminations within the brick wall within the service pits - one in each crosspassage (4/203 and 4/204)
| 02SL - Stations (LUL) | Cxxx-NCR-000986 | NCR | W - Several nonconformities for the certification of W056 |  | Contr | __M |  |  | 2016-10-21 | 2016-06-16 13:33 | -127 | 2015-01-14 15:55 | Utilities Engineering - Utilities General | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | During the preparation of the Certification Package W056, the following items have been identified as missing from the deliverable records: For Cxxx-__M-C-ITP-D061-50068 – Drilling ITP: ITP item B1 – MCR for Annulus Filling Sand hasn't been submitted ITP item 2.7 – the drillers did not log the arisings due to negligence and due to the fact that a tremendous amount of data had been collected during the first round of drilling boreholes. This issue had been raised during a surveillance at the time of the works and it was agreed between __ and CRL that an NCR would be raised ITP item 3.1 – missing PW4A and PW9 Pump Installation Record Sheets. And for Cxxx-__M-C-ITP-D061-50073 – Installation ITP ITP Item 3.2 – Standby generator check hasn't been recorded on the daily logs ITP item 3.6 – The failure text test hasn't been recorded on the daily logs.
| 02SL - Stations (LUL) | Cxxx-NCR-000987 | NCR | L -PTE-E/CP8: __ over sprayed with 2nd lining |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-10-30 | 2015-10-27 14:57 | -3 | 2015-01-15 13:43 | Tunnelling - Linings - Sprayed Concrete | 6000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | The 12/01/15: The __ Sprayed waterproofing has been over sprayed with the 2nd layer of the secondary lining. As per the photos Att01. and Att02., the __ is no more visible. As of 02/06/2015 , the proposed repair method was carried out however both of the __ hoses were injected and sealed off, therefore making them redundant to further injection.
| 02SL - Stations (LUL) | Cxxx-NCR-000988 | NCR | L - PTE-W Ch 60-80: __ poor quality ( de-bonding, incorrect thickness and checksheet ) |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-04-25 | 2015-03-30 19:12 | -26 | 2015-01-15 17:33 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | The 10/01/15 DS: The PTE-W Ch 60 - 80 __ Layer 1 has been sprayed. After completion of Layer 2 by the NS, de-bonding between the two layers has been spotted. After investigation it seems that layer 1 was too thick. Refer to the __ Sample 1 Photos (Att01.) and __ Sample 2 Photos (Att02. ) Moreover this issue should have been spotted by the shift engineer during the wet thickness test done just after the __ spray. (Att03.)
| 02SL - Stations (LUL) | Cxxx-NCR-000989 | NCR | W - Missing documents for certification of W056 - Vallance Road Depressurisation |  | Contr | __M |  |  | 2017-07-20 | 2017-07-19 13:08 | -1 | 2015-01-21 11:18 | Utilities Engineering - Utilities General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | During the preparation of the Certification Package W056 - Vallance Road Depressurisation, the following items have been identified as missing from the deliverable records for Deliverable Cxxx-__M-C-LLG-D061-50035 – Excavation of Trenches, Chambers and Reinstatement: 1) ITP item 3.1 – Delivery Ticket for 'Utilities in trench: Service suround - material conformity' not available. 2) ITP item 3.7 - Missing Trunk Main Access (__-Form D3-58) and Concrete Pre Pour (__-Form D3-18) Checksheets. 3) ITP item 3.8 and 3.10 - Missing Delivery Docket Photos 4) ITP item 3.11, 4.8, 4.10 and 3.12, 4.11 - Missing Concrete Pour checksheet and tests results for chamber and pavement. 5) ITP item 6.2 and 6.3: Missing information on __-Form D3-79 (Daily Site Report) although this has been done as part of the work to connect into the manhole.
| 02SL - Stations (LUL) | Cxxx-NCR-000990 | NCR | L - PTE packers overpray with SL first layer |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-05-02 | 2015-04-20 14:44 | -12 | 2015-01-22 09:29 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | The 11/12/14: During injection some packers were not visible due to over-spraying in PTE Block 17. Refer to the photos attached ( Att01.) The 17/12/14: Packers were not extended prior spray of the Secondary lining. Refer to the photos attached (Att02.)
| 02SL - Stations (LUL) | Cxxx-NCR-000991 | NCR | L - PTE-W Hollow spots in secondary lining |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-07-31 | 2015-05-28 13:09 | -64 | 2015-01-21 11:43 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The 08/01/15: During hammer testing in Block 17, 18 and 19 hollow areas have been spotted. Refer to the Hammer Testing Checksheet (Att01.) Survey of the hollow areas to show the exact location has been done (Att02.)
| 02SL - Stations (LUL) | Cxxx-NCR-000992 | NCR | L - Fibre content failure |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-09-25 | 2015-05-21 15:30 | -127 | 2015-01-26 13:02 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Sample number CR2084 taken during of pour of block 30 in PTE-W at Liverpool site fail to comply with min 0.8kg/m3 of fibre content for mix Invert – mix design 1kg/m3. Refer to the Attachment Att01 for evidence
| 02SL - Stations (LUL) | Cxxx-NCR-000993 | NCR | L - LCWa Adv.1 and 2 underthickness |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-08-31 | 2015-03-13 15:56 | -171 | 2015-02-12 10:18 | Tunnelling - Linings - In-situ Concrete | 2500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The 30/01/15 DS: Some areas on the crown in LCWa Adv1 and 2 are under sprayed, refer to the photo Att01.
| 02SL - Stations (LUL) | Cxxx-NCR-000994 | NCR | L - PTE-E Adv 165: Missing data on Beamer Thickness |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-06-11 | 2015-03-10 11:04 | -93 | 2015-03-03 09:34 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | • During Certification process of PTE-E, it has been decided to raise a NCR due to missing data for PTE-E Adv 165 invert lining thickness on Beamer Profile (from 4 to 8 o clock). (see att02).
| 02SL - Stations (LUL) | Cxxx-NCR-000995 | NCR | L - Non conformity of aggregate – sample E1464 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-06-17 | 2015-05-28 13:00 | -20 | 2015-01-28 15:03 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The 12/01/15: One sample taken from one load at LIV site has shown a marginal grading failure on the 0.500mm sieve on sample No E1464. Repeated test shown the same outcome. Refer to the attachement (Att01)
| 02SL - Stations (LUL) | Cxxx-NCR-000996 | NCR | L - PTW Block 23: Nonconforming radial joint in the LCW transition area |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-12-18 | 2015-11-13 11:09 | -35 | 2015-01-28 15:41 | Tunnelling - Linings - In-situ Concrete | 3000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The 12/01/15: Radial joint in the transition area between PTW and LCW hasn't been formed as per the requirements. Refer to the sketch (Att01.). In red the non conforming radial joint as it is the 12/01/15 and in black as it should be as per the drawings
| 02SL - Stations (LUL) | Cxxx-NCR-000998 | NCR | L - PTE-W B24 RHS wingwall joint: Poor compaction of the concrete and spraying in of rebound |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-07-31 | 2015-03-30 19:01 | -123 | 2015-02-09 15:10 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On 08/02/15 DS, PTE-W B24 RHS, a poor compaction of the concrete and spraying in of rebound between the wingwall and the top heading has resulting in a joint not properled bounded. This may have cause potential voiding within the concrete. See att1-picture attached
| 02SL - Stations (LUL) | Cxxx-NCR-000999 | NCR | L - LCE Block 31 LHS Sidewing: Poor compaction of the concrete and exposed rebar |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-10-30 | 2017-02-01 15:45 | 94 | 2015-02-10 09:49 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Planning | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On 09/02/15 DS, in LCE Block 31 LHS Sidewing, concrete has been poorly compacted and rebar exposed. This has lead to inadequate capsulation of the reinforcement, major air voids and poor quality of concrete. Refer to Att01. for pictures of the defects.
| 02SL - Stations (LUL) | Cxxx-NCR-001000 | NCR | ITP/Method statement decal code 2 for more than six months |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2015-05-01 | 2015-04-28 10:52 | -3 | 2015-02-16 12:56 | Tunnelling - Linings - In-situ Concrete | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | During a pre-surveillance review of the ITP and MS for the Setting out of water bars, shutters, for the cast Insitu secondary lining (slabs, side/wing walls) it was found the following; Method Statement General secondary lining methodology Cxxx- __M-C4-GMS-CR092-50005 Rev 5.0 Decal code 2 since10/09/2014, ITP In-situ tunnelling methodology for secondary lining Cxxx-__M-C4-ITP-CR092-50009 rev 2.0 Decal code 2 since 24/02/2014 ITP Invert shutter assembly Cxxx-__M-C4-ITP-CR092-50006 rev 1.0 decal code 2 since 20/01/2014
| 02SL - Stations (LUL) | Cxxx-NCR-001001 | NCR | Invert slab joint not prepared as per the ITP/Specification and method statement |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2015-04-17 | 2015-04-09 11:02 | -8 | 2015-02-16 14:03 | Tunnelling - Linings - In-situ Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Whilst carrying a surveillance on setting out of water bars, shutters, for the cast Insitu secondary lining slabs, side/wing walls, found invert slab PTE block 31 construction joint between the cast invert and the forthcoming wing wall had not prepared been as per the method statement Cxxx- __M-C4-GMS-CR092-50005 rev 5.0 section 5.3.4 phase 14-pour side walls; Joints shall be clean and perpendicular to the lining, and to be brushed clean and free of laitance (with an exposed aggregate finish). The concrete inspected was smooth with no aggregate exposed. Cxxx-MMD-Z4-RSP-CR001-50006 Rev.1.0 Specification for Secondary Linings - Cast In-Situ Inverts 6.10 Construction Joints; (e) At construction joints, the surface of the concrete shall be clean with laitance removed
| 02SL - Stations (LUL) | Cxxx-NCR-001002 | NCR | L - Failure of fibre fresh tests on mix P1 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-10-30 | 2015-08-18 10:22 | -73 | 2015-02-25 08:50 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Sample number CR2103 taken during spray of in LCWa at liverpool site fail to comply with min 36kg/m3 of fibre content for P1 mix - mix design 45kg/m3. As per Att01.: - CR2103 average fibre content = 35 kg/m3 instead of min 36 kg/m3 (80% of mix design 45kg/m3) -so 1 kg out of min spec. - CR2116 = 42 kg/m3 instead of min 36 kg/m3 (80% of mix design 45kg/m3)
| 02SL - Stations (LUL) | Cxxx-NCR-001003 | NCR | L - CP3a missing rebars in the invert |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-06-04 | 2015-04-14 15:55 | -51 | 2015-02-24 16:57 | Tunnelling - Linings - Sprayed Concrete | 2000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | During construction of the invert in CP3a, NF2 rebars were missed out ( 6-B25-25-25-150 NF2 ) and sidewalls/invert have been poured.
| 02SL - Stations (LUL) | Cxxx-NCR-001004 | NCR | L - LCWa - Non conforming cores in Adv 5 (CR2118), Adv 30 (CR2121) and Adv 40 (CR2127) |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-08-26 | 2016-07-19 13:48 | -38 | 2015-02-25 09:23 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The 29/01/15 DS: LCWa Adv 5 has been sprayed The 04/02/05 NSL LCWa Adv 30 has been sprayed The 08/02/05 NS: LCWs Adv 40 has been sprayed The 13/02/15 NS: seven cores were taken in the RK (CR2118) of the LCWa Adv 5. Cores have been review the 20/02/14 and found with major voids, honeycombing, cracks, laminations and broken several times. The 15/02/15 DS: nine cores have been taken in the RK (CR2121) of the LCWa Adv 30. They have been review the 20/02/15 and dust has been found at the end the cores. The 16/02/15 NS: three cores have been taken in the LS (CR2127) of the LCWa Adv 40. They have been review the 20/02/15 and major voids/honeycombing have been found. During the 23/02/15 SRG meeting it has been decided that a NCR will be raised and the cores reports sent to __ Designer ( UnPS ) for review. See core report attached (Att01., Att02 and Att03)
| 02SL - Stations (LUL) | Cxxx-NCR-001005 | NCR | L - PTE/CP8 and CP4 Thickening Inspections were not carried out as per the ITP |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-08-28 | 2015-05-18 13:49 | -102 | 2015-02-24 14:41 | Tunnelling - Linings - In-situ Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | During the review of the PTE/CP8 Thicknening delivery documents ( Cxxx-__M-C4-LLG-C101-50058 ) numerous signatures were missing. ITP was not adhered to. Inspections were not carried out as per the ITP requirements. During the review of the PTE/CP4 Thicknening ( Cxxx-__M-C4-LLG-C101-50062) FF1 – Sheet has been completed 6 months after work took place. Inspections not signed at time of work taking place.
| 02SL - Stations (LUL) | Cxxx-NCR-001006 | NCR | L - PTW-E/CP9: __ over sprayed with 2nd lining |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-06-05 | 2015-05-12 15:12 | -24 | 2015-02-25 15:10 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | The 17/02/15 DS: The __ Sprayed waterproofing has been over sprayed with the 2nd layer of the secondary lining. As per the photos Att01. __ has been partially oversprayed.
| 02SL - Stations (LUL) | Cxxx-NCR-001007 | NCR | L - Low Residual Flexural Strength - Beam Testing |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-02-29 | 2015-12-12 01:00 | -79 | 2015-02-26 17:41 | Civil - Structural Engineering | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | The 26/02/2015: cast beam set CR2055 from December has achieved too low individual D3 results of beams A – S0.8, C – S0.8, D – S1.2, E – S1.2, F – S1.0, G – S1.1 at 28 days with average for set of seven beams - S1.1, LIV cast beam set CR2082 from January has achieved too low individual D1 results of beams F – S1.4, G – S1.4 , at 28 days with average for set of seven beams for D1 – S2.2, as well as too low individual D3 results of beams A – S0.5, B – S0.4, C- S0.2, D – S0.6, E – S0.6, F – S0.6, G – S0.4 , at 28 days with average for set of seven beams for D1 – S0.5 Second cast set for January CR2089 has achieved too low individual D3 results of beam A – S0.8, B – 0.6, C – S1.0, D – S0.4, E – S0.8, F – 0.9, G – S0.4 at 28 days with average for set of six beams – S0.7
| 02SL - Stations (LUL) | Cxxx-NCR-001008 | NCR | L - PTW: Localised Secondary Lining Underthickness |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-01-29 | 2016-01-19 11:26 | -10 | 2015-03-02 15:48 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The 02/03/15: PTW scans profiles as per the latest 3d scan results have shown some underthickness areas Refer to the PTE-W Ch 16-104 ( Att01.)
| 02SL - Stations (LUL) | Cxxx-NCR-001009 | NCR | L - CP3a/PTW: Secondary lining over-sprayed with MS345 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-06-12 | 2015-04-27 11:35 | -46 | 2015-03-04 15:41 | Civil - Tunnelling | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | 17/02/2015: Overspray of water proofing with secondary, therefore losing 300mm overlay
| 02SL - Stations (LUL) | Cxxx-NCR-001010 | NCR | L - CP10 - Damage to __ Membrane |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-06-12 | 2015-04-01 15:21 | -72 | 2015-03-04 16:01 | Civil - Tunnelling | 4000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | The 26/02/2015 DS: During cleaning works to obtain overlap between layers, a jigger was being used to clean rebound off the 3rd layer of Masterseal. The jigger damaged the Masterseal membrane causing underlying regulating layer to be visible. Refer to the Photo Att01.
| 02SL - Stations (LUL) | Cxxx-NCR-001011 | NCR | L - VD2: VD2 Sheet membrane damaged |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-12-16 | 2016-02-01 16:41 | -319 | 2015-03-12 17:30 | Civil - Tunnelling | 4000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Previous Construction - Interfacing issues | Completed |  | The 24/02/2015 DS: During VD2 condition survey for temporary hand over to Cxxx, sheet membrane has been found damaged in both sides by the metalic structure supporting the VD2 bulkhead. Refer to the photos attached ( Att01. and Att02. )
| 02SL - Stations (LUL) | Cxxx-NCR-001012 | NCR | L - Moorgate Shaft: Damaged Reinforcement Couplers in the first stage concrete slab |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-12-16 | 2016-11-24 11:11 | -22 | 2015-03-13 14:54 | Civil - Tunnelling | 2000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | The 12/03/15 DS - Moorgate Shaft - A number of couplers that have been damaged during the breakout of the temporary invert in the Moorgate shaft. 20 couplers were damaged when breaking out the protection concrete on top of the first stage concrete slab near Ch182.346. Refer to the photos (Att01 Att02) for the damaged couplers photos and Att03 for the location.
| 02SL - Stations (LUL) | Cxxx-NCR-001013 | NCR | L - CP6: Bulking out not done properly |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-10-30 | 2015-09-24 13:16 | -36 | 2015-03-09 12:06 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Previous Construction - Other | Completed |  | L-09/03/2015- DS- Shift 2 PTW/CP6 junction - The primary lining was originally meant to be bulked out back to the primary lining profile fully before any application of the waterproofing or secondary lining. Discussions between __ and Cxxx in design meetings led to __ misunderstanding the situation, from this __ were led to believe that the North Side (opposite the Cross Passage) required bulking out back to primary lining profile and the South Side (the Junction) only required the protection layer to be poured higher to compensate for the additional bulking out. Following these discussions all works beneath the axis were undertaken - waterproofing, invert and sidewalls in PTW Block 16 were completed, including the sidewall in to the CP6 Junction and the start of the CP6 invert. To complete the works in the crown the primary lining required further bulking out. The bulking out started on the North side and could not be completed on the south side (and around the CP6 junction) due to the waterproofing (sheet membrane and connection detail) being installed on the un-bulked out primary lining which could not be sprayed over, therefore leaving the bulking out incomplete and potentially hazardous.
| 02SL - Stations (LUL) | Cxxx-NCR-001014 | NCR | L - PTW-E-Block 8 - Joint close to waterbar |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-12-16 | 2016-01-19 11:57 | -332 | 2015-03-04 15:09 | Civil - Tunnelling | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The DS - 05/12/2014: The edge of the invert slab in PTW-E Block 8 has been found near the waterbar, less than 50mm away. As per the attached photos ( Att01, Att02, At03, Att04 and Att05.) both sides of the invert slab are too close to the waterbar
| 02SL - Stations (LUL) | Cxxx-NCR-001016 | NCR | Overspraying of Masterseal waterproofing with secondary lining concrete at PTW-W/CP1 |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2015-06-03 | 2015-05-05 17:18 | -29 | 2015-03-05 14:05 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Junction PTW-W/CP1 has been oversprayed with secondary lining concrete (1st layer) without leaving a lap of 300mm to achieve a continuous waterproof membrane. It should be noted that this is now the 10th occasion where junctions have been affected by overspraying. As non standard repair methods are required there will be a future risk of a defective membrane.
| 02SL - Stations (LUL) | Cxxx-NCR-001017 | NCR | L - PTW-W Ch27.4 – 31.5m: 2nd layer of secondary lining joint defective at connection to wing wall. |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-12-18 | 2015-12-18 10:11 | 0 | 2015-03-09 08:30 | Tunnelling - Linings - Sprayed Concrete | 4000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | The 01/03/15: 2nd layer of secondary lining sprayed from Ch27.4 – 31.5m. Spray was completed at 15:15. At 17:00 hours, work commenced to clean the lower section of the sec lining spray where it connects with the In-Situ sec lining wing wall. This cleaning was being carried out by an 8T excavator with a bucket attachment. While carrying out these works, the bucket of the excavator came in contact with the shutter that was fixed on top of the wing wall. This action pulled the shutter from the top of the wing wall and resulted in the concrete pouring out. This has now left a gap between the sprayed secondary lining (2nd layer) and the top of the in-situ wing wall. Refer to the Att01 to Att04 for photos of the non conforming joint
| 02SL - Stations (LUL) | Cxxx-NCR-001018 | NCR | L - PTW-W / CP1: Overspraying of SL 1st layer at CP1 Eye area |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-06-24 | 2015-04-22 15:12 | -63 | 2015-03-16 14:30 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The 12/03/2015 NS: In the junction between the platform PTW-W and the cross passage CP1, near the eye, SL 1st layer has been found oversprayed.
| 02SL - Stations (LUL) | Cxxx-NCR-001019 | NCR | L-Low Residual Flexural strength - Beam Testing CR2093 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-02-29 | 2015-12-12 01:10 | -79 | 2015-03-20 17:11 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | LIV spray beam set CR2093 (sprayed in moulds) from January 2015 has achieved too low individual D3 results of beam C – S0.9, D – S1.1, E – S1.2, at 28 days and passed results for beams A – S1.4, B – S1.5, F – S1.5 with average for whole set of six beams - S1.3. At the same time we sprayed additional two panels where panel number 1 achieved too low individual D3 results of beam P1A – S1.0, P1C – S1.1, P1D – S1.2 at 28 days and Panel number 2 achieved pass results – of beam P2A – S2.1, P1B – S2.3, P2C – S1.7, P2D – S2.0 with average for whole set of 8 beams - S1.6 Refer to Att01
| 02SL - Stations (LUL) | Cxxx-NCR-001020 | NCR | L - Strength failure on the running mean strength |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-06-26 | 2015-04-09 11:32 | -78 | 2015-03-18 09:11 | Tunnelling - Tunnelling General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The 17/03/2015: - 90 days samples of Mix P1 C32/40 - CR2059 with result of 71.3 N/mm2, CR2060 with result of 58.3 N/mm2 and CR2061 with result of 58.7 N/mm2 failed to comply with criterion 2. Difference of compressive strength between sample CR2026 (49N/mm2) and next sample CR2059 (71.3N/mm2) leads to increase the standard deviation that has caused failures on the running mean results with failure range between 0.9 – 1.6N/mm². Effected samples are highlighted on attached summary (Att01)
| 02SL - Stations (LUL) | Cxxx-NCR-001021 | NCR | W - CS1: Trimming of thickening layer |  | Contr | __M |  |  | 2015-07-03 | 2015-04-14 11:27 | -80 | 2015-03-25 10:29 | Tunnelling - Linings - Sprayed Concrete | 6000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The 02/03/15: CS1 thickening scans and profiles have shown areas to be trimmed back in the lower and upper areas. Refer to the Att01 and Att02 for the scans and profiles before the trimming.
| 02SL - Stations (LUL) | Cxxx-NCR-001022 | NCR | L - Low Residual Flexural Strength - Beam CR2134 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-02-29 | 2015-12-12 01:20 | -79 | 2015-04-09 10:19 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | LIV spray beam set CR2134 (sprayed in moulds) from February 2015 has achieved too low individual D3 results of beam A – S0.81, B – S0.96, C – S0.81, E – S1.21, F – S0.98 at 28 days and passed results for beams D – S1.54, G – S1.6, with average for whole set of six beams - S1.1; At the same time we sprayed additional two panels where panel number 1 achieved too low individual D3 results of beams P1B – S0.92, P1C – S0.45 and pass results – of beams P1A –S1.34, P1D – S1.28 , Panel number 2 has achieved too low individual D3 results of beams P2B – S0.62, P2C – S0.25, P2D – S0.67, and pass results – of beams P2A –S1.77 at 28 days with average for whole set of 8 beams – S0.9; Also beam from panel 2 number P2D failed on minimum individual result of S1.62 for D1 achieving S1.31;
| 02SL - Stations (LUL) | Cxxx-NCR-001023 | NCR | L - Non conformity of aggregate – sample E1511 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-07-19 | 2015-07-13 12:49 | -6 | 2015-04-10 11:22 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | The 20/03/15: Sample taken from one load at LIV site has shown a grading failure on the 2.0mm (6% out) and (0.7%) on 0.063mm sieves on sample No E1511 Repeated test confirmed higher fines content. Refer to the attachement (Att01)
| 02SL - Stations (LUL) | Cxxx-NCR-001024 | NCR | L - Low Residual Flexural strength - Beam Testing CR2152 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-06-23 | 2016-04-13 14:17 | -436 | 2015-04-13 11:22 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | LIV spray beam set CR2152 (sprayed in moulds) from March 2015 has achieved too low individual D3 results of beam A – S0.95, D – S1.25, E – S0.87, at 28 days and passed results for beams B – S1.37, C – S1.62, F – S1.34, G – S1.76 with average for whole set of six beams - S1.3; At the same time we sprayed additional two panels where panel number 1 achieved too low individual D3 results of beams P1C – S1.09 and pass results – of beams P1A –S1.49, P1B – S1.54, P1D – S1.58 , Panel number 2 has achieved all pass results – of beams P2A –S1.31, P2B –S1.37, P2C – S1.27, P2D –S1.36 at 28 days with average for whole set of 8 beams – S1.4 Refer to the Att01 for beam results summary
| 02SL - Stations (LUL) | Cxxx-NCR-001025 | NCR | L- Moorgate Box: Missing Mix P cubes tests |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-06-23 | 2016-05-23 10:21 | -31 | 2015-04-13 14:23 | Tunnelling - Grouting | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Between the 03/10/13 and 12/12/13 during the first stage of injection in Moorgate, some of the P Mix cubes could not be tested. Cxxx5/C1863/C1865/C1868/C1874/C1997/C2001/C2014 - cubes were damaged during stripping C1797/C1800/C1804/C1978 - cubes were unable to be tested due to their poor condition Refer to the Att01.
| 02SL - Stations (LUL) | Cxxx-NCR-001026 | NCR | L - Moorgate Box: Grout compressive strength did not conform to ITP specified range. |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-10-30 | 2015-10-29 11:09 | -1 | 2015-04-13 15:47 | Tunnelling - Grouting | 1000 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The laboratory in charge of the testing of the strength of the grout cubes sampled on site never tested a complete set of 3no. cubes. Consequently, every result can be challenged versus revision 3 of ITP 50043. Out of the cubes that could be tested, the recorded strengths varied between 0.3N/mm2 and 11.2N/mm2. Sets for 07/10/2013 and 31/10/2013 were recorded below 1N/mm2m and for 26/10/2013 and 27/11/2013 above 4N/mm2. Refer to the Att.01 for the test summary of Mix P Microfine Grout - Phase 1
| 02SL - Stations (LUL) | Cxxx-NCR-001027 | NCR | L - CP3: Overspraying of Masterseal waterproofing with secondary lining concrete |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-04-28 | 2015-04-22 15:30 | -6 | 2015-04-14 16:51 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | PTW-W/CP3 has been oversprayed with secondary lining concrete 2nd layer without leaving a lap of 300mm to achieve a continuous waterproof membrane.
| 02SL - Stations (LUL) | Cxxx-NCR-001028 | NCR | L - PTW/CP7: Overspraying of Masterseal waterproofing with secondary lining concrete |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-07-30 | 2015-04-22 14:46 | -99 | 2015-04-21 14:29 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the spray of the secondary lining in PTW, water proofing has been oversprayed in CP7, therefore losing 300mm overlay
| 02SL - Stations (LUL) | Cxxx-NCR-001029 | NCR | L - PTW/CP4a: Overspraying of Masterseal waterproofing with secondary lining concrete |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-08-21 | 2015-05-22 16:59 | -91 | 2015-05-13 13:19 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the spray of the secondary lining in PTW, water proofing has been oversprayed in CP4a, therefore losing 300mm overlay
| 02SL - Stations (LUL) | Cxxx-NCR-001030 | NCR | L- AP6 Adv 16 LK: One core is less than 250mm |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-07-31 | 2015-06-26 15:42 | -35 | 2015-04-22 17:31 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | The 16/04/15: 5 cores were taken in AP6 Adv 16 LK and core #5 was found less than the 250mm required Refer to the core report attached Att01
| 02SL - Stations (LUL) | Cxxx-NCR-001031 | NCR | L - Moorgate box phase 1: Mix P Grout Bleed test frequency not conform to ITP |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-11-30 | 2015-11-09 15:19 | -21 | 2015-04-20 16:43 | Tunnelling - Grouting | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Bleed tests frequency of 1 test every 5th mix was not respected during the first phase of grouting from Moorgate Box. There was no mention of 3hr bleed to be recorded on the grout sample records distributed to the site operatives. As such, every bleed test that was carried out can be challenged versus revision 3.0 of applicable ITP. Refer to the Att.01 for the Grout Sample Record – Mix P Stage 1
| 02SL - Stations (LUL) | Cxxx-NCR-001032 | NCR | L - Grout Density for Mix S did not conform to ITP specified range |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-10-30 | 2015-10-29 16:04 | -1 | 2015-04-20 15:56 | Tunnelling - Grouting | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | As per the Grout Sample Record - Mix S Stage 1( Att04 ), 5 results of density test were outside of tolerance range. They were recorded on 18/09/2013, 20/09/2013, 21/09/2013, 24/09/2013 and 26/09/2013 at 1.37, 1.36, 1.42, 1.37, and 1.42. Refer to the Att.04 for the Grout Sample Record - Mix S Stage 1 Att.01 not used anymore
| 02SL - Stations (LUL) | Cxxx-NCR-001033 | NCR | L - Grout Bleed for Mix S did not conform to ITP specified range |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-11-27 | 2015-11-09 15:21 | -18 | 2015-04-20 15:59 | Tunnelling - Grouting | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | As per the Grout Sample Record - Mix S Stage 1 (Att04.), 3 results of bleed test were outside of tolerance range, recorded on 10/09/2013 and 2 on 11/09/2013 respectively at 5%, 5% and 4%. Att.01 not used anymore
| 02SL - Stations (LUL) | Cxxx-NCR-001034 | NCR | L - Moorgate box phase 1 - Mix S Grout Viscosity result did not conform to ITP |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-11-27 | 2015-11-09 15:23 | -18 | 2015-04-20 16:02 | Tunnelling - Grouting | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | As per the Grout Sample Record - Mix S Stage 2 (Att04), 2 results of viscosity test were outside of tolerance range, both recorded at 46sec on 05/09/2013 and 17/09/2013. Att.01 not used anymore
| 02SL - Stations (LUL) | Cxxx-NCR-001035 | NCR | L- CP1: __ poor quality in Ch 05-12 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-08-02 | 2015-05-06 15:51 | -88 | 2015-04-24 13:36 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Material | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The 15/04/15: __ Layer 1 in CP1 Ch 05 - 10 sprayed between 22h00 and 23h30. The 17/04/15: __ Layer 2 in CP1 Ch 03 - 10 sprayed between 01h00 and 02h00. The 17/04/15: __ Layer 3 in CP1 Ch 05 - 12 sprayed between 10h00 and 11h00. Refer to the CP1 __ __ Placement checksheets Att01. After completion of Layer 3, de-bonding between the layers has been spotted - Photos Att.02 and Att.03.
| 02SL - Stations (LUL) | Cxxx-NCR-001036 | NCR | W - PTW-E/RCW ch 73.0 to 74.8: Cast invert damaged |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-03-18 | 2016-02-29 16:41 | -18 | 2015-09-18 11:43 | Tunnelling - Tunnelling General | 4000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | On the 15/09/15 DS During breaking out the infill concrete in the transition area PTW-E/RCW, small section of secondary lining cast invert has been damaged. The area is around 1.8m in length. As per drawing Cxxx-MMD-C4-DDB-D061_5_00100 Att.01 , the top layer of steel reinforcement (B1131 Mesh) has been damaged. Refer to Att.02 for the coordinates of the defect.
| 02SL - Stations (LUL) | Cxxx-NCR-001037 | NCR | L - VD7 liner wall pour A01: Pour not completed in one go |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-02-26 | 2016-02-12 09:48 | -14 | 2015-04-22 11:11 | Tunnelling - Linings - In-situ Concrete | 5000 |  | Planning | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | • The 01/04/15: Rebar installation has been completed and after inspection with __ and CRL, rebars were found installed as per the drawings - Refer to the Reinforcement check sheet (Att01.) • The 11/04/15: Pre-pour inspection of the VD7 A01 Liner wall has been done and accepted - Refer to the Pre-pour Check Sheet (Att02.) • The 20/04/15: VD7 A01 Liner wall pour has started Below a summary of what happen during the spray: • 07:00 called batcher to confirm pour • First wagon on site 8:20 tested all ok and started to pour 8:55, all ok flow was good and pump rate was within the prescribed 11m3/hour - Refer to the Att03 • Second load on site 9:00 so all going well • Wagon discharged at 10:50. 11:20 I phoned the batcher to find out where next load was he assured it had been batched and on way • The pump man noticed that the pressures where elevating whilst he was pulsing the line keeping it live, so he blew the line and cleaned. • Freshly grouted line • Third wagon started discharge 11:55 • Fourth wagon discharged 13:15 • At this point everything was good with the slump of the mix and the pour was keeping +/- 11m3/hour • This was the point that the temporary works designer requested a hold in the pour to ensure the hydrostatic head did not exceed that as required by the design. __ had previously contacted the batcher requesting a short delay between loads at this point • The fifth load was batched at 13:40 but did not arrive on site until 14:40 • During this time the pump man was pulsing the line to keep it live when again he noticed the pump pressures elevated, so they split the lines and attempted to blow the line through. • This they struggled with and had to clean the flexi that was connected to the shutter • We connected and pulsed the line, all seemed ok • The fifth load was tested and was found to be out of spec, 550mm and 500mm slump results. The lowest value on the range allowed for the mix was 650mm. So this load was rejected • At this point the pump man was setting up to fully blow lines and clean, but the pump pressures very high, the line was blocked • Checked the mix that was in the shutter and it had also started to set • It was at this point I looked at the situation and called an end to the pour, as all lines down the shaft fully blocked and very little or no life left in the main pour. • At the end VD7 A01 liner wall has been unfinished - Refer to the Photos Att04 and the profiles and cross sections Att07. • In elevation, the concrete forms a mound / step in the middle of the Pour 1 wall. • In cross-section, the concrete is fairly smooth for the back 2/3 of the wall thickness.
| 02SL - Stations (LUL) | Cxxx-NCR-001038 | NCR | L - AP1 Pilot: __ debonding |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-08-19 | 2015-05-19 17:21 | -92 | 2015-05-11 10:43 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Material | Repair | 3 (3-6k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | On 21/04/15 NS, __ in the crown of the AP1 Pilot has been found debonding - Refer to the Att01
| 02SL - Stations (LUL) | Cxxx-NCR-001039 | NCR | L - VD7 liner wall: Line blocked during pour no3 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-08-07 | 2015-07-08 11:31 | -30 | 2015-04-29 15:06 | Tunnelling - Linings - In-situ Concrete | 2500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | On 29/04/15: No check of the concrete line was undertaken prior to the order and attempted pour of wall A2-3 on the north east corner of the Moorgate shaft leading to concrete wagons being rejected as concrete supply line was filled with set concrete from previous pour and the pour was abandoned.
| 02SL - Stations (LUL) | Cxxx-NCR-001040 | NCR | L - AP5/CH5, CH7 and CP5: No P2 mix applied in regulating layer |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-08-08 | 2015-05-28 13:41 | -72 | 2015-04-30 16:29 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | In AP5/CH5, CH7 and CP5 regulating layers have been done with Reader only. Refer to the placement chesksheets of AP5 (Att01), CH7 (Att02) and CP5(Att03.) where only reader has been applied for the regulating layer.
| 02SL - Stations (LUL) | Cxxx-NCR-001041 | NCR | L - AP6 South Adv 14 and 46: Face logs pictures missing |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-08-13 | 2015-05-06 11:58 | -99 | 2015-05-05 15:48 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During April 2015: AP6 Advance 14 picture of the full face has not been done. AP6 Advance 46 picture of the invert has not been done.
| 02SL - Stations (LUL) | Cxxx-NCR-001042 | NCR | L - AP7-W CP3/CP4 over spraying at the junctions |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-08-15 | 2015-05-28 13:51 | -79 | 2015-05-07 15:41 | Tunnelling - Linings - Sprayed Concrete | 6000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | On 07/05/2015, during snagging works in CH1-2, 3d scan has shown areas over sprayed around the eyes in AP7-W CP3 and CP4 Scan and profiles are in Att01 and Att02.
| 02SL - Stations (LUL) | Cxxx-NCR-001043 | NCR | L - CP4a: Pins through Masterseal |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-08-21 | 2015-05-26 16:53 | -87 | 2015-05-13 10:54 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | On 12/05/15 DS: During remedial works on the Masterseal lap in CP4a Block 1 (NCR 1029), pins for rebar were found drilled through the Masterseal. Photos have been provided (Att01.)
| 02SL - Stations (LUL) | Cxxx-NCR-001044 | NCR | L - CH5/CP2: Debonded __ around eye |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-09-06 | 2015-07-17 09:18 | -51 | 2015-05-29 11:47 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Material | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On 15/05/2015 - DS - __ in the crown of the CH5 near CP2 eye has been found debonding - Refer to the Att01
| 02SL - Stations (LUL) | Cxxx-NCR-001045 | NCR | L - LCWa/CP10: Missing early strength tests |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-06-03 | 2015-05-21 14:33 | -13 | 2015-05-20 10:00 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | • Primary Lining • LCWa Advance 55-56 – Missing 1, 3, 6 and 12 hour tests • LCWa Advance 54 – Missing 1 hour test • LCWa Advance 53 – Missing all tests • LCWa Advance 49 – Missing 3 hour test • LCWa Advance 22 – Missing 1 hour test • LCWa Advance 19 – Missing 3 hour test • LCWa Advance 16 – Missing 1 hour • LCWa Advance 14 – Missing 1 and 3 hour tests • LCWa Advance 12 – Missing penetrometer and 12 hour tests • LCWa Advance 10 – Missing 1 and 12 hour tests • LCWa Advance 8 – Missing 3 and 12 hour tests • CP10 L-Bars – Missing 6 and 12 hour tests • CP10 Advance 10 – Missing penetrometer tests • CP10 Advance 10 – Missing 3, 6 and 12 hour tests (Initial) • CP10 Advance 9 – Missing 3, 6 and 12 hour tests • CP10 Advance 6 – Missing penetrometer tests
| 02SL - Stations (LUL) | Cxxx-NCR-001046 | NCR | L - VD7: Hanson concrete delivery and testing fails |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-10-08 | 2015-07-24 15:19 | -76 | 2015-06-30 09:24 | Tunnelling - Linings - In-situ Concrete | 3000 |  | Planning | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | • On 13/05/15 batcher has been informed at 7:15 that a pour will start in VD7 in the morning and that a 720mm target slump (range 650mm – 750mm) is requested. • 08:15: The Fixer Foreman inform the PIC that no concrete has been delivered on site yet, batcher assured it was batched on the road. • 09:00 First load arrived on site, with a tested slump of 470mm by the lab boys. __ has rejected the load • Various calls to the batcher, and ascertained that the second load was due. But the third load would be the wagon we had turned around, it would be possibly 2/2.5 hrs before it was back on site • 9:50 second load on site which again failed the slump test, tested at 590mm • At this point die to the uncertain of loads and the duration between loads, __ decided to stop the delivery’s and reschedule the pour time/date.
| 02SL - Stations (LUL) | Cxxx-NCR-001047 | NCR | L - VD7 lining wall A01 Pour 2: Poor compaction in joint at stop end RHS |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-08-29 | 2015-08-06 10:27 | -23 | 2015-05-21 09:47 | Civil - Tunnelling | 3000 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | L - 20/05/2015: When the right hand stop end was removed voiding along the construction joint between the two pours was evident Refer to the Att01 for evidence
| 02SL - Stations (LUL) | Cxxx-NCR-001048 | NCR | L- VD7 Lining wall Pour A01 - Poor compaction in joint at stop end and LHS |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-12-18 | 2015-10-07 10:41 | -72 | 2015-05-26 10:04 | Tunnelling - Tunnelling General | 3000 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On 21/05/15 when striking the shutter for Pour one it was evident that at the left hand end of the pour, the concrete did not reach the soffit of the pour above. The area affected is approximately 1.15 x 1.4 x 0.150 m Refer to the Att01. for photos and the build sketch
| 02SL - Stations (LUL) | Cxxx-NCR-001049 | NCR | L - CH2 / CP7 & CP8: Over spraying at the junctions |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-09-05 | 2015-06-19 12:23 | -78 | 2015-05-28 14:40 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | On 23/05/2015, during snagging works in CH2, 3d scan has shown areas over sprayed around the eyes in AP7-E CP7 and CP8 Scan and profiles are in Att06 and Att07.
| 02SL - Stations (LUL) | Cxxx-NCR-001050 | NCR | L - RCWa / VD1: Overspraying the __ in the crown with regulating layer |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-12-05 | 2015-11-13 10:55 | -22 | 2015-09-02 16:11 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | L- 30/09/2014 -DS - The __ MS 345 was sprayed throughout VD1 and the seoncdary lining was then sprayed in VD1, the secondary lining started far enough away leaving an overlap for the MS 345 at the junction of RCWa. However, when regulating the Reception Chamber the overlap left was oversprayed in the crown (from 4 O'clock to 8 O'clock) with the regulating layer and hence lossed the 300mm overlap. The MS 345 lap that was oversprayed with regulating layer was about 2m in length. NCR 1126 refers to the loss of overlap detail in the invert, due to mechanical damage when removing backfill.
| 02SL - Stations (LUL) | Cxxx-NCR-001052 | NCR | L - AP1d: Small headwall oversprayed |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-09-05 | 2015-08-03 15:08 | -33 | 2015-05-28 08:59 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | L- NS - 25/05/2015 - Small head wall was over sprayed up to 70mm in various areas. Refer to Att01 and Att02. Only 50mm are left to fit in the fireproof regulating layer instead of the 90mm required. __ have received new scans for AP1d/b Small headwall, which has provided new information to this area in terms of profile and thicknesses. This information shows 2 different things; 1. In certain areas there is under thickness, the majority being between 310-350mm (thickness should be 350mm), although there is also ONE area which is 280mm thick. 2.The head wall has been sprayed out of profile and has been sprayed to the CRL zero line in areas (worst case) – unfortunately this cannot be trimmed back as the head wall will then encounter under thickness. Refer to the scans and profiles scans (Att01 to Att06
| 02SL - Stations (LUL) | Cxxx-NCR-001053 | NCR | L- VD5 - Monitoing targets are sprayed over by MS |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-09-05 | 2015-08-18 10:20 | -18 | 2015-05-28 16:35 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | L- 24/05/2015 - 2 monitoring targets have been sprayed over by Masterseal as seen in Att.01. After investigation the two monitoring targets were installed before the regulating layer. As per Att02. regulation layer check has been signed by all parties whereas some monitoring targets were remaining in place.
| 02SL - Stations (LUL) | Cxxx-NCR-001054 | NCR | L -LCWa Primary Lining Ch 180 to 185 – Localised underthickness |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-08-26 | 2016-07-19 17:46 | -38 | 2015-06-29 10:35 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 3D Scans Thickness for LCWa Primary Lining has been checked and show potential localised underthickness in crown between chainages 180 and 185. Thickness seems to be between 300mm and 490mm instead of 500mm in some area. See 3D scans in att01. for better understanding.
| 02SL - Stations (LUL) | Cxxx-NCR-001055 | NCR | L-VD5- Masterseal on joint of secondary lining |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-09-12 | 2015-08-18 10:21 | -25 | 2015-06-04 11:38 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On 02/06/15 DS during a visual inspection on VD5, it has been seen that the masterseal has been sprayed onto the circumferential joint of the existing secondary lining, at the LCE end. Refer to the Att01. for a photo of the joint oversprayed with Masterseal
| 02SL - Stations (LUL) | Cxxx-NCR-001056 | NCR | L- CH2-AP7 - Hollow Spots |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-09-13 | 2015-08-10 14:06 | -34 | 2015-06-05 10:58 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On 29/05/2015 - NS - Shift 3 - During snagging works in PTE-W/CH2 thickening, construction team found hollow spot in the crown. - Dimension: around 4.5m2 - Depth 200m-300mm - Thickness of void: 30-90mm - Position : Chainage 57-59 Refer to the attachement 01 , 02 and 03
| 02SL - Stations (LUL) | Cxxx-NCR-001057 | NCR | L - CH2: No sump installed |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-10-08 | 2015-07-17 09:42 | -83 | 2015-06-30 15:58 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | • The thickenings in CH2 have been completed in the invert without the indicated sumps installed as per IFC drawings. • Cxxx requirement for these sump have not been taken into consideration in the Cxxx design.
| 02SL - Stations (LUL) | Cxxx-NCR-001058 | NCR | L - Cross Passages: Missing tests |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-07-31 | 2015-07-13 12:56 | -18 | 2015-06-24 10:08 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | • CP1 – Advance 3 – Missing 3 hour test (ATT.01) • CP1 – Advance 6 – Missing 3 hour test (ATT.02) • CP1 – Advance 9 – Missing 6 and 12 hour tests (ATT.03) • CP1 – Advance 11 – Missing 1 hour test (ATT.04) • CP1 – Advance L-Bars – Missing 6 hour test (ATT.05) • CP2 – Advance 3 – Missing 3 and 6 hour tests (ATT.06) • CP2 – Advance L-Bars – Missing 3 hour test (ATT.07) • CP2 – Advance 6 – Missing 3 and 6 hour tests (ATT.08) • CP2 – Advance 9 – Missing 1, 3, 6 and 12 hour tests (ATT.09) • CP2 – Advance L-Bars 2 – Missing 3 hour test (ATT.10) • CP2 – Advance L-Bars – Shotcrete placement checksheet specifies that P1 mix has been used for L-Bar(ATT.39). This is not what has been sprayed - Refer to the last line of the Proposed answer for the evidences. • CP3 – L-Bars – Missing 3 and 6 hour tests (ATT.11) • CP3 – Advance 3 – Missing 1 hour test (ATT.12) • CP3 – Advance 9 – Missing 1, 3 and 12 hour tests (ATT.13) • CP3 – Advance 12 – Missing 3 hour test (ATT.14) • CP3 – Advance L-Bars – Reinforcement checksheet not produced for this advance. • CP4 – Advance 4 – Missing 1, 3, 6 and 12 hour tests (ATT.15) • CP4 – Advance 11 – No flow test results (ATT.16) • CP4 – Advance 12+13 – Missing 1, 3 and 6 hour tests (ATT.17) • CP3a – Advance 1+2 – Missing 3, 6 and 12 hour tests (ATT.18) • CP3a – Advance 3 – Missing 3 hour test (ATT.19) • CP3a – Advance 4 – Missing 1 hour test (ATT.20) • CP3a – Advance 7 – Missing 3 hour test (ATT.21) • CP3a – Advance 10 – Missing 12 hour test (ATT.22) • CP3a – Advance 10 – No flow test results (ATT.23) • CP3a – Advance 13 – Missing 1 and 12 hour tests & Understrength (ATT.24) • CP3a – Advance 15+16 – No flow test results (ATT.25) • CP4a – Advance 3 – Missing 1 and 3 hour tests (ATT.26) • CP4a – Advance 4 – Missing 1, 6 and 12 hour tests (ATT.27) • CP4a – Advance 6 – Missing 3, 6 and 12 hour tests (ATT.28) • CP4a – Advance 7 – Missing 6 and 12 hour tests (ATT.29) • CP4a – Advance 10 – Missing 3 hour test (ATT.30) • CP4a – Advance 14 – Missing 3, 6 and 12 hour tests (ATT.31) • CP7 – Advance 7 – Missing 3, 6 and 12 hour tests (ATT.32) • CP8 – Advance 1+2 – Missing 3 hour test (ATT.33) • CP8 – Advance 15 – Missing 1, 6 and 12 hour tests (ATT.34) • CP8 – Advance 18 – Missing 6 and 12 hour tests (ATT.35) • CP8 – Advance 21+22 – Panel damaged after 15mins, no testing as a result (ATT.36)
| 02SL - Stations (LUL) | Cxxx-NCR-001059 | NCR | L- AP6 - Underthickness in advance 166 - 167 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-10-03 | 2015-07-17 09:26 | -78 | 2015-06-25 16:43 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Previous Construction - Improper As Built | Completed |  | On 15/05/15: During excavation of the advance 166-167, obstructions was found in the crown . __, with CRL agreement, have made a pocket excavation and have installed some flexcell around it in order to control a water leak. Refer to the Att01 for the photos of the obstruction and the flexcell installed. Primary lining has been sprayed and at the location of the flexcell the spray has been done aiming the +0mm with the beamer ( theorical lining ) After completion of the primary lining, proof drilling have done and in a very located area (200mm x 300mm) 220mm found instead of the 250mm required. Refer to the Att02. for the proof drilling results.
| 02SL - Stations (LUL) | Cxxx-NCR-001060 | NCR | L-AP6 Thickening: Non conforming cores (CR2269, CR2270 and CR2274) |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-07-22 | 2016-04-29 09:43 | -84 | 2015-06-18 11:19 | Tunnelling - Linings - Sprayed Concrete | 50000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • On 15/06/15: Whilst breaking out , the quality of the reinforcement encapsulations in the chamber are checked. Three cores have been taken out of AP6a thickening next to AP10 eye. CR2268 - The first core in right knee shows a good encapsulation of the reinforcement CR2269 - The first core in the left shoulder presents some voids CR2270 - The second core taken in the left shoulder shows also some sign of bad encapsulation. This additional core have been taken due to the poor quality of the first one from the same location Refer to the Att01 for the full core report. • On following day ( 16/06/15 ) three additional cores have been taken in the Left Knee ( CR2274 ) and major voids / bad encapsulation have been found - Refer to the Att01b • After investigation it seems that the rebar installation was not done proprely in the AP6a thickening. Refer to Att03. for photos of the rebar thicknening. • CR2283 - A core taken from AP6a/AP10 - Thickening right shoulder - shows signs of major voids (>30m). - No laminations or cracks. (Att.09) • Cores location and grading can be seen in Att.13
| 02SL - Stations (LUL) | Cxxx-NCR-001061 | NCR | L-AP1d Transition - Rebar not casted in wingwall |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-09-25 | 2015-08-03 12:56 | -53 | 2015-06-17 11:47 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | L - 14/06/2015 - One of the reinforcement bars (BM 257 FF1) was not cast in the wingwall on the south side of AP1d transition, so not per design. The reinforcement bar now protrudes out the side of the wingwall.( Att.01)
| 02SL - Stations (LUL) | Cxxx-NCR-001062 | NCR | W - Compensation Grouting: Missing or failed tests |  | Contr | __M |  |  | 2015-07-10 | 2015-07-03 11:24 | -7 | 2015-06-26 16:20 | Geotechnical Engineering - Compensation Grouting | 1000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | The ITP indicates a range of viscosity for grout mix S. The ITP was not updated to reflect a change of grout used e.g. Mix S to Mix A, which has a different viscosity. As a result of not updating the ITP the viscosity tolerances as given in the ITP were not respected for tests carried out during the works. See Att01. and Att02. “Grout sample records – WHI” for a complete list of results. The ITP also gives a frequency of cubes to be sampled in order to undertake strength tests, however 36 sets out of 183 (20%) for Mix A were either not recorded or it was not possible to test the sample. Refer to Att03. and Att04. In accordance with the ITP samples were to be tested for grout stiffness, these samples were not tested.
| 02SL - Stations (LUL) | Cxxx-NCR-001063 | NCR | L - CH5 Sump constructed slightly out of tolerance |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-08-28 | 2015-08-28 12:00 | 0 | 2015-06-23 14:08 | Tunnelling - Tunnelling General | 1000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Due to the lack of, and inaccurate information provided by the CRL Designer (Cxxx) in PMI 944 (i.e. no IFC drawings or bar bending schedules), the sump has been constructed slightly out of tolerance. PMI 944 gave __ two different pieces of information about the position of the sump (500mm offset from axis and SOP which is only 212mm away from it). The sump has been constructed larger than the original design (see attached as-built survey - Att.01)
| 02SL - Stations (LUL) | Cxxx-NCR-001064 | NCR | L- AP6 Adv 157: One core is less than 250mm |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-10-04 | 2015-08-10 14:11 | -55 | 2015-06-26 08:53 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the coring of the lining of the right knee of advance 157 for laboratory testing, out of the 5 cores that were taken, 1 no. core was measured to be 240mm (10mm short of the minimum thickness). Refer to the core report Att03.
| 02SL - Stations (LUL) | Cxxx-NCR-001065 | NCR | L-AP1d - Lack of reinforcement cover on side walls |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-10-03 | 2015-08-07 11:36 | -57 | 2015-06-25 10:12 | Tunnelling - Linings - In-situ Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | On the 23/06/15: AP1d, the reinforcement cover in the side walls is under the required specification of 70mm, however there is minimum cover of 50mm. Please see Att.01.
| 02SL - Stations (LUL) | Cxxx-NCR-001066 | NCR | L - CH5: Missing bars in the wingwalls |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-10-07 | 2015-08-10 14:08 | -58 | 2015-06-29 10:01 | Train - Interfaces | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | On 27/06/15, in CH5 23 B16 bars instead of 24 have been installed in the wingwalls near CP2 East and in the west it is 21 B16 bars that have been installed instead of the 19 bars needed. In CH5/CP1 West 21 B16 bars have been installed instead of the 22 needed. Refer to the drawings Att02 and Att04 for the location and information of the bars missing.
| 02SL - Stations (LUL) | Cxxx-NCR-001067 | NCR | L - Moorgate box phase 3 – Coreholes relocation without Project Manager’s validation |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-11-06 | 2015-09-18 00:18 | -49 | 2015-06-30 10:36 | Tunnelling - Grouting | 1000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | During installation of phase 3 boreholes, __ was struck with large amounts of running water and sand, seemingly coming out of the contact between the Dwall and the ground to treat. Under CRL instruction, __ is to install 50 cores in the Dwall and start a contact grouting exercise. However, __ moved coreholes B2 and C2 without informing the Project manager. Refer to Att02. for the location of the coreholes. B2 was cored on 23rd June 2015, in the stop end outside AP9 footprint. C2 was cored on 22nd June 2015, relocated inside the footprint of AP9. Refer to the Att02. for the location of the coreholes
| 02SL - Stations (LUL) | Cxxx-NCR-001068 | NCR | L- AP1 Hollow Area |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-11-05 | 2015-08-10 13:39 | -87 | 2015-07-28 17:09 | Tunnelling - Linings - Sprayed Concrete | 4000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On 30/06/2015 - During snagging works in AP1 SL , the construction team found hollow spot in the crown. - Dimension: 2.5m x 1m - Depth 150m-200mm - Position : Chainage 116.5 Refer to the Att01 for the details
| 02SL - Stations (LUL) | Cxxx-NCR-001069 | NCR | L - VD7 Pour 12: Cracks and water ingress in the lining |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-12-18 | 2015-10-30 09:05 | -49 | 2015-07-15 10:10 | Tunnelling - Linings - In-situ Concrete | 2000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On the 02/07/15 during a routine site visit, Section Engineeer has spotted some cracks in the VD7 pour 12. After investigation, 13 cracks have been found - refer to the Att01 for the location and the photos of the cracks
| 02SL - Stations (LUL) | Cxxx-NCR-001070 | NCR | L - __ meter (Sr no. 6159) and __ (Sr PB20160) found out of calibration |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-10-16 | 2015-07-22 17:29 | -86 | 2015-07-08 10:55 | Tunnelling - Tunnelling General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Other management problem | Completed |  | On 29/04/15 during __ Waterproofing activities surveillance __ meter ( Sr no. 6159 ) and __ (Sr PB20160) were found out of calibration. As per Att01. Calibration was due 13 March 2015 for the __ meter ( Sr no. 6159 ) and 27/02/14 for the __ (Sr PB20160) Att03. For more details on the surveillance No. 79 please refer to the Cxxx-__M-O4-RGN-CR092-50112 for the __ Waterproofing activities at LIV surveillance report
| 02SL - Stations (LUL) | Cxxx-NCR-001071 | NCR | L- AP1 Hollow Spots - Chainage 116.5 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-11-08 | 2015-08-10 12:54 | -90 | 2015-07-31 11:26 | Tunnelling - Linings - Sprayed Concrete | 4000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On 08/07/15 for the closure of the NCR 1068, hammer tapping was carried out and two additional hollow spots were found as per Att.01. Dimension 1: 0.2mm x 0.250mm Position 1 : Chainage 116.5 Depth 1: ~10/15mm Dimension 2: 0.8mm x 1.0mm Position 2: Chainage 116.5 Depth 2: up to 470mm
| 02SL - Stations (LUL) | Cxxx-NCR-001072 | NCR | L- AP1 - Reinforcement Not Recorded On Checksheet |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-11-12 | 2015-08-07 10:09 | -97 | 2015-08-04 10:18 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | On 03/07/2015 __ Form D3-26 Reinforcement checksheet was signed off with some rebars installed but not recorded. (Att.01) The following information isn't recorded: 17 hoop bars above CP9 (bar mark 75) installed but not signed off 17 hoop bars above CP10 (bar mark 86) installed but not signed off And bar marks 105, 108 and 112 between CP9 and CP10 eyes (3 bar marks lapped, bottom one coupled into wingwall)
| 02SL - Stations (LUL) | Cxxx-NCR-001073 | NCR | L - AP7W Ch15: Underthickness found in the knee |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-05-31 | 2017-06-07 15:14 | 7 | 2015-07-13 11:32 | Tunnelling - Linings - Sprayed Concrete | 2000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | On 12/07/15 during snagging works, proof drillings have shown an area of underspray with a depth of 180mm to 200mm. Resulting in a total thickness of the primary lining below the required 300mm. This can be confirmed by the email attached (Att.A ) As detailed in the proposed answer area has been cleaned and resprayed, new beamer records issued showing sufficient thickness everywhere ( see Att.10 ). But on the 15/08/15 primary thickness scans have shown that areas where still below 300mm, see Att.08a. Please note that in Att.08a the title is incorrect, there is no thicknening in AP7W ch 7 to 27, correct title should be Primary lining thickness.
| 02SL - Stations (LUL) | Cxxx-NCR-001074 | NCR | L - AP1: Under thickness of the fire regulating layer bays |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-10-25 | 2015-08-13 16:18 | -73 | 2015-07-17 11:41 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On 16/07/15 after issuing the scans of the fire regulating layer thickness in the AP1 bays 0 to 5 showed areas that were thin. Further to this on 23/07/2015 additional scans were released which showed additional areas of under thickness. Please see the attached mark up Att01. Profiles of the underthickness are also attached, see Att02. After investigating these areas with Cxxx three areas were identified which needed remediating as these areas were severely underthickness and of a reasonable size, see Att01 and Att02 and detailed below. Ch. 104 - 2 o'clock look towards blomfield - 2.0m2 area Ch. 125 - 2 o'clock look towards blomfield - 1.0m2 area Ch. 137 - 5 o'clock look towards blomfield - 4.0m2 area
| 02SL - Stations (LUL) | Cxxx-NCR-001075 | NCR | L - AP1: Non conforming regulating layer profile |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-10-25 | 2015-08-10 12:22 | -76 | 2015-07-17 12:16 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On 16/07/15 after issuing the profile scans of the fire regulating layer in the AP1 bays 0 to 5, some tight spots have been found Refer to the Att01 for the profile scans of the fire proofing regulating layer Bay 0 to 5 in AP1
| 02SL - Stations (LUL) | Cxxx-NCR-001076 | NCR | Flexural strength testing being undertaken by a non UKAS accredited organisation and no CRL PM acceptance in place. |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2015-11-05 | 2015-11-04 13:31 | -1 | 2015-07-21 09:44 | Civil - Tunnelling | 3000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Improper resource allocation | Completed |  | During a planned Crossrail surveillance which was undertaken on 25th June 2015 to review flexural beam failures, it was that testing was being undertaken by University of Greenwich. During a post surveillance examination of University of Greenwich’s UKAS accreditation schedule it was identified that the organisation is not UKAS accredited to undertake flexural beam testing; furthermore it was noted that __ did not have Crossrail Project Managers (PMs) acceptance to alleviate the UKAS requirement. Works Information Vol 2B Part 20.8 states “All on-site and off-site testing shall be carried out by laboratories accredited by UKAS or similar ….. The requirement for UKAS accreditation may be waived for the testing of systems and their components, subject to an alternative testing proposal by the Contractor and the acceptance of the proposal by the Project Manager.”
| 02SL - Stations (LUL) | Cxxx-NCR-001077 | NCR | L - CP1 and CP2 SL: Missings tests and/or documentation |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-08-17 | 2017-08-14 09:55 | -3 | 2017-08-04 07:55 | Tunnelling - Linings - In-situ Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | • A) Cxxx-__M-C4-LLG-C101-50238 Deliverables Records for CP1 and CP2 Sprayed Waterproofing Membrane: - Missing Pre-Placement Checksheets (__ Form D3-98 - 1/4) for CP1 Block 1 ( ch 10 to 12.108 ) Layer 2 - Missing __ Placement Checksheet (__ Form D3-101 2/4) for CP1 Block 1 ( ch 10 to 12.108 ) Layer 2 - Missing D3-109 Spraying Consumption Rate (D3-109) for CP1 and CP2 B) Cxxx-__M-C4-LLG-C101-50240 Deliverables Records for CP1 and CP2 Cast in-situ works: - Missing Post-pour check sheets ( __ Form D3-88 ) for CP1 Block 1 and CP2 Block 2.
| 02SL - Stations (LUL) | Cxxx-NCR-001078 | NCR | L - Compressive strength failure of mix RL2 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-11-29 | 2015-10-28 15:01 | -32 | 2015-08-21 15:01 | Materials - General | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | As per KT 20 strengths to be under the two criterions below: - Criterion 1 being, than mean of “n” results should be equal or exceed design strength +4N/mm² - Criterion 2 being, that any individual test result to be less than design strength -4N/mm². The 28 days samples CR2297, CR2310, CR2312, CR2314, CR2316 and CR2317 taken between 07/07/15 and 20/07/15 failed to comply with criterion 1 and sample CR2297 failed to comply with criterion 2. Effected samples are highlighted on attached summary.
| 02SL - Stations (LUL) | Cxxx-NCR-001079 | NCR | L - CP9: Under Thickness Of Fire Regulating Layer |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-11-12 | 2015-08-12 08:14 | -92 | 2015-08-04 11:02 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On 31/07/15 after issuing the scans of the fire regulating layer thickness in the CP9 , some thickness have been spotted below the requirements. Missing 10mm approximately in an area of 1.5m2 in ch28.5 Refer to Att.01 for the scans and profile thickness
| 02SL - Stations (LUL) | Cxxx-NCR-001080 | NCR | L- CP9, CH32-20, Test of substrate temperature not done |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-11-12 | 2015-08-07 10:17 | -97 | 2015-08-04 17:34 | Tunnelling - Tunnelling General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | L - 24/07/2015 - During the CRL surveillance of the fire proofing activities in CP9 (CH 32-20), a number of checksheets were checked. It has been found that on the Permit to spray fireproofing (Att.01), the question ' temperature is within 15-30 degrees' wasnt ticked. As the form wasnt filled out correctly , it makes it non - compliant.
| 02SL - Stations (LUL) | Cxxx-NCR-001081 | NCR | L - CP10: Hollow Area in Secondary Lining |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-11-08 | 2015-08-10 13:45 | -90 | 2015-07-31 13:50 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | On 28/07/15 Following hammer testing in CP10 (Att.01), voids have been found in the secondary lining 1st and 2nd layers on both sides of the tunnel under axis level. Att.01 shows a red line, underneath red line is the hollow area. The line is at level 77.461, where the sheet membrane ends. Refer to the Att02 and Att03 for the CP10 Photos After the removal of the delaminated 2nd layer voids were still found in the 1st layer.
| 02SL - Stations (LUL) | Cxxx-NCR-001082 | NCR | L - CP3/CP3A: MS 1st layer sprayed without holes backfilled |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-03-18 | 2016-01-19 11:45 | -59 | 2015-08-25 11:42 | Tunnelling - Tunnelling General | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | L-Day Shift - 24/07/2015 - DS - In CP3/CP3a when the fixing were removed , holes were left behind. Prior to the masterseal being sprayed, the holes should have been filled in with grout but this was not done. The permit to cover also didn't reflect the ongoing works and was signed off before repairs took place - Refer to the Att03 for the final visual inspection sing off by all parties. The masterseal was sprayed in this area hence the holes have been noticed (Att04.). There is also concern about the curing of the masterseal in the holes.
| 02SL - Stations (LUL) | Cxxx-NCR-001083 | NCR | L- CP10 - Non conforming regulating layer profile |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-12-18 | 2015-10-29 12:24 | -50 | 2015-08-03 10:03 | Tunnelling - Tunnelling General | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | L- On 02/08/15 after issuing the profile scans of the fire regulating layer in CP10, two tight spots have been found, bot are around 1m2 and are located on East (right) hand side of CP10 and under axis level (See Att.01). Refer to the Att01 for the fire proofing regulating layer profile scans and Att02. for the fire proofing regulating layer profiles, which shows encroachment. The first tight spot closest to the axis shows encroachment up to 30mm. The second tight spot shows encroachment up to 10 mm
| 02SL - Stations (LUL) | Cxxx-NCR-001084 | NCR | No accepted MCR in place for the RL2 2kg/m3 fire proofing mix design which is being used in the works. |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2015-11-17 | 2015-11-13 10:24 | -4 | 2015-08-03 10:29 | Civil - Tunnelling | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | During a surveillance undertaken on 23rd, 24th and 28th July 2015 which looked at fire proofing application and documentation, it was identified that the MCR for the revised 2kg fireproofing mix had not been accepted, with the mix being submitted to CRL (22nd July 2015) for approval after the mix had started to be used to fireproof AP1 and CP9 at Liverpool Street. Following review of MCR (Cxxx-__M-C-RGN-CR092-50115), Rev 1 and Rev 2 contained the __ test report for the 1kg polypropylene mix design with Rev 2 being Decal Code 2 since July 2013. Rev 3 of the MCR had been submitted on 22nd July 2015 for CRL approval which contained the new 2kg fireproof mix design and __ test report; it was detailed that the 2kg mix was a new mix to that of Rev 2 with the 1kg mix becoming redundant. Following review of eB Rev 3 had yet to be approved by CRL/ Cxxx and CRL CEG; as such the new concrete mix design was being incorporated in the works with out acceptance. Works Information Vol 2B Part 13.3.8 states “The Contractor shall utilise the template attached in Appendix 13J (MCR) for the purpose of recording material and product acceptances for the works and submit such records to the Project Manager for acceptance”. Additionally CRL and Cxxx comments from Rev 2 of the MCR had not been addressed for approximately 24 months, which is against the contractual period of reply. Under CRL Document Management Procedure Clause 7 a Decal Code 2 refers to “Not Accepted. Revise and resubmit. Work may proceed subject to incorporation of changes indicated”. Works Information Vol 2B Part 14.1 states “…Any further revisions, submissions and responses by the Contractor or Project Manager shall be made within the period for reply”. This NCR was raised resulting from the surveillance visit to ensure appropriate measures and corrective actions are adopted to ensure future materials have MCRs in place before incorporation in the works, and MCR comments are addressed within the contractual period of reply.
| 02SL - Stations (LUL) | Cxxx-NCR-001085 | NCR | L-CP9-Non conforming regulating layer profile |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-11-12 | 2015-10-27 14:42 | -16 | 2015-08-04 16:10 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | On 02/08/15 after issuing the profile scans of the fire regulating layer in the CP9 some tight spots have been found. The tight spots are around the joint that connects CP9 to AP1. This was using the old method where timber stopends were being used, therefore overspray was achieved on the joint at CH 4.5. Tight spots are up to -10mm (one area in the crown), the remainig smaller ones around are just over the Zero line. Refer to the Att01 for the profile scans of the fire proofing regulating layer and Att02 for the thickness profiles
| 02SL - Stations (LUL) | Cxxx-NCR-001086 | NCR | L - AP1 PL: Missing tests, Beamer Profile |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-04-15 | 2016-02-04 09:27 | -71 | 2016-02-03 10:03 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | - AP1 – Advance 1 – No flow test results for Initial and sampling after start of spraying for Primary (See Att01) - AP1 – Advance 11 – Flow Test sampling after start of spraying for Initial (See Att02) - AP1 – Advance 13 – Flow Test sampling after start of spraying for Primary (See Att03) - AP1 – Advance 20 – Compliance with flow test frequencies not adhered for Initial and Primary (See Att04) - AP1 – Advance 36 – Beamer point in left shoulder indicates lining is thin (414mm instead of 500mm) (See Att05) - AP1 – Advance 40 – Flow Test sampling after start of spraying for Initial and Primary (See Att06) - AP1 – Advance 41 – Flow Test sampling after start of spraying for Initial and Primary (See Att07) - AP1 – Advance 44 – Flow Test sampling after start of spraying for Initial and Compliance with flow test frequencies not adhered for Primary (See Att08) - AP1 – Advance 45 – Compliance with flow test frequencies not adhered for Primary (See Att09) - AP1 – Advance 51 – Flow Test sampling after start of spraying for Initial and Primary (See Att10) - AP1 – Advance 59 – Flow Test sampling after start of spraying for Initial and Primary (See Att11) - AP1 – Advance 60 – Early strength test frequency missed at 1 hour (See Att12) - AP1 – Advance 63 – Beamer point in left shoulder indicates lining is thin (331mm instead of 400mm) (See Att13) - AP1 – Advance 66 – Early strength test frequency missed at 1 hour (See Att14) - AP1 – Advance 67 – Flow Test sampling after start of spraying for Initial and No flow test results for Primary (See Att15) - AP1 – Advance 76 – Flow Test sampling after start of spraying for Initial (See Att16) - AP1 – Advance 81-82 – Flow Test sampling after start of spraying for Initial and Primary (See Att17) - AP1 – Deep Invert Advance 7 – No flow test results for Initial and Compliance with flow test frequencies not adhered for Primary (See Att18) - AP1 – Deep Invert Advance 17 – Flow Test sampling after start of spraying for Initial and Primary (See Att19) - AP1 – Deep Invert Advance 18 – Flow Test sampling after start of spraying for Initial (See Att20) - AP1 – Deep Invert Advance 22 – Profile within the tunnel envelope to 10mm (See Att21) - AP1 – Deep Invert Advance 22 – Low Early strength test result at 1 hour (See Att22) - AP1 Thickening: 3 reinforcement check sheets with typo refering to P revisions of the drawing instead of C revisions used on site (see Att25).
| 02SL - Stations (LUL) | Cxxx-NCR-001087 | NCR | L - AP6a/AP10b - One bar exposed |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-11-27 | 2015-09-24 13:02 | -64 | 2015-08-19 09:49 | Tunnelling - Tunnelling General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On the 03/08/15 NS During the opening works for AP10b, a 16mm bar protruding was struck by an excavator and cut as shown in Att.01. Only one bar is damanged Refer to the Att01. for the photos and the location of the rebar damaged
| 02SL - Stations (LUL) | Cxxx-NCR-001088 | NCR | L- AP1 - Overspray Of Masterseal at Blomfield Box End |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-11-20 | 2015-08-18 10:24 | -94 | 2015-08-12 11:25 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | At the end of AP1 @chainage 139.456 a stopend was put in place to spray the secondary lining up to. Unfortunately the __ masterseal overlap was over sprayed and the connection was lost. (Att.01, 02 , 03)
| 02SL - Stations (LUL) | Cxxx-NCR-001089 | NCR | L - AP1: Concrete drying shrinkage failure of mix RL2 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-12-05 | 2015-10-28 15:04 | -38 | 2015-08-27 11:31 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | 28 days samples CR2292, CR2299, CR2304 and CR2306 taken between 07/07/15 and 15/07/15 failed to comply with specification limit in failure range between 0.005% and 0.012%. Effected samples are presented on the Att01 to Att04.
| 02SL - Stations (LUL) | Cxxx-NCR-001090 | NCR | L-AP1d Transition - Non Conforming Profile |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-11-21 | 2015-10-28 14:55 | -24 | 2015-08-13 14:22 | Tunnelling - Tunnelling General | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | L- 12/08/2015 -In AP1d (ie the “cupboard”), after receiving the scans for the invert and wing walls, it has shown that the top of the wing wall on the northern side of the transition area is out of tolerance up to 30mm (In one local area up to 40mm).
| 02SL - Stations (LUL) | Cxxx-NCR-001091 | NCR | L - VD7 Liner Wall Pour A01 LHS: Repair works done incorrectly |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-11-27 | 2015-09-29 15:30 | -59 | 2015-08-19 10:03 | Tunnelling - Linings - In-situ Concrete | 2500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On the 22/08/15 a meeting with CRL, Cxxx and __ has been organised to agreed on the appropriate repair works to be done in VD7 lining wall LHS Pour 1 2 (Cxxx-NCR-001048) It was agreed that one hydrophilic strip and one __ hose needed to be installed as per Att01. prior filling the area with Parex LA Repair. On the 01/08/15 repair works were done and __ hose glued on the upper part instead of the bottom as agreed during the meeting. Refer to Att02 and Att03. for photos, the repair checksheet and location of the __ hose.
| 02SL - Stations (LUL) | Cxxx-NCR-001092 | NCR | W - PTE-E SL: Missing tests and documentation |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-02-24 | 2017-03-02 14:12 | 6 | 2016-12-06 17:30 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | - Cxxx-__M-C4-LLG-D061-50074 Deliverables PTE-E Regulating Layer: 1) Missing Invert Hammer Testing checksheet (__ Form D3-80) for PTE-E ch.18-100. - Cxxx-__M-C4-LLG-D061-50092 Deliverables PTE-E Ch.9-99m, __ Sprayed Waterproofing Membrane: 2) Missing Wet film thickness Test (__ Form D3-101) for PTE-E 1st layer: ch. 87-99 and 3rd layer: ch. 24-60. 3) Missing Spraying Consumption Rate – Material Site Record checksheet (__ Form D3-100) for PTE-E 1st layer: ch 87-99 and 3rd layer: ch 24-60. - Cxxx-__M-C4-LLG-D061-50120 Deliverables PTE-E Cast In-Situ Inverts and Sidewalls 4) Missing Secondary Lining Concrete Pour Checksheet (__ Form D3-84) for PTE-E Block 7 ch.32.5 to 44.135 - Protective Concrete ITP Item C3, C4 and 2.4 5) Missing Secondary Lining Concrete Pour Checksheet (__ Form D3-84) for the PTE-E Block 7 ch.32.5 to 44.135,RHS - Sidewall Concrete ITP Item C3, C4, 3.6 and 3.7 - Cxxx-__M-C4-LLG-D061-50159 Deliverables PTE-E Secondary 2nd 1st Layer through Fireproofing Layer ch.9 - 68 6) Missing Hammer Testing Checksheet (__ Form D3-80) for PTE-E Secondary 1st Layer ch.58-60 and Fireproofing Layer ch.15.5-18.
| 02SL - Stations (LUL) | Cxxx-NCR-001093 | NCR | W - PTE-W SL: Missing Test and documentation |  | Contr | __M |  |  | 2017-07-20 | 2017-07-19 14:07 | -1 | 2016-05-31 14:53 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • A) Cxxx-__M-C4-LLG-D061-50109 Deliverable Records for PTE-W Regulation Layer, Sheet Membrane and Sprayed Waterproofing 1) Regulation Layer: ITP item C5 Missing Hammer Testing Checksheet (__ Form D3-80) for PTE-W invert ch. 20 to 82.5. • B) Cxxx-__M-C4-LLG-D061-50219 Deliverable Records for PTE-W Secondary 1st Layer, Secondary 2nd Layer and Fireproofing Layer 2) Secondary Lining 1st layer: ITP item C5 Missing Hammer testing check sheet (__ form D3-80) for PTE-W crown ch. 18-21 3) Secondary lining 2nd layer: ITP item C2, C4, 1.1, 4.2, 4.3, 4.4, 4.6, 5.2, 5.3, 5.4 and 5.5 Missing Secondary lining placement check sheet (__ form D3-86) for PTE-W crown ch. 18-20 • C) Cxxx-__M-C4-LLG-D061-50220 Deliverable Records for PTE-W Bulking Layer, Secondary 1st Layer and Fireproofing Layer 4) Reader strip: ITP items 1.1, 5.3, 5.11, 6.11, 6.12, 6.13, 6.14, 6.15 Missing Secondary Lining Placement checksheet (__ Form D3-86) for PTE-W Reader Strop ch.42-54 and ch.80-102.
| 02SL - Stations (LUL) | Cxxx-NCR-001094 | NCR | W - PTW-E SL: Missing Test and documentation |  | Contr | __M |  |  | 2017-04-30 | 2017-05-26 10:13 | 26 | 2015-12-15 10:35 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Cxxx-__M-C4-LLG-D061-50123 Deliverable for PTW-E Regulating Layer (W008) 1) Regulation: ITP item C.1 No early strength tests were performed during the regulation layer in PTW-E 2) Regulation: ITP item C.2 No rebound test was performed during the time period in which PTW-E was constructed 3) Regulation: ITP item C4 Missing Hammer Testing Checksheet (__ Form D3-80) for PTW-E regulation layer Crown RHS Ch. 46 to 100 and LHS Ch.57 to 66 and Invert Ch.7.5 to 100. 4) Regulation: ITP item 2.1 Permit to Cover signed 14/11/2013 for Invert Ch. 58-75 explicitly stating that Ch. 61-64 and Ch. 66-68 must not be sprayed due to 2 open NCR’s in the area (NCRs 538 and 539). That same day, the entire area was covered with regulating layer, from Ch. 59-74. It is not clear whether this was approved by all parties prior to spraying, as the cover sheet for the Permit to Cover was not amended nor was any gap noted on the placement checksheets. (See Att01. and Att02.) Cxxx-__M-C4-LLG-D061-50101 Deliverables for PTW-E Sheet Waterproofing Membrane (W008) 5) Sheet Waterproofing: ITP item 1.2 Missing Acceptance of Substrate for Waterproofing Layer (__ Form D3-96) for PTW-E ch. 7.5-10 Cxxx-__M-C4-LLG-D061-50124 Deliverables for PTW-E Cast In-Situ Inverts and Sidewalls (W008) 6) Cast In-Situ Invert: ITP item 4.1, ITP item 4.2, ITP item 4.3, ITP item 4.4, ITP item 4.5, Missing Secondary Lining Concrete Pre-Pour Checksheet (__ Form D3-85) for PTW-E Block 3. 7) Cast In-Situ Invert: ITP item C5, ITP item C6, ITP item 4.6 Missing Secondary Lining Concrete Pour Checksheet (__ Form D3-84) for PTW-E Block 3. 8) Cast In-Situ Invert: ITP item 5.3 Missing Secondary Lining Post Pour Checksheet (__ Form D3-88) for PTW-E Blocks 3, 4, 5, 6, 7, 8 & 9. 9) Cast In-Situ Sidewalls: ITP item 3.1, ITP item 3.2, ITP item 3.3, ITP item 3.4 Missing Secondary Lining Concrete Pre-Pour Checksheet (__ Form D3-85) for PTW-E Block 4 Right Hand Side. 10) Cast In-Situ Sidewalls: ITP item C5, ITP item C6, ITP item 3.5 Missing Secondary Lining Concrete Pour Checksheet (__ Form D3-84) for PTW-E Block 4 Right Hand Side and Block 8 Cxxx-__M-C4-LLG-D061-50158 Deliverables for PTW-E Bulking Layer through Fireproofing Layer, Ch.69-107 (W008) 11) Bulking Layer, Secondary 1st Layer and Fireproofing Layer: ITP item C.2 No rebound test was performed during the time period in which PTW-E was constructed 12) Fireproofing Layer: ITP item C4 Missing Hammer Testing Checksheet (__ Form D3-80) for PTW-E fireproofing layer Ch. 69 to 72. Cxxx-__M-C4-LLG-D061-50151 Deliverables for PTW-E Secondary 2nd 1st Layer, Ch.7.5-70 (W008) 13) 2nd 1st Layer ITP item C.1 Ch. 7.5m to 13m – No record for 1 hour and 3 hour test results Ch. 21 m – No record for 1 hour to 12 hours test results Ch. 26 m – No record for 1 hour to 12 hours test results Ch. 34m to 39m – No record for 1 hour, 6 hour and 12 hour test results Ch. 40m to 50m – Missing Early Strength test results Ch. 51 m to 56 m – No record for 12 hour test results Ch. 60m to 65m – No record for 1 hour test results Ch. 65m to 70m – No record for 12 hour test results (See Att04.) 14) 2nd 1st Layer ITP Item 4.6 No curing carried out between Ch.45 to 47 and Ch. 60 to 65. Cxxx-__M-C4-LLG-D061-50150 Deliverables for PTW-E Secondary 2nd 2nd Layer, Ch.11.5-68.5 (W008) 15) 2nd 2nd Layer ITP Item 4.6 No curing carried out for ch.11.5 to 25.5 and 32.5 to 68.
| 02SL - Stations (LUL) | Cxxx-NCR-001095 | NCR | W - PTW-W SL: Missing tests |  | Contr | __M |  |  | 2017-07-06 | 2017-07-21 08:34 | 15 | 2017-03-28 13:15 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | • Cxxx-__M-C4-LLG-D061-50200 Deliverable Records for PTW-W Sheet Waterproofing Membrane and Cast In-situ: 1) Cast in-situ Invert: ITP item 4.1 & Sidewall Cast in-situ: ITP item 4.1 Missing Secondary Lining Post-Pour checksheet (__ Form D3-88) for PTW-E/PTW-W block 10 (ch. 7.5 to 7.5) invert. Missing Secondary Lining Post-Pour checksheet (__ Form D3-88) for PTW-E/PTW-W block 10 (ch. 7.5 to 7.5) sidewall. 2) Sidewall Cast in-situ: ITP Item 3.3 Missing Reinforcement checksheet (__ Form D3-26) for Junction PTW-W/EP1 sidewall ch.160.804-173.693 • Cxxx-__M-C4-LLG-D061-50201 Deliverable Records for PTW-W __ Sprayed Waterproofing Membrane: 3) __: ITP item A3, ITP item A4, ITP item 1.3, ITP item 1.4, ITP item 2.1, ITP item 2.2 Missing Pre-placement checksheet (__ form D3-98) for PTW-W 2nd layer – ch.137-147 & 186-195 and 3rd layer – ch.99-107.5 & 186-195 4) __: ITP Item 2.5, ITP item 2.10 Missing Final Layer Visual Check (__ form D3-102) for PTE-W ch.7.7 to PTW-W ch.2.5 5) __: ITP 4.1 Missing Permit to Cover (__ form D3-131) for PTE-W ch.7.7 to PTW-W ch.2.5 and PTW-W ch.106-120.
| 02SL - Stations (LUL) | Cxxx-NCR-001096 | NCR | W - EP2 SL Missing Test and documentation |  | Contr | __M |  |  | 2017-06-04 | 2017-05-24 09:39 | -11 | 2017-02-24 10:48 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | • Cxxx-__M-C4-LLG-D061-50128 Deliverable Records for EP2 Regulation Layer: 1) ITP item C5 - Hammer testing after each layer (inclusion of cracks on checksheet) Ch.5 to 15.5 – Hammer Testing Checksheet (__ Form D3-80) no sheet on file for invert. 2) ITP item 7.2 – Scanner: Thickness and Profile Check of regulation layer Ch.5 to 18.5 - Shotcrete thickness check (__ Form D3-61) not on file for regulation layer.
| 02SL - Stations (LUL) | Cxxx-NCR-001097 | NCR | W - CP3 SL Missing Test and documentation |  | Contr | __M |  |  | 2017-04-28 | 2017-05-24 09:45 | 26 | 2016-02-15 16:32 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | • Cxxx-__M-C4-LLG-D061-50127 Deliverable Records for CP3 regulation layer, sheet membrane and cast in-situ: 1) Regulation Layer: ITP item C5 CP3 Regulation layer: No Hammer Testing Checksheet (__ Form D3-80) for invert ch.6-41. 2) Protection Concrete: - ITP Item C3; ITP Item C4; ITP Item 2.4 CP3 Protection Concrete: No Secondary Lining Pour Checksheet (__ Form D3-84) for Block 5 (ch.12.429-15.118). - ITP Item 2.1; ITP Item 2.2; ITP Item 2.3 CP3 Protection Concrete: No Secondary Lining Pre-Pour Checksheet (__ Form D3-85) for Block 5 (ch.12.429-15.118)
| 02SL - Stations (LUL) | Cxxx-NCR-001098 | NCR | W - VA4 SL Missing Test and documentation |  | Contr | __M |  |  | 2017-06-07 | 2017-05-25 14:30 | -13 | 2017-02-27 08:17 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | • Cxxx-__M-C4-LLG-D061-50125 Deliverable Records for VA4 Secondary Lining Regulation through Cast In-Situ: 1) ITP Item C3, ITP Item 2.1, ITP Item 2.2, ITP Item 2.3, ITP Item 2.4 VA4 Block 2 Protection Layer: No Secondary Lining Concrete Pour Checksheet (__ Form D3-84) on file: no evidence of workability, waterproofing membrane inspection / remediation, cleanliness, setting out, curing. 2) ITP Item C4 – Temperature (Ambient Temperature of Workface) VA4 Block 2 Protection Layer: No Secondary Lining Concrete Pour Checksheet (__ Form D3-84): no temperature available VA4 Block 1&2 Cast In-Situ Invert Layer: Ambient temperature missing from Checksheet VA4 Block 1&2 Sidewall In-Situ Invert Layer: Ambient temperature missing from Checksheet • Cxxx-__M-C4-LLG-D061-50146 Deliverable Records for VA4 Secondary Lining Spray waterproofing through fireproofing: 1) ITP item C1 – SCL Early strength requirement & ITP Item 6.12 – SCL Spraying Strength Gain VA4 Second Secondary with Fireproofing: no SCL Early Strength Test (__ Form D3-48) available. 2) ITP item C2 – Estimated Fibre and Aggregate Rebound VA4 Bulking Layer, First Secondary and Secondary with Fireproofing: no SCL Rebound Measure Sheet (__ Form D3-46) available
| 02SL - Stations (LUL) | Cxxx-NCR-001099 | NCR | Fireproof profile pins installed greater than a 100mm X and Y offset as identified during a CRL surveillance. |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2016-08-26 | 2016-04-29 09:52 | -119 | 2015-08-19 10:32 | Civil - Tunnelling | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During a surveillance undertaken on 23rd, 24th and 28th July 2015 which looked at fireproofing preparation, application and documentation survey scans were made available for the dowels installed within the secondary lining and for the pins installed into the secondary lining for fire proofing. A sample inspection was undertaken on CP9 chainage 29 – 26 to ensure the fire proofing pins are installed within X – 100mm and Y – 100mm of the embedded secondary lining dowels as required. Following review, and following meetings with Crossrail and __ survey personnel, it was identified that the fireproof pins were radially offset by approximately 200 - 240mm (i.e. secondary lining dowel location average chainage 27.72m vs fireproof pin location average chainage 27.96m). Additionally, when discussing with the __ survey team, they were not aware of the X and Y 100mm defined requirement. ITP Cxxx-__M-C4-ITP-CR092-50008 Inspection Number 6.5 states Activity - ‘Profile Bar Installation’ with the Parameter being ‘Up to max. 100mm offset in X and Y direction of pre-existing profile bars in secondary lining and must avoid fixings of future contracts’. Method Statement Cxxx-__M-C4-GMS-CR092-50010 states “The profile bars location will be marked up on the secondary lining before installation, ensuring that they are on top (with a slight offset) of the existing profile bars within the secondary lining” with an image showing the 100mm X and Y offset. NCR was raised as the necessary evidence to demonstrate compliance with the ITP and Method Statement defined X and Y offset requirements was not provided.
| 02SL - Stations (LUL) | Cxxx-NCR-001100 | NCR | Permit to Spray checksheet is being signed as completed without undertaking appropriate checks as defined in the ITP inspection number 6.5. |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2015-12-23 | 2015-12-22 12:46 | -1 | 2015-08-19 10:38 | Civil - Tunnelling | 1000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During a surveillance undertaken on 23rd, 24th and 28th July 2015 which looked at fireproofing preparation, application and documentation, it was identified that the verifying document, Permit to Spray Checksheet __-D3-137, for ITP Cxxx-__M-C4-ITP-CR092-50008 Inspection Number 6.5, which is a deliverable record and a hold point had been signed as acceptable by the site engineers / surveyors prior to spraying fireproof concrete, however following a sample inspection of CP9 chainage 29 – 26 it was identified (NCR 1099) that the offset was greater than the defined parameter requirement. This NCR was raised as the checks are either not being undertaken or the check activity is not robust enough to ensure compliance; if the checks were being undertaken the offset deficiencies would have been highlighted sooner. Works Information Vol 2B states “Record and other deliverables generated as part of the inspection and test process shall be identified within the ITPs. The ITPs shall also make clear who is responsible for implementing the planned arrangements, as well as who is responsible for certifying that compliance with requirements has been achieved in practice” and “The Contractor shall conduct inspections and tests in accordance with his detailed quality plans and ITPs”.
| 02SL - Stations (LUL) | Cxxx-NCR-001101 | NCR | W - ES1: Cover meter survey not done prior installation of the winch. |  | Contr | __M |  |  | 2016-12-09 | 2016-11-30 09:26 | -9 | 2015-08-19 16:40 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | On the 17/08/15 DS when fixings the winch some of the drilled holes encountered steel. After investigation it seems that no cover meter was made in the first place. The process set out in the method statement was not followed.
| 02SL - Stations (LUL) | Cxxx-NCR-001102 | NCR | L - CP8: Hollow Spots in the fireproofing layer |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-12-06 | 2015-09-24 12:58 | -73 | 2015-08-28 16:31 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On 24/08/2015 - During hammer tapping in CP8 (CH115) (Att.01), the construction team found hollow spot in the crown (Att.02). It was found at 8 o'clock where we spray the sides down to the invert slab on either side ( To ensure that the rebound is not over sprayed). The hollow area is 800 x 950 (Att.03)
| 02SL - Stations (LUL) | Cxxx-NCR-001103 | NCR | L - AP5 - Primary Lining Underthickness |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-09-30 | 2016-12-14 12:54 | 75 | 2015-09-15 11:11 | Tunnelling - Linings - Sprayed Concrete | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | L - 10/08/2015 - During secondary lining cleaning works, in AP5, within 100mm of the diaphragm wall it was noted that small were between 100mm - localised areas didnt meet the required thickness. D-wall has been found at chainage 149.5 as shown in Att.07, underthickness is around 149.4 on either sides of the invert slab at 4-5o'clock and 7-8 o'clock. The size of these areas are 100mm length and 2m height. The required thickness is 250mm and the thickness of these two areas 150mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001104 | NCR | L - CP8: Underthickness in the Fireproofing layer |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-05-15 | 2017-04-23 15:31 | -22 | 2015-09-02 15:13 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | L- 19/08/2015 - When the scan was received , it was noted that some areas showed underthickness as can be seen in Att.01. These areas are in CH 15 and CH18 of CP8. Although it is marked CP9, __ confirms that the scans concerns the CP8. Refer to Att04. for the email from __ SL Engineer. The scans have also been amended in Att.01a
| 02SL - Stations (LUL) | Cxxx-NCR-001105 | NCR | W - PTW-E/CP3: Under thickness around CP3 eye |  | Contr | __M |  |  | 2016-02-29 | 2016-02-04 16:08 | -25 | 2015-10-27 12:04 | Tunnelling - Linings - Sprayed Concrete | 4000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | • Areas of secondary lining around the eye of CP3 were less than the required 250mm thickness as outlined in the Att.01 scans. North Side of the PTW-E tunnel chainage 45.5 to 55 between 7'o and 12 clock all around the CP3 eye. Maximum thickness missing is 100mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001106 | NCR | L-PTW-E - Sheet Membrane Penetration |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-02-24 | 2016-03-11 14:28 | -350 | 2015-09-02 15:18 | Tunnelling - Tunnelling General | 2000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | On 20/08/15 condition survey prior PTW ( RCW to CP1) handover to Cxxx has been done. During the site visit it has been agreed with all parties ( CRL, Cxxx and Cxxx ) that an assessment of the sheet membrane will be done after cleaning. Refer to the Att.03 for the condition survey report - page 2 note 6 ( Notes as of 20/08/15 ) On 28/08/2015 during a site visit in PTW-E at CH.123 it was observed that the waterproofing sheet membrane has been damaged when Cxxx fixed bolts into the lining and penetrated through the sheet membrane to support their transformer frame. This damage has been done during PTW temporary handover to Cxxx for TBM transit. Refer to the Att01 for a photo of the waterproofing sheet membrane damaged by Cxxx with bolts
| 02SL - Stations (LUL) | Cxxx-NCR-001107 | NCR | L-AP10b - MS345 No Bonding |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-10-07 | 2016-08-09 14:36 | -59 | 2015-09-10 14:05 | Tunnelling - Tunnelling General | 2000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | On the 28/08/2015- The 1st layer of MS345 was found debonded at CH 8 (left hand side at 9 O'clock). The area is about 0.5m2 Refer to the Att.01 and Att.02 for photos of the defect.
| 02SL - Stations (LUL) | Cxxx-NCR-001108 | NCR | L - AP5 and CH5: Leaks and damage to sprayed waterproof lining |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-08-15 | 2017-08-02 15:03 | -13 | 2015-09-02 15:33 | Tunnelling - Linings - Sprayed Concrete | 4000 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • AP5 sprayed waterproofing lining has been damaged in the crown (From 10 oclock to 2 o'Clock - approximately 5m2 damaged) following removal of over sprayed shotcrete on the area of AP5 next to the opening for Moorgate box. (CH 149.438) Following the spray of secondary lining shotcrete, the over sprayed shotcrete on the sprayed waterproof membrane was not removed immediately with a jet wash or protected. Hence the sprayed waterproof membrane became damaged close to the sprayed shotcrete lining, from the remedial works to remove the hardened over sprayed shotcrete, meaning that a specified 300mm overlap was not achievable. • During site visit to check if area was dry in AP5, some areas in CH5 below platform have been found wet. Refer to Att.09 for photos
| 02SL - Stations (LUL) | Cxxx-NCR-001109 | NCR | L - RCWa: Unintentional break out of permanent works of the foot of the wing walls |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-12-11 | 2015-11-13 11:05 | -28 | 2015-09-02 16:07 | Tunnelling - Tunnelling General | 4000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | L-31/08/2015- In RCWa blocks 2 & 3 (CH 150 - CH 123), there are TBM pliths attached solely to the wing wall which needed to be removed. There are severel different versions of pliths which can be attached to the invert , the sidewall or a combination of both,hence this can be easily confused. Attachment 03 shows the sketch of blocks 2+3 and shows the mistaken style of plinth and the damaged area. It is clear from the sketch that when they came to break out the plinth, they started at the bottom of the side wall assuming it was the a chamfered edge of the plinth and hence broke out up to 500mm (Worst Case) of the sidewall (see attachment 1)
| 02SL - Stations (LUL) | Cxxx-NCR-001110 | NCR | W - ES1 Uphill Pilot Under thickness |  | Contr | __M |  |  | 2015-11-25 | 2015-10-28 15:13 | -28 | 2015-10-16 09:20 | Tunnelling - Linings - In-situ Concrete | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | • ES1 Pilot Uphill Adv 17 has been found to be approx. 150mm. at 9'o clock. Refer to the Att.01 for the photo • After investigation the thickness beamer profile has been found with no value in this area. Refer to the Att.02
| 02SL - Stations (LUL) | Cxxx-NCR-001111 | NCR | L- PRM Lift: __ Bar out of position |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-12-03 | 2015-11-17 16:01 | -16 | 2015-09-09 16:29 | Tunnelling - Tunnelling General | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On the 01/9/2015 the halfen bar in pour 1 was found to be out of position once shutter were struck. Refer to the Att.05 for the sketch of the halfen bar out of position. On the 14/10/15 inspection of the halfen bar has been done in the PRM lift to measure the dimensions and offsets Sketch with the physical dimensions measured can be seen in Att.06
| 02SL - Stations (LUL) | Cxxx-NCR-001112 | NCR | L - PRM Lift Pour 2/3: Waterbar Fins casted during the pour |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-12-18 | 2015-10-06 11:35 | -73 | 2015-09-09 17:09 | Tunnelling - Tunnelling General | 2500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | L- 05/09/2015 - Waterbar is required across the horizontal joint between pours 2 and 3a in the PRM Lift Lobby structure. Three sealing ribs were cast into the top of Pour 2, rather than the two required. This means that there is only one sealing rib remaining to be cast into Pour 3a. This means that any penetrating water will have a less tortuous path into the construction joint, reducing the effectiveness of the waterbar.(Att.01).
| 02SL - Stations (LUL) | Cxxx-NCR-001113 | NCR | L- J2 Curves tests done but without any checksheets printed or reviewed |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-03-25 | 2015-11-04 14:24 | -142 | 2015-10-21 17:03 | Tunnelling - Tunnelling General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | L- 14/09/2015 - During the monthly quality surveillance of secondary lining, it was noted that Early strength test were being conducted however there was no evidence of checksheets done or filled. The missing print out J2 curve found was in AP5. As per document Cxxx–__M–O4–RGN–CR092– 50121 Surveillance No. 83: PRM Lift Works and Secondary Lining at Liverpool Street Item 8, engineers were witnessed doing the Early Strength test and recording the results. But no evidence of checksheet printed and review by QC nor CRL/Cxxx inspectors have been found.
| 02SL - Stations (LUL) | Cxxx-NCR-001114 | NCR | L- VD5 Encroachment from Fire regulating layer CH7 - CH22 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-12-24 | 2015-12-11 15:37 | -13 | 2015-09-15 13:12 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | L-Shift 2 -VD5 – 12/09/2015- Non-Conforming Profile -There are some occurrences where the finished tunnel lining has encroached on the CRTL final profile. Various areas have been oversprayed ( max by 20mm ) meanly in the crown ( from 9 to 2 o'clock ) and between the CH7 and CH22. The largest area oversprayed is in the crown ch 11 to 13 and is approximately 4m2 Further details are in the Att.01 and Att.04
| 02SL - Stations (LUL) | Cxxx-NCR-001115 | NCR | L-VD5- Hollow Areas @ CH 9 in Fireproofing Layer |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-12-25 | 2015-10-13 11:45 | -73 | 2015-09-16 14:08 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | L-14/09/2015 - NS (Shift 3) - During hammer tapping it was revealed there was a hollow area in the invert at 6 O'Clock - 7 O'Clock (CH9-See Att.01). Size: 2000mm x 2000mm ( See Att.02)
| 02SL - Stations (LUL) | Cxxx-NCR-001116 | NCR | L-CP2 - Hollow spots in fire proofing layer |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-11-15 | 2016-12-06 14:06 | 21 | 2015-09-16 14:13 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | L-14/09/2015 - Shift 3 - During Hammer tapping , hollow spot were found at 8'O'Clock at CH 6. (See.Att.01 - for picture and Hammer tapping checksheet) Area (800mm x 600mm = 0.48m2)
| 02SL - Stations (LUL) | Cxxx-NCR-001117 | NCR | L-CH2 Thickening Layer - Missing Step |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-02-26 | 2016-02-01 16:48 | -25 | 2015-10-14 10:43 | Tunnelling - Linings - Sprayed Concrete | 4000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | L- 14/09/2015 - Whilst on site it had been noticed that the construction team has not created of 1m2 step between the primry lining and the primary lining thickening in CH2 around chainage 63 on both knees ( sketch can be seen in Att.07 ). According to drawing 00526 (Sections G1-G1 and G2-G2)(See Att.01) it shows that there should be a step between primary and thickening, with the primary lining 500mm above axis and the thickening 500mm below the axis. Currently there is no step between the primary and thickening and the lining has been cut back to where the thickening level should be (1m below where it should be, 500mm below axis).
| 02SL - Stations (LUL) | Cxxx-NCR-001118 | NCR | L-AP10b - MS345 contaminated with oil spillage |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-09-30 | 2016-08-09 14:41 | -52 | 2015-09-24 11:54 | Tunnelling - Tunnelling General | 2000 |  | Equipment Breakdown | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | L- 11/09/2015 - Shift 2 - There is a big patch of MS345 in AP10b towards the end on the RHS above axis (2 O'clock) which might be contaminated with oil spillage. (As shown in Att.01) Events in Order: -Waterproofing works were carried out during the last month in AP10b. The crown was regulated, and Masterseal 345 was sprayed from knee level, and passed off. (CH22-5) -Once the Crown was signed off, the far invert was mucked out, regulated, waterproofed, and signed off.(CH13-22) - Between the 05/09 and 06/09, whilst carrying out the invert mucking out (CH13-8), using the 8T machine (Yanmar), a hydraulic hose failed and oil was spread on both shoulder level(Att.01), around Ch 8, on an approximate 2* 1m2. -After spending few shifts trying to jetwash it off from the Masterseal 345, the oil was still there.
| 02SL - Stations (LUL) | Cxxx-NCR-001119 | NCR | L - Northern Line Link- Punctured Waterbar |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-12-30 | 2015-10-13 13:52 | -78 | 2015-09-21 16:00 | Tunnelling - Linings - In-situ Concrete | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | L -18/9/2015 - Shift 3 - Waterbar is required across the construction joint (In Northern line line) between pours 4 & 6a in the 4/204 Opening Set structure. Operatives were breaking the plywood off to exposed back face of the concrete. The breaker point slipped and punctured the waterbar (Att.02)
| 02SL - Stations (LUL) | Cxxx-NCR-001120 | NCR | W - ES1: Missing early strengh tests |  | Contr | __M |  |  | 2016-01-29 | 2016-01-26 13:44 | -3 | 2015-10-16 09:26 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Training Deficiency - Insufficient practice or hands -on experience | Completed |  | • At Advance 4, early strength test measurements at 15min below J2 curve. 1 and 3 hour tests missed. Measurements taken at 4 hours. • At Advance 5, early strength test measurements at 1hr < 0.5N/mm2 and 3 hour test also missed. Measurements taken at 4 hours. • At Advance 6, additional panel sprayed due to low 1 hour reading at Advance 5, again 1 hour at 0.44N/mm2 • At Advance 8, panel not sprayed at end of spray but should have been as Advance 6 1 hour results less than 0.5N/mm2. Refer to the Att.01
| 02SL - Stations (LUL) | Cxxx-NCR-001121 | NCR | L-VD1 Encroachment from Fire regulating layer CH10 - CH34.1 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-01-01 | 2015-11-02 12:28 | -60 | 2015-09-23 10:57 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | L-VD1-19/09/2015- Shift 3 : From Att.01 and Att.02 (CTRL Profiles) - it can be seen that there is encroachment in the (crown) fire proofing layer between CH10 - CH34.1 (9 O'clock - 2 O'Clock) The depth of these encroachment vary from 0mm-20mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001122 | NCR | L- PRM - Insufficient cover to Near Face Reinforcement in PRM Lift Pour 2 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-01-03 | 2015-11-12 11:27 | -52 | 2015-09-25 14:50 | Tunnelling - Linings - In-situ Concrete | 3000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Concrete bars have insufficient cover to the concrete surface (Att.03). __ Designer has reviewed the situation and has advised that the minimum allowable cover is 25mm to the couplers. Attached sketch shows cover to rebars in the wall in the affected area.(Att.01) The defect is on the Southern half of the Eastern wall of the PRM lift at an approximate level of 90.5-92m ATD.
| 02SL - Stations (LUL) | Cxxx-NCR-001123 | NCR | L - September 15 Sprayed test beam: Low Residual Flexural strength |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-06-10 | 2016-05-31 14:21 | -10 | 2015-11-06 14:51 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On the 04/09/15 DS spray in moulds beam set CR2378 from September 2015 has achieved too low individual D3 result of beam F - S1.2 at 28 days with average for set of six beams - S1.6 Refer to the Att.01 for the summary of beam test results
| 02SL - Stations (LUL) | Cxxx-NCR-001124 | NCR | L - ES2 Cracks in Crown |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-10-28 | 2016-12-06 14:15 | 39 | 2015-10-12 10:48 | Tunnelling - Linings - Sprayed Concrete | 6000 |  | Design | Repair | 3 (3-6k) | Complete | Previous Construction - Not Defined | Completed |  | • On 16/09/15 cracks have been discovered in CH2 crown ( ch 63 and 68 - 10 to 2 o'clock ) adjacent to the anchor 15 and 19 raising concerns with regard to the safe installation and operation of the excavator. • Width is maximum 2-3 mm and depth estimated to be up to 500mm • Photos of the cracks and location can be seen in Att.01 and Att.02.
| 02SL - Stations (LUL) | Cxxx-NCR-001125 | NCR | L-CH5 - Underthickness In the Crown - Fire proofing |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-09-30 | 2016-09-07 12:13 | -23 | 2015-09-28 14:20 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | L- 24/09/2015 -DS (Shift 3) - When the scan of Ch5 Fire Proofing, was received, it was noted that some areas showed underthickness in the crown @ CH113 between 12 O'clock and 2 O'clock. The area of underthickness are all under 0.5 m2 and less than 50mm. See Att.01 for full details (~7 areas concerned).
| 02SL - Stations (LUL) | Cxxx-NCR-001126 | NCR | L - VD1SL: Loss of connection detail in the invert |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-01-29 | 2015-11-18 16:11 | -72 | 2015-09-28 14:27 | Tunnelling - Tunnelling General | 3000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | 24/09/2015 - NS (Shift 2): When removing the temporary muck out of the invet to the entrance of VD1, the masterseal was damaged all the way up to the joint this is between 4 O'clock - 8 O'clock, hence not leaving a 300mm overlap to connect the waterproofing.
| 02SL - Stations (LUL) | Cxxx-NCR-001127 | NCR | L- CH5, VD5 and AP10 PL: Missing tests and documentation |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-07-26 | 2017-08-14 10:40 | 19 | 2016-07-14 08:38 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | • Cxxx-__M-C4-LLG-C101-50109 Deliverable Records for CH5 Primary Lining Thickening - Package No L054 1) ITP Item C1 & C2: SCL Early strength requirement - CH5 Crown 1st layer FF1; 2nd layer FF2; 3rd layer NF2; 2nd layerP1: Early strength tests missed (See Att11; 13) - CH5 Invert 1st layer FF1; 2nd layer FF2; 3rd layer NF2&3: Early strength tests missed (See Att12) - CH5 Invert 1st layer P1: Early strength tests result missing at 1 and 3 hours (See Att14) - CH5 Invert 2nd layer P1: Early strength tests result missing at 1 and 12 hour (See Att15) 2) ITP Item D2: SCL Compressive strength by core sampling even distributed around lining including joints CH5 Thickening: No Compressive Strength Test carried out 3) ITP Item 5.3: Installation of guide rebars and Survey of Lining position relative to reinforcement position - CH5 Crown & Invert 1st layer P1: Missing beamer records for the guide rebars - CH5 Invert 1st layer FF: Missing beamer records for the reinforcement 4) ITP Item 5.4: Reinforcement Installation (Thickening, Headwalls, Inverts) CH5 Crown 2nd layer FF2; 3rd layer NF3&NF2: Typo: Revision ‘P’ written instead of ‘C’ 5) ITP Item 5.11: Curing & Protection of final layer (intrados) CH5 Crown 3rd layer NF2and Invert 3rd layer NF3&NF2: no curing applied • Cxxx-__M-C4-LLG-C101-50037 Deliverable Records for CH5 Primary Lining SCL Methodology ITP - Package No L054 6) ITP Item C5 & D4: Workability/Flow on point of spray application - CH5 Advance 1: No primary flow recorded (See Att01.) - CH5 Advance 25: Spraying commenced before sampling regime (See Att06) - CH5 Advance 31: Spraying commenced before sampling regime (See Att09) 7) ITP Item C1 & C2: SCL Early strength requirement - CH5 Advance 8; 12; 14; 27: Early strength tests missed (See Att02; 03; 04; 07) - CH5 Advance 19; 30: Early strength tests result missing at 1 hour (See Att05; 08) - CH5 Advance 33: Early strength tests result missing at 6 and 12 hour (See Att10) • Cxxx-__M-C4-LLG-C101-50044 Deliverable Records for VD5 Primary Lining SCL Methodology ITP - Package No L043 8) ITP Item C1 & C2: SCL Early strength requirement - VD5 Advance 5: Early strength tests missed (See Att16) - VD5 Advance 14: 6 and 12 hour strength test missed (See Att17) 9) ITP Item C5 & D4: Workability/Flow on point of spray application -VD5 Advance 15; 18; 20; 21 and 27: Spray commenced before sampling (See Att18; 19; 20; 21; 22) • Cxxx-__M-C4-LLG-C101-50110 Deliverable Records for AP10 Primary Lining SCL Methodology ITP - Package No L031 10) ITP Item C1 & C2: SCL Early strength requirement AP10a sump2 – Early strength tests result at 1 hour missing
| 02SL - Stations (LUL) | Cxxx-NCR-001128 | NCR | L-PRM Lift - Crack from surface to Near Face reinforcement |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-01-13 | 2015-11-12 11:50 | -62 | 2015-10-05 10:24 | Tunnelling - Linings - In-situ Concrete | 4000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | A crack has formed following placing of the repair detailed in NCR #1122. The repair concrete was acceptably homogenous i.e. not cracked when the shutter was removed. A crack has appeared approx. 2 days after shutter removal. This is limited to an area approx. 200mm high x 300mm wide x 100mm deep into the wall.
| 02SL - Stations (LUL) | Cxxx-NCR-001129 | NCR | L- PRM mix – Strength cube failure ( C4046 ) |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-02-11 | 2016-01-14 10:44 | -28 | 2015-11-03 09:50 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | Sample C4046 ( MIX PRM C50/60 ) taken the 04/09/15 from a batch of concrete for Pour 2 Wall of the PRM Lift failed to comply with 28 days strength equal or exceeding +1N/mm2 ( Criteria 1 ). However individual test results were found to be less than the -4N/mm2 design strength ( Criteria 2 ). C4046 sample was taken the 04/09/15 for the PRM stage 2. Sample result is showed in attached summary Att.01
| 02SL - Stations (LUL) | Cxxx-NCR-001130 | NCR | W - ES1 Enl Adv 15: Non-conforming thickness, delamination and rebound entrapment |  | Contr | __M |  |  | 2016-05-27 | 2016-03-23 16:45 | -65 | 2015-10-06 10:31 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On the 29/09/15 NS excvation of the adv 15 invert has started. On the 30/09/15 DS after temporary invert was sprayed it has been noticed the following: • Non-conforming thickness of temporary invert of adv 15 in the left knee area, required thickness of 100mm, achieved thickness ~20mm • De-Lamination of the SCL layer • Rebound entrapment
| 02SL - Stations (LUL) | Cxxx-NCR-001131 | NCR | L - PTWE/RCWb: Transition profile out of tolerance |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-01-14 | 2015-10-13 12:06 | -93 | 2015-10-06 18:20 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | • On 03/10/15 DS the programme was to start spraying the Secondary lining 1st layer from CH 114 to CH 120 in PTW-E/RCWb transition. • As __ was set up and ready to start spraying, the engineer, shooting randomly on the regulating lining, noticed “tight” values on the south side (-200mm on the 2nd 1st file at CH 116.5) and “big” values (+1000 to +1200 on the 2nd 1st file at CH 118) on the North side • Shift Engineer decided to cancel the spray and report it to his section engineer. • After the scans have been issued (Att.01) it has been found that the lining was tight on the south side from CH 116 and CH 118 - 2'o clock to 4 o'clock and "big" on the opposite side ( north side ). • Refer to the Att.02 for the tight spots beamer survey and Att.03 for the proof-drillings of the south side ( tight area )
| 02SL - Stations (LUL) | Cxxx-NCR-001132 | NCR | L - CP8: Hollow Spots in the fireproofing layer (below axis) |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-12-30 | 2017-01-18 12:25 | 19 | 2015-10-07 10:19 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On 06/09/2015 DS - During hammer tapping in CP8 (below axis) at CH 9.5 (Att.01 (Wrong box ticked on Att.01, the hollow spot is in invert), the construction team found a hollow spot in the left knee at CH 9.5. Area affected is below 1sqm. The hollow is less than 1.0 m x 1.0 m. It is in clad area.
| 02SL - Stations (LUL) | Cxxx-NCR-001133 | NCR | L - Moorgate Shaft / AP5 connection: Leaks and potential damage to the exposed Masterseal |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-01-22 | 2016-01-21 13:31 | -1 | 2015-10-14 10:31 | Tunnelling - Tunnelling General | 2000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | L-07/10/2015 - DS (Shift 2 detected the blisters visually during a routine inspection) - Leaks were found in the masterseal by the joint of the secondary lining. (See in Att.01 + Att.02). Leaks were then found at the left hand side from the water blisters (around 9'o clock - South Side ) at chainage 150 of AP5. __ in AP5 chainage 150 has been sprayed End of June / Beginning of July
| 02SL - Stations (LUL) | Cxxx-NCR-001134 | NCR | L- AP5 FR Layer - Encroachment |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-01-22 | 2016-01-19 11:29 | -3 | 2015-10-14 10:08 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | L-AP5-21/09/2015- Shift 3 : From Att.01 (CTRL Profiles) - it can be seen that there is encroachment in the (crown) fire proofing layer between CH113 - CH141.10 (3 O'clock - 4 O'Clock) and by the axis level. The depth of these encroachment vary from 10mm-40mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001135 | NCR | L - RCE: Transition profile out of tolerance |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-01-22 | 2016-01-26 16:17 | 4 | 2015-10-14 16:02 | Tunnelling - Tunnelling General | 7000 |  | Design | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After raising NCR 1131 (PTWE/RCWb Transition profile out of tolerance ) transition in PTE/RCE has been checked for same issue. On 09/10/15 DS scans have been issued (Att.01) it has been found that the lining was tight on the north side from CH 113.5 at 7 to 10 'o clock and "big" on the opposite side ( south side ).
| 02SL - Stations (LUL) | Cxxx-NCR-001136 | NCR | W - Mix P1 45kg Fibre content fresh failure |  | Contr | __M |  |  | 2016-03-11 | 2016-02-02 15:37 | -38 | 2015-10-16 10:05 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • Sample number CR2407 (Att.01) taken during spray of in ES1 Adv 18 at WHI fail to comply with min 36kg/m3 of fibre content for P1 Mix - Mix design 45kg/m3. Refer to the Att.02 for the fibre results summary • Sample number CR2466 (Att.04) taken the 13/11/15 at Whitechapel site fail to comply with min 36kg/m3 of fibre content for P1 mix – mix design 45kg/m3. Refer Att.04 for the fibre results summary
| 02SL - Stations (LUL) | Cxxx-NCR-001137 | NCR | L - Non conformity of aggregate – sample E1511 |  | Contr | __M |  |  | 2016-04-15 | 2016-04-13 13:36 | -2 | 2015-10-16 14:46 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Lack or improper material identification and traceability | Completed |  | Sample taken from one load at LIV site on 17/09/15 has shown a grading failure on sample No E1616. The material was too coarse. Distribution for E1511: 8mm: 88 instead of 100 6.3mm: 88 instead of 100 4mm: 83 instead of 94-100 2mm: 59 instead of 60-100 Refer to Att.01
| 02SL - Stations (LUL) | Cxxx-NCR-001138 | NCR | W - EPW1/ES1 junction: Nonconforming Cores CR2431/32 ( Delamination of thickening layer ) |  | Contr | __M |  |  | 2016-02-19 | 2015-12-10 15:25 | -71 | 2015-10-29 10:02 | Tunnelling - Linings - Sprayed Concrete | 6000 |  | Workmanship | Use As-Is | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | • On the 11/10/15 An area of delamination between Primary Lining and Thickening in EPW1 was discovered upon excavation and formation of the junction with the ES1 downhill enlargement. This area was broken back and found to be limited to the thickening above axis and prevalent toward the junction of the EPW1 and the old headwall that existed before ES1 enlargement was completed. • On the 15/10/15, 7 cores have been taken in EPW1 Adv 42 (Att.01 and Att.02 for the cores reports) • Visual inspection of the delamination and subsequent cores CR2431&32 taken in the North Side ( Att.01) confirmed that there was a layer of dust between the primary and thickening and that there was no delamination in the invert (proved by coring). The cores and hammer tapping (Att.04) also indicated that the delamination tapered off to a good joint away from the now removed headwall. • On the 24/10/15 NS additional cores ( CR2443 - Att.03 ) have been taken to know the extent of the delamination. Refer to Att.01, Att.02 and Att.03 for the cores reports and Att.04 for the hammer tapping. For a better understanding a photo of the location of the delamination can be seen in Att.05.
| 02SL - Stations (LUL) | Cxxx-NCR-001139 | NCR | W - RCW Blocks 1 & 1A: Damage to waterproof membrane junction |  | Contr | __M |  |  | 2016-02-26 | 2016-01-26 14:52 | -31 | 2015-10-22 16:20 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | • On the 16/10/2015 NS Sheet membrane and water bar connection was damaged all around the joint during the excavation of temporary works to expose and commence work on the invert transition between Blocks 1 and 1A. • Refer to the Att.01 • Wing walls/invert are installed in the invert from 4 to 8'o clock. • Sheet membrane and water bar connection were damaged all around the cast in situ therefore between 4 to 8'oclock.
| 02SL - Stations (LUL) | Cxxx-NCR-001140 | NCR | W - CP2 SL: Missing tests / documentation |  | Contr | __M |  |  | 2017-06-21 | 2017-06-21 08:34 | 0 | 2017-06-07 14:35 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | • Cxxx-__M-C4-LLG-D061-50132 Deliverable Records for CP2N/PTE-W & PTE-E Secondary Lining: Regulation Layer, Sheet Membrane, Cast In Situ, Sprayed Waterproofing, Bulking Layer, Secondary 1st Layer & Fireproofing Layer (Combined Method) (W022) - Regulation Layer – ITP item C5 Missing Hammer testing check sheet (__ form D3-80) for CP2N Invert Ch. 8.2 – 20.5 and Ch. 36 – 39 and PTE-E Invert Ch. 0 – 7.5. - Sheet Waterproofing Membrane – ITP items 4.1, 4.2 and 4.3 Missing Acceptance of injection tubes (__ form D3-82) for block 2 (Ch. 8.211 – 16.741). • Cxxx-__M-C4-LLG-D061-50224 Deliverable Records for CP2N/PTE-W and PTE-E Secondary Lining: Secondary 1st, Secondary 2nd & Fireproofing (Traditional Method) (W022) - Secondary 1st layer – ITP item C5 Missing Hammer testing check sheet (__ form D3-80) for CP2N Crown Ch. 8.2 – 16.7 and PTE-W Crown Ch. 15 - 18. - Secondary 2nd layer – ITP items C2, C4, 1.1, 4.2, 4.3, 4.4, 4.6, 5.3 and 5.4 Missing Secondary lining concrete placement check sheet (__ form D3-86) for PTE-W Ch. 15 - 18.
| 02SL - Stations (LUL) | Cxxx-NCR-001141 | NCR | W - CS1 SL and Completion Works: Missing checks / documentation |  | Contr | __M |  |  | 2016-10-21 | 2016-11-09 11:38 | 19 | 2015-12-08 10:05 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | • Regulating Layer: o Early Strength Testing: No early strength testing was performed in CS1. Tests are to be taken every third bay. o Rebound Testing A rebound test of regulating layer was not performed during the time period in which CS1 was constructed. • Cast-In Situ Layer o Temperature / Ambient Temperature of Workface No temperature measurements taken of concrete and recorded on concrete pour checksheets. Refer to Att.01 • Secondary Lining Layers o Early Strength Testing No early strength testing was performed in CS1. Tests are to be taken every third bay. o Rebound Testing A rebound test of regulating layer was not performed during the time period in which CS1 was constructed. o Hammer Testing
| 02SL - Stations (LUL) | Cxxx-NCR-001142 | NCR | W - VA2 SL Missing Test and documentation |  | Contr | __M |  |  | 2017-06-30 | 2017-05-26 14:26 | -35 | 2017-02-24 10:44 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | • Cxxx-__M-C4-LLG-D061-50175 Deliverable Records for VA2 Shaft Opening: 1) ITP item 4.2, Installation/Flushing of re-injectable and contact grouting tubes (Prior to pouring) Acceptance of injection tubes (__ Form D3-82) no sheet on file 2) ITP item 7.2, Repair works – formwork tie system Concrete Repair Checksheet (__ Form D3-60) not in file.
| 02SL - Stations (LUL) | Cxxx-NCR-001143 | NCR | L - RCW Block 1: Water Leaks in the SL 1st layer |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-01-31 | 2015-12-18 09:46 | -44 | 2015-10-23 11:49 | Tunnelling - Tunnelling General | 3000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | L-19/10/2015 - DS- Shift 1 - The first layer of the secondary lining has been sprayed in RCW Block 1 and water ingress has been notices in 2 places (see att. 01). Leakage 1: Through the invert of the junction between RCW and VD1 Block 1 in the location of where there is sheet membrane (Between 5 O'clock and 7 O'clock) therefore not meeting the required specification. Leakage 2: Through the invert of the junction between the “connection” concrete Invert and the TBM segments in the location of where there is sheet membrane (Between 5 O'clock and 7 O'clock) therefore not meeting the required specification. (Att.01 -Show pictures of leakage 1 + 2)
| 02SL - Stations (LUL) | Cxxx-NCR-001144 | NCR | W - PTW-W from CP2 to EP1: Tights spots in the primary lining |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-08-05 | 2016-03-17 16:26 | -141 | 2015-12-03 16:20 | Tunnelling - Linings - Sprayed Concrete | 6000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • PTW-W Primary Lining profile scans from CP2 to EP1 ( Chainage 0 to 160 ) show some tights spots between CH5 - CH104 (3 O'clock to 9 O'Clock). The depth of these encroachment vary from 0mm to 130mm. • Refer to Att.01 for the plan view of the tights spots and Att.02 for the profiles thickness.
| 02SL - Stations (LUL) | Cxxx-NCR-001145 | NCR | L-PRM-__ channel misalignment |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2015-11-22 | 2015-11-17 16:05 | -5 | 2015-10-23 12:04 | Tunnelling - Tunnelling General | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | L-20/10/2015 - DS- Shift 1 - Each __ channel pair is designed to span across two pours. Permission was given to install part in one pour and part in the following pour. __ __ channels did not line up perfectly between the two pours, with a “step” of 20-30mm between the two sections. Location 1: The first halfen channel pair was part of pour 1 & 4/5 which is situated below. (See Att.04 for location) Location 2: The second halfen channel pair was part of pour 3a/b & 6 which is situated above. (See Att.04 for location) See marked up drawings attached. Att.02- Mark Up drawing (Location 1) Att.03- Mark Up drawing (Location 2)
| 02SL - Stations (LUL) | Cxxx-NCR-001146 | NCR | L- PTW-W - Underthickness In Fireproofing Layer |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-01-29 | 2016-01-19 11:40 | -10 | 2015-11-12 16:07 | Tunnelling - Linings - Sprayed Concrete | 4000 |  | Testing and Commissioning | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | L-12/10/2015 -DS-Shift 3 - During the trial application of Fire proofing layer using the Logica, the scans attached indicate areas of underthickness shown in red of the FP(Att.01). These areas are present between CH85-CH89 and are located primarily betenn two bays as well as with the single bays. The location are between 8 O'Clock - 4O'Clock (South Side) with the depth ranging from 0mm - 30mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001147 | NCR | L-CP3 & CP3a / PTW-W - Tight Spots in Fireproofing Layer |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-02-06 | 2015-12-18 10:05 | -50 | 2015-10-29 16:20 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | L-26/10/2015-(NS - Shift 3)- The tight spots are located in the areas sprayed with profiles bars with the __. PTW Block 16 / CP3a - From the scan (Att.01) it can be seen that there is tight spots in the crown between CH34-CH42 (10 O'Clock - 2 O'Clock). The depth of the tight spots vary from 0mm-40mm. The biggest tight spot is 2mx1m. PTW Block 19 / CP3 - There tight spots found in Block 19 outside of CP3 (Att.02). It can be seen that the tight spots are in the crown between CH69-CH75 (11 O'Clock x 1 O'Clock). The depth varies from 10mm-20mm. The biggest one is 800mm x 800mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001148 | NCR | W - PTW E RCW transition block poured without signed off paperwork |  | Contr | __M |  |  | 2016-02-26 | 2016-02-02 15:26 | -24 | 2015-11-03 10:42 | Train - Interfaces | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | • On the 30/10/15 pouring of PTW-E RCW Transition Block 1 Invert ( chainage 100-110 ) was done without Cxxx/CRL being given the opportunity to inspect ( As per ITP Cxxx-__M-C4-ITP-CR092-50009 CRL/Cxxx Item 3.3 it is a Witness point ) . Refer to Att.01 for the pre-pour checksheet not signed by CRL/Cxxx
| 02SL - Stations (LUL) | Cxxx-NCR-001149 | NCR | W - PTW E RCW insufficient thickness of sprayed membrane in transition area |  | Contr | __M |  |  | 2016-02-26 | 2016-01-29 16:27 | -28 | 2015-11-04 16:59 | Tunnelling - Linings - In-situ Concrete | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | • On the 31/10/15 Insufficient thickness of sprayed waterproofing near the TBM segments and in the transition block area has been found. • The dry cut-out patches test done have shown 1 mm in the north side invert between ch 121.85 and 123.85 and 2 mm for the south invert side invert between ch 121.85 and 123.85. • Refer to Att.01 for the test results checksheets and Att.05 for plan with section of the affected areas
| 02SL - Stations (LUL) | Cxxx-NCR-001150 | NCR | W - PTW E/RCW: Insufficient embedding of wiremesh in transition slab |  | Contr | __M |  |  | 2016-02-11 | 2016-01-22 13:22 | -20 | 2015-11-03 13:42 | Tunnelling - Linings - In-situ Concrete | 2000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | • On 31/10/2015, at Whitechapel site, the transition block between PTW-E and RCW was poured leaving a section of the wire mesh reinforcement exposed and not encased in concrete. Refer to marked up plan Att.01 for specific location of the defect. Exposed area is approximately 3000mm x 400mm and 300mm deep. Refer to the Att.01 for photo of the defect
| 02SL - Stations (LUL) | Cxxx-NCR-001151 | NCR | W - RCW Block 1A: No curing applied in Cast In-Situ Sidewalls |  | Contr | __M |  |  | 2016-02-12 | 2016-01-21 16:48 | -22 | 2015-11-06 11:00 | Tunnelling - Linings - In-situ Concrete | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | On the 03/11/15 DS - Block 1A cast in-situ sidewalls were found with no evidence on application of curing product.
| 02SL - Stations (LUL) | Cxxx-NCR-001152 | NCR | L-PTW-W - Block 22 - Exposed masterseal in transition area |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-02-11 | 2015-12-11 15:35 | -62 | 2015-11-03 17:04 | Tunnelling - Linings - Sprayed Concrete | 4000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | L-02/10/2015-DS-Shift 3 - Whilst the team was hammer tapping they found hollow spots in the transition are in Block 22 (PTW-W Headwall). To remove the hollow spot the construction team should trim by hand but instead the supervisior decided to use the road header to remove the hollow spots which exposed and damaged the masterseal, an area of 300mm x 600mm (Att.01)
| 02SL - Stations (LUL) | Cxxx-NCR-001153 | NCR | W - PTW-E/CP3: Over spraying of Masterseal with Secondary lining |  | Contr | __M |  |  | 2016-02-12 | 2016-02-02 16:59 | -10 | 2015-11-04 15:31 | Tunnelling - Linings - Sprayed Concrete | 8000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | CP3 South eye was formed before the transit of the Cxxx TBM through the station. At that time, works were not completed in cleaning and forming an appropriate joint connection for the remaining secondary lining in CP3. The original SCL was placed around the CP3 South eye on 08/06/2014. After gaining access post Cxxx TBM handover to Cxxx, work has commenced on completing the secondary lining in the CP3 South area. On the 02/11/15 when trying to remove the overspray from the __ waterproofing, damage was caused in knee of PTW-E/CP3 junction inside CP3 tunnel around 8 and 9' oclock ( West Side ). Due to the concrete being in place for so long, it is not possible to form an acceptable joint and remove overspray without damaging the __ waterproofing. Refer to Att.01
| 02SL - Stations (LUL) | Cxxx-NCR-001154 | NCR | L- PTW-W - Hollow Spots in Fireproofing Layer |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-09-30 | 2017-09-14 13:40 | -16 | 2015-11-05 14:35 | Tunnelling - Tunnelling General | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • During PTW-W hammer tapping of the fire proofing layer, the following hollow spots have been found: - Block 19 ch 73 Crown ( near CP3 junction ), see Att.01 - Block 21 ch 98.5 track side, see Att.07 - Block 21 ch 105 track side, see Att.02 - Block 22 ch 115 at 2'o clock, see Att.21 - Block 22 ch 115 platform side, see Att.21 - Block 22 ch 118 platform side, see Att.23 • This is summarized in Att.29 hollow spot tracker
| 02SL - Stations (LUL) | Cxxx-NCR-001155 | NCR | L-RCW-__ hoses Lost between block 1 and block 2 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-02-12 | 2015-12-11 15:29 | -63 | 2015-11-04 15:53 | Tunnelling - Tunnelling General | 1000 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | L-28/10/2015- NS- Shift 2 - When surveying the __ (Re-injectable) hoses in Block 1 RCW, water was flushed through all the hoses and it was noted that Hose No 9 was blocked. After injecting the hoses to try and solve the water ingress problem, 3 other hoses became blocked (Hose No 10 , 11 & 31) during the injection process. When flushing afterwards with water, the hoses were found to be blocked. Please see Att.01 for __ hoses injection tracker Please see Att.02 for As-Built plan and __ Locations
| 02SL - Stations (LUL) | Cxxx-NCR-001156 | NCR | W - RCW __ Wet film thickness checksheets ( __ Form D3-101 ) lost |  | Contr | __M |  |  | 2015-12-04 | 2015-11-27 13:37 | -7 | 2015-11-04 16:31 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | On the 02/11/15 it has been found that the first two layers of wet film thickness in RCW segmental connection haven’t been recorded in D3-101 form.
| 02SL - Stations (LUL) | Cxxx-NCR-001157 | NCR | L - Moorgate Shaft Wall 4: Waterbar not installed |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-07-08 | 2016-06-10 11:28 | -28 | 2015-11-05 16:39 | Tunnelling - Linings - In-situ Concrete | 3000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On the 05/11/15 DS (Shift 3 ) The waterbar at the joint between wall A3 and future wall B4 has not been installed. Location of defect can be seen in Att.02A. Att.02 is superseeded by Att.02A
| 02SL - Stations (LUL) | Cxxx-NCR-001158 | NCR | LIV & WHI: Pour of the transition blocks in the Chambers starting without approved WMS. |  | Contr | __M |  |  | 2016-02-05 | 2015-11-26 08:22 | -71 | 2015-11-10 15:01 | Tunnelling - Linings - In-situ Concrete | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | • Connection to TBM Rings works in the chambers were covered by the secondary lining methodology WMS but due to FCD 717, raised by __ the 28/09/15 and closed by CRL the 08/10/15, a WMS was put in place to help formalise this and capture the process again for the next chambers in LIV and WHI. • On the 01/10/15, Cxxx-__-C4-GMS-CR092-50013 WMS - Secondary Lining Addendum 2 - Segmental Lining Connection has been submitted to CRL in eB. • On the 07/10/15, pour of the transition blocks in the RCW in Whitechapel station has started under Cxxx instructions to start the works without having the WMS accepted ( Refer to the Att.01 email ) • On the 2/11/15, Cxxx-__-C4-GMS-CR092-50013 WMS - Secondary Lining Addendum 2 - Segmental Lining Connection has been coded 2 by CRL.
| 02SL - Stations (LUL) | Cxxx-NCR-001159 | NCR | L - Concrete drying shrinkage failure of mix RL2 C28/34 2kg PP |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-08-26 | 2016-04-29 10:00 | -119 | 2016-01-29 14:53 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | • 28 days samples CR2381 taken 09/09/15 and CR2424 taken 12/10/15 failed to comply with specification limit. Failure range - 0.025% and 0.009% respectively. • See Att.01 and Att.02 for the test results.
| 02SL - Stations (LUL) | Cxxx-NCR-001160 | NCR | W - PTW-W: Core Holes backfilled with muck |  | Contr | __M |  |  | 2016-05-31 | 2016-03-17 10:18 | -75 | 2015-11-13 09:49 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On 10/11/15, it has been found that in PTW-W Enlargement Invert Chainage 150 around 6'o clock , some core holes have been backfilled with muck. (see photo att01)
| 02SL - Stations (LUL) | Cxxx-NCR-001161 | NCR | W - PTE & PTW: Incorrect position of the termination boxes |  | Contr | __M |  |  | 2016-02-21 | 2016-02-02 17:53 | -19 | 2015-11-13 12:14 | Tunnelling - Linings - Sprayed Concrete | 8000 |  | Planning | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | On 11/11/15 PTW and PTE termination boxes in the platform side have been found installed at level 86.500 instead of 85.200 ( 84.700 top wingwall + 0.500 ). All termination boxes in the PTE and PTW platforms ( platfrom side ) are affected - around 100.
| 02SL - Stations (LUL) | Cxxx-NCR-001162 | NCR | W - Disrupted shotcrete supply to Durward Street Shaft |  | Contr | __M |  |  | 2016-02-26 | 2016-01-26 14:24 | -31 | 2015-12-10 15:48 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | • On 04/10/2015 Because Cxxx did not have possession of the running tunnels ES1 enlargement was carried out from inside Durwrad Street Shaft. • Shotcrete deliveries came from Whitechapel batching plant utilising road registered remixer wagons. • On December 3rd Whitechapel main site access was blocked by Cxxx crane maintenance operations and shotcrete was being supplied from the Liverpool Street batching plant. • Only 1 concrete wagon was used which created a disrupted concrete supply due to the 2hr turn around.
| 02SL - Stations (LUL) | Cxxx-NCR-001163 | NCR | W - PTW-W Block 1A: Incorrect IAT repair works of the wingwalls |  | Contr | __M |  |  | 2016-02-26 | 2016-02-01 17:07 | -25 | 2015-12-10 16:05 | Tunnelling - Linings - In-situ Concrete | 2500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | • On 25/10/2015 Sheet membrane has been found damaged, probably during the placement of invert shutters in Block 1A ( Bay 4 and Bay 6 - ch111.9 to 121.8 in the invert )
| 02SL - Stations (LUL) | Cxxx-NCR-001164 | NCR | W - RCW: Debonding of Masterseal |  | Contr | __M |  |  | 2016-02-19 | 2016-02-01 16:53 | -18 | 2015-12-01 14:18 | Tunnelling - Linings - Sprayed Concrete | 8000 |  | Material | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | • On 19/11/15 __ Masterseal 345 bond tests in the area of RCW (chainage 107.9 to 114.3 from 3 to 9' oclock ) were found to be less than 0.5 N/mm2 in all the 7 tests cases. • De-bonding between the individual layers and also the first layer and the substrate was observed. • Refer to Att.01 for the bond tests results
| 02SL - Stations (LUL) | Cxxx-NCR-001165 | NCR | W - PTW Tights spots in the secondary lining |  | Contr | __M |  |  | 2016-02-26 | 2016-01-25 16:14 | -32 | 2015-12-09 11:33 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | • On 07/09/15 scans have shown from Ch10 to Ch70 between 8 and 4'oclock several areas of secondary lining 2nd layer that were tighter than 90mm to the Crossrail tolerance zero line. • Refer to Att.01
| 02SL - Stations (LUL) | Cxxx-NCR-001166 | NCR | L- RCW- Underthickness in FP Layer - CH137 - CH167 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-08-25 | 2017-09-14 12:59 | 20 | 2015-11-26 19:03 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | L-15/11/2015 - The scans for RCW shows underthickness (Required thickness is 50mm) in the fire proofing layer between CH 137 - CH 167. There are 10 points of underthickness ( Between 30mm - 45mm), mainly located just above the wing walls (Between 8 O'Clock and 4 O'Clock),this can be seen in Att.01. To clarify areas highlighted yellow in Att.01 are between 50mm - 60mm. Areas highlighted red are under 50mm and other areas green/blue are 60mm. It has been agreed between CRL/Cxxx and __ quality teams to raise multiple under thickness in one area as one NCR (NCR Meeting - 18/11/2015- Attended by __ , __ , __ , __ and __). Photos of the set of underthicknesses will be stated via a photo.
| 02SL - Stations (LUL) | Cxxx-NCR-001167 | NCR | L-PTWE- Underthickess In FP Layer - CH 30 - CH 60 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-10-15 | 2016-11-16 09:31 | 32 | 2015-11-26 19:03 | Tunnelling - Linings - Sprayed Concrete | 7000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | L-15/11/2015 - The scans for PTWE shows underthickness (Required thickness is 50mm) in the fire proofing layer between CH 30 - CH 60.There are 4 points of underthickness ( around 45mm), mainly located by the wing walls (Between 7 O'Clock and 5 O'Clock),this can be seen in Att.01.To clarify areas highlighted yellow in Att.01 are between 50mm - 60mm. Areas highlighted red are under 50mm and other areas green/blue are 60mm. It has been agreed between CRL/Cxxx and __ quality teams to raise multiple under thickness in one area as one NCR (NCR Meeting - 18/11/2015- Attended by __ , __ , __ , __ and __).
| 02SL - Stations (LUL) | Cxxx-NCR-001168 | NCR | L-PTWW- Underthickess In FP Layer - CH 18 - CH 50.5 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-11-18 | 2016-11-19 12:18 | 1 | 2015-11-26 19:04 | Tunnelling - Linings - Sprayed Concrete | 8000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | L-15/11/2015 - The scans for PTW-W shows underthickness (Required thickness is 50mm) in the fire proofing layer between CH 18 - CH 50.5. There are 9 points of underthickness (Between 30mm and 45mm), mainly located just above the wing walls (At 7 O'Clock and 5 O'Clock),this can be seen in Att.01. To clarify areas highlighted yellow in Att.01 are between 50mm - 60mm. Areas highlighted red are under 50mm and other areas green/blue are 60mm. It has been agreed between CRL/Cxxx and __ quality teams to raise multiple under thickness in one area as one NCR (NCR Meeting - 18/11/2015- Attended by __ , __ , __ , __ and __). Photos of the set of underthicknesses will be stated via a photo.
| 02SL - Stations (LUL) | Cxxx-NCR-001169 | NCR | L-RCW- Underthickess In FP Layer - CH 127 - CH 138 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-07-29 | 2016-07-29 14:30 | 0 | 2015-11-26 19:04 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | L-15/11/2015 - The scans for RCW shows underthickness (Required thickness is 50mm) in the fire proofing layer between CH 127 - CH 137. There are 3 points of underthickness ( Between 30mm - 45mm), mainly located just above the wing walls (At 7 O'Clock and 5 O'Clock),this can be seen in Att.01. To clarify areas highlighted yellow in Att.01 are between 50mm - 60mm. Areas highlighted red are under 50mm and other areas green/blue are 60mm. It has been agreed between CRL/Cxxx and __ quality teams to raise multiple under thickness in one area as one NCR (NCR Meeting - 18/11/2015- Attended by __ , __ , __ , __ and __). Photos of the set of underthicknesses will be stated via a photo.
| 02SL - Stations (LUL) | Cxxx-NCR-001170 | NCR | L-PTWW - Underthickess In FP Layer - CH 77- CH 107 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-11-18 | 2016-10-13 09:05 | -36 | 2015-11-26 19:07 | Tunnelling - Linings - Sprayed Concrete | 7000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | L-15/11/2015 - The scans for PTW-W shows underthickness (Required thickness is 50mm) in the fire proofing layer between CH 77 - CH 107. There are 5 points of underthickness (between 30mm and 45mm) , mainly located just above the wing walls (between 8 O'clock - 4 O'clock ),this can be seen in Att.03. To clarify areas highlighted yellow in Att.01 are between 50mm - 60mm. Areas highlighted red are under 50mm and other areas green/blue are 60mm. It has been agreed between CRL/Cxxx and __ quality teams to raise multiple under thickness in one area as one NCR (NCR Meeting - 18/11/2015- Attended by __ , __ , __ , __ and __). Photos of the set of underthicknesses will be stated via a photo.
| 02SL - Stations (LUL) | Cxxx-NCR-001171 | NCR | L-PTWW- Underthickess In FP Layer - CH 50.5 - CH 77 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-10-14 | 2016-11-22 09:46 | 39 | 2015-11-26 19:07 | Tunnelling - Linings - Sprayed Concrete | 9000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | L-15/11/2015 - The scans for PTW W shows underthickness (Required thickness is 50mm) in the fire proofing layer between CH 50.5- CH 77. There are 6 points of underthickness( Between 35mm and 45mm) , mainly located just above the wing walls (Between 7 O'Clock and 5 O'Clock),this can be seen in Att.01. To clarify areas highlighted yellow in Att.01 are between 50mm - 60mm. Areas highlighted red are under 50mm and other areas green/blue are 60mm. It has been agreed between CRL/Cxxx and __ quality teams to raise multiple under thickness in one area as one NCR (NCR Meeting - 18/11/2015- Attended by __ , __ , __ , __ and __). Photos of the set of underthicknesses will be stated via a photo.
| 02SL - Stations (LUL) | Cxxx-NCR-001172 | NCR | L - PTW-W and LCWb SL: Missing tests and documentation |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-09-06 | 2017-09-14 13:09 | 8 | 2017-08-04 09:12 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • Cxxx-__M-C4-LLG-C101-50150 Deliverable Records for PTW-W and LCWb Cast In-situ – L077: 1) Cast In-situ ( Inverts ): - Cubes not taken for blocks 19, 21 and 22 - Cubes not taken for Chainage 147.512 - 149.346 ( Block 24 ) - Missing __ Form D3-84 Concrete Pour Check Sheet for Chainage 147.512 - 149.346 ( Block 24 ) Cast In-situ ( Side walls ): - ITP item 3.7 (method of curing) is not filled in for check sheets covering blocks 13, 14, 15, 16, 17, 18, 19, 20 and 23. - Cubes not taken for blocks 13, 15 and 21 - Missing records for Workability and Concrete Temperature on __ Form D3-84 for Block 21 • Cxxx-__M-C4-LLG-C101-50174 Deliverable Records for PTW-W and LCWb Regulation layer – L077: 2) Regulation: ITP Item C3, 1.1, 2.1, 2.3 and 2.5 - Missing Shotcrete Placement Checksheet (__ Form D3‐86) of PTW-W Ch 82 to 88 crown and ch 97-108 invert - Missing Shotcrete Placement Checksheet (__ Form D3‐86) of PTW-W Ch 68 to 83 crown 3) Regulating: ITP Item 2.6 - Missing hammer tapping checksheet ( __ Form D3-80 ) of PTW-W Ch 65-83 ( Crown ), Ch 100-108 ( Crown ) and Ch 110 to 129 ( Mix P2 ) • Cxxx-__M-C4-LLG-C101-50175 Deliverable Records for PTW-W and LCWb Sprayed Waterproofing – L077: 4) __: Missing bags calculation prior application of the __ Missing calculation of the bags before application of the TSL 865 in the Pre-placement checksheet ( __ Form D3-98 ) PTW-W Ch 60 to 85 • Cxxx-__M-C4-LLG-C101-50182 Deliverable Records for PTW-W and LCWb Secondary lining – L077: 5) - Combined secondary lining: ITP 5.9 Survey of Layer Thickness and Profile Check (As built records) Scans in Cxxx-__M-C4-LLG-C101-50510 page 233, 295, 335, 367,416,450 and 463 show some localised total secondary lining undethickness. Worst case is 220mm instead of 250mm at PTW-W / CP3 crown at ch 71.5 ( page 416 ). Please note that underthickness shown in page 386 is at the boundary and should be disregarded, values are not relevant. - Missing concrete workability/flow and temperature test information for LCWb Ch 143-145.5 on Second First • Cxxx-__M-C4-LLG-C101-50222 Deliverable Records for PTW-W and LCWb Portal Opening – L077: 6) Portal Opening: Missing Post concrete inspection datas Missing Post pour concrete checks on Concrete Pour checksheet Pour No 4 ( page 54 )
| 02SL - Stations (LUL) | Cxxx-NCR-001174 | NCR | W - PTW-E Ch 28 to 32: Incorrect fireproofing length bay sprayed. |  | Contr | __M |  |  | 2016-01-22 | 2015-12-10 15:50 | -43 | 2015-12-03 14:33 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | • On 01/12/15 NS a 4 meter length fireproofing bay was sprayed, chainages 28 to 32 in PTW-E. Chainages 28 to 31 was to be sprayed.
| 02SL - Stations (LUL) | Cxxx-NCR-001175 | NCR | W - CP3: Debonding of Masterseal |  | Contr | __M |  |  | 2016-03-18 | 2016-02-02 17:59 | -45 | 2015-12-09 15:38 | Tunnelling - Linings - Sprayed Concrete | 4000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | • A small section of was being prepared for secondary lining and Masterseal 345 was applied. • On 20/11/15 __ Masterseal 345 bond tests in CP3 (Ch6 – Ch12 ) were found to be less than 0.5 N/mm2. De-bonding between the individual layers and also the first layer and the substrate was observed (note this also happened to a much greater extent in RCW at the same time) • Areas debonding are in the RHS and LHS knees ( around 8 to 9 o'clock and 3 to 4o'clock ) and approx 2m2 on each side.
| 02SL - Stations (LUL) | Cxxx-NCR-001176 | NCR | W - PTW-E: Underthickness in FP Layer - CH13 - CH66 |  | Contr | __M |  |  | 2016-03-25 | 2016-02-29 14:40 | -25 | 2015-12-09 11:41 | Tunnelling - Linings - Sprayed Concrete | 15000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On 25/01/16 - The scans for PTW-E shows underthickness (Required thickness is 50mm) in the fire proofing layer between CH 13 - CH 66. There are 10 points of underthickness between 40mm - 45mm from 10 O'Clock to 4 O'Clock,this can be seen in Att.A, AttB and AttC. To clarify the attachments (A, B and C): - areas highlighted in red have a thickness under 50mm, - areas highlighted in yellow have a thickness between 50mm - 60mm. - other areas in green/blue have a thickness above 60mm. (Please disregard Att01, 02 and 03 which have been attached by mistake and can't be removed)
| 02SL - Stations (LUL) | Cxxx-NCR-001177 | NCR | W - PTW-E and CP3: Encroachment of the FP profile - CH13 to CH66 and CH03 to CH10 |  | Contr | __M |  |  | 2016-07-29 | 2016-03-01 16:48 | -150 | 2015-12-09 16:14 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On 25/01/16, there are some occurrences where the finished tunnel lining has encroached on the CRTL final profile in PTW-E, between CH13 to 66 and in CP3 between CH03 to CH10. The exact location of the tights spots are available in Att. A, B, C for PTW-E and in Att.D for CP3 These various areas have been over-sprayed by max 20mm (and 2 areas by 30mm), meanly in the crown from 10 to 4 o'clock. The thickness of the tights spots are available in Att. E, F, G for PTW-E and in Att. H for CP3 (Please disregard Att01 and 02 which have been attached by mistake and can't be removed)
| 02SL - Stations (LUL) | Cxxx-NCR-001178 | NCR | L- RCW - Block 4a - Wing wall final thickness not achieved |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-01-29 | 2016-01-21 13:19 | -8 | 2015-12-08 09:12 | Tunnelling - Linings - In-situ Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | L-26/11/2015 - The thickness on the side of the wing wall in RCW Block 4a (CH116) has been spotted at roughly 270 - 290mm (Att.01). Area of under thickness is very remote (200mm x 200mm area). It is located at 4 O'Clock. This NCR has been seperated from NCR954.
| 02SL - Stations (LUL) | Cxxx-NCR-001179 | NCR | W - PTW-E Ch36 – 39: __ hoses missing in the secondary lining layer |  | Contr | __M |  |  | 2016-01-28 | 2016-02-04 11:39 | 7 | 2015-12-09 15:29 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | • The re-injectable __ hoses in PTW-E Ch36-39 invert that are part of the sheet membrane installation are extended above the wing walls and then brought out through the sprayed secondary lining to terminate in boxes for later access. • The secondary lining first and second layers were sprayed in this location over a year ago. When the timber box outs were removed recently there were no hoses present. Further break out in the location of the box outs showed no sign of the hoses.
| 02SL - Stations (LUL) | Cxxx-NCR-001180 | NCR | W - RCW: Tights spots in the SL 1st layer |  | Contr | __M |  |  | 2016-02-26 | 2016-01-26 16:26 | -31 | 2015-12-09 16:04 | Tunnelling - Linings - In-situ Concrete | 4000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | • On 07/12/15 NS in the transition zone to the TBM segments ( Ch122 Approx.) the secondary lining fisrt layer was sprayed to final profile instead of CRTL ZERO +230mm. Areas of defect approx 2000mm x 200mm at 3 to 4'o clock and 8 to 9 o'clock, max +70mm ( Refer to Att.01) • This was restricted to the trailing edge connection to the cast wing walls • There was no space to spray the final 150mm combined FP layer
| 02SL - Stations (LUL) | Cxxx-NCR-001181 | NCR | L- PTW-W - Underthickness In FR Layer - CH0 To CH18 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-07-29 | 2016-07-28 15:19 | -1 | 2015-12-09 11:47 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | L-09/12/2015 - The scans for PTW-W shows underthickness (Required thickness is 50mm) in the fire proofing layer between CH 0 - CH 18. There are 3 points of underthickness ( Between 30mm - 45mm), mainly located just above the wing walls (Between 3 O'Clock and 5 O'Clock),this can be seen in Att.01. To clarify areas highlighted yellow in Att.01 are between 50mm - 60mm. Areas highlighted red are under 50mm and other areas green/blue are 60mm. It has been agreed between CRL/Cxxx and __ quality teams to raise multiple under thickness in one area as one NCR (NCR Meeting - 18/11/2015- Attended by __ , __ , __ , __ and __). Photos of the set of underthicknesses will be stated via a photo.
| 02SL - Stations (LUL) | Cxxx-NCR-001182 | NCR | L-PTWW- Underthickess In FP Layer - CH 107 - CH 122 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-08-05 | 2016-08-19 12:41 | 14 | 2015-12-09 13:05 | Tunnelling - Linings - Sprayed Concrete | 8000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | L-09/12/2015 - The scans for PTW-W shows underthickness (Required thickness is 50mm) in the fire proofing layer between CH 107 - CH 122. There are 7 points of underthickness (45mm), mainly located just above the wing walls (At 7 O'Clock and 5 O'Clock),this can be seen in Att.01. To clarify areas highlighted yellow in Att.01 are between 50mm - 60mm. Areas highlighted red are under 50mm and other areas green/blue are 60mm. It has been agreed between CRL/Cxxx and __ quality teams to raise multiple under thickness in one area as one NCR (NCR Meeting - 18/11/2015- Attended by __ , __ , __ , __ and __). Photos of the set of underthicknesses will be stated via a photo.
| 02SL - Stations (LUL) | Cxxx-NCR-001183 | NCR | L-PTW-E- Underthickess In FP Layer - CH 0 - CH 30 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-11-18 | 2016-12-14 18:06 | 26 | 2015-12-09 14:06 | Tunnelling - Linings - Sprayed Concrete | 4000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | L-09/12/2015 - The scans for PTW-E shows underthickness (Required thickness is 50mm) in the fire proofing layer between CH 0 - CH 30. There are 2 points of underthickness, mainly located in the wing walls (this can be seen in Att.01. To clarify areas highlighted yellow in Att.01 are between 50mm - 60mm. Areas highlighted red are under 50mm and other areas green/blue are 60mm. It has been agreed between CRL/Cxxx and __ quality teams to raise multiple under thickness in one area as one NCR (NCR Meeting - 18/11/2015- Attended by __ , __ , __ , __ and __). Photos of the set of underthicknesses will be stated via a photo.
| 02SL - Stations (LUL) | Cxxx-NCR-001184 | NCR | L-PTWE- Underthickess In FP Layer - CH 60 - CH 90 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-12-21 | 2017-01-19 10:15 | 29 | 2015-12-09 14:21 | Tunnelling - Linings - Sprayed Concrete | 8000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | L-09/12/2015 - The scans for PTW-E shows underthickness (Required thickness is 50mm) in the fire proofing layer between CH 60 - CH 90. There are 7 points of underthickness ( Between 40mm and 45mm), mainly located in the wing walls (this can be seen in Att.01. To clarify areas highlighted yellow in Att.01 are between 50mm - 60mm. Areas highlighted red are under 50mm and other areas green/blue are 60mm. It has been agreed between CRL/Cxxx and __ quality teams to raise multiple under thickness in one area as one NCR (NCR Meeting - 18/11/2015- Attended by __ , __ , __ , __ and __). Photos of the set of underthicknesses will be stated via a photo.
| 02SL - Stations (LUL) | Cxxx-NCR-001185 | NCR | L-PTW-E- Underthickess In FP Layer - CH 90 - CH 120 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-08-02 | 2017-08-17 09:55 | 15 | 2015-12-09 14:30 | Tunnelling - Tunnelling General | 10000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | L-09/12/2015 - The scans for PTW-E shows underthickness (Required thickness is 50mm) in the fire proofing layer between CH 90 - CH 120. There are 9 points of underthickness, mainly located in the wing walls (this can be seen in Att.01. To clarify areas highlighted yellow in Att.01 are between 50mm - 60mm. Areas highlighted red are under 50mm and other areas green/blue are 60mm. It has been agreed between CRL/Cxxx and __ quality teams to raise multiple under thickness in one area as one NCR (NCR Meeting - 18/11/2015- Attended by __ , __ , __ , __ and __). Photos of the set of underthicknesses will be stated via a photo.
| 02SL - Stations (LUL) | Cxxx-NCR-001186 | NCR | L-PTW-E- Underthickess In FP Layer - CH 120 - CH 127 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-09-02 | 2016-08-22 09:55 | -11 | 2015-12-17 16:29 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | L-09/12/2015 - The scans for PTW-E shows underthickness (Required thickness is 50mm) in the fire proofing layer between CH 120 - CH 127. (this can be seen in Att.01. To clarify areas highlighted yellow in Att.01 are between 50mm - 60mm. Areas highlighted red are under 50mm and other areas green/blue are 60mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001187 | NCR | L-RCW- Underthickess In FP Layer - CH 120 - CH 137 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-08-25 | 2017-09-14 13:51 | 20 | 2015-12-09 14:52 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | L-09/12/2015 - The scans for RCW shows underthickness (Required thickness is 50mm) in the fire proofing layer between CH 60 - CH 90. There are 1 points of underthickness. (this can be seen in Att.01). To clarify areas highlighted yellow in Att.01 are between 50mm - 60mm. Areas highlighted red are under 50mm and other areas green/blue are 60mm. It has been agreed between CRL/Cxxx and __ quality teams to raise multiple under thickness in one area as one NCR (NCR Meeting - 18/11/2015- Attended by __ , __ , __ , __ and __). Photos of the set of underthicknesses will be stated via a photo.
| 02SL - Stations (LUL) | Cxxx-NCR-001188 | NCR | L-VD1- Underthickess In FP Layer - CH 0 - CH 36 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-08-02 | 2017-08-17 10:13 | 15 | 2015-12-09 15:01 | Tunnelling - Linings - Sprayed Concrete | 8000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | L-09/12/2015 - The scans for VD1 shows underthickness (Required thickness is 50mm) in the fire proofing layer between CH 0 - CH 36. There are 11 points of underthickness, between 40mm and 45mm mainly located near RCW. This can be seen in Att.01, for a better understanding please note that areas highlighted in yellow are between 50mm - 60mm, in red are under 50mm and in green/blue are above 60mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001189 | NCR | W - EP1: Removal of damaged Masterseal |  | Contr | __M |  |  | 2016-06-03 | 2016-05-05 10:26 | -29 | 2015-12-09 16:16 | Tunnelling - Linings - Sprayed Concrete | 10000 |  | Planning | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | • __ 345 Masterseal waterproofing was applied to the crown of EP1. • After application the tunnel was backfilled and ramps sprayed with SCL to allow access for block removal works to connect in to Durward Street Shaft. • On October 2014 during wall removal the ramps, backfill and block removal works caused extensive damage to the spray applied membrane. • Damage discovered upon removal of the ramp on December 2014, but __ had no time to remediate it as tunnel had to be handed over to Cxxx. • Investigation of the defect has been done in November 2015 once __ had removed the TBM rails and segments. • Damaged Masterseal was found extensive and in the crown, shoulder, sides and knees ( from 7 to 4 o'clock ) all through the 10m of EP1 tunnel.
| 02SL - Stations (LUL) | Cxxx-NCR-001190 | NCR | L- Briefing on __ Hoses |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-03-19 | 2016-02-12 14:55 | -36 | 2015-12-10 14:24 | Tunnelling - Tunnelling General | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | L- 10/12/2015 This NCR has been raised on the basis of NCR 1143. Cxxx have asked for a briefing to be done with the following content; In the absence of a check-sheet of injection of FUKO hoses for 27-Oct-2015 – it is noted that __ are retesting all FUKO hoses prior to handover of PTW. This is a punch works item (ref. Cxxx-PWK-00103). __ must provide detail briefing covering (a) physical tagging/numbering (b) as built-schematics (c) grouting/injection check-sheets and (d) injection tracker. __ to upload (1) contents of briefing and (2) attendance lists of briefing. CRL/__ may wish to raise this as a separate NCR. This NCR will be closed once the briefing has been done. This has also been agreed between __ and Daniel reader on 09/12/2015.
| 02SL - Stations (LUL) | Cxxx-NCR-001191 | NCR | L- PTW-E & RCW - Hollow Spots In FP |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-03-03 | 2017-01-31 10:29 | -31 | 2015-12-15 17:44 | Tunnelling - Linings - Sprayed Concrete | 4000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | L- After hammer tapping the fire proofing layer in PTW-E and RCW the following hollow spots have been found: 1. 23/11/2015 - CH163 - 0.3 x 1.0m - Located at 3 O'Clock on the southside of the tunnel, see Att.01 2. 23/11/2015 - CH153 - 0.3 x 1.0m - Located at 9 O'clock Northside of the tunnel, see Att.01 3. 06/12/2015 - CH162.2 - 0.4 x 2.8m - Location at 1 O'clock Southside of the tunnel, see Att.01 4. 06/12/2015 - CH163.7 - 2.0 x 1.2m - Located at 1 O'Clock Southside of the tunnel, see Att.01 5. 09/12/2015 - ch 52.5 - Located between 2 and 4'Oclock Southside of the tunnel, see Att.04 6. 09/12/2015 - ch 67.5 - Located between 2 and 4'Oclock Southside of the tunnel, see Att.04
| 02SL - Stations (LUL) | Cxxx-NCR-001192 | NCR | L - AP6 Primary Lining: Missing tests and documentation |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-07-19 | 2017-07-21 13:50 | 2 | 2016-06-24 10:08 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Cxxx-__M-C4-LLG-C101-50115 Deliverable Records for AP6 Primary Lining Temporary Access from LCE Adv1-43 and Backfilling of Temporary Access from LCE - Package No L025 1) ITP Item C1 & C2: SCL Early strength requirement - Advances 09, 18, 22, 25, 37, 43 – Early strength tests missed - Advance 23 – Early strength tests missed at 1 and 3 hours - Advance 34 – Early strength tests missed at 3 hour 2) ITP Item C4: Estimated fibre & aggregate rebound No Rebound Tests carried out at Liverpool Street between the 03/02/15 and 01/06/15 (circa 4 months instead of 2 months) 3) ITP Item C5 & D4: Workability/Flow on point of spray application and ITP Item C6 &D5: Temperature of Shotcrete on point of spray application - Advances 16, 37 – No flow tests & temperature records for Initial and Primary Lining 4) ITP Item 2.1: Profiling of the Excavation (Sides, crown, invert, face) - Advance 01: under-excavation from 1mm to 42mm 5) ITP Item 4.3: Layer Thickness + Profile Check - Advance 01: underthickness of 2 localised points at 241mm & 242mm instead of 250mm - Advances 01, 02, 03, 05, 06, 07, 08, 11, 13, 15, 16, 19, 20, 21, 22, 23, 24, 25, 29, 30, 31, 35, 36, 37, 38, 39, 40, 41, 42, 43: profile encroachments from 1mm to 91mm Cxxx-__M-C4-LLG-C101-50117 Deliverable Records for AP6 Primary Lining Adv. 44-117 - Package No L025 6) ITP Item C1 & C2: SCL Early strength requirement - Advances 47, 65, 70, 71, 79, 83, 87, 100 – Early strength tests missed - Advances 44, 50, 56, 59, 67, 76, 102, 111 – Early strength tests missed at 1 hour - Advance 89, 97, 117 – Early strength tests missed at 1 and 3 hours - Advance 62 – Early strength missed at 12 hour - Advance 84 – Early strength tests missed at 1, 6 and 12 hours - Advance 92 – Early strength tests missed at 1, 3 and 12 hours - Advances 94, 105 – Early strength tests missed at 1 and 12 hours 7) ITP Item C4: Estimated fibre & aggregate rebound No Rebound Tests carried out at Liverpool Street between the 03/02/15 and 01/06/15 (circa 4 months instead of 2 months) 8) ITP Item C5 & D4: Workability/Flow on point of spray application and ITP Item C6 &D5: Temperature of Shotcrete on point of spray application - Advances 60, 72, 73, 96 – No flow & temperature tests records for Initial and Primary Lining - Advance 92 – No flow & temperature tests records for Initial Lining - Advance 98 – Missing information for Initial Lining Cxxx-__M-C4-LLG-C101-50130 Deliverable Records for AP6 Primary Lining Adv. 118-173 - Package No L025 9) ITP Item C1 & C2: SCL Early strength requirement - Advances 120, 139, 153, 158, 168 – Early strength tests missed - Advances 124, 133 – Early strength tests missed at 1 hour - Advance 127 – Early strength tests missed at 3 and 12 hours - Advance 130 – Early strength tests missed at 12 hour - Advance 140, 143, 169 – Early strength tests missed at 1 and 12 hours - Advance 147 – Early strength tests missed at 3 hour - Advance 154 – Early strength tests missed at 3, 6 and 12 hours 10) ITP Item C4: Estimated fibre & aggregate rebound No Rebound Tests carried out at Liverpool Street between the 03/02/15 and 01/06/15 (circa 4 months instead of 2 months) 11) ITP Item C5 & D4: Workability/Flow on point of spray application and ITP Item C6 &D5: Temperature of Shotcrete on point of spray application - Advance 139 – No flow & temperature tests records for Initial and Primary Lining Cxxx-__M-C4-LLG-C101-50116 Deliverable Records for AP6 Primary Lining - Access from Moorgate shaft Adv1-58 - Package No L025 12) ITP Item C1 & C2: SCL Early strength requirement - Advances 09, 19, 23, 31, 40, 55 – Early strength tests missed - Advance 06 – Early strength tests missed at 3, 6 and 12 hours - Advance 10 – Early strength tests missed at 3 and 6 hours - Advances 13, 44 – Early strength tests missed at 3 hours - Advance 16 – Early strength tests missed at 6 hours - Advance 41 – Early strength tests missed at 6 and 12 hours - Advance 58-1, 58-2, 58-3 – Early strength tests missed at 12 hours, 1 hour and 3 hours 13) ITP Item C4: Estimated fibre & aggregate rebound No Rebound Tests carried out at Liverpool Street between the 03/02/15 and 01/06/15 (circa 4 months instead of 2 months) 14) ITP Item C5 & D4: Workability/Flow on point of spray application and ITP Item C6 &D5: Temperature of Shotcrete on point of spray application - Advance 07 – No flow & temperature tests records for Initial and Primary Lining - Advance 22 – No flow & temperature tests records for Initial Lining 15) ITP Item 4.1: Ensure Joint Cleanliness / Substrate Cleanliness of previous Layer / surface of shotcrete to be cleaned wet / Removal of rebound - Advance 01 – Pocket II, 02 – Pocket I – Missing signatures for Pre-Shotcrete Check Primary Lining. See Att05 and Att06 16) ITP Item 7.3: Proof Drilling: Layer Thickness + Profile Check - Advances 1‐6, the proof drilling show that locations 12 and 13 have a thickness of 300 and 340mm respectively, instead of 350mm. See Att52. Cxxx-__M-C4-LLG-C101-50118 Deliverable Records for AP6a Thickening - Package No L025 17) ITP Item D2: SCL Compressive strength by core sampling even distributed around lining including joints AP6a/AP10 Thickening: No Compressive Strength Test carried out 18) ITP Item 5.3: Installation of guide rebars and Survey of Lining position relative to reinforcement position AP6 Thickening above LCE Far Face and AP6a/AP10 Thickening: Missing beamer records for the reinforcement 19) ITP Item 5.10: Layer Thickness + Profile Check The scans show significant underthickness (areas in red) around AP10a and AP10b openings 20) ITP Item 5.11: Curing & Protection of final layer (intrados) AP6a/AP10 Thickening Invert Pour 1 Sump: Missing Concrete Pour Checksheet (__ Form D3-05) therefore it’s impossible to demonstrate that curing has been applied
| 02SL - Stations (LUL) | Cxxx-NCR-001193 | NCR | L - PTE-W: Underthickess in FP Layer |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-08-25 | 2017-09-14 13:55 | 20 | 2016-03-02 12:13 | Tunnelling - Tunnelling General | 6000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Management Problem - Other | Completed |  | On 09/02/16 - Thickness scans (Att.01) for PTE-W shows underthickness (Required thickness is 50mm) in the fire proofing layer. They are between CH 23 - CH 72, three points of underthickness ( Between 40mm - 45mm), mainly located just above the wing walls (Between 2 O'Clock and 4 O'Clock),this can be seen in Att.01. To clarify areas highlighted yellow in Att.01 are between 50mm - 60mm. Areas highlighted red are under 50mm and other areas green/blue are 60mm. • From 17-30: 800 x 200mm at Ch 23 crown is 45mm thick - profile 40mm Underthickness in top wing wall at Ch 19 NS and Ch 23 SS • From 30-60: Underthickness in top wing wall at Ch 36 NS, Ch 40 to 42 NS and Ch 47 SS • From 60-90: 300 x 500mm at Ch 68 crown is 45mm thick - profile 50mm 1000 x 200mm at Ch 72 SS is 40mm thick - profile 40mm 200 x 200mm at Ch 80 SS is 45mm thick - profile 70mm Underthickness in top wing wall at Ch 62 NS and Ch 83 NS • From 90-106: Underthickness in top wing wall at Ch 91.5 SS and Ch 103 SS
| 02SL - Stations (LUL) | Cxxx-NCR-001194 | NCR | L - PTE-E: Underthickess in FP Layer |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-11-15 | 2017-12-04 09:32 | 19 | 2016-03-02 16:59 | Tunnelling - Linings - Sprayed Concrete | 6000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Management Problem - Other management problem | Completed |  | • Fire proofing thickness scans for PTE-E show underthickness (Required thickness is 100mm for combined layer and 50mm with the old method ) between CH 0 - CH 110. There are in total 24 points of underthickness that can be seen in Att.01 PTE-W 1 ch 4.5 crown - Thickness 80mm - Size 1.0m x 1.0m PTE-W 2 ch 15 above wing wall north side - Thickness 40mm - Size 0.2m x 0.1m PTE-W 3 ch 13.5 crown - Thickness 35mm - Size 0.2m x 0.2m PTE-W 4 ch 13.5 crown - Thickness 45mm PTE-W 5 ch 13.5 crown - Thickness 35mm - Size 0.2m x 0.9m PTE-W 6 ch 13.5 crown - Thickness 35mm - Size 0.3m x 1.3m PTE-W 7 ch 16 above wing wall south side PTE-W 8 ch 23 above wing wall south side - Thickness 40mm - Size 0.2m x 0.1m PTE-W 9 and 10 at ch 36 and 39.5 above wing walls north side are for the hollow repairs ( this is recorded in a separate NCR, Cxxx-NCR-001206 ) PTE-W 11 ch 46.5 above wing wall south side - Thickness 40mm - Size 0.2m x 0.1m PTE-W 12 ch 52 above wing wall south side - Thickness 45mm PTE-W 13 ch 71.5 above wing wall south side - Thickness 45mm PTE-W 14 ch 91 and 93 above wing wall north side PTE-W 15 ch 103 above wing wall north side PTE-W 16 ch 100 crown - Thickness 45mm PTE-W 17 ch 100 crown - Thickness 45mm PTE-W 18 ch 100 crown - Thickness 45mm PTE-W 19 ch 96.5 crown - Thickness 45mm PTE-W 20 ch 96.5 above wing wall south side - Thickness 45mm PTE-W 21 ch 93 above wing wall south side PTE-W 22 ch 102 above wing wall south side - Thickness 45mm PTE-W 23 ch 104 above wing wall south side PTE-W 24 ch 100 crown - Thickness 45mm - Size 0.9m x 0.9m Please note that Att.02 is similar to Att.01 page 1, thus can be disregarded and Att.03 is also similar to Att.01.
| 02SL - Stations (LUL) | Cxxx-NCR-001195 | NCR | W - Bypass: Thickening spray starting without any engineer supervision |  | Contr | __M |  |  | 2016-02-26 | 2016-02-04 10:53 | -22 | 2015-12-14 14:56 | Tunnelling - Linings - Sprayed Concrete | 2000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | • The Bypass tunnel primary lining is being thickened with reinforced SCL to allow an adit to be mined out from the side connecting the new access shafts. • The thickening is sprayed in stages and the second stage was set out using profile bears as a guide for the nozzlemen. • The spray commenced without an engineer or Beamer present to control the thickness of the spray and it was subsequently oversprayed.
| 02SL - Stations (LUL) | Cxxx-NCR-001196 | NCR | W - PTW-E: __ drilled through by another contractor - Ch 70-74 |  | Contr | __M |  |  | 2016-04-15 | 2016-02-04 16:06 | -71 | 2015-12-16 15:32 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Planning | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | • __ 345 Masterseal waterproofing was applied to the crown of PTW-E and covered up to Ch70 with Secondary Lining. • This tunnel was handed over to another contractor who drilled through the lining at the transition zone at the end of the secondary lining despite the fact the area was marked with "Not Drill". Refer to Att.01 • The SCL lining wasn’t thick enough to do an injection repair (R22) and removal of the SCL to expose the drill holes was unsuccessful causing further damage to the Masterseal. • Unsuccessful repair areas have been found in the RHS ( 3 o'clock), LHS ( 9 o'clock ) and in the crown of PTW-E ch 70. • Refer to Att.01 for photos of the defect
| 02SL - Stations (LUL) | Cxxx-NCR-001197 | NCR | W - BYP: Thickening overspray |  | Contr | __M |  |  | 2016-10-14 | 2016-07-07 12:55 | -99 | 2016-01-14 08:53 | Tunnelling - Linings - Sprayed Concrete | 2500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not trained for the work being performed | Completed |  | • On 09/01/16 Section of the Bypass tunnel in Whitechapel was being thickened to enable breakout of a new access adit. • 1st layer of thickening was being applied to the crown of the tunnel and has been found to be sprayed over thickness and out of tolerance. • Approximate size of area 3m x 4m. Ch37-40. • Right shoulder at 1 o’clock. • Sprayed 100mm tight. (No beamer records available as it was 1st layer thickening)
| 02SL - Stations (LUL) | Cxxx-NCR-001198 | NCR | L - NLL: Non-conforming bolts used to control grout ingress. |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-06-20 | 2016-06-22 08:11 | 2 | 2015-12-18 09:48 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | On 24/11/15: To alleviate grout ingress into the LUL Northern Line one of the mitigation measures included in PMI-00996 was to insert a bolt at locations where no bolt was present. In accordance with this PMI and LUL Standard S1055 the bolts inserted should have been marked grade 4.6. During the works, at locations where no bolt was in place, a grade 4.8 bolts was inserted.
| 02SL - Stations (LUL) | Cxxx-NCR-001199 | NCR | W - Drying shrinkage failures of P2 Mix on September |  | Contr | __M |  |  | 2016-04-29 | 2016-04-06 15:58 | -23 | 2016-01-07 08:49 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | 28 days samples CR2373, taken at WHI site on 03.09.15 failed to comply with specification limit 0.03% in failure of 0.04%. CR2373 testing sample worksheet can be found in Att.01
| 02SL - Stations (LUL) | Cxxx-NCR-001200 | NCR | L - Drying shrinkage failures of P1 Mix on September - CR2343 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-04-29 | 2016-05-03 08:04 | 4 | 2016-01-07 09:06 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | 28 days samples CR2343, taken at LIV site on 03.08.15 failed to comply with specification limit 0.03% in failure of 0.036%. Testing sample worksheet can be seen in Att.01
| 02SL - Stations (LUL) | Cxxx-NCR-001201 | NCR | L- CP3a Ch 14.7 - Incorrect location of the contraction joint |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-04-16 | 2016-02-12 14:57 | -64 | 2016-01-07 13:47 | Tunnelling - Tunnelling General | 2500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | L- 15/12/2015-DS-Shift 3 -The contraction joint for CP3a connection with PTW has been cut in the wrong place. Refer to Att.01 for photo of the saw cut done at the incorrect location, too far south After investigation the saw cut in CP3a for the contraction joint has been found at chainage 15.719 instead of 14.692. Refer to Att.02 for a drawing with the actual position of the contraction joint compared to the theoretical position (Att.02).
| 02SL - Stations (LUL) | Cxxx-NCR-001202 | NCR | W - PTW-E: Connection detail damaged - Ch 69-71m |  | Contr | __M |  |  | 2016-03-06 | 2016-02-01 18:16 | -34 | 2016-01-06 16:35 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Planning | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • On the 05/01/2015, in PTW-E Ch69-71RHS ( North side ) around 7-9 o'clock sheet membrane has been found damaged. This happen during the removal of secondary lining. • Refer to Att.01 for photo of the damaged connection detail
| 02SL - Stations (LUL) | Cxxx-NCR-001203 | NCR | W - PTW-E Ch100-105: Remedial work to hair line crack in the bulking layer |  | Contr | __M |  |  | 2016-03-12 | 2016-01-26 12:35 | -46 | 2016-01-12 16:41 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | • PTW-E the Primary Lining was constructed over profile to prevent the Cxxx TBM clashing with the tunnel lining during transit. • This additional thickness of Secondary Lining introduced a bulking layer to keep overall layer thickness to less than 200mm in line with good spraying practice. • Mid December a crack greater than 0.3mm was observed in the bulking layer during an inspection prior to spraying the Secondary Lining 1st Layer. • Crack is between ch100 and 105 from 4 to 9 o'clock • Refer to Att.01 for photos of the crack done on the 05/01/2016
| 02SL - Stations (LUL) | Cxxx-NCR-001204 | NCR | L- PTE-W - Block 20 - Hollow spot in crown |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-04-17 | 2016-02-12 14:45 | -65 | 2016-01-08 13:29 | Tunnelling - Linings - Sprayed Concrete | 2500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | L-06/01/2016 - DS - Shift 3 - During hammer tapping in block 19, the construction team found a hollow spot in the crown within the 2nd layer of SL. Dimension: 1.2m x 2m Depth: 0-270mm Position: Crown Refer to Att.01 for the hammer tapping checksheet.
| 02SL - Stations (LUL) | Cxxx-NCR-001205 | NCR | W - Bypass thickening: 8 BM06 missing in the crown |  | Contr | __M |  |  | 2016-03-01 | 2016-02-29 17:14 | -1 | 2016-01-11 14:47 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | On 08/01/16 before starting the spray of the upper part of the Bypass thickening, required for the Cavern adit breakout, construction team noticed that some BM06 vertical bar around the left part of the eye were missing. After investigation it has been found that 8BM16 bars were missing in the approved drawing Cxxx-__M-C4-DDB-D061-00642 P03.0. Refer to the Att.01 for the photos of the missing bars and Att.02 for the location of the missing bars
| 02SL - Stations (LUL) | Cxxx-NCR-001206 | NCR | L- PTE-E - 2 Hollow Spots found at CH 36.5 and CH 39.5 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-04-30 | 2016-03-11 14:09 | -50 | 2016-01-21 16:30 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | L-11/01/2016- DS - Shift 1 - Whilst hammer tapping in PTE-E , the construction team found 2 hollow spots. Both of the hollow spots are at the 9 O'Clock. Hollow 1 - CH 36.5 - 500mm x 500mm Hollow 2 - CH 39.5 - 700mm x 500mm
| 02SL - Stations (LUL) | Cxxx-NCR-001207 | NCR | L- CP7 - Hollow Spot |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-09-23 | 2016-10-11 15:10 | 18 | 2016-02-04 12:43 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | L- 13/01/2016 - Shift 1 - Whilst hammer tapping in CP7 , the construction team found 2 hollow spots.(Att.01) Hollow 1 - Eastbound (Rough Ch18) - 3m x 1m , Depth: 50mm x 100mm Hollow 2 - Westbound ( Ch18) - 3m x 1m, Depth : 50mm x 100mm
| 02SL - Stations (LUL) | Cxxx-NCR-001208 | NCR | W - Bypass thickening: Incorrect mix used |  | Contr | __M |  |  | 2016-03-14 | 2016-01-26 13:33 | -48 | 2016-01-14 17:32 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | • On 11/01/16 Bypass thickening ( ch37-50) final layer in the crown has been sprayed with P1 mix with Poly Fibres ( P1FP ) instead of P1. • Refer to Att.01 for the Shotcrete Placement Check Sheet • Refer to Att.02 and Att.03 for evidence that incorrect mix has been used
| 02SL - Stations (LUL) | Cxxx-NCR-001209 | NCR | W - PTW-E SL 2nd Layer: Spray done without correct paperwork |  | Contr | __M |  |  | 2016-03-19 | 2016-01-25 18:08 | -54 | 2016-01-19 17:36 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | • On 10/01/16 DS section of tunnel in PTW-E Ch 112 – 115 was sprayed with combined fire proof layer before the Permit was signed by Cxxx representative. • Refer to Att.01 for the RCW Ch112-115 permit to spray signed the 11/01/15
| 02SL - Stations (LUL) | Cxxx-NCR-001210 | NCR | W - PTW-E Ch69 – 72: De-bonding of Masterseal |  | Contr | __M |  |  | 2016-04-15 | 2016-02-01 18:19 | -74 | 2016-01-22 14:47 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • On 13/01/16 the __ Masterseal 345 bond tests in the PTW-E ch 69-72 repair area were found to be less than 0.5 N/mm2. • De-bonding between the first layer and the substrate was observed in some parts.
| 02SL - Stations (LUL) | Cxxx-NCR-001211 | NCR | L- AP5 Incorrect lap lengths On Far-face reinforcement |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-05-14 | 2016-04-29 08:44 | -15 | 2016-02-04 09:40 | Tunnelling - Tunnelling General | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Details: L – 7/01/2016 – Shift 3 – DS – Location: AP5 pour 3 and pour 4. The reinforcement in the far-face of AP5 for pour 3 and pour 4 was installed with incorrect lap lengths (i.e. too short – not in accordance with the sketches provided by Crossrail/Cxxx on 4th December 2016 indicating requirement for longer laps above axis level (Att.01). – email dated 07/01/2016 at 16.18
| 02SL - Stations (LUL) | Cxxx-NCR-001212 | NCR | L-Areas outside of CTRL +100mm profile line in PTW and RCW |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-02-24 | 2017-02-22 09:54 | -2 | 2016-01-20 17:12 | Tunnelling - Tunnelling General | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | L - 20/01/2016 - Shift 3 (DS) - There are several areas (majority under 0.5m2) that have been identified on the scans (Att.01 - Att.24)throughout PTW and RCW that are greater than 100mm from the CTRL (zero) line (these are highlighted in blue), overall about 1% of the whole tunnel lining. The vast majority of these areas are between 10-20mm bigger than the expected 100mm, with the exception of one area that is 30mm bigger than the expected 100mm. The tunnel lining itself is not encroaching the required space-proofing and the thickness of the lining meets the minimum requirement as according to the drawings.
| 02SL - Stations (LUL) | Cxxx-NCR-001213 | NCR | L- RCE Encroachment - CH150 - CH169 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-05-13 | 2016-04-13 14:26 | -30 | 2016-01-20 16:40 | Tunnelling - Linings - Sprayed Concrete | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | L- 20/01/2016 - DS - Shift 2 - There is some encroachment around the transition towards the TBM and throughout RCE in the 2nd layer of the secondary lining which include the fire proofing. This can be seen in Att.01. The encroachment is between CH 150 - 169.
| 02SL - Stations (LUL) | Cxxx-NCR-001214 | NCR | W - Bypass: Hollow spots in the primary lining |  | Contr | __M |  |  | 2016-04-23 | 2016-03-23 16:37 | -31 | 2016-02-23 17:08 | Tunnelling - Linings - Sprayed Concrete | 6000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • A) On 30/11/15 during hammer tapping three hollow spots have been found in the invert: At Ch 39 - Size 0.7m x 0.3m - 5'oclock At Ch 47 - Size 3.0m x 0.2m - From 7 to 5'oclock At Ch 49 - Size 0.4m x 0.4m - 5'oclock Refer to Att.01 for the Bypass Ch 38 to 50 Invert hammer tapping checksheet • B) On 19/11/15 during hammer tapping two hollow spots have been found in the invert At Ch42 - From 8 to 9'oclock At Ch42 - From 3 to 4'oclock Refer to Att.02 for the Bypass Ch 35 to 45 Invert hammer tapping checksheet • C) On 20/11/15 during hammer tapping seven hollow spots have been found in the crown: At Ch 49.5 - Size 1.4m x 0.4m - 10'oclock At Ch 49.5 - Size 1.6m x 0.5m - 2'oclock At Ch 49.5 - Size 0.2m x 0.2m - 2'oclock At Ch 49.5 - Size 0.5m x 0.3m - 3'oclock At Ch 48 - Size 0.6m x 0.2m - 12'oclock At Ch 48 - Size 1.3m x 0.2m - 2'oclock At Ch 47 - Size 0.3m x 0.3m - 2'oclock Refer to Att.03 for the Bypass Ch 35 to 50 Crown hammer tapping checksheet • D) On 10/12/15 during hammer tapping one hollow spot has been found in the invert: At Ch 37 - Size 0.5m x 0.7m - 4'oclock Refer to Att.04 for the Bypass Ch 37 to 42 invert hammer tapping checksheet
| 02SL - Stations (LUL) | Cxxx-NCR-001215 | NCR | L- VD2 - Bleed pipes protruding through lining |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-05-13 | 2016-02-12 14:54 | -91 | 2016-02-03 14:57 | Tunnelling - Linings - Sprayed Concrete | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | L- 22/01/2016 - Shift 2/3 - Whilst conducting a walk through the VD2 tunnel , it had been noted that the bleed pipes in the crown should have been injected (Att.01). According to the secondary lining method statement, all bleeding pipes should be injected prior to spraying second combined Secondary Lining. the secondary first layer has been sprayed. This has now been in the case in this area.
| 02SL - Stations (LUL) | Cxxx-NCR-001216 | NCR | L - CP10 and CP10/PTE junction - Secondary Lining Underthickness + Encroachment of final profile |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-03-31 | 2017-04-06 12:23 | 6 | 2016-02-15 17:05 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Part 1 L- 09/02/2016 - DS - Shift 2- Whilst reviewing the scan , it can been see that there is underthickness in this area. (Att.01). 3 areas have been identified, worse case is 174mm instead of 300mm in the CP10 eye right shoulder approximately 3.0m x 1.0m Quick history: After the issues in the junction of PTW , the secondary lining of CP10 junction was scanned. The scan revealed under thickness in the secondary lining (was excluding fire proofing layer). Part 2 After following the remedial works for part 1 was completed, encroachment was noticed on the final layer of fire proofing. Encroachment on the eastside between 8- 9 O'Clock of upto 30mm, see Att.12 Some areas in the CP10/PTE junction crown have been also found encroaching the CTRL zero line, see Att.08 Part 3 During certification package review, one area of underthickness in CP10 ch9 shoulder near CP10/PTE junction has been noted. Part 4 Following tights spots in CP10 tunnel have been found while reviewing the Att.14 profile scan: - One tight spot encroaching by max 10m has been found in the ch 7 crown - Three termination boxes on both sides have been found encroaching the CTRL profile - And multiple other areas in the invert, all below the Cxxx slab level All tights spots describe above are in red in the Att.14 scan. This is confirmed in Att.15 profile scans. Please note that the tights spots in the junction area are already covered in Part 2 above, see Att.08
| 02SL - Stations (LUL) | Cxxx-NCR-001217 | NCR | W - PTW-E Hollow Spot in Secondary Lining |  | Contr | __M |  |  | 2016-05-20 | 2016-02-29 16:22 | -81 | 2016-01-25 16:47 | Tunnelling - Linings - Sprayed Concrete | 8000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • On 22/01/16 DS, during a routine post spray hammer tapping inspection a hollow spot, around 2m2, was located in the secondary lining 1st layer, in the crown of the PTW-E (above VA4) at Ch90. Refer to Att01. • On 07/01/2016 during hammer tapping inspection in the 2nd layer secondary lining a hollow spot has been found in the crown at chainage 15.5. Size: 1.2 x 0.3 at 3o'clock Refer to Att.02 • On 22/01/2016 during hammer tapping inspection in the 2nd layer secondary lining a hollow spot has been found in the crown at chainage 34.5. Size: 0.5 x 0.3 at 3o'clock Refer to Att.04 • On 02/02/2016 during hammer tapping inspection in the 2nd layer secondary lining a hollow spot has been found in the crown at chainage 56. Size: 0.4 x 1.5 at 9o'clock Refer to Att.04 • On 03/02/2016 during hammer tapping inspection in the 2nd layer secondary lining a hollow spot has been found in the crown at chainage 94.5. Size: 0.5 x 0.5 at 3o'clock Refer to Att.05
| 02SL - Stations (LUL) | Cxxx-NCR-001218 | NCR | L - PTE and RCE: Encroachment from Fire proofing profile |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-03-17 | 2017-03-15 09:36 | -2 | 2016-03-09 11:46 | Tunnelling - Linings - Sprayed Concrete | 10000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | L- 14/03/2016- After spraying the fire proofing layer in PTE and RCE the profile scans have been issued and checked. As shown in Att.01 finished lining has encroached in some areas on the CRTL final profile. Please find all repair works between Att.01 - Att.06 . Please views scans for the extent of encroaching areas and the number of encroachments.
| 02SL - Stations (LUL) | Cxxx-NCR-001219 | NCR | W - December 15: Low Residual Flexural strength of Mix P1 45kg - Beam Testing CR2521 |  | Contr | __M |  |  | 2016-04-01 | 2016-03-10 12:25 | -22 | 2016-02-01 10:48 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | • WHI December sprayed beam CR2521D has achieved a D3 result of S0.91 at 28 days (lower than specified individual result S1.26). Average result for whole set S1.7 comply with spec limit - S1.4 • Refer to Att.01 for the CR2521 Beam Set Results
| 02SL - Stations (LUL) | Cxxx-NCR-001220 | NCR | W - VA5: Masterseal debonding |  | Contr | __M |  |  | 2016-05-31 | 2016-05-06 10:24 | -25 | 2016-02-04 11:05 | Tunnelling - Linings - Sprayed Concrete | 10000 |  | Workmanship | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • On the 30/01/15 DS __ 2nd layer was sprayed. • During night shift the sprayed 2nd layer has been considered to dry. • After discussion with on shift CRL Inspector/Cxxx/__ QA, it has been agreed that the 2nd layer should be removed. • Layer has been jet washed but unfortunately due to layer one still wet, whole application has started debonding. • Refer to Att.01 to Att.03 for photos of __ layer one and two.
| 02SL - Stations (LUL) | Cxxx-NCR-001221 | NCR | L- L- Loose shotcrete behind rebar at LCE - CH 164 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-08-26 | 2016-08-09 14:02 | -17 | 2016-03-17 12:20 | Tunnelling - Tunnelling General | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Inadequate/insufficient tooling. | Completed |  | L- 28/01/2016 - Shift 3 - L- 28/01/2016 - Shift 3 - The loose shotcrete was found in the secondary layer of the secondary lining at approx. Ch 164. The second layer of the secondary lining was sprayed at Ch 164 on 18/03/2015 (before the TBM transit through LCE) (see. Att.10). The loose shotcrete was found just above the wing-wall and documented by Shift 3 on 28/01/2016 (see Att.06) after the TBM transit.
| 02SL - Stations (LUL) | Cxxx-NCR-001222 | NCR | W - CP3/PTW: Tight areas in the junction |  | Contr | __M |  |  | 2016-07-29 | 2016-07-07 07:47 | -22 | 2016-02-04 09:38 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | • After completion of the fireproofing layer in CP3/PTW junction, scan have shown that some areas in the right knee ( 3 to 4 o'clock ) of CP3 tunnel from PTW-E were tight. • Refer to Att.01 for the CP3/PTW Fireproofing profile
| 02SL - Stations (LUL) | Cxxx-NCR-001223 | NCR | W - ES1 PL: Missing tests / documentation |  | Contr | __M |  |  | 2016-06-30 | 2016-06-16 13:31 | -14 | 2016-02-19 13:22 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not trained for the work being performed | Completed |  | • Pilot (Uphill) o Early Strength Testing: - Advance 3 – Missing test - Advance 4 – Missing at 6 and 12 hrs (Att.09) - Advance 9 – Missing at 3, 6 and 12 hrs (Att.09) - Advance 10 – Missing at 3, 6 and 12 hrs (Att.09) - Advance 11 – Missing at 12 hrs (Att.09) - Advance 12 – Missing at 3 hrs (Att.09) - Advance 15 – Low at 1 hr (Att.09) - Advance 17 – Missing at 12 hrs (Att.09) o Rebound Testing - a rebound test was not performed during the time period in which ES1 pilot was constructed • Enlargement (Downhill) o Early Strength Testing: - Advance 2&3 – Low at 1 hr (Att.01) - Advance 4 RHS – Missing at 1 hr and 3 hrs (Att.02) - Advance 5 – Low at 1 hr, missing at 3 hrs (Att.03) - Advance 6 – Low at 1 hr (Att.04) - Advance 8 – Missing at 1 hr and 3hrs (Att.05) - Advance 11 – Missing test - Advance 15 – Missing at 3, 6 and 12 hrs. (Att.06) - Advance 16 – Low at 3 hrs (Att.07) - Advance 20 – Missing Test - Advance 27 – Low at 1 hr (Att.08) o Rebound Testing – a rebound test of regulating layer was not performed during the time period in which ES1 primary was constructed.
| 02SL - Stations (LUL) | Cxxx-NCR-001224 | NCR | L- Encroachment of at AP5 transition |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-07-08 | 2016-03-11 14:32 | -119 | 2016-02-10 10:27 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | L- 27/01/2016 - Shift 3 - There is some encroachment around the transition of AP5. It is in the 9 O'Clock position, see in Att.01.The lip is approx. 50 to 60mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001225 | NCR | L- CP1 - Tunnel Junction Encroachment |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-02-24 | 2017-02-16 11:55 | -8 | 2016-02-06 21:27 | Tunnelling - Tunnelling General | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | L- 22/01/2016 - DS - Shift 3 - • After completion and handover of the fireproofing layer in PTW , scans from the following contractor has shown that areas were tight in the junction to the cross passages. In CP1 two 2 areas have been found encroaching the CTRL zero line: Westside:-132mm @ 8-10 O'clock Eastside: - 62mm @ 2-3 O'clock • Areas affected by the encroachment can be seen in Att.03 and worse case encroachment in Att.06
| 02SL - Stations (LUL) | Cxxx-NCR-001226 | NCR | L- CP3 - Tunnel Junction Encroachment |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-02-24 | 2017-01-19 10:17 | -36 | 2016-02-06 21:40 | Tunnelling - Linings - Sprayed Concrete | 4000 |  | Design | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | L- 22/01/2016 - DS - Shift 3 - • After completion and handover of the fireproofing layer in PTW , scans from the following contractor have shown that areas were tight in the junction to the cross passages. In CP3 two 2 areas have been found encroaching the CTRL zero line: Westside:-132mm @ 8-10 O'clock Eastside: - 50mm @ 2-3 O'clock • Refer to Att.01 for the 3d scans with the areas affected by the encroachment and Att.03 for how much
| 02SL - Stations (LUL) | Cxxx-NCR-001227 | NCR | L- CP3a - Tunnel Junction |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-10-28 | 2016-11-24 11:29 | 27 | 2016-02-06 21:46 | Tunnelling - Linings - Sprayed Concrete | 20000 |  | Design | Repair | 2 (6-60k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | L- 22/01/2016 - DS - Shift 3 - • After completion and handover of the fireproofing layer in PTW , scans from the follow on contractor have shown areas that were tight in the junction to the cross passages. • Specifically in CP3a - 2 areas of encroachment westside:-123mm @ 8 O'clock Eastside:- 140mm @ 3 O'clock Att.01 - Core
| 02SL - Stations (LUL) | Cxxx-NCR-001228 | NCR | L- CP5 - Tunnel Junction Encroachment and Out of profile |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-09-30 | 2016-08-09 14:39 | -52 | 2016-02-08 13:53 | Tunnelling - Linings - Sprayed Concrete | 4000 |  | Design | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | L- 22/01/2016 - DS - Shift 3 - After completion and handover of the fireproofing layer in PTW , scans from the follow on contractor have shown areas that were tight in the junction to the cross passages. Specifically in CP5 - 3 areas of encroachment - 1 on the westside and 2 on the eastside. Westside:- 48mm @ 7 O'clock Eastside: - 48mm + 36mm @ 4 O'clock & 5 O'clock Att.01 - Encroachments can be seen in Att.01. Please note that there is also a few areas out of profile (blue areas in Att.01).
| 02SL - Stations (LUL) | Cxxx-NCR-001229 | NCR | L- CP 7 - Tunnel Junction encroachment, out of profile and underthickness |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-09-30 | 2016-09-23 09:47 | -7 | 2016-02-06 22:06 | Tunnelling - Linings - Sprayed Concrete | 4000 |  | Design | Repair | 3 (3-6k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | L- 22/01/2016 - DS - Shift 3 - After completion and handover of the fireproofing layer in PTW , scans from the follow on contractor have shown areas that were tight in the junction to the cross passages. There are 2 areas of encroachment and a few areas of out of profile (blue areas) Westside:-12mm @ 8 O'clock Eastside: - 25mm @ 4 O'clock Two areas of fire proofing underthickness can be seen in scan Att.14. There are located in the CP7/PTW-E junction crown. The encroachments can be seen in Att.01.
| 02SL - Stations (LUL) | Cxxx-NCR-001230 | NCR | L- CP9 - Tunnel Junctions Encroachment + Out of profile |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-12-31 | 2017-03-02 14:14 | 61 | 2016-02-06 22:11 | Tunnelling - Linings - Sprayed Concrete | 2500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | L- 22/01/2016 - DS - Shift 3 - There are a few issues captured in this NCR. --Profile-- After completion and handover of the fireproofing layer in CP9/PTW , scans from the follow on contractor have shown areas that were tight in the junction to the cross passages. Specifically in CP9 - 1 area of encroachment in the westside: Encroachment of 54mm @ 9 O'clock Refer to Att.01 and Att.03 for the 3d scans --Under thickness of fireproofing-- After trimming a thickness scan of the fireproofing was taken and has highlighted 3 areas of underthickness (1 caused by the trimming works), which can be seen in Att.04, which details also the remedial works for each of the 3 repairs. Underthickness 1: Left hand shoulder - worst case 44mm Underthickness 2: Left hand side at axis - varying thickness, down to 0mm Underthickness 3: Bottom right hand side - worst case 18mm --Under thickness of total secondary lining-- A total thickness scan was taken (Att.10) which also shows an underthickness of the total underthickness of secondary lining. Minimum thickness is 236mm (14m under the required thickness) over an area of 0.05m2.
| 02SL - Stations (LUL) | Cxxx-NCR-001231 | NCR | L- CP4a - Tunnel Junction Encroachment and Out of Profile |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-12-31 | 2017-03-02 14:16 | 61 | 2016-02-08 13:58 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | L- 22/01/2016 - DS - Shift 3 - After completion and handover of the fireproofing layer in PTW , scans from the follow on contractor have shown areas that were tight in the junction to the cross passages. This highlighted that there could be potential problems in PTE. Specifically in CP4a - 1 areas of encroachment on the westside. There are also 2 areas of out of profile (1 on the eastside shoulder and 1 on the westside shoulder) On the westside the encroachment is -51mm at about 4 O'clock. See in Att.01 for the Core location and Att.06 for the scan before trimming
| 02SL - Stations (LUL) | Cxxx-NCR-001232 | NCR | L - VD4 - Incorrect rebar installation in invert |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-02-10 | 2017-01-19 16:11 | -22 | 2016-05-12 10:18 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | L - 11/05/2016 - Shift 3 - DS - Number of rebar used in hoop direction not as per design at Invert blocks 1,2,4,5,6,7. According to the drawing; Cxxx-MMD-C4-DDB-C101_6-00201, B785 mesh is to be installed in the invert with the steel positioned in tunnel as ø10//100mm(radial) and ø8//200mm(longitudinal). However the steel has been installed; - B10bars have been used in longitudinal direction @100mm rather than B08 bar @200 - B10 bars used in hoop direction @200mm spacing rather than @100mm See Att.02 for pictures of reinforcement installed incorrectly and Cxxx recommendations
| 02SL - Stations (LUL) | Cxxx-NCR-001233 | NCR | L- Moorgate station – Reinstated duct follows a tortuous path which preventing cable installation |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-09-30 | 2016-10-06 08:38 | 6 | 2016-02-06 23:39 | Tunnelling - Tunnelling General | 1000 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | L- 04/02/2016 - The required cable cannot be installed in the Southern duct, as its path is too tortuous for the cable to follow. Two ducts were uncovered, which were to be reinstated and cast into the new pit structure. The ducts were installed along the least tortuous path possible without compromising the new structure. The more Northerly duct conforms; it accepts the required cable with no issues. The more Southerly duct will not accept the required 38mm cable.
| 02SL - Stations (LUL) | Cxxx-NCR-001234 | NCR | W - PTWE and RCW: Minor areas outside of CTRL +100mm profile line |  | Contr | __M |  |  | 2016-07-01 | 2016-03-24 15:27 | -99 | 2016-02-09 14:35 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | On 05/02/2016, after the initial scan review with Cxxx - there are 2 areas (from Ch68.5 to 73.5 and around Ch107) identified on the scans throughout PTW-E and RCW (see Att.01&2), greater than 100mm from the CTRL (zero) line. The areas are highlighted in blue on scans. These areas are between 10-20mm bigger than the expected 100mm. The tunnel lining itself is not encroaching the required space-proofing and the thickness of the lining meets the minimum requirement as according to the drawings.
| 02SL - Stations (LUL) | Cxxx-NCR-001235 | NCR | W - Compensation Grouting Completion Works: cubes not taken and tests missed |  | Contr | __M |  |  | 2016-03-18 | 2016-02-25 16:24 | -22 | 2016-02-09 10:10 | Materials - General | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | • On August 2015 a total of 384m3 of concrete was poured into the grout shaft. This equates to 7 sets of cubes created for strength testing. Only 3 sets were produced and crushed ( see att01. ) • Crush testing parameters – cubes were to be crushed at the interval of 1 x 7-day, 2 x 28-day and 1 x 56-day. The 56-day strength was not tested ( see att01. ) • Sampling frequencies: several Slump Tests and Temperature Tests missed (see att02.) • Batch volumes omitted on Concrete Pour checksheet (see att02.)
| 02SL - Stations (LUL) | Cxxx-NCR-001236 | NCR | W - VA4 Connection: Reinforcement starter bars bent over |  | Contr | __M |  |  | 2016-10-28 | 2016-05-05 09:58 | -176 | 2016-02-11 18:20 | Tunnelling - Linings - In-situ Concrete | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | • The back of the diaphragm wall at VA4 CHS connection required waterproof membrane to be applied. • On 10/02/16 invert starter bars were in the way of the spray and the site team bent these down out of the way of the spray.
| 02SL - Stations (LUL) | Cxxx-NCR-001237 | NCR | L- CP4 - Tunnel Junctions Encroachment + Out of profile |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-10-28 | 2016-12-23 10:27 | 56 | 2016-02-11 12:54 | Tunnelling - Linings - Sprayed Concrete | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | L-22/01/2016 - DS - Shift 3 - • After completion and handover of the fireproofing layer in PTW , scans from the follow on contractor have shown areas that were tight in the junction to the cross passages. This highlighted that there could be potential problems in PTE. Specifically in CP4 - 1 areas of encroachment on the eastside was noted in the second layer of secondary lining and as can be seen in Att 6.2 there are 2 areas out of profile. (1 on the westside - shoulder. 1 on the eastside - knee below platform level) Throughout the works CP4 junction has undergone several repairs on the East side of the junction and the history of these repairs and outcomes are detailed below: - Secondary lining around junction appeared to be tight over 100mm tight (see att.1) and hence __ decided to trim the secondary lining back to allow space for the fireproofing (+90 from CRTL zero line) - During trimming works it was revealed that the reinforcement in the junction was also tight (see att.2.1 and att.2.2) - The reinforcement was trimmed out and removed and then replaced back in to position - On top of moving the bars additional stainless steel profile bars were added for anchorage either side of the repair (see att.3.1 and att.3.2). This was now in a smaller grid size of 500x500mm - The repair was then sprayed in with P2 and polypropylene fibres mix - This was then reveal that the area was tight up to 57mm (see att.4.1 and att.4.2) and hence __ trimmed back - Trimming then revealed the stainless steel profile bars - A new remedial measure was agreed. This was to flash over the remedial bars with Reader spraycrete 50AAA and then apply on top a proprietary product (ronabond 150) that offered additional corrosion resistance - The Reader Spraycrete was then sprayed tight in places up to 15mm (see att.5.1) - CRL then told __ to not trim, __ however trimmed this area to bring the area back to profile, however they also revealed the stainless steel bars (see att. 6.1 – att.6.2) - The expose bars were patched with Nanocrete R4
| 02SL - Stations (LUL) | Cxxx-NCR-001238 | NCR | W - EPW1 Ch 6: Hollow spot in primary lining |  | Contr | __M |  |  | 2016-04-29 | 2016-03-23 16:40 | -37 | 2016-02-12 10:38 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On 20/10/15 during hammer tapping one hollow spot has been found in the crown at Ch 6 - Size 0.5m x 2.8m from 1 to 2'oclock Refer to Att.01 for the EPW1 Primary Lining hammer tapping checksheet
| 02SL - Stations (LUL) | Cxxx-NCR-001239 | NCR | L - PTE: Hollow spots in fire proofing layer Ch 10.5 and |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-10-14 | 2016-08-18 12:21 | -57 | 2016-03-09 14:57 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • On 11/02/16 NS, during hammer tapping inspection a hollow spot, size 1m x 1.5m was located in the fire proofing layer crown PTE Ch10.5 at 12 o'clock . Refer to Att01. for the hammer tapping check sheets On 18/02/2016 NS, During hammer tapping inspection a hollow spot, size,100mm x 300mm was located in the fire proofing layer in CP4a crown Ch42. Att.02 • On 11/02/16 NS, during hammer tapping inspection a hollow spot, size 0.4m x 1m was located in the fire proofing layer crown PTEE Ch111.5. The are was inspected by Cxxx and __ and when retapped there was no sound of a hollow so it was not considered as a hollow spot as per Att.04
| 02SL - Stations (LUL) | Cxxx-NCR-001240 | NCR | L - PTE Ch22: Hollow spots in Fire proofing layer ( Full Arch Repair ) |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-03-20 | 2017-03-31 11:09 | 11 | 2016-03-21 14:43 | Tunnelling - Linings - Sprayed Concrete | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • On 11/02/16 NS, during hammer tapping inspection a hollow spot, size 1m x 1m was located in the fire proofing layer crown in PTE-W Ch22 above the axis. Refer to Att.01 for the coordinates of the hollow spot
| 02SL - Stations (LUL) | Cxxx-NCR-001241 | NCR | L- RCE - Ch110 - Ch126 - No thickness data for the final layer |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-01-07 | 2016-11-23 14:45 | -45 | 2016-02-16 12:46 | Tunnelling - Tunnelling General | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | L- 15/02/2016 - Shift 3 - For PTE-E between ch. 110 – 126, there is no scan for the 1st layer of secondary lining and therefore unable to determine the thickness of the 2nd layer of the secondary lining (which is the new combined mix and includes polypropylene fibres and therefore requires a minimum thickness of 100mm).
| 02SL - Stations (LUL) | Cxxx-NCR-001242 | NCR | W - PTE-E/CP3: Underthickness in SL 2nd layer - CH55 |  | Contr | __M |  |  | 2016-09-02 | 2016-05-13 15:03 | -112 | 2016-02-25 14:00 | Tunnelling - Linings - Sprayed Concrete | 2000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | • On 13/02/16 PTE-E thickness scans have been issued and a localised area, approx. 0.5m x 1m, of secondary lining around the eye of CP3 was less than the required 250mm thickness as outlined in the scans attached. The thinnest spot is 220mm at the centre of the area and the rest is 230 – 240mm. • Upon review of the scans it was found that the area of under thickness was all a result of the secondary lining not being sprayed to profile. • A review of the profile scan was also done and the distance away from Crossrail Tolerance Zero was noted. This shows that there is room to make up the additional missed secondary lining thickness plus the fireproofing layer without exceeding the CRTL ZERO line.
| 02SL - Stations (LUL) | Cxxx-NCR-001243 | NCR | L-PTW-Encroachment On profile |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-08-02 | 2017-08-18 14:47 | 16 | 2016-04-19 13:59 | Tunnelling - Linings - Sprayed Concrete | 6000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | L- 08/01/2015 - Shift 2 - After spraying the fire proofing layer in PTW, the profile scans have been issued and checked. As shown in Att.01 - Att.06 and Att.13 - Att.17 finished lining has encroached in some areas on the CRTL final profile. Please find all repair works between Att.07- Att.12 and - Att.18 - Att.21 .
| 02SL - Stations (LUL) | Cxxx-NCR-001244 | NCR | L- PTEW- Ch63- Underthickness in the total thickness of secondary Lining |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-06-17 | 2016-05-31 14:11 | -17 | 2016-03-09 15:42 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | L-16/02/2016 - DS - Shift 3 - Whilst reviewing the thickness scans , it has been noted that there is underthickness in the secondary lining total thickness. The thickness of the lining drops down to 280mm (Meant to be 300mm thick) in an area of about 1m2 at Ch 63. The location of the underthickness is in the crown.
| 02SL - Stations (LUL) | Cxxx-NCR-001245 | NCR | L- PTE-W- CP2 - Tight areas in Junction |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-08-06 | 2016-10-13 09:07 | 68 | 2016-06-07 14:25 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | L-22/01/2016 - DS - Shift 3 After completion and handover of the fireproofing layer in PTE , scans from the follow on contractor have shown areas that were tight in the junction to the cross passages. • Specifically in CP2 - 1 areas of encroachment Eastside: - 20mm - 30mm @ 1-2 O'clock
| 02SL - Stations (LUL) | Cxxx-NCR-001246 | NCR | L- PTE-W Hollow Spot - CH42 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-05-15 | 2017-05-25 17:38 | 10 | 2016-03-24 12:57 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | L-17/02/2016 - DS - Shift 3 - During the hammer tapping of this section , it has been noticed that there was two hollow spots in PTE-W ch 43.5 and Ch 41. The hollow spots are located in the crown (12 O'Clock) size 300mm x 100mm and on the Southside at 9 o'clock. Att.01 - The hammer tapping check sheet shows where the hollow spots were originally found
| 02SL - Stations (LUL) | Cxxx-NCR-001248 | NCR | L - PTW and PTE: Termination boxes with zinc spraying not approved |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-12-27 | 2016-11-18 13:14 | -39 | 2016-07-29 08:09 | Tunnelling - Tunnelling General | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | • On the 03/05/16 Following the PMI 1131 __ have instructed IAT to install the Termination Boxes for Cxxx in the platform Tunnels. • For the installing of the “Termination Boxes” on top of the surface IAT has drill some holes for fixing and leading the pipes through. After drilling this holes IAT has used a zinc spray for repairing the affected area. • The details of the works should have been approved through a MCR before being used on site
| 02SL - Stations (LUL) | Cxxx-NCR-001249 | NCR | W - EPW1: Hollow spots in Regulating layer |  | Contr | __M |  |  | 2016-04-25 | 2016-04-25 13:45 | 0 | 2016-02-25 08:50 | Tunnelling - Linings - Sprayed Concrete | 4000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • On 13/02/16 during hammer tapping four hollow spots have been found in the regulating layer crown: 1) At Ch 17 - Size <0.5m x 0.5m - 10'oclock 2) At Ch 20 - Size <0.5m x 0.5m - 11'oclock 3) At Ch 20 - Size 1m x 0.8m - 1 to 2'oclock 4) At Ch 22 - Size 0.7m x 0.5m - 5'oclock Refer to Att.01 for the EPW1 Ch 4 to 25 RL Hammer tapping checksheet
| 02SL - Stations (LUL) | Cxxx-NCR-001250 | NCR | W - WBCAV: Hollow spots in primary lining |  | Contr | __M |  |  | 2016-08-19 | 2016-05-05 15:34 | -106 | 2016-02-25 10:57 | Tunnelling - Linings - Sprayed Concrete | 8000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • On 04/02/16 during hammer tapping 13 hollow spots have been found in the invert. Refer to Att.01 for the WBCAV Ch 215-235 Invert hammer tapping checksheet for the exact location
| 02SL - Stations (LUL) | Cxxx-NCR-001251 | NCR | W - WBEC: Hollow spots in regulating layer |  | Contr | __M |  |  | 2016-08-26 | 2016-09-14 11:36 | 19 | 2016-05-17 13:46 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • On 28/01/16 DS, during the hammer tapping of WBEC regulating layer ch 226 to headwall ( Ch 256 ), four hollow spots have been found. • Size Max 2000 x 1000 at 12'o clock, ch 230 • Refer to Att.01 for the hammer tapping before repairs
| 02SL - Stations (LUL) | Cxxx-NCR-001252 | NCR | W - Bypass/Adits: Exposed rebars during breakout of the adits |  | Contr | __M |  |  | 2016-06-24 | 2016-05-05 15:51 | -50 | 2016-02-26 16:24 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | • On 17/01/16 NS during breakout of the adits from bypass tunnel reinforcement has been exposed in the crown ( BYP Chainage 45 at 12'oclock ) • Refer to Att.01 for photo of the exposed reinforcement
| 02SL - Stations (LUL) | Cxxx-NCR-001253 | NCR | W - CP3/PTE: Over spraying of Masterseal with Secondary lining |  | Contr | __M |  |  | 2016-10-07 | 2016-07-07 12:53 | -92 | 2016-02-29 17:17 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | • CP3 North eye was formed before the transit of the Cxxx TBM through the station. At that time, works were not completed in cleaning, forming and protecting an appropriate joint connection for the remaining secondary lining in CP3. • After gaining access post Cxxx TBM handover to Cxxx, work has commenced on completing the secondary lining in the CP3 North area. • On 17/01/16 as the concrete being in place for so long, it was not possible to form an acceptable joint and remove overspray without damaging the __ waterproofing in the RHS and LHS. • Refer to Att.01 for photos of the damage Masterseal in CP3 north
| 02SL - Stations (LUL) | Cxxx-NCR-001254 | NCR | W - PTE-W Ch 155: Over spraying of Masterseal with Secondary lining |  | Contr | __M |  |  | 2016-10-21 | 2017-01-27 15:05 | 98 | 2016-03-01 17:29 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | • Secondary lining up to PTE-W Ch155 was formed before the transit of the Cxxx TBM through the station. At that time, works were not completed in cleaning, forming and protecting an appropriate joint connection for the remaining secondary lining in CP3. • On mid-February, after gaining access post Cxxx TBM handover to Cxxx and resuming the secondary lining works in PTE-W, CRL/Cxxx and __ decided to organise a site visit to know the extent of the defects in the secondary lining after the Cxxx TBM transit through the station. • During the site visit the PTE-W ch 155 Masterseal has been found oversprayed with secondary lining. • Refer to Att.01 for photo of the defect
| 02SL - Stations (LUL) | Cxxx-NCR-001255 | NCR | W - PTW-E: Sump installed in incorrect position |  | Contr | __M |  |  | 2016-07-01 | 2016-05-05 10:46 | -57 | 2016-03-02 10:45 | Tunnelling - Linings - In-situ Concrete | 3000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • After handing over PTW-E to following contractor Cxxx, it has been found out on 01/03/2016 that the sump was in the incorrect location. • The four corner co-ordinates of the sump were set out by an engineer and the sump cut out using concrete sawing equipment. • Refer to Att.01 for the As-built survey of incorrect sump
| 02SL - Stations (LUL) | Cxxx-NCR-001256 | NCR | W - CP1A North: Over spraying of Masterseal with Secondary lining |  | Contr | __M |  |  | 2016-11-12 | 2017-01-30 11:33 | 79 | 2016-03-02 14:49 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | • Secondary lining in CP1A North was formed before the transit of the Cxxx TBM through the station. At that time, works were not completed in cleaning, forming and protecting an appropriate joint connection for the remaining secondary lining in CP1A North. • On mid-February, after gaining access post Cxxx TBM handover to Cxxx and resuming the secondary lining works in the area, CRL/Cxxx and __ decided to organise a site visit to know the extent of the defects in the secondary lining after the Cxxx TBM transit through the station. • During the site visit CP1A-North Masterseal was found oversprayed with secondary lining. • Refer to Att.01 for photo of the defect
| 02SL - Stations (LUL) | Cxxx-NCR-001257 | NCR | L - LCE Ch 142: Water Leaks in the SL 1st layer + 2nd layer |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-07-29 | 2016-08-09 13:47 | 11 | 2016-03-07 12:02 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | L- 07/03/16 - DS: 1.The first layer of the secondary lining ( 2nd/1st) has been sprayed in LCE. On 07/03/2016, it has been noticed that there is water ingress around Ch 142 (see damp patch survey in attachment 01+07). The leak is only in 1 location (Att.02) and is about 1m x 1m. It can be located about 3 O'clock in the northside. 2. Packers were installed and injected ( Att.03) 3. Inspection was carried out of 2nd/ 1st and the area was dry 4. The 2nd/2nd of __ was sprayed. 5. Post spray inspection showed that the same area was damp 6. Additional packers were installed and injected (Att.05) 7. Post inspection shows that the area is now dry.
| 02SL - Stations (LUL) | Cxxx-NCR-001258 | NCR | L- VD4 - No waterbar on construction joint of invert block |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-06-18 | 2016-05-13 14:11 | -36 | 2016-03-10 12:02 | Tunnelling - Linings - Sprayed Concrete | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | L- 09/03/2016 - DS - Shift 3 - Following a walk through , it had been noticed that there was no water bar on the construction joint of the invert block. As per attachment Att.01. (Elevation A-A ( Completed Connection). There is no waterbar at the construction joint between the invert of VD4 portal and the first pour of the ring
| 02SL - Stations (LUL) | Cxxx-NCR-001259 | NCR | L- VD4 - No radial joint at invert |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-06-18 | 2016-05-09 11:04 | -40 | 2016-03-10 16:35 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | L- 07/03/2016 - DS - Shift 3 - Whilst doing a walk through it had been noticed that a radial joint was not installed at the invert portal as Per Att.01. (Ch 40.677 - Ch 44).
| 02SL - Stations (LUL) | Cxxx-NCR-001260 | NCR | W - WBEC SL: Missing tests / documentation |  | Contr | __M |  |  | 2017-06-22 | 2017-06-21 09:59 | -1 | 2017-03-24 16:11 | Tunnelling - Linings - In-situ Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | • Cxxx-__M-C4-LLG-D061-50202 Deliverable Records for WB CAV regulation layer: Regulation Layer: ITP item 2.1: Missing Permit to Cover Primary Lining (__ form D3-93) for WB Cavern Invert Ch.245 to 255 (blocks 6 & 7)
| 02SL - Stations (LUL) | Cxxx-NCR-001261 | NCR | W - Incorrect invert mix design used |  | Contr | __M |  |  | 2016-08-26 | 2016-05-23 13:44 | -95 | 2016-03-21 10:46 | Tunnelling - Linings - In-situ Concrete | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | • Failures on flexural beams tests results and fibre content fresh test results from Mix Invert due to un updated mix design for mix Invert at WHI batching plant database. • Refer to Att01 for the failed flexural beams tests results and Att.02 and Att.03 for the fibre content fresh results
| 02SL - Stations (LUL) | Cxxx-NCR-001262 | NCR | L- PTE/E - Block 8 - Cold Joint |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-06-25 | 2016-04-29 09:20 | -57 | 2016-03-17 12:21 | Tunnelling - Tunnelling General | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | L- 28/01/2015- A potential cold joint was observed in the second layer of secondary lining (in the mini-shutter above the wingwall) on the north side (LHS) of PTE-E Block 8. This was raised as a potential NCR 'ITEM 348' on 28/01/2015. During the temporary handover to Cxxx for the TBM transit through PTE (from March until October 2015) it was not possible to inspect the area to confirm if this was actually a cold-joint and whether an NCR was needed. During review of the potential NCR it was included into existing NCR 960 covering cold-joints in wingwalls. However the description of the location of this particular cold joint was incorrectly added into NCR 960. The fireproofing layer was sprayed in the area onto the second layer of secondary lining without a Permit to Cover signed by Crossrail or Cxxx. During close out of NCR 960 it became apparent that the cold joint was not in the wingwall as per the other cold joints in that NCR and that it was no longer possible to inspect.
| 02SL - Stations (LUL) | Cxxx-NCR-001263 | NCR | L - ES2: Wrong Mix been sprayed |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-06-04 | 2016-04-29 09:12 | -36 | 2016-04-05 13:18 | Tunnelling - Linings - Sprayed Concrete | 2000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | L- 12/03/2016 - DS - Shift 3 - Sub-carriers were set out and surveyed at the start of the shift. By that time (11 o’clock) right mix of concrete (P1) was already ordered. As the survey result were not satisfactory spray couldn't start and had to be postponed. The sub-carriers were reset and re-surveyed. But the results were far from being satisfactory, results were found satisfactory at the third attempt. By that time (4 o’clock in the morning) right mix was not usable any more. Spraying was on-going in LCE with RL2 mix. Assuming that mix was okay, sub-carriers were sprayed with RL2 mix.
| 02SL - Stations (LUL) | Cxxx-NCR-001264 | NCR | L- CP3a / PTW: Contraction joints through reinforcement |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-11-04 | 2016-11-24 11:34 | 20 | 2016-07-27 10:48 | Tunnelling - Tunnelling General | 2500 |  | Material | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | • L- 11/03/2016 - Shift 1 - In CP3a/ PTW, the contraction joint was cut at first instance at the incorrect location ( Cxxx-NCR-001201 ). Contraction joint done at chainage 15.719 instead of 14.692. Decision to do a new contraction joint at correct chainage ( i.e. 14.692 ) was taken. Unfortunately after inspection it has been found out that both saw cuts have gone through the reinforcement steel in CP3a. • General depths of both contraction joints are between 120mm - 150mm. • Refer to Att.01 for photos of both contraction joints
| 02SL - Stations (LUL) | Cxxx-NCR-001265 | NCR | W - EP2 Connection: Contaminated __ and sheet membrane damaged |  | Contr | __M |  |  | 2016-06-24 | 2016-06-24 10:52 | 0 | 2016-03-21 10:16 | Tunnelling - Linings - Sprayed Concrete | 2723.36 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | On 11/03/2016 DS, EP2 sheet membrane has been found damaged in the invert (6 o'clock) and sprayed __ contaminated with oil in the LHS around 9 o'clock. Refer to Att.01 and Att.02 for photos of the defects
| 02SL - Stations (LUL) | Cxxx-NCR-001266 | NCR | W - CP2 South: Missing contact grouting tubes in the invert |  | Contr | __M |  |  | 2016-07-01 | 2016-05-05 11:14 | -57 | 2016-04-01 09:42 | Tunnelling - Linings - In-situ Concrete | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | • On 17/03/16 DS waterproof membrane in CP2 south was installed without the contact grouting tube. • The invert was cast prior to installation of the tube. • The thin annulus between the cast invert and the sheet membrane caused by shrinkage of the cast concrete could not be contact grouted. • Refer to Att.01 for photo of the CP2 South invert before pouring
| 02SL - Stations (LUL) | Cxxx-NCR-001267 | NCR | L- LCE - Areas Of Underthickness in FP |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-10-30 | 2017-03-03 13:55 | 124 | 2016-03-24 14:02 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | L- 18/03/2016 - Thickness scans (Att.01) for LCE show underthickness in 4 areas. (Required thickness is 50mm from Ch 97 - 13 and 100mm for combined layer Ch13 - 00) in the fire proofing layer. LCE 1 - CH159.5 on trackside just above axis - 1m x 0.5m (Size on Att.01 is incorrect) - Underthickness = 30mm LCE 2 - Ch159.5 on trackside just off centre of the crown - 1m x 0.8m - Underthickness = 30mm LCE 3 - Ch 161 On platform side just above the wing wall - 2m x 1m - Underthickness = 35mm LCE 4 - Ch 175 - Ch 178 on platform side (Between 12 O'clock and 4 O'clock) - Size is various as per Att.01 - Underthickness = 45mm It has been agreed between CRL/Cxxx and __ quality teams to raise multiple under thickness in one area as one NCR (NCR Meeting - 18/11/2015- Attended by __ , __ , __ , __ and __). Photos of the set of underthicknesses will be stated via a photo
| 02SL - Stations (LUL) | Cxxx-NCR-001268 | NCR | W - PTE-E: Encroachment of the FP profile - CH37 to CH60 |  | Contr | __M |  |  | 2016-09-29 | 2016-07-07 12:33 | -84 | 2016-03-24 11:17 | Tunnelling - Linings - Sprayed Concrete | 4000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | On 22/03/16 there are some occurrences where the finished tunnel lining has encroached on the CRTL final profile in PTE-E, between CH37 to 60. The exact location of the tights spots are available in Att01. These various areas have been over-sprayed by max 30mm ( and 1 area by 50mm), meanly in the crown from 10 to 4 o'clock. The thickness of the tights spots are available in Att02.
| 02SL - Stations (LUL) | Cxxx-NCR-001269 | NCR | L - CP6 Encroachment |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-06-30 | 2016-06-22 09:44 | -8 | 2016-03-22 16:08 | Tunnelling - Tunnelling General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | L - 21/03/2016 - DS - Shift 2 - In CP6 there is a small area of encroachment in the wing walls on the right hand side. The encroachment is in a localised area at ch. 14-15 at 5 O’clock and up to 10mm pass the zero line
| 02SL - Stations (LUL) | Cxxx-NCR-001270 | NCR | L - LCE Block 26: Sheet membrane penetrated by core hole |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-09-30 | 2016-08-30 12:14 | -31 | 2016-03-30 15:11 | Tunnelling - Linings - In-situ Concrete | 6000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | Issue 1: On 30/03/16 DS one core hole done in the LCE Block 26 north wingwall has penetrated through the sheet membrane, rendering the sheet membrane damaged and losing the guarantee from IAT. The core hole has a 50mm diameter. Location is in the North wingwall (trackside) at Block 26 on the very east side of the wing wall, just before Block 25 and right next to the joint. Refer to Att.01 for the core hole picture. Issue 2: After __ had carry out the repair works and handed over the area following contractor Cxxx, while working in LCE, has drilled through the repaired area. On the 04/06/16 after the drilling, leaks appeared in the area, as shown in the Att.03 photos
| 02SL - Stations (LUL) | Cxxx-NCR-001271 | NCR | PTE: Incorrect termination box levels |  | Contr | __M |  |  | 2017-08-02 | 2017-06-23 12:09 | -40 | 2016-03-31 16:47 | Tunnelling - Linings - In-situ Concrete | 1500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • In March 2015 after PTE handover to following contractor Cxxx, some termination boxes have been found to clash into Cxxx slab. • Top termination boxes level has been found above the bottom of cast in-situ slab of future works (77.9m) for a number of termination boxes. • Refer to Att.01 and Att.02 for the Cxxxs termination boxes survey which compares the given level from Crossrail of 77.9m. Termination boxes concerned are in PTE-E Ch 87, PTE-E 41.5, PTE-W Ch 22 and PTE-W Ch 31 Refer to Cxxx PTE-E and PTE-W termination box survey.
| 02SL - Stations (LUL) | Cxxx-NCR-001272 | NCR | W - PTW-W: Lining outside CTRL +100mm profile |  | Contr | __M |  |  | 2016-11-04 | 2016-11-09 15:56 | 5 | 2016-04-05 08:19 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other management problem | Completed |  | On 04/04/2016, after the initial scan review with CRL/Cxxx - some areas between Ch28.0 to 91.0 have been identified on the scans throughout PTW-W (see Att.01), greater than 100mm from the CTRL (zero) line. The areas are highlighted in blue on scans. These areas are between 10-20mm bigger than the expected 100mm. The tunnel lining itself is not encroaching the required space-proofing and the thickness of the lining meets the minimum requirement as according to the drawings.
| 02SL - Stations (LUL) | Cxxx-NCR-001273 | NCR | W - PTW-W Ch72 Crown: Hollow spot found in the combined layer |  | Contr | __M |  |  | 2016-09-30 | 2017-01-24 14:18 | 116 | 2016-05-05 07:11 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • On 03/04/16 DS, during the hammer tapping of PTW-W combined layer ch 53.5 to 72 one hollow spot has been found. • Ch 72 Size 1300 x 900 at 12'o clock • Refer to Att.01 for the hammer tapping before injection
| 02SL - Stations (LUL) | Cxxx-NCR-001274 | NCR | L - AP5: Encroachment of at AP5 transition |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-10-30 | 2016-10-27 08:39 | -3 | 2016-04-07 13:54 | Tunnelling - Linings - In-situ Concrete | 3000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • L- 27/01/2016 - Shift 3 - There is some encroachment around the transition of AP5. It is in the 9 O'Clock position and lip is approx. 50 to 60mm. • Refer to Att.01 for the As built survey of the encroachment and Att.02 for some photos.
| 02SL - Stations (LUL) | Cxxx-NCR-001275 | NCR | W - LCW & WCAV: Cxxx drainage pipe out of position |  | Contr | __M |  |  | 2016-05-27 | 2016-05-23 10:29 | -4 | 2016-04-07 16:20 | Tunnelling - Linings - In-situ Concrete | 1000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | • On 05/04/16 DS an as-built of the Cxxx drain pipe in LCW at Whitechapel has been issued and pipe found to be installed as per agreed position i.e 83.552 instead of 83.551 • Unfortunately the level 83.551 was for the bottom of the pipe albeit in the coordinates sent to construction team it was marked centre of the pipe. • Refer to Att.01 for the drain pipes coordinates received by the construction team and Att.02 for Cxxx email approving the drain pipes coordinates • Refer to Att.02 for the pipe position sketch.
| 02SL - Stations (LUL) | Cxxx-NCR-001276 | NCR | No single seam checks had been recorded as being completed as required on check sheet D3-94 for Eastbound Cavern Block 5 water bars. |  | Crossrail | XRL |  |  | 2016-06-06 | 2016-06-07 12:33 | 1 | 2016-04-08 09:06 | Civil - Tunnelling | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | During a planned Crossrail surveillance undertaken on 8th April 2016 which looked at Sheet Waterproof Membrane installation and records at Whitechapel, check sheets D3-94, D3-96 and D3-82 were looked at for Eastbound Cavern Block 5 as a sample of the works. On review of check sheet D3-94 it was identified that no ‘Single Seam’ checks had been undertaken (visual and mechanical hook) on the water bar seams (A-D – refer to check sheet visual) with the space left blank on the record, as such the integrity of the welding cannot be confirmed for this block location. Furthermore, the check sheet had been signed as acceptable by IAT and __ personnel. Inspection and Test Plant (ITP) Cxxx-__M-C4-ITP-CR092-50012 (Rev 5) states under Inspection Number 3.3 that all Single Welded Joints shall be ‘mechanically checked’ and recorded on check sheet D3-94. This is a Hold Point for IAT and __ personnel. Works Information Volume 2B states the following under Part 20.8 ‘Inspection and Testing; “The Contractor shall conduct inspections and tests in accordance with his detailed quality plans and ITPs …. The Contractor shall record the completion of inspections and tests and identify records for the results.”
| 02SL - Stations (LUL) | Cxxx-NCR-001277 | NCR | Single seam checks had only been completed for seam A in PTW-W Block 12, with the remaining seams not checked (B-D) as required by the ITP and check sheet. |  | Crossrail | XRL |  |  | 2016-06-06 | 2016-06-07 16:46 | 1 | 2016-04-08 09:10 | Civil - Tunnelling | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During a planned Crossrail surveillance undertaken on 8th April 2016 which looked at Sheet Waterproof Membrane installation and records at Whitechapel, check sheets D3-94, D3-96 and D3-82 were looked at for PTW-W Block 12 as a sample of the works. On review of check sheet D3-94 it was identified that ‘Single Seam’ checks had only been undertaken (visual and mechanical hook) on water bar seam A, with seams B-D left blank (refer to check sheet visual); as such based on the record produced it can only be confirmed that 25% of the seams had been checked with the integrity of the joints remaining questionable. Furthermore, the check sheet had been signed as acceptable by IAT and __ personnel. Inspection and Test Plant (ITP) Cxxx-__M-C4-ITP-CR092-50012 (Rev 5) states under Inspection Number 3.3 that all Single Welded Joints shall be ‘mechanically checked’ and recorded on check sheet D3-94. This is a Hold Point for IAT and __ personnel. Works Information Volume 2B states the following under Part 20.8 ‘Inspection and Testing; “The Contractor shall conduct inspections and tests in accordance with his detailed quality plans and ITPs …. The Contractor shall record the completion of inspections and tests and identify records for the results.”
| 02SL - Stations (LUL) | Cxxx-NCR-001278 | NCR | No visual checks for sheet membrane damage had been recorded as being completed as required on check sheet D3-94 for PTW-W Block 12. |  | Crossrail | XRL |  |  | 2016-06-06 | 2016-06-07 15:41 | 1 | 2016-04-08 09:13 | Civil - Tunnelling | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During a planned Crossrail surveillance undertaken on 8th April 2016 which looked at Sheet Waterproof Membrane installation and records at Whitechapel, check sheets D3-94, D3-96 and D3-82 were looked at for PTW-W Block 12 as a sample of the works. On review of check sheet D3-94 it was identified that no visual checks for damage had been recorded as being completed for the installed sheet membrane in block 12, with the section left blank, as such it cannot be confirmed that the installed membrane is defect free based on the records provided. Furthermore, the check sheet had been signed as acceptable by IAT and __ personnel. Inspection and Test Plant (ITP) Cxxx-__M-C4-ITP-CR092-50012 (Rev 5) states under Inspection Number 5.1 that the installed sheet membrane should be defect free with the sections completed on the ITP documented check sheets, in this case D3-94. This is a Hold Point for IAT and __ personnel. Works Information Volume 2B states the following under Part 20.8 ‘Inspection and Testing; “The Contractor shall conduct inspections and tests in accordance with his detailed quality plans and ITPs …. The Contractor shall record the completion of inspections and tests and identify records for the results.”
| 02SL - Stations (LUL) | Cxxx-NCR-001279 | NCR | L- AP10a - Contraction Joint Location Changed |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-11-30 | 2016-12-05 15:57 | 5 | 2016-04-11 15:40 | Tunnelling - Tunnelling General | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | L- 11/04/2016- Shift 2 - DS - 1. Contraction joint detailed moved by 400mm towards AP6a from the original location (Att.01) 2. No reinforcement bars were installed in invert slab (Att.02) 3. Therefore as reinforcement is missing from the invert, there is no way to link the reinforcement into the wing wall 4. Waterbar location moved 400mm towards AP6a 5. In the invert slab with the missing reinforcement , the invert was cast with a horizontal joint between the new contraction joint and the wall of the lift shaft instead of a radial joint.
| 02SL - Stations (LUL) | Cxxx-NCR-001280 | NCR | L - Liner Wall B - Starter coupler |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-07-29 | 2016-06-23 14:00 | -36 | 2016-04-20 09:52 | Tunnelling - Tunnelling General | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | L - 24/02/2016 - DS - Shift 1 Whilst doing a walk through of Moorgate pit bottom, it was spotted that the horizontal couplers within the southside of Liner wall B were positioned incorrectly. As a result of this, the couplers sit outside the face of the box connection for LCWb. The couplers should have been installed as per the design supplied. A survey of the coupler positions has been undertaken that illustrates the above. (Att.02)
| 02SL - Stations (LUL) | Cxxx-NCR-001281 | NCR | L - VD7: Fire proofing profile outside tolerances |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-09-30 | 2016-11-17 10:07 | 48 | 2016-04-20 10:54 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate resources | Completed |  | • On the 12/06/2016 DS, after review of the fire proofing profile scans and junction scans in VD7 some areas from Ch3 to 9 have been found outside the CTRL or CTRL +100mm profile. • They are highlighted in red ( tights – above the CTRL profile ) and blue ( big areas – outside the CTRL + 100mm ) in Att.01 and Att.02 scans. • To summarize there is: - LCE / VD7 junction: Two tights spots encroaching by less than 30mm in the crown and in the invert ( Att.01 ) - VD7 Tunnel: There is 4 areas encroaching the profile by max 60mm and 7 areas outside the CTRL + 100mm profile by max +40 ( Att.02 ) • Profiles for every chainage can be seen in Att.03
| 02SL - Stations (LUL) | Cxxx-NCR-001282 | NCR | L - LCE - Underthickess Of Fireproofing Layer |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-11-11 | 2016-10-13 08:51 | -29 | 2016-05-24 12:40 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | L-23/03/2016- DS - Shift 2 - Whilst viewing the scan , there were a number of areas of underthickness (Required thickness is 50mm) in the fire proofing layer between CH 160 - CH 184. There are 4 areas of underthickness ( Between 30mm - 45mm). 1 - CH 160 - 1500 x 500mm - Thickness 30mm - 10 O'clock 2 - CH 160 - 1000 x 500mm - Thickness 30mm - 11 O'Clock 3 - CH 161 - 1000 x 500mm - Thickness 35mm - 4 O'clock ( Just above the wing wall) 4 - Various - between CH 175 - CH 178 - Thickness greater than 40mm - 8O'clock to 12 O'clock This can be seen in Att.01. To clarify areas highlighted yellow in Att.01 are between 40mm - 50mm. Areas highlighted red are under 40mm and other areas green/blue are >50mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001283 | NCR | L-LCE -Encroachment |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-11-04 | 2017-02-01 15:50 | 89 | 2016-04-20 15:30 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | L-23/03/2016 - DS - Shift 3 - There is one area that have been identified on the scans (Att.01)throughout LCE that are greater than 100mm from the CTRL (zero) line (these are highlighted in blue).The vast majority of these areas are between 10-20mm bigger than the expected 100mm.The area lies at Chainage 184. It ranges from 8 O'clock to 4 O'clock in this area.
| 02SL - Stations (LUL) | Cxxx-NCR-001284 | NCR | L- LCE, AP10a and AP6a-AP10 junction - Debonded waterproofing |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-04-30 | 2017-01-20 08:46 | -100 | 2016-04-27 08:35 | Tunnelling - Linings - Sprayed Concrete | 4000 |  | Material | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Contamination | Completed |  | L- 09/04/2016 – NS – Shift 3 - Sprayed waterproof membrane has been found debonding or with a bond strength of less than the required 0.5MPa in the areas of AP6-AP6a (i.e. AP6a-AP10 junction ), LCE TBM transition( Mainly in the crown) and AP10a. Although these were sprayed in different tunnels, the same equipment was used and they were both sprayed in the same week. This can be seen in Att.01 ( LCE ) , Att.02 ( AP10a ) , Att.03 ( AP6-AP10 junction ) photos
| 02SL - Stations (LUL) | Cxxx-NCR-001285 | NCR | W - CP2 South: Hollow spots in thicknening layer |  | Contr | __M |  |  | 2016-11-25 | 2016-06-01 10:38 | -177 | 2016-04-21 14:21 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • On 05/04/16 during hammer tapping 5 hollow spots have been found in the crown. Major one is located in the crown between 12 O’clock and 1 O’clock (0.8 m x 1.0 m) and needs to be injected • Refer to Att.01 for the CP2 South crown hammer tapping checksheet for the exact location of all the hollow spots • Regulating layer / __ applied without the hammer tapping and permit to cover signed off. Application of __ proceeded prior to review the core showing that the injections were satisfactory.
| 02SL - Stations (LUL) | Cxxx-NCR-001286 | NCR | L- AP10a - Installation Of stainless steel pipes without approved documentations |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-07-31 | 2016-06-14 15:24 | -47 | 2016-04-21 15:34 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | L- 12/04/2016 - Shift 2 (DS) - 1. An MCR (Materials conformance report) by __ was sent to CRL on 10/02/2016 for the approval of stainless steel pipes to be used in AP10a. 2. 2 early warning were sent to CRL to ensure that the appropriate MCR was approved before the pour. The 1st early warning (No.01023) was sent on 21/3/2016 and the 2nd early warning (No.01023) was sent on 30/3/2016. 3. On 12/04/2016, there was a verbal agreement given from CRL to __ to go ahead and pour and install the pipes. At this point the MCR had not been approved and returned to __ from CRL. 4. The MCR was returned to __ on 13/4/2016 approved. 5. Steel pipes installed had a lower steel grading and have now been accepted through the revised MCR ( Refer to Att.03 )
| 02SL - Stations (LUL) | Cxxx-NCR-001287 | NCR | W - PTE-E Ch 25-60: Underthickness (45-50mm) in the Fireproofing layer |  | Contr | __M |  |  | 2016-07-03 | 2016-06-09 13:37 | -24 | 2016-05-04 07:36 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • On 18/04/16 PTE-E fire proofing thickness scans have been issued and 6 localised areas with a thickness between 45 and 50mm have been found • Refer to Att.01 exact location and size
| 02SL - Stations (LUL) | Cxxx-NCR-001288 | NCR | L- RCW Leak - Block 2 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-01-07 | 2017-02-01 15:58 | 25 | 2016-04-29 07:22 | Tunnelling - Tunnelling General | 2000 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | L- 14/04/2016 - Shift 2 - DS 1. Cxxx contacted __ about water ingress through the lining, in the invert through Block 2 and Block 3. 2. __ did a walk through with CRL to find that there was water ingress between the joint of blocks 2 ad block 3 on the northside, in the invert.
| 02SL - Stations (LUL) | Cxxx-NCR-001289 | NCR | W - VA2: Void in the top cast opening |  | Contr | __M |  |  | 2016-12-16 | 2016-10-18 15:18 | -59 | 2016-04-27 15:18 | Tunnelling - Linings - In-situ Concrete | 5000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Management Problem - Inadequate administrative control | Completed |  | • On 19/04/16 DS a void 150mm depth has been found in the VA2 cast opening crown - chainage 8 - 13 from 11 to 1'o clock. • Photos of the void can be seen in the Att.01
| 02SL - Stations (LUL) | Cxxx-NCR-001290 | NCR | L- AP10a - Voids in top of lift shaft pour |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-02-28 | 2017-01-24 11:21 | -35 | 2016-04-25 10:57 | Tunnelling - Linings - In-situ Concrete | 4000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | L- 25/04/2016 - Shift 1 - DS - Step 1: 1.The shutter in AP10a was poured on 17/04/2016 using a SCC mix and bleed pipes were installed in the crown. The concrete was poured until it flowed out of the bleed pipes. 2. After striking the shutter, it was noticed that the concentrate had not filled to the top of the shutter and there are voids within the front area of the pour. (The far face has been filled).(Att.01) Northwall: 300mm deepest voids , Length Of void about 1.6m West wall: 100mm deepest void , Length of void about 0.6m Southwall: Minor voiding Step 2: Further to the repairs in AP10a ( L.A repair), the construction team has observed that there has been further issues; 1. Cracking in a small area on the rear well (Att.03a) 2. A small area has crumbed (Att.03b)
| 02SL - Stations (LUL) | Cxxx-NCR-001291 | NCR | L- AP10a – Termination boxes placed in wrong location |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-10-28 | 2017-01-18 12:57 | 82 | 2016-04-26 08:40 | Tunnelling - Linings - Sprayed Concrete | 2000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | L- 25/04/2016 - Shift 1 - DS - In the lift shaft in AP10a the termination boxes for the Re-injectable hoses were originally in the lift shaft walls (see att. 01), however this was deemed a problem and therefore it was agreed to place the termination box within the SCL in AP10a closer to AP6a. This was captured in RFI 854 (see att. 02 and att. 03). However, the RFI was not followed and therefore the termination boxes were placed in the lift shaft wall as per design drawing (att. 01).
| 02SL - Stations (LUL) | Cxxx-NCR-001292 | NCR | W - CP2 South: Hollow spots found in regulating layer and __ sprayed over |  | Contr | __M |  |  | 2016-09-23 | 2016-06-09 13:56 | -106 | 2016-04-27 14:29 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | • On 08/04/16 NS, 8 hollows spots have been found in the regulating layer crown, three were more than 0.5 x 0.5 m2. • As required in the WMS the area should have been tapped with excavator bucket or a larger hammer. • As bringing the 944 into this tunnel seemed quite impractical and as the area was already extensively hammer tapped, __ construction team decided that ‘the area did not fall apart and therefore could remained in place’ decision to spray __ taken. • Refer to Att.01 for the hammer tapping checksheets of CP2 South regulating layer
| 02SL - Stations (LUL) | Cxxx-NCR-001293 | NCR | W - EP1: Fire proofing profile outside tolerances |  | Contr | __M |  |  | 2017-02-28 | 2017-02-23 13:50 | -5 | 2016-10-28 08:13 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • On 16/07/2016, after review of the fire proofing profile scan in EP1, three areas from Ch3 to 7 and 7 to 3'oclock have been found encroaching the CTRL profile ( red areas ) • Four minor areas from Ch3 to 7 and 8 to 4'oclock have been found outside the CTRL +100mm profile ( blue areas ) • They are highlighted in blue and red on Att.01 scan. • Att.02 are profile thicknesses ( 1st layer and overall ) and show that thickness is acceptable
| 02SL - Stations (LUL) | Cxxx-NCR-001294 | NCR | No mechanical hook or pressure testing undertaken on patch repairs for areas sampled during a CRL surveillance |  | Crossrail | XRL |  |  | 2016-07-04 | 2016-07-20 08:15 | 16 | 2016-05-09 07:47 | Tunnelling - Tunnelling General | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | A planned Crossrail surveillance was undertaken on 8th April 2016 which looked at Sheet Waterproof Membrane installation and records at Whitechapel. The process for testing and recording patch repairs was looked at, in particular, for those areas where penetrations had been made to support secondary lining installation. On review of check sheet D3-132 (sheet membrane repair) for WBC Block 3 and EBC Block 5, it was identified that the check sheet only recorded one repair (A) being checked via visual inspection, however five repairs had been recorded. The check sheet was also identified as not differentiating between repairs undertaken on the PVC sheet membrane and those undertaken on the protection membrane. Furthermore, it was identified that the requirements of Cxxx-RFI-00577 and the documented Method Statement was not being met with respect to single seam testing and repair testing. The confirmed answer of RFI 577 (dated Nov 13), which was raised to relax KW21-06 testing requirements, states that the ‘blunt’ tool method may be used to prove the quality of the welded single seams providing that operatives undertake a test panel verified by vacuum testing to demonstrate competence. Additionally, the RFI states that patch repairs to the sheet membrane should be vacuum tested. Based on the above the following was agreed during the post surveillance exit meeting for the areas sampled during the surveillance; 1) visual inspections are only being undertaken on patch repairs as recorded, 2) no test panels have been completed and tested with the vacuum test to validate IAT single seam competence and 3) no vacuum pressure testing has been undertaken on patch repairs. The surveillance was based on a sample of the works, the extent of the check sheets not being completed correctly, or the checks not being undertaken should be investigated across areas that have been recorded as completed to identify the full extent.
| 02SL - Stations (LUL) | Cxxx-NCR-001295 | NCR | L- AP2 - Advance 11 left knee out of profile |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-10-28 | 2016-12-16 09:59 | 49 | 2016-05-03 09:52 | Tunnelling - Tunnelling General | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | L- 03/05/2016 - Shift 3 - NS - The left knee of the tunnel of the AP2 top heading was not excavated to profile. The level of the connection detail between the top heading and invert construction is incorrect which doesnt allow the tunnel to maintain the correct profile and thickness. The continuity L-bars in this area will no longer be usable as it falls outside the design profile of the tunnel lining. (Att.01) Att.02 - Location sketch of the correct levels (Addition sketch to show where the detail is and where it should be)
| 02SL - Stations (LUL) | Cxxx-NCR-001296 | NCR | L- AP10b Encroachment |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-09-16 | 2016-06-15 10:50 | -93 | 2016-05-03 15:45 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | L- 03/05/2016 - Shift 2 - DS When viewing the final scan in AP10b , it can been seen that there is some encroachments. (Att.01+ Att.02).The are several different areas within the invert which encroach from 0mm to 50mm. The location of the encroachments can be seen in Att.01+ Att.02.
| 02SL - Stations (LUL) | Cxxx-NCR-001297 | NCR | W - VA2: Waterproof Membrane damaged |  | Contr | __M |  |  | 2016-07-29 | 2016-07-01 12:25 | -28 | 2016-05-03 11:16 | Tunnelling - Linings - In-situ Concrete | 3000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • On 29/04/16 NS Full 100% coverage of sheet membrane not obtained due to holes and tears. • __ tubes have been found damaged, preventing grouting system from functioning. • Refer to Att.01 for photos of the damaged waterproofing system
| 02SL - Stations (LUL) | Cxxx-NCR-001298 | NCR | W - PTW-W Ch82-102: No hammer tapping carry out in the fire proofing layer. |  | Contr | __M |  |  | 2016-09-30 | 2016-05-23 10:57 | -130 | 2016-05-04 09:28 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | On 03/04/16 NS: Reader in PTW-W Ch82-102 has been applied without the underlying fire proofing layer hammer tapped.
| 02SL - Stations (LUL) | Cxxx-NCR-001299 | NCR | W - WCAV Block 3: Interruption of pouring during 3.5hrs |  | Contr | __M |  |  | 2016-09-30 | 2016-07-07 12:37 | -85 | 2016-05-16 09:16 | Tunnelling - Linings - In-situ Concrete | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | On 04/04/16 DS casting of the WBCAV Block 3 concrete was interrupted for a period of 3.5 hours ( from 6pm to 9.30pm ) due to concrete line blocks / batching plant breakdown Refer to Att.01 for the 04/04/16 WCAV shift report
| 02SL - Stations (LUL) | Cxxx-NCR-001300 | NCR | W - VA2: Masterseal damaged on the LHS next to the shaft connection |  | Contr | __M |  |  | 2016-11-26 | 2016-10-18 15:33 | -39 | 2016-05-05 10:43 | Tunnelling - Linings - In-situ Concrete | 2000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | • During the pour of the VA2 shaft connection ( 17-19 April 2016 ), a stop-end panel on the left hand side released a small amount of concrete material from the shaft connection pour. • The released concrete material settled on the exposed sprayed waterproofing membrane next to the shaft connection on the left hand side looking towards the shaft. • The concrete was not removed and cured on the sprayed waterproofing membrane. • When the shutter was struck and removed ( 20-22 April 2016 ), the concrete was broken off in preparation for secondary lining. • In removing the surplus concrete, the sprayed waterproofing membrane was locally damaged on the LHS - 9 o'clock.
| 02SL - Stations (LUL) | Cxxx-NCR-001301 | NCR | L- LCWb Encroachment And Out of profile |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-10-14 | 2016-10-13 09:08 | -1 | 2016-05-05 14:00 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | L- 04/05/2016- Shift 2 - DS - Whilst reviewing the scans , it has been spotted that there are a number of area which encroach. ( Ch 122 - Ch 143) At the transition between the platform tunnel and LCWb there is encroachment up to 40mm, however this looks to be exactly on the transition. For the rest of the tunnel the max encroachment is under 20mm. Most of these lie between 8 O'Clock and 12 O'Clock on the platform side. ( Att.01-04) This area is non cladded area and shouldn't have an effect on future fixing. Out Of Profile - There are 2 areas ) that have been identified on the scans (Att.01 - Att.06) throughout LCWb that are greater than 100mm from the CTRL (zero) line (these are highlighted in blue), overall about 1% of the whole tunnel lining. The vast majority of these areas are between 5-10mm bigger than the expected 100mm. The tunnel lining itself is not encroaching the required space-proofing and the thickness of the lining meets the minimum requirement as according to the drawings.
| 02SL - Stations (LUL) | Cxxx-NCR-001302 | NCR | W - CP2 North: Hollow spots found in the Secondary lining |  | Contr | __M |  |  | 2016-12-18 | 2017-01-24 14:51 | 37 | 2016-05-17 15:54 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • On 29/08/2014 NCR 841 ( PTE-E Ch 12-70: Hollow areas and non conforming core CR1923 at ch 15 ) has been raised. As the PTE-E will be handed over before CP2 North and PTE-E Ch 15 was included in CP2 North Area, a NCR was raised to record the PTE-E Ch 15 hollow spot ( i.e NCR 1302 ) and removed from NCR 841. • On 24/07/14 during hammer tapping of the secondary lining 2nd layer in WHI PTE-East chainage 12-70m - crown one hollow spot has been found: - Ch 15 at 1 o'clock • Refer to Att01. WHI PTE-East chainage 12-70m Hammer Testing Checksheet and Att.02 for a detailed sketch • On 13/08/14 DS core was taken and inspection has confirmed the voiding • Refer to Att03. for the core report
| 02SL - Stations (LUL) | Cxxx-NCR-001303 | NCR | L- LCWb Underthickness including top of the wingwalls |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-12-02 | 2017-03-31 09:07 | 119 | 2016-05-12 09:54 | Tunnelling - Linings - Sprayed Concrete | 2500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | L- 04/05/2016 - Shift 1 - NS Thickness scans (Att.01) for LCWb shows underthickness in one area (Required thickness is 50mm) in the fire proofing layer. Location: CH 125 in the crown Thickness: 35mm To profile: 60mm Size: 900mm x 300mm As per Att.01 scans there is also underthickness in top of the wing walls chainage 121 and 122.
| 02SL - Stations (LUL) | Cxxx-NCR-001304 | NCR | W - CP2 South/PTW: Tight areas in the junction |  | Contr | __M |  |  | 2016-11-29 | 2017-01-27 16:23 | 59 | 2016-09-30 15:42 | Tunnelling - Linings - In-situ Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | • On the 27/05/2016 after review of the fire proofing profile 3d scan in CP2 South / PTW junction, three areas on both sides of the junction have been found encroaching the CTRL zero line by max 13m. • It is highlighted in orange in Att.01. Area concerned by the defect is localised, below 2%.
| 02SL - Stations (LUL) | Cxxx-NCR-001305 | NCR | L- LCWb - Termination boxes incorrect levels |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-10-07 | 2016-07-01 10:09 | -98 | 2016-05-09 09:57 | Tunnelling - Linings - Sprayed Concrete | 6000 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | L- 04/05/2016 - Shift 2 - DS Throughout LCWb the termination boxes have been installed at El 77.85 m on track-side and platform side however the levels on platform side were meant to be lower than this (El 77.32 according to Cxxx-RFI-000733). Att.01+ Att.02 - The survey shows the amount of incorrect level termination boxes
| 02SL - Stations (LUL) | Cxxx-NCR-001307 | NCR | L- PTE-E, RCE, PTE-W & LCE - Blocked Re-injectable Tubes |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2018-01-25 | 2018-02-02 10:07 | 8 | 2016-06-07 10:48 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | While flushing the hoses in PTE, RCE and LCE, the following hoses have been found blocked: PTE-E & RCE (Package L002 – Schematic Cxxx-__M-C4-LLG-C101-50203) - PTE-E Block 1 – Track Side Box 2: 1 hose blocked (blue) - PTE-E Block 1 – Platform Side Box 1: 1 hose blocked (transparent) - PTE-E Block 1 – Platform Side Box 2: 1 hose blocked (yellow) - PTE-E Block 1 – Platform Side Box 4: 1 hose blocked (green) - PTE-E Block 1 – Platform Side Box 6: 1 hose blocked (transparent) - PTE-E Block 2 – Track Side Box 2: 2 hoses blocked (blue & blue) - PTE-E Block 4 – Track Side Box 2: 2 hoses blocked (blue & blue) - PTE-E Block 4 – Platform Side Box 1: 1 hose blocked (transparent) - PTE-E Block 4 – Platform Side Box 3: 1 hose blocked (transparent) - PTE-E Block 5 – Track Side Box 1: 1 hose blocked (transparent) - PTE-E Block 6 – Track Side Box 2: 1 hose blocked (transparent) - PTE-E Block 6 – Platform Side Box 2: 1 hose blocked (red) - PTE-E Block 9 – Track Side Box 1: 1 hose blocked (transparent) - PTE-E Block 9 – Track Side Box 5: 1 hose blocked (transparent) - PTE-E Block 9 – Platform Side Box 1: 2 hoses blocked (transparent & yellow) - PTE-E Block 9 – Platform Side Box 4: 1 hose blocked (transparent) - PTE-E Block 11 – Track Side Box 1: 1 hose blocked (transparent) - PTE-E Block 11 – Track Side Box 2: 1 hose blocked (black) - PTE-E Block 11 – Track Side Box 4: 2 hoses blocked (green & transparent) - PTE-E Block 11 – Platform Side Box 1: 1 hose blocked (transparent) - PTE-E Block 11 – Platform Side Box 3: 1 hose blocked (transparent) - PTE-E Block 11 – Platform Side Box 4: 1 hose blocked (transparent) - PTE-E Block 12 – Platform Side Box 2: 3 hoses blocked (blue, blue & transparent) - PTE-E Block 12 – Platform Side Box 3: 2 hoses blocked (black & transparent) - PTE-E Block 12 – Platform Side Box 4: 2 hoses blocked (yellow & transparent) - PTE-E Block 13 – Platform Side Box 2: 3 hoses blocked (yellow, yellow & transparent) - PTE-E Block 13 – Platform Side Box 3: 3 hoses blocked (blue, blue & transparent) - PTE-E Block 14 – Track Side Box 3: 1 hose blocked (transparent) - PTE-E Block 14 – Platform Side Box 1: 1 hose blocked (blue) - PTE-E Block 14 – Platform Side Box 3: 1 hose blocked (transparent) - PTE-E Block 14 – Platform Side Box 4: 1 hose blocked (green) - PTE-E Block 15 – Track Side Box 2: 2 hoses blocked (transparent & blue) - PTE-E Block 15 – Track Side Box 3: 1 hose blocked (transparent) - PTE-E Block 15 – Platform Side Box 2: 2 hoses blocked (yellow & transparent) - PTE-E Block 15 – Platform Side Box 4: 1 hose blocked (blue) - PTE-E/W Block 16 – Track Side Box 2: 1 hose blocked (transparent) - PTE-E/W Block 16 – Platform Side Box 1: 1 hose blocked (black) All flushing records checksheets for block 1 to block 16 can be seen in Cxxx-__M-C4-LLG-C101-50203 Re-Injectable Tube Schematics and Flushing Records for PTE-E & RCE SL - Package No. L002. PTE-W & LCE (Package L076 – Schematic Cxxx-__M-C4-LLG-C101-50504) - PTE-W Block 18 – Platform Side Box 2: 1 hose blocked (transparent) - PTE-W Block 18 – Platform Side Box 4: 1 hose blocked (transparent) - PTE-W Block 19 – Platform Side Box 2: 2 hoses blocked (transparent & transparent) - PTE-W Block 19 – Platform Side Box 5: 1 hose blocked (transparent) - PTE-W Block 20 – Platform Side Box 2: 1 hose blocked (transparent) - PTE-W Block 20 – Platform Side Box 3: 1 hose blocked (transparent) - PTE-W Block 21 – Platform Side Box 2: 1 hose blocked (transparent) - PTE-W Block 27 – Track Side Box 1: 1 hose blocked (transparent) - PTE-W Block 27 – Platform Side Box 1: 1 hose blocked (transparent) - PTE-W Block 28 – Track Side Box 2: 1 hose blocked (transparent) - PTE-W Block 28 – Track Side Box 3: 1 hose blocked (transparent) - PTE-W Block 28 – Platform Side Box 2: 1 hose blocked (transparent) - PTE-W Block 29 – Track Side Box 2: 1 hose blocked (transparent) - PTE-W Block 31 – Track Side Box 1: 2 hoses blocked (black & transparent) - PTE-W Block 31 – Track Side Box 3: 1 hose blocked (green) - PTE-W Block 31 – Track Side Box 4: 1 hose blocked (transparent) - PTE-W Block 31 – Platform Side Box 1: 2 hoses blocked (yellow & transparent) - PTE-W Block 31 – Platform Side Box 2: 1 hose blocked (black) - PTE-W Block 31 – Platform Side Box 3: 1 hose blocked (blue) - PTE-W Block 31 – Platform Side Box 4: 1 hose blocked (green) - PTE-W Block 31 – Platform Side Box 6: 1 hose blocked (transparent) - PTE-W Block 32 – Platform Side Box 1: 1 hose blocked (black) - PTE-W Block 32 – Platform Side Box 3: 1 hose blocked (green) All flushing records checksheets block 16 to block 32 can be seen in Cxxx-__M-C4-LLG-C101-50204 Re-Injectable Tube Schematics and Flushing Records for PTE-W & LCE SL - Package No. L076.
| 02SL - Stations (LUL) | Cxxx-NCR-001308 | NCR | L - PTW-E, RCW, PTW-W & LCWb - Blocked Re-injectable Tubes after corbel installation |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2018-01-25 | 2018-02-02 10:12 | 8 | 2017-01-03 11:07 | Tunnelling - Tunnelling General | 1000 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | 02/04/2016 - Shift 3 DS - CRL instructed __, via PMI 1115, to reflush the re-injectable tubes that have been casted into the corbel by Cxxx in PTW, RCW and LCWb. After re-flushing the re-injectable tubes, the following hoses have been found blocked: PTW-E & RCW (Package L004 – Schematic Cxxx-__M-C4-LLG-C101-50205) - PTW-E Block 1 – Platform Side Box 1: 3 hoses blocked (black, green & transparent) - PTW-E Block 1 – Platform Side Box 2: 3 hoses blocked (yellow, red & blue) - PTW-E Block 1 – Platform Side Box 3: 2 hoses blocked (yellow & red) - PTW-E Block 1 – Platform Side Box 5: 2 hoses blocked (red & transparent) - PTW-E Block 1 – Track Side Box 1: 3 hoses blocked (black, green & white) - PTW-E Block 1 – Track Side Box 2: 4 hoses blocked (green, yellow, yellow, transparent) - PTW-E Block 1 – Track Side Box 3: 3 hoses blocked (black, transparent & green) - PTW-E Block 1 – Track Side Box 4: 4 hoses blocked (black, black, red and transparent) - PTW-E Block 2 – Platform Side Box 1: 1 hose blocked (black) - PTW-E Block 2 – Track Side Box 1: 2 hoses blocked (black & blue) - PTW-E Block 2 – Track Side Box 3: 2 hoses blocked (blue & green) - PTW-E Block 2 – Track Side Box 4: 1 hose blocked (blue) - PTW-E Block 3 – Track Side Box 2: 1 hose blocked (transparent) - PTW-E Block 4a – Platform Side Box 2: 1 hose blocked (yellow) - PTW-E Block 4a – Track Side Box 2: 1 hose blocked (transparent) - PTW-E Block 4b – Platform Side Box 2: 1 hose blocked (blue) - PTW-E Block 4b – Track Side Box 1: 1 hose blocked (transparent) - PTW-E Block 5 – Platform Side Box 3: 1 hose blocked (green) - PTW-E Block 5 – Platform Side Box 4: 1 hose blocked (black) - PTW-E Block 5 – Track Side Box 2: 1 hose blocked (transparent) - PTW-E Block 6 – Platform Side Box 2: 1 hose blocked (yellow) - PTW-E Block 6 – Platform Side Box 3: 1 hose blocked (transparent) - PTW-E Block 6 – Platform Side Box 4: 1 hose blocked (blue) - PTW-E Block 6 – Track Side Box 3: 1 hose blocked (transparent) - PTW-E Block 7 – Platform Side Box 1: 1 hose blocked (black) - PTW-E Block 7 – Platform Side Box 2: 2 hoses blocked (green & transparent) - PTW-E Block 7 – Track Side Box 1: 1 hose blocked (yellow) - PTW-E Block 7 – Track Side Box 2: 2 hoses blocked (blue & transparent) - PTW-E Block 8 – Platform Side Box 3: 1 hose blocked (transparent) - PTW-E Block 8 – Track Side Box 3: 1 hose blocked (transparent) - PTW-E Block 9 – Platform Side Box 2: 1 hose blocked (transparent) - PTW-E Block 9 – Platform Side Box 5: 1 hose blocked (transparent) - PTW-E Block 9 – Track Side Box 3: 1 hose blocked (transparent) - PTW-E Block 10 – Platform Side Box 2: 1 hose blocked (transparent) - PTW-E Block 10 – Track Side Box 2: 1 hose blocked (transparent) All flushing records checksheets for block 1 to block 10 can be seen in Cxxx-__M-C4-LLG-C101-50205 Re-Injectable Tube Schematics and Flushing Records for PTW-E & RCW SL - Package No. L004. PTW-W & LCWb (Package L077 – Schematic Cxxx-__M-C4-LLG-C101-50506) - PTE-E/W Block 13 – Track Side Box 3: 1 hose blocked (transparent) - PTW-W Block 14 – Platform Side Box 1: 2 hoses blocked (yellow & transparent) - PTW-W Block 14 – Platform Side Box 3: 1 hose blocked (blue) - PTW-W Block 14 – Platform Side Box 4: 1 hose blocked (transparent) - PTW-W Block 14 – Track Side Box 1: 1 hose blocked (transparent) - PTW-W Block 14 – Track Side Box 2: 2 hoses blocked (black & transparent) - PTW-W Block 14 – Track Side Box 4: 2 hoses blocked (green & transparent) - PTW-W Block 15 – Track Side Box 1: 2 hoses blocked (yellow & transparent) - PTW-W Block 15 – Track Side Box 2: 1 hose blocked (blue) - PTW-W Block 16 – Platform Side Box 2: 1 hose blocked (blue) - PTW-W Block 16 – Track Side Box 2: 2 hoses blocked (green & transparent) - PTW-W Block 16 – Track Side Box 4: 1 hose blocked (black) - PTW-W Block 17 – Track Side Box 1: 1 hose blocked (transparent) - PTW-W Block 18 – Platform Side Box 1: 1 hose blocked (transparent) - PTW-W Block 18 – Platform Side Box 2: 1 hose blocked (red) - PTW-W Block 18 – Track Side Box 1: 1 hose blocked (transparent) - PTW-W Block 18 – Track Side Box 2: 2 hoses blocked (red & transparent) - PTW-W Block 19 – Platform Side Box 2: 1 hose blocked (transparent) - PTW-W Block 19 – Platform Side Box 5: 1 hose blocked (transparent) - PTW-W Block 19 – Track Side Box 1: 1 hose blocked (transparent) - PTW-W Block 19 – Track Side Box 2: 1 hose blocked (transparent) - PTW-W Block 19 – Track Side Box 3: 1 hose blocked (transparent) - PTW-W Block 19 – Track Side Box 4: 1 hose blocked (transparent) - PTW-W Block 20 – Platform Side Box 2: 1 hose blocked (transparent) - PTW-W Block 20 – Platform Side Box 3: 1 hose blocked (transparent) - PTW-W Block 20 – Track Side Box 1: 1 hose blocked (transparent) - PTW-W Block 20 – Track Side Box 2: 1 hose blocked (transparent) - PTW-W Block 20 – Track Side Box 3: 1 hose blocked (transparent) - PTW-W Block 20 – Track Side Box 4: 1 hose blocked (transparent) - PTW-W Block 21 – Platform Side Box 1: 1 hose blocked (transparent) - PTW-W Block 21 – Platform Side Box 2: 1 hose blocked (transparent) - PTW-W Block 21 – Track Side Box 1: 1 hose blocked (transparent) - PTW-W Block 21 – Track Side Box 2: 1 hose blocked (transparent) - PTW-W Block 22 – Platform Side Box 1: 1 hose blocked (transparent) - PTW-W Block 22 – Platform Side Box 2: 1 hose blocked (transparent) - PTW-W Block 22 – Platform Side Box 6: 1 hose blocked (transparent) - PTW-W Block 22 – Track Side Box 2: 1 hose blocked (transparent) - PTW-W Block 23 – Platform Side Box 3: 1 hose blocked (transparent) - PTW-W Block 23 – Track Side Box 3: 1 hose blocked (transparent) - PTW-W Block 24 – Platform Side Box 2: 1 hose blocked (transparent) - PTW-W Block 24 – Track Side Box 2: 1 hose blocked (transparent) - LCWb Portal Opening – Platform Side Box 2: 1 hose blocked (red) - LCWb Portal Opening – Track Side Box 2: 2 hoses blocked (red & blue) All flushing records checksheets block 13 to LCWb Portal Opening can be seen in Cxxx-__M-C4-LLG-C101-50206 Re-Injectable Tube Schematics and Flushing Records for PTW-W & LCWb SL - Package No. L077.
| 02SL - Stations (LUL) | Cxxx-NCR-001309 | NCR | W - E&W Cavern Invert: Off-Site Fire Main UTX construction started without ITP in place |  | Contr | __M |  |  | 2016-06-08 | 2016-05-27 13:09 | -12 | 2016-05-09 14:08 | Tunnelling - Linings - In-situ Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | • Cxxx-__M-C4-ITP-D061-50019 ITP for Off-Site fire main UTX construction has been submitted the 04/05/2016 after the off-site fabrication of the fire main UTX in West and East Cavern invert had started
| 02SL - Stations (LUL) | Cxxx-NCR-001310 | NCR | W - EBRT,EB Cav and LCE: Hollow spots in primary lining |  | Contr | __M |  |  | 2017-04-25 | 2017-05-25 09:00 | 30 | 2017-02-24 09:55 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • On 09/10/14 during hammer tapping 2 hollow spots have been found in the primary lining near ch 105. • Refer to Att.01 page 1 for the EBRTW Ch 30-105 hammer tapping checksheet for the exact location • Beamer survey can be seen in Att.02 • On 11/10/14 during hammer tapping 4 hollow spots have been found in the primary lining from ch 128 to 145. • Refer to Att.01 page 2 for the EBRTW Ch 105-145 hammer tapping checksheet for the exact location • On 11/10/14 during hammer tapping 3 hollow spots have been found in the primary lining from ch 180 to 190. Please note that the 4 hollows in ch145 are already covered in point 2 • Refer to Att.01 page 3 for the EBRTW Ch 120-190 hammer tapping checksheet for the exact location • On 24/02/16 during hammer tapping 8 hollow spots have been found in the primary / thickening lining crown. • Refer to Att.02 for the EBRTW Ch 100-110 hammer tapping checksheet for the exact location
| 02SL - Stations (LUL) | Cxxx-NCR-001311 | NCR | W - WB CAV Block 6/7: Missing or incomplete sheet membrane installation checksheets |  | Contr | __M |  |  | 2016-07-16 | 2016-07-20 08:20 | 4 | 2016-05-17 13:55 | Tunnelling - Linings - In-situ Concrete | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | • On 26/02/16 WB Cavern Block 7 Sheet Membrane Installation Sheet D3-94 ( Att.01 ) during CRL review of the checkhseet is it has been found at that there were ' Block not finished 2 Rows Welded' noted and no reference if this was addressed or not before application of the protective membrane. • D3-94 Sheet Membrane Installation Checkhseet for WB CAV Block 7 is missing
| 02SL - Stations (LUL) | Cxxx-NCR-001312 | NCR | W - PTE-E Ch70-108: Minor areas outside CTRL +100mm profile line |  | Contr | __M |  |  | 2016-11-26 | 2016-12-09 14:24 | 13 | 2016-05-12 13:13 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • On 12/05/2016, after the review of the fire proofing profile in PTE-E, some areas ( Ch72 to 76 and Ch100 to 108 - 7 to 4'oclock) have been found to be outside the CTRL +100mm profile • They are highlighted in blue on Att.01 scans.
| 02SL - Stations (LUL) | Cxxx-NCR-001313 | NCR | W - VA2: Areas outside CTRL +100mm profile lining |  | Contr | __M |  |  | 2016-09-02 | 2016-08-26 14:32 | -7 | 2016-05-12 13:21 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • On 12/05/2016, after review of the fire proofing profile in PTE-E, areas ( Ch8 to 11 - 9 to 3'oclock) have been found to be outside the CTRL +100mm profile • They are highlighted in blue on Att.01 scans. Area concerned by the defect is localised, below 2%.
| 02SL - Stations (LUL) | Cxxx-NCR-001314 | NCR | W - PTE-E: __ hoses blocked in the invert |  | Contr | __M |  |  | 2016-10-07 | 2016-09-07 16:11 | -30 | 2016-06-02 09:01 | Tunnelling - Linings - In-situ Concrete | 1000 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | On 12/05/16 DS while flushing the hoses in PTE-E Block 1 to 10 the following hoses have been found blocked: Block 1 - Box 2 - Platform side: 1 hose ( red ) Block 3 - Box 4 - Track side: 1 hose (transparent ) Block 4 - Box 1 - Track side: 1 hose ( black ) Block 5 - Box 1 - Track side: 1 hose ( green ) Block 5 - Box 1 - Track side: 1 hose ( blue ) Block 6 - Box 2 - Track side: 5 hoses ( 1 green, 1 red, 1 blue and 2 transparents ) Block 7 - Box 2 - Track side: 1 hose ( yellow ) Block 7 - Box 2 - Platform side: 1 hose ( blue ) Block 8 - Box 4 - Track side: 1 hose ( green) Block 8 - Box 2 - Platform side: 2 hoses ( 1 blue and 1 green ) Block 9 - Box 1 - Track side: 1 hose ( red ) Block 9 - Box 2 - Track side: 1 hose ( red ) Block 9 - Box 2 - Platform side: 1 hose ( red ) Block 9 - Box 3 - Platform side: 1 hose ( blue ) Block 10 - Box 3 - Track side: 1 hose ( blue ) Block 10 - Box 1 - Platform side: 1 hose ( red ) Block 10 - Box 4 - Platform side: 1 hoses ( 1 blue, 1 red ) Refer to Att.01 for the VA2 flushing records
| 02SL - Stations (LUL) | Cxxx-NCR-001315 | NCR | W - VA2: __ hoses blocked in the invert |  | Contr | __M |  |  | 2016-09-30 | 2016-09-07 15:59 | -23 | 2016-06-02 09:04 | Tunnelling - Linings - In-situ Concrete | 1000 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | On 12/05/16 DS while flushing the hoses in VA2 the following hoses have been found blocked: Block 1 - Box 1 - Track side: 4 hoses (2 red and 2 transparent ) Block 1 - Box 1 - Platform side: 3 hoses (2 red and 1 transparent ) Block 1 - Box 2 - Platform side: 1 hose ( yellow ) Block 1 - Box 2 - Track side: 1 hose ( Black ) Block 2 - Box 2 - Platform side: 1 hose1 ( Black) Refer to Att.01 for the VA2 flushing records
| 02SL - Stations (LUL) | Cxxx-NCR-001316 | NCR | W - ES1: Starter bars bented at transition block |  | Contr | __M |  |  | 2016-09-16 | 2016-08-26 15:06 | -21 | 2016-05-23 11:04 | Tunnelling - Linings - In-situ Concrete | 3000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | • The back of the diaphragm wall at ES1 transition block required waterproof membrane to be installed. • On 14/05/16 invert B16 starter bars were in the way of the membrane installation and the site team bent these down out of the way. • Refer to Att.01 for photos of the B16 starter bars bented
| 02SL - Stations (LUL) | Cxxx-NCR-001317 | NCR | L-AP6 - LCE connection + Injection hoses |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-10-07 | 2016-10-13 09:20 | 6 | 2016-06-29 12:51 | Tunnelling - Tunnelling General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | L-17/05/2016 - Shift 1 - DS By AP6-LCE connection (Block1): The south side of inner and outer loop of injection hoses have been damaged during profiling of LCE Pr. Lining crown. - Att.02 An As-built can be seen in Att.07
| 02SL - Stations (LUL) | Cxxx-NCR-001318 | NCR | W - PTW-W Block 19: No evidence of single seam tests done |  | Contr | __M |  |  | 2016-10-28 | 2016-09-23 11:11 | -35 | 2016-05-18 08:41 | Tunnelling - Linings - In-situ Concrete | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Upon review of PTW-W Block 19 before placement of protection layer concrete, following anomalies have been found: • The sheet for chainage 107.5 to 118m was completed for dayshift 15TH April. The sheet itself was not completed and states that single seam testing was done and had passed. This was not the case on site. • The sheet for chainage 107.5-121.5m was completed on nightshift 15th April. There is no reference to single seam tests being done. • Refer to Att.01 for PTW-W Block 19 Sheet membrane installation check sheet
| 02SL - Stations (LUL) | Cxxx-NCR-001319 | NCR | W - CP2 South / CS1: Over spraying of Masterseal with Secondary lining |  | Contr | __M |  |  | 2017-04-30 | 2017-03-24 18:43 | -37 | 2016-07-05 07:36 | Tunnelling - Linings - In-situ Concrete | 2000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | • CP2 South / CS1 junction was formed before the transit of the Cxxx TBM through the station. At that time, works were not completed in cleaning, forming and protecting an appropriate joint connection for the remaining secondary lining in CP2 South. • After gaining access post Cxxx TBM handover to Cxxx, work has commenced on completing the secondary lining in the CP2 South area. • As the concrete being in place for so long, it was not possible to form an acceptable joint and remove overspray without damaging the __ waterproofing in the RHS and LHS.
| 02SL - Stations (LUL) | Cxxx-NCR-001320 | NCR | L- VD7 - Secondary Lining Targets |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-09-23 | 2016-10-14 09:04 | 21 | 2016-05-24 13:49 | Tunnelling - Tunnelling General | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | L- 23/05/2016 - Shift 2 - DS near face steel were found too far back within VD7 section. The records and the facts are as follows: - FF steel back cover = 50mm - 2nd 1st thickness = 100mm - NF steel is set at +300 average (meaning space between NF & FF steel = 130mm) - NF steel back cover = 50-80mm - 2nd 1st profile is at +380 This can be seen in the sketch Att.01 and photo Att.02
| 02SL - Stations (LUL) | Cxxx-NCR-001321 | NCR | W - WBCAV: Incorrect flanges welded on the fire main UTX |  | Contr | __M |  |  | 2016-09-30 | 2016-10-07 13:24 | 7 | 2016-05-25 07:35 | Tunnelling - Linings - In-situ Concrete | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | • On May 2015 WB Cavern fire main UTX arrived on site and all documentation provided by the supplier __ to __. • While reviewing the documentation it has been found out that the two flanges welded at the end of the pipe were TYPE 1 instead of TYPE 12. • Refer to Att.01 for the inspection certificate to confirm that flanges are TYPE 1
| 02SL - Stations (LUL) | Cxxx-NCR-001322 | NCR | W & L - Drying shrinkage failures of RL2 Mix on March - CR2662 & CR2692 |  | Contr | __M |  |  | 2016-08-26 | 2016-07-19 16:45 | -38 | 2016-05-25 16:20 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | 28 days samples CR2662 taken 10/03/16 at LIV and CR2692 taken 19/03/16 at WHI failed to comply with specification limit, see attached summary sheets. Refer to Att.01 for the Drying Shrinkage Summary of Mix RL2 C28-34
| 02SL - Stations (LUL) | Cxxx-NCR-001323 | NCR | W - Drying shrinkage failure of P1 Mix on March - CR2674 |  | Contr | __M |  |  | 2016-09-09 | 2016-07-19 16:47 | -52 | 2016-05-25 16:25 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | 28 days samples CR2674 taken 14/03/16 at WHI failed to comply with specification limit, see Att.01 for the Mix P1 C32/40 45kg 2kg PP summary sheets.
| 02SL - Stations (LUL) | Cxxx-NCR-001324 | NCR | W & L - Drying shrinkage failures of P2 Mix on Feb/March - CR2574 & CR2672 |  | Contr | __M |  |  | 2016-09-02 | 2016-10-10 10:45 | 38 | 2016-05-25 16:36 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | 28 days samples CR2574 taken 01/02/16 and CR2672 taken 14/03/16, both at WHI site failed to comply with specification limit, see Att.01 for Mix P2 C32/40 2kg PP and Mix P2 C32/40 summary sheets.
| 02SL - Stations (LUL) | Cxxx-NCR-001325 | NCR | L - VD4 Cold joints at the top of wing wall |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-10-30 | 2016-11-18 13:36 | 19 | 2016-05-25 16:16 | Tunnelling - Tunnelling General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | L - 29/03/2016 - Shift 3 - DS At the top of the wing walls ( both left and right side), stage 1 in Block 1 + 2, a cold joint was formed. Cold joint can be seen in Att.01- 04
| 02SL - Stations (LUL) | Cxxx-NCR-001326 | NCR | L - AP1 Leak at top of wing wall |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-08-04 | 2017-08-02 14:35 | -2 | 2016-06-22 16:14 | Tunnelling - Tunnelling General | 2000 |  | Material | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | L- 17/05/2016 - Shift 1 - DS 1.Water leaks from the longitudinal construction joint between cast in situ wing wall and SC lining on the south wall around Block AP1-5. This can be seen in Att.01+ Att.02 2.Water leakage also observed on the invert through 2No radial joints between BlockAP1-4 and Block AP1-5 / BlockAP1-5 and BlockAP1-6 As seen in Att.03+Att.04
| 02SL - Stations (LUL) | Cxxx-NCR-001327 | NCR | L- VD4 - Terminaton boxes in the wrong location |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-02-03 | 2017-01-24 09:29 | -10 | 2016-05-26 14:53 | Tunnelling - Tunnelling General | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | L- 25/05/2016 - Shift 2 - DS In VD4 (Block 7) the left hand side termination of injection hoses is much lower than others. It is below the required level of 1.266m from center line Refer to Att.01 for photo of the termination box
| 02SL - Stations (LUL) | Cxxx-NCR-001328 | NCR | W - PTW-W/CP1: FF steel incorrect position in junction |  | Contr | __M |  |  | 2016-07-30 | 2016-07-27 08:56 | -3 | 2016-05-31 09:13 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | • On 30/05/2016 steel reinforcement not installed as per dimensions specified on drawing. Steel moved from 2075mm to 1600mm from CP1a centreline in Block 19 ( PTW-W / CP1 junction ) in the CP1a crown
| 02SL - Stations (LUL) | Cxxx-NCR-001329 | NCR | W - WB CAV Block 7: Adding water to FSC Mix |  | Contr | __M |  |  | 2016-07-30 | 2016-07-19 16:42 | -11 | 2016-05-31 09:31 | Tunnelling - Linings - In-situ Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Supervisor does not have sufficient experience | Completed |  | • On 29/05/16 during WB CAV Block 7 pouring water has been added to mixer at pour location for final 2 mixer trucks, approx. 6m cube, (FSC Polyfibre mix) for pour to increase workability around steel reinforcement. • Decision taken without PIC was informed of the addition of water • Refer to Att.01 for pour records
| 02SL - Stations (LUL) | Cxxx-NCR-001330 | NCR | W - WB CAV Block 6: Interruption of pouring |  | Contr | __M |  |  | 2016-07-30 | 2016-07-11 13:03 | -19 | 2016-05-31 10:57 | Tunnelling - Linings - In-situ Concrete | 2000 |  | Material | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | • On 04/05/16 DS pouring of the WB CAV Block 6 was abandoned due to concrete line blocks. • Refer to Att.01 for the 04/05/16 WB CAV shift report
| 02SL - Stations (LUL) | Cxxx-NCR-001331 | NCR | W - CP2 South: Western wing wall 40mm tight |  | Contr | __M |  |  | 2016-09-16 | 2016-08-26 15:13 | -21 | 2016-05-31 15:14 | Tunnelling - Linings - In-situ Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • On 28/05/16 __ survey of cast wing walls in CP2 South has been issued and western wing wall found to 40mm tight from chainage 7 to 12 • Refer to Att.01 for the survey report
| 02SL - Stations (LUL) | Cxxx-NCR-001332 | NCR | L- AP6 SL: Missing tests and documentation |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-11-02 | 2017-11-06 16:02 | 4 | 2017-10-19 08:35 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Cxxx-__M-C4-LLG-C101-50218 Deliverable Records for LIV AP6 __ Sprayed Waterproofing Membrane - Package No L026 1) __ – ITP item 3.2, 3.3 Missing Spraying Consumption Rate (__ Form D3-109) for AP6 Ch. 8-119 and 170-183 Cxxx-__M-C4-LLG-C101-50219 Deliverable Records for LIV AP6 Sheet Waterproofing Membrane - Package No L026 2) Sheet – ITP item 1.2 Missing Acceptance of Substrate For Waterproofing Layer (__ Form D3‐96) for AP6 Ch. 0-8 and 22-173 3) Sheet – ITP items 4.1 and 4.2 Missing Acceptance of Injection Tubes (__ Form D3‐82) for AP6 Ch. 36-143. Cxxx-__M-C4-LLG-C101-50220 Deliverable Records for LIV AP6 Cast In Situ - Package No L026 4) Protection Layer – ITP items 2.1, 2.2, 2.3 Missing Secondary Lining Concrete Pre‐Pour Checksheet (__ Form D3‐85) for AP6 Block 10 (Ch. 98-107) 5) Invert – ITP item C1 No cubes taken for AP6 Invert Block 1, 4, 6, 8, 10, 12, 13, 14, 16, 19, 21 and AP10a/AP6a. Cxxx-__M-C4-LLG-C101-50221 Deliverable Records for LIV AP6 Secondary Lining - Package No L026 6) Secondary 1st – ITP item 5.1 Missing Hammer Tapping Checksheet (__ Form D3‐80) for AP6 Second 1st Ch. 29-62, Ch.85-90, Ch.147-183. 7) Secondary 1st – ITP items C3, 1.1, 4.1, 4.4, 4.5, 5.2, 5.3, 5.5, 5.6, 5.7, 5.8, 5.10 Missing Secondary Lining Shotcrete Placement Checksheet (__ Form D3‐86) for AP6 Wings Ch. 84-88, Ch. 127-129, Ch.156-164, Ch.169-183 and AP6 Crown Ch.115-120 8) Secondary 2nd – ITP item 4.2 Missing Reinforcement Checksheet (__ D3‐26) for AP6 Second 2nd NF Blocks 10&11 (Ch.100-118).
| 02SL - Stations (LUL) | Cxxx-NCR-001333 | NCR | W - RCW SL: Missing tests and documentation |  | Contr | __M |  |  | 2017-03-31 | 2017-04-09 14:59 | 9 | 2016-06-28 14:39 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | • Cxxx-__M-C4-LLG-D061-50144 Deliverable Records for RCW Regulation Layer, Sheet Membrane and Cast In-Situ Regulation Layer 1) Early Strength Testing – The frequency with which early strength testing was undertaken was not met. Testing should be undertaken every 3rd bay, but tests were only undertaken once during the construction of RCW (ch.100 to 124). Protection Layer, Cast In-Situ Invert Layer and Sidewall In-Situ Invert Layer 2) Ambient temperature is missing from Secondary Lining Concrete Pour Checksheet (__ Form D3-84). • Cxxx-__M-C4-LLG-D061-50145 Deliverable Records for Spray Waterproofing through Fireproofing Bulking Layer, First Secondary Layer and Second Secondary with Fireproofing Layer 3) No SCL Rebound Measure Sheet (__ Form D3-46) performed during this period • Cxxx-__M-C4-LLG-D061-50156 Deliverable Records for RCW Foam Plug and Rain Installation TBM Slabs, Plinths and Rail Beams and Foam Plug 4) Missing Engineer’s Setting Out Form (__ D3-27) for both parts of rail plinth and TBM foam plug that remain as part of the permanent works behind the TBM rings
| 02SL - Stations (LUL) | Cxxx-NCR-001334 | NCR | W - PTW-W Ch100-144: Fire proofing profile outside tolerances |  | Contr | __M |  |  | 2016-11-15 | 2017-01-17 14:28 | 63 | 2016-06-08 08:00 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • On 07/06/2016, after review of the fire proofing profile in PTW-W, areas ( Ch100 to 144 - 7 to 5'oclock) have been found encroaching the CTRL profile ( red areas ) and outside the CTRL +100mm profile ( blue areas ) • They are highlighted in blue and red on Att.01 scans. Area concerned by the defect is localised, below 1%.
| 02SL - Stations (LUL) | Cxxx-NCR-001335 | NCR | W - CP3: Tights spots in Reader lining |  | Contr | __M |  |  | 2016-08-08 | 2016-08-05 14:49 | -3 | 2016-06-09 16:51 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | On 22/03/16 there are some occurrences where the reader is tight between CH10 to 16 and CH 30 to 37 at 6 and 9 o'clock. The exact location of the tights spots are available in Att.01 and Att.03. These various areas have been over-sprayed by max 50mm The thickness of the tights spots are available in Att.02 and Att.04.
| 02SL - Stations (LUL) | Cxxx-NCR-001336 | NCR | W - EP2 Injection tubes covered with Masterseal |  | Contr | __M |  |  | 2016-08-12 | 2016-08-03 11:38 | -9 | 2016-06-13 14:39 | Tunnelling - Linings - Sprayed Concrete | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | On 12/03/2016 the injection tubes in EP2 invert have been found covered with Masterseal. Refer to Att.01 for photo of covered tubes Damaged invert shown in the photo is recorded in Cxxx-NCR-001265
| 02SL - Stations (LUL) | Cxxx-NCR-001337 | NCR | W - VA2 SL 1st layer sprayed without final visual inspection signed off |  | Contr | __M |  |  | 2016-08-12 | 2016-08-16 09:54 | 4 | 2016-06-13 14:52 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | On 05/05/2016 VA2 Secondary lining 1st layer sprayed without final visual inspection checksheet signed off by CRL
| 02SL - Stations (LUL) | Cxxx-NCR-001338 | NCR | W - CP3 North: Shore A test results not available |  | Contr | __M |  |  | 2016-11-30 | 2016-10-17 10:12 | -44 | 2016-06-13 15:17 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | On 24th April DS 8-9am bolt holes were existing - See Att.01 page 1 On 24th April DS/NS bolt holes repaired by 19:30 - See Att.01 photo 2 On 24th April NS 20:00 Secondary lining bulking layer commenced spraying without any evidence of shore A test done for the repairs in CP3 North ch40 (6 and 9 o'clock )
| 02SL - Stations (LUL) | Cxxx-NCR-001339 | NCR | W - PTW-W Ch102: Small rebate between FP layers on either side of the bulkhead |  | Contr | __M |  |  | 2016-08-27 | 2016-08-26 14:25 | -1 | 2016-06-28 08:55 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | • A bulkhead was installed at Ch102 in the PTW-W tunnel to demarcate the work areas between Cxxx & Cxxx. • On 14/06/16 when works were complete on the Cxxx side and the bulkhead removed it became apparent that the profile of the final fireproof layer of SCL did not match on either side of the bulkhead. This left a small ‘rebate’ which was visible from the crown of the tunnel down over the trackside of the tunnel. • Refer to Att.01 for the photos of the rebate and Att.02 for the fire proofing profile scans of the area.
| 02SL - Stations (LUL) | Cxxx-NCR-001340 | NCR | W - PTE-E Ch 60-90: Incorrect hammer tapping sequence |  | Contr | __M |  |  | 2016-10-21 | 2016-08-26 15:24 | -56 | 2016-06-15 07:48 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | On 07/05/2016 DS Fire proofing in PTE-E has been completed - Refer to Att.01 for the shift report On 08/05/2016 hammer tapping has been done one day after fire proofing application instead of 3 days and reader applied Refer to Att.02 for the hammer tapping before application of the reader
| 02SL - Stations (LUL) | Cxxx-NCR-001341 | NCR | L- PTW-E and RCW SL: Missing tests and documentation |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-08-04 | 2017-07-21 15:47 | -14 | 2017-07-21 10:08 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Cxxx-__M-C4-LLG-C101-50210 Deliverable Records for LIV PTW-E & RCW Regulating Layer - Package No L004 1) Regulation Layer – ITP item C4 Hammer Testing for PTW-E RCW Regulation Layer Block 0 and 1 Crown, Ch. 150 to 165, not witnessed by CRL/Cxxx even so Item C4 is a hold point on the ITP. Refer to Hammer Testing Checksheet (__ Form D3-80). See Att01. Cxxx-__M-C4-LLG-C101-50214 Deliverable Records for LIV PTW-E & RCW SCL - Package No L004 2) Secondary 1st and 2nd (Traditional method) – ITP item C4 Missing Hammer Tapping Check Sheet (__ Form D3-80) for PTW-E Secondary Bulking Layer Ch. 116-120 after repair of fall out (23/10/15) and PTW-E Secondary 2nd Layer Ch. 113-114 after repair of fall out (28/10/15). Cxxx-__M-C4-LLG-C101-50215 Deliverable Records for LIV PTW-E & RCW Fire Protection Layer - Package No L004 3) Fireproofing Layer – ITP item 6.1 Missing contact grouting quantities and location sketch on Grouting of Injection Tubes Check sheet (__ Form D3-109) for PTW-E RCW Blocks 0-1 and 3-8. 4) Fireproofing Layer – ITP item 6.9 Missing Logica Process Check Sheet (__ Form D3-144) for PTW-E RCW Ch. 9-13; 24-50; 68-76; 84-89; 97-101; 124-128; 134-138; 148-149. 5) Fireproofing Layer – ITP item 6.10 Missing Robot Output Rate on Shotcrete Placement Checksheet (__ Form D3-86) for PTW-E Ch. 115-118; 121-123; 126-129. 6) Fireproofing Layer – ITP item 6.11 Missing Accelerator Dosage on Shotcrete Placement Checksheet (__ Form D3-86) for PTW-E Ch. 126-129. Cxxx-__M-C4-LLG-C101-50213 Deliverable Records for LIV PTW-E & RCW Insitu Concrete Invert & Wingwall - Package No L004 7) Invert – ITP item 3.3 - Missing Reinforcement Check Sheet (__ Form D3-26) for PTW-E & RCE Invert Block 0; 4B - Missing bars reported on Reinforcement Check Sheet (__ Form D3-26) for PTW-E & RCE Invert Block 8. See Att03. No RFI or FCD raised about this issue. 8) Invert and Wingwall – ITP item 3.7 Curing information missing on Secondary Lining Concrete Pour Checksheet (__ Form D3-84) for PTW-E and RCW Invert block 11, 10, 9, 7, 2, 1 and sidewalls Block 10, 8, 4a, 3 & 1.
| 02SL - Stations (LUL) | Cxxx-NCR-001342 | NCR | L - AP11&12 Underthickness in Primary Lining Thickenings |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-05-28 | 2017-06-23 14:06 | 26 | 2017-02-17 12:01 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | • During L033 certification package preparation, scan showing areas with underthickness has been found in AP11/AP12 primary lining ( excavation to thicknening ). • They are between ch 3 and 5 from 6'oclock to 2'oclok, worst case is 360mm instead of 500mm located at ch 3.5 - 6oclock • They are highlighted in red Att.01 planview scan and in the Att.02 profile scans
| 02SL - Stations (LUL) | Cxxx-NCR-001343 | NCR | L - AP2, AP2-ES2, CH1-ES3: Missing face log and pictures - May and June 2016 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-10-28 | 2016-11-24 11:37 | 27 | 2016-06-14 15:51 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | During May 2016 at LIV, the following face logs photos have been found missing in AP2: - TOP HEADING Advance 13 - TOP HEADING Advance 29 TOP - TOP HEADING Advance 31 - TOP HEADING Advance 44 - TOP HEADING Advance 61 - TOP HEADING Advance 62 During June 2016 at LIV, the following have been found missing : - in AP2/ES2 ENLARGEMENT DOWNHILL Advance 5 - face log photo - in AP2 INVERT Advance 9 - face log and photo - in CH1/ES3 Adaptation works Advance 1 - face log and photo - in CH1/ES3 Adaptation works Advance 3 - face log photo
| 02SL - Stations (LUL) | Cxxx-NCR-001344 | NCR | W - EP2: Fire proofing profile outside tolerances |  | Contr | __M |  |  | 2016-10-28 | 2017-01-03 12:38 | 67 | 2016-06-15 08:35 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • On 10/06/2016, after review of the fire proofing profile in EP2, areas from Ch11 to 17 and 8 to 4'oclock have been found outside the CTRL +100mm profile ( blue areas ) • They are highlighted in blue on Att.01 page 1 scan. Areas concerned by the defect are localised, below 2%. • Att.01 Page 2 and 3 are secondary lining thicknesses ( 1st layer and overall ) and show that thickness is acceptable
| 02SL - Stations (LUL) | Cxxx-NCR-001345 | NCR | L- AP6 - 2 areas of timber/materials left in the concrete |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-09-25 | 2016-11-24 11:44 | 60 | 2016-06-17 14:48 | Tunnelling - Tunnelling General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | L- 17/06/2016 - Shift 2 - DS 1. During in trimming works on the joint in Block 8, it has been seen that some of the timber/materials have been concreted over. This has occurred where the mini shutter strokes (3 O'clock and 9'Oclock) and on both sides over the stop end. This can be seen in Att.01-Att.02. 2. Block 13 - LHS (Looking towards AP6 headwall) - This is another area where timber has been left in. (Att.03)
| 02SL - Stations (LUL) | Cxxx-NCR-001346 | NCR | L- CP1 Junction (Concourse side) out of profile and underthickness |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-12-25 | 2017-02-01 16:09 | 38 | 2016-06-17 15:28 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | L-17/06/2016 - Shift 3 - DS - • After completion of the fireproofing layer in CH5/CP1 , scans have shown 2 aspects of non conformance 1. Out of profile •3 areas of encroachment westside: - 60mm (worst case) @ 2-5 O'clock Eastside: - 14mm @9 O'clock Eastside: - 15mm @ 7 O'clock •1 area out of profile (blue) crown: Greater than 200mm (Worst case) @ 10-2 O'clock Att.01 shows the area of encroachment in PDF format Att.02 is the raw data of the junction and therefore can be process and modelled against the 3D model for the cladding 2.Underthickness of total secondary lining •2 areas of concern westside: 222mm (28mm underthick) @ 1 O'clock with 0.11mm2 area westside: 246mm (4mm underthick) @2 O'clock with 0.01mm2 area Att.03 show the total thickness of the secondary lining Att.04 show the fireproofing thickness
| 02SL - Stations (LUL) | Cxxx-NCR-001347 | NCR | L- VD7 - Liner Wall A – Couplers in wrong position |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-10-01 | 2016-10-10 15:19 | 9 | 2016-06-23 15:34 | Tunnelling - Tunnelling General | 2000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | L- 23/06/2016 - Shift 3 - DS - Drawing C501-__-C-DDL-C101-50748 (C01) states couplers that will be picked up by VD7 opening reinforcement have to be installed in the range of 590-665 away from the front face of the concrete. This will ensure we have 70mm cover when constructing VD7 opening. Couplers have been installed in wrong position and therefore, on site couplers below axis have a 200mm cover.
| 02SL - Stations (LUL) | Cxxx-NCR-001348 | NCR | L-VD2 - Longitudinal Crack |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-09-29 | 2016-10-13 12:04 | 14 | 2016-06-21 12:57 | Tunnelling - Linings - Sprayed Concrete | 2000 |  | Design | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | L- 17/06/2016 - In VD2 we have a longitudinal crack along directly in the top of the crown. The crack is about 0.45mm wide and about 1500mm long, starting on the box connection side.
| 02SL - Stations (LUL) | Cxxx-NCR-001349 | NCR | L- VD7/LCE - Re-injectable hoses exposed |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-12-25 | 2017-01-19 10:32 | 25 | 2016-07-27 14:49 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | L- 16/06/2016 DS - Shift 2 The inner-most (intrados) re-injectable injection hoses have been found exposed in the invert and crown. Refer to Att.01 for photos of the exposed __ hoses
| 02SL - Stations (LUL) | Cxxx-NCR-001350 | NCR | L- AP9: Data from inclinometer above tunnel is unreliable |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-09-30 | 2016-08-09 10:54 | -52 | 2016-06-22 15:34 | Tunnelling - Tunnelling General | 2000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | L- 22/06/2016 The data received from the inclinometer cannot be processed in such way as to provide relevant and reliable information regarding the ground movement in response to the excavation of the excavation of tunnels AP9, CH6 and ES3.
| 02SL - Stations (LUL) | Cxxx-NCR-001351 | NCR | L- VD4 - Breather pipe required from grouting casted in |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-10-28 | 2017-02-01 16:02 | 96 | 2016-06-23 10:50 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | L- 22/06/2016 In VD4 , the breather pipe in Block 3 has been casted in when the shutter was put in. Originally the breather pipe came out of the stop end in Block 3 and had to be removed after the stop end was struck. Whilst this was meant to be done , the construction team continued to install the shutter in Blocks 3 , 4 & 5 , leaving the breather pipe inaccessible.
| 02SL - Stations (LUL) | Cxxx-NCR-001352 | NCR | W - Galvanic corrosion occured on the suspension rods IE50101 and IE50501 |  | Contr | __M |  |  | 2016-11-27 | 2016-10-17 19:36 | -41 | 2016-06-28 10:20 | Tunnelling - Tunnelling General | 1000 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | • On June 2016, following the decommissioning of inclinometers IE50101, IE50102, IE50203, IE50204, IE50501, IE50502, IE50503 in Whitechapel, it was noted that galvanic corrosion had occurred on the suspension rods IE50101 and IE50501 (2 out 7 inclinometers). • Refer to Att.01 for photos of the defect • It can be noted that no mention of the material used for the rods have been found in the installation report Ref. Cxxx-__M-C2-RGN-D061-50039 Rev 2 prepared by __. • It has been confirmed internally that the design on the above boreholes had been changed by __’s own decision at installation time for safety reasons, in order to reduce risk associated with manual handling during the installation (weight reduction). This decision was made based upon previous similar experience where no corrosion where observed.
| 02SL - Stations (LUL) | Cxxx-NCR-001353 | NCR | L- AP2: __ hoses blocked |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-11-15 | 2017-11-08 12:55 | -7 | 2016-09-19 09:29 | Tunnelling - Tunnelling General | 1000 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | • On 17/09/16 and 26/01/17 while flushing the hoses in AP2 Portal the following hoses have been found blocked: AP2 Block 2 - Box 1 - East side: one hose blocked ( transparent ) AP2 Block 4 - Box 2 - East side: two hoses blocked ( red and transparent ) AP2 Block 4 - Box 1 - West side: two hoses blocked ( both green ) AP2 Block 4 - Box 2 - West side: one hose blocked ( black ) AP2 Block 5 - Box 2 - East side: two hoses blocked ( red and transparent) AP2 Block 5 - Box 2 - West side: one hose blocked ( red ) AP2 Block 6 - Box 1 - East / south side: one hose blocked ( transparent ) AP2 Block 6 - Box 2 - East / south side: one hose blocked ( transparent ) AP2 Block 6 - Box 4 - West / north side: one hose blocked ( transparent ) AP2 Block 7 - Box 1 - East / south side: one hose blocked ( transparent ) AP2 Block 7 - Box 2 - East / south side: 5 hoses blocked ( two red and three transparent ) AP2 Block 7 - Box 1 - West / north side: one hose blocked ( green ) AP2 Block 7 - Box 2 - North side: 6 hoses blocked ( two red, three transparent and one black ) AP2 Portal - Box 1 - South side: 4 hoses blocked (2 blues and 2 greens) AP2 Portal - Box 2 - South side: 1 hose blocked (blue) AP2 Portal - Box 1 - North side: 4 hoses blocked (2 blue and 2 greens ) AP2 Portal - Box 2 - North side: 3 hoses blocked (2 blue and one yellow ) Refer to Att.A for the AP2 flushing records Please disregards Att.01 and Att.02, all AP2 flushing records are now available for review in Att.A • During re-injectable tube schematics preparation, it was found out that 8 termination boxes survey were missing: - 2 boxes in Block 4 - 4 boxes in Block 5 - 2 boxes in Block 6 Refer to Att.B for the AP2 Termination boxes survey
| 02SL - Stations (LUL) | Cxxx-NCR-001354 | NCR | L - AP10a: Cracks in Lintel across top of headwall |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-07-30 | 2017-07-19 13:18 | -11 | 2017-03-22 08:59 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • On 11/07/16 during routine inspection, cracks in lintel across top of headwall have been found • This is confirmed in Att.01 photo
| 02SL - Stations (LUL) | Cxxx-NCR-001355 | NCR | W - PTW-W Block 22: Failure of PP fibres fresh test - CR2854 |  | Contr | __M |  |  | 2016-09-03 | 2016-10-02 17:30 | 29 | 2016-07-05 09:14 | Tunnelling - Linings - In-situ Concrete | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | • Sample CR2854 taken during the cast of invert - PTW-West block 22 at Whitechapel site fail (0.7kg/m3) to comply with min 0.8kg/m3 of PP fibre content for Mix Invert C32/40 45kg 1kg PP – mix design 1kg/m3. • Refer to Att.01 for the PP fibres fresh tests results • After investigation it has been found out that the mix used was incorrectly recorded in the pour records ( Att.02). • Mix used in sample C4782 ( batch ticket No 33 590 ) is invert mix without fibres and not Invert 1kg PP as shown in the Whitechapel batch logs ( Att.03 ). • Shift repors have been also added to demonstrate that no wing walls ( Invert 1kg PP) have been poured on the 02/06/16 NS. Only the PTW-W invert • The C32/40 45kg 1 kg PP WHI summary has been revised and sample C4782 removed ( Att.04 )
| 02SL - Stations (LUL) | Cxxx-NCR-001356 | NCR | W - CP3: __ hoses blocked in the invert |  | Contr | __M |  |  | 2016-09-04 | 2016-09-07 16:00 | 3 | 2016-07-06 10:54 | Tunnelling - Linings - In-situ Concrete | 1000 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | On 14/06/16 DS while flushing the hoses in CP3 the following hoses have been found blocked: Block 1 - Box 1 - Left Hand Side ( EP2 side ): 7 hoses blocked (3 black, 1 green, 1 red and 2 white ) Block 1 - Box 1 - Right Hand Side: 4 hoses blocked (1 black, 1 green, 1 red and 1 white ) Block 2 - Box 1 - Left Hand Side ( EP2 side ): 2 hoses blocked ( 1 black and 1 white ) Block 2 - Box 1 - Right Hand Side: 1 hose blocked ( 1 Blue ) Block 3 - Box 1 - Left Hand Side ( EP2 side ): 1 hose blocked ( 1 white ) Block 3 - Box 2 - Left Hand Side: 3 hoses blocked ( 1 black, 1 white and 1 yellow ) Block 3 - Box 2 - Right Hand Side: 3 hoses blocked ( 2 white and 1 yellow) Block 4 - Box 2 - Left Hand Side ( EP2 side ): 3 hoses blocked ( 2 black and 1 white ) Block 4 - Box 1 - Right Hand Side: 1 hose blocked ( 1 Blue ) Block 4 - Box 2 - Right Hand Side: 4 hoses blocked ( 3 Blue, 1 black and 1 white ) Block 5 - Box 1 - Left Hand Side ( EP2 side ): 2 hoses blocked ( 1 white and 1 yellow ) Block 5 - Box 1 - Right Hand Side: 2 hoses blocked ( 1 Blue and 1 black ) Block 6 - Box 1 - Left Hand Side ( EP2 side ): 4 hoses blocked ( 3 blue and 1 yellow ) Block 6 - Box 1 - Right Hand Side: 2 hoses blocked ( 2 white ) Refer to Att.01 for the CP3 flushing records and schematics
| 02SL - Stations (LUL) | Cxxx-NCR-001357 | NCR | L- VD1 SL : Missing tests and documentation. |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-07-13 | 2017-07-21 12:30 | 8 | 2017-06-26 09:09 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Cxxx-__M-C4-LLG-C101-50185 Deliverable Records for VD1 Regulation Layer, Secondary Lining & Fireproofing Layer - L038: 1) Regulation Layer: ITP Item C4 Missing Hammer Tapping Check Sheet (__ Form D3-80) between chainage 5 – 35 for the crown 2) Secondary Lining – First Layer: ITP Item C4 Missing Hammer Tapping Check Sheet (__ Form D3-80) between chainage 6 – 34 for the crown and for chainage 7 in the invert 3) Secondary Lining – First Layer: ITP Item 5.6 Missing robot output rate between chainage 10 – 35 4) Secondary Lining – First Layer: ITP Item 5.7 Missing accelerator dosage between chainage 10 – 14 5) Secondary Lining – Second Layer: ITP Item C4 Missing Hammer Tapping Check Sheet (__ Form D3-80) for chainage 35 in the crown and between chainage 25 – 35 for the invert 6) Secondary Lining – Second Layer: ITP Item 5.6 Missing robot output rate between chainage 5 – 6 & 34 – 35 7) Secondary Lining – Second Layer: ITP Item 5.7 Missing accelerator dosage between chainage 34 – 35 8) Fireproofing Layer: ITP Item C4 Hammer tapping done less than 72 hours after spraying between chainage 32 – 35. See Att05. 9) Fireproofing Layer: ITP Item 5.6 Missing robot output rate between chainage 20 – 22 & 32 – 35 10) Fireproofing Layer: ITP Item 5.7 Missing accelerator dosage between chainage 20 – 22 & 32 – 35
| 02SL - Stations (LUL) | Cxxx-NCR-001358 | NCR | L- VD2- Secondary Lining Missing Documents |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-07-20 | 2017-07-21 12:59 | 1 | 2017-07-06 14:15 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | • Cxxx-__M-C4-LLG-C101-50134 Deliverable Records for VD2 Regulation Layer, Secondary Lining, Fireproofing - Package No. L040 1) Regulation Layer- ITP item 2.6 Missing Hammer Testing Checksheet (__ Form D3-80) for AP1 Regulation Layer Invert, Ch. 5.002 to 7.158. 2) Secondary 1st Layer - ITP item C4 Missing Hammer Testing Checksheet (__ Form D3-80) for AP1 Secondary 1st layer Invert, Ch. 5.002 to 7.158. 3) Secondary 1st Layer - ITP item C1 & C2 VD2 Secondary 1st Layer, Ch. 5 to 7 - Early strength tests missed at 1 hour. See Att01. 4) Fireproofing- ITP item 6.15 No information on galvanized steel boxes for re-injectable tubes available 5) ITP item D7 – Flexural Strength No testing of flexural strength carried out for AP1 in August 2014. 6) ITP item D8 – Concrete drying shrinkage No testing of Concrete drying shrinkage carried out for AP1 in August 2014. No testing of Concrete drying shrinkage carried out for AP1, mix P1 in November 2015.
| 02SL - Stations (LUL) | Cxxx-NCR-001359 | NCR | L- AP5 SL: Missing tests and documentation |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-08-17 | 2017-08-17 12:17 | 0 | 2017-08-04 09:18 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | • Cxxx-__M-C4-LLG-C101-50140 Deliverables Records for AP5 Regulating Layer, Secondary Lining and Fireproofing ( Package L024 ): - Missing Permit to cover ( __ Form D3-93 ) AP5-CH5 Ch 102 to 130 crown - Missing Permit to cover ( __ Form D3-93 ) AP5-CH5 Ch 136 to 149 crown
| 02SL - Stations (LUL) | Cxxx-NCR-001360 | NCR | L- AP10a+AP10b - missing documents |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-08-17 | 2017-08-17 13:24 | 0 | 2017-08-04 09:23 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | • Cxxx-__M-C4-LLG-C101-50224 Deliverable Records for AP10a __ Spraye Waterproofing membrane - L032: 1) __: ITP item 1.2, 1.5 and 2.1 Missing Acceptance of Substrate for Waterproofing Layer ( __ Form D3-81 ) from AP10a ch 10 to 10.538 2) __: ITP item 1.3, 1.4, 2.1 and 2.2 Missing Waterproofing Application Report ( __ Form D3-98 ) from AP10a ch 10 to 10.538 Layer 1 and 2 3) __: ITP item 1.3, 1.4, 2.1 and 2.2 Missing Waterproofing Application Report ( __ Form D3-98 ) from AP10a ch 7 to 10.538 Layer 3 3) __: ITP item 2.6 and 2.8 Missing Wet Film Thickness Test ( __ Form D3-101 ) from AP10a ch 7 to 10.538 Layer 3 4) __: ITP item 3.1 Missing Tube Installation Check Sheet ( __ Form D3-82 ) from AP10a ch 4 to 10.538 5) __: ITP item 4.1 Missing Permit to Cover __ Membrane ( __ Form D3-131 ) from AP10a ch 3.676 to 10.538 • Cxxx-__M-C4-LLG-C101-50192 Deliverable Records for AP10b Regulating Layer, Secondary Lining and Fireproofing Layer - L032: 6) Secondary lining 1st layer: ITP item 5.2, 5.3, 5.4, 5.8 and 5.10 Missing Shotcrete Placement Checksheet ( __ Form D3-86 ) from AP10b ch 18 to 19 7) Secondary lining 1st layer: ITP item 5.6 and 5.7 Missing SCL spraying setting: Robot Output Rate and Accelerator from AP10b ch 5 to 9, ch 15 to 17 and ch 19 to 21.180 ( only Robot Output Rate )
| 02SL - Stations (LUL) | Cxxx-NCR-001361 | NCR | W - VA5 SL Missing Test and documentation |  | Contr | __M |  |  | 2017-04-28 | 2017-05-24 15:20 | 26 | 2017-02-27 16:23 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | • Cxxx-__M-C4-LLG-D061-50177 Deliverable Records for VA5 Sprayed Waterproofing, Secondary 1st Layer and Fireproofing Layer Reader Layer VA5 Ch.25-37.5: No Secondary Lining Placement Checksheet (__ Form D3-86) for the LHS-Reader Layer • Cxxx-__M-C4-LLG-D061-50176 Deliverable Records for VA5 Regulation Layer, Sheet Membrane and Cast In-Situ Cast In-Situ Invert Layer VA5 Blocks 2 and 4: Compaction not registered on the Secondary Lining Pour Checksheet (__ Form D3-84). Different revisions of check sheets have been used (See Att01.).
| 02SL - Stations (LUL) | Cxxx-NCR-001362 | NCR | L - VD4 SL: Missing tests and/or documentation |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-09-03 | 2016-09-07 11:53 | 4 | 2016-07-05 15:13 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | • On 07/06/16 during CRL surveillance on sheet membrane installation the VD4 Block 11 Form D3-94 ( Sheet Membrane installation ) has been reviewed and found signed off without any evidence that the double seam and single seam where checked before the protective membrane was applied. • Refer to Att.01 for the VD4 Block 11 Form D3-94 Sheet Membrane installation checksheet • No D3-132 REPAIR checksheet was available for review to demonstrate that the BA anchors installed in VD4 have been mechanically tested before the protective membrane was applied
| 02SL - Stations (LUL) | Cxxx-NCR-001363 | NCR | L-LCWb - Non‐Stainless Steel temporary fixings |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-10-27 | 2017-01-18 18:19 | 83 | 2016-07-19 23:22 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | L- 05/07/2016 - Shift 2 - DS In LCWb, there is a portal at the end which is being held in place by mild steel temporary fixings. Normally the steel fixings are removed once the pour has been conducted for a portal however in this instance they have been casted in. This can be seen in Att.01. The temporary fixings go all the way around from wing wall to crown on both sides within the D-wall and Tunnel.
| 02SL - Stations (LUL) | Cxxx-NCR-001364 | NCR | L- LCWb - Shutter Slip |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-10-14 | 2016-08-09 14:34 | -66 | 2016-07-06 15:43 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | L- 04/07/2016 - Shift 2 - DS During a site visit, it was noticed that the shutter had slipped by about 100mm in the crown (1 O'clock - westside). The shutter appears to have slipped in the area highlighter in red in Att.02/Att.02a
| 02SL - Stations (LUL) | Cxxx-NCR-001365 | NCR | L- LCWb - Cracks in Portal |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-01-31 | 2017-05-24 16:21 | 113 | 2016-07-06 16:33 | Tunnelling - Tunnelling General | 2000 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A - 04/07/2016 - Shift 2 - DS During a walk through of LCWb , it was noticed that there were cracks in crown of the portal. There were 3 cracks that were noticed and details as below; Crack 1 - Length -1.55m , Crack Opening 0.4 - 0.5mm Crack 2 - length - 1.02m , Crack Opening 0.2 - 0.3mm Crack 3 - Length 0.94 , Crack opening 0.1 - 0.3mm This can be seen in Att.01, Att.03 and Att.04 B - 05/07/2016 - DS A thin layer of concrete has been found overspilling onto the shotcrete in LCWb near the portal ( around chainage 150 - between 7 to 5'oclock ) This has been found on the 05/07/16. Photos can be seen in Att.05
| 02SL - Stations (LUL) | Cxxx-NCR-001366 | NCR | L - LCW Violation of the Permit to Cover Process (remaining open NCRs) |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-09-04 | 2016-07-19 14:32 | -47 | 2016-07-06 14:51 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | • Permit to Cover primary lining has been sign off in LCW tunnel with comments from Cxxx on open NCRs 1004 and NCR 1054 still not addressed. • Secondary lining spray has started without CRL/Cxxx comments been addressed
| 02SL - Stations (LUL) | Cxxx-NCR-001367 | NCR | W - PTW-W Block 10 - 26 ( Ch -7.5 - 201.6) __ hoses blocked |  | Contr | __M |  |  | 2017-07-23 | 2017-06-15 08:12 | -38 | 2016-07-06 16:26 | Tunnelling - Linings - In-situ Concrete | 1000 |  | Equipment Breakdown | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • While flushing the __ hoses in PTW-W the following hoses have been found blocked: Block 10 - Box 1 - Track side: 1 hose blocked ( yellow ) Block 10 - Box 2 - Track side: 1 hose blocked ( blue ) Block 10 - Box 1 - Platform side: 1 hose blocked ( yellow ) Block 10 - Box 2 - Platform side: 1 hose blocked ( blue ) Block 10 - Box 2 - Platform side: 1 hose blocked ( transparent ) Block 11 - Box 1 - Track side: 2 hoses blocked ( red and transparent ) Block 11 - Box 2 - Track side: 1 hose blocked ( transparent ) Block 11 - Box 1 - Platform side: 1 hose blocked ( red ) Block 12 - Box 2 - Track side: 1 hose blocked ( transparent ) Block 12 - Box 3 - Track side: 1 hose blocked ( transparent ) Block 13 - Box 1 - Platform side: 1 hose blocked ( transparent ) Block 13 - Box 2 - Platform side: 1 hose blocked ( transparent ) Block 18 - Box 1 - Track side: 1 hose blocked ( red ) Block 18 - Box 1 - Platform side : 1 hose blocked ( red ) Block 19 - Box 1 - Track side: 1 hose blocked ( transparent ) Block 19 - Box 2 - Track side: 1 hose blocked ( transparent ) Block 20 - Box 1 - Track side: 1 hose blocked ( red ) Block 20 - Box 3 - Track side: 1 hose blocked ( yellow ) Block 20 - Box 4 - Track side: 1 hose blocked ( blue ) Block 20 - Box 1 - Platform side : 2 hoses blocked ( 1 red and 1 yellow ) Block 20 - Box 2 - Platform side : 1 hose blocked ( 1 blue ) Block 21 - Box 1 - Track side : 2 hoses blocked ( 1 black and 1 transparent ) Block 21 - Box 2 - Track side : 2 hoses blocked ( 1 green and 1 transparent ) Block 21 - Box 1 - Platform side : 1 hose blocked ( 1 transparent ) Block 21 - Box 2 - Platform side : 1 hose blocked ( 1 transparent ) Block 22 - Box 1 - Track side: 1 hose blocked ( transparent ) Block 22 - Box 2 - Track side: 2 hoses blocked ( 1 transparent and 1 red ) Block 22 - Box 1 - Track side: 2 hoses blocked ( red and yellow ) Block 22 - Box 2 - Track side: 3 hoses blocked ( red and 2 blue) Block 23 - Box 1 - Left hand side: 3 hoses blocked ( 2 yellow and 1 red ) Block 23 - Box 2 - Left hand side: 2 hoses blocked ( both blue ) Block 23 - Box 3 - Left hand side: 2 hoses blocked ( both yellow ) Block 23 - Box 4 - Left hand side: 2 hoses blocked ( both blue ) Block 23 - Box 1 - Right hand side: 1 hose blocked ( red ) Block 24 - Box 1 - Left Hand Side: 2 hoses blocked ( 1 red and 1 yellow ) Block 24 - Box 2 - Left Hand Side: 1 hose blocked ( 1 blue ) Block 24 - Box 3 - Left Hand Side: 2 hoses blocked ( both black ) Block 24 - Box 4 - Left Hand Side: 2 hoses blocked ( both green ) Block 24 - Box 1 - Right Hand Side: 5 hoses blocked ( 2 yellow, 1 black and 1 red ) Block 24 - Box 2 - Right Hand Side: 3 hose blocked ( 1 green and 2 blue ) Block 24 - Box 3 - Right Hand Side: 4 hose blocked ( 2 black and 2 yellow ) Block 24 - Box 4 - Right Hand Side: 4 hoses blocked ( 2 green and 2 blue ) • Flushing records and schematics can be seen in Att.04 Please note that Att.01 and Att.02 are now superseded by Att.04
| 02SL - Stations (LUL) | Cxxx-NCR-001368 | NCR | L- AP6 - Opening Underthickness |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-04-22 | 2017-04-22 11:13 | 0 | 2017-01-12 11:34 | Tunnelling - Linings - Sprayed Concrete | 4000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | L-06/07/2016 - DS When viewing the scans in AP6 opening ( AP6 Ch 8 ), some underthickness have been found in the crown from 1’oclock to 8’oclock. They are highlighted in red in Att.01 scan Worst case is between 50mm and 60mm instead of 100mm and is located at 11 o'clock Profile scans can be seen in Att.02 and photo of underthickness in Att.03
| 02SL - Stations (LUL) | Cxxx-NCR-001370 | NCR | W - May 16: Low Residual Flexural strength of Mix P1 45kg 2kg PP - Beam Testing CR2826 |  | Contr | __M |  |  | 2016-10-04 | 2016-11-17 10:22 | 44 | 2016-08-05 10:38 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | WHI spray in moulds beam set CR2826 from May 2016 (27/05/16) has achieved too low individual D3 result of beam A,B - S1.1and D – S1.2 at 28 days with average for set of 4 beams - S1.3 Refer to Att.01 for the test results
| 02SL - Stations (LUL) | Cxxx-NCR-001371 | NCR | L - Moorgate Box Phase 3: Grout density, viscosity and compressive strength for Mixes P, A6 and Trial did not conform to ITP specified range |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-10-28 | 2016-07-27 07:21 | -93 | 2016-07-25 10:31 | Geotechnical Engineering - Compensation Grouting | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 1. Moorgate Box Phase 3: the grout density results for Mix P dated 21/07/2015 – mixes 27, 29 and 30 were out of ITP tolerance. See att01. 2. Moorgate Box Phase 3: the results for all Mix A6 Stable compressive strength, with exception to Cube numbers: C4006, C4012, C4047 and Cxxx9, exceed the 8.0N/mm2 tolerance. See att02. 3. Moorgate Box Phase 3: the results for Trial Mix; density, viscosity and compressive strength were out of ITP tolerance. See att03 and att04.
| 02SL - Stations (LUL) | Cxxx-NCR-001372 | NCR | W - DSS / PTE-W Block 22: Sheet membrane damaged |  | Contr | __M |  |  | 2017-04-30 | 2017-05-17 14:56 | 17 | 2016-07-26 13:17 | Tunnelling - Linings - In-situ Concrete | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • On the 11/07/16 LHS invert of the connection detail has been found damaged. Sheet membrane in the PTE-W Block 22 near the DSS head wall between 7 and 8 o'clock has been found damaged. • Refer to Att.01 for photos of the defect
| 02SL - Stations (LUL) | Cxxx-NCR-001373 | NCR | L - June 16: Low Residual Flexural strength of Mix P1 45kg - Beam Testing CR2893 |  | Contr | __M |  |  | 2017-06-15 | 2017-04-09 15:09 | -67 | 2016-08-05 10:44 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | • FIN spray in moulds beam set CR2893 from June 2016 (10/06/16) has achieved too low individual D3 result of beams A – S1.0, B - S1.2 and D – S1.1 at 28 days with average for set of 4 beams - S1.2, • CR2893 test results can be seen in Att.01 • Individual deflection test results can be seen in Att.02 and photos in Att.03 • Areas affected are all tunnels with P1 Mix sprayed from the 27/05/16 to the 24/06/16. This includes AP6 secondary lining, LCWa/b secondary lining, AP9 primary lining ( enlargement ), ES3 Pilot and AP2 primary lining. Refer to Att.04 for the pour records.
| 02SL - Stations (LUL) | Cxxx-NCR-001374 | NCR | W - ES1 Block 10: Void left in the surface |  | Contr | __M |  |  | 2016-12-25 | 2016-10-18 15:59 | -68 | 2016-07-27 13:23 | Tunnelling - Linings - In-situ Concrete | 2000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | On the 19/07/16 after removal of the shutter in ES1 Block 10, voids have been found in the invert. Area affected is 1320 x 1160 x 90mm in the invert at 6 o'clock
| 02SL - Stations (LUL) | Cxxx-NCR-001375 | NCR | L - LCE Block 29 North Wall: Void between wing wall and SL 1st layer |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-08-18 | 2017-08-12 12:41 | -6 | 2016-07-29 12:20 | Tunnelling - Linings - In-situ Concrete | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • On the 10/07/16 void between the cast in-situ wing walls ( North Wall ) and the SL 1st layer has been found in LCE Block 29. • Refer for Att.01 for photo of the void
| 02SL - Stations (LUL) | Cxxx-NCR-001376 | NCR | L - VD7 and AP5: Violation of the Permit to Cover Process (remaining open NCRs) |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-12-27 | 2016-12-14 18:10 | -13 | 2016-07-29 12:44 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | • On the 17/11/14 VD7 Adv 1 to Adv 9 Permit to cover primary lining has been sign off with NCR 940 ( VD7 Enl Adv 5: Localised insufficient thickness ) still open and not referenced in the checksheet. • In the same checksheet Item 2 "Is the Primary Lining within Tolerances?" was also ticked as Yes. • Refer to Att.01 for the VD7 Adv 1 to Adv 9 Permit to cover primary lining • On the 12/08/15 AP5 Ch 147 to 150 Permit to cover primary lining has been sign off with NCR 1103 ( AP5 - Primary Lining Under thickness ) still open and not referenced in the checksheet • In the same checksheet Item 2 "Is the Primary Lining within Tolerances?" was also ticked as Yes. • Refer to Att.02 for the AP5 Ch 147 to 150 Permit to cover primary lining • LCWa permit to cover primary lining has also been signed off with two NCRs Cxxx-NCR-001054 ( LCWa - Underthickness in the primary lining) and Cxxx-NCR-001004 ( LCWa - Non conforming cores in the primary lining) still open.
| 02SL - Stations (LUL) | Cxxx-NCR-001377 | NCR | L - Moorgate box: Slab damaged |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-02-28 | 2017-02-14 16:26 | -14 | 2016-08-03 16:06 | Tunnelling - Linings - In-situ Concrete | 3000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | • On 22/07/16 DS During Moorgate box condition survey site visit to handover the area to Cxxx, one area of the slab has been found damaged (pot holes) between VD5 and LCWa. • Refer to Att.01 for photos of the slab damaged • Area affected is between VD5 and LCWa approximately 5 m x 3 m x 0.7 m. Picture with more details can be seen in Att.02
| 02SL - Stations (LUL) | Cxxx-NCR-001378 | NCR | W - WB CAV Pour 2: Scabling preparation not done in LCW and Crossover |  | Contr | __M |  |  | 2016-10-04 | 2016-10-02 17:20 | -2 | 2016-08-05 13:33 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | As raised in 05/08/16 SRG, it is believed that green cutting was not done on the surface of Pour 2 in WB CAV and therefore it will be very difficult to prepare the construction joint especially in LCE and Crossover due to lack of access. Shutter is now installed in WB cav and workers cannot acccess safely to the LCE and Crossover areas that needs to be prepared for the pour 2
| 02SL - Stations (LUL) | Cxxx-NCR-001379 | NCR | L - CP2: Fire proofing profile outside tolerances |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-10-28 | 2016-12-16 10:13 | 49 | 2016-08-08 10:11 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • On 29/02/2016, after review of the fire proofing profile in CP2, areas from Ch4 to 8 below platform level have been found outside the CTRL +100mm profile ( blue areas ) and encroaching the CTRL zero line ( red areas ) • They are highlighted in blue and in red on Att.01 scan. Areas concerned by the defect are localised, below 2%.
| 02SL - Stations (LUL) | Cxxx-NCR-001380 | NCR | L - LCWa: SCL Overspray onto __ |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-11-25 | 2017-03-01 19:03 | 96 | 2016-08-08 11:03 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | • On 22/07/16 Whilst spraying Secondary 2nd near the portal opening on the LHS, there was a bit of overspray of SCL onto the __. Area affected 4m x 0.5m from 7 to 11 o'clock at chainage 182. Shotcrete patch is around 50mm in depth. • Refer to Att.01 for photo of the defect.
| 02SL - Stations (LUL) | Cxxx-NCR-001381 | NCR | L - AP5: Fire proofing profile outside tolerances |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-10-22 | 2017-03-02 10:38 | 131 | 2016-08-08 15:33 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • On 22/07/2016, after review of the fire proofing profile scans in AP5-CH5, areas from Ch122 to 131 have been found encroaching the CTRL zero line ( red areas ) and some other areas found outside the CTRL +100mm profile ( blue areas ) • They are highlighted in blue and in red on Att.01 scan. Areas concerned by the defect are localised, below 2%.
| 02SL - Stations (LUL) | Cxxx-NCR-001382 | NCR | L - AP9 Dewatering: Well position outside specified tolerance |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-09-30 | 2016-10-13 10:09 | 13 | 2016-08-08 16:13 | Geotechnical Engineering - Dewatering | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Counterfeit Items | Completed |  | The AP9 Dewatering boreholes were surveyed and plotted against tolerance lines. They were all within tolerance in plan; however, 1 out of 15 was out of tolerance vertically (PA1-W_15) by 0.13m downwards at 12m. See att01. Borehole PA1-W_15 alignment survey
| 02SL - Stations (LUL) | Cxxx-NCR-001383 | NCR | W - ES1 Block 10: Starter bars bented |  | Contr | __M |  |  | 2017-01-10 | 2016-11-09 11:44 | -62 | 2016-08-11 14:51 | Tunnelling - Linings - In-situ Concrete | 4874.34 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | • On 08/08/16 invert ES1 block 10 starter bars were in the way of the membrane installation and the site team bent these down out of the way for a better access to the sheet membrane. • Refer to Att.01 for photos of the B16 starter bars bented
| 02SL - Stations (LUL) | Cxxx-NCR-001384 | NCR | L - VD5: Fire proofing profile outside tolerances |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-11-04 | 2017-05-24 08:20 | 201 | 2016-08-09 09:51 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • On the 17/07/2016 DS, after review of the fire proofing profile scans in VD5 some areas from Ch3 to 22 have been found outside the CTRL or CTRL +100mm profile. • They are highlighted in red ( tight – above the CTRL profile ) and blue ( big area – outside the CTRL + 100mm ) in Att.01 scans.
| 02SL - Stations (LUL) | Cxxx-NCR-001385 | NCR | W - PTE-W Ch85-97: SL 1st layer not sprayed as per RFI 987 |  | Contr | __M |  |  | 2017-01-11 | 2016-10-18 15:38 | -85 | 2016-08-12 15:13 | Tunnelling - Linings - Sprayed Concrete | 2500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | • On 09/08/16 NS PTE-W Ch85-87 and Ch 91-97 SL 1st layer have been found not sprayed as per RFI 987. • RFI 987 states: “Spraying 1st Layer secondary lining where necessary up to axis”. During the nightshift commencing 09/08/2016, construction team sprayed secondary lining first layer up to the shoulder of PTE-W, not the axis as specified in RFI 987. • This has therefore led to a section of sprayed concrete lining hanging in the shoulder without the full ring being formed therefore increasing the risk of debonding.
| 02SL - Stations (LUL) | Cxxx-NCR-001386 | NCR | L - CH5 Headwall: Fireproofing layer encroaching the CRTL ZERO |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-10-11 | 2017-02-27 11:25 | 139 | 2016-08-12 09:28 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | • On 25/07/2016, after review of the fire proofing profile scans in CH5, areas in the left knee, right knee, invert and crown of the CH5 headwall have been found encroaching the CTRL profile ( red areas ) • Some tight spots are up to 30mm, mainly on the edges (junction with the profile), they highlighted in red on Att.01 scans.
| 02SL - Stations (LUL) | Cxxx-NCR-001387 | NCR | W - CP3/PTE: Fire proofing tigh spot in the junction crown |  | Contr | __M |  |  | 2017-04-28 | 2017-03-28 08:31 | -31 | 2016-08-16 08:08 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | • On 09/06/2016, after review of the fire proofing profile 3d scan in CP3/PTE junction, two areas in CP3 crown near PTE-E have been found encroaching for 11mm and 17mm the CTRL zero line. See Att.01. • The areas have been marked on the scans - see Att.02. • Areas concerned by the defect are localised, below 1%.
| 02SL - Stations (LUL) | Cxxx-NCR-001388 | NCR | L - AP2 ch152-154: Incorrect fireproofing mix used ( P2 instead of P1 ) |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-02-28 | 2016-12-21 11:23 | -69 | 2016-08-19 10:22 | Tunnelling - Linings - Sprayed Concrete | 35000 |  | Supervision/Management | Use As-Is | 2 (6-60k) | Complete | Management Problem - Inadequate supervision | Completed |  | On 18/08/16 NS AP2 ch 152-154 was sprayed with P2 fireproofing mix rather than P1 fireproofing. Due to a failure on previous shift a small area in Ch154 to 156 arch was not finished and has been also sprayed with P2 fireproofing mix Area sprayed with incorrect mix can be seen in Att.06 profile scan.
| 02SL - Stations (LUL) | Cxxx-NCR-001389 | NCR | L - Moorgate Shaft Liner Wall B Pour 13: Small voids between top of the pour and ring beam |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-03-30 | 2017-02-22 16:15 | -36 | 2016-08-19 15:11 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | After pouring of Moorgate Shaft Liner Wall B (Pour 13), it was noted that the concrete had not compacted against the underside of the ring beam above resulting in small voids between the top of the pour and ring beam above AP5 (RHS) and LCWb (LHS), see att01 and 02. As this had been anticipated, contact grouting tubes had been installed along the underside of the ring beam. These contact grouting pipes were grouted. __ trimmed back and cleaned any over spill grout. Following this, an inspection was carried out to find pour compaction and crumbling grout across the joint. Further to this, an attempt to repair the joint was carried out above LCWb. This had not been agreed and has not filled the voids.
| 02SL - Stations (LUL) | Cxxx-NCR-001390 | NCR | W - PTE-W / DSS connection: exposed rebar link |  | Contr | __M |  |  | 2016-10-21 | 2016-12-12 16:39 | 52 | 2016-08-22 14:31 | Tunnelling - Linings - In-situ Concrete | 2000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | • On 22/08/16 after casting the connection and stripping the stop end one of the rebar links just above axis on the shaft side was left exposed with cover to face of concrete less than 10mm. This happen in PTE-W / DSS connection at chainage 160 LHS ( shaft side ), refer to Att.01 for photo of the exposed rebar
| 02SL - Stations (LUL) | Cxxx-NCR-001391 | NCR | L - Moorgate Shaft Liner Wall A West Side: End of __ hose can not be located and Termination box not installed |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-03-31 | 2017-02-22 15:51 | -37 | 2016-08-24 12:49 | Structural Engineering - Structural Engineering - General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Whilst Pouring 1 – Moorgate Shaft Liner Wall A, wall was not poured as one (see Cxxx-NCR-001037). An FCD was then raised, Cxxx-FCD-691 – Joints to be prepared and __ hose to be installed. Box out on west side was not installed. Upon inspection, end of __ hose cannot be located. Therefore, we cannot install termination box on west side of joint.
| 02SL - Stations (LUL) | Cxxx-NCR-001392 | NCR | L - VD4 PL: Missing tests and documentation |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-08-18 | 2017-08-17 12:57 | -1 | 2016-09-13 10:18 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | During Cxxx-__M-C4-LLG-C101-50168 Deliverable Records for VD4 Primary Lining Adv 1-43 and Trumpets 1-2 Backfilling - Package No L041 preparation, following has been found missing: 1. VD4 Primary Lining – Missing early strength tests: - Advance 4: early strength tests missed at 6hr - Advance 4 L-Bars: early strength tests missed - Advance 5 Enlarg. early strength tests missed - Advance 10 early strength tests missed at 1hr and 3hours - Advance 14 early strength tests missed - Advance 22 early strength tests missed - Advance 26 early strength tests missed at 6 hours - Advance 29 early strength tests missed - Advance 32 early strength tests missed - Advance 36 early strength tests missed at 1 and 3 hours - Advance 42 early strength tests missed - Trumpet 1 Bulking early strength tests missed See Att.A: VD4 PL Missing early strength tests 2. VD4 Primary Lining – Missing Rebound Test: - No rebound test carried out at LIS in April 2016 3. VD4 Primary Lining – Missing workability/flow tests and temperature of shotcrete / ambient temperature of workface: - Advance 4 initial no flow test and temperature recorded - Advance 31 initial ( Pocket 1 ) no flow test and temperature recorded - Advance 32 initial ( Pocket 3 ) no flow test and temperature recorded - Advance 34 initial ( Pocket 2 ) no flow test and temperature recorded See Att.B: VD4 PL Missing flow tests 4. VD4 Primary Lining – Missing excavation profile - Advance 6 (before enlargement) no excavation profile See Att.C: VD4 PL Missing excavation profile 5. VD4 Primary Lining – Encroachment of the profile: - Advance 4 Enlarg. encroachment of the profile by max 68mm - Advance 5 Enlarg. encroachment of the profile by max 14mm - Advance 6. (before enlargement) encroachment of the profile by max 48mm and missing thickness record - Advance 6 Enlarg. encroachment of the profile by max 23mm - Advance 25 Enlarg. encroachment of the profile by max 16mm - Advance 31 Enlarg. encroachment of the profile by max 13mm See Att.D: VD4 PL Encroachment of the profile
| 02SL - Stations (LUL) | Cxxx-NCR-001393 | NCR | L - CP3a and CP4a SL: Missing tests and documentation |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-11-02 | 2017-11-06 16:15 | 4 | 2017-10-19 09:29 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Cxxx-__M-C4-LLG-C101-50170 Deliverable Records for LIV CP3a and CP4a Secondary Lining - Package No L012 1) Secondary 2nd – ITP item 5.12 Missing Hammer Tapping Checksheet (__ Form D3‐80) for CP3a Second 2nd Block 2 (Ch. 8-14).
| 02SL - Stations (LUL) | Cxxx-NCR-001394 | NCR | L - AP9 Pipe Arch: TAM position, Grout viscosity, density and compressive strength outiside of specified tolerance |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-12-23 | 2016-10-17 14:04 | -67 | 2016-09-02 08:48 | Geotechnical Engineering - Compensation Grouting | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | 1. TAM positions outside specified tolerance. The boreholes were surveyed and plotted against tolerance lines. 5 out of 110 (PA2: 4, 13, 26, 30 and PA3:12) were out of tolerance in plan and 17 out of 110 (PA1: 8, 9, 10, 11, 12, 13, 14, 15, 16, 17, 18, 19, 23, 24 and PA3: 6, 16, 30) were out of tolerance vertically. See att01. In plan, the maximum deviation value recorded is 140mm outside the tolerated envelope for PA3-12; vertically, the maximum deviation value recorded is 350mm outside the tolerated envelope for PA1-16. 2. Grout viscosity and density for Mix A1, A6 and S2 did not conform to ITP specified range Below are the numbers of occurrences that are out of tolerance over the total number of test. - Mix A1 Viscosity: 14/140 - Mix A6 Viscosity: 53/155 - Mix A6 Density: 1/155 - Mix S2 Density: 4/412 See att02. 3. Compressive Strength Mix A6 Stable and Mix A1 did not conform to ITP specified The results for all Mix A6 Stable and Mix A1 compressive strength, exceeded the 4.0N/mm2 tolerance. See att03.
| 02SL - Stations (LUL) | Cxxx-NCR-001395 | NCR | W - WB Cav, EB Cav and Crossover: Non-compliant First Stage Concrete surface finish |  | Contr | __M |  |  | 2016-11-25 | 2017-01-03 12:42 | 39 | 2016-09-06 18:13 | Tunnelling - Linings - In-situ Concrete | 2500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | - A significant proportion of the first stage track concrete slabs in the WB Cavern, Crossover and EB cavern were cast with a tamped finish. The face of the Haunches in the Crossover tunnel were also cast with a U3 finish. - During a pre-handover inspection by Cxxx (who would later cast the second stage track concrete), it was noted that surfaces of the concrete were too ‘smooth’ and that the bottom section of the haunches in the crossover also required exposed aggregate. - At this point Cxxx became aware of the requirement to remove laitance on the joint between the first stage and second stage track concrete and the lower half of the haunches.
| 02SL - Stations (LUL) | Cxxx-NCR-001396 | NCR | W - WB Cavern: Catch pits and UTX out of tolerances |  | Contr | __M |  |  | 2016-11-15 | 2017-01-27 16:35 | 73 | 2016-09-16 08:17 | Tunnelling - Linings - In-situ Concrete | 1000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | • During the casting of the first stage concrete in the WB cavern, numerous Under Track Crossing ducts and drainage lines were installed. • These were set out in accordance with the drawings Cxxx-MMD-C4-DDA-CR092-01020 rev C02 and Cxxx-MMD-C4-DDJ-CR092-0002 rev C01. • Upon completion of the works the as built survey was produced and __ submitted this to CRL. • Whilst there were no specified tolerances on the UTX, the tolerance on the drainage and catch pits was defined in KK10. • Using the same tolerances for the UTX as for the Drainage there are UTX that are out of tolerance. • WB cavern cast in services as built compared to the design can be seen in Att.01.
| 02SL - Stations (LUL) | Cxxx-NCR-001397 | NCR | L - Galvanic corrosion of the suspension rods for in-ground automated inclinometer instruments |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-03-03 | 2017-02-14 15:51 | -17 | 2016-09-02 10:59 | Tunnelling - Grouting | 1000 |  | Equipment Breakdown | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | In January and February 2016 during the removal of automated inclinometers at Liverpool Street it was noted that out of 5 of the 8 instruments the material used for the suspension rods were a mixture of aluminium and stainless steel. The non conformance has occurred as the specification only states that Stainless Steel is used, though this specification only states for the housing material to be Stainless steel, this has been accepted that all elements of the IPI string should be stainless steel and not just the housing material of the sensors but the suspension rods as well. Galvanic corrosion had occurred on some of the suspension rods for instruments Cxxx IE10204, Cxxx IE11203, Cxxx IE10506, Cxxx IE10513 and Cxxx IE10514. Instruments Cxxx IE10205, Cxxx IE10507 and Cxxx IE11401 only used stainless steel suspension rods and no corrosion was noted. • Refer to Att.01 for photos of the defect • It should be noted that no mention of the material used for any rods have been found in the installation reports for the inclinometers prepared by __’s monitoring subcontractor. • It has been confirmed internally that the design on the above boreholes had been changed by __’s own decision at installation time for safety reasons, in order to reduce risk associated with manual handling during the installation (weight reduction). This decision was made based upon previous similar experience where no corrosion was observed.
| 02SL - Stations (LUL) | Cxxx-NCR-001398 | NCR | W - PTE-W/DSS Connection: Damaged waterproofing |  | Contr | __M |  |  | 2016-11-18 | 2017-01-30 11:37 | 73 | 2016-09-19 13:05 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • On September 2016 during the concrete pour the stop ends leaked extensively leading to concrete build up in the side wings and invert of Block 22 in the PTE-W tunnel. This concrete was allowed to harden and when this concrete was broken out the waterproof membrane suffered excessive damage requiring repair and re-work. • Refer to Att.01 for photos of the damaged waterproofing membrane near DSS / PTE-W cast connection
| 02SL - Stations (LUL) | Cxxx-NCR-001399 | NCR | W - PTE-W/DSS Connection: Non-conforming finish ( voids, honeycombing...) |  | Contr | __M |  |  | 2017-04-28 | 2017-04-28 13:48 | 0 | 2016-09-19 13:29 | Tunnelling - Linings - Sprayed Concrete | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | • On September 2016 during the concrete pour the stop ends leaked extensively requiring remedial works during the pour to prevent further leakage. The leakage lead to the honeycombing and voids on the surface of the shutter. • Refer to Att.01 for photos of the honeycombing / voiding
| 02SL - Stations (LUL) | Cxxx-NCR-001400 | NCR | W - WB Cav: Low Voltage UTX blocked or damaged |  | Contr | __M |  |  | 2017-01-03 | 2016-10-18 15:48 | -77 | 2016-09-19 09:02 | Tunnelling - Linings - In-situ Concrete | 4000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | • Concrete from the headwall pour has filled the LV UTX ducts in the Crossover chamber of the WB cavern. In total four UTX have been found blocked. • The four UTX blocked are L1-5, L1-6, L1-7 and L1-8 in the WB cavern • Another duct ( WC Cav H2-2 ) opposite to the bypass entrance was damaged when run over by plant. • Refer to Att.01 for location of the UTX blocked or damaged and Att.02 for some photos.
| 02SL - Stations (LUL) | Cxxx-NCR-001401 | NCR | W - EBRT/DSS: Insufficient cover to the reinforcement in the cast connection |  | Contr | __M |  |  | 2017-06-23 | 2017-06-19 14:46 | -4 | 2016-09-19 10:55 | Tunnelling - Linings - In-situ Concrete | 1000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • On September 2016 as __ set the shutter for EBRT connection to DSS it became apparent that the shutter would encroach on the steel bar reinforcement previously fixed. • After attempting to adjust the shutter it became apparent that the design of the shutter did not allow for the longitudinal fall across the opening. If it was set to the fall of the tunnel it wouldn’t encroach on the steel but would not line up with the face of the D-Wall and Liner Wall. The opposite situation was true if it was set flat. • As there was significant amount of work required to either remove the shuttering and adjust the steel or to adapt the shutter to suit the fall, it was agreed to complete a survey of the steel and shutter highlighting the areas that did not comply. This could then be used to highlight areas of low cover and remedial works be proposed, post casting. • Refer to Att.01 for additional information of the location of the defect and beamer surveys • Att.01 shows surveys taken at the worst locations and there is in total 3 no points on pages 1/2 and 3 no points on pages 3/4 that have low NF cover ( i.e. below 70mm )
| 02SL - Stations (LUL) | Cxxx-NCR-001402 | NCR | L - AP2 Opening: Portal is encroaching the CTRL zero line |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-11-03 | 2017-11-09 14:00 | 6 | 2016-09-12 14:27 | Tunnelling - Linings - In-situ Concrete | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On the 11/09/16 final lining scans of the AP2 opening ( from Ch 172.5 to 174 ) have been issue and portal found encroaching the CTRL zero line from 7 to 5 o'clock by max 12mm. Refer to Att.01 and Att.02 for the profile scans.
| 02SL - Stations (LUL) | Cxxx-NCR-001403 | NCR | L - Moorgate Box Ground Treatment - Phase 3: Forms D3-14 and D3-23 are missing |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-11-11 | 2016-11-07 16:06 | -4 | 2016-09-12 15:11 | Tunnelling - Grouting | 1500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | __ is not able to provide D3-14 Borehole Drilling Forms and D3-23 Crossrail Inspection Request Forms for phase 3 of Moorgate Box Ground Treatment.
| 02SL - Stations (LUL) | Cxxx-NCR-001404 | NCR | L – PTW Contraction joint clash with reinforcement at the following junctions with Platform Tunnel Westbound: CP1, CP3, CP3a, CP5, CP7, CP9 and VD1 |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2016-09-28 | 2017-01-30 11:40 | 124 | 2016-09-14 14:51 | Tunnelling - Linings - Sprayed Concrete | 10000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | Further to Cxxx-NCR-001264 where it was apparent that at CP3a where __ had cut contraction joints these had exposed the structural reinforcement. __ were instructed via Cxxx-SVI-00010 (dated 9/05/2016) to inspect all other contraction joints. Based on these inspections it was clear that structural steel was visible in the following contraction joints:- CP1 north CP3 north CP3a north (now injected) CP5 north CP7 north Based on RFI 997 the following were identified to be injected:- CP1 west CP3a east and west CP5 east and west CP9 east Further to Cxxx-EWN-01082 (dated 2/09/2016) on the basis that more than 50% of the inspected contraction joints within the cross passage junctions have positively identified a defect and in the absence of a complete survey the durability of the structural reinforcement can be assumed to be compromised:- CP9 north VD1 north and east It is worth noting the joint VD1 east should not have been cut in the first place as it is not shown on the drawing. Crossrail are assuming that the joints are being injected as per the repair methodology in Cxxx-NCR-001264 (or similar accepted method). Further to Cxxx-PMI-01196 (dated 6/09/2016) the agreed methodology (as proposed in Cxxx-NCR-001264 and accepted by Cxxx) is to date being undertaken on site. It is noted that is it also acceptable to use __ 4a to plug the gap instead of Masterseal 590 prior to injection of the contraction joints. Where repairs are carried out in unclad areas the plug should be hammer tapped to ensure bond of plug to SCL – e.g. CP1(W), CP9(E), VD1 (N) and VD1 (E). Refer ATT 01 - Sketch locations of Liverpool Street Platform Tunnel Westbound contraction joints requiring resin injection_14-09-2016.pdf
| 02SL - Stations (LUL) | Cxxx-NCR-001405 | NCR | W - EBRT/DSS: Damage to Cast in Drainage Duct |  | Contr | __M |  |  | 2016-11-26 | 2017-02-21 11:30 | 87 | 2016-09-27 07:51 | Tunnelling - Linings - In-situ Concrete | 1500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | • On the 14/09/16 during the anchor installation by a Kern operative, 2 no. Dywidag ties were found to be drilled through the drainage ducting. • As a result, there are 4 no. holes in the duct (i.e. top and bottom) as shown in the Att.01 photos.
| 02SL - Stations (LUL) | Cxxx-NCR-001406 | NCR | L - CH3 Thicknening: FF extension up to headwall |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-11-18 | 2017-01-27 16:41 | 70 | 2016-09-19 14:32 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | • On 11/09/16 FF reinforcement required in the CH3 crown thickening have been extended up to the headwall. • Refer to Att.01 for sketch summarising the as built situation.
| 02SL - Stations (LUL) | Cxxx-NCR-001407 | NCR | L - CH7/AP1 Connection: No __ overlapping |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-04-30 | 2017-05-25 17:36 | 25 | 2016-09-21 16:36 | Tunnelling - Linings - Sprayed Concrete | 2500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | • On 19/09/16 the __ overlapping at secondary lining stop end has been oversprayed with sprayed shotcrete as shown in Att.01 photos
| 02SL - Stations (LUL) | Cxxx-NCR-001408 | NCR | L - PTE-E and RCE SL: Missing tests and documentation |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-09-05 | 2017-09-14 14:02 | 9 | 2017-08-22 11:13 | Tunnelling - Linings - In-situ Concrete | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | • Cxxx-__M-C4-LLG-C101-50176 – PTE-E & RCE Regulation Layer - L002 Regulation Layer 1) Hammer Tapping Check Sheet (__ Form D3-80) missing for half the tunnel of PTE-E Block 11 Crown (Ch62.3 – 77.3). See Att01. 2) PTE-E Block 2 Invert (Ch144.3 – 149.2), Permit to Cover (__ Form D3-93) refer to a damp patch, however no repair records are available. See Att02. • Cxxx-__M-C4-LLG-C101-50177 – PTE-E & RCE __ Sprayed Applied Waterproofing Membrane - L002 3) Missing Grouting of Injection Tubes (__ Form D3-109) for PTE-E Block 16. • Cxxx-__M-C4-LLG-C101-50178 – PTE-E & RCE Waterproofing Sheet Membrane - L002 4) Missing Single welded joint/production checks on Sheet Membrane Installation Checksheet (__ Form D3-94) for PTE-E Block 2 to 15 and TBM Ring. See Att03. • Cxxx-__M-C4-LLG-C101-50181 – PTE-E & RCE Fireproofing Layer - L002 5) Missing Logica Process Parameter Checksheet (__ Form D3-144) for PTE-E Ch16 – 62; Ch70 – 74; Ch 88 – 92.
| 02SL - Stations (LUL) | Cxxx-NCR-001409 | NCR | W - CP1a/EPW1-E Cast wing walls: Poor finish and honeycombing |  | Contr | __M |  |  | 2016-11-21 | 2017-01-30 11:43 | 70 | 2016-09-22 15:38 | Tunnelling - Linings - In-situ Concrete | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | • On the 21/09/16 after striking the timber shutter from CP1a wing wall leading into EPW1 invert and wing walls, a poor finish and honeycombing was found localised in a small area at the break point. • This included an exposed reinforcing bar. • Photos of the defect can be seen in Att.01
| 02SL - Stations (LUL) | Cxxx-NCR-001410 | NCR | W - RCE SL: Missing tests and documentation |  | Contr | __M |  |  | 2017-04-30 | 2017-03-24 18:54 | -37 | 2017-03-01 15:32 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | • Cxxx-__M-C4-LLG-D061-50161 Deliverable Records for RCE Regulation Layer, Sheet Membrane and Cast In-Situ Regulation Layer 1) Ambient temperature is missing from Secondary Lining Shotcrete Placement Checksheet (__ Form D3–86) for RCE regulation layer ch.111 -121.5 – invert. • Cxxx-__M-C4-LLG-D061-50162 Deliverable Records for Spray Waterproofing through Fireproofing Bulking Layer, First Secondary Layer and Combined Second Secondary with Fireproofing Layer 2) No SCL Rebound Measure Sheet (__ Form D3-46) performed during this period. • Cxxx-__M-C4-LLG-D061-50161 Deliverable Records for RCE Regulation Layer, Sheet Membrane and Cast In-Situ Sidewall In-Situ Invert Layer 3) Reinforcement Check Sheet (__ Form D3-26) is missing for RCE RHS Sidewall In-Situ Invert Layer – Block Transition (Ch.119.5 to 121.4) (reinforcement installation).
| 02SL - Stations (LUL) | Cxxx-NCR-001411 | NCR | L – PTE Contraction joint clash with reinforcement at the following junctions with Platform Tunnel Eastbound: LCE, CP2, CP4, CP4a, CP6, CP8, CP10, VD2 |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2016-11-22 | 2017-02-21 14:14 | 91 | 2016-09-23 15:11 | Tunnelling - Linings - Sprayed Concrete | 15000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Further to Cxxx-NCR-001264 where it was apparent that at CP3a where __ had cut contraction joints these had exposed the structural reinforcement. __ were instructed via Cxxx-SVI-00010 (dated 9/05/2016) to inspect all other contraction joints. Based on these inspections it was clear that structural steel was visible in the following contraction joints in PTW:- CP1 north CP3 north CP3a north CP5 north CP7 north Based on RFI 997 the following were identified to be injected in PTE, RCE and LCE:- VD5 east LCE (SOP 529) VD7 east and west (SOP 516 and 523) CP2 west and south CP4 south CP4a south CP6 west, east and south CP8 south CP10 east and south VD2 east, west and south For VD2 south the contraction joint was formed using a stop end however __ mistakenly started to saw-cut. If __ can demonstrate that the location of the saw-cut is at the location of the stop-end or south of the stop-end then VD2 south does not require injection. For VD4 south and west __ to confirm these were constructed by stop-end. Further to Cxxx-EWN-01082 (dated 2/09/2016) on the basis that more than 50% of the inspected contraction joints within the cross passage junctions in PTW have positively identified a defect and in the absence of a complete survey the durability of the structural reinforcement can be assumed to be compromised. Crossrail are assuming that the joints are being injected as per the repair methodology in Cxxx-NCR-001264 (or similar accepted method). Further to Cxxx-PMI-01196 (dated 6/09/2016) the agreed methodology (as proposed in Cxxx-NCR-001264 and accepted by Cxxx) is to date being undertaken on site. It is noted that is it also acceptable to use __ 4a to plug the gap instead of Masterseal 590 prior to injection of the contraction joints. Where repairs are carried out in unclad areas the plug should be hammer tapped to ensure bond of plug to SCL (all in LCE and RCE, CP2 west, CP10 east). Refer Att 01 - Liverpool Street Platform Tunnel Eastbound Contraction Joints Requiring Resin Injection 19-09-2016.pdf
| 02SL - Stations (LUL) | Cxxx-NCR-001412 | NCR | L - VD4: Fire proofing profile outside tolerances |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-04-21 | 2017-03-17 15:09 | -35 | 2016-09-27 13:18 | Tunnelling - Linings - Sprayed Concrete | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | • On 16/07/2016, after review of the fire proofing profile scans in VD4, several areas from Ch4 to 8 have been found encroaching the CTRL zero line ( red areas ) and some other areas found outside the CTRL +100mm profile ( blue areas ) • They are highlighted in blue and in red on Att.01 scan. Fire proofing profiles can be seen Att.02
| 02SL - Stations (LUL) | Cxxx-NCR-001413 | NCR | L - LCE Ch 180-209: Fire proofing profile outside tolerances |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-02-10 | 2017-03-03 15:55 | 21 | 2016-09-27 13:36 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | • On 22/07/2016, after review of the fire proofing profile scans in LCE Ch 180 to 209, areas from Ch186 to 209 have been found encroaching the CTRL zero line ( red areas ) and some other areas found outside the CTRL +100mm profile ( blue areas ) • They are highlighted in blue and in red on Att.01bis scan. • Please note that Att.01 is superseded by Att.01bis. Same scans except that area in red in page 2 at Chainage 209 LHS is now marked as a tight spot.
| 02SL - Stations (LUL) | Cxxx-NCR-001414 | NCR | L - AP6/AP6a/AP10a/AP10b: Fire proofing profile outside tolerances |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-08-25 | 2017-09-14 13:44 | 20 | 2016-09-28 11:05 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | AP6 Tunnel: • On 21/07/2016, after review of the fire proofing profile scans in AP6, several areas from Ch22 to 182 have been found encroaching the CTRL zero line ( red areas ) and some other areas found outside the CTRL +100mm profile ( blue areas ) • Encroachments are generally of the 5-10mm with a tighter area at Ch 23 at 30mm, another tighter area at Ch 36 at 40mm and 2 tight areas at ch. 173-176 of up to 180mm. Out of profile throughout the tunnel are generally 5mm larger with one exception of 10mm larger. • They are highlighted in blue and in red on Att.01 scans. Fire proofing profiles can be seen in Att.02 • Please note that Att.01 and Att.02 have been superseded by Att.01a and Att.02a due to scanning error between ch. 172-182. This area is near the transition of AP6a, which can be seen in the photo in Att.10. AP6a Headwall: • On 03/08/2016, after review of the fire proofing profile scans in AP6a headwall, some areas have been found encroaching the CTRL zero line ( red areas ) by up to 24mm and some other areas have been found outside the CTRL +100mm profile ( blue areas ) by up to 150mm • They are highlighted in blue and in red on Att.03 scans. AP10a Junction: • On 06/07/2016, after review of the final 3d scans in AP10a junction, some areas have been found encroaching the CTRL zero line ( red areas ) by up to 10mm and some other areas have been found outside the CTRL +100mm profile ( blue areas ) by up to 100mm • They are highlighted in blue and in red on Att.04 scans. AP10b Junction: • On 22/07/2016, after review of the final 3d scans in AP10a junction, some areas have been found encroaching the CTRL zero line ( red areas ) by up to 50mm and some other areas have been found outside the CTRL +100mm profile ( blue areas ) by up to 100mm • They are highlighted in blue and in red on Att.05 scans. AP10a Tunnel: • On 06/07/2016, after review of the fire proofing profile scans in AP10a, some areas from Ch2 to 5 have been found encroaching the CTRL zero line ( red areas ) by up to 10mm • They are highlighted in red in Att.06 scans. Fire proofing profiles can be seen in Att.07 AP10b Tunnel: • On 22/07/2016, after review of the fire proofing profile scans in AP10b, some areas from Ch2 to 6 have been found encroaching the CTRL zero line ( red areas ) by up to 90mm. The remainder of the tunnel is covered by Cxxx-NCR-001296. • They are highlighted in red in Att.08 scans. Fire proofing profiles can be seen in Att.09
| 02SL - Stations (LUL) | Cxxx-NCR-001415 | NCR | W - WB cav: Areas outside CTRL +100mm profile line |  | Contr | __M |  |  | 2017-05-05 | 2017-05-24 09:48 | 19 | 2016-09-28 11:45 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | • On 25/09/2016, after the review of the fire proofing profile in WB cav, some areas ( Ch227 to 254 - 7 to 4'oclock) have been found to be outside the CTRL +100mm profile by max 10mm ( i.e CTRL +110mm ) • They are highlighted in blue in Att.01 scans. This can be confirmed in Att.02 fire proofing profiles
| 02SL - Stations (LUL) | Cxxx-NCR-001416 | NCR | W - July 16: Low Residual Flexural strength of Mix Invert C32/40 45kg - Beam Testing CR2933 |  | Contr | __M |  |  | 2016-11-29 | 2016-11-24 12:00 | -5 | 2016-09-30 13:58 | Tunnelling - Linings - In-situ Concrete | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | • WHI cast beam set CR2933 from July has achieved too low individual D3 results of beam B – S1.1, D – S1.1, at 28 days with average for set of four beams - S1.3 • Test results can be seen in Att.01
| 02SL - Stations (LUL) | Cxxx-NCR-001417 | NCR | L - August 16: Low Residual Flexural strength of Mix P1 C32/40 45kg - Beam Testing CR2998 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-11-29 | 2017-04-28 15:10 | 150 | 2016-09-30 13:52 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | • FIN spray in moulds beam set CR2898 to cover July production of shotcrete sprayed in August (10/08/16) has achieved too low individual D3 result of beams C – S1.1, at 28 days with average for set of 5 beams - S1.7, Beam B appear to be broken – not tested. • Test results can be seen in Att.01 • Individual deflection test results can be seen in Att.02 and photos in Att.03 • Areas affected are all tunnels with P1 Mix sprayed from the 27/07/16 to the 24/08/16. This includes ES3 primary lining, CH5 secondary lining, AP11/AP12 thicknening and AP2 primary lining. Refer to Att.04 for the pour records.
| 02SL - Stations (LUL) | Cxxx-NCR-001418 | NCR | W - PTE-W / DSS connection: Invert coupler offset from theoretical position |  | Contr | __M |  |  | 2017-02-24 | 2017-01-24 15:32 | -31 | 2016-09-29 10:33 | Tunnelling - Linings - In-situ Concrete | 4000 |  | Design | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | • On the 27/09/16 invert couplers have been found to be offset from theoretical position in the PTE-DSS connection as shown in the photos ( Att.01 ) and sketch ( Att.02 ) attached. • Couplers and reinforcement shown in Att.01 protrude beyond the face of the box connection whereas the design required them to finish flush with the face of the box connection • Couplers and reinforcement now protrude into the 500mm wide infill section by between 230-360mm (majority 250mm) • Please note that all couplers as shown on the drawing are protruding i.e. 100 no
| 02SL - Stations (LUL) | Cxxx-NCR-001419 | NCR | L - LCE: Leak adjacent to TBM transition |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2016-12-04 | 2017-03-01 18:53 | 87 | 2016-10-05 13:15 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | • On the 01/08/16 leaks in LCE invert adjacent to TBM transition has been found. • Defect has been found in LCE Block 32 invert near transition with TBM
| 02SL - Stations (LUL) | Cxxx-NCR-001420 | NCR | L - VD4 Block 8: One termination box out of line in the east side |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-03-31 | 2017-05-25 17:31 | 55 | 2016-09-30 15:54 | Tunnelling - Linings - In-situ Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | • On the 19/05/16 one termination box in the VD4 Block 8 east side has been found out of line as shown in Att.01 • Termination box has been found at 1300mm below the agreed level of boxes. This can be confirmed by Att.02
| 02SL - Stations (LUL) | Cxxx-NCR-001421 | NCR | W - LCW/WB Cav/Crossover: __ Hoses blocked |  | Contr | __M |  |  | 2017-06-02 | 2017-06-07 15:09 | 5 | 2016-10-03 14:59 | Tunnelling - Tunnelling General | 1000 |  | Equipment Breakdown | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A - Crossover Block 1 to 5 ( Ch 258 - 303 ): While flushing the __ hoses in Crossover Block 1 to 5 the following hoses have been found blocked: Block 1 - Box 2 - Track side: 1 hose blocked ( 1 white ) Block 1 - Box 1 - Platform side: 2 hoses blocked ( 1 black and 1 red ) Block 1 - Box 2 - Platform side: 2 hoses blocked ( 2 blue ) Block 1 - Box 3 - Platform side: 2 hoses blocked ( 2 yellow ) Block 3 - Box 1 - Track side: 1 hose blocked ( 1 white ) Block 5 - Box 1 - Track side: 1 hose blocked ( 1 blue ) All Crossover flushing records can be seen in Att.01. Schematics are also available for review in Att.01 B - LCW: While flushing the __ hoses in LCW the following hoses have been found blocked: Box 2 - Track side: 3 hoses blocked ( 3 blue ) Box 3 - Track side: 1 hose blocked ( 1 yellow ) All LCW flushing records can be seen in Att.02. Schematics are also available for review in Att.01 C - WB Cavern Block 1 to 7 ( Ch 202 - 254 ): While flushing the __ hoses in WB Cavern the following hoses have been found blocked: Block 2 - Box 1 - Track side: 1 hose blocked ( 1 blue ) Block 2 - Box 2 - Track side: 1 hose blocked ( 1 yellow ) Block 2 - Box 1 - Platform side: 1 hose blocked ( 1 blue ) Block 2 - Box 2 - Platform side: 1 hose blocked ( 1 yellow ) Block 3 - Box 1 - Platform side: 1 hose blocked ( 1 blue ) Block 3 - Box 2 - Platform side: 1 hose blocked ( 1 yellow ) Block 6 - Box 1 - Track side: 1 hose blocked ( 1 blue ) Block 6 - Box 2 - Track side: 1 hose blocked ( 1 yellow ) Block 7 - Box 2 - Track side: 2 hoses blocked ( 2 transparent ) Block 7 - Box 3 - Track side: 1 hose blocked ( 1 transparent ) Block 7 - Box 2 - Platform side: 2 hoses blocked ( 2 blue )
| 02SL - Stations (LUL) | Cxxx-NCR-001422 | NCR | W - WB Cav headwall: Hollow in LCW and Xover entrance |  | Contr | __M |  |  | 2016-12-16 | 2017-01-30 11:45 | 45 | 2016-10-04 15:34 | Tunnelling - Linings - In-situ Concrete | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | • On 02/10/16, during hammer tapping before handover of the area to Cxxx, hollows in the WB cavern headwall in LCW and Xover crown have been found. • Hollow area in LCW crown is 1500 x 100mm x 55mm. • For the crossover, after investigation it has been found out that the hollow sound was due to two small pieces of ply ( 2 x 4000 x 100mm x 90mm ) • Both areas have been marked in yellow and can be seen in Att.01 page 1 and Att.02 page 2
| 02SL - Stations (LUL) | Cxxx-NCR-001423 | NCR | W - PTW-E Block 5: Sidewalls are slightly out of tolerance (10mm) at chainage 63 |  | Contr | __M |  |  | 2016-12-05 | 2017-01-27 15:53 | 53 | 2016-10-06 10:13 | Tunnelling - Linings - In-situ Concrete | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | • During certification package review of package PTW-E W008, two points in PTW-E Block 5 Ch 62.83 have been found outside the CTRL profile by 10mm. • This can be seen in Att.01
| 02SL - Stations (LUL) | Cxxx-NCR-001424 | NCR | L - CP8: Fire proofing profile outside tolerances |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-06-30 | 2017-04-07 07:07 | -84 | 2016-10-05 07:26 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | • On 15/02/2016, after review of the fire proofing profile scans in CP8 Ch 9 to 24, areas from Ch9 to 17 have been found encroaching the CTRL zero line ( red areas ) and some other areas found outside the CTRL +100mm profile ( blue areas ) • They are highlighted in blue and in red on Att.01 scan.
| 02SL - Stations (LUL) | Cxxx-NCR-001425 | NCR | W - PTW-E and RCW: __ Hoses blocked |  | Contr | __M |  |  | 2017-06-09 | 2017-06-15 08:17 | 6 | 2016-10-06 12:31 | Tunnelling - Linings - In-situ Concrete | 1000 |  | Equipment Breakdown | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | While flushing the __ hoses in PTW-E the following hoses have been found blocked: PTW-E / RCW Block Transition - Box 1 - Track side : 2 hoses blocked ( red ) PTW-E / RCW Block Transition - Box 2 - Track side : 1 hose blocked ( blue ) PTW-E / RCW Block Transition - Box 3 - Track side : 1 hose blocked ( transparent ) PTW-E / RCW Block Transition - Box 2 - Platform side : 2 hoses blocked ( green and yellow ) PTW-E / RCW Block Transition - Box 3 - Platform side : 1 hose blocked ( blue ) PTW-E / RCW Block Transition - Box 4 - Platform side : 1 hose blocked ( transparent ) PTW-E Block 1A - Box 1 - Platform side: 3 hoses blocked ( green and 2 yellows ) PTW-E Block 1 - Box 1 - Platform side: 1 hose blocked ( blue ) PTW-E Block 2 - Box 1 - Track side: 1 hose blocked ( red ) PTW-E Block 2 - Box 1 - Platform side: 2 hoses blocked ( red and transparent ) PTW-E Block 4 - Box 1 - Platform side: 1 hose blocked ( green ) PTW-E Block 5 - Box 1 - Track side: 1 hose blocked ( blue ) PTW-E Block 5 - Box 1 - Platform side: 1 hose blocked ( blue ) PTW-E Block 6 - Box 1 - Track side: 1 hose blocked ( green ) PTW-E Block 6 - Box 2 - Track side: 1 hose blocked ( blue ) PTW-E Block 6 - Box 2 - Platform side: 1 hose blocked ( transparent ) PTW-E Block 7 - Box 1 - Track side: 1 hose blocked ( green ) PTW-E Block 7 - Box 2 - Track side: 1 hose blocked ( green ) PTW-E Block 7 - Box 3 - Track side: 1 hose blocked ( transparent ) PTW-E Block 7 - Box 1 - Platform side: 2 hoses blocked ( blue and green ) PTW-E Block 7 - Box 3 - Platform side: 1 hose blocked ( blue ) PTW-E Block 8 - Box 2 - Platform side: 3 hoses blocked ( 2 blue and 1 yellow ) PTW-E Block 9 - Box 1 - Track side: 2 hoses blocked ( blue and green ) PTW-E Block 9 - Box 1 - Platform side: 1 hose blocked ( 1 green ) PTW-E Block 9 - Box 2 - Platform side: 1 hose blocked ( 1 blue ) Flushing records and schematics can be seen in Att.01 ( PTW-E Block 1 to 9 )
| 02SL - Stations (LUL) | Cxxx-NCR-001426 | NCR | L - LCWa and b: Fire proofing profile outside tolerances |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-08-02 | 2017-08-18 14:41 | 16 | 2016-10-06 14:58 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | • During the review of the latest fire proofing scans in LCWa and LCWb some areas ( LCWa - Ch180 to 194 - 7 to 4'oclock and LCWb - Ch123 and 149 - 7 to 4'oclock) have been found to be outside the CTRL +100mm profile by max 18mm ( i.e CTRL +180mm ). • Please note that in LCWb some areas near transition have been found encroaching the CTRL profile by max 40mm • They are highlighted in blue ( outside CTRL +100mm ) and red ( tight ) in Att.01 / Att.03 scans. • This can be confirmed looking to Att.02 and Att.04 showing the fire proofing profiles
| 02SL - Stations (LUL) | Cxxx-NCR-001427 | NCR | L - VD4 Block 4: Exposed __ hose along axis level in RHS |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-06-23 | 2017-06-15 15:15 | -8 | 2016-10-10 13:24 | Tunnelling - Linings - In-situ Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • On the 10/10/16 during inspection of the cast in situ in VD4, one __ hose along axis level in VD4 Block 4 RHS has been found exposed. • Photo of the exposed __ hose can be seen in Att.01
| 02SL - Stations (LUL) | Cxxx-NCR-001428 | NCR | W - EB Cavern Headwall: Steel bars tight in the north side |  | Contr | __M |  |  | 2017-04-30 | 2017-03-22 09:34 | -39 | 2016-10-11 15:42 | Tunnelling - Linings - In-situ Concrete | 1500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | • On the 11/10/16 where the couplers extend out of the kicker on the north side of the EBRT eye there is between 30mm and 55mm cover to face of concrete. • This affects 20 number B16 starter bars. • The shutter for the eye will have to tie into the kicker and cannot move inwards as it will encroach on our internal tolerance too much. • Refer to Att.01 for photos of the tight reinforcement
| 02SL - Stations (LUL) | Cxxx-NCR-001429 | NCR | W - ES1 Block 11 South Wing Wall: Non-conforming spacings between couplers |  | Contr | __M |  |  | 2017-01-20 | 2017-02-27 13:24 | 38 | 2016-10-20 13:16 | Tunnelling - Linings - In-situ Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | • On 19/10/16 couplers in the ES1 Block 11 south wing wall have been found installed incorrectly. As shown in Att.01 photos the required 100mm spacing has not been achieved. • Please note that Att.01 title is incorrect, should be read Att.01 ES1 Block 11 South Wing wall couplers and not Block 10
| 02SL - Stations (LUL) | Cxxx-NCR-001430 | NCR | L - Moorgate Shaft Liner Wall A: Leaks between VD7 and VD5 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-05-31 | 2017-03-27 07:52 | -65 | 2016-11-14 16:16 | Tunnelling - Linings - In-situ Concrete | 1500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On 14/10/16 during a Moorgate shaft site visit with Cxxx and Cxxx __, leaks have been found in the Moorgate shaft wall A between VD7 and VD5 as shown in the Att.01 photos.
| 02SL - Stations (LUL) | Cxxx-NCR-001431 | NCR | L - CP9 and CP10 SL: Missing tests and documentation |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-07-26 | 2017-08-17 13:53 | 22 | 2017-07-12 09:55 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | • Cxxx-__M-C4-LLG-C101-50045 Deliverable Records for LIV CP9&10 In-situ Concrete Invert - Package No L018 Invert Layer – ITP item C3; C4 Missing Workability and Temperature results on Secondary Lining Concrete Pour Checksheet (__ Form D3‐84) for CP9 Invert Block 2, Ch. 15.6 to 24.767
| 02SL - Stations (LUL) | Cxxx-NCR-001432 | NCR | W - PTE-W: Fire proofing profile outside tolerances |  | Contr | __M |  |  | 2017-04-25 | 2017-05-25 09:09 | 30 | 2017-02-24 11:45 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | • After the review of the latest fire proofing profile in PTE-W ch 0 to DSS, some areas have been found to be outside the CTRL +100mm profile or encroaching the CTRL profile. • They are highlighted in blue ( outside CTRL +100, big areas ) and red ( tight spots ) in Att.01 scans. Profiles can be seen in Att.02 to Att.08
| 02SL - Stations (LUL) | Cxxx-NCR-001433 | NCR | L - LCWa: Non‐Stainless Steel temporary fixings |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-04-30 | 2017-05-25 17:30 | 25 | 2016-11-08 16:12 | Tunnelling - Linings - In-situ Concrete | 2000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | • On 25/10/2016 DS LCWa portal steel fixings have been found casted in. Affected temporary fixings have been circled in red in Att.01a. • Please note that Att.01 is not anymore relevant as it is now superseded by Att.01a • The temporary fixings are all the way around the portal from wing wall to crown on both sides within the D-wall and Tunnel.
| 02SL - Stations (LUL) | Cxxx-NCR-001434 | NCR | L - CH7 / LS7: Extra concrete cover on the near face reinforcement |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-01-27 | 2017-01-27 16:00 | 0 | 2016-10-31 15:23 | Tunnelling - Linings - In-situ Concrete | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | • On 31/10/16 setting out of the near face reinforcement has been done using a conservative target of +200mm from concrete outlines. • Front concrete cover has been measured between +150 and +250mm from ‘’CRTL Line’’ and back cover has been measured between +300 and +700mm from near face reinforcement. • Photos showing front and back cover measurements by Cxxx done on the 31/10/16 can be seen in Att.01. • Photos have been taken in CH7 left and right side behind shutter, location can be seen in Att.02 drawing • Please note that Cxxx sketch has been also added for a better readability
| 02SL - Stations (LUL) | Cxxx-NCR-001435 | NCR | L - LCWa, LCWb & VD7: Overspilling on the sprayed lining |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-04-22 | 2017-05-24 16:13 | 32 | 2016-11-02 10:58 | Tunnelling - Linings - In-situ Concrete | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | • As shown in Att.01 photo, a thin layer of concrete has been found overspilling onto the shotcrete in LCWa near the portal ( around chainage 185 - between 2 and 4'oclock and below axis ). This has been found on the 31/10/16 • Same issue occurred in LCWb on October 2016, concrete has been found overspilling onto the shotcrete in LCWb near the portal. This is shown in Att.03 photo • Same issue occurred in VD7, concrete has been found overspilling onto the shotcrete in VD7
| 02SL - Stations (LUL) | Cxxx-NCR-001436 | NCR | W - SuperstressCem material used for filling voids not tested |  | Contr | __M |  |  | 2017-04-28 | 2017-05-25 14:03 | 27 | 2016-11-08 14:46 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | • There was several occasions where __ backfilled voids in the secondary lining using Superstresscem without carrying out all of the testing required in the ITP ( e.g. VA2 , PTW-W) • The voids were filled and check sheets completed but no samples or cubes were taken and recorded for the operation.
| 02SL - Stations (LUL) | Cxxx-NCR-001437 | NCR | W - PTE-W/DSS: Hollow spot found in the connection |  | Contr | __M |  |  | 2017-01-27 | 2017-02-03 10:26 | 7 | 2016-11-03 17:06 | Tunnelling - Tunnelling General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During hammer tapping prior PTE-W ch 125 to 165 handover to Cxxx some area in the DSS/PTE-W connection ( chainage 165 - East face ) have been found debonding. Refer to Att.01 for the hammer tapping checksheet
| 02SL - Stations (LUL) | Cxxx-NCR-001438 | NCR | L - CH7: Fire proofing profile outside tolerances |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-01-27 | 2017-03-02 14:27 | 34 | 2016-11-07 10:41 | Tunnelling - Linings - Sprayed Concrete | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | • During CH7 fire proofing scans review some areas ( Ch5 to 12 - 7 to 9'oclock and 3 to 5'oclock) have been found encroaching the CTRL profile or found outside the CTRL +100mm profile. • Encroachment is by max -40mm and out of profile CTRL +160mm • They are highlighted in red ( tights spots ) and blue ( outside CTRL +100mm ) in Att.01 / Att.02 scans.
| 02SL - Stations (LUL) | Cxxx-NCR-001439 | NCR | W - EBRT: Cracks in the cast in situ |  | Contr | __M |  |  | 2017-04-30 | 2017-05-26 12:05 | 26 | 2016-11-09 15:52 | Tunnelling - Linings - In-situ Concrete | 2000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • On the 07/11/16, 24hrs after pouring, cracks began to appear on the surface of Block 10-11 Eastbound Running Tunnel. • One crack, more significant the others followed the line of the drainage duct which is cast in close to the surface of the slab. • The remainder of the cracks, a lot thinner and shallower, randomly propagated out to the extremities in the slab. • Additional cracks in the crown and invert have been found in block 1, block 2, block 3 and block 4. See Att.01 cracks register
| 02SL - Stations (LUL) | Cxxx-NCR-001440 | NCR | L - CH7 Headwall: Fireproofing and total SL underthickness |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-01-27 | 2017-01-27 16:59 | 0 | 2016-11-08 12:09 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | • On 06/11/2016 while reviewing the CH7 headwall scans the following has been found out: Profile – Within tolerance and Okay. See Att.01 Fireproofing Thickness – Thickness drops down to 68mm in the worst case, which is 32mm short of the required 100mm. See Att.02 Total (structural) Thickness – In very minor areas this drops down to 244mm, with a significant amount of under thickness being between 250-300mm. The required thickness according to design is 300mm. See Att.03
| 02SL - Stations (LUL) | Cxxx-NCR-001441 | NCR | L - VD4: Encroachment of the fire proofing profile |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-07-07 | 2017-04-28 15:11 | -70 | 2016-11-09 14:43 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | • On 07/11/2016, after review of the fire proofing profile scans in VD4, areas in the crown from ch 7 to 42 and in ch 40-42 both knees have been found encroaching the CTRL zero lining by max 90mm • They are highlighted in red in Att.01 scans. This is confirmed by Att.02 profiles scans
| 02SL - Stations (LUL) | Cxxx-NCR-001442 | NCR | W - EPW1-E Headwall: Underthickness in the secondary lining |  | Contr | __M |  |  | 2017-02-04 | 2017-02-27 13:32 | 23 | 2016-12-06 16:29 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • During review of the EPW1-E Secondary lining headwall thickness scans, some areas have been found with a thickness below the required 400mm. Worst case is 355mm • This is highlighted in red in Att.01 scans
| 02SL - Stations (LUL) | Cxxx-NCR-001443 | NCR | L - VD4: Leak around termintation box at ch 27 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-01-27 | 2017-03-02 16:50 | 34 | 2016-11-10 10:55 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | • On 09/11/16 during VD4 walk around one leak has been found around termination box 5.2 in the left hand side chainage 27.225
| 02SL - Stations (LUL) | Cxxx-NCR-001444 | NCR | L - AP2: Hollow spot in the secondary lining ch 161 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-01-09 | 2017-02-25 12:23 | 47 | 2016-11-10 12:06 | Tunnelling - Linings - Sprayed Concrete | 4000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • On 21/08/2016 during hammer tapping of AP2 it has been noticed that there was a hollow spot in Ch 161. The hollow spot is located in the left hand side knee(9 O'Clock) and is 300mm x 100mm as shown in Att.01 drawing • Refer to Att.02 for the hammer tapping check sheet showing where the hollow spot was originally found
| 02SL - Stations (LUL) | Cxxx-NCR-001445 | NCR | L – Contraction joint clash with reinforcement CH5, CP1, CP2 |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2017-02-23 | 2017-03-03 14:43 | 8 | 2016-11-15 13:55 | Tunnelling - Linings - Sprayed Concrete | 4000 |  | Planning | Repair | 3 (3-6k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Further to Cxxx-NCR-001264 where it was apparent that at CP3a where __ had cut contraction joints these had exposed the structural reinforcement. __ were instructed via Cxxx-SVI-00010 (dated 9/05/2016) to inspect all other contraction joints. Based on inspections in westbound it was clear that structural steel was visible in the following contraction joints:- CP1 north CP3 north CP3a north (now injected) CP5 north CP7 north Further to RFI 997 the following are considered requiring resin injection:- CH5 west CH5 east CP1 north CP2 south (now injected) Refer to attachments:- Att 01 – Sketch locations of Liverpool Street centre concourse contraction joints_1 of 3 Crossrail are assuming that the joints are being injected as per the repair methodology in Cxxx-NCR-001264 (or similar accepted method). Further to Cxxx-PMI-01196 (dated 6/09/2016) the agreed methodology (as proposed in Cxxx-NCR-001264 and accepted by Cxxx) is to date being undertaken on site. It is noted that is it also acceptable to use __ 4a to plug the gap instead of Masterseal 590 prior to injection of the contraction joints. Where repairs are carried out in unclad areas the plug should be hammer tapped to ensure bond of plug to SCL.
| 02SL - Stations (LUL) | Cxxx-NCR-001446 | NCR | L – Contraction joint clash with reinforcement AP1, CP9, CP10, CH7 |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2017-02-23 | 2017-03-03 09:08 | 8 | 2016-11-15 14:59 | Tunnelling - Linings - Sprayed Concrete | 6000 |  | Planning | Use As-Is | 3 (3-6k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Further to Cxxx-NCR-001264 where it was apparent that at CP3a where __ had cut contraction joints these had exposed the structural reinforcement. __ were instructed via Cxxx-SVI-00010 (dated 9/05/2016) to inspect all other contraction joints. Based on inspections in westbound it was clear that structural steel was visible in the following contraction joints:- CP1 north CP3 north CP3a north (now injected) CP5 north CP7 north Further to RFI 997 the following are considered requiring resin injection however are no longer accessible because of Cxxx block work and shall remain as a potential permanent defect:- AP1 east AP1 west CP9 north CP10 south CH7 north **__ to confirm whether contraction joint in CH7 north was formed using a stop end rather than saw cutting and therefore would not be considered a defect. Refer to attachments:- Att 01 – Sketch locations of Liverpool Street centre concourse contraction joints_3 of 3
| 02SL - Stations (LUL) | Cxxx-NCR-001447 | NCR | L - VD5: __ damaged in the invert |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-01-20 | 2017-02-28 13:02 | 39 | 2016-11-21 14:36 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | • On the 22/07/16 sprayed waterproof membrane (masterseal 345) was damaged in the invert after the waterproofing was already completed and had been signed off. This can be seen from attached Att.01 photos at the time of handover to Cxxx (22nd July 2016). • The damaged waterproofing has therefore compromised the waterproof system and is now no longer 100% continuous as required by specification. • __ layers in some areas have been found peeled off, damaged or performed. Waterproofing protection was not anymore achieved. See Att.01 Page 2 and 3
| 02SL - Stations (LUL) | Cxxx-NCR-001448 | NCR | W - EPW1/CP1a: Radial and longitudinal injection hoses extended over 16m |  | Contr | __M |  |  | 2017-04-28 | 2017-03-28 10:37 | -31 | 2016-11-16 11:01 | Tunnelling - Linings - In-situ Concrete | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | • On 13/11/16 injection hoses for longitudinal and radial waterbars have been extended to the termination boxes and final length found to be over 16m. • Worst case for the radial is 21m and horizontal 22m, see Att.01 • Photos taken on the 24/10/16 of the hoses before cast in can be seen in Att.02. Horiz. Waterbar ca. 22,00m
| 02SL - Stations (LUL) | Cxxx-NCR-001449 | NCR | L - Moorgate Shaft bottom: Leaks near VD4 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-01-15 | 2017-03-02 15:11 | 46 | 2016-11-16 17:04 | Tunnelling - Linings - In-situ Concrete | 2500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | • In November during a routine site visit, leaks have been reported in the Moorgate shaft bottom near VD4.
| 02SL - Stations (LUL) | Cxxx-NCR-001450 | NCR | L - AP12-11: Hollow areas in the primary lining invert |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-03-31 | 2017-03-31 11:11 | 0 | 2016-11-21 15:00 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | • On the 17/11/16, hollow areas have been found in the primary lining invert. • This is confirmed by Att.01 photo showing area after removal of the hollow spot • Hollow spots have been found near ch 17 on both sides (i.e. 3 and 9'oclock). This is confirmed by hammer tapping checksheet Att.04
| 02SL - Stations (LUL) | Cxxx-NCR-001451 | NCR | W - ES1 Block 6: Missing coupled bars |  | Contr | __M |  |  | 2017-01-29 | 2017-02-28 13:00 | 30 | 2016-11-30 17:01 | Tunnelling - Linings - In-situ Concrete | 1000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | • 22/11/16 - BM44 were found not installed so the threaded bars BM43 could not be attached as shown in the design. • Excerpt from Cxxx-MMD-C4-DDD-D061_5-00871 showing coupled bars that were left out can be seen in Att.01
| 02SL - Stations (LUL) | Cxxx-NCR-001452 | NCR | W - ES1/DSS: SL final layer poor finish and compaction |  | Contr | __M |  |  | 2017-01-27 | 2017-02-24 13:53 | 28 | 2016-11-24 09:13 | Tunnelling - Linings - Sprayed Concrete | 2000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | • On 13/11/16 The spray of the final fireproofing layer of the ES1, escalator barrel, up against the Durward Street Shaft connection had a particularly poor finish including voiding and entrapped rebound. • Defect is shown in Att.01 photos
| 02SL - Stations (LUL) | Cxxx-NCR-001453 | NCR | L - VD2: Leak in the invert |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-06-01 | 2017-04-28 16:09 | -34 | 2016-11-24 11:06 | Tunnelling - Linings - In-situ Concrete | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | • On the 7th November 2016 3 locations were noted as damp (areas are 1.8x0.2m and 0.05x0.2m) or as a minor leak (0.4x0.2m). • The 3 areas can be seen from the two photos Att.01 were they have been marked up.
| 02SL - Stations (LUL) | Cxxx-NCR-001454 | NCR | L - CP1: Fire proofing profile outside tolerances |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-05-26 | 2017-03-09 09:18 | -78 | 2016-11-24 15:08 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • On 22/07/2016, after review of the fire proofing profile scans in CP1, areas from ch 4 to 12 from 7'o clock to 5 have been found encroaching the CTRL zero lining by max 10mm and one area found above the CTRL+100mm. • They are highlighted in red ( tights spots ) and blue ( out of CTRL+100mm) in Att.01 scans. This is confirmed by Att.02 profiles scans
| 02SL - Stations (LUL) | Cxxx-NCR-001455 | NCR | L - CP1: Fire-proofing underthickness |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-06-16 | 2017-04-28 15:02 | -49 | 2016-11-24 15:25 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | • On 22/07/2016, after review of the fire proofing thickness scans in CP1, areas from ch 5 to 12 in the crown have been found with a thickness below the required 50mm. • They are highlighted in yellow in Att.01 scans. This is confirmed by Att.02 profiles scans
| 02SL - Stations (LUL) | Cxxx-NCR-001456 | NCR | L - CP2: Fire proofing profile outside tolerances |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-01-27 | 2017-05-26 13:41 | 119 | 2016-11-24 15:56 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | • On 22/07/2016, after review of the fire proofing profile scans in CP2, areas from ch 4 to 12 above wing walls have been found encroaching the CTRL zero lining by max 10mm. • They are highlighted in red in Att.01 scans. This is confirmed by Att.02 profiles scans
| 02SL - Stations (LUL) | Cxxx-NCR-001457 | NCR | L - CP2: Fire-proofing underthickness |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-06-16 | 2017-04-07 07:45 | -70 | 2016-11-24 16:16 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | • On 22/07/2016, after review of the fire proofing thickness scans in CP2, areas from ch 5 to 6 at 11o'clock have been found with a thickness below the required 50mm. • They are highlighted in yellow in Att.01 scans. This is confirmed by Att.02 profiles scans
| 02SL - Stations (LUL) | Cxxx-NCR-001458 | NCR | L - CP2/CH5 Junction: Out of profile and underthickness in the secondary lining |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-07-07 | 2017-06-23 12:20 | -14 | 2016-11-25 10:28 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • After completion of the fireproofing layer in CH5/CP2, scans have shown 4 aspects of non conformance: 1) Encroachment of the CTRL profile: 3 areas of encroachment in the crown, 3 in the right hand shoulder and 2 in the right knee have been found. They are highlighted in orange and yellow in Att.01 3d scan 2) Profile above CTRL + 100mm: One big area in the crown from 10'oclock to 3 o'clock This is highlighted in blue and violet in Att.01 3d scan 3) Fire proofing underthickness: Some areas on both knees have a fire proofing thickness between 40mm and 50mm They are highlighted in yellow in Att.02 3d scan 4) Total secondary lining underthickness ( SL 1st layer + SL 2nd layer + fire proofing layer ): One area in the left shoulder and two in the right shoulder have been found with the thickness between 250mm and 300mm. They are highlighted in yellow in Att.04, Att.04a and Att.04b 3d scan Worst case is in the left shoulder, 267mm thickness instead of 300mm. Area concerned by the underthickness is 1720mm x 815mm, this is confirmed by Att.05 scans Please note that Att.03 is now superseded by Att.04, Att.04a and Att.04b which are the same scans but with additional information. All scans are recorded as CP2/AP7 but __ confirms that this should be read CP2/CH5. This is due to CH5/AP5 pilot and enlargement recorded by the survey team as a continuation of AP7 tunnel
| 02SL - Stations (LUL) | Cxxx-NCR-001459 | NCR | W – EP1 SL Missing Test and documentation |  | Contr | __M |  |  | 2017-04-28 | 2017-05-26 13:20 | 28 | 2017-02-27 09:39 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | • Cxxx-__M-C4-LLG-D061-50179 Deliverable Records for EP1 regulation layer, sheet membrane and cast in-situ: 1) ITP item C2 – SCL Early strength requirements: Thumb Test EP1 Regulation Layer: Secondary Lining Placement Checksheet (__ form D3-86) rev 6 doesn’t register thumb test (See Att01.). 2) ITP item 2.1 – Crack inspection / remediation of primary lining EP1 Regulation Layer: No Repair Checksheet (__ Form D3-60) for Hollow repairs ch.6-7 Invert. (See Att02. Snagging Checksheet). 3) ITP Item 5.3 – Defective Concrete and repairs EP1 Cast In-Situ Invert Layer & Sidewall In-Situ Invert Layer: No Secondary Lining Concrete Post-Pour Checksheet (__ Form D3-88) for ch.14.036 – 15.800.
| 02SL - Stations (LUL) | Cxxx-NCR-001460 | NCR | W - PTE-W: Hollow spot in fireproofing layer ch 120 |  | Contr | __M |  |  | 2017-02-03 | 2017-03-01 11:38 | 26 | 2016-12-05 09:40 | Tunnelling - Linings - Sprayed Concrete | 2600 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | • On 01/12/16 DS, during the hammer tapping of PTE-W fire proofing ch 108.5 to 126 one hollow spot has been found. • Ch 72 Size 1000 x 1400 at 11'o clock looking towards CP2 North • Refer to Att.01 for the hammer tapping before repairs
| 02SL - Stations (LUL) | Cxxx-NCR-001461 | NCR | W & L - __s reinstatement with an insertion of a plastic screw |  | Contr | __M |  |  | 2018-01-31 | 2018-02-01 10:02 | 1 | 2017-05-30 15:37 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | On May 2017 all the __s at WHI and LIV that were proposed or agreed for decommissioning until 18/05/2017 have been found reinstated by the insertion of a plastic screw instead of a stainless steel flathead socket screw.
| 02SL - Stations (LUL) | Cxxx-NCR-001462 | NCR | W - ES1: Hollow area in Ch 32 |  | Contr | __M |  |  | 2017-04-13 | 2017-05-25 13:00 | 42 | 2017-03-30 09:57 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | On 15/12/16 during hammer tapping of the fireproofing layer one hollow in the crown ( size 1.3m x 1.1m ) has been found. Refer to Att.01 page 1
| 02SL - Stations (LUL) | Cxxx-NCR-001463 | NCR | W - PTE-W / DSS connection: Enlarged transition |  | Contr | __M |  |  | 2017-04-28 | 2017-04-28 14:12 | 0 | 2016-12-13 11:27 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | • On 05/12/2016, further to Cxxx-FCD-000590 related to the over excavation of the PTE-W to permit access to core the DSS Dwall, the over-excavation was not bulked out prior to application of the sprayed waterproofing. • Same incorrect sequence of the works occurred in EBRT / DSS connection. This is recorded in a separate NCR, Cxxx-NCR-001502 • Refer to Att.01 sketch for a better understanding
| 02SL - Stations (LUL) | Cxxx-NCR-001464 | NCR | W - CP2 North: Damaged bars in the headwall |  | Contr | __M |  |  | 2017-02-12 | 2017-03-02 16:31 | 18 | 2016-12-14 14:26 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | • On 13/12/16 while trimming tight areas on Secondary lining 1st layer at the face of the headwall in CP2 North, few bars BM-70 have been exposed and other damaged. See Att.01 for photos • In total 5-6 bars BM-70 have been affected. For the exact location, this is highlighted in red in Att.02 and Att.03.
| 02SL - Stations (LUL) | Cxxx-NCR-001465 | NCR | W - ES1/EPW1 and CP1a: __ hoses blocked |  | Contr | __M |  |  | 2017-06-02 | 2017-05-25 14:46 | -8 | 2016-12-20 10:51 | Tunnelling - Tunnelling General | 1000 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • On December 2016 while flushing the hoses in CP1a the following hoses have been found blocked: CP1a Block 1 - Box 1 - Left side: 4 hoses (2 green, 1 white and 1 red ) CP1a Block 1 - Box 2 - Left side: 1 hose (1 blue ) CP1a Block 1 - Box 1 - Right side: 3 hoses (2 white and 1 green ) CP1a Block 2 - Box 1 - Left side: 2 hoses (1 red and 1 green) CP1a Block 2 - Box 1 - Right side: 1 hose (blue) CP1a Block 2 - Box 2 - Right side: 1 hose (red) CP1a Block 3 - Box 1 - Left side: 2 hoses (1 black and 1 blue) CP1a Block 3 - Box 1 - Right side: 1 hose (1 white) CP1a Block 3 - Box 2 - Right side: 2 hoses (1 white and 1 yellow) CP1a Block 4 - Box 1 - Left side: 1 hose (1 white) CP1a Block 4 - Box 2 - Left side: 4 hoses (2 white, 1 blue and 1 green) CP1a Block 5 - Box 1 - Left side: 3 hoses (1 red, 1 yellow and 1 white) CP1a Block 5 - Box 2 - Left side: 1 hose (blue) CP1a Block 5 - Box 2 - Right side: 2 hoses (1 white and 1 yellow) CP1a Block 5 - Box 3 - Right side: 1 hose (1 white ) CP1a Block 5 - Box 4 - Right side: 1 hose (1 red ) Refer to Att.01 for the CP1a flushing records and schematics • On December 2016 while flushing the hoses in ES1 and EPW1 the following hoses have been found blocked: ES1 Block 8 - Box 2 - Right side: 1 hose (1 yellow ) ES1 Block 9 - Box 1 - Right side: 1 hose (1 blue ) ES1 Block 10 - Box 1 - Left side: 1 hose (1 white ) ES1 Block 10 - Box 2 - Left side: 3 hoses (2 red and 1 black ) ES1 Block 10 - Box 1 - Right side: 1 hose (1 red ) ES1 Block 10 - Box 2 - Right side: 1 hose (1 white ) Refer to Att.02 for the ES1 flushing records and schematics
| 02SL - Stations (LUL) | Cxxx-NCR-001466 | NCR | W - EB Cavern and LCE: __ hoses blocked |  | Contr | __M |  |  | 2017-06-23 | 2017-06-15 12:48 | -8 | 2017-04-24 12:44 | Tunnelling - Tunnelling General | 1000 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • On November 2016 while flushing the hoses in EB Cavern the following hoses have been found blocked: EBC Block 1 - Box 1 - Track side: 4 hoses (2 green, 1 white and 1 yellow) EBC Block 1 - Box 1 - Platform side: 3 hoses (1 green and 2 yellow) EBC Block 1 - Box 2 - Platform side: 1 hose (1 white) EBC Block 3 - Box 1 - Track side: 1 hose (1 red) EBC Block 3 - Box 2 - Track side: 1 hose (1 white) EBC Block 3 - Box 1 - Platform side: 1 hose (1 red) EBC Block 4 - Box 1 - Track side: 1 hose (1 red) EBC Block 4 - Box 1 - Platform side: 3 hoses (1 white, 1 blue and 1 red) EBC Block 4 - Box 2 - Platform side: 1 hose (1 white) EBC Block 5 - Box 1 - Track side: 1 hose (1 white) EBC Block 5 - Box 2 - Track side: 1 hose (1 white) EBC Block 5 - Box 1 - Platform side: 2 hoses (1 white and 1 blue) EBC Block 5 - Box 2 - Platform side: 1 hose (1 white) EBC Block 6 - Box 2 - Track side: 1 hose (1 transparent) EBC Block 7 - Box 2 - Platform side: 1 hose (1 transparent) EBC Block 8 - Box 1 - Platform side: 1 hose (1 transparent) EBC Block 9 - Box 1 - Platform side: 2 hoses (1 transparent and 1 yellow) EBC Block 9 - Box 2 - Platform side: 1 hose (1 blue) LCE - Box 1 - Track side: 1 hose (1 red) LCE - Box 2 - Track side: 4 hoses (2 blues, 1 transparent and 1 red) LCE - Box 2 - Platform side: 1 hose (1 transparent) EBRT Block 10 - Box 2 - North side: 2 hoses blocked (both yellow) EBRT Block 10 - Box 4 - North side: 1 hose blocked (white) EBRT Block 10 - Box 1 - South side: 2 hoses blocked (both yellow) EBRT Block 10 - Box 4 - South side: 1 hose blocked (white) EBRT Block 11 - Box 1 - North side: 1 hose blocked (black) EBRT Block 11 - Box 2 - North side: 2 hoses blocked (both yellow) EBRT Block 11 - Box 3 - North side: 2 hoses blocked (white and green) EBRT Block 11 - Box 4 - North side: 1 hose blocked (black) EBRT Block 11 - Box 1 - South side: 1 hose blocked (black) EBRT Block 11 - Box 2 - South side: 2 hoses blocked (both blue) EBRT Block 11 - Box 3 - South side: 1 hose blocked (white) EBRT Block 11 - Box 5 - South side: 2 hoses blocked (both green) EBRT Block 11 - Box 6 - South side: 3 hoses blocked (two blue and one white) Refer to Att.01 for the EBC and LCE flushing records and schematics Refer to Att.02 for the EBRT flushing records and schematics
| 02SL - Stations (LUL) | Cxxx-NCR-001467 | NCR | W - CP1a & ES1/EPW1: Fire proofing profile outside tolerances |  | Contr | __M |  |  | 2017-07-21 | 2017-07-21 13:54 | 0 | 2016-12-21 10:00 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | • On 19/12/2016, after review of the fire proofing profile scan in CP1a, five areas from Ch5 to 39 have been found outside the CTRL +100mm profile. • They are highlighted in blue in Att.01 scan. This is confirmed by profile scans, see Att.02 • Worst case is at ch 33 crown: an area of 5.0m x 0.8m has been found at CTRL + 140mm. • On 19/12/2016, after review of the fire proofing profile scan in ES1/EPW1 two areas from Ch4 to 20 - 3 to 5'oclock have been found encroaching the CTRL profile by max 30mm ( red areas ) • Six minor areas from Ch4 to 46 have been found outside the CTRL+100mm profile ( blue areas ) • They are highlighted in blue and red on Att.03 scan. This is confirmed by profile scans, see Att.04
| 02SL - Stations (LUL) | Cxxx-NCR-001468 | NCR | L - AP6: Termination boxes out of position |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-08-14 | 2017-08-18 14:38 | 4 | 2017-01-10 14:44 | Tunnelling - Tunnelling General | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | On 14/12/16 some termination boxes have been found clashing with Cxxx steel cladding ribs. This is the case for R22, as shown in Att.01. Termination boxes as-built has been added, see Att.02, in order to allow Cxxx to check which termination boxes clashes with the cladding.
| 02SL - Stations (LUL) | Cxxx-NCR-001469 | NCR | L - Flexural beam failure CR3182 Mix P1 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-06-15 | 2017-04-28 15:01 | -48 | 2017-01-03 09:09 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | • FIN spray in moulds beam set CR3182 to cover November’s production of shotcrete has achieved too low individual D3 result of beam E – S1.1, at 28 days with average for set of 5 beams - S1.5 • See Att.01 for FIN beam test results • Please note that CR2893 failure is already covered in Cxxx-NCR-001373 • Test results can be seen in Att.01 • Individual deflection test results can be seen in Att.02 • Areas affected are all tunnels with P1 Mix sprayed from the 02/11/16 and the 30/11/16. This includes ES3 Pilot, ES2 enlargement, LS7 lift, AP9 Arch, AP2 secondary lining FP and AP11/AP12 invert. Refer to Att.03 for the pour records.
| 02SL - Stations (LUL) | Cxxx-NCR-001470 | NCR | W & L - Non conformity of aggregate: samples E2001, E2002, E2005 (LIS) and E1998 (WHI) |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-04-28 | 2017-04-07 07:29 | -21 | 2017-01-23 12:22 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Samples E2001, E2002, E2005 (LIS) and, E1998 (WHI) between 30/11/16 and 05/12/16 have shown grading failure (between 78 and 87 instead of 70max) on the 0.500mm sieve. Repeated test shown the same outcome. See results in Att01. for Liverpool Street. See results in Att02 for Whitechapel
| 02SL - Stations (LUL) | Cxxx-NCR-001471 | NCR | Leaks in LCWa portal |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2017-09-30 | 2017-10-12 09:15 | 12 | 2017-01-16 11:19 | Civil - Tunnelling | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There are several leaks within the LCWa portal in Moorgate Shaft. They are coming through from behind the cast in-situ concrete and manifesting as damp patches/drips above axis on the portal itself. __ to provide annotated photographs illustrating areas.
| 02SL - Stations (LUL) | Cxxx-NCR-001472 | NCR | AP2 portal leaks |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2017-03-31 | 2017-03-07 09:15 | -24 | 2017-01-16 16:02 | Civil - Tunnelling | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | AP2 portal to Broadgate box has leaks/damp patches in crown. They appear to be coming through minor cracks in the concrete and through the SCL/cast in-situ interface. __ are to attach photos illustrating locations of leaks as well as records of injection to date.
| 02SL - Stations (LUL) | Cxxx-NCR-001473 | NCR | W - Flexural beam failure Mix P1 45kg CR3205 |  | Contr | __M |  |  | 2017-06-09 | 2017-05-11 08:13 | -29 | 2017-02-09 09:46 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | WHI spray in moulds beam set CR3205 to cover November’s production of shotcrete has achieved too low individual D3 result of beams C – S1.08 and beam E – S1.00, at 28 days with average for set of 6 beams - S1.6. See Att01. Cxxx WHI beam results summary The sprayed linings which may have been affected (typically applied within +/- 2 wks of the date of the test spraying) are: Secondary lining of Crossover ch310-347; ES1 ch22-32; CP1 ch6-32.5; EB CAV ch113-132.5; CP2 ch0-12; PTE-W ch75-108
| 02SL - Stations (LUL) | Cxxx-NCR-001474 | NCR | Leaks in VD7 SCL invert at LCE/VD7 junction. |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2017-08-02 | 2017-08-18 13:23 | 16 | 2017-01-19 10:25 | Civil - Tunnelling | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A damp patch in the invert of VD7 which was noticed after application of the first layer of secondary lining. The damp patch appeared to be coming from the joint between sprayed concrete and reinforced concrete at SOP 518 (see drawing Cxxx-MMD-C4-DDB-C101_6-00219 Rev C03, attached be Cxxx). This joint at SOP 518 is a contraction joint.
| 02SL - Stations (LUL) | Cxxx-NCR-001475 | NCR | L - AP11: NF 2nd lining missing reinforcement around lifting eye |  | Contr | __M |  |  | 2017-03-31 | 2017-03-29 15:04 | -2 | 2017-01-19 17:01 | Tunnelling - Linings - Sprayed Concrete | 86000 |  | Design | Repair | 1 (>60k) | Complete | Management Problem - Inadequate supervision | Completed |  | On 16/01/17, A393 additional mesh reinforcement around the lifting eye in AP11 crown has been cut. Resulting in gaps of reinforcement between the lifting eye and the near face mesh installed in vault as per proposed FCD 880. This is shown in Att.01 Photo. The following has also been provided: - Secondary lining 1st layer Reinforcement checksheets, see Att.03 - Total secondary lining thickness, see Att.04 and Att.05 - Secondary lining 1st layer Hammer tapping checksheet, see Att.06 - Compressive strength test results, see Att.07 - Secondary lining NF Reinforcement checksheet, see Att.08
| 02SL - Stations (LUL) | Cxxx-NCR-001476 | NCR | L - AP11 Headwall: Fireproofing layer encroaching the CRTL ZERO |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-03-20 | 2017-03-03 13:59 | -17 | 2017-01-19 14:42 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • On 17/01/2017, after review of the fire proofing profile scans in AP11, areas in headwall have been found encroaching the CTRL profile • Some tight spots are up to 170mm, they highlighted in red, orange and purple in Att.01 scans.
| 02SL - Stations (LUL) | Cxxx-NCR-001477 | NCR | L - AP9 Ch20-35.5: Hollow spot found in the 1st bulking layer |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-04-07 | 2017-03-30 16:35 | -8 | 2017-01-19 17:26 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | • On 17/01/17, a hollow area of 1.0m2 (Approx 1000mm * 800mm) was found in AP9 crown tonight (at 11 o’clock looking towards ES3) at approx ch34-35m. • This is confirmed by Att.01 photo • Location of hollow spot can be seen in Att.02
| 02SL - Stations (LUL) | Cxxx-NCR-001478 | NCR | L - ES2 Block 2: Starter bars bent |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-03-31 | 2017-02-23 13:59 | -36 | 2017-01-20 12:21 | Tunnelling - Linings - In-situ Concrete | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | • On 18/01/17 invert ES2 block 2 NF2 starter bars were in the walking area and site team bent these bars up. • Concerned bars are the B12-BM02-100 and B12-BM03-100 NF2 ALT, as per drawing Cxxx-MMD-C4-DDD-C101_Z-00501 Att.02 • Refer to Att.01 for photos of the bars bent
| 02SL - Stations (LUL) | Cxxx-NCR-001479 | NCR | W - EBRT Block 10 Crown Pour: Uncontrolled release of concrete due to shutter lifted |  | Contr | __M |  |  | 2017-03-17 | 2017-03-16 22:57 | -1 | 2017-01-23 18:19 | Tunnelling - Linings - In-situ Concrete | 84000 |  | Material | Repair | 1 (>60k) | Complete | Material/Preservation Problems - Insufficient quantity of material to do the job | Completed |  | On 20/01/17 DS, the crown section of EBRT Secondary Lining Block 10 was being cast using the KERN travelling shutter. When the concrete reached shoulder height the shutter lifted allowing an uncontrolled release of concrete and resulting in suspension of the pour.
| 02SL - Stations (LUL) | Cxxx-NCR-001480 | NCR | W - EBRT SL Block 10: __ hoses damaged during coring operations |  | Contr | __M |  |  | 2017-04-14 | 2017-04-28 13:17 | 14 | 2017-01-26 09:17 | Tunnelling - Linings - In-situ Concrete | 3000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | On 24/01/17 NS, during investigation works to Cxxx-__M-C4-CCN-D061-50027 SNC – Remedial works to EBRT Block 10 Cast Crown (see also NCR 1479), 2 no. cores were completed to the Left Hand Side of pour. These cores severed the non-perforated tubes coming from the water bar to junction boxes. Re-injectable system for sheet membrane thus compromised. See photo of the cores in attachement Att01.
| 02SL - Stations (LUL) | Cxxx-NCR-001481 | NCR | L - AP11: __ hoses blocked |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-06-30 | 2017-06-15 09:17 | -15 | 2017-01-26 19:05 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On 26/01/17 while flushing the hoses in AP11 the following hoses have been found blocked: AP11 Block 1 - Box 3 - North Side: 2 hoses (2 green) AP11 Block 1 - Box 3 - South Side: 2 hoses (2 green) AP11 Block 2 - Box 1 - North Side: 1 hose (1 transparent) AP11 Block 2 - Box 2 - South Side: 2 hoses (1 blue, 1 red) Refer to Att.01 for the AP11 flushing records and schematics
| 02SL - Stations (LUL) | Cxxx-NCR-001482 | NCR | W - EBRT SL Blocks 10 and 11: Profile encroachment |  | Contr | __M |  |  | 2017-06-30 | 2017-06-23 12:32 | -7 | 2017-02-08 19:08 | Tunnelling - Linings - In-situ Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After reviewing the profile scans of EBRT on 31/01/17, it appears that Blocks 10 and 11 show 2 localised tight areas up to 10mm on the North Wall between knee and axis of the tunnel profile. See att01 and att02 for Plan View and Profile Scans.
| 02SL - Stations (LUL) | Cxxx-NCR-001483 | NCR | L - CH2 PL Thickening: Missing thickness data Ch.67 to 72 Invert |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-07-21 | 2017-07-21 14:39 | 0 | 2017-06-30 10:08 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • During L050 certification package preparation, CH2 primary lining thickening scans have shown that from ch 67 to 72 invert the thickness data was missing. This is confirmed by the Att.01 scan • Please note that primary lining underthickness areas shown in red in Att.01 scan, are already covered in a separate NCR (Cxxx-NCR-000755)
| 02SL - Stations (LUL) | Cxxx-NCR-001484 | NCR | L - AP9 Block 1 - Starter bars bent |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-06-09 | 2017-03-30 16:30 | -71 | 2017-02-10 08:41 | Tunnelling - Linings - Sprayed Concrete | 2000 |  | Design | Repair | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | On 01/02/17, AP9 block 1 invert slab, the starter bars (NF2) were bent in 90 degrees angle as visible in attached picture (see Att01.).
| 02SL - Stations (LUL) | Cxxx-NCR-001485 | NCR | W - CP1a SL: Missing tests and documentation |  | Contr | __M |  |  | 2017-04-28 | 2017-05-26 13:39 | 28 | 2017-03-23 17:20 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Cxxx-__M-C4-LLG-D061-50195 Deliverable Records for CP1a regulation layer, sheet membrane and cast in-situ: Cast In-Situ Wing Wall Layer: ITP item 3.4 - CP1a Block 5 wing walls – no reinforcement checksheet (D3-26).
| 02SL - Stations (LUL) | Cxxx-NCR-001486 | NCR | W - EBRT Block 11: Surface Irregularities in cast secondary |  | Contr | __M |  |  | 2017-05-26 | 2017-03-28 12:54 | -59 | 2017-02-06 11:29 | Tunnelling - Linings - In-situ Concrete | 2500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the pre-handover inspection, on 03/02/2017, the finish of the cast concrete in EBRT Block 11 showed 3 distinct irregularities in the crown: - Two at axis in the connection with EB CAV Headwall, approximately 600mm long by 50mm wide by 80mm deep and - One in the crown of the tunnel, approximately 300mm x 300mm by 30mm deep. See photos in Att01.
| 02SL - Stations (LUL) | Cxxx-NCR-001487 | NCR | W - Dec 16: Low Residual Flexural strength of Mix P1 45kg 2kg PP - Beam Testing CR2346 |  | Contr | __M |  |  | 2017-06-23 | 2017-05-11 08:38 | -43 | 2017-02-09 13:28 | Materials - General | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not trained for the work being performed | Completed |  | WHI spray in moulds beam set CR3246 to cover December’s production of shotcrete has achieved too low individual D3 result of beams C – S1.06 and beam D – S1.14 and beam E – S1.04, at 28 days with average for set of 6 beams - S1.3. The sprayed linings which may have been affected (typically applied within +/- 2 wks of the date of the test spraying) are: Secondary lining of ES1 ch22-32; CP2 ch0-12; PTE-W ch75-108
| 02SL - Stations (LUL) | Cxxx-NCR-001488 | NCR | W - EB CAV SL: Missing tests and documentation |  | Contr | __M |  |  | 2017-05-28 | 2017-06-19 13:12 | 22 | 2017-04-10 11:16 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Cxxx-__M-C4-LLG-D061-50205 Deliverable Records for EB CAV regulation layer, sheet membrane and cast in-situ (W037) - Sheet membrane – ITP item 4.1, ITP item 4.2: Missing acceptance of injection tubes check sheet (__ form D3-82) for EB CAV Headwall transition block (ch. 109.55 – 113.250). - Cast In-Situ Invert – ITP item 4.1: Missing Secondary lining post-pour checksheets (__ form D3-88) for EB CAV Headwall transition block (ch. 109.55 – 113.250).
| 02SL - Stations (LUL) | Cxxx-NCR-001489 | NCR | W - EBRT SL Block 11: Damaged connection detail from sheet to spray membrane |  | Contr | __M |  |  | 2017-05-26 | 2017-03-30 13:43 | -57 | 2017-02-27 17:24 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | On 09/02/17 during EBRT Block 11 pouring, burst has been found at connection detail between the sheet membrane and the sprayed membrane. Please note that __ doesn’t have any photos of the damaged connection detail.
| 02SL - Stations (LUL) | Cxxx-NCR-001490 | NCR | W - Missing monthly Bleed Test on Mix FSC - September to December 2016 |  | Contr | __M |  |  | 2017-06-16 | 2017-06-21 15:18 | 5 | 2017-02-09 13:52 | Materials - General | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Missing monthly Bleed Test on Mix FSC - September -December '2016, blocks affected: - September – XOV – Block 10, Block 9; EBRT – Block 11; - October – XOV – Block 6; EBRT – Block 1, Block 2; - November – EBRT – Block 10, Block 9, Block 8; - December – EBRT – Block 7;
| 02SL - Stations (LUL) | Cxxx-NCR-001491 | NCR | L - LS7: Final Profile Encroachment |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-06-30 | 2017-06-23 11:05 | -7 | 2017-02-14 10:49 | Tunnelling - Linings - In-situ Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During LS7 fire proofing scans review, some areas ( Ch82.5 to 90 - 9 to 3'oclock) have been found encroaching the CTRL profile for max 10mm. They are highlighted in yellow in Att.01 / Att.02 scans.
| 02SL - Stations (LUL) | Cxxx-NCR-001492 | NCR | L - Moorgate Shaft North Liner Wall: Poor finish |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-04-15 | 2017-03-15 08:19 | -31 | 2017-02-14 15:29 | Tunnelling - Linings - In-situ Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • On 01/02/17 during site visit with CRL, north liner wall has been found with a poor finish. • This is confirmed by Att.01a photos Please note that Att.01 is not anymore relevant
| 02SL - Stations (LUL) | Cxxx-NCR-001493 | NCR | W - CP2 / PTE: Tight areas in the junction |  | Contr | __M |  |  | 2017-05-28 | 2017-06-15 14:12 | 18 | 2017-02-17 13:16 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | • On 17/02/2016 after review of the fire proofing profile 3d scans in CP2 North / PTE junction, some areas on both sides of the junction have been found encroaching the CTRL zero line by max 30mm. • They are highlighted in orange in Att.01. • While reviewing the CP2 plan view profile scans, one area above platform level at ch 16.5/17 has been found encroaching the CTRL zero line by max 40mm. • This is shown in red in Att.03 and Att.04 scans. Please note that invert encroachment is recorded in a separate NCR ( i.e. Cxxx-NCR-000860 - Use as-is accepted ) and tight spots in the lower side walls ch17 to 22.5 was anticipated by Cxxx-RFI-000755.
| 02SL - Stations (LUL) | Cxxx-NCR-001494 | NCR | L - CH3/AP2 Junction: Wrong front cover on NF reinforcement |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-04-21 | 2017-05-24 16:11 | 33 | 2017-02-20 09:43 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | • On 19/02/16 DS in AP2/CH3 Junction NF reinforcement was installed as per Cxxx-MMD-C4-DDD-C101_Z-00850 drawing, following previous layer (2nd 1st) shape. As usual for the final layer of Secondary lining, profile bars were installed and it was found, on the bottom right corner of the junction, that there was a space of 400mm between the profile bar and the NF reinforcement, ie 400mm of front cover. • Reinforcement affected can be seen in Att.01 sketch and photo Att.02
| 02SL - Stations (LUL) | Cxxx-NCR-001495 | NCR | L - ES2 Invert: NF Reinforcement couplers damaged |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-04-22 | 2017-04-28 13:44 | 6 | 2017-02-21 08:49 | Tunnelling - Linings - In-situ Concrete | 2000 |  | Design | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | • On 20/02/17 after removing the shutter, no couplers were visible and scabbling was needed to connect the BM06 to the casted BM01 in ES2 invert. • After completion of the scabbling works around 30 NF couplers were found damaged and could not be used anymore. • This is explained in Att.01 sketch • On 06/03/17 NF reinforcement as built has been done and can be seen in Att.02 • After investigation is has been found that, in addition to the damaged couplers, the FCD 886 regarding spacing and diameter of the reinforcement, was not followed on site: - For the NF: __ installed B12 couplers instead of B25 and spacing was 100mm instead of 200mm - For the FF: Couplers installed were also B12 and BM32 was B16@100 instead of B25@200
| 02SL - Stations (LUL) | Cxxx-NCR-001496 | NCR | L - AP2 Block 1: Hollow spot found in the combined layer |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-04-27 | 2017-05-15 14:17 | 18 | 2017-02-23 09:27 | Tunnelling - Linings - Sprayed Concrete | 15000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | • On 21/02/17 NS after spraying the Secondary Lining Second Layer ( including Fireproofing ), hammer tapping has been done and during the test in AP2 Block 1, a hollow spot was found • Hollow spot is in the crown ( 12o'clock ), 2 meters long and 2,5m wide, see Att.02 hammer tapping checksheet
| 02SL - Stations (LUL) | Cxxx-NCR-001497 | NCR | LIV - AP2: Termination boxes at incorrect position |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-04-24 | 2017-03-13 15:41 | -42 | 2017-02-23 10:27 | Tunnelling - Linings - Sprayed Concrete | 4000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Not Defined | Completed |  | • Further to NCR 1468 ( AP6: Termination boxes out of position ) termination boxes location in AP2 have been provided to Cxxx through RFI 1086 to check current position against the Cxxx vertical GRC ribs and the horizontal struts between ribs shown in Att.01. • After Cxxx investigation, positions of Cxxx grout tube termination boxes have been found clashing with Cxxx cladding structure • In total there is three termination boxes clashing with the cladding structure, they are shown in red in Att.02
| 02SL - Stations (LUL) | Cxxx-NCR-001498 | NCR | L - Dec 16 Sprayed in Jan 17: Low Residual Flexural strength of Mix P1 45kg - Beam Testing CR2366 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-05-05 | 2017-04-28 12:31 | -7 | 2017-03-06 13:11 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | • FIN spray in moulds beam set CR3266 to cover December’s production of shotcrete (sprayed in January) has achieved too low individual D3 result of beams B – S0.77 and beam C – S1.05, at 28 days with average for set of 6 beams - S1.3. • The sprayed linings which may have been affected (typically applied within +/- 2 wks of the date of the test spraying) are: Primary Lining enlargement – ES3 – adv 12-24, Secondary lining AP11- ch4-17.5, AP9 – ch18.5-30, CH3 – ch6.6-8.2 • Refer to Att.01 and Att.02 for the test results
| 02SL - Stations (LUL) | Cxxx-NCR-001499 | NCR | W - CP2 North: A393 mesh layer in crown exposed |  | Contr | __M |  |  | 2017-07-30 | 2017-06-16 08:27 | -44 | 2017-02-24 13:46 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | • On 23/02/17 area around CP2 North eye was trimmed back to allow the space proofing and tolerance to apply 50mm FP Regulating layer. • During trimming, the layer A393 mesh was also removed. • This is shown in Att.01 Photo • Area affected by the NCR can be seen in Att.02 drawing
| 02SL - Stations (LUL) | Cxxx-NCR-001500 | NCR | LIV - AP2/ES2 transition: Damaged Masterseal |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-05-31 | 2017-05-15 15:00 | -16 | 2017-02-27 09:14 | Tunnelling - Linings - Sprayed Concrete | 2500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | • On 25/02/16, during removal of rebounds in the transition from AP2 to ES2 near the contraction joint/stop end, Masterseal has been exposed damaged. • Size of the defect: 150mm x 100mm found at the south side bordering AP2 and ES2 ( 3 o'clock from ES2 looking towards AP2 ) • Minimum 200mm overlap is not anymore achieved • This is confirmed by Att.01 photos
| 02SL - Stations (LUL) | Cxxx-NCR-001501 | NCR | L - AP1 SL underthickness and profile and out of tolerances |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-09-25 | 2017-09-14 14:12 | -11 | 2017-03-16 15:03 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • Underthickness: During L020 certification review, the following underthickness have been found: 1) As shown in Att.01, there is three areas of underthickness in the AP1 headwall. Secondary lining 1st and 2nd layer thickness is 250mm instead of 310mm in some locations. This is highlighted in red in Att.01 scan 2) As shown in Att.02, there is some areas showing the secondary lining 1st and 2nd layer thickness below the required 450mm. Worst case is 430mm in ch 110 crown This is highlighted in red in Att.02 scan 3) As shown in Att.03, there is one area with 290mm of secondary lining 1st and 2nd layer thickness instead of the required 300mm. It is located above wing wall in ch 128. This is highlighted in red in Att.03 scan 4) As shown in Att.04, there is fire proofing underthicknees in AP1 / CP9 junction, left shoulder. Area concerned by the underthickness (between 35 and 40mm) is 220mm x 380mm including a very small area of 50mm x 90mm where thickness is at 35mm instead of 50mm. This is highlighted in red in Att.04 scan. Isolated red tight spots can be considered as irregularities. 5) As shown in Att.05, there is one area of total underthickness (regulation to fire proofing layer) in AP1/CP10 junction at 290mm instead of 300mm. This is highlighted in yellow in Att.05 scan • Profile out of tolerances: 6) As shown in Att.06, AP1 headwall is encroaching everywhere compared to the CTRL profile. This is highlighted in red in Att.6 scan 7) As shown in Att.07, there is several areas encroaching by max 20mm the CTRL profile and two areas in ch 112 and 139 at CTRL + 100mm ( out of tolerances). There are highlighted in red and blue in Att.07 scan. 8) As shown in Att.08, there is two tights spots on each side of the CP9 / AP1 junction. Worst case is in the left knee, profile has encroached by 116mm the CTRL profile. This is highlighted in red and orange in Att.08, worst case values can be seen in Att.09 9) As shown in Att.10, there is two tights spots on each side of the C10 / AP1 junction. Worst case is in the right knee, profile has encroached by max 30mm the CTRL profile. This is highlighted in orange in Att.10
| 02SL - Stations (LUL) | Cxxx-NCR-001502 | NCR | W - EBRT / DSS connection: Enlarged transition |  | Contr | __M |  |  | 2017-04-22 | 2017-05-26 14:06 | 34 | 2017-03-23 16:20 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • On December 2016, further to Cxxx-FCD-000593 related to the over excavation of the EBRT to permit access to core the DSS Dwall, the over-excavation was not bulked out prior to application of the sprayed waterproofing. • Same incorrect sequence of the works occurred in PTE-W / DSS connection. This is recorded in a separate NCR 1463, Cxxx-NCR-001463 • Refer to Att.01 sketch for a better understanding
| 02SL - Stations (LUL) | Cxxx-NCR-001503 | NCR | W - CP2: __ hoses blocked |  | Contr | __M |  |  | 2017-05-01 | 2017-05-25 10:02 | 24 | 2017-03-02 17:02 | Tunnelling - Linings - Sprayed Concrete | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | On 27/02/207 while flushing the hoses in CP2 North the following hoses have been found blocked: CP2 N Block 1 - Box 3 - Left side: 1 black hose CP2 N Block 1 - Box 2 - Right side: 1 black hose CP2 N Block 1 - Box 3 - Right side: 2 hoses blocked ( 1 black and 1 green ) CP2 N Block 2 - Box 1 - Left side: 5 hoses ( 1 green, 2 red, 1 white and 1 yellow ) CP2 N Block 2 - Box 2 - Left side: 1 hose ( 1 yellow ) CP2 N Block 2 - Box 1 - Right side: 4 hoses blocked ( 1 blue, 1 green, 1 red and 1 yellow ) Refer to Att.01 for the CP2 North flushing records and schematics
| 02SL - Stations (LUL) | Cxxx-NCR-001504 | NCR | W - LCE SL: Missing Test and documentation |  | Contr | __M |  |  | 2017-05-10 | 2017-05-24 14:59 | 14 | 2017-04-10 12:37 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During Cxxx-__M-C4-LLG-D061-50216 Deliverable Records for LCE Foam Concrete Plug and Rail Installation (W004) preparation the following has been found missing: - TBM Slabs, Plinths and Rail Beams – ITP item 1.1, ITP item 1.2: Missing Engineers Setting out form (__ Form D3-27). - Foam Plug – ITP item 2.1, ITP item 2.2: Missing Engineers Setting out form (__ Form D3-27).
| 02SL - Stations (LUL) | Cxxx-NCR-001505 | NCR | L - PTE-W and LCE SL: Missing Tests and Documentation |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-07-21 | 2017-07-21 13:46 | 0 | 2017-07-04 15:58 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Cxxx-__M-C4-LLG-C101-50194 Deliverable Records for LIV PTE-W & LCE Regulating Layer - Package No L076 1) Regulation Layer – ITP item C3, 1.1, 2.1, 2.3, 2.5 Missing Shotcrete Placement Checksheet (__ Form D3-86) for PTE-W Regulation Layer Block 25 Crown, Ch. 108 to 120. Missing Shotcrete Placement Checksheet (__ Form D3-86) for PTE-W Regulation Layer Block 29 Invert, Ch. 160 to 169 2) Regulation Layer – ITP item 2.6 Missing Hammer Testing Checksheet (__ Form D3-80) for PTE-W Regulation Layer Block 25 Crown, Ch. 108 to 121 Cxxx-__M-C4-LLG-C101-50198 Deliverable Records for LIV PTE-W & LCE Secondary Lining SCL , Combined Secondary Lining / Fireproofing & Fireproofing Layer - Package No L076 3) Secondary 1st and 2nd (Traditional method) – ITP item 5.9 Missing thickness scans for secondary lining (first layer + second layer) for traditional method areas, PTE-W Ch. 16-105 and 160-194. 4) Fireproofing Layer – ITP item 6.9, 6.10 Missing Logica Process Check Sheet (__ Form D3-144) for PTE-W Ch. 163-167 and 176-180 Cxxx-__M-C4-LLG-C101-50195 Deliverable Records for LIV PTE-W & LCE __ Sprayed Waterproofing Membrane - Package No L076 5) __ – ITP item A3, A4, 1.3, 1.4, 2.1, 2.2 Missing Pre-placement checksheet (__ Form D3-98 1/4) for PTE-W Ch. 105-106 LAYER 1 6) __ – ITP item 2.6, 2.8 Missing Placement checksheet (__ Form D3-101 2/4) for PTE-W Ch. 105-106 LAYER 1 7) __ – ITP item 2.9 Missing Shoredhardness results on Post Application Quality Checks (__ Form D3-100 3/4) for PTE-W Ch. 123-159 8) __ – ITP item 3.2, 3.3 Missing Spraying Consumption Rate (__ Form D3-109) for Ch. 0-7, 81-107 and 146-159 Cxxx-__M-C4-LLG-C101-50197 Deliverable Records for LIV PTE-W & LCE Insitu Concrete Invert & Wingwall - Package No L076 9) Protection Layer – ITP item 4.1 Missing protection layer survey data for blocks 16, 18, 21, 26, 27, 28, 29, 30 and 31.
| 02SL - Stations (LUL) | Cxxx-NCR-001506 | NCR | L - AP2 PL: Missing Tests and Documentation |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-08-02 | 2017-06-23 12:41 | -40 | 2017-04-25 07:37 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During Cxxx-__M-C4-LLG-C101-50234 Deliverable Records for AP2 Primary Lining Top Heading - Package No L021 preparation, the following has been found missing: 1. Workability/flow tests and temperature of shotcrete / ambient temperature of workface: - Advance 41 initial & primary no flow test and temperature recorded - Advance 55 primary no flow test and temperature recorded See Att.A: AP2 PL Missing flow tests 2. & 3. Ensure Joint Cleanliness / Substrate Cleanliness and Embedded Items: - Advance 23: Missing Shotcrete Placement Checksheet (__ Form D3-37) for Adv. 23 Primary Lining During Cxxx-__M-C4-LLG-C101-50242 Deliverable Records for AP2 Primary Lining Invert - Package No L021 preparation, the following has been found missing: 4. Visual core sampling: - No D1 - Visual core sampling taken for July 2016 (refer to Cxxx-__M-C-RGN-CR092-50233).
| 02SL - Stations (LUL) | Cxxx-NCR-001507 | NCR | L - AP2 and AP11-AP12: Fire proofing profile outside tolerances |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-04-05 | 2017-05-12 11:58 | 37 | 2017-03-06 13:52 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Other | Completed |  | • During A2 and AP11-AP12 fire proofing scans review some areas ( AP2 Ch102 to 162 - 7 to 5'oclock and AP11-AP12 ch 4 to 15 -10 to 2 o'clock ) have been found outside the CTRL +100mm profile. Out of profile is by max CTRL +150mm in AP2 ch 153 to 154 • They are highlighted in blue in Att.01 and Att.05 scans. • Profile scans can be seen in Att.02, Att.03, Att.04 and Att.06
| 02SL - Stations (LUL) | Cxxx-NCR-001508 | NCR | W - Decommissioning of Valance Gardens De-Watering without an approved ITP |  | Contr | __M |  |  | 2017-04-28 | 2017-04-28 13:22 | 0 | 2017-03-13 18:19 | Tunnelling - Tunnelling General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | • On February 2017 boreholes and wells were backfilled using a previous ITP that didn't include the Vallance Gardens boreholes. • Following boreholes and wells have been found backfilled without an updated ITP: PW1, PW4A, PW6, PW7, PW8, WH59A, WH60, WH62, WH63 and WH8CPT (2" monitoring well) • Refer to Att.01 and Att.03 for the site records. • Please note that PW8 shown in Cxxx-__M-C4-GMS-D061-50045 Rev 1.0 has been renamed and is now PW64. Location can be seen in Att.02.
| 02SL - Stations (LUL) | Cxxx-NCR-001509 | NCR | L - CH7 PL: Missing Tests and Documentation |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-05-26 | 2017-05-24 16:24 | -2 | 2017-04-24 16:28 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Cxxx-__M-C4-LLG-C101-50246 Deliverable Records for CH7 Primary Lining & Thickening - Package No L058: - Reinforcement Check Sheet (__ Form D3-26) missing for Advance 6 NF and for Advance 8 FF
| 02SL - Stations (LUL) | Cxxx-NCR-001510 | NCR | L - CH7 Headwall: Primary lining underthickness |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-04-13 | 2017-04-28 14:54 | 15 | 2017-03-14 11:46 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | • During L058 certification package preparation, CH7 headwall primary lining scan has been found showing several locations with thickness below the required 650mm. • Worst case is 543mm, see Att.01 for the location of the underthickness • Please note that there is already a NCR for CH7 headwall underthickness of the Secondary lining (Cxxx-NCR-001440)
| 02SL - Stations (LUL) | Cxxx-NCR-001511 | NCR | L - AP9 Block 1 – Joint out of Waterbar |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-04-08 | 2017-04-28 14:59 | 20 | 2017-03-09 15:04 | Tunnelling - Linings - In-situ Concrete | 3500 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Supervision - Other | Completed |  | • In AP9 Block 1, after using the RMD shutter to cast the first pour (up to shoulders) it was noticed after striking the shutter that the joint is not correctly located within the waterbar and is outside of the fins for a small stretch (approximately 500mm starting from the East joint) on the South side of AP9 tunnel. • Refer to Att.01 for photo of the joints
| 02SL - Stations (LUL) | Cxxx-NCR-001512 | NCR | W - EBRT Block 3: Starter bars bent |  | Contr | __M |  |  | 2017-04-20 | 2017-05-11 09:21 | 21 | 2017-03-21 13:34 | Tunnelling - Tunnelling General | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | • On 18/03/17 NS steel reinforcement, bar marks 52 and 96, located on south side of Block 3 in EBRT (with junction to Bypass), have been bent after installation and pour of Block 3 First Stage Concrete Invert. • Photos of starter bars bent can be seen in Att.01
| 02SL - Stations (LUL) | Cxxx-NCR-001513 | NCR | L - CP7: Hollow spot found in the fire proofing layer |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-04-15 | 2017-04-28 14:33 | 13 | 2017-03-16 13:46 | Tunnelling - Linings - Sprayed Concrete | 4000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | On March 2017 hollows spots have been found below axis on both sides of the CP7 tunnel See Att.01 for photos For clarity the secondary lining works chronology is the following : - SL 2nd layer has been hammer tapped on the 07/08/15, see Att.02. No hollows found - Permit to spray fire proofing signed on the 17/08/15 ( see Att.03 ) and fire proofing sprayed on the same day, see Att.04 - All fire proofing spraying completed on the following day, see Att.05 - Final layer hammer tapped from ch 10.5 to 16.5 on the 25/08/15, no hollows found. See Att.06 - Last section of the CP7 ( ch 16.0 and 18.5 ) has been also hammer tapped on 11/01/16 and hollows found on both sides, see Att.07. This was recorded in a separate NCR, i.e. Cxxx-NCR-001207 - This has been repaired see Att.08 and rehammer tapped, see Att.09. No voids found, this is confirmed by Att.10
| 02SL - Stations (LUL) | Cxxx-NCR-001514 | NCR | L - ES2 Block 1: Joint out of Waterbar |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-05-20 | 2017-05-15 14:42 | -5 | 2017-03-21 15:44 | Tunnelling - Linings - In-situ Concrete | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | • On 20/03/17 DS in ES2 Block 1 LHS ( north side ) it was noticed after striking the shutter that 250mm of joint on the stop end was not correctly located within the waterbar. • This is located around 7'oclock looking to AP2 ( LHS - North side ) • Refer to Att.01 for photo
| 02SL - Stations (LUL) | Cxxx-NCR-001515 | NCR | L - ES2 Block 0: __dur has been drilled |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-04-04 | 2017-05-12 14:11 | 38 | 2017-03-21 17:23 | Tunnelling - Linings - In-situ Concrete | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | • On 20/03/17 __dur has been found drilled through in ES2 block 0, all around the lining, from 8 to 4 o'clock • This is shown in Att.01 photos
| 02SL - Stations (LUL) | Cxxx-NCR-001516 | NCR | W - ES1 SL: Missing tests and documentation |  | Contr | __M |  |  | 2017-06-30 | 2017-06-22 09:52 | -8 | 2017-03-24 14:01 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | • Cxxx-__M-C4-LLG-D061-50186 Deliverable Records for ES1 regulation layer, sheet membrane and cast in-situ: Sheet membrane - ITP item 4.1, ITP item 4.2: Missing acceptance of injection tubes check sheet (__ form D3-82) for ES1 block 10 (ch.38.069 – 43.366).
| 02SL - Stations (LUL) | Cxxx-NCR-001517 | NCR | L - CH1-1: Primary lining underthickness |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-10-15 | 2017-10-11 08:14 | -4 | 2017-03-27 13:58 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During L048 (CH1 Primary Lining) Certification package preparation, Ch1-1 primary lining scans have shown several locations, between Ch.35.5 and Ch.45.5, with total thickness below the required 800mm. Worst case is 570mm instead of 800mm in CH1-1/CP3a junction invert. See Att.01 and Att.02 for the location of underthickness.
| 02SL - Stations (LUL) | Cxxx-NCR-001518 | NCR | L - ES2 Block 8: NF and FF missing reinforcement |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-04-27 | 2017-05-16 08:10 | 19 | 2017-03-28 15:44 | Tunnelling - Linings - In-situ Concrete | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • On 27/04/17 NF and FF radial bars were found missing in ES2 Block 8 north and south side. • After investigation the following reinforcement was found missing: In ES2 Block 8 North side: - FF: 13 radial B25 bars installed instead of 20 bars - NF: 14 radial B12 bars installed instead of 20 bars In ES2 Block 8 South side: - FF: 14 radial B25 bars installed instead of 20 bars - NF: 13 radial B12 bars installed instead of 20 bars See Att.01 for photos and Att.02 location of the missing reinforcement
| 02SL - Stations (LUL) | Cxxx-NCR-001519 | NCR | L - CP8: Two hollows found in the fireproofing layer |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-05-03 | 2017-05-12 14:27 | 9 | 2017-04-03 11:05 | Tunnelling - Linings - Sprayed Concrete | 4500 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | • On 27/03/17 during hammer tapping of the fire proofing layer two hollows have been found on the second layer of secondary lining ( P1 mix). • See Att.01 for the hammer tapping checksheet • On 05/04/17 after repair works were carry out ( see Proposed answer for details ) and during final hammer tapping post repair, an additional hollow spot was found around ch 20-21 on the east side. This is confirmed by Att.05 hammer tapping checksheet and Att.06 photos
| 02SL - Stations (LUL) | Cxxx-NCR-001520 | NCR | W - Low Residual Flexural strength of Mix P1 C32/40 45kg 2kg PP KERN |  | Contr | __M |  |  | 2017-04-30 | 2017-05-25 09:16 | 25 | 2017-03-31 10:49 | Tunnelling - Linings - In-situ Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | WHI cast beam set CR3351 from Feb 2017 has achieved too low individual D3 results of beam C – S0.9, D – S1.2, at 28 days with average for set of four beams - S1.3, This is confirmed by Att.01 test results. CR3351 individual test results can be seen in Att.02
| 02SL - Stations (LUL) | Cxxx-NCR-001521 | NCR | L - ES3/CH5: Non conforming stainless steel chutes installed |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-04-18 | 2017-05-20 14:48 | 32 | 2017-04-04 12:19 | Tunnelling - Linings - In-situ Concrete | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | • On April 2017 stainless seel chutes installed between ES3 and CH5 have been found to be non conforming against specifications detailed in the RFI 950 and drawings. - Stainless steel grade is 1.4307 instead of 1.4404 - Flange sizes on the chutes is 4mm instead of 10mm each • This is shown in Att.01 drawing and in Cxxx-__M-C-RGN-CR092-50259 Rev 1.0 MCR – Service Chutes
| 02SL - Stations (LUL) | Cxxx-NCR-001522 | NCR | L - LCW SL: Missing tests and documentation |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-07-21 | 2017-07-21 15:52 | 0 | 2017-07-03 09:13 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | • Cxxx-__M-C4-LLG-C101-50019 Deliverable Records for LCWa Regulation Layer, Secondary Lining SCL & Combined Secondary Lining / Fireproofing 1) Regulation Layer – ITP item C3, 1.1, 2.1, 2.3, 2.5 Missing placement check sheets for regulation layer between Ch 193 – 195.228 2) Regulation Layer – ITP item 2.6 Missing hammer tapping check sheets after repair of regulation layer in crown over D-wall. See Att01. 3) Second 1st Layer – ITP item C1, 5.8, 5.9, 7.1 ITP items C.1, 5.8, 5.9, 7.1 not filled in on Secondary Lining Shotcrete Placement checksheet (__ Form D3-86) covering Secondary 1st Layer Ch 186 to 189; Ch 184 to 186 (RHS) & Ch 179.5 to 181 (LHS); Ch 188 to 195 (invert) and Ch 189 to 195 (crown). See Att02. • Cxxx-__M-C4-LLG-C101-50106 Deliverable Records for LCWa Sprayed Waterproofing Membrane 4) __ – ITP item A3, A4, 1.3, 1.4, 2.1, 2.2, 2.6, 2.8 Missing Pre-Placement Checksheets (__ Form D3-98 - 1/4) and __ Placement Checksheets (__ Form D3-101 - 2/4) for LCWa Invert Layer 3 and Layer 4, Ch.182 to 192 • Cxxx-__M-C4-LLG-C101-50199 Deliverable Records for LCWa Portal Opening 5) Portal Opening – Cxxx-MMD-C4-DDD-C101_Z-00628 2 areas of under thickness in overall Thickness Scan. See Att03: - 1st area – This is due to the geometry of the tunnel and considered as aberrations - 2nd area - This localised area (approx. 300mm x 300mm) is around 20mm under thick
| 02SL - Stations (LUL) | Cxxx-NCR-001523 | NCR | W - CS1: Insufficient lap length on Masterseal at top of SCL |  | Contr | __M |  |  | 2017-07-01 | 2017-06-19 11:17 | -12 | 2017-05-26 08:37 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • On 12/04/17 the exposed __ Masterseal at the joint 94.2m in the CS1 shaft has been found over-sprayed with SCL • The minimum 300mm overlapping of __ was not achieved
| 02SL - Stations (LUL) | Cxxx-NCR-001524 | NCR | L - LCWa Portal Opening: Low 28 day strength results for SCC 50/60 mix |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-05-26 | 2017-05-25 17:05 | -1 | 2017-04-26 11:10 | Tunnelling - Linings - In-situ Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | During Cxxx-__M-C4-LLG-C101-50019 Deliverable Records for LCWa SCL Tunnelling Methodology Secondary Lining ITP ( Package No. L006 ) preparation the following cube test results have been found below the specifications: - C4943, see Att.01 for the test results - C4950, see Att.02 for the test results - C5096, see Att.03 for the test results - Cxxx1, see Att.04 for the test results - Cxxx7, see Att.05 for the test results
| 02SL - Stations (LUL) | Cxxx-NCR-001525 | NCR | L - CH7 SL: Missing tests and documentation |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-05-26 | 2017-05-24 16:28 | -2 | 2017-04-25 10:40 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Cxxx-__M-C4-LLG-C101-50252 Deliverable Records for CH7 Secondary lining CAST IN-SITU INVERT AND COLLAR - Package No L059: Cast In-Situ (invert): 1. Cubes not taken for CH7 cast invert block 2. Flexural strength of cast beams tests not taken for CH7 ‘Invert Mix’ Refer to the following Material Compliance Reports: Laboratory Compliance Report LIV and WHI May’15 (Cxxx-__M-C-RGN-CR092-50204, Rev 2.0) Laboratory Compliance Report LIV and WHI Jul’16 (Cxxx-__M-C-RGN-CR092-50233, Rev 2.0) Laboratory Compliance Report LIV and WHI Aug’16 (Cxxx-__M-C-RGN-CR092-50234, Rev 2.0) Laboratory Compliance Report LIV and WHI Sep’16 (Cxxx-__M-C-RGN-CR092-50235, Rev 2.0) Laboratory Compliance Report LIV and WHI Oct’16 (Cxxx-__M-C-RGN-CR092-50236, Rev 1.0) Laboratory Compliance Report LIV and WHI Nov’16 (Cxxx-__M-C-RGN-CR092-50237, Rev 1.0) Laboratory Compliance Report LIV and WHI Dec’16 (Cxxx-__M-C-RGN-CR092-50238, Rev 1.0) Laboratory Compliance Report LIV and WHI Jan’17 (Cxxx-__M-C-RGN-CR092-50260, Rev 1.0)
| 02SL - Stations (LUL) | Cxxx-NCR-001526 | NCR | W - EBRT W Ch40: One UTX ducting blocked |  | Contr | __M |  |  | 2017-05-09 | 2017-05-11 09:30 | 2 | 2017-04-25 08:15 | Tunnelling - Linings - In-situ Concrete | 2000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During EBRT handover preparation done on the 24/04/2017, all UTX where checked against any blockage. One UTX in ch 40 has been found blocked.
| 02SL - Stations (LUL) | Cxxx-NCR-001527 | NCR | L - LCwa: no contraction joint done at Ch. 191.4 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-08-02 | 2017-08-17 14:25 | 15 | 2017-05-02 12:03 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On 28/04/17, during the redline drawing process, it has been found that no contraction joint was done in LCWa at Ch. 191.4
| 02SL - Stations (LUL) | Cxxx-NCR-001528 | NCR | L - AS1: Primary lining out of profile |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-08-01 | 2017-08-18 09:37 | 17 | 2017-05-02 10:06 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • On 28/04/17 when AS1 shaft scans have been issued, all junctions have been found built out of profile, hence secondary lining thickness will not be achieved in the CP5, CP6, AP7W and AP7E junctions. • For AS1 / AP7 East junction, worst case is 370mm instead of 500mm. This is confirmed by Att.01 and Att.02 scans showing available space between the regulating layer and CTRL profile. Beamer survey can be seen in Att.12 • For AS1 / AP7 West junction, worst case is 380mm instead of 500mm. This is confirmed by Att.03 and Att.04 scans showing available space between the regulating layer and CTRL profile. Beamer survey can be seen in Att.13 • For AS1 / CP5 junction, worst case is 370mm instead of 500mm. This is confirmed by Att.05 and Att.06 scans showing available space between the regulating layer and CTRL profile. Beamer survey can be seen in Att.14 • For AS1 / CP6 junction, worst case is 400mm instead of 500mm. This is confirmed by Att.07 and Att.08 scans showing available space between the regulating layer and CTRL profile. Beamer survey can be seen in Att.15 • Cover meter survey to the AS1 slipform reinforcement can be seen in Att.09 • Cross section sketches can be seen in Att.10 and Att.11
| 02SL - Stations (LUL) | Cxxx-NCR-001529 | NCR | L - VD5 SL: Missing tests and documentation |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-07-17 | 2017-07-21 09:41 | 4 | 2017-07-03 08:41 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • Cxxx-__M-C4-LLG-C101-50264 Deliverable Records for VD5 Regulation Layer, Secondary Lining SCL & Fireproofing 1) Secondary 2nd Layer – ITP item 7.1 Missing Repair Check Sheet ( __ Form D3-54 ) for VD5 Secondary 2nd layer, Ch. 7.354 to 11.560 2) Fireproofing – ITP Item 6.3, 6.4, 6.5, 6.6, 6.7, 6.8 Missing Permit To Spray Check Sheet (__ Form D3-137) for VD5 Fireproofing, Ch. 5 to 7.5
| 02SL - Stations (LUL) | Cxxx-NCR-001530 | NCR | L - VD4 SL: Missing tests, documentation and FP thickness scans |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-08-04 | 2017-08-18 14:47 | 14 | 2017-05-11 15:54 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Cxxx-__M-C4-LLG-C101-50227 Deliverable Records for VD4 Regulation, Secondary Lining & Combined fireproofing SCL - L042: 1) Regulating Layer: ITP item 2.5 Missing survey of regulating layer profile after application of reader between Ch. 4.700 to 7.765. 2) Regulating Layer: ITP Item 2.6 Missing Hammer Tapping checksheet (__ Form D3-80) for VD4 crown and invert from Ch. 7 to 10.5 (Block 12). 3) and 4) Second First layer: ITP Item 4.2 and Combined layer: ITP Item 4.2 Missing reinforcement checksheet ( __ Form D3-26) for Far Face and Near Face invert reinforcement between Ch. 4.700 to 7.765 5) Combined layer: ITP Item 5.10 Missing survey of fireproofing layer thickness between Ch. 4.700 to 7.765. Cxxx-__M-C4-LLG-C101-50229 Deliverable Records for VD4 Sheet Waterproofing Membrane - L042: 6) Sheet Membrane: ITP Items C1, C2, 1.3, 2.1 to 2.8 and 3.1 to 3.3 Missing Sheet Membrane Installation Checksheet (__ Form D3-94) for Moorhouse Shaft Ch. 40.677 to 43.874.
| 02SL - Stations (LUL) | Cxxx-NCR-001531 | NCR | L - ES2 Block 9: Crack in the cast in situ |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-05-17 | 2017-05-15 14:26 | -2 | 2017-05-03 15:07 | Tunnelling - Linings - In-situ Concrete | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | • After striking the shutter and inspecting the ES2 block 9, one crack ( 0.5mm) in the north side has been found • Sketch for more details can be seen in Att.01 lower part
| 02SL - Stations (LUL) | Cxxx-NCR-001532 | NCR | L - CH2: Final profile outside tolerances |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-05-15 | 2017-05-15 14:36 | 0 | 2017-05-04 09:29 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | • During CH2 final profile and invert scan review some areas in CH2 Ch44 to 73 wing walls and secondary lining at 6 and 9 o'oclock have been found encroaching the CTRL profile or outside the CTRL +100mm profile. Encroachment is by max 20mm and out of profile is by max CTRL +130mm • They are highlighted in red ( encroachment ) and blue ( out of profile ) in Att.01 scan and Att.02 profile scans.
| 02SL - Stations (LUL) | Cxxx-NCR-001533 | NCR | W - EBRT SL: Missing tests and documentation |  | Contr | __M |  |  | 2017-07-20 | 2017-07-21 09:37 | 1 | 2017-07-06 14:06 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | • Cxxx-__M-C4-LLG-D061-50228 Deliverable Records for EBRT Secondary Lining – Package W059: Missing Acceptance of Injection Tubes (__ Form D3-82) for block 0, 5 and 6.
| 02SL - Stations (LUL) | Cxxx-NCR-001534 | NCR | W - Bypass South: Fire proofing profile outside tolerances |  | Contr | __M |  |  | 2017-05-26 | 2017-05-24 10:01 | -2 | 2017-05-12 09:12 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • After review of the latest fire proofing profile in Bypass south ch 4 to ch 19, some areas have been found to be outside the CTRL +100mm profile or encroaching the CTRL profile. • They are highlighted in blue ( outside CTRL +100, big areas ) and red ( tight spots ) in Att.01 scan. Profiles can be seen in Att.02 • Worst case is at ch 5 east side knee level, where profile is encroaching by max 30mm the CTRL zero line. See Att.01 for location
| 02SL - Stations (LUL) | Cxxx-NCR-001535 | NCR | W - Bypass Block 2: One __ hose blocked |  | Contr | __M |  |  | 2017-08-30 | 2017-05-24 09:23 | -98 | 2017-05-11 14:51 | Tunnelling - Linings - Sprayed Concrete | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On 15/05/2017 while flushing the hoses in Bypass south block 2 the following hose has been found blocked: Bypass South S Block 2 - Box 3 - West side: 1 white hose Bypass South S Block 2 - Box 3 - East side: 1 white hose Refer to Att.01 for the Bypass South Block 2 flushing records and schematics
| 02SL - Stations (LUL) | Cxxx-NCR-001536 | NCR | L - ES2 Block 7: One breather hole was lost |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-05-26 | 2017-05-24 16:27 | -2 | 2017-05-12 12:03 | Tunnelling - Linings - In-situ Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | • On 10/05/17 during contact grouting, breather holes in block 7 were found lost. • This is can be seen in Att.01 page 7 Grouting checksheet of ES2 block 7
| 02SL - Stations (LUL) | Cxxx-NCR-001537 | NCR | L - ES2/CH2: Adpation works underthickness |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-08-04 | 2017-08-17 14:42 | 13 | 2017-05-16 07:20 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • During L016 certification package preparation, ES2/CH2 primary lining scans have shown two locations with a thickness below the required 800mm. • Worst case is 740mm instead of 800mm in the ES2/CH2 left hand side when looking towards ES2 • See Att.01 and Att.02 for the location of the underthickness
| 02SL - Stations (LUL) | Cxxx-NCR-001538 | NCR | L - ES3 Block 5 and CH5: Incorrect chute lengths |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-05-30 | 2017-06-23 15:29 | 24 | 2017-05-16 07:58 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | 1) • On 15/05/17 when measuring the chute in ES3 block 5 with the beamer against the profile, the chute has come up short by approximately 100mm for part of it • This is shown in the Att.01 pictures. In the pictures the black line marks the profile which confirms that it finishes short on the higher side. • Details of the chute can be seen in Att.02 2) • On 17/05/17 the chute in CH5 has been also found short. • This is shown in the Att.03 pictures.
| 02SL - Stations (LUL) | Cxxx-NCR-001539 | NCR | L - AP7-E Block 1: SCL Overspray onto __ |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-09-30 | 2017-10-12 09:41 | 12 | 2017-05-16 13:48 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • On 11/05/17 whilst spraying in AP7-E, some SCL has been sprayed onto the __ on both sides of the block 1. This is confirmed in Att.01 photo • The minimum 300mm overlapping of __ was lost
| 02SL - Stations (LUL) | Cxxx-NCR-001540 | NCR | L - CP7 and CP8 SL: Missing tests and documentation |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-09-05 | 2017-09-14 14:10 | 9 | 2017-08-22 09:24 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | • Cxxx-__M-C4-LLG-C101-50303 – CP7& 8 Secondary Lining SCL, Combined Secondary Lining/Fireproofing & Fireproofing - L016 Fireproofing Layer (Traditional Method) 1) Under thickness in traditional layer of fireproofing between 40mm and 50mm at CP7 - Chainage 15.8m and CP8 - Various spots around Chainage 7m and 13m. See Att01. • Cxxx-__M-C4-LLG-C101-50302 3 – CP7& 8 Cast In-Situ Invert - L016 2) CP7 Block 2 Invert: Missing Cube Strength
| 02SL - Stations (LUL) | Cxxx-NCR-001541 | NCR | L - AP2: Incorrect waterproofing in no 2 box outs |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-06-13 | 2017-07-17 14:57 | 34 | 2017-05-30 16:46 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | • On 16/05/17 during AP2 condition survey visit, re-injectable tubes in the two box-outs have been found out of the concrete with no termination box. • This is confirmed by page 7 of the Cxxx-__M-C4-RGN-C101-50142 REV 1.0 Condition Survey report for AP2(Ch.113.6-103) / CH3 / ES2 / CH2 / CP8 and CP7 handover to Cxxx – May 2017, see Att.01
| 02SL - Stations (LUL) | Cxxx-NCR-001542 | NCR | L - ES2 PL: Missing tests and documentation |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-07-17 | 2017-07-21 12:58 | 4 | 2017-07-03 09:04 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • Cxxx-__M-C4-LLG-C101-50267 Deliverable Records for ES2 Pilot Construction: Missing subcarrier check sheets (D3-125) for A19 & A26 • Cxxx-__M-C4-LLG-C101-50268 Deliverable Records for ES2 Enlargement: Missing excavation beamer profiles (Top Heading) for A32 & A41 Missing primary thickness beamer profiles (Top Heading) for A25, A27 & A41
| 02SL - Stations (LUL) | Cxxx-NCR-001543 | NCR | W - PTE-W and PTE-E: __ Hoses blocked |  | Contr | __M |  |  | 2017-07-20 | 2017-07-21 12:35 | 1 | 2017-05-17 15:52 | Tunnelling - Linings - In-situ Concrete | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • While flushing the __ hoses in PTE platform the following hoses have been found blocked: PTE Transition - Box 1 - Track side: 2 hoses blocked ( both black ) PTE Transition - Box 1 - Platform side: 2 hoses blocked ( both black ) PTE Block 0 - Box 2 - Track side: 1 hose blocked ( red ) PTE Block 3 - Box 1 - Track side : 1 hose blocked ( red ) PTE Block 3 - Box 2 - Track side : 2 hoses blocked ( blue and green ) PTE Block 3 - Box 4 - Platform side : 1 hose blocked ( black ) PTE Block 3 - Box 5 - Platform side : 1 hose blocked ( blue ) PTE Block 4 - Box 2 - Track side : 1 hose blocked ( blue ) PTE Block 5 - Box 2 - Track side : 1 hose blocked ( yellow ) PTE Block 5 - Box 1 - Platform side : 4 hoses blocked ( transparent, blue, green and red ) PTE Block 5 - Box 2 - Platform side : 1 hose blocked ( yellow ) PTE Block 5 - Box 3 - Platform side : 2 hoses blocked ( black and blue ) PTE Block 6 - Box 3 - Track side : 1 hose blocked ( green ) PTE Block 6 - Box 3 - Platform side : 3 hoses blocked ( Green, Red, Blue ) PTE Block 7 - Box 2 - Track side : 1 hose blocked ( red ) PTE Block 7 - Box 2 - Platform side : 1 hose blocked ( red ) PTE Block 8 - Box 1 - Platform side : 1 hose blocked ( red ) PTE Block 8 - Box 2 - Platform side : 1 hoses blocked ( red ) PTE Block 10 - Box 2 - Platform side : 4 hoses blocked ( blue, green, red and yellow ) PTE Block 10 - Box 2 - Platform side : 5 hoses blocked ( black, green, red and two yellows ) PTE Block 11 - Box 3 - Platform side : 1 hose blocked ( black ) PTE Block 12 - Box 1 - Track side : 1 hose blocked ( black ) PTE Block 12 - Box 2 - Track side : 1 hose blocked ( yellow ) PTE Block 12 - Box 4 - Platform side : 1 hose blocked ( yellow ) PTE Block 13 - Box 1 - Track side : 1 hose blocked ( blue ) PTE Block 13 - Box 2 - Track side : 1 hose blocked ( yellow ) PTE Block 13 - Box 1 - Platform side : 3 hoses blocked ( yellow, blue and black ) PTE Block 13 - Box 4 - Platform side : 2 hoses blocked ( blue ) PTE Block 14 - Box 2 - Track side : 2 hoses blocked ( both black ) PTE Block 14 - Box 4 - Track side : 2 hoses blocked ( both yellow ) PTE Block 14 - Box 5 - Track side : 2 hoses blocked ( both yellow ) PTE Block 14 - Box 2 - Platform side : 3 hoses blocked ( yellow, 1 transparent and 1 black ) PTE Block 15 - Box 2 - Track side : 2 hoses blocked ( both bleu ) PTE Block 15 - Box 1 - Platform side : 1 hose blocked ( transparent) PTE Block 16 - Box 1 - Track side : 1 hose blocked ( transparent ) PTE Block 16 - Box 3 - Track side : 3 hoses blocked ( transparent and 2 yellow ) PTE Block 16 - Box 2 - Platform side : 3 hoses blocked ( 2 black and 1 transparent ) PTE Block 16 - Box 3 - Platform side : 1 hose blocked ( black ) PTE Block 17 - Box 3 - Track side : 3 hoses blocked ( red and 2 yellow ) PTE Block 17 - Box 1 - Platform side : 2 hoses blocked ( black and yellow ) PTE Block 18 - Box 1 - Track side : 1 hose blocked ( blue ) PTE Block 18 - Box 3 - Track side : 1 hose blocked ( transparent ) PTE Block 18 - Box 4 - Track side : 2 hoses blocked ( black and yellow ) PTE Block 18 - Box 2 - Platform side : 2 hoses blocked ( transparent and red ) PTE Block 18 - Box 3 - Platform side : 4 hoses blocked ( two yellow and two red ) PTE Block 18 - Box 4 - Platform side : 1 hose blocked ( transparent ) PTE Block 19 - Box 2 - Track side : 1 hose blocked ( yellow ) PTE Block 19 - Box 4 - Track side : 1 hose blocked ( green ) PTE Block 19 - Box 5 - Track side : 4 hoses blocked ( black, transparent, red and yellow ) PTE Block 19 - Box 1 - Platform side : 2 hoses blocked ( black and yellow ) PTE Block 19 - Box 3 - Platform side : 1 hose blocked ( blue ) PTE Block 19 - Box 5 - Platform side : 3 hoses blocked ( transparent and two yellow ) PTE Block 20 - Box 1 - Track side : 1 hose blocked ( black ) PTE Block 20 - Box 2 - Track side : 3 hoses blocked ( black and 2 yellow ) PTE Block 20 - Box 1 - Platform side : 1 hose blocked ( yellow ) PTE Block 21 - Box 3 - Track side : 1 hose blocked ( yellow ) PTE Block 21 - Box 1 - Platform side : 1 hose blocked ( transparent ) PTE Block 21 - Box 3 - Platform side : 1 hose blocked ( yellow ) PTE Block 22 - Box 1 - Track side : 10 hoses blocked ( 2 yellow, 4 green, red and 3 black ) PTE Block 22 - Box 2 - Track side : 5 hoses blocked ( 2 yellow, 2 red and black ) PTE Block 22 - Box 3 - Track side : 2 hoses blocked ( green and red ) PTE Block 22 - Box 4 - Track side : 1 hose blocked ( red ) PTE Block 22 - Box 5 - Track side : 2 hoses blocked ( yellow and green ) PTE Block 22 - Box 1 - Platform side : 6 hoses blocked ( 2 yellow, 2 green and 2 red ) PTE Block 22 - Box 2 - Platform side : 1 hose blocked ( black ) PTE Block 22 - Box 3 - Platform side : 1 hose blocked ( red ) PTE Block 22 - Box 4 - Platform side : 2 hoses blocked ( transparent and red ) PTE Block 22 - Box 5 - Platform side : 2 hoses blocked ( transparent and red ) • Flushing records and schematics can be seen in Att.02 and Att.03 Please note that Att.01 is now superseded by Att.02 and Att.03
| 02SL - Stations (LUL) | Cxxx-NCR-001544 | NCR | L - AP2 Block 1/2: Profile bars missing |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-08-04 | 2017-07-19 17:25 | -16 | 2017-05-19 10:08 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | • On 17/05/17, __ found out that two BM63 long L-bars were missing in AP2 Block 1&2 box out • Location can be seen in Att.01 and photo in Att.02 • Please note that the box out was requested to install a snatch block in AP2 to enable the good handover of ES2, refer to Cxxx-FCD-000926 (Att.03)
| 02SL - Stations (LUL) | Cxxx-NCR-001545 | NCR | L - PTE-W Invert encroachment from ch 18 to 30 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-07-14 | 2017-07-21 09:06 | 7 | 2017-06-01 14:17 | Tunnelling - Linings - In-situ Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • On May 2017, during L076 certification package preparation, scans have shown some areas in the PTE-W block 17 and 18 inverts encroaching the CTRL by max 20mm. • This can be seen Att.01 profile scans and confirmed by Att.02 profile scans
| 02SL - Stations (LUL) | Cxxx-NCR-001546 | NCR | L - ES3 Block 8: Missing couplers |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-06-29 | 2017-07-20 13:46 | 21 | 2017-05-30 15:42 | Tunnelling - Linings - In-situ Concrete | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • On 29/05/17 longitudinal B12 NF2 (BM06) couplers in ES3 block 8 have been found missing. • This is confirmed by Att.01 photo • Location can be seen in Cxxx-MMD-C4-DDD-C101_Z-00505 annotated drawing ( Att.02 )
| 02SL - Stations (LUL) | Cxxx-NCR-001547 | NCR | W - CP2 South: Encroachment of the FP profile |  | Contr | __M |  |  | 2018-02-14 | 2018-01-22 13:55 | -23 | 2017-05-30 10:24 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • After review of the latest fire proofing profile in CP2 south ch 4 to ch 8, some areas have been found encroaching the CTRL. • They are highlighted in red in Att.01 scan.
| 02SL - Stations (LUL) | Cxxx-NCR-001548 | NCR | W - EP2: __ hoses blocked |  | Contr | __M |  |  | 2017-06-13 | 2017-06-08 07:52 | -5 | 2017-05-30 10:44 | Tunnelling - Linings - In-situ Concrete | 1000 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • While flushing the __ hoses in EP2 the following hoses have been found blocked: EP2 Block 1 - Box 2 - LHS: 2 hoses blocked ( 1 black and 1 green ) EP2 Block 1 - Box 1 - RHS: 3 hoses blocked ( 1 black, 1 blue and 1 white ) EP2 Block 1 - Box 2 - RHS: 1 hose blocked ( yellow ) EP2 Block 2 - Box 2 - LHS: 3 hoses blocked ( 1 white, 1 green and 1 black ) EP2 Block 2 - Box 2 - RHS: 3 hoses blocked ( 1 white, 1 green and 1 black ) EP2 Block 4 - Box 2 - LHS: 3 hoses blocked ( 1 white, 1 green and 1 red ) • Flushing records and schematics can be seen in Att.01
| 02SL - Stations (LUL) | Cxxx-NCR-001549 | NCR | W - VA4: __ hoses blocked |  | Contr | __M |  |  | 2017-06-16 | 2017-06-19 13:03 | 3 | 2017-06-05 16:06 | Tunnelling - Linings - In-situ Concrete | 1000 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • While flushing the __ hoses in VA4 the following hoses have been found blocked: VA4 / DSS Connection - Box 1 - West side: 3 hoses blocked ( 2 white and 1 black ) VA4 / DSS Connection - Box 2 - West side: 1 hose blocked ( white ) VA4 / DSS Connection - Box 3 - West side: 1 hose blocked ( white ) VA4 / DSS Connection - Box 5 - West side: 2 hoses blocked ( white and red ) VA4 / DSS Connection - Box 1 - East side: 2 hoses blocked ( 2 black ) VA4 / DSS Connection - Box 2 - East side: 1 hose blocked ( white ) VA4 / DSS Connection - Box 3 - East side: 1 hose blocked ( white ) VA4 / DSS Connection - Box 5 - East side: 2 hoses blocked ( white and red ) • Flushing records and schematics can be seen in Att.01
| 02SL - Stations (LUL) | Cxxx-NCR-001550 | NCR | L - CH2: Leak in the invert ch 62-66 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-08-04 | 2017-07-17 14:59 | -18 | 2017-06-01 07:44 | Tunnelling - Linings - In-situ Concrete | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • On 16/05/17 during condition survey site visit, CH2 invert has been found wet due to final cleaning done before the handover of the area to Cxxx. Decision to wait for water to dry and to monitor the area taken with CRL and Cxxx • See Att.01 for extract of the CH2 condition survey report ( Cxxx-__M-C4-RGN-C101-50142 ) • After a couple of days one area in the invert in ch 62-66 was found still wet
| 02SL - Stations (LUL) | Cxxx-NCR-001551 | NCR | W - EP1: __ hoses blocked |  | Contr | __M |  |  | 2017-07-19 | 2017-06-22 11:02 | -27 | 2017-06-05 08:01 | Tunnelling - Linings - In-situ Concrete | 1000 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • While flushing the __ hoses in EP1 the following hoses have been found blocked: EP1 - Box 1 - LHS: 1 hose blocked ( 1 white ) EP1 - Box 4 - LHS: 3 hoses blocked ( 1 green, 1 red and 1 yellow ) EP1 - Box 1 - RHS: 1 hose blocked ( 1 red ) EP1 - Box 2 - RHS: 5 hoses blocked ( 1 white, 1 green and 3 yellow ) EP1 - Box 3 - RHS: 3 hoses blocked ( 1 white and 1 black ) EP1 - Box 4 - RHS: 8 hoses blocked ( 3 blue, 1 red, 1 green, 1 yellow and 2 black ) EP1 / DSS connection - Box 1 - West side: 4 hoses blocked ( 1 green, 1 red, 1 blue and 1 black ) EP1 / DSS connection - Box 3 - West side: 2 hoses blocked ( both yellow ) EP1 / DSS connection - Box 1 - East side: 4 hoses blocked ( 1 green, 1 red, 1 blue and 1 black ) EP1 / DSS connection - Box 3 - East side: 2 hoses blocked ( both yellow ) • Flushing records and schematics can be seen in Att.01a Please note that Att.01 is superseded by Att.01a
| 02SL - Stations (LUL) | Cxxx-NCR-001552 | NCR | L - CH5 chutes leaks |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-08-18 | 2017-08-18 14:36 | 0 | 2017-08-04 10:27 | Tunnelling - Linings - In-situ Concrete | 6000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | • On 02/06/16 leaks at the bottom of both chutes in CH5 have been reported by Cxxx, area already handed over. • On 07/06/17 CH5 chutes have been inspected and internal diameter checked. This was done using a 435mm diameter template with long tie rod. As shown in Att.01 checksheet and Att.02 photos template gone through all the way without any problem.
| 02SL - Stations (LUL) | Cxxx-NCR-001553 | NCR | L - AP6 Portal leak |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-08-18 | 2017-08-18 13:12 | 0 | 2017-08-08 12:34 | Tunnelling - Linings - In-situ Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | • On June 2017, after handing over the area to Cxxx, some leaks in the portal have been reported.
| 02SL - Stations (LUL) | Cxxx-NCR-001554 | NCR | W - VA5: __ hoses blocked |  | Contr | __M |  |  | 2017-06-16 | 2017-06-15 09:13 | -1 | 2017-06-05 16:10 | Tunnelling - Linings - In-situ Concrete | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • While flushing the __ hoses in VA5 the following hoses have been found blocked: VA5 Block 1 - Box 2 - LHS: 2 hoses blocked ( 1 green and 1 black ) VA5 Block 1 - Box 3 - LHS: 1 hose blocked ( black ) VA5 Block 1 - Box 4 - LHS: 1 hose blocked ( transparent ) VA5 Block 1 - Box 1 - RHS: 2 hoses blocked ( both green ) VA5 Block 1 - Box 2 - RHS: 1 hose blocked ( green ) VA5 Block 1 - Box 3 - RHS: 2 hoses blocked ( red and yellow ) VA5 Block 2 - Box 1 - LHS: 1 hose blocked ( transparent ) VA5 Block 2 - Box 2 - LHS: 1 hose blocked ( green ) VA5 Block 2 - Box 1 - RHS: 1 hose blocked ( transparent ) VA5 Block 2 - Box 2 - RHS: 1 hose blocked ( green ) VA5 Block 6 - Box 1 - LHS: 1 hose blocked ( transparent ) VA5 Block 6 - Box 2 - LHS: 1 hose blocked ( yellow ) VA5 Block 6 - Box 3 - LHS: 1 hose blocked ( transparent ) VA5 Block 6 - Box 4 - LHS: 3 hoses blocked ( all yellow ) VA5 Block 6 - Box 2 - RHS: 1 hose blocked ( blue ) VA5 Block 6 - Box 4 - RHS: 2 hoses blocked ( both yellow ) VA5 Block 6 - Box 5 - RHS: 3 hoses blocked ( all blue ) VA5 / DSS connection - Box 1a - West side: 4 hoses blocked ( red, black, green and blue ) VA5 / DSS connection - Box 2a - West side: 2 hoses blocked ( both yellow ) VA5 / DSS connection - Box 1b - East side: 4 hoses blocked ( red, black, green and blue ) VA5 / DSS connection - Box 2b - East side: 2 hoses blocked ( both yellow ) • Flushing records and schematics can be seen in Att.01
| 02SL - Stations (LUL) | Cxxx-NCR-001555 | NCR | L - CH1-2: Bent bars in the invert north side |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-08-04 | 2017-07-03 15:10 | -32 | 2017-06-08 08:40 | Tunnelling - Linings - In-situ Concrete | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | • On 06/06/17 in the CH1-2 invert north side BM20 ( B16 bars ) have found bent near CP4 eye, see Att.01 photos In total 15bars on the west side and 3bars in the east side were bent. • Affected bars can be seen in Att.01 photos and Att.02 Mark up drawing for location
| 02SL - Stations (LUL) | Cxxx-NCR-001556 | NCR | W - CP2 South: Exposed steel reinforcement during fireproofing trimming |  | Contr | __M |  |  | 2017-06-26 | 2017-06-22 09:08 | -4 | 2017-06-12 09:01 | Tunnelling - Linings - Sprayed Concrete | 2000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • On 10/06/17 during trimming works for NCR 1547 ( CP2 South: Encroachment of the FP profile ) stainless steel reinforcement was exposed in ch 12-14 west side • This can be seen in Att.01 photo
| 02SL - Stations (LUL) | Cxxx-NCR-001557 | NCR | L - ES3 Block 1: Couplers damaged in the invert |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-06-30 | 2017-07-10 14:40 | 10 | 2017-06-16 12:36 | Tunnelling - Linings - In-situ Concrete | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | • On 09/06/17 the ES3 Block 1 FF couplers have been found damaged or lost on the north and south side. • On the north side none of the couplers can be used whereas on the south side some couplers can be used
| 02SL - Stations (LUL) | Cxxx-NCR-001558 | NCR | W - CP2 North: Fire proofing under thickness and encroachment of the CTRL |  | Contr | __M |  |  | 2017-06-27 | 2017-07-21 08:09 | 24 | 2017-06-13 07:44 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A - Encroachment: • After review of the latest fire proofing profile scans in CP2 north ch 4 to ch 26, some areas have been found encroaching the CTRL. • They are highlighted in red in Att.01 scan and Att.02 profile scans B - Fire proofing underthickness: • After review of the latest fire proofing thickness scans in CP2 north ch 4 to ch 26, some thickness have been found below the required 50mm. • They are highlighted in red in Att.03 scan and Att.04 profile scans
| 02SL - Stations (LUL) | Cxxx-NCR-001559 | NCR | W - CS1: Fire proofing profile above CTRL+100mm |  | Contr | __M |  |  | 2017-06-27 | 2017-06-22 12:41 | -5 | 2017-06-13 08:09 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • After review of the fire proofing profile scans in CS1 some areas have been found above the CTRL +100mm profile. • They are highlighted in blue in Att.01 scan and confirmed by profile scans, see Att.02
| 02SL - Stations (LUL) | Cxxx-NCR-001560 | NCR | W - CS1: __ Hoses blocked |  | Contr | __M |  |  | 2017-06-27 | 2017-06-22 11:58 | -5 | 2017-06-13 08:49 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • While flushing the __ hoses in VA4 the following hoses have been found blocked: CP2 North / CS1 Junction - Box 1 - East side: 1 hose blocked ( black ) CP2 South / CS1 Junction - Box 1 - East side: 4 hoses blocked ( 2 black and 2 red ) CP2 South / CS1 Junction - Box 2 - East side: 2 hoses blocked ( 1 yellow and 1 black ) CP2 South / CS1 Junction - Box 1 - West side: 3 hoses blocked ( 1 black, 1 red and 1 white ) CP2 South / CS1 Junction - Box 2 - West side: 2 hoses blocked ( 1 green and 1 white ) CS1 level 87.6 - Box 1 - East side: 3 hoses blocked ( 1 blue, 1 white and 1 yellow ) CS1 level 87.6 - Box 2 - East side: 1 hose blocked ( green ) CS1 level 87.6 - Box 1 - West side: 2 hoses blocked ( both white ) CS1 level 87.6 - Box 2 - West side: 2 hoses blocked ( white and black ) • Flushing records and schematics can be seen in Att.01
| 02SL - Stations (LUL) | Cxxx-NCR-001561 | NCR | L - CH3: Hammer tapping requirements not achieved |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-07-07 | 2017-07-21 15:43 | 14 | 2017-06-19 09:38 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | On 10/01/17 and 06/02/17, hammer tapping of Secondary Lining Second Layer has been done less than 72 hours after spraying and only above elevation 93.7m. (see Att01.)
| 02SL - Stations (LUL) | Cxxx-NCR-001562 | NCR | W - CP2 South: __ hoses blocked |  | Contr | __M |  |  | 2017-07-31 | 2017-07-21 08:26 | -10 | 2017-06-26 12:36 | Tunnelling - Linings - In-situ Concrete | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • While flushing the __ hoses in CP2 South the following hoses have been found blocked: CP2 South Block 1 - Box 1 - East side: 2 hoses blocked ( both blue ) CP2 South Block 1 - Box 2 - East side: 2 hoses blocked ( blue and red ) CP2 South Block 1 - Box 1 - West side: 1 hose blocked ( blue ) CP2 South Block 2 - Box 1 - East side: 1 hose blocked ( yellow ) CP2 South Block 2 - Box 2 - East side: 2 hoses blocked ( red and black ) CP2 South Block 2 - Box 2 - West side: 2 hoses blocked ( red and yellow ) • Flushing records can be seen in Att.01
| 02SL - Stations (LUL) | Cxxx-NCR-001563 | NCR | L - CP4a: Hollow in the fire proofing layer ch 14 east side |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-07-07 | 2017-07-21 14:41 | 14 | 2017-06-19 11:15 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | - During 13/06/17 NS hammer tapping before handover of CP4a to following contractor, one hollow has been found on the fire proofing layer (RL2). - Hollow is on the east side at axis level ch : 14.000 - Size = 800*300mm See Att.01 for the hammer tapping checksheet and Att.02 for photos of the hollow
| 02SL - Stations (LUL) | Cxxx-NCR-001564 | NCR | L - PTE-W / CP 4: One hollow in the crown ch 74 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-07-29 | 2017-07-21 09:01 | -8 | 2017-06-29 07:59 | Tunnelling - Linings - Sprayed Concrete | 6000 |  | Workmanship | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • During 14/06/17 hammer tapping before handover of CP4 to following contractor, one hollow has been found on the fire proofing layer ( RL2). • See Att.01 for the hammer tapping checksheet and Att.02 for photo of the hollow • Hollow is on the crown from 11-12 o’clock at ch : 74.000. Size =1200*2500mm
| 02SL - Stations (LUL) | Cxxx-NCR-001565 | NCR | W - EBRT-DSS invert - reduced cover to invert rebar |  | Contr | __M |  |  | 2017-07-20 | 2017-07-06 10:29 | -14 | 2017-07-06 08:41 | Tunnelling - Tunnelling General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • On 16/06/17 in order to inspect whether it would be possible to trim cover enabling an adjustment to Cxxx trackform, Cxxx has cored inspection windows in the DSS / EBRT and PTE-W invert. • It was established that the level of the invert by Cxxx was satisfactory, however the reduced cover (<70mm) was detected, worst case is 40mm cover, and no trimming of the invert has been permitted. This is confirmed by Att.01 report • Inspection windows were remediated by Cxxx using Nanocrete R4 mortar.
| 02SL - Stations (LUL) | Cxxx-NCR-001566 | NCR | L - AP2 SL: Missing tests and documentation |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-08-03 | 2017-07-21 13:44 | -13 | 2017-07-20 08:43 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Cxxx-__M-C4-LLG-C101-50282 Deliverable Records for LIV AP2 Cast In-situ Invert - Package No L022 Invert Layer – ITP item C1 Missing compressive strength results for AP2 – Block 3. See Att01. Cxxx-__M-C4-LLG-C101-50284 Deliverable Records for LIV AP2 Portal Opening - Package No L022 Portal – ITP item 7.3; 7.4 Missing compressive strength and density results for SCC cube for AP2 Portal – Lift 3. See Att02. Cxxx-__M-C4-LLG-C101-50286 Deliverable Records for LIV AP2 Sheet Waterproofing Membrane - Package No L022 Sheet – ITP item 2.7 Missing Hold Point signatures on Sheet Membrane Installation Checksheet Page #2 (__ Form D3-94) for Acceptance of sheet membrane system prior protective layer installation for AP2 Block 5 (QC & CRL Signatures) and Blocks 6 and 7 (CRL Signature). See Att03.
| 02SL - Stations (LUL) | Cxxx-NCR-001567 | NCR | L - CP3a Invert ch 9-11: Encroachment of the fire proofing profile |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-08-19 | 2017-07-21 09:02 | -29 | 2017-06-26 09:03 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | • On 24/06/2017, after review of the final fire proofing profile scans in CP3a, area in the invert west side from ch 9 to 11has been found encroaching the CTRL zero lining by max 30mm • It is highlighted in red in Att.01 scan and confirmed by Att.02 profiles scans
| 02SL - Stations (LUL) | Cxxx-NCR-001568 | NCR | L - CP6: Encroachment of the fire proofing profile |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-07-27 | 2017-07-19 14:08 | -8 | 2017-06-27 12:53 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • On 26/06/2017, after review of the final fire proofing profile scans in CP6, six areas have been found encroaching the CTRL zero lining by max 30mm • They are highlighted in red in Att.01 scan and confirmed by Att.02 profiles scans
| 02SL - Stations (LUL) | Cxxx-NCR-001569 | NCR | L - AP6: Hollow spot found around ch 50 crown |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-07-17 | 2017-07-19 14:11 | 2 | 2017-06-27 15:57 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | • During DS 27/06/17 hammer tapping, one hollow spot has been found in the fire proofing layer. • Hollow is at 1'oclock looking north and around ch 50.000 - Size = 200mm x 300mm See Att.01a for the hammer tapping checksheet and Att.02 for photos of the hollow Please note that Att.01 is now superseded by Att.01a.
| 02SL - Stations (LUL) | Cxxx-NCR-001570 | NCR | L - AP9 SL: Missing tests and documentation |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-10-04 | 2017-10-12 09:56 | 8 | 2017-09-20 07:18 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Cxxx-__M-C4-LLG-C101-50307 Deliverable Records for LIV AP9 __ Sprayed Waterproofing Membrane - Package No L030 __ – ITP item A3, A4, 1.3, 1.4, 2.1, 2.2, 2.6, 2.8: - Missing __ Pre-Placement Checksheet (__ Form D3-98 1/4) and Placement checksheet (__ Form D3-101 2/4) for AP9 D-Wall Invert, Ch. 10.0 to 11.5
| 02SL - Stations (LUL) | Cxxx-NCR-001571 | NCR | L - ES3 PL: Missing tests and documentation |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-09-05 | 2017-09-14 14:21 | 9 | 2017-08-22 09:20 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | • Cxxx-__M-C4-LLG-C101-50297 - ES3 Pilot (L062) 1) There are no visual records of cores being taken in CH1-2, ES3 or CH6 contained within the laboratory compliance reports for the period June, July, August, September, October or November 2016. Records cannot be located with __. 2) Missing subcarrier check sheets (D3-125) for ES3 Pilot A14, A25, A32 3) Missing primary profile & primary thickness beamer scans for ES3 Pilot A33 • Cxxx-__M-C4-LLG-C101-50298 - ES3 Enlargement (L062) 4) There are no visual records of cores being taken in CH1-2, ES3 or CH6 contained within the laboratory compliance reports for November 2016, January 2017 and February 2017. Records cannot be located with __. 5) Missing reinforcement check sheets (D3-26) for ES3 Enlargement A1, A2, A4, A5&6 6) Missing primary profile and primary thickness beamer profiles for ES3 Enlargement A25 7) Missing excavation profile, primary profile and primary thickness for ES3 Enlargement A33
| 02SL - Stations (LUL) | Cxxx-NCR-001572 | NCR | L - AP11&12 SL: Missing Tests and documentation |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-07-20 | 2017-07-21 11:07 | 1 | 2017-07-06 14:09 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | • Cxxx-__M-C4-LLG-C101-50275 Deliverable Records for AP11 and AP12 Regulation Layer, Secondary Lining SCL & Combined Secondary Lining / Fireproofing - Package No. L034: Secondary 1st Layer: ITP item 5.12 Missing hammer tapping check sheet (__ Form D3-80) for AP11 Secondary 1st over far face steel, Ch. 16 to headwall.
| 02SL - Stations (LUL) | Cxxx-NCR-001573 | NCR | L - CH6: Two hollow spots found in the combined fire proofing layer |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-07-19 | 2017-07-21 16:25 | 2 | 2017-07-05 08:57 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • During DS 04/07/17 hammer tapping, two hollow spots have been found in the combined proofing layer. • Hollows are above the wing wall on the south side at chainage 121 and 125 - Sizes: 0.15m x 0.40mm and 0.5m x 0.1m • This can be seen in Att.01 hammer tapping checksheet
| 02SL - Stations (LUL) | Cxxx-NCR-001574 | NCR | W - SL Tunnels: Additional __ hoses blocked |  | Contr | __M |  |  | 2017-09-28 | 2017-09-22 11:48 | -6 | 2017-07-14 09:31 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | While flushing the hoses in WHI, the following hoses have been found blocked: • 1) In VA4 / DSS Connection: VA4 / DSS Connection - Box 1 - West side: 2 hoses blocked ( both white ) VA4 / DSS Connection - Box 2 - West side: 2 hoses blocked ( white and red ) VA4 / DSS Connection - Box 4 - West side: 1 hose blocked ( white ) VA4 / DSS Connection - Box 5 - West side: 1 hose blocked ( white ) VA4 / DSS Connection - Box 1 - East side: 2 hoses blocked ( 2 black ) VA4 / DSS Connection - Box 2 - East side: 1 hose blocked ( white ) VA4 / DSS Connection - Box 3 - East side: 1 hose blocked ( white ) VA4 / DSS Connection - Box 4 - East side: 2 hoses blocked ( white and red ) All flushing records checksheets can be seen in Cxxx-__M-C4-LLG-D061-50163 As-Built Schematic for VA4 Waterproofing Membrane Package No W016. Please note that Cxxx-NCR-001549, already raised for __ hoses blocked in VA4, is not anymore relevant and is superseded by Cxxx-NCR-001574. • 2) In CP3: CP3 Block 1 - Box 1b – East side: 2 hoses blocked ( both blue ) CP3 Block 2 - Box 1a – West side: 1 hose blocked ( blue ) CP3 Block 2 - Box 1b – East side: 2 hoses blocked ( black and transparent ) CP3 Block 3 - Box 1a – West side: 1 hose blocked (transparent ) CP3 Block 4 - Box 1a – West side: 2 hoses blocked ( blue and transparent ) CP3 Block 4 - Box 2a – West side: 1 hose blocked ( black ) CP3 Block 4 - Box 1b – East side: 3 hoses blocked ( blue, black and yellow) CP3 Block 4 - Box 2b – East side: 1 hose blocked ( black ) CP3 Block 5 - Box 1a – West side: 3 hoses blocked ( blue, transparent and black ) CP3 Block 6 - Box 1a – West side: 4 hoses blocked ( 3 blue and 1 transparent) CP3 Block 6 - Box 1b – East side: 5 hoses blocked ( 4 blue and 1 transparent) All flushing records checksheets can be seen in Cxxx-__M-C4-LLG-D061-50167 As-Built Schematic for CP3 Waterproofing Membrane Package No W024. Please note that Cxxx-NCR-001356, already raised for __ hoses blocked in CP3, is not anymore relevant and is superseded by Cxxx-NCR-001574. • 3) In EP2: EP2 Block 1 - Box 1b – South side: 3 hoses blocked (black, blue and transparent) EP2 Block 2 - Box 1a – North side: 2 hoses blocked (black and green ) EP2 Block 2 - Box 1b – South side: 2 hoses blocked (both transparent ) EP2 Block 4 - Box 1a – North side: 1 hose blocked ( red ) EP2 Block 4 - Box 1b – South side: 2 hoses blocked ( both blue ) EP2/CH5 Connection – Box 1b – South side: 4 __ hoses ( black, blue, green and red ) All flushing records checksheets can be seen in Cxxx-__M-C4-LLG-D061-50168 As-Built Schematic for EP2 Waterproofing Membrane Package No W028. Please note that Cxxx-NCR-001548, already raised for __ hoses blocked in EP2, is not anymore relevant and is superseded by Cxxx-NCR-001574. • 4) In VA5: VA5 Block 1 - Box 2a – West side: 2 hoses blocked ( black and green ) VA5 Block 1 - Box 3a – West side: 1 hose blocked ( black ) VA5 Block 1 - Box 4a – West side: 1 hose blocked ( transparent ) VA5 Block 1 - Box 1b – East side: 2 hoses blocked ( both green ) VA5 Block 1 - Box 2b – East side: 1 hose blocked ( green ) VA5 Block 1 - Box 3b – East side: 2 hoses blocked ( red, yellow ) VA5 Block 2 - Box 1a – West side: 1 hose blocked ( transparent ) VA5 Block 2 - Box 2a – West side: 1 hose blocked ( green ) VA5 Block 2 - Box 1b – East side: 1 hose blocked ( transparent ) VA5 Block 2 - Box 2b – East side: 1 hose blocked ( green ) VA5 Block 6 - Box 1a – West side: 1 hose blocked ( transparent ) VA5 Block 6 - Box 2a – West side: 1 hose blocked ( yellow ) VA5 Block 6 - Box 3a – West side: 1 hose blocked ( transparent ) VA5 Block 6 - Box 4a – West side: 3 hoses blocked ( all yellow ) VA5 Block 6 - Box 2b – East side: 1 hose blocked ( blue ) VA5 Block 6 - Box 4b – East side: 2 hoses blocked ( both yellow ) VA5 Block 6 - Box 5b – East side: 3 hoses blocked ( all blue ) VA5 / DSS Connection – Box 1a – West side: 4 hoses blocked ( red, black, green, blue ) VA5 / DSS Connection – Box 2a – West side: 2 hoses blocked ( both yellow ) VA5 / DSS Connection – Box 1b – East side: 4 hoses blocked ( red, black, green, blue ) VA5 / DSS Connection – Box 2b – East side: 2 hoses blocked ( both yellow ) All flushing records checksheets can be seen in Cxxx-__M-C4-LLG-D061-50170 As-Built Schematic for VA5 Waterproofing Membrane Package No W018. Please note that Cxxx-NCR-001554, already raised for __ hoses blocked in VA5, is not anymore relevant and is superseded by Cxxx-NCR-001574. • 5) In VA2: VA2 Block 2 - Box 1a – East side: 1 hose blocked ( black ) VA2 Block 2 - Box 2a – East side: 2 hoses blocked ( both transparent ) VA2 Block 2 - Box 2b – West side: 2 hoses blocked ( both transparent ) VA2 / CH5 Connection – Box 2: 2 hoses blocked ( red and black) VA2 / CH5 Connection – Box 6: 2 hoses blocked ( red and black ) All flushing records checksheets can be seen in Cxxx-__M-C4-LLG-D061-50188 As-Built Schematic for VA2 Waterproofing Membrane Package No W014. Please note that Cxxx-NCR-001315, already raised for __ hoses blocked in VA2, is not anymore relevant and is superseded by Cxxx-NCR-001574. • 6) In ES1 and EPW1: ES1 Block 3 - Box 1 – South side: 1 hose blocked ( white ) ES1 Block 3 - Box 2 – South side: 1 hose blocked ( white ) ES1 Block 5 - Box 1 – South side: 1 hose blocked ( white ) ES1 Block 5 - Box 2 – South side: 1 hose blocked ( white ) ES1 Block 6 - Box 1 – South side: 1 hose blocked ( yellow ) ES1 Block 6 - Box 1 – South side: 1 hose blocked ( blue ) ES1 Block 10 - Box 1 – South side: 2 hoses blocked ( white and red ) ES1 Block 10 - Box 2 – South side: 1 hose blocked ( white ) ES1 Block 10 - Box 1 – North side: 2 hoses blocked ( white and red ) ES1 Block 10 - Box 2 – North side: 1 hose blocked ( white ) ES1 / Shaft Connetion - Box 1 – South side: 1 hose blocked ( white ) ES1 / Shaft Connetion - Box 1 – North side: 1 hose blocked ( white ) All flushing records checksheets can be seen in Cxxx-__M-C4-LLG-D061-50194 As-Built Schematic for ES1 and EPW1 Waterproofing Membrane Package No W030 and W032. Please note that Cxxx-NCR-001465, already raised for __ hoses blocked in ES1 and EPW1, is not anymore relevant and is superseded by Cxxx-NCR-001574. • 7) In CP1a CP1a Block 1 - Box 1 - Left side: 3 hoses blocked ( yellow, red and white ) CP1a Block 1 - Box 2 - Left side: 2 hoses blocked ( blue and white ) CP1a Block 1 - Box 1 – Right side: 3 hoses blocked ( yellow, red and white ) CP1a Block 1 - Box 2 - Right side: 2 hoses blocked ( blue and white ) CP1a Block 2 - Box 1 - Left side: 1 hose blocked ( red ) CP1a Block 2 - Box 2 – Left side: 1 hose blocked ( red ) CP1a Block 2 - Box 1 – Right side: 1 hose blocked ( red ) CP1a Block 2 - Box 2 – Right side: 1 hose blocked ( red ) CP1a Block 3 - Box 1 - Left side: 1 hose blocked ( yellow ) CP1a Block 3 - Box 2 - Left side: 1 hose blocked ( blue ) CP1a Block 3 - Box 1 – Right side: 2 hoses blocked ( white and yellow ) CP1a Block 3 - Box 3 - Right side: 2 hoses blocked ( white and blue ) CP1a Block 4 - Box 1 - Left side: 1 hose blocked (white ) CP1a Block 4 - Box 2 - Left side: 1 hose blocked ( white ) CP1a Block 5 - Box 1 - Left side: 3 hoses blocked ( red, white and blue ) CP1a Block 5 - Box 2 - Left side: 2 hoses blocked ( white and yellow ) CP1a Block 5 - Box 4 - Left side: 1 hose blocked ( red ) CP1a Block 5 - Box 1 - Right side: 2 hoses blocked ( red and blue ) CP1a Block 5 - Box 2 - Right side: 1 hose blocked ( yellow ) CP1a Block 5 - Box 4 - Right side: 1 hose blocked ( red ) All flushing records checksheets can be seen in Cxxx-__M-C4-LLG-D061-50197 As-Built Schematic for CP1a Waterproofing Membrane Package No W020. Please note that Cxxx-NCR-001465, already raised for __ hoses blocked in CP1a, is not anymore relevant and is superseded by Cxxx-NCR-001574. • 8) In LCW and WB Cavern: WB Cavern Block 2 - Box 1 - Track side: 1 hose blocked ( 1 blue ) WB Cavern Block 2 - Box 2 - Track side: 1 hose blocked ( 1 yellow ) WB Cavern Block 2 - Box 1 - Platform side: 1 hose blocked ( 1 blue ) WB Cavern Block 2 - Box 2 - Platform side: 1 hose blocked ( 1 yellow ) WB Cavern Block 3 - Box 1 - Platform side: 1 hose blocked ( 1 blue ) WB Cavern Block 3 - Box 2 - Platform side: 1 hose blocked ( 1 yellow ) WB Cavern Block 6 - Box 1 - Track side: 1 hose blocked ( 1 blue ) WB Cavern Block 6 - Box 2 - Track side: 1 hose blocked ( 1 yellow ) WB Cavern Block 7 - Box 2 - Track side: 2 hoses blocked ( both transparent ) WB Cavern Block 7 - Box 4 - Track side: 1 hose blocked ( transparent ) WB Cavern Block 7 - Box 2 - Platform side: 2 hoses blocked ( both blue ) LCW – Box 2 – Track side: 3 hoses blocked ( all blue ) LCW – Box 3 – Track side: 1 hose blocked ( yellow ) All flushing records checksheets can be seen in Cxxx-__M-C4-LLG-D061-500207 As-Built Schematic for WB Cavern and LCW Waterproofing Membrane Package No W010 and W036. Please note that Cxxx-NCR-001421, already raised for __ hoses blocked in WB Cavern and LCW, is not anymore relevant and is superseded by Cxxx-NCR-001574. • 9) In LCE and EB Cavern: EB Cavern Block 1 - Box 1 – North side: 4 hoses blocked ( 2 green, 1 yellow and transparent ) EB Cavern Block 1 - Box 2 – North side: 1 hose blocked ( transparent ) EB Cavern Block 1 - Box 1 – South side: 3 hoses blocked ( 1 green and 2 yellow ) EB Cavern Block 1 - Box 2 – South side: 1 hose blocked ( transparent ) EB Cavern Block 3 - Box 1 – North side: 1 hose blocked ( red ) EB Cavern Block 3 - Box 2 – North side: 1 hose blocked ( transparent ) EB Cavern Block 3 - Box 1 – South side: 1 hose blocked ( red ) EB Cavern Block 4 - Box 1 – North side: 1 hose blocked ( red ) EB Cavern Block 4 - Box 1 – South side: 3 hoses blocked ( red, blue and transparent ) EB Cavern Block 4 - Box 2 – South side: 1 hose blocked ( yellow ) EB Cavern Block 5 - Box 1 – North side: 1 hose blocked ( transparent ) EB Cavern Block 5 - Box 2 – North side: 1 hose blocked ( transparent ) EB Cavern Block 5 - Box 1 – South side: 2 hoses blocked ( transparent and blue ) EB Cavern Block 5 - Box 2 – South side: 2 hoses blocked ( transparent and yellow ) EB Cavern Block 6 - Box 2 – South side: 1 hose blocked ( yellow ) EB Cavern Block 7 - Box 1 – North side: 1 hose blocked ( transparent ) EB Cavern Block 7 - Box 1 – South side: 1 hose blocked ( transparent ) EB Cavern Block 9 - Box 2 – North side: 2 hoses blocked ( transparent and yellow ) LCE – Box 1 – North side: 1 hose blocked ( transparent ) LCE – Box 1 – South side: 4 hoses blocked ( 2 blue, transparent and red ) LCE – Box 2 – South side: 1 hose blocked ( red ) All flushing records checksheets can be seen in Cxxx-__M-C4-LLG-D061-500210 As-Built Schematic for EB Cavern and LCE Waterproofing Membrane Package No W037 and W004. Please note that Cxxx-NCR-001466, already raised for __ hoses blocked in EB Cavern and LCE, is not anymore relevant and is superseded by Cxxx-NCR-001574. • 10) In CS1 __ hoses have been re-flushed and all found unblocked, see Cxxx-__M-C4-LLG-D061-500217 As-Built Schematic for CS1 Waterproofing Membrane Package No W049 for the latest flushing records. Please note that Cxxx-NCR-001560, already raised for __ hoses blocked in CS1, is not anymore relevant. • 11) In CP2 North: CP2 North Block 2 - Box 2 – East side: 1 hose blocked ( black ) CP2 North Block 2 - Box 3 – East side: 1 hose blocked ( green ) CP2 North Block 2 - Box 3 – West side: 1 hose blocked ( black ) CP2 North Block 3 - Box 1 – East side: 4 hoses blocked ( blue, green, red and transparent ) CP2 North Block 3 - Box 2 – East side: 2 hoses blocked ( yellow and transparent ) CP2 North Block 3 - Box 1 – West side: 5 hoses blocked ( 2 red, yellow, green and transparent ) All flushing records checksheets can be seen in Cxxx-__M-C4-LLG-D061-500221 As-Built Schematic for CP2 North and CP2 South Waterproofing Membrane Package No W022. Please note that Cxxx-NCR-001503, already raised for __ hoses blocked in CP2 North, is not anymore relevant and is superseded by Cxxx-NCR-001574. For __ hoses blocked in CP2 South, please refer to Cxxx-NCR-001562. • 12) In Crossover: Xover Block 1 - Box 1 – South side: 3 hoses blocked ( 2 blue and 1 yellow ) Xover Block 5 - Box 1 – North side: 2 hoses blocked ( transparent and red ) Xover Block 5 - Box 1 – South side: 3 hoses blocked ( transparent, red and black ) Xover Block 5 - Box 2 – South side: 1 hose blocked ( yellow ) Xover Block 6 - Box 1 – North side: 2 hoses blocked ( transparent and blue ) Xover Block 6 - Box 2 – North side: 1 hose blocked ( yellow ) Xover Block 6 - Box 1 – South side: 2 hoses blocked ( transparent and black ) Xover Block 6 - Box 2 – South side: 1 hose blocked ( yellow ) Xover Block 7 - Box 2 – North side: 1 hose blocked ( transparent ) Xover Block 8 - Box 2 – North side: 1 hose blocked ( transparent ) Xover Block 8 - Box 2 – South side: 1 hose blocked ( transparent ) Xover Block 9 - Box 1 – North side: 2 hoses blocked ( transparent and red ) Xover Block 9 - Box 2 – North side: 1 hose blocked ( transparent ) Xover Block 9 - Box 1 – South side: 1 hose blocked ( red ) Xover Block 9 - Box 2 – South side: 1 hose blocked ( transparent ) Xover Block 10 - Box 1 – North side: 1 hose blocked ( transparent ) Xover Block 10 - Box 2 – North side: 1 hose blocked ( transparent ) Xover Block 10 - Box 1 – South side: 1 hose blocked ( transparent ) All flushing records checksheets can be seen in Cxxx-__M-C4-LLG-D061-500226 As-Built Schematic for Crossover Waterproofing Membrane Package No W039. Please note that Cxxx-NCR-001421, already raised for __ hoses blocked in the Crossover, is not anymore relevant and is superseded by Cxxx-NCR-001574. • 13) In EBRT: EBRT Block 0 - Box 1 – North side: 3 hoses blocked ( 2 green and 1 black ) EBRT Block 0 - Box 2 – North side: 2 hoses blocked ( 1 yellow and 1 black ) EBRT Block 0 - Box 1 – South side: 5 hoses blocked ( 1 transparent and 4 black ) EBRT Block 0 - Box 2 – South side: 6 hoses blocked ( 1 yellow and 5 green ) EBRT Block 0 - Box 3 – South side: 1 hose blocked ( red ) EBRT Block 1 - Box 2 – South side: 2 hoses blocked ( 2 green ) EBRT Block 2 - Box 3 – North side: 1 hose blocked ( transparent ) EBRT Block 2 - Box 3 – South side: 1 hose blocked ( transparent ) EBRT Block 3 - Box 4 – South side: 1 hose blocked ( transparent ) EBRT Block 10 - Box 1 – North side: 1 hose blocked ( transparent ) EBRT Block 10 - Box 4 – North side: 2 hoses blocked ( yellow ) EBRT Block 10 - Box 5 – North side: 1 hose blocked ( transparent ) EBRT Block 10 - Box 5 – South side: 2 hoses blocked ( yellow ) EBRT Block 11 - Box 1 – North side: 2 hoses blocked ( black and transparent ) EBRT Block 11 - Box 2 – North side: 1 hose blocked ( green ) EBRT Block 11 - Box 3 – North side: 1 hose blocked ( black ) EBRT Block 11 - Box 4 – North side: 2 hoses blocked ( transparent and green ) EBRT Block 11 - Box 5 – North side: 2 hoses blocked ( yellow ) EBRT Block 11 - Box 6 – North side: 1 hose blocked ( black ) EBRT Block 11 - Box 1 – South side: 3 hoses blocked ( 2 black and 1 transparent ) EBRT Block 11 - Box 2 – South side: 2 hoses blocked ( both green ) EBRT Block 11 - Box 4 – South side: 2 hoses blocked ( both transparent ) EBRT Block 11 - Box 5 – South side: 2 hoses blocked ( both black ) EBRT Block 11 - Box 6 – South side: 1 hose blocked ( black ) All flushing records checksheets can be seen in Cxxx-__M-C4-LLG-D061-500229 As-Built Schematic for EBRT Waterproofing Membrane Package No W059. Please note that Cxxx-NCR-001466, already raised for __ hoses blocked in EBRT, is not anymore relevant and is superseded by Cxxx-NCR-001574.
| 02SL - Stations (LUL) | Cxxx-NCR-001575 | NCR | W - BYP Backfilling: 7- and 28-day Compressive Strength not achieved for __ |  | Contr | __M |  |  | 2017-08-04 | 2017-08-18 14:59 | 14 | 2017-07-21 13:50 | Tunnelling - Tunnelling General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 7 days and 28 days Compressive Strength was not achieved for __, used for the backfilling of the Bypass. See Att01 - Summary of compressive strength results for HS Daemmer 35 – Whitechapel
| 02SL - Stations (LUL) | Cxxx-NCR-001576 | NCR | L - AP9/CH6: Predimax hoses not installed in the invert |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-08-08 | 2017-08-18 13:16 | 10 | 2017-07-25 14:50 | Tunnelling - Linings - In-situ Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • During construction of the AP9 / CH6 connection the two predimax in the invert have been found not installed, this is shown in Att.01 sketch. • Only the waterbars and two re-injectable hoses have been installed in the invert
| 02SL - Stations (LUL) | Cxxx-NCR-001577 | NCR | L - VD1: Leaks |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-07-29 | 2017-07-28 16:10 | -1 | 2017-07-28 14:30 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | •After handing over VD1 to following contractor, 7 areas have been found leaking
| 02SL - Stations (LUL) | Cxxx-NCR-001578 | NCR | Water Ingress into the Eastbound Tunnels at LIS |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2018-02-09 | 2018-02-28 09:09 | 19 | 2017-07-31 14:38 | Civil - Tunnelling | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | It has been observed that recently there has been standing water in the ventilation corridor under the eastbound tunnel platforms at Liverpool Street. __ are currently undertaking an investigation into the cause of the water ingress before determining if there are to be defect corrections to be undertaken. There is an assumption that the water going into the EB tunnel is coming from the CP6 shaft due to the wash out at the pit bottom. The waterproofing at the shaft pit bottom to CP6, CP5, AP7E and AP7W is not completed yet. Stopping the water going into EB tunnel from the pit bottom will be part of the investigation. The conclusion of the investigation will decide whether any remedial works will be required. If this proves no defects then this NCR can be closed. See Att.01.
| 02SL - Stations (LUL) | Cxxx-NCR-001579 | NCR | L - ES3: Cracks injection in the cast in situ blocks 1 and 9 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-09-05 | 2017-09-14 13:17 | 9 | 2017-08-22 13:33 | Tunnelling - Linings - In-situ Concrete | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A) Cracks on lining: • On 01/08/17, during joint inspection of ES3 block 1 two cracks have been found. One crack on north wall approx. 1.1mm width and second crack on south wall approx. 1.2 mm width. Refer to Att.01 • On 16/08/17, during post pour inspection of ES3 block 9, one 2m long crack ( 0.4mm width ) has been found. See Att.02 for the ES3 block 9 post pour checksheet B) Cracks on construction joints: Joint Block 1-2: No visible crack Joint Block 2-3: One 0.5mm wide crack along the joint Joint Block 3-4: One 0.3mm wide crack along the joint Joint Block 4-5: One 400mm long crack in the crown along the joint Joint Block 5-6: No visible crack Joint Block 6-7: One 300mm long 0.3mm wide crack in crown along the joint Joint Block 7-8: One 300mm long 4mm wide crack in crown along the joint Joint Block 8-9: No visible crack See Att.04 for the ES3 post pour checksheets
| 02SL - Stations (LUL) | Cxxx-NCR-001580 | NCR | Water Ingress into the Westbound Tunnels at LIS |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2018-02-09 | 2018-02-27 16:14 | 18 | 2017-08-03 14:40 | Civil - Tunnelling | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | It has been observed that recently there has been standing water in the ventilation corridor under the Westbound tunnel platforms at Liverpool Street. __ are currently undertaking an investigation into the cause of the water ingress before determining if there are to be defect corrections to be undertaken. There is an assumption that the water going into the WB tunnel is coming from the CP5 shaft due to the wash out at the pit bottom. The waterproofing at the shaft pit bottom to CP6, CP5, AP7E and AP7W is not completed yet. Stopping the water going into WB tunnel from the pit bottom will be part of the investigation. The conclusion of the investigation will decide whether any remedial works will be required. If this proves no defects then this NCR can be closed.
| 02SL - Stations (LUL) | Cxxx-NCR-001581 | NCR | L - AS1: Incorrect Setting Out to Near Face Reinforcement |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-08-23 | 2017-09-14 14:06 | 22 | 2017-08-09 10:07 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | • On 04/08/17, radius used by __ construction team for the near face reinforcement installation in AS1 bays 1 to block 6 was found to be the incorrect one. Installation was done using the old radius ( 6.25 radius ) instead of the 6.15m radius. As agreed in Cxxx-RFI-001130, __ had an agreement to reduce the internal radius to 6.15m. This was due to space constraints of the existing cast in situ collar. • It was also noted that the U-bars in bays 1 to 6 have a changing front cover and do not align with the NF rebars, despite being bent in line with the bar bending schedule.
| 02SL - Stations (LUL) | Cxxx-NCR-001582 | NCR | Leaks in Whitechapel Station |  | Crossrail | XRL | LIS - Liverpool Street Station (Central) |  | 2018-02-09 | 2018-02-27 13:52 | 18 | 2017-08-08 14:58 | Civil - Tunnelling | 500 |  | System Defect | Repair | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | It has been observed that there is standing water in the under platform areas under the Westbound tunnel platforms, in VA4 and VA5 at Whitechapel Station. __ are currently undertaking an investigation into the cause of the water ingress before determining if there is any remedial action required. It appears that the water under platform in PTW is coming from the PRD drainage discharge channels. It is unclear where the water in both VA4 and VA5 is coming from. However, all areas are to be dried up entirely and then monitored to check for leaks. Please see attached photographs of exact areas of ingress (the attached schematic illustrates the location of each). If no defects are found then this NCR can be closed. Update 27/09/17: Whitechapel Station has been inspected and monitored for leaks over the past 2 weeks. See Att.01 and 02 detailing locations of observed leaks and action to be taken. A meeting is being held Thursday 28/09/17 to update leak sealing progress and reconcile all areas on of under platform standing water. Following this, to target these areas of standing water, an injection sequence for platform termination boxes is to be added to this NCR.
| 02SL - Stations (LUL) | Cxxx-NCR-001583 | NCR | L - GAD2: No maxibor as-built survey |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-09-14 | 2017-09-11 14:10 | -3 | 2017-08-31 08:00 | Tunnelling - Tunnelling General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | • During Cxxx-__M-C2-LLG-C101-50246 Deliverable Records for Drilling of Supplementary TAMs in LIV GAD2 for Corrective Grouting Package No L069 preparation no Maxibor as-built survey was available for review.
| 02SL - Stations (LUL) | Cxxx-NCR-001584 | NCR | L - AP10a: Leak in the cast in-situ |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-12-22 | 2017-12-22 09:25 | 0 | 2017-08-31 09:00 | Tunnelling - Linings - In-situ Concrete | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | • On August 2017, after handing over the area to Cxxx, some leaks in the AP10a cast in situ have been reported.
| 02SL - Stations (LUL) | Cxxx-NCR-001585 | NCR | L - CH5: Leak near the 2nd chute away from headwall |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-09-30 | 2017-10-11 08:47 | 11 | 2017-08-31 10:17 | Tunnelling - Linings - In-situ Concrete | 10000 |  | Supervision/Management | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | • On August 2017, after handing over the area to Cxxx, one leak near the second chute away from the headwall, has been reported. • See Att01 for a photo
| 02SL - Stations (LUL) | Cxxx-NCR-001586 | NCR | L - AS1 Slip-form encroaching profile |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-10-12 | 2017-10-12 14:12 | 0 | 2017-09-07 14:02 | Tunnelling - Linings - Sprayed Concrete | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | In Access Shaft AS1, inverts of the slip-form in AP7E-AP7W-CP6-CP5 are encroaching the primary lining thickening profile (75.477m). Refer to Att01 for levels before trimming. As a consequence there is not sufficient space proofing to deliver the secondary lining within tolerances (Top of beam = +76.181m)
| 02SL - Stations (LUL) | Cxxx-NCR-001587 | NCR | L - AP5: Blocked Re-injectable Tubes |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-11-30 | 2017-12-04 09:35 | 4 | 2017-09-07 08:19 | Tunnelling - Linings - Sprayed Concrete | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The 6 following hoses have been found blocked while flushing the hoses in AP5: AP5 Block 1 - Box 1 - Right side: one hose blocked (transparent) AP5 Block 2 - Box 2 - Left side: one hose blocked (red) AP5 Block 2 - Box 2 - Right side: two hoses blocked (red and transparent) AP5 Portal Opening - Box 2 - Left side: one hose blocked (black) AP5 Portal Opening - Box 2 - Right side: one hose blocked (black) Refer to Cxxx-__M-C4-LLG-C101-50200 for all AP5 flushing records
| 02SL - Stations (LUL) | Cxxx-NCR-001588 | NCR | L - SL Tunnels: Blocked Re-injectable Tubes |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2018-02-02 | 2018-02-02 10:17 | 0 | 2018-01-23 14:34 | Tunnelling - Linings - Sprayed Concrete | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | While flushing the hoses in Liverpool Street, the following hoses have been found blocked or lost: 01) In LCWa (Package L006 – Schematic Cxxx-__M-C4-LLG-C101-50255) - LCWa Portal Opening – Track Side Box 1: 1 hose blocked (red) - LCWa Portal Opening – Track Side Box 3: 1 hose blocked (red) - LCWa Portal Opening – Track Side Box 4: 2 hoses blocked (yellow & yellow) - LCWa Portal Opening – Platform Side Box 1: 7 bleeding pipes blocked (7 x yellow) - LCWa Portal Opening – Platform Side Box 4: 1 hose blocked (yellow) - LCWa TBM Ring Connection – Platform Side Box 5: 2 hoses blocked (red & red) All flushing records checksheets for LCWa can be seen in Cxxx-__M-C4-LLG-C101-50255. 02) In CP3 & CP4 (Package L010 – Schematic Cxxx-__M-C4-LLG-C101-50157) - CP3 Block 1 – East Side Box 2: 1 hose blocked (transparent) - CP3 Block 1 – West Side Box 2: 1 hose blocked (transparent) - CP4 Block 1 – East Side Box 1: 1 hose blocked (transparent) - CP4 Block 1 – West Side Box 1: 1 hose blocked (transparent) - CP4 Block 1 – West Side Box 2: 1 hose blocked (red) - CP4 Block 2 – East Side Box 1: 1 hose blocked (transparent) - CP4 Block 2 – West Side Box 2: 1 hose blocked (transparent) - Termination Boxes: survey is missing for CP3 block 1 (1 box) and CP4 block 2 (3 boxes). All flushing records checksheets for CP3 and CP4 can be seen in Cxxx-__M-C4-LLG-C101-50157. 03) In CP3a & CP4a (Package L012 – Schematic Cxxx-__M-C4-LLG-C101-50171) - CP3a Block 1 – East Side Box 1: 1 hose blocked (transparent) - CP3a Block 1 – East Side Box 2: 1 hose blocked (transparent) - CP3a Block 1 – West Side Box 1: 1 hose blocked (transparent) - CP3a Block 2 – East Side Box 1: 1 hose blocked (transparent) - CP3a Block 2 – East Side Box 2: 3 hoses blocked (transparent, green & green) - CP3a Block 2 – West Side Box 1: 2 hoses blocked (yellow & transparent) - CP3a Block 2 – West Side Box 2: 3 hoses blocked (black, red & transparent) - CP4a Block 1 – East Side Box 1: 1 hose blocked (black) - CP4a Block 1 – East Side Box 2: 1 hose blocked (green) - CP4a Block 1 – West Side Box 2: 1 hose blocked (transparent) - CP4a Block 2 – West Side Box 2: 1 hose blocked (transparent) All flushing records checksheets for CP3a and CP4a can be seen in Cxxx-__M-C4-LLG-C101-50171. 04) In CP5 & CP6 (Package L014 – Schematic Cxxx-__M-C4-LLG-C101-50158) - CP5 Block 1 – East Side Box 1: 1 hose blocked (transparent) - CP5 Block 1 – East Side Box 2: 1 hose blocked (transparent) - CP5 Block 1 – West Side Box 2: 1 hose blocked (transparent) - CP5 Block 2 – East Side Box 1: 1 hose blocked (transparent) - CP5 Block 2 – East Side Box 2: 1 hose blocked (transparent) - CP5 Block 2 – West Side Box 2: 1 hose blocked (transparent) - CP6 Block 1 – East Side Box 1: 3 hoses blocked (black, blue & transparent) - CP6 Block 1 – East Side Box 2: 3 hoses blocked (green, yellow & transparent) - CP6 Block 1 – West Side Box 2: 1 hose blocked (transparent) - CP6 Block 2 – East Side Box 1: 1 hose blocked (transparent) - CP6 Block 2 – East Side Box 2: 1 hose blocked (transparent) - CP6 Block 2 – West Side Box 1: 2 hoses blocked (blue & red) - CP6 Block 2 – West Side Box 2: 2 hoses blocked (yellow & transparent) All flushing records checksheets for CP5 and CP6 can be seen in Cxxx-__M-C4-LLG-C101-50158. 05) In CP7 & CP8 (Package L016 – Schematic Cxxx-__M-C4-LLG-C101-50304) - CP7 Block 2 – East Side Box 2: 1 hose blocked (red) - CP7 Block 2 – West Side Box 2: 1 hose blocked (red) - CP8 Block 1 – East Side Box 1: 1 hose blocked (transparent) - CP8 Block 1 – East Side Box 2: 1 hose blocked (red) - CP8 Block 1 – West Side Box 2: 1 hose blocked (red) - CP8 Block 2 – West Side Box 1: 1 hose blocked (blue) - CP8 Block 2 – West Side Box 2: 1 hose blocked (green) - CP8 Block 3 – East Side Box 2: 1 hose blocked (transparent) - Termination Boxes: survey is missing for CP7 block 1 (2 boxes). All flushing records checksheets for CP7 and CP8 can be seen in Cxxx-__M-C4-LLG-C101-50304. 06) In CP9 & CP10 (Package L018 – Schematic Cxxx-__M-C4-LLG-C101-50191) - CP9 Block 1 – East Side Box 1: 2 hoses blocked (blue & transparent) - CP9 Block 1 – East Side Box 2: 2 hoses blocked (yellow & transparent) - CP9 Block 1 – West Side Box 1: 1 hose blocked (transparent) - CP9 Block 1 – West Side Box 2: 1 hose blocked (transparent) - CP9 Block 2 – East Side Box 1: 1 hose blocked (transparent) - CP9 Block 2 – East Side Box 2: 1 hose blocked (transparent) - CP9 Block 2 – West Side Box 1: 1 hose blocked (transparent) - CP9 Block 2 – West Side Box 2: 1 hose blocked (transparent) - CP9 Block 3 – East Side Box 1: 1 hose blocked (transparent) - CP9 Block 3 – East Side Box 2: 1 hose blocked (transparent) - CP9 Block 3 – West Side Box 1: 1 hose blocked (transparent) - CP9 Block 3 – West Side Box 2: 1 hose blocked (transparent) - CP10 Block 1 – East Side Box 1: 1 hose blocked (transparent) - CP10 Block 1 – East Side Box 2: 1 hose blocked (transparent) - CP10 Block 1 – West Side Box 1: 1 hose blocked (transparent) - CP10 Block 1 – West Side Box 2: 1 hose blocked (transparent) - Termination Boxes: survey is missing for CP9 block 1 (2 boxes). All flushing records checksheets for CP9 and CP10 can be seen in Cxxx-__M-C4-LLG-C101-50191. 07) In AP1 (Package L020 – Schematic Cxxx-__M-C4-LLG-C101-50248) - AP1 Block 1 – South Side Box 1: 1 hose blocked (blue) - AP1 Block 1 – South Side Box 2: 1 hose blocked (black) - AP1 Block 1 – South Side Box 3: 1 hose blocked (yellow) - AP1 Block 1 – South Side Box 4: 1 hose blocked (yellow) - AP1 Block 2 – North Side Box 1: 1 hose blocked (black) - AP1 Block 2 – North Side Box 2: 1 hose blocked (green) - AP1 Block 2 – South Side Box 1: 1 hose blocked (blue) - AP1 Block 2 – South Side Box 2: 1 hose blocked (yellow) - AP1 Transition Block – North Side Box 2: 1 hose blocked (transparent) - AP1 Transition Block – South Side Box 2: 1 hose blocked (transparent) All flushing records checksheets for AP1 can be seen in Cxxx-__M-C4-LLG-C101-50248. 08) In AP6 (Package L026 – Schematic Cxxx-__M-C4-LLG-C101-50207) - AP6 Block 5 – East Side Box 1: 1 hose blocked (transparent) - AP6 Block 6 – East Side Box 2: 1 hose blocked (transparent) - AP6 Block 8 – East Side Box 1: 1 hose blocked (transparent) - AP6 Block 9 – East Side Box 2: 1 hose blocked (transparent) - AP6 Block 10 – West Side Box 1: 1 hose blocked (transparent) - AP6 Block 11 – West Side Box 2: 1 hose blocked (transparent) - AP6 Block 11 – East Side Box 1: 2 hoses blocked (yellow & transparent) - AP6 Block 11 – East Side Box 2: 2 hoses missing (black & black) - AP6 Block 12 – East Side Box 1: 2 hoses missing (yellow & yellow) - AP6 Block 12 – East Side Box 2: 2 hoses blocked (black & transparent) - AP6 Block 13 – East Side Box 1: 2 hoses blocked (yellow & transparent) - AP6 Block 14 – East Side Box 1: 1 hose blocked (transparent) - AP6 Block 14 – East Side Box 2: 1 hose blocked (transparent) - AP6 Block 15 – East Side Box 1: 1 hose blocked (transparent) - AP6 Block 17 – East Side Box 1: 1 hose blocked (transparent) - AP6 Block 18 – East Side Box 2: 1 hose blocked (transparent) - AP6a (including Headwall) – West Side Box 1: 1 hose blocked (green) - AP6a (including Headwall) – East Side Box 1: 2 hoses blocked (green & transparent) - AP6a (including Headwall) – East Side Box 2: 1 hose blocked (transparent) - AP6a (including Headwall) – East Side Box 3: 1 hose blocked (transparent) - AP6a (including Headwall) – East Side Box 4: 1 hose blocked (transparent) All flushing records checksheets for AP6 can be seen in Cxxx-__M-C4-LLG-C101-50207. 09) In AP7 (Package L028 – Schematic Cxxx-__M-C4-LLG-C101-50159) - AP7-E Block 1 – North Side Box 21: 2 hoses blocked (blue & transparent) - AP7-E Block 1 – North Side Box 22: 1 hose blocked (transparent) - AP7-E Block 2 – North Side Box 18: 1 hose blocked (transparent) - AP7-E Block 2 – South Side Box 17: 1 hose blocked (transparent) - AP7-E Block 2 – South Side Box 19: 1 hose blocked (transparent) - AP7-E Block 3 – North Side Box 2: 2 hoses blocked (transparent & transparent) - AP7-E Block 3 – South Side Box 1: 1 hose blocked (transparent) - AP7-E Block 3 – South Side Box 2: 1 hose blocked (transparent) - AP7-E Block BT5 – North Side Box 1: 1 hose blocked (yellow) - AP7-E Block BT5 – North Side Box 2: 2 hoses blocked (blue & transparent) - AP7-E Block BT5 – South Side Box 1: 1 hose blocked (transparent) - AP7-E Block BT5 – South Side Box 2: 1 hose blocked (transparent) - AP7-W Block 1 – North Side Box 1: 2 hoses blocked (blue &transparent) - AP7-W Block 1 – North Side Box 2: 2 hoses blocked (yellow & transparent) - AP7-W Block 1 – South Side Box 1: 1 hose blocked (transparent) - AP7-W Block 2 – North Side Box 1: 2 hoses blocked (red &transparent) - AP7-W Block 2 – North Side Box 2: 1 hose blocked (transparent) - AP7-W Block 2 – South Side Box 1: 2 hoses blocked (red &transparent) - AP7-W Block 3 – South Side Box 1: 1 hose blocked (transparent) - AP7-W Block 3 – South Side Box 2: 2 hoses blocked (black &black) - AP7-W Block 4 – North Side Box 2: 1 hose blocked (red) - AP7-W Block 4 – South Side Box 1: 2 hoses blocked (green &green) - AP7-W Block 4 – South Side Box 2: 1 hose blocked (red) All flushing records checksheets for AP7 can be seen in Cxxx-__M-C4-LLG-C101-50159. 10) In AP9 (Package L030 – Schematic Cxxx-__M-C4-LLG-C101-50310) - AP9 Portal – North Side Box 1: 1 hose blocked (transparent) - AP9 Portal – North Side Box 2: 2 hoses blocked (transparent & transparent) - AP9 Portal – North Side Box 3: 2 hoses blocked (transparent & transparent) - AP9 Portal – North Side Box 4: 2 hoses blocked (transparent & transparent) - AP9 Portal – South Side Box 1: 1 hose blocked (transparent) - AP9 Portal – South Side Box 2: 2 hoses blocked (transparent & transparent) - AP9 Portal – South Side Box 3: 2 hoses blocked (transparent & transparent) - AP9 Block 1 – North Side Box 1: 1 hose blocked (green) - AP9 Block 1 – South Side Box 1: 3 hoses blocked (yellow, yellow & green) - AP9 Block 2 – North Side Box 1: 2 hoses blocked (black & black) - AP9 Block 2 – North Side Box 2: 4 hoses blocked (red, green, green & transparent) - AP9 Block 2 – South Side Box 1: 1 hose blocked (black) - AP9 Block 2 – South Side Box 2: 5 hoses blocked (green, green, blue, transparent & red) - AP9 Block 3 – North Side Box 1: 5 hoses blocked (yellow, yellow, transparent, red & black) - AP9 Block 3 – North Side Box 2: 1 hose blocked (green) - AP9 Block 3 – South Side Box 1: 4 hoses blocked (yellow, transparent, yellow & red) - AP9 Block 4 – North Side Box 1: 4 hoses blocked (transparent, black, red & red) - AP9 Block 4 – North Side Box 2: 4 hoses blocked (transparent, transparent, transparent & transparent) - AP9 Block 4 – North Side Box 3: 1 hose blocked (green) - AP9 Block 4 – South Side Box 1: 7 hoses blocked (red, red, transparent, transparent, transparent, transparent & transparent) - AP9 Block 5 – North Side Box 1: 2 hoses blocked (black & black) - AP9 Block 5 – North Side Box 2: Box lost - AP9 Block 5 – South Side Box 2: 2 hoses blocked (blue & blue) All flushing records checksheets for AP9 can be seen in Cxxx-__M-C4-LLG-C101-50310. 11) In AP10 (Package L032 – Schematic Cxxx-__M-C4-LLG-C101-50208) - AP10a – West Side Box 1: 1 hose blocked (transparent) - AP10a – East Side Box 1: 1 hose blocked (transparent) All flushing records checksheets for AP10 can be seen in Cxxx-__M-C4-LLG-C101-50208. 12) In AP11 & AP12 (Package L034 – Schematic Cxxx-__M-C4-LLG-C101-50279) - AP11 Block 1 – East Side Box 1: 1 hose blocked (transparent) - AP11 Block 1 – East Side Box 2: 2 hoses blocked (green & green) - AP11 Block 1 – West Side Box 2: 3 hoses blocked (green, green & transparent) - AP11 Block 2 – East Side Box 5: 2 hoses blocked (transparent & red) - AP11 Block 2 – West Side Box 5: 2 hoses blocked (blue & red) - AP12 Block 1 – East Side Box 1: 5 hoses blocked (blue, blue, black, black & transparent) - AP12 Block 1 – West Side Box 1: 4 hoses blocked (blue, blue, green & green) All flushing records checksheets for AP11 & AP12 can be seen in Cxxx-__M-C4-LLG-C101-50279. Please note that Cxxx-NCR-001481, already raised for fuko hoses blocked in AP11, is not anymore relevant and is superseded by this Cxxx-NCR-001588. 13) In VD2 (Package L040 – Schematic Cxxx-__M-C4-LLG-C101-50202) - VD2 Block 1 – East Side Box 1: 1 hose blocked (transparent) - VD2 Block 1 – East Side Box 2: 1 hose blocked (transparent) All flushing records checksheets for VD2 can be seen in Cxxx-__M-C4-LLG-C101-50202. 14) In VD4 (Package L042 – Schematic Cxxx-__M-C4-LLG-C101-50263) - VD4 Portal Opening – East Side Box 1: 1 hose blocked (red) - VD4 Portal Opening – East Side Box 5: 2 hoses blocked (blue & red) - VD4 Portal Opening – East Side Box 6: 4 hoses blocked (black, black, black & blue) - VD4 Portal Opening – West Side Box 1: 2 hoses blocked (red & transparent) - VD4 Portal Opening – West Side Box 3: 3 hoses blocked (black, transparent & red) - VD4 Portal Opening – West Side Box 4: 4 hoses blocked (black, black, blue & blue) - VD4 Block 1 – East Side Box 3: 1 hose blocked (transparent) - VD4 Block 1 – West Side Box 3: 1 hose blocked (transparent) - VD4 Block 2 – East Side Box 1: 1 hose blocked (transparent) - VD4 Block 2 – West Side Box 1: 1 hose blocked (transparent) - VD4 Block 4 – West Side Box 1: 1 hose blocked (blue) - VD4 Block 4 – West Side Box 2: 2 hoses blocked (green & green) - VD4 Block 7 – East Side Box 1: 1 hose blocked (red) - VD4 Block 7 – West Side Box 1: 1 hose blocked (red) - VD4 Block 9 – East Side Box 1: 1 hose blocked (red) & 1 hose lost (blue) - VD4 Block 9 – East Side Box 2: 3 hoses blocked (transparent, yellow & red) - VD4 Block 9 – West Side Box 1: 1 hose blocked (red) & 2 hoses lost (black & black) - VD4 Block 9 – West Side Box 2: 4 hoses blocked (transparent, green, green & red) - VD4 Block 10 – East Side Box 1: 1 hose blocked (transparent) & 2 hoses lost (black & black) - VD4 Block 10 – East Side Box 2: 4 hoses blocked (green, green, transparent & red) - VD4 Block 10 – West Side Box 1: 1 hose blocked (transparent) & 2 hoses lost (black & black) - VD4 Block 10 – West Side Box 2: 3 hoses blocked (green, green & red) - VD4 Block 11 – East Side Box 1: 1 hose blocked (transparent) - VD4 Block 11 – West Side Box 1: 1 hose lost (blue) - VD4 Block 11 – West Side Box 2: 2 hoses blocked (yellow & transparent) - VD4 Block 12 – East Side Box 1: 1 hose blocked (red) - VD4 Block 12 – East Side Box 2: 2 hoses blocked (transparent & red) - VD4 Block 12 – West Side Box 1: 2 hoses blocked (transparent & red) - VD4 Block 12 – West Side Box 2: 1 hose blocked (red) - VD4 Block 13 – East Side Box 1: 2 hoses blocked (red & transparent) - VD4 Block 13 – West Side Box 1: 1 hose blocked (red) All flushing records checksheets for VD4 can be seen in Cxxx-__M-C4-LLG-C101-50263. 15) In VD5 (Package L044 – Schematic Cxxx-__M-C4-LLG-C101-50266) - Termination Boxes: survey is missing for VD5 block 1 (2 boxes). 16) In VD7 (Package L046 – Schematic Cxxx-__M-C4-LLG-C101-50236) - VD7 Portal Opening – East Side Box 1: 2 hoses blocked (red & transparent) - VD7 Portal Opening – East Side Box 2: 1 hose blocked (transparent) - VD7 Portal Opening – West Side Box 1: 2 hoses blocked (red & transparent) - VD7 Portal Opening – West Side Box 2: 1 hose blocked (transparent) All flushing records checksheets for VD7 can be seen in Cxxx-__M-C4-LLG-C101-50236. 17) In CH1 (Package L049 – Schematic Cxxx-__M-C4-LLG-C101-50160) - Block CH1-1 – North Side Box 2: 3 hoses blocked (black, blue & transparent) - Block CH1-1 – North Side Box 3: 1 hose blocked (black) - Block CH1-1 – North Side Box 4: 1 hose blocked (blue) - Block CH1-1 – South Side Box 2: 4 hoses blocked (black, black, yellow & yellow) - Block BT2 – North Side Box 5: 2 hoses blocked (black & transparent) - Block CH1-2 – North Side Box 2: 1 hose blocked (transparent) - Block CH1-2 – North Side Box 3: 2 hoses blocked (transparent & black) - Block CH1-2 – South Side Box 1: 2 hoses blocked (yellow & yellow) - Block CH1-2 – South Side Box 2: 1 hose blocked (transparent) - Block CH1-2 – South Side Box 3: 2 hoses blocked (transparent & transparent) - Block CH1-2 – South Side Box 4: 2 hoses blocked (blue & blue) - Transition Block – North Side Box 1: 3 hoses blocked (yellow, green & green) - Transition Block – North Side Box 2: 2 hoses blocked (blue & transparent) - Transition Block – North Side Box 3: 1 hose blocked (transparent) - Transition Block – South Side Box 1: 1 hose blocked (green) - Transition Block – South Side Box 2: 1 hose blocked (transparent) - Transition Block – South Side Box 3: 2 hoses blocked (black & transparent) All flushing records checksheets for CH1 can be seen in Cxxx-__M-C4-LLG-C101-50160. 18) In CH2 (Package L051 – Schematic Cxxx-__M-C4-LLG-C101-50292) - Block CH2-1 – South Side Box 1: 1 hose blocked (transparent) - Block CH2-1 – South Side Box 2: 1 hose blocked (transparent) - Block CH2-1 – North Side Box 1: 1 hose blocked (transparent) - Block CH2-1 – North Side Box 2: 1 hose blocked (transparent) - Block CH2-2 – South Side Box 1: 1 hose blocked (transparent) - Block CH2-2 – South Side Box 2: 2 hoses blocked (transparent & black) - Block CH2-2 – South Side Box 3: 2 hoses blocked (transparent & transparent) - Block CH2-2 – South Side Box 4: 1 hose blocked (transparent) - Block CH2-2 – North Side Box 1: 1 hose blocked (transparent) - Block CH2-2 – North Side Box 2: 2 hoses blocked (transparent & black) - Block CH2-2 – North Side Box 3: 1 hose blocked (transparent) - Block CH2-2 – North Side Box 4: 2 hoses blocked (transparent & green) - Block CH2-3 – South Side Box 1: 1 hose blocked (transparent) - Block CH2-3 – South Side Box 2: 1 hose blocked (transparent) - Block CH2-3 – North Side Box 1: 1 hose blocked (yellow) - Block CH2-4 – South Side Box 2: 3 hoses blocked (black, black & transparent) - Block CH2-4 – North Side Box 2: 3 hoses blocked (black, black & transparent) - Block CH2/ES2 Transition – South Side Box 2: 2 hoses blocked (transparent & red) - Block CH2/ES2 Transition – North Side Box 1: 1 hose blocked (black) - Block CH2/ES2 Transition – South Side Box 2: 3 hoses blocked (transparent, green & red) All flushing records checksheets for CH2 can be seen in Cxxx-__M-C4-LLG-C101-50292. 19) In CH5 (Package L055 – Schematic Cxxx-__M-C4-LLG-C101-50161) - CH5 Headwall – South Side Box 1: 1 hose blocked (transparent) - CH5 Headwall – North Side Box 1: 1 hose blocked (transparent) - CH5 Block 1 – South Side Box 2: 1 hose blocked (black) - CH5 Block 2 – South Side Box 1: 1 hose blocked (green) - CH5 Block 2 – North Side Box 1: 2 hoses blocked (green & green) All flushing records checksheets for CH5 can be seen in Cxxx-__M-C4-LLG-C101-50161. 20) In CH6 (Package L057 – Schematic Cxxx-__M-C4-LLG-C101-50162) - AP9/CH6 Transition Block – North Side Box 1: 2 hoses blocked (transparent & transparent) - AP9/CH6 Transition Block – South Side Box 1: 2 hoses blocked (transparent & transparent) - Block CH6-2 – North Side Box 4: 1 hose blocked (transparent) - Block CH6-2 – South Side Box 4: 1 hose blocked (transparent) All flushing records checksheets for CH6 can be seen in Cxxx-__M-C4-LLG-C101-50162. 21) In CH7 (Package L059 – Schematic Cxxx-__M-C4-LLG-C101-50254) - CH7 – East Side Box 1: 1 hose blocked (transparent) - CH7 – East Side Box 2: 2 hoses blocked (transparent & red) - CH7 – West Side Box 1: 2 hoses blocked (yellow & transparent) - CH7 – West Side Box 2: 2 hoses blocked (transparent & red) All flushing records checksheets for CH7 can be seen in Cxxx-__M-C4-LLG-C101-50254. 22) In ES2 (Package L061 – Schematic Cxxx-__M-C4-LLG-C101-50317) - ES2 Block 1 – North Side Box 1: 1 hose blocked (transparent) - ES2 Block 1 – North Side Box 2: 1 hose blocked (transparent) - ES2 Block 1 – South Side Box 1: 1 hose blocked (transparent) - ES2 Block 1 – South Side Box 2: 1 hose blocked (transparent) - ES2 Block 2 – North Side Box 1: 1 hose blocked (transparent) - ES2 Block 2 – North Side Box 2: 1 hose blocked (transparent) - ES2 Block 2 – South Side Box 1: 1 hose blocked (transparent) - ES2 Block 2 – South Side Box 2: 1 hose blocked (transparent) - ES2 Block 3 – North Side Box 2: 1 hose blocked (transparent) - ES2 Block 3 – South Side Box 2: 1 hose blocked (transparent) - ES2 Block 4 – South Side Box 1: 1 hose blocked (black) - ES2 Block 4 – South Side Box 2: 1 hose blocked (green) - ES2 Block 6 – North Side Box 2: 1 hose blocked (transparent) - ES2 Block 6 – South Side Box 2: 1 hose blocked (transparent) - ES2 Block 7 – North Side Box 1: 1 hose blocked (transparent) - ES2 Block 7 – North Side Box 2: 2 hoses blocked (transparent & transparent) - ES2 Block 7 – South Side Box 1: 1 hose blocked (transparent) - ES2 Block 7 – South Side Box 2: 2 hoses blocked (transparent & transparent) - ES2 Block 9 – North Side Box 1: 5 hoses blocked (yellow, yellow, yellow, yellow & transparent) - ES2 Block 9 – North Side Box 2: 3 hoses blocked (transparent, black & blue) - ES2 Block 9 – North Side Box 3: 1 hose blocked (transparent) - ES2 Block 9 – South Side Box 2: 4 hoses blocked (yellow, yellow, yellow & yellow) - ES2 Block 9 – South Side Box 3: 3 hoses blocked (transparent, black & blue) - ES2 Block 9 – South Side Box 4: 2 hoses blocked (transparent & transparent) All flushing records checksheets for ES2 can be seen in Cxxx-__M-C4-LLG-C101-50317. 23) In ES3 (Package L063 – Schematic Cxxx-__M-C4-LLG-C101-50163) - ES3 Block 1 – North Side Box 2: 1 hose blocked (transparent) - ES3 Block 1 – South Side Box 2: 1 hose blocked (transparent) - ES3 Block 2 – North Side Box 1: 1 hose blocked (transparent) - ES3 Block 2 – North Side Box 2: 1 hose blocked (transparent) - ES3 Block 2 – South Side Box 1: 1 hose blocked (transparent) - ES3 Block 2 – South Side Box 2: 1 hose blocked (transparent) - ES3 Block 3 – North Side Box 1: 1 hose blocked (transparent) - ES3 Block 3 – North Side Box 2: 1 hose blocked (transparent) - ES3 Block 3 – South Side Box 1: 1 hose blocked (transparent) - ES3 Block 3 – South Side Box 2: 1 hose blocked (transparent) - ES3 Block 4 – North Side Box 1: 1 hose blocked (transparent) - ES3 Block 4 – North Side Box 2: 1 hose blocked (transparent) - ES3 Block 4 – South Side Box 1: 1 hose blocked (transparent) - ES3 Block 4 – South Side Box 2: 1 hose blocked (transparent) - ES3 Block 5 – North Side Box 1: 1 hose blocked (transparent) - ES3 Block 5 – North Side Box 2: 1 hose blocked (transparent) - ES3 Block 5 – South Side Box 1: 1 hose blocked (transparent) - ES3 Block 5 – South Side Box 2: 1 hose blocked (transparent) - ES3 Block 6 – North Side Box 1: 1 hose blocked (transparent) - ES3 Block 6 – North Side Box 2: 1 hose blocked (transparent) - ES3 Block 6 – South Side Box 1: 1 hose blocked (transparent) - ES3 Block 6 – South Side Box 2: 1 hose blocked (transparent) - ES3 Block 7 – North Side Box 1: 1 hose blocked (transparent) - ES3 Block 7 – North Side Box 2: 1 hose blocked (transparent) - ES3 Block 7 – South Side Box 1: 1 hose blocked (transparent) - ES3 Block 7 – South Side Box 2: 1 hose blocked (transparent) - ES3 Block 8 – North Side Box 1: 1 hose blocked (transparent) - ES3 Block 8 – North Side Box 2: 1 hose blocked (transparent) - ES3 Block 8 – South Side Box 1: 1 hose blocked (transparent) - ES3 Block 8 – South Side Box 2: 1 hose blocked (transparent) - ES3 Block 9 – North Side Box 1: 1 hose blocked (transparent) - ES3 Block 9 – South Side Box 1: 1 hose blocked (transparent) All flushing records checksheets for ES3 can be seen in Cxxx-__M-C4-LLG-C101-50163. For blocked hoses in PTE, RCE and LCE refer to Cxxx-NCR-001307. For blocked hoses in PTW, RCW and LCWb refer to Cxxx-NCR-001308. For blocked hoses in AP2 refer to Cxxx-NCR-001353. For blocked hoses in AP5 refer to Cxxx-NCR-001587.
| 02SL - Stations (LUL) | Cxxx-NCR-001589 | NCR | L - CP3 and CP4 SL: Missing tests and documentation |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-11-13 | 2017-11-08 12:08 | -5 | 2017-10-19 09:48 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Cxxx-__M-C4-LLG-C101-50155 Deliverable Records for LIV CP3 and CP4 Cast In Situ - Package No L010 1) Invert – ITP item C1 No cubes taken for CP4 Invert Block 2.
| 02SL - Stations (LUL) | Cxxx-NCR-001590 | NCR | L - CH5: Encroachment of chutes diameter |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-12-07 | 2017-12-04 11:21 | -3 | 2017-09-22 07:50 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | • On 13/09/2017, __ carried out an injection campaign in CH5 (near chutes) to seal a leak captured into NCR1585. After injection, bulges have been noted inside both chutes. • The western chute is deformed on its east side. The eastern chute is deformed on its north side. • As a result the internal diameter has been reduced. Refer to Att01. for space proofing reduction.
| 02SL - Stations (LUL) | Cxxx-NCR-001591 | NCR | Cxxx Liverpool Street Access Shaft AS1 – As-Built condition of “top-shelf” to slip-formed Primary Lining thickening. |  | Contr | HAG | LIS - Liverpool Street Station (Central) |  | 2017-10-26 | 2017-11-10 12:47 | 15 | 2017-09-28 14:52 | Civil - Tunnelling | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The top shelf to the LIS AS1 slip-formed Primary Lining will form the bearing surface for the future cover / capping slab. Cxxx has identified defects (including a temporary recess and boot prints) in the surface of the top shelf (reference site inspection and email Talliss 10th July 2017). With reference to the Crossrail Materials and Workmanship Specification KF10 In Situ Concrete Document No. Cxxx -OVE-Z4-RSP-CR001-00002, there are four areas of non-conformance: 1. Class of finish 2. Protection of finished concrete 3. Dimensional deviation 4. Defective work/making good of temporary recesses and holes 1. Class of finish KF10.3230 Unformed Surfaces - Classes of Finish a) Concrete surface finishes shall be as specified below unless specified otherwise on the Drawings. i) Class U1 • The concrete shall be uniformly levelled and screeded to produce a plain, textured or ridged surface. No further work shall be applied to the surface unless it is used as the first stage for a Class U2 or Class U3 finish. Immediately after placing the concrete, the surface shall be struck off with a screed board to produce a plain or ridged surface to the levels, grades and within the dimensional deviations, described in the Contract. d) Exposed upper surfaces, other than screeds, in contact with water shall be floated with a steel trowel to a dense smooth uniform finish free from trowel marks. Other exposed upper surfaces, other than screeds, shall have a smooth finish obtained with a wood float. Suggested Non-Conformance: the finished unformed surface of the top shelf is not uniformly levelled or smooth 2. Protection of finished concrete KF10.3231 Protection of Finished Concrete The finished concrete surfaces shall be protected from damage and from rust or oil staining and any necessary protective measures shall be adopted. Suggested Non-Conformance: The boot-marks indicate that the finished concrete was not satisfactorily protected 3. Dimensional deviation KF10.3232 Dimensional Deviation a) The positions and dimensions of the finished surfaces shall be in accordance with the Drawings, subject to the provisions of BS EN 13670:2009 for in situ concrete and erection of precast concrete, or such lesser deviations as may be specified elsewhere in the Contract. BS EN 13670:2009 Annex G G.10.7 Tolerances for surfaces and edge straightness Figure G5 – Permitted deviations for surfaces and edges Flatness: Tolerance Class 1 – Not-moulded surface Permitted deviation (Delta) Global length, l = 2.0 m , Delta = 15mm ; Local Length, l = 0.2m ; Delta = 6mm Suggested Non-Conformance: The non uniform level of the surface and depth the recesses, holes and boot marks exceeds the permitted deviations 4. Defective work/making good of temporary recesses and holes KF10.3212 Defective Work a) Concrete, which is honeycombed or fails to attain the specified or characteristic strength, and concrete work which in any way fails to comply with the Specification, will be considered to be defective. b) The Method Statements shall include procedures for considering individual defects and for remedial work where the long term performance of the structure is not at risk. Where there is any such risk, the defective work shall be removed, together with any work obstructing access for its removal, or the subsequent reconstruction, and any work requiring support from the work to be removed. BS EN 13670:2009 Cl 5.6.2 Making good of temporary recesses and holes (1) Recesses and holes used for temporary works shall be filled and finished with a material of similar characteristics to the surrounding concrete, or as given in the execution specification. Suggested Non-Conformance: The recess (which was formed by the Cxxx Contractor to accommodate a temporary inclinometer). The Contractor should make good temporary recesses and holes in the unformed surface as required by British Standard BS EN 13670:2009 Execution of concrete structures
| 02SL - Stations (LUL) | Cxxx-NCR-001592 | NCR | L - CH5 SL: Missing tests and documentation |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-11-02 | 2017-11-07 13:54 | 5 | 2017-10-19 10:38 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Cxxx-__M-C4-LLG-C101-50324 Deliverable Records for LIV CH5 __ Sprayed Waterproofing Membrane - Package No L055 1) __ – ITP items 1.3, 1.4, 2.1, 2.2 Missing __ Pre‐Placement Checksheet D3‐98 (1/4) for CH5 Headwall (Ch.103-105) Layer 2 2) __ – ITP items 2.6, 2.8 Missing __ Placement Checksheet D3‐101 (2/4) for CH5 Headwall (Ch.103-105) Layer 2 Cxxx-__M-C4-LLG-C101-50325 Deliverable Records for LIV CH5 Cast In Situ - Package No L055 3) Invert – ITP item C1 No cubes taken for CH5 Block BT4 Invert, CH5/CP1 Transition and CH5/CP1&2 Wingwall Cxxx-__M-C4-LLG-C101-50326 Deliverable Records for LIV CH5 Secondary Lining - Package No L055 4) Fireproofing – ITP item 6.1 Missing Grouting of Injection Tubes (__ Form D3-109) for CH5 Fireproofing Ch.110-127.
| 02SL - Stations (LUL) | Cxxx-NCR-001593 | NCR | L - AP1, AP9, CP9, CP10, AS1, CP6, AP7E and AP7W: Leaks |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2018-02-09 | 2018-02-28 09:13 | 19 | 2018-01-23 14:57 | Tunnelling - Linings - Sprayed Concrete | 2000 |  | System Defect | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Following Liverpool Street Tunnels handover, water ingress has been observed and leaks treatment decided for the following areas: - AP1 - CP10 - CP9 - AP7-E - AP7-W - AS1 - CP6 and - AP9.
| 02SL - Stations (LUL) | Cxxx-NCR-001594 | NCR | L - VD5: Leaks in Moorgate Portal and LCE Connection |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-10-30 | 2017-11-10 12:16 | 11 | 2017-10-16 11:14 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | On September 2017, after hand over of VD5 Tunnel to Cxxx, two leaks were reported: - 1 leak in VD5/LCE Connection - 1 leak in VD5/Moorgate Shaft Portal. See Inspection Report attached for pictures of the leaks before the tests. See Att01.
| 02SL - Stations (LUL) | Cxxx-NCR-001595 | NCR | L - CP5 and CP6 SL: Missing tests and documentation |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-11-27 | 2017-12-04 11:23 | 7 | 2017-11-13 14:54 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Cxxx-__M-C4-LLG-C101-50342 Deliverable Records for LIV CP5 and CP6 Cast In-Situ - Package No L014 1) Invert – ITP items C1 No cube taken on 18/04/2015 for CP5 Invert block 2, therefore no compressive strength available.
| 02SL - Stations (LUL) | Cxxx-NCR-001596 | NCR | L - September 17: Low Residual Flexural Strength of Mix P1 + PP - Beam Testing CR3535 |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-12-10 | 2017-12-04 11:32 | -6 | 2017-10-27 12:33 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | LIV sprayed beam set CR3535 from September 2017 has achieved too low individual D3 results of beam B - D3 - S1.14, at 28 days with average for set of four beams - S1.4. Refer to Att.01 and Att.02 for the test results. The sprayed linings which may have been affected (typically applied within +/- 2 wks of the date of the test spraying) are: AS1 Secondary Lining.
| 02SL - Stations (LUL) | Cxxx-NCR-001597 | NCR | L - AP7 SL: Missing tests and documentation |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-11-23 | 2017-12-04 11:33 | 11 | 2017-11-09 17:48 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Cxxx-__M-C4-LLG-C101-50334 Deliverable Records for LIV AP7 Regulation - Package No L028 1) Regulation – ITP items 2.6 Missing Hammer Testing Checksheet (__ Form D3-80) for AP7 Regulation Ch.7.850 to Ch.17 Crown and Ch.45 to 46.607 Invert
| 02SL - Stations (LUL) | Cxxx-NCR-001598 | NCR | L - CH6 SL: Missing tests and documentation |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-11-23 | 2017-12-04 11:39 | 11 | 2017-11-09 17:19 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Cxxx-__M-C4-LLG-C101-50344 Deliverable Records for LIV CH6 Regulation - Package No L057 1) Regulation – ITP items 2.1, 2.3, 2.4 Missing Permit to Cover (__ Form D3-93) for CH6 Ch.116.4 to Ch.120 Crown 2) Regulation – ITP items C3, 1.1, 2.1, 2.3, 2.5 Missing Shotcrete Placement Checksheet (__ Form D3-86) for CH6 Ch.116.4 to Ch.120 P2 Mix Invert
| 02SL - Stations (LUL) | Cxxx-NCR-001599 | NCR | L - CH1 SL: Missing tests and documentation (missing Fireproofing thickness scan data for below axsis) |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2017-11-10 | 2017-11-09 15:10 | -1 | 2017-10-27 14:09 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Cxxx-__M-C4-LLG-C101-50331 Deliverable Records for LIV CH1 Secondary Lining - Package No L049 2nd 2nd with PP – ITP item 5.10 - Missing Fireproofing Thickness scan data for CH1-2 Ch. 81.5 to 93, below axis. See Att01.
| 02SL - Stations (LUL) | Cxxx-NCR-001600 | NCR | L - PTW-W Block 18: Damping through tiny cracks above axis level |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2018-02-09 | 2018-02-02 10:20 | -7 | 2018-01-16 12:00 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | As leak sealing progressed in the Westbond tunnel (refer to Cxxx-NCR-001580), a damp area appeared through a fine crack above axis at block 18. See photo before the injection works in final report (Att.01)
| 02SL - Stations (LUL) | Cxxx-NCR-001601 | NCR | L - Top of AS1: As-found conditions |  | Contr | __M | LIS - Liverpool Street Station (Central) |  | 2018-01-24 | 2018-01-18 16:15 | -6 | 2018-01-10 08:57 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Further to the ongoing Cxxx follow-on works at AS1 and the inspections carried out to the top of AS1 by Crossrail Cxxx and Cxxx (inspection dates of 15/12/17-Cxxx and 18/12/17-Crorssrail Cxxx and Cxxx), a number of areas of non-complaint sprayed waterproof membrane have been identified which have required remedial works to be undertaken. This NCR has been raised to record the as-found conditions to the top of AS1 during commencement of the Cxxx follow works at AS1. The NCR is to be reviewed by Crossrail Cxxx and Cxxx and details are to be included of the site inspections undertaken with photos to be included of non-compliant areas of the sprayed waterproof membrane. Also to be included are details of the remedial works carried out by Cxxx to the non-compliant sprayed waterproof membrane.
| 02SL - Stations (LUL) | Cxxx-NCR-001603 | NCR | Excessive leaks in UPE Eastbound, AP10, AP5, AP6, CH5, CP6/AP7 junction. |  | Crossrail | PDP | LIS - Liverpool Street Station (Central) |  | 2019-05-22 | 2020-10-09 10:32 | 506 | 2019-01-22 17:18 | Tunnelling - Linings - Sprayed Concrete | 100000 |  | Workmanship | Repair | 1 (>60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Cxxx have measured water ingress in various locations within the tunnels and established 2 locations where the flow rate of water ingress is in excess of the Cxxx specification requirement: 1. East bound UPE between duct grill 26 and 28 (page 4 in report) 2. AP5 platform level (page 19 in report) In addition, item 2. above is in a passenger area and should be dry. The referred to report, Cxxx-LAO-S-RGN-C101-50012, is attached. In addition, a third area has been identified in AP10, which is a passenger area and should also be dry, see attached photo 'AP10 leak'. Further leaks and damp patches in public areas have been noted and instructed to Cxxx to rectify, as per Cxxx-PMIs 1917 and 1927.
| 02SL - Stations (LUL) | Cxxx-NCR-000014 | NCR | West Vehicle Deck Ramp |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2011-08-17 | 2011-08-19 11:15 | 2 | 2011-08-12 | Civil - Civil Engineering General | 500 |  | System Defect | Rework |  | Complete |  | Completed |  | Obstruction encountered whilst installing Pile No. 3 to the west ramp
| 02SL - Stations (LUL) | Cxxx-NCR-000041 | NCR | Rod Extensometers ITP |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2011-10-03 | 2011-09-26 09:40 | -7 | 2011-09-23 | Surveying - Instrumentation and Monitoring | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | Contractor commenced works without an ITP approved by the CRL Project Manager
| 02SL - Stations (LUL) | Cxxx-NCR-000042 | NCR | Incorrect diameter of the extensometer borehole |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2011-10-07 | 2011-09-26 14:19 | -11 | 2011-09-23 | Surveying - Instrumentation and Monitoring | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | The diameter of the borehole for the extensometer was too small which meant that the instrument didn't reach its final position
| 02SL - Stations (LUL) | Cxxx-NCR-000050 | NCR | Concrete Strength Pile P5 - West Ramp |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2011-10-07 | 2011-10-04 13:40 | -3 | 2011-10-03 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | 2 No's cubes for Pile P5 are below strength. 45 and 45.5 N/mm2 respectively
| 02SL - Stations (LUL) | Cxxx-NCR-000053 | NCR | Concrete finish to West Run slab bearing plinth |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2011-10-14 | 2011-12-01 15:31 | 48 | 2011-10-06 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Poor concrete finish to west Run on slab bearing plinth
| 02SL - Stations (LUL) | Cxxx-NCR-000065 | NCR | Piling mat installation Cambridge Heath shaft |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2011-11-04 | 2011-11-16 16:30 | 12 | 2011-11-02 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The roller drivers not been absolutely clear of how many passes were required for each of the rollers used on site. Also drivers were counting the number of passes wrongly. The have being counting each forward and backward run as one pass instead of two.
| 02SL - Stations (LUL) | Cxxx-NCR-000071 | NCR | ITP for Inclinometers - Issue of the Installation Log to CRL |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2011-11-30 | 2011-11-29 13:24 | -1 | 2011-11-15 | Surveying - Instrumentation and Monitoring | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The installation log for the Inclinometers IM6/IM7 to __ JV and CRL is now overdue, as they should have been submited on the 4th and 7th of November respectively. Also we have the Indication by __- Getec, that they won't be able to also issue, the Installation Logs for the Inclinometers IM8/IM11 WHICH due dates are the 17th and the 19th respectively.
| 02SL - Stations (LUL) | Cxxx-NCR-000074 | NCR | ITP for Rod Extensometers- Issue of the Installation log to CRL |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2011-11-30 | 2011-11-29 13:26 | -1 | 2011-11-18 | Surveying - Instrumentation and Monitoring | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The installation log for the rod Extensometers XR1/2 and 3 to __ JV is nverdue, as they should have been submited on the 11th and 13th of November .
| 02SL - Stations (LUL) | Cxxx-NCR-000075 | NCR | Quality Procedures for: ITP for The Guide walls - Witness Points |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2011-11-22 | 2011-11-29 13:01 | 7 | 2011-11-18 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The Works for the Guidewall have already started this week, but no IRF's have been sent yet.
| 02SL - Stations (LUL) | Cxxx-NCR-000080 | NCR | IRF form |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2011-12-02 | 2011-11-29 12:59 | -3 | 2011-11-28 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | In a couple of instances the IRF has not been completed/referenced correctly
| 02SL - Stations (LUL) | Cxxx-NCR-000081 | NCR | Piling mat CHS |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2011-12-02 | 2011-11-29 12:42 | -3 | 2011-11-28 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | The double thick concrete slab that __ has been uncovering and breaking out once removed, it leaves the formation across the site at 110.50m. Please refer to EWN-017 & EWN-029. The design formation level is 110.60m as per the drawings. However, once __ has removed the slab, the formation level is 100mm lower than design level. It would not be possible to lay 100mm of 6F2 material to bring the formation level back to design as if we placed 100mm of material and tried to compact it then it would just disappear into the formation level. We therefore decided to build up in 375mm layers as per the approved design. The piling mat is designed as 4 layers of 375mm. If you add this thickness to the formation level of 110.50m then we are at a top of piling mat level of 112.00m. This leaves a 100mm 'top up' of 6F2 in order to bring the mat up to design level. This 100 mm layer has been compacted as per Table 6/2 Series 600 from Highway specifications.
| 02SL - Stations (LUL) | Cxxx-NCR-000085 | NCR | Guide- Wall at CHS- Section and Reinforcement Detailed Drawing |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2011-12-20 | 2012-01-03 17:00 | 14 | 2011-12-16 | Civil - Civil Engineering General | 500 |  | Design | Rework |  | Complete |  | Completed |  | Reference to Works Information, Volume 2B -General Requirements, Part 22 – Equipment & Temporary Works - Design & Implementation: -Section 22.6 -“Detailed drawings and calculations for all Temporary Works shall be included in the method statement at least 28 days before purchase or manufacture commences”. The Guide Wall Section and Reinforcement detail Drawing, wasn’t attached to the MS.
| 02SL - Stations (LUL) | Cxxx-NCR-000089 | NCR | Installation of Site Offices |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-01-12 | 2012-01-16 09:28 | 4 | 2012-01-10 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | The ground floor offices have been installed the wrong way round. 2 main issues: - frosted glass was meant to be on Trahorn Close side and is on site side - ground floor reception access door was meant to be in SW corner and has been installed in NE corner
| 02SL - Stations (LUL) | Cxxx-NCR-000092 | NCR | Relocation due to Instrumentation not Working |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-01-18 | 2012-02-08 09:18 | 21 | 2012-01-17 | Surveying - Instrumentation and Monitoring | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | During Installation work for the rod extensometer XR00052 on Monday 16.01.2012 the reference head unit was pulled separate from the anchored rods. It appeared that the rope was snagged by the casing as the casing was being extracted and pulled off the head. The exposed rods in the borehole could not be identified as to which depth of anchor they were connected to so the head could not be reconnected.
| 02SL - Stations (LUL) | Cxxx-NCR-000093 | NCR | Repositioning of Inclinometers due to Instruments not working |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-01-18 | 2012-02-08 09:22 | 21 | 2012-01-17 | Surveying - Instrumentation and Monitoring | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | On 16/01/12 __ were informed by subcontractors __ that the inclinometer tube had been separated at 27m depth and that the commissioning could not be achieved due to the probe reels departing from the grooves within the tube. Getec technical support confirmed that an inner lining substitute would not work with IN Place inclinometers.
| 02SL - Stations (LUL) | Cxxx-NCR-000111 | NCR | Calibration records for the support fluid test equipment |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-02-27 | 2012-02-27 09:53 | 0 | 2012-02-20 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | No calibration records for the support fluid test equipment were made available to demonstrate compliance with the above requirement
| 02SL - Stations (LUL) | Cxxx-NCR-000113 | NCR | Bentonite shear strength test |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-02-27 | 2012-03-08 14:21 | 10 | 2012-02-20 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The test and equipment used by the Contractor to measure the shear strength were not in accordance with the specified requirements. The test was confirmed to be a DIN test which is not referenced in the Contract. The contactor confirmed that the change to specified requirements with respect to the shear strength had no Field Change Document in place to demonstrate acceptance as required by Project Technical Requests (RFI, NCR, FCD) Procedure CRL1-XRL-Z-GPD-CR001-50006 Rev 1.0 clause 6.0
| 02SL - Stations (LUL) | Cxxx-NCR-000117 | NCR | DSS Barrettes P50 & P51 - Sonic Tube Size |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-02-24 | 2012-02-28 10:21 | 4 | 2012-02-23 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | 2 No oversized sonic logging tubes (1 in each barrette) P50 & P51.
| 02SL - Stations (LUL) | Cxxx-NCR-000118 | NCR | DSS Barrette 50 reservation tubes |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-03-01 | 2012-02-27 08:55 | -3 | 2012-02-23 | Civil - Structural Engineering | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | Two 60.3 mm and two 150 mm inclinometer reservation tubes installed in Barrette number 50
| 02SL - Stations (LUL) | Cxxx-NCR-000120 | NCR | Excavation of Barrette B38 on CHS is out of tolerance on the y-axis. |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-03-06 | 2012-03-08 14:32 | 2 | 2012-02-28 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Inconsistent reading of the inclinometer in the grab operators cabin. Before starting the excavation below cut-off level the excavation was rectified from platform level down to cut-off level to reduce displacement of barrette.
| 02SL - Stations (LUL) | Cxxx-NCR-000125 | NCR | Piling platform check for deterioration |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-03-09 | 2012-03-19 14:24 | 10 | 2012-03-03 | Civil - Excavation | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Before commencing pre excavation works it is required from the contractor to inspect the working platform and record the results in the daily report form, No evidence provided when requested by CRL on 02/03/2012 , __ field engineer did not fill the relevant inspection form
| 02SL - Stations (LUL) | Cxxx-NCR-000126 | NCR | CHS B35 Reinforcement out of Vertical Tolerance |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-03-07 | 2012-05-01 11:40 | 55 | 2012-03-05 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Please see attached __ NCR: The panel was only excavated to its final depth at its centre but not at its edges. The final depth at the centre of the panel is 61.45 mATD This has resulted in the final cage level being 61.97 mATD, 270mm above tolerance Maximum vertical tolerance for the reinforcement is 75mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000131 | NCR | Boxouts Details For Panel 3 at DSS |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-03-11 | 2012-03-08 13:48 | -3 | 2012-03-07 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | During the Inspection for Panel 3 For the Reinforcement details, the following problems were noticed: 1. Damaged boxouts 2. Bracket system was changed by __'s supplier as recent experience on other jobs were not satisfactory, these changes were not sent to the Designers for approval. 3- An Absence chamfered top end of the boxouts was detected and it wasn't compliant with the design detail.
| 02SL - Stations (LUL) | Cxxx-NCR-000132 | NCR | Boxout chamfering edge |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-03-14 | 2012-03-28 11:50 | 14 | 2012-03-07 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The 45 degree chamfer to top timber member for the box-outs shown on the drawing Cxxx-__-C-DWG-D061-50179 was missing for panel P3.
| 02SL - Stations (LUL) | Cxxx-NCR-000133 | NCR | Incorrect dimension for the overall lenght of cage 2 |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-03-14 | 2012-03-28 11:58 | 14 | 2012-03-07 | Civil - Civil Engineering General | 500 |  | Design | Repair |  | Complete |  | Completed |  | The dimension for the overall length of cage 2 shown on drawing Cxxx-__-C-DWG-D061-50137 (18225 mm) upon routine inspection on site did not appear to correspond to the dimensions shown on the __ drawing. It was not apparent which dimension was correct and only after investigation it was established that the __ drawing was incorrect.
| 02SL - Stations (LUL) | Cxxx-NCR-000134 | NCR | Cage 1 Damaged Boxout |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-03-14 | 2012-03-08 13:08 | -6 | 2012-03-07 | Civil - Civil Engineering General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | The timber box for the cage no 1 of P3 boxout damaged during transportation.
| 02SL - Stations (LUL) | Cxxx-NCR-000135 | NCR | Panel 3 - Maximum time Excavation & Concreting exceeded |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-03-16 | 2012-05-01 11:54 | 46 | 2012-03-08 | Civil - Civil Engineering General | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | The 66 hrs maximum allowance for the Excavation & Concreting was exceeded.
| 02SL - Stations (LUL) | Cxxx-NCR-000141 | NCR | Concreting for Panel 51- Time Between batching and pouring a concrete load |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-03-16 | 2012-03-28 12:27 | 12 | 2012-03-09 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Time Between batching and pouring the concrete load for the Panel 51 has exceeded the 2 hrs limit.
| 02SL - Stations (LUL) | Cxxx-NCR-000143 | NCR | Box out for Panel 12 - DSS |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-03-15 | 2012-04-13 12:59 | 29 | 2012-03-12 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | On today's Cages Inspection for Panel 12, we have registered the following: Cage 2 - 1) - The Box Out 11/ 14 /16 have the Chanfers positioned the wrong way. 2 ) Also the Chanfers are 45 mm dimension. 3) - 2 Spacers Bars are missing. We should have 24 in total in cage 2 but only have 22 . Cage 3 1- Box Out damage 2 - No Chamfer in one of of the Box outs
| 02SL - Stations (LUL) | Cxxx-NCR-000144 | NCR | DSS Panel 12 Sliding Bars |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-03-19 | 2012-03-19 14:15 | 0 | 2012-03-13 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | Splice bars were found to be welded up.
| 02SL - Stations (LUL) | Cxxx-NCR-000145 | NCR | Instrumentation and Monitoring IM00006 & IM00007 |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-03-23 | 2012-03-14 11:34 | -9 | 2012-03-13 | Civil - Civil Engineering General | 500 |  | Equipment Breakdown | Rework |  | Complete |  | Completed |  | Inclinometers prop guidewheels (IM00006 & IM00007) are not staying in the grooves and therefore the readings given are unreliable.
| 02SL - Stations (LUL) | Cxxx-NCR-000147 | NCR | Tremie Embedment |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-03-19 | 2012-08-06 15:03 | 140 | 2012-03-14 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Panel 38 ( Barrette): On one occasion, during pouring of P38 on CHS, the tremie embedment was 10.5m. Panel 35 ( Barrette): On one ocasion during pouring P35 on CHS, the tremie embedment was 10.3m. The root cause of these NCR was the timing of tremie removal was miss judged as concrete was coming up more than anticipated.
| 02SL - Stations (LUL) | Cxxx-NCR-000148 | NCR | P38 ( Barrette) - Panel Key time - 5hrs |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-03-19 | 2012-03-28 12:37 | 9 | 2012-03-14 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The time for P38 was exceeded by 35 min, making a total of 5:35 min for this activity. This was the first cage to be installed at CHS site, therefore, it required more time as expected as personnel needed to get used to the operations and interaction of activities on site.
| 02SL - Stations (LUL) | Cxxx-NCR-000149 | NCR | P35 ( Barrette) - Panel Key time - 5hrs |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-03-19 | 2012-03-28 12:41 | 9 | 2012-03-14 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The actual time was exceeded by 73 min. An issue was noted during the reinforcement cage installation which delayed the construction by approximatly 1.5 h.
| 02SL - Stations (LUL) | Cxxx-NCR-000150 | NCR | P3- Panel Key time - 5hrs |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-03-21 | 2012-05-01 11:59 | 41 | 2012-03-14 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The time required for P3 was exceeded 180 min. This issue was caused by use of extension cage resulted in an additional splice, thus additional time was required to install the cage. In addition to this, there was a desanding of the pump/ tremmie removed prior to completion of stop end installation ( pump removed when installing waterbar).
| 02SL - Stations (LUL) | Cxxx-NCR-000151 | NCR | P3 - Bentonite Testing |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-03-23 | 2012-05-01 13:26 | 39 | 2012-03-14 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Test was carried out on the 7th of March at 18:30 hrs, but however the result was not noted on Bentonite Site testing Report sheet. The Bentonite plant operator failed to fill in the Bentonite site testing report sheet. As the desanding process does not stop without the benonite plant operator confirming the completion of the exchange to the site engineer/ supervisor we can confrim that the sand content was within the limit.
| 02SL - Stations (LUL) | Cxxx-NCR-000152 | NCR | Surveillance for D- Wall - Cubes Storage |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-03-21 | 2012-04-30 11:58 | 40 | 2012-03-14 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Cubes were seen in back of van where the air temperature was 10 degrees.
| 02SL - Stations (LUL) | Cxxx-NCR-000153 | NCR | D- Wall Surveillance - Excavation Check sheet- Panel 12 |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-03-21 | 2012-03-28 12:47 | 7 | 2012-03-14 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Records presented for the days work for Panel 12 were not fully complete ( this had previously been raised, hence the NCR).
| 02SL - Stations (LUL) | Cxxx-NCR-000157 | NCR | P12 - Panel Key time - 5hrs |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-03-26 | 2012-05-01 13:30 | 36 | 2012-03-19 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Sliding bar detail was not as per fabrication drawing. Bars were not wired tied but welded. The additional bars to satisfy the lap requirements were fixed on site with bulldog grips. Post fixed bars were difficult to install which caused clashing of bars during splicing up the cage sections, thus required more time for the installation. In addition the requirement for the extention cage resulted in additional cage splicing time.
| 02SL - Stations (LUL) | Cxxx-NCR-000158 | NCR | P25 - Reinforcement Details |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-04-12 | 2012-05-01 13:37 | 19 | 2012-03-19 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Trim bar detail for reinforcement cage DSS P25 was not in accordance with drawing Cxxx-__-C-DWG-D061-50196-P03. Trim bar detail drawing was drawn mirrored compared to the cage fabrication drawing. This circumstance was not recognised during fabrication which caused the detail to be in the wrong orientation. The non-conformance was recognised before the cage was installed and was be resolved before the cage was used and thus does not have any effect on the final quality of the panel.
| 02SL - Stations (LUL) | Cxxx-NCR-000161 | NCR | Missing Spacers |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-04-03 | 2012-05-08 14:57 | 35 | 2012-03-20 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Three spacers installed on each row to cage number one and two of CHS B-37k
| 02SL - Stations (LUL) | Cxxx-NCR-000162 | NCR | Discrepancy between welding and CHS Barrette design Drawings |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-04-03 | 2012-05-18 19:16 | 45 | 2012-03-20 | Civil - Structural Engineering | 500 |  | Design | Repair |  | Complete |  | Completed |  | Below conflict between CHS Barrette Design and Welding and Lifting Details drawings regarding the skid spacers noted: Note 4 of drawing Cxxx-__-C-DWG-D061-50180 revP08 states '' 75mm SKID SPACERS PLACED 4 PER ROW AND SPACED 3m VERTICALLY-FRONT FACE.100mm BACK FACE LADDER FIXED ON SITE'', Drawing Cxxx-__-C-DWG-D061-50191 states ''SLEDGES SPACER IN PAIRS AT APPROX.4000mm CENTRES WELDED TO MAIN BARS ON FRONT FACE''
| 02SL - Stations (LUL) | Cxxx-NCR-000164 | NCR | Barrette - P53 Cage Links |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-03-23 | 2012-03-28 13:14 | 5 | 2012-03-20 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | 2 No. link sets were welded and not wire tied as per fabrication drawing. Drawing Cxxx-C08.090-DWG-BAU-0209 requires for the 2 top links of cage section 1 to be wire tied. Links were found welded during the cage inspection. The top trap-off band is desgined to be the top lifting point for the tandem lift (to bring the cage from horizontal to vertical orientation). To allow lifting parts of the 2 welded top links had to be cut off to give room for the lifting chains. Please see attached sketch.
| 02SL - Stations (LUL) | Cxxx-NCR-000168 | NCR | Composite sampling-DSS-P48 |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-04-02 | 2012-05-31 10:21 | 59 | 2012-03-26 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | Concrete compressive specimen cube samples (DSS-P48) from the first ready mix delivery truck were not sampled in accordance with the requirements of BS 8500 -1 annex B5 which specifies that testing shall be based on composite samples as defined in BS EN 12350-1. The laboratory technician confirmed that the cubes were made from a second spot sample, taken for consistency measurement. The first ready mix load was witnessed discharging the majority of its content into the pour with no planned arrangements that would facilitate composite sampling to be undertaken in a safe manner.
| 02SL - Stations (LUL) | Cxxx-NCR-000169 | NCR | Cathedral lifting bar welds |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-04-02 | 2012-05-01 13:40 | 29 | 2012-03-26 | Structural Engineering - Welding | 500 |  |  | Repair |  | Complete |  | Completed |  | 2x3 number weld per leg to the cathedral lifting bar of Barrette 43
| 02SL - Stations (LUL) | Cxxx-NCR-000173 | NCR | P49 ( Barrette) - Temporay steel works - Raker Bars |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-04-05 | 2012-04-04 15:18 | -1 | 2012-04-03 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | In one position on cage section 2 the legs of the raker bars are 200mm apart although the temporary design requires them to be almost butted. The position of the raker bars was not set out correctly during fabrication. N.B. The barrette cage was manufactured prior to __ QA engineer being on site at the factory.
| 02SL - Stations (LUL) | Cxxx-NCR-000176 | NCR | P25 - Cage Inspection |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-04-13 | 2012-04-13 13:26 | 0 | 2012-04-10 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Cage 1: 1) - Damage main bar / this bar has been bent when lifted.( please see photos 1 on the attached doc.) Cage 2: 2) -1 set of links missing. 3) -2 sets of links welded below the trapping band when they should be tied ( please see photo 2 on the attached document). 4) - 4 Nr spacers bars missing. 5) - 4 Nr racker bars missing. 6) - Raker bars are butted up to each other instead of lapped ( please see photo 3 on the attached doc.) 7) -box outs only have 2 angles securing then instead of 3, except for box 3. Cage 3: 8) - Hanging bars welded to the main bars out side the trapping band ( please see photo 4 on the attached doc.). 9) - Welds on the hanging bars are single sided not double sided.
| 02SL - Stations (LUL) | Cxxx-NCR-000180 | NCR | Barrette P36 Overrun of 5h Rule |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-04-16 | 2012-05-08 15:01 | 22 | 2012-04-10 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The time needed for B36 on CHS is 6:48h and thus exceeded the limit by 1:48 hours. Causes for this Occurrence : First 7 concrete trucks which arrived on site had to be rejected due to the flow limit being out of tolerance. First concrete truck which was out of tolerance arrived 1:54h earlier than the first concrete truck which was used for the actual start of concreting and would have allowed commencement of concreting in the case of compliance within the 5h limit. The non compliance of the concrete was caused by a defect pipe used to add the admixture to the concrete.
| 02SL - Stations (LUL) | Cxxx-NCR-000181 | NCR | Barrette P33 Not concreted to cut-off level |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-05-31 | 2012-05-31 11:00 | 0 | 2012-04-10 | Civil - Civil Engineering General | 500 |  |  | Rework |  | Complete |  | Completed |  | The concrete quality at cut off level (notionally at a level 100mm below the bottom of the lower coupler - B33 cut off is above platform level and is to be built up later by others during capping beam construction) is suspected to be of poor quality due to the concrete not being over poured/flushed correctly. The concrete was not poured to the top of guidewall level as required to allow access to the sonic tubes which had been provided at lengths which did not allow access above guidewall level. - Cause of this ocurrance: The top level of the sonic tubes detailed on the reinforcement drawing (Cxxx-__-C- DWG- 50190 - P07) does not allow to carry out integrity testing when concreting to the required cut-off level.
| 02SL - Stations (LUL) | Cxxx-NCR-000182 | NCR | D-Wall Panel P12 Not concreted to cut-off level |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-05-31 | 2012-05-31 11:08 | 0 | 2012-04-10 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The panel was poured just to platform level 111.3 mATD, however the last metre is contaminated with bentonite, hence the concrete at cut-off level is not as of the required quality. Causes for this ocurrance: Concrete was not flushed over platfrom level to guarantee the the required quality of concrete at cut-off level.
| 02SL - Stations (LUL) | Cxxx-NCR-000183 | NCR | Concrete Cube Storage Temperature |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-06-20 | 2012-06-19 14:05 | -1 | 2012-04-13 | Structural Engineering - Diaphragm Walls | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | The temperature in the bentonite lab where the cubes are kept was read as 7 degrees celcius at 09:00 on Friday 13/04/12. Having completed concreting that morning the temperature was found to be below that required.
| 02SL - Stations (LUL) | Cxxx-NCR-000186 | NCR | P46 - Raker Bar |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-04-20 | 2012-04-24 14:59 | 4 | 2012-04-18 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The raker bars on cage 2 for panel 46 were not positioned as per drawing details. Please see Photo attached
| 02SL - Stations (LUL) | Cxxx-NCR-000192 | NCR | P10 - Overrunning the 42 Hrs Rule |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-04-27 | 2012-05-02 14:26 | 5 | 2012-04-26 | Structural Engineering - Diaphragm Walls | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The time passing during construction for P10 on CHS was 64:30h. However, as per PTR-00103, starter panels on CHS will not themselves be extended by 3m but the adjacent runner panel will be. What caused this delay: It was understood by __ that all of the required paperwork was in place and accessible prior to and during excavation and construction of Panel 10. However, permission was not given by CRL for __ to use the stop end lifting cap because the existing certification was deemed insufficient. This caused a hold on work until sufficient certification could be sourced, delaying construction progress by approximately 24hours.
| 02SL - Stations (LUL) | Cxxx-NCR-000193 | NCR | P24 - Reinforcement - Temporary Works Issue |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-05-25 | 2012-05-31 13:31 | 6 | 2012-05-22 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | During the Inspection for the Cages for Panel 24 the following issues have been identified: 1) - Cage 5 and 6, hanging bars are 110mm too long. 2) - Splice Lengths main bars vary on all cages approx 100 - 150 mm short. 3) - Cage 3 / 4/5 & 6, raker bars not overlapped and welded length at nodes 50% of the design. 4) - All cages cathedral hangers welds not as per design in qty, number, length of weld. Weld is really poor in a number of locations specially on back face. Please see photo attached. 5) - Cage 3 and 4, Temp raker bars shown in design as fixed on outside face,are actually welded on inside of cage. Cannot be removed as per the design. .
| 02SL - Stations (LUL) | Cxxx-NCR-000195 | NCR | P10 - Overrunning 1 Hr rule for concrete |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-05-03 | 2012-05-02 14:09 | -1 | 2012-04-26 | Structural Engineering - Structural Engineering - General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The time limit between two consecutive concrete pours was exceeded on 1 occasion when concreting P10 on CHS with a overrun of 17min. What caused the issue: Compounding contributing factors lead to the time between concrete pours being placed to exceed the 1 hour rule. Firstly the diesel slurry pump on site broke down and could not be repaired. As such the toyo pump was used to continue sucking out the slurry. The overall time required to fix the pumping problem was underestimated, and as such the concrete dispatches were not called off or held. As a result 6No concrete trucks were queueing up on site before it was possible to recommence pouring. Due to the concrete having to wait, the 6No. loads were out of specification and had to be rejected. More concrete was called off and poured as soon as possible.
| 02SL - Stations (LUL) | Cxxx-NCR-000199 | NCR | P11- Excavation |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-06-20 | 2012-06-19 14:13 | -1 | 2012-04-24 | Civil - Excavation | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | P11 has not been excavated to the designed toe level. Panel 11 has been under - dug by approximately 450 mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000200 | NCR | P25- Panel Key time - 5hrs |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-05-11 | 2012-06-20 14:25 | 40 | 2012-05-01 | Structural Engineering - Diaphragm Walls | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The time needed for P25 on DSS is 6:47 h and thus exceeded the limit by 107min. What caused the delay: Installing the reservation tube in the slot at the back of the steel stop-end took longer than expected due to the slot not beeing perfectly aligned at the stop-end joind.
| 02SL - Stations (LUL) | Cxxx-NCR-000201 | NCR | P1 - 42 Hr rule and cage Extension |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-05-04 | 2012-05-18 19:23 | 14 | 2012-05-03 | Structural Engineering - Diaphragm Walls | 500 |  | Equipment Breakdown | Use As-Is |  | Complete |  | Completed |  | P1 on CHS was excavated to a depth of 15m and was subsequently backfilled due to a breakdown of the grab. Top of London clay is at 8m depth, therefore the depth for commencement of the 42 hour rule is 11m. Excavation depth of 11m was reached 0830. Backfill was completed at 1950. This means that a 4m length of panel will be open in excess of 42 hours. In view of the relatively short length of panel exposed – and that the exposed length is at the top of the panel - we request that the panel is not extended by the specified 3m. N.B. The extra 3m excavation results in the panel being open longer than a standard panel due to the additional time taken to excavate, install the extended stop end, install the extended cage and concrete.
| 02SL - Stations (LUL) | Cxxx-NCR-000202 | NCR | P10 Tremmie Embedment |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-04-27 | 2012-05-08 15:09 | 11 | 2012-04-25 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Tremie embedment was recorded as 12.3m and 12.8m at consecutive tremie breaks during pouring the concrete for P10 on CHS. What caused the Problem: Primarily, the length of tremie embedment was misjudged leading to a 12.3m embedment. At this stage, unaware of the over embedment and following the normal proceedures, a 3m section of tremie was removed before and the next batch was poured. Following this pour, it was then realised that the tremie was over embeded, now by 12.8m, and as such 6m of tremie were immediately removed to correct the embedment to within the specifications.
| 02SL - Stations (LUL) | Cxxx-NCR-000207 | NCR | P32- Tremie Embedment |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-05-24 | 2012-05-23 11:34 | -1 | 2012-05-01 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Tremie embedment exceeded allowed tolerances of min 3m to max 10m stated in the D-wall ITP. Tremie embedment was recorded as 11.8m at consecutive tremie breaks during pouring the concrete for P32 on CHS. What was the root cause: Primarily, the length of tremie embedment was misjudged leading to a 11.8m embedment. Following this pour, it was then realised that the tremie was over embeded and as such 6m of tremie were immediately removed to correct the embedment to within the specifications.
| 02SL - Stations (LUL) | Cxxx-NCR-000208 | NCR | DSS P2 - Damage to Reinforcement Cage During Fabrication |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-04-30 | 2012-05-08 15:24 | 8 | 2012-04-27 | Civil - Civil Engineering General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | It has been brought to CRL attention that during the inspection of DSS P2 at the fabrication yard it was observed that 2nr near face and 2nr far face main bars had been damaged. The bars had been scored along their length with a grinder during the removal of some missed placed welded temporary works bars. This has been marked up on the attached fabrication drawing with the details of the damaged bars.
| 02SL - Stations (LUL) | Cxxx-NCR-000224 | NCR | P24 - 66 Hrs rule, exceeded 2nd time around |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-05-31 | 2012-05-31 13:08 | 0 | 2012-05-21 | Structural Engineering - Diaphragm Walls | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | The 66 hour rule was exceeded during the construction of Panel 24 at Durward Street. Also the 5hour rule was exceeded during the construction of Panel 24 at Durward Street. Root Cause And Timeline : The length of time for panel installation was a cumulitive problem with two sequences of excavation being undertaken: During the 1st Excavation, the 1st bite was not vertical in the x direction due to the positioning of the grab (the grab had to be outside the 6m exclusion zone and its orientation to the corner panel was less than ideal.) The 2nd bite deviated due to its overlap with the 1st bite which had left a wedge of material because of its x deviation. Furthermore there was excess concrete on the stop end adjacent to Panel 25 which caused difficulty in excavation. Before the 2nd bite was fully complete, the grab broke down. With the weekend approaching limiting personnel availability, and uncertainty of the time it would take to repair the grab, the excavation was terminated and backfilled with a PFA mix. During the 2nd excavation, 3 days later, there was a reaction between the PFA mix backfill while it was being excavated and the bentonite slurry. The bentonite required treatment multiple times to counteract the reaction and maintain the correct properties. This reaction and treatment made the exchange of the bentonite very slow for it to reach the required properties for concreting.
| 02SL - Stations (LUL) | Cxxx-NCR-000225 | NCR | P24 - Reinforcement Issues- link in the cage/ Splice Coupler |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-05-30 | 2012-06-06 10:51 | 7 | 2012-05-21 | Structural Engineering - Reinforcement | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | 1) Link below trap off band on middle cage had to be cut at 12 positions to allow trapping off of the cage. Please see attachments: P24 Mid Cage Link Cut 1of2 120428.pdf and P24 Mid Cage Link Cut 2of2 120428.pdf 2) 1No coupler was only torqued to a approx. 80Nm and not as required to 350Nm. See attachments: P24 Mid-Top Splice Coupler 1of2 120428.pdf and P24 Mid-Top Splice Coupler 2of2 120428.pdf Root Cause: 1) Space between trapping band and link was only 120mm which was not sufficent to use 160mm high trap off beams. The link was detailed in this position and missed during checking. 2) If coupler would have been torqued to 350Nm the limit groove would have been fully visible above the lock nut which would result in an overextension of the coupler. It is not entirely certain why the 2 main bars with the coupler did not match up but it is suspected that due to the position of the coupler during fabrication in the centre at the bottom of the cage and the high density of reinforcement the position could not set out prefectly.
| 02SL - Stations (LUL) | Cxxx-NCR-000226 | NCR | P01- Panel Key time - 5Hrs |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-06-15 | 2012-06-12 11:49 | -3 | 2012-05-21 | Structural Engineering - Diaphragm Walls | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The 5 hour rule was exceeded during the construction of Panel 1 at Cambridge Heath. The 5 hour rule is the window between the end of bentonite circulation and the commencement of concreting. The Root Cause: 1. The shear links below the trap off bands were closer than the design position which did not allow the trap off beams to pass through. The cage was finally trapped off below the obstructing link and the gap to the trap off band was supported with wood spacers. 2. The guide wall had a slight step in it and was damaged, requiring an I-beam to be placed along it's length for the trap off bars to sit on. 3. The installation of the cage was slower than expected due to a revised method of connecting the couplers (multiple coupler sizes requiring different torques, a revised system was put in place to make the different torquing more visable to __ and CRL.)
| 02SL - Stations (LUL) | Cxxx-NCR-000230 | NCR | P23- locaation of the 60.3mm Sonic Reservation Tubes |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-05-28 | 2012-07-16 13:24 | 49 | 2012-05-14 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Fabrication drawing no Cxxx-__-C-DWG-D061-50241 shows the 4x 60.3 mm sonic reservation tubes to be installed between B16-71-LK (Outside links) and B32-14 (rakes bars), During the inspection to the P23 cage the two outer sonic tube found between bars B32-14 (rakes bars) and B16-70-LK For more clarification please refer to the attached photo and the fabrication drawing
| 02SL - Stations (LUL) | Cxxx-NCR-000232 | NCR | P24- Final Grab Pass ( DSS ) |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-05-23 | 2012-07-10 16:36 | 48 | 2012-05-21 | Civil - Excavation | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | On Panel 24 no data was recorded during the final grab pass. Therefore we are unable to confirm that the verticality is within tolerance. Root Cause : The grab pass is normaly carried out in the morning by the day shift operator. Due to the circumstances during the construction of P24 the grab pass was carried out at night. The grab operator on the night shift was not briefed to do a digital recording of the grab pass.
| 02SL - Stations (LUL) | Cxxx-NCR-000234 | NCR | P2 - Exceeding 42 Hrs Rule (DSS) |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-05-30 | 2012-07-03 10:39 | 34 | 2012-05-22 | Structural Engineering - Diaphragm Walls | 500 |  | Equipment Breakdown | Use As-Is |  | Complete |  | Completed |  | As per PTR-135 __ was instructed to extend P02 on DSS by 3m within the 42h timeframe due to an overrun of the 66h rule on P03. The time passing during construction for P02 on DSS was 43:55h. Root Cause: Due to slow excavation caused by concrete behind the steel stop-end and a hydraulic hose breakdown on the grab the excavation was only finished at 14:50 on the second day. This caused all activties which were scheduled to start in the morning of the second day to be delayed to the afternoon. N.B. the additional cage section and volume of concrete also contributed to the total time to build the panel.
| 02SL - Stations (LUL) | Cxxx-NCR-000235 | NCR | P32- Sonic Integrity Testing Results ( CHS) |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-06-29 | 2012-08-15 09:00 | 47 | 2012-05-22 | Civil - Civil Engineering General | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | Sonic logging of Panel 32 at Cambridge Heath shows a flaw at approximately 27-28m below top of guide wall. The logging shows the flaws on all except one of the readings, with flaws being shown on both the diagonal readings, indicating the inclusion is located central to the panel. Root Cause: The bentonite extraction pump broke down during the pour. The concrete pour was stopped temporarily until the bentonite pumping could be resumed. The concrete record shows the pour commencing at 23:03 and completing at 00:00, during which time there was a break of approximately 40minutes. During this stoppage, the one hour rule between consecutive pours was not exceeded, the concrete workability of 4 hours was not exceeded and the tremmie embedment was within the limits. However it is suspected that the lack of continuity in the pour has caused the inclusion of bentonite into the concrete.
| 02SL - Stations (LUL) | Cxxx-NCR-000236 | NCR | P12- Exceeding 5hrs rule (CHS) |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-05-23 | 2012-06-20 15:16 | 28 | 2012-05-21 | Structural Engineering - Diaphragm Walls | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | D-Wall Panel P12 has exceeded the 5hrs rule -> The time needed for P12 on CHS is 5:52h and thus exceeded the limit by 52min. Root Cause: As the pour was simulataneous with a continuing pour at DSS (P44) the concrete wagons were busy. As DSS was pouring backfill mix trucks could not be diverted immediately. In addition the concrete supplier had some issues with securing additional trucks on the day. This resulted in a delay to the start of CHS.
| 02SL - Stations (LUL) | Cxxx-NCR-000237 | NCR | P12- Concrete ( CHS) |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-06-24 | 2012-06-20 14:45 | -4 | 2012-05-22 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Only 2No sets were taken for a concrete quantity of 175,5m3. Root Cause: Concrete tester only brought 2No sets of moulds to site for the pour of P12.
| 02SL - Stations (LUL) | Cxxx-NCR-000238 | NCR | P22 - Excavation ( CHS) |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-06-07 | 2012-07-03 10:56 | 26 | 2012-05-21 | Civil - Excavation | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | Excavation tolerance is not within tolerance of 1:225 specified in D-wall ITP .The achieved deviation in the y-axis in 26m depth was only 1:195. Root Cause of these Ocurrance: When experiencing the deviation the grab operator did not start countermeasures fast enough which would have allowed him to rectify the excavation enough to stay within the tolerances.
| 02SL - Stations (LUL) | Cxxx-NCR-000239 | NCR | P3 - Horizontal Couplers ( CHS) |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-06-07 | 2012-06-06 11:12 | -1 | 2012-05-22 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | 2No coupler U-bars are missing in cage P03 on CHS. See attached drawing for details of the missing bars/couplers. Root Cause: The coupler bars were not installed during fabrication due to an error reading from the drawing - the missing couplers are adjacent to the earthing connection. The cross section for the earthing connection only shows 2 coupler. The additional slab coupler detail was not noticed.
| 02SL - Stations (LUL) | Cxxx-NCR-000241 | NCR | P3 - exceeding 42hr rule ( CHS) |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-06-07 | 2012-07-16 13:31 | 39 | 2012-05-17 | Structural Engineering - Diaphragm Walls | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The 42hr hour rule on P03 has been exceeded. The panel was completed yesterday evening at 22:00hrs.This resulted in approximatly 22hrs exceedence. Root Cause: The spliced connection between top and middle steel cages gave a number of problems requiring 5No of the couplers to be omitted and replced with conventional splicing bars. The time taken to resolve these issues extended the time at which the panel was ready for concreting until around 11pm on 15/5/2012 by which time the concrete supplier was unable to secure sufficient resource to guarantee continuity of pouring threough the night. Consequently the concreting phase was abandoned that evening and an efficient bentonite circulation system set up within the panel to run overnight, (the cage remaining fully installed at this stage). N.B. During the reconnection of the top to middle cages 5 no 50/32mm couplers had to be removed due to damage. 40mm bars 6m long were spliced across the connections where the couplers removed. The splice length equates to 93 x bar diameter. N.B. All of the above has been discussed and agreed with CRL/Cxxx.
| 02SL - Stations (LUL) | Cxxx-NCR-000242 | NCR | Spacing between links and Cathedral bars shape code |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-05-31 | 2012-07-26 12:56 | 56 | 2012-05-17 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Incorrect spacing between links located below the first BX22 –Cage4 (as built=380mm Design 225mm) Incorrect spacing between links located below the second BX22 –Cage4 (as built=350mm Design 225mm) Incorrect spacing between links located below BX20 –Cage5&6 (as built=310mm Design 225mm) Incorrect spacing between links located below BX21 –Cage5&6 (as built=290mm Design 225mm) Incorrect spacing between links located between the first trapping band and first set of links-Cage6&5 (as built=510mm Design 375mm) Shape code to the cathedral bars of cages 1,3&5 is not as specified (99-003) on the fabrication drawing Cxxx-__-C-DWG-D061-50139 P05
| 02SL - Stations (LUL) | Cxxx-NCR-000243 | NCR | P4 - Cage Modifications(DSS) |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-06-29 | 2012-07-10 16:47 | 11 | 2012-05-22 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | To allow installation of the cage, 7m of main bars, links and sonic tubes were cut off from the bottom cage as per attached drawing from cage P04 (Cxxx-C08.090-DWG-BAU-0158/0159) on DSS. Root Cause: Panel 03 has been constructed with a significant concrete overbreak behind and underneath the steel stop end towards panel 04. This was caused as the grab length equalled the panel length (3200mm) during excavation of panel 03. In this case, concrete obstructions on the stop end push the grab constantly into the opposite excavation face and thus cause breakouts which fill with concrete during the subsequent pour. During excavation of the following panel, overbreak concrete behind the steel stop end can be removed by the grab as it uses the steel stop end as a lock and guide system. Below the steel stop end there is no lock and guide system available. The free hanging grab can not remove significant concrete overbreaks as, always depending on the concrete strength, it runs away from the obstruction rather than breaking through it. The remaining concrete below the steel stop end in panel 04 could not be removed and required the cage to be trimmed in order to avoid clash with the obstruction.
| 02SL - Stations (LUL) | Cxxx-NCR-000244 | NCR | P13 - Tunnel Trimmer |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-05-21 | 2012-05-23 12:26 | 2 | 2012-05-18 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | P13 Layer F3 main bar is missing it's trimming anchor (welded on the next bar).
| 02SL - Stations (LUL) | Cxxx-NCR-000248 | NCR | P21 - Tremie Embedment |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-06-08 | 2012-06-25 17:51 | 17 | 2012-05-22 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Tremmie embedment was recorded as 10.5m on one occasion during pouring the concrete for P21 at CHS. Root Cause: Insufficient attention paid to the rise of concrete leading to over embedment which was immediately corrected.
| 02SL - Stations (LUL) | Cxxx-NCR-000252 | NCR | P15 - DSS Missing trim bars |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-06-08 | 2012-05-31 13:38 | -8 | 2012-05-29 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | 2No trim bars in cage P15 on DSS were not installed as per fabrication drawing. Root Cause: QA check from __ foreman and __ QA engineers carried out in the __ fabrication yard did not recognize the lack of trim bars.
| 02SL - Stations (LUL) | Cxxx-NCR-000253 | NCR | P13 - Final Grab Pass |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-06-12 | 2012-05-31 13:49 | -12 | 2012-05-29 | Structural Engineering - Diaphragm Walls | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | On Panel 13 on CHS no record of the final grab pass is available. Therefore we are unable to confirm the the verticality is within tolerance. Root Cause: File recorded by the MC64 grab system during the final grab pass was corrupted and could not be read by the computer software. There is no evidence of the MC64 grab computer being broken as records on following panels could be read. It would appear that the reading error was caused by defect sectors on the storage medium.
| 02SL - Stations (LUL) | Cxxx-NCR-000254 | NCR | P04 -DSS -Exceeding 66+5h rule |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-06-15 | 2012-07-10 16:55 | 25 | 2012-05-29 | Structural Engineering - Diaphragm Walls | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The 66 hour rule was exceeded during the construction of Panel 4 at Durward Street by 28min. The 66 hour rule is an extension of the 42 hour rule, and measured between the time when the soil profile 3m below the top of London Clay is exposed to the time when the soil profile is covered again by the concrete. Also the 5hour rule was exceeded during the construction of Panel 4 at Durward Street by 4:13h. The 5 hour rule is measured as the time between the end of bentonite exchange and the commencement of the concrete pour. Root Cause: The modifications required to the bottom cage as per __ NCR "040 NCR DSS P04 Cage modification" required additional time to be prepared and carried out. This resulted in exceeding both the 5h and 66h rule.
| 02SL - Stations (LUL) | Cxxx-NCR-000255 | NCR | P13 Reinforcement cage issues -CHS |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-06-14 | 2012-06-12 11:54 | -2 | 2012-05-31 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | 1-)1No coupler overextended when joining the top and middle cage of P13. The limit groove was 23mm above the locking nut of the coupler. See attached sketch for position of coupler. 2) - 1No 40mm sliding bar was replaced by a 32mm 7m long splicing bar. See attached sketch for position of replaced sliding bar. Root Cause: 1-) The root cause of this issue is not yet known. 2-) Sliding bar was wire tied to the cage during delivery. Wire was cut in accordance to the note on the fabrication drawing saying the sliding bar to be lowered into position after the cage section is spliced. However, after cutting the wire the sliding bar was sliding down in free fall and the weld on the stopper bar was not strong enough to withstand the forces caused by the falling bar. Sliding bar fell into the trench and could not been recovered.
| 02SL - Stations (LUL) | Cxxx-NCR-000256 | NCR | P14 - Overrun 5Hrs Rule |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-06-11 | 2012-06-20 15:07 | 9 | 2012-05-31 | Structural Engineering - Diaphragm Walls | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The time needed for P14 on CHS is 5:48 h and thus exceeded the limit by 48min. Root Cause: The last grab pass and precast stop end installation were completed earlier than on previous panels due to improved routine of the workforce. As a consequence the bentonite circulation finished early at 10:45h and cage installation started at 11:10h. Concrete and backfill material deliveries were booked for 16:00h and could not be brought forward. The remaining time did not allow sufficient time to offload the backfill gravel and test concrete prior to start of the pour within the 5 hour rule. The site supervisor and site engineer did not check if sufficient time is available to start concreting within the 5 hour rule when the decision was taken to stop bentonite circulation and start reinforcement installation.
| 02SL - Stations (LUL) | Cxxx-NCR-000257 | NCR | P23 Exceeding 42+5h rule-DSS |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-06-15 | 2012-06-21 08:21 | 6 | 2012-05-31 | Structural Engineering - Diaphragm Walls | 500 |  | Equipment Breakdown | Use As-Is |  | Complete |  | Completed |  | __ was instructed by CRL to extend P23 on DSS by 3m within the 42 timeframe due to an overrun of the 66h rule on P24. The 42 hour rule was exceeded during the construction of Panel 23 at Durward Street by 2:25h. Also the 5hour rule was exceeded during the construction of Panel 23 at Durward Street by 3h. Root Cause: A leakage on the grab machine required immediate repair which delayed the excavation. A further delay was caused by a blockage within the toyo pump, which was dealt with on site immediately . The combination of these two circumstances did not allow to finish the construction within 42h.
| 02SL - Stations (LUL) | Cxxx-NCR-000259 | NCR | P25 - Overrun the 42 Hr rule -CHS |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-06-20 | 2012-07-10 17:02 | 20 | 2012-06-06 | Structural Engineering - Diaphragm Walls | 500 |  | Equipment Breakdown | Use As-Is |  | Complete |  | Completed |  | The time passed during construction for P25 on CHS was 54.5 hours. Root Cause: The MC64 hydraulic grab unit experienced two major machine breakdowns during excavation of P25. The bespoke interruptions caused delays which could have resulted in a working hour exceedance according to the prevailing section 61 and D9 agreement. __ postponed the concrete pour upon request of __ to the following day.
| 02SL - Stations (LUL) | Cxxx-NCR-000260 | NCR | P05-Position Installation -DSS |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-07-27 | 2012-07-24 16:57 | -3 | 2012-06-08 | Civil - Excavation | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | DSS P5 D-wall reinforcement cage was installed with 250mm cover to the near face of the panel. With design cover to the near face being 100mm, the cage has been positioned 150mm out of position towards the far face of the diaphragm wall. During the installation of the cage, cover to the front of the cage was kept to 100mm. During the final stages of lowering the cage to its final position, the cage took up a position towards the far face of the excavation. An attempt to move the cage was not successful so the cage was trapped off and cast in this position. Root Cause: It is uncertain what exactly has caused the as-built position of the cage. One possible explanation is that due to the shape and inherant rigidity of the cage, any deviations of the excavations will have a greater effect on the position of the top of the cage at ground level as the cage sits rigid and vertical within a deviating excavation. Records of the excavation were within construction tolerances.
| 02SL - Stations (LUL) | Cxxx-NCR-000262 | NCR | P23 and P22- Waterbar detachment |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-06-29 | 2012-07-10 17:10 | 11 | 2012-06-08 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Waterbar between DSS P23 and P22 not in design position for bottom 15m: During the extraction of the steel stop end when excavating DSS P22, it was noticed that the waterbar slot in the stop end was full of hardened concrete. We must therefore conclude that the waterbar is not in its intended position for the bottom 15m. Root Cause: The root cause cannot be clearly identified as it was only discovered 3 weeks after the stop end was placed. It is suspected that the water bar became either undone during the installation of the stop end (not securely fixed into slot). We do not believe that the placing of the cage was the root cause at it was not moved upwards and thus could not have caught the waterbar.
| 02SL - Stations (LUL) | Cxxx-NCR-000269 | NCR | P22 - Position Installation -DSS |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-07-27 | 2012-07-24 17:20 | -3 | 2012-06-15 | Civil - Excavation | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | DSS P22 D-wall reinforcement cage was installed with 250mm cover to the near face of the panel as previously occured for T-panel P05 (BTL-__-Cxxx-NCR-000049). With design cover to the near face being 100mm, the cage has been positioned 150mm out of position towards the far face of the diaphragm wall. During the installation of the cage, cover to the front of the cage was kept to 100mm. During the final stages of lowering the cage to its final position, the cage took up a position towards the far face of the excavation. An attempt to move the cage was not successful so the cage was trapped off and cast in this position. Root Cause: It is uncertain what exactly has caused the as-built position of the cage. One possible explanation is that due to the shape and inherant rigidity of the cage, any deviations of the excavations will have a greater effect on the position of the top of the cage at ground level as the cage sits rigid and vertical within a deviating excavation. Records of the excavation were within construction tolerances.
| 02SL - Stations (LUL) | Cxxx-NCR-000270 | NCR | DSS-P7-Missing fish plates from cage 1 |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-06-27 | 2012-07-05 15:39 | 8 | 2012-06-13 | Civil - Structural Engineering | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Missing two fish plates from cage 1
| 02SL - Stations (LUL) | Cxxx-NCR-000274 | NCR | DSS-P07-Horizontal Couplers |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-06-27 | 2012-07-02 09:36 | 5 | 2012-06-13 | Civil - Structural Engineering | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Number of horizontal couplers on cage 2&3 listed below and shown on the attached file found recessed and the face level was lower than the designed level, as a result the couplers were not protruding the boxout’s foam at the time of inspection, Cage 2: • Boxout 1: 2 No. couplers in row 5, 1no. coupler in row 7 and 1no.coupler in row 8 • Boxout 4: 1 No. coupler in row 1 Cage 3: • Boxout 1: 1No. coupler in row 2 • Boxout 2: 1 No. coupler in row 1, 1 No. coupler in row 2
| 02SL - Stations (LUL) | Cxxx-NCR-000278 | NCR | P22 - Slab Coupler |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-07-06 | 2012-06-21 09:41 | -15 | 2012-06-15 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Slab couplers in P22 top slab short: Some slab couplers in P22 top slab connection (boxout type 72 between 109.950mATD and 109.500mATD) are unevenly protruding the near face of the cage. ( please see BTL-NCR-000052 attached for further details and photos). Root Cause: The cutting and bending accuracies required to make the couplers sit all at one level for this U bar are difficult to achieve, which results in uneven placing of horizontal couplers.
| 02SL - Stations (LUL) | Cxxx-NCR-000279 | NCR | P05- Overrun of 42hour rule |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-07-09 | 2012-07-16 13:42 | 7 | 2012-06-15 | Structural Engineering - Diaphragm Walls | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The time passed during construction for P05 on CHS was 77h 10min. Root Cause: The supplier of backfill material for precast stop ends cancelled the delivery due to a lack of lorries without informing the __ site team properly (an answer phone message was left but no direct conversation or written confirmation took place). This was discovered when site was ready for concreting on Tuesday, 12.06.12 at 18:30h. No alternative backfill material could be provided at this time and the pour was postponed to Wednesday, 13.06.12.__ requested additional brushing of the precast stop end waterbar prior to concreting. Consequently the cage had to be removed from the panel which took until 14:00h on Wednesday due to complicated desplicing. Finalization of the panel on the same day would have resulted in a working hour exceedance according to the prevailing section 61 and D9 agreement. __ postponed the concrete pour upon request of __ to the following day. Brushing of the waterbar and reinstallation of the reinforcement took place on Thursday, 14.06.12 followed by installation of concrete.
| 02SL - Stations (LUL) | Cxxx-NCR-000280 | NCR | P06 Missing verticality report |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-06-29 | 2012-06-21 10:30 | -8 | 2012-06-15 | Civil - Excavation | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Verticality report for final grab pass on P06 (DSS) is missing. Before the final grab pass for P22-1, the operator did not change the panel number in the BTronic software. As a consequence the system overwrote the last file (panel 06).
| 02SL - Stations (LUL) | Cxxx-NCR-000281 | NCR | P04 Strain gauge damage -CHS |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-07-06 | 2012-07-11 16:36 | 5 | 2012-06-15 | Civil - Civil Engineering General | 500 |  | Damaged | Reject |  | Complete |  | Completed |  | One pair of strain gauges on CHS P04 has no useable reading after concreting. Strain gauge #11 has no reading at all whilst the reading for adjacent strain gauge #12 is out of the allowed strain range of 3000µs. See attached strain gauge installation report for details. Root cause: Strain gauge 11 damaged during concreting.Strain gauge 12 has been predamaged. Sensor has been tested but not replaced prior to reinforcement installation into the panel. The technician was unaware of the 3000µs strain range.
| 02SL - Stations (LUL) | Cxxx-NCR-000290 | NCR | DSS Barrete 47 - 5 hour rule |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-08-06 | 2012-08-06 15:53 | 0 | 2012-07-06 | Civil - Civil Engineering General | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | The time needed for P47 on DSS is 5:30 h and thus exceeded the limit by 30min. Root Cause: Due to the sudden closure of the Cxxxmain concrete batching plant (Bow) by the olympic authorities on 16/06/12, the concrete supplier had to redistribute the complete workload to surrounding batching plants. The resulting reorganisation caused delays to booked and confirmed pours (B47 concrete was ordered for 14:00 on the 19/06/2012, first load arrived on site at 15:59h).
| 02SL - Stations (LUL) | Cxxx-NCR-000294 | NCR | P15: Overrun of 5 hour rule-CHS |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-08-10 | 2012-08-06 16:57 | -4 | 2012-07-06 | Structural Engineering - Diaphragm Walls | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | The time needed for P15 on CHS is 6:03 h and thus exceeded the limit by 63min. ROOT CAUSE: During the installation of the reinforcement cage a few couplers did not match correcly. The cage installation took longer than normal.
| 02SL - Stations (LUL) | Cxxx-NCR-000295 | NCR | P05 Coupler issues -CHS |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-08-10 | 2012-08-10 08:58 | 0 | 2012-07-06 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | During the installation of the reinforcement cage on Panel 5, the splice between top and middle cages, the following issues arose with couplers;• 1no. Coupler was tightened to the specified torque but showed signs of overextension above the tolerance band by 5mm showing above the locking band. • 1no. Bar wouldn’t sit fully inside the receiving coupler and thus was restricting the connection of all other remaining coupler/bars. Please see sketch no. Cxxx-BTL-SK170 - P05 - COUPLER NCR's - REV A which is attached for further illustration of location of coupling issues.
| 02SL - Stations (LUL) | Cxxx-NCR-000296 | NCR | P21: Overrun of 5+42 hour rules |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-08-17 | 2012-08-15 12:11 | -2 | 2012-07-09 | Structural Engineering - Diaphragm Walls | 500 |  | Equipment Breakdown | Use As-Is |  | Complete |  | Completed |  | __ was instructed to extend P21 on DSS by 3m within the 42 timeframe due to an overrun of the 66h rule on P24.The 42 hour rule was exceeded during the construction of panel 21 by 4h 47min. The 42 hour rule is measured between the time when the soil profile 3m below the top of London Clay is exposed to the time when the soil profile is covered again by the concrete.Also the 5hour rule was exceeded during the construction of panel 21 by 45min. The 5 hour rule is measured as the time between the end of bentonite exchange and the commencement of the concrete pour. ROOT CAUSE: 42 hour rule - The grab crane unit had two breakdowns due an intercooler hose blowing off. Also the concrete supply was 45 min late and due to a lack of concrete wagons the supply rate was slow. 5 hour rule - Concrete arrived on site 45 min later that ordered as __ concrete lorries were finishing off another delayed pour.
| 02SL - Stations (LUL) | Cxxx-NCR-000297 | NCR | P21 and P20 waterbar detachment |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-08-30 | 2012-08-15 12:22 | -15 | 2012-07-09 | Civil - Civil Engineering General | 500 |  | Damaged | Use As-Is |  | Complete |  | Completed |  | During the extraction of the steel stop end whilst excavating DSS P20, it was noticed that the bottom 6m of the waterbar slot in the stop end was full of hardened concrete. We must therefore conclude that the waterbar is not in its intended position for the bottom 6m. Root Cause: During the installation of the stopend between P20 and P19 it was noticed that the stopend was bent which could have caused the water bar to slide out of the slot during positioning of the stop end.
| 02SL - Stations (LUL) | Cxxx-NCR-000298 | NCR | P20: Overrun of 42 hour rule-DSS |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-08-17 | 2012-08-09 09:30 | -8 | 2012-07-06 | Structural Engineering - Diaphragm Walls | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | __ was instructed to extend P20 on DSS by 3m within the 42 timeframe due to an overrun of the 66h rule on P24. The 42 hour rule was exceeded during the construction of panel 20 by 7h 30min. The 42 hour rule is measured between the time when the soil profile 3m below the top of London Clay is exposed to the time when the soil profile is covered again by the concrete. Root Cause: 1) 3m additional excavating prolonged the excavation time2) The stop end released from panel 21 was deformed (top 10m were bent) which extended the stop end positioning process.3) CHS and DSS pours on the day were planned consecutively, backshift concrete was booked for DSS only. Delays on CHS resulted in a simultaneous pour of CHS and DSS. The wagons booked for DSS had to be shared with CHS, additional concrete lorrie swere unavailable on short notice. As a consequence, concreting time was prolonged. 4) The start of concrete pour was delayed as the concrete batcher of the new main plant (Greenwich) decided to finish off CHS pour before supplying DSS. This was denied by the __ site engineer who instructed the batcher to release DSS concrete immediately.
| 02SL - Stations (LUL) | Cxxx-NCR-000299 | NCR | P26 Strain gauge damage-CHS |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-08-30 | 2012-08-06 17:20 | -24 | 2012-07-09 | Civil - Civil Engineering General | 500 |  | Damaged | Reject |  | Complete |  | Completed |  | One pair of strain gauges on CHS P04 (strain gauges #03 and #04) has no useable reading after concreting. See attached strain gauge installation report for details. ROOT CAUSE: Strain gauges #03 and #04 damaged during concreting.
| 02SL - Stations (LUL) | Cxxx-NCR-000300 | NCR | P19 - Reinforcement Cage Issues- DSS (BTL-66) |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-09-07 | 2012-08-10 09:16 | -28 | 2012-07-17 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Bar mark 33 on cages C3 &C 4 (mid section, Panel 19) were not present on delivery. Root Cause: Human error - QA checks by __ and __ QA Engineer carried out at the __ fabrication yard did not recognize the lack of bars.
| 02SL - Stations (LUL) | Cxxx-NCR-000301 | NCR | P28 - Trim Bars out of Tolerance -CHS ( BTL-67) |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-08-31 | 2012-08-06 17:54 | -25 | 2012-07-19 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Following delivery, it was noted during the on-site QA check that the trim bars had been installed out of position and out of the allowable tolerances.Remedial Works to Trim-Bars InsufficientOn return to site following initial remedial works the reinforcement cage was rechecked by the site engineering team where it was found that although the trim bars had been extended, some were non-aligned and a number had not been welded to the previous trim bar. Trim-Bars out of Toleran__he cage was returned to __ fabrication yard where 50mm dia bar sections of varying length were welded abut to the existing trim-bars to ensure that the length required by the design was met - please refer to attached drawing Cxxx-BTL-SK168 - P28 - Trim-bar and Weld Positions - Design and As-Built.pdf.Remedial Works to Trim-Bars InsufficientThe decision was taken to weld a connection between the existing and remedial trim-bars onsite - Note: no welding of trim bar to main bars took place. All remedial works were carried out by an approved __ Technologies Ltd welder using 4mm low hydrogen electrodes working at temperatures between 150 & 160 degrees. Please refer to the attached pictures Trim-bar Remedial #1.jpg and Trim-bar Remedial #2.jpg and again to the attached drawing Cxxx-BTL-SK168 - P28 - Trim-bar and Weld Positions - Design and As-Built.pdf. Root Cause: Trim-Bars out of Tolerance __ fabricated the cage from an incorrect revision of the fabrication drawing - the later revision changes related to the positions of the trim-bars. Remedial Works to Trim-Bars InsufficientExpress not following remedial work instructions. __ quality engineer not identifying inadequate remedial works.
| 02SL - Stations (LUL) | Cxxx-NCR-000304 | NCR | Splicing of Waterbar in Steel Stop-ends: P1, P18, P19, P20-DSS-BTL(68) |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-08-31 | 2012-08-15 12:30 | -16 | 2012-07-19 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Two sections of waterbar rather than a single continuous length was used in the steel stop-ends of the following panels: • Panel 01 (P1 - P42 interface). Joint level 86.0mOD. • Panel 18 (P18 – P17 interface). Joint level 86.1mOD • Panel 19 (P19 – P18 interface). Joint level 86.0mOD • Panel 20 (P20 – P19 interface). Joint level 86.1mOD Root Cause: 33m length of waterbar unavailable.Waterbar splicing procedure not followed.
| 02SL - Stations (LUL) | Cxxx-NCR-000307 | NCR | P13: Overrun of 5 hour rule -CHS |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-07-30 | 2012-08-06 16:48 | 7 | 2012-07-16 | Structural Engineering - Diaphragm Walls | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The time needed for P13 on CHS is 7:28 h and thus exceeded the limit by 2:28 min. Root Cause As part of the installation of the reinforcement cage on panel 16, it was required to lower 4 no. ”sliding bars” down from the middle cage into the lower section (bar mark 207, 40mm x 8.7m). As 1 no. of these bars was being lowered, the rope slipped and the lap bar dropped into the panel as the welds on the restraining bar were not sufficient to hold the impact load.
| 02SL - Stations (LUL) | Cxxx-NCR-000308 | NCR | P16: Link damage, missing couplers and breach of 5hr rule -CHS- ( BTL-062) |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-08-31 | 2012-09-05 09:31 | 5 | 2012-07-16 | Structural Engineering - Diaphragm Walls | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | 1- The time needed for P16 on CHS was 6h10m and thus exceeded the limit by 1h10m. ROOT CAUSE:• 5 Hour Rule Breach - Time delays were caused by incidents which occurred during the tandem lift and lowering of the sliding bars during the installation of the reinforcement cage. 2-2 nos horizontal couplers are missing from the middle cage at 84.295 ATD, see attached sketch for details (Cxxx-BTL-SK168 - P16 - MISSING COUPLERS - REV A). ROOT CAUSE: 2 nos horizontal couplers were not installed during cage fabrication by the reinforcement supplier. The missing couplers were not picked up by the Quality Control at the fabricators yard. 3- One shear link is missing on P16 middle cage, see attached sketch for details (Cxxx-BTL-PH001 - P16 - DAMAGED LINK and Cxxx-BTL-SK169 - P16 - DAMAGED LINK - REV A). - ROOT CAUSE :The shear link was damaged during the tandem lift of P16 middle cage. An incident occurred which resulted in the bottom of the cage clashing with the tracks of the 200t crane (please refer to incident report for CHS dated 26/06/2012 for details). This contact damaged the lowest “loose” link on the cage. This is further illustrated by the attached photo (Cxxx-BTL-PH001 - P16 - Damaged Link.jpg) due to impact with left-hand track of 200t crane during tandem lift.
| 02SL - Stations (LUL) | Cxxx-NCR-000310 | NCR | P03: Overrun of 5 hour rule -CHS ( BTL- 63) |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-08-17 | 2012-08-06 17:10 | -11 | 2012-07-17 | Structural Engineering - Diaphragm Walls | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | The time needed for P03 on CHS is 9:52 h and thus exceeded the limit by 4:52 min. Root Cause: During the installation of the reinforcement cage a few couplers did not match correcty. The cage installation took longer than normal.
| 02SL - Stations (LUL) | Cxxx-NCR-000313 | NCR | Barrette P45 - Concrete strength @28 Days - DSS - BTL(86) |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-09-09 | 2012-08-17 10:16 | -23 | 2012-08-14 | Structural Engineering - Concrete Member | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | At Barrette 45 in DSS one of the two sets produced an uncharacteristically low average 28day strength of 44 N/mm² and a 56day strength of 48.8 N/mm². Root Cause: Mix details of the load were anaylsed and found to be within the allowable tolerances set by British Standards. The flow rate was also measured and found to be 590mm which is also within tolerance. The root cause can therefore be assumed to be error in the fabrication of the cubes such as air bubbles causing weakness and early shearing during testing.
| 02SL - Stations (LUL) | Cxxx-NCR-000314 | NCR | P8 - 5hr rule exceeded- CHS - __ ( 69) |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-07-31 | 2012-08-06 16:35 | 6 | 2012-07-23 | Structural Engineering - Diaphragm Walls | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | The panel key time for P08 was 5h 33m, thus exceedance of the limit by 33mins. Root Cause: Initial concrete supply was delayed due to a traffic accident - wagons were delayed travelling to the batching plant to load concrete for CHS.
| 02SL - Stations (LUL) | Cxxx-NCR-000315 | NCR | P8 - Couplers Position -CHS - (BTL-71) |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-08-31 | 2012-09-05 09:36 | 5 | 2012-07-23 | Structural Engineering - Reinforcement | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | During the installation of the reinforcement cage on Panel 08, the splice between the middle and bottom cages, the following coupler issue arose: • 1no. side coupler (ref EL50 P13Z5E43) was tightened using a torque wrench to the specified torque of 350nm but it was recorded that the bar didn't appear to be completely installed within the coupler. Please see sketch no. Cxxx-BTL-SK169 - P08 - COUPLER NON-CONFORMANCE which is attached for further illustrates the location of the coupling issue.
| 02SL - Stations (LUL) | Cxxx-NCR-000316 | NCR | P18 - 5hrs rule exceeded - CHS - (__ - 76) |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-09-20 | 2012-08-10 09:41 | -41 | 2012-08-01 | Structural Engineering - Diaphragm Walls | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The panel key time for P18 was 8hr14mins from the moment the exchange of bentonite finished, thus exceeding the limit by 3hr 14mins. The time taken from the installation of the first part of the reinforcement cage was 7hr09mins. Root Cause: During cage installation 4 no. couplers did not meet the specification and so remedial works were required. Please refer to PTR - 317- CHS P18 Reinforcement + Coupler Issues for the full details.
| 02SL - Stations (LUL) | Cxxx-NCR-000317 | NCR | P18- Reinforcement - Couplers Issues -CHS - __ ( 77) |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-09-26 | 2012-08-10 09:48 | -47 | 2012-08-01 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | During the installation of the reinforcement cage on Panel 18, the following coupler issues arose during the splice between the middle and bottom cages. ROOT CAUSE: Coupler Out of Tolerance - The root cause of the coupler non-conformance cannot be clearly identified. Grinder Cut in Rebar - A grinder used in the vicinity of the U-bar either prior or post fixing within the cage. It is not clear why a grinder would have been required - 4 no. far face couplers, ref: EL50-13 32R 35 E143 JMT, were tightened using a calibrated torque wrench to the specified torque of 300nm however - 2 no. showed no signs of extension and 2 no. overextended by 10mm. Please refer to the attached sketch no.Cxxx-BTL-SK172-P18-Coupler NCR 1.pdf which illustrates the location of these couplers. Grinder Cut in Rebar : During the checking of the reinforcement cage it was noticed that there was a cut in one of the reinforcement U-Bars. The reinforcement bar is 25mm in diameter and the cut was approximately 12.5mm in depth. Please refer to the attached sketches and pictures which illustrate the location and extent of the damage: Cxxx-BTL-SK170 - P18 - Gash in U-Bar #1.pdf, Cxxx-BTL-SK170 - P18 - Gash in U-Bar #2.pdf, P18 - Cut in Bar - Before Weld.jpg.
| 02SL - Stations (LUL) | Cxxx-NCR-000320 | NCR | CHS + DSS High Concrete Casting Level for Barrettes-(__ 70) |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-09-21 | 2012-08-17 14:45 | -35 | 2012-07-23 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Reject |  | Complete |  | Completed |  | The concrete level for the barrettes constructed at both CHS and DSS exceed the specified amount. Please see attached the tables below for a summary. Root Cause: Due to the increased risk of contamination from re-starting the concrete pour with P280 following removal and replacement of the tremmie string, a maximum pour level of CoL + 3m was used for the barrettes. However a lack of unstanding of the specification and this figure resulted in it not being adhered to.
| 02SL - Stations (LUL) | Cxxx-NCR-000321 | NCR | P15- Concrete Pour Timings exceeded -CHS - __ ( 75) |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-09-14 | 2012-08-10 09:58 | -35 | 2012-08-02 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | This limit was exceeded on whilst concreting P15 at CHS (15/06/2012) with load 22 overrunning by 11 minutes. Root Cause: Due to the night-shift / day-shift changeover at the __ batching plant, there was a delay in batching the final 'top-up' load. Site were unaware of this and so did not slow the pouring of the penultimate load.
| 02SL - Stations (LUL) | Cxxx-NCR-000327 | NCR | P22 - time betwen consecutive loads exceeded -DSS- ( BTL-73) |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-09-14 | 2012-08-10 10:09 | -35 | 2012-08-02 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | This limit was exceeded on whilst concreting P22 at DSS (08/06/2012) with load 34 overrunning by 35 minutes. Root Cause: Due to the shape of P22 (T panel), the concreting process requires 2 wagons pouring simultaneously to ensure an equal rise and level of concrete across the panel.Following the double wagon discharge at 04:30AM, 2 no. concrete wagons were rejected due to out of spec concrete. In addition 1 other wagon experienced a puncture and was delayed on-site for approx. 1 hr, further reducing the no. of wagons on turnaround for that period.Supervision did not ensure that the 2 no. rejected wagons were flow tested prior to completing previous pour (this would have allowed the pour to be slowed). With the delay realised, when 1 no. wagon arrived on-site (04:45AM) it was not poured in 0.5m^3 volumes in alternate tremmies to continue moving the concrete.
| 02SL - Stations (LUL) | Cxxx-NCR-000329 | NCR | P15: Overrun of 5 hour rule -DSS- ( BTL-74) |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-09-19 | 2012-08-10 10:19 | -40 | 2012-08-01 | Structural Engineering - Diaphragm Walls | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | The time needed for P15 on DSS is 6:15 h and thus exceeded the limit by 1hr 15mins. Root Cause: Bentonite exchanged was completed at 19:00 on 25/05/2012, however cage installation did not commence until 20:35.Due to the late finish of the exchange, the concreting operation would not have been completed prior to 10PM. __ were instructed to hold works until permission was given by __ to exceed the Section 61 - this delay caused the exceedence of the 5hr rule.
| 02SL - Stations (LUL) | Cxxx-NCR-000330 | NCR | P29 - 5 hr rule exceeded -CHS - ( __ 78) |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-09-21 | 2012-08-17 13:07 | -35 | 2012-08-07 | Structural Engineering - Diaphragm Walls | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The panel key time for P29 was 7hr02mins from the moment the exchange of bentonite finished, thus exceeding the limit by 2hr 02mins. Root Cause: Due to previous NCRs CHS P29 required an additional 3m depth and extension reinforcement cage. While lowering the bottom cage onto the trapped off extension, it became apparent that the fishplates would not align correctly and that there was a 220mm gap between the two fishplates on the left side of the cage. As a result, bolting of the fishplates was impossible and alternative solution was required to connect the cage sections.The extension cage had been previously fabricated and delivered. As it was not possible to connect the two section together during fabrication, __ used the as-built dimensions of the fishplates on the extension cage to place the fishplates within the bottom cage.
| 02SL - Stations (LUL) | Cxxx-NCR-000331 | NCR | P3/4/5/7/12/15/17/24/26/27/28/29.- Insufficient Sonic Tube Wall Thickness- __ (79) |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-09-21 | 2012-08-07 12:09 | -45 | 2012-08-02 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | All sonic tubes installed at both Whitechapel Cxxxsites (DSS and CHS) by __ have a wall thickness of 3.6mm. Root Cause: 5mm wall thickness for a nominal pipe size of 50mm dia is not available. Please refer to attached document Sonic Tube Datasheet.pdf. 01
| 02SL - Stations (LUL) | Cxxx-NCR-000332 | NCR | P31- Hanger's dimension on top cage- CHS - BTL( 83) |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-09-10 | 2012-08-13 09:50 | -28 | 2012-08-10 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Incorrect Hanging Bar Level: On delivery to site, the hanging bars on the top cage section for P31 were 200mm low which would have resulted in the cage sitting 200mm high within the panel. Replacement hanging bars were welded to the main bar projection on site. Root Cause: Misreading of the drawing - the top of steel level (ToS) of 111.9mAOD was used rather than the guidewall level of 112.1mAOD. Failure to identify issue during QA checking process at __ Fabrication facility.
| 02SL - Stations (LUL) | Cxxx-NCR-000333 | NCR | P31 - Reinforcement Issues + 5hr Overrun - CHS- BTL( 83) |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-09-21 | 2012-08-24 13:48 | -28 | 2012-08-10 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | - Lower cage section 950mm short: Approx. 950mm of the lower cage for CHS P31 was removed prior to installation and concreting. -Overun of the 5hr Rule: The panel key time for P31 was 6hr11mins from the moment the exchange of bentonite finished, thus exceeding the limit by 1hr 11mins. Root Cause: Lower cage section 950mm short: Following removal of the lower cage section from the panel, small localised damage to some linksets was identified - please refer to the attached picture CHS P31 Damage to Lower Cage Section.jpg. The panel was subsequently redipped and the toe level increased from 71.4mAOD (centrally and at the stop-end with panel 32 on the Near Face) to 72.5mAOD in between these two positions. Due to the demobilisation programme, the grab was not available to attempt to remove this material and so the reinforcement cage had to be reduced in overall length. -Overun of the 5hr Rule: The remedial works to enable placing the reinforcement cage at the correct level.
| 02SL - Stations (LUL) | Cxxx-NCR-000334 | NCR | Sonic Reservation Tubes Grouting |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-08-20 | 2012-08-06 14:54 | -14 | 2012-08-05 | Structural Engineering - Grouting | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | ‘’Cxxx Cement’’ has been accepted to be used for backfilling the sonic reservation tubes in MCR Cxxx-__-C-XDS-D061-50007 rev04, contractor observed on site using ‘’Rugby Sulphate Cement’’ instead of the accepted material
| 02SL - Stations (LUL) | Cxxx-NCR-000336 | NCR | P23 - Inclinometer Installation - DSS |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-09-07 | 2012-08-10 10:26 | -28 | 2012-08-07 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | The Inclinometer tube currently only extends 2m below the toe of the D-Wall, this is less than the specified 5m. Root Cause: Borehole support and soft ground ingress into borehole. Further drilling would have further distabilised the ground and redrilling would have caused delay.
| 02SL - Stations (LUL) | Cxxx-NCR-000337 | NCR | Installation of IE0001 - DSS |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-09-07 | 2012-08-09 10:16 | -29 | 2012-08-07 | Geotechnical Engineering - Geotechnical Engineering - General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Due to the lack of straightness of the reservation tube, in panel P1 –DSS the drill out operation was impaired and drilling rod snapped leaving the core barrel stuck at the base of the tube.
| 02SL - Stations (LUL) | Cxxx-NCR-000338 | NCR | P30-Couplers / 5hr rule -CHS-BTL(80) |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-09-21 | 2012-08-29 08:10 | -23 | 2012-08-07 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | 1) -Couplers : During the splicing of the middle and bottom cages of P30 reinforcement cage, the following coupler issues arose: 1no. near face coupler (ref EL50 P13 45 E118 JJV, 50mm-50mm) was tightened using a torque wrench to the specified torque of 350nm but it was overextended by 20mm. Please see attached picture P30 Coupler Overextension.jpg.1no. far face coupler (ref EL50P13 32R 35 E143 JMT, 32mm-50mm) was tightened using a torque wrench to the specified torque of 300nm however it showed no signs of extension.Please see the attached P30 coupler positions.pdf which illustrates the location of these couplers. 2) -Exceeding the 5 Hour Rule: The panel key time for P30 was 5h 15m, thus exceedance of the limit by 15mins ROOT CAUSE: 1) Couplers -> The root cause of the coupler non-conformance cannot be clearly identified. 2) Exceeding 5hr rule ->Remedial works on the cage at the splice location due to the out of tolerance couplers.
| 02SL - Stations (LUL) | Cxxx-NCR-000339 | NCR | P09 - Insufficient Concrete Cubes Taken -CHS-BTL(81) |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-09-21 | 2012-08-10 14:08 | -42 | 2012-08-07 | Structural Engineering - Concrete Member | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | 4 no. sets were taken during the concreting of P09 at CHS, with a total poured concrete volume of 251.5m^3. Root Cause Engineering supervision + __ Technician did not recognise that the final 'top-up' load of 4m^3 took the total poured volume above 250m^3 and so required an additional set of cubes.
| 02SL - Stations (LUL) | Cxxx-NCR-000340 | NCR | P31 - Insufficient Projection - CHS- __ (82) |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-09-21 | 2012-08-17 13:02 | -35 | 2012-08-07 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The projection on the reinforcement cage for P31 was 400mm short of design length. Root Cause: Reinforcement for both P9 and P31 was detailed on one reinforcement drawing (CRL dwg no: Cxxx-__-C-DWG-0061-50249). __ fabricated the top cage section to P9 ToS level..
| 02SL - Stations (LUL) | Cxxx-NCR-000342 | NCR | P11 - Flaws on the sonic Logging test results - __ ( 85)- DSS |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-09-17 | 2012-08-23 14:22 | -25 | 2012-08-10 | Structural Engineering - Structural Engineering - General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The sonic logging report for DSS P11 shows that there is a defect on 5 of the 6 no. traces at 7.5m. Root Cause: During the attempt to remove the stuck tube within the stop end of P12/P11, a trench box was placed which extended beyond P11 into P10. The toe level of the trench box was beneath the water table (approx 7.5m from top of sonic tube), and there was a flow of water during this operation into the trenchbox which may have caused movement within the gravels and overbreak around the S/E location.During the concreting of P11, the stop-end was supported by a 75mm gravel backfill due to the overexcavation of the trench box. Thisbackfill was placed to a depth of 6m when the concrete dip was at 9m. In light of the sonic results it is likely that some of this gravel backfil has migrated around the stop-end during placement, causing the defect shown in the results.
| 02SL - Stations (LUL) | Cxxx-NCR-000343 | NCR | P31 - Concreting Issues at CHS - BTL( 84) |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-10-26 | 2012-10-09 08:57 | -17 | 2012-08-09 | Structural Engineering - Concrete Member | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | - Concrete greater than 4hrs from batching to pour: 5 no. concrete loads poured exceeded the 4hr time limit from batching to placement. Please see the attached CHS P31 Concreting Record.pdf with the relevant loads highlighted. - Addition of Water to Concrete Load:: 30l of water was added to 1 no. wagon during the concrete pour on CHS P31.Wagon Details:Ticket no: 63354506, Batch Time: 18:16, Initial flow: 540mm, Flow after water addition: 580mm, Pour Time: 21:58 - 22:04. Root Cause: Concrete was confirmed prior to completing reinforcement installation on P31. This resulted in 11 no. wagons waiting on-site whilst the remedial works detailed within __ NCR 083 were carried out.Load #5 of the pour had already been rejected (flow of 520mm) when wagon #6 was flow tested (flow 540mm). The decision was taken by the Engineering Supervision to add 30l of water to the load and re-test the flow to see if it met the target of 560mm-690mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000344 | NCR | P08 - 66 hr exceeded - DSS - ( BTL- 90) |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-09-11 | 2012-09-13 11:37 | 2 | 2012-09-03 | Structural Engineering - Diaphragm Walls | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The 66 hour rule was exceeded during the construction of Panel 8 at Durward Street by 17:57. The 66 hour rule is an extension of the 42 hour rule, and measured between the time when the soil profile 3m below the top of London Clay is exposed to the time when the soil profile is covered again by the concrete. The 5hour rule was exceeded during the construction of Panel 8 at Durward Street by 01:51. The 5 hour rule is measured as the time between the end of bentonite exchange and the commencement of the concrete pour. Root Cause: Removal of two steel stop ends The bond between concrete and steel stop end at the interfaces between P08/P07 and P08/09 was very strong causing the stop end removal to take longer than usual (stop end between P08/P07 was 1200mm wide in a 1500mm trench causing additional overconcrete). Pump blocked The TOYO pump blocked and needed maintenance during bentonite exchange. Grab Break Down On day 1 the grab broke down and needed maintenance.
| 02SL - Stations (LUL) | Cxxx-NCR-000349 | NCR | Inspection and Testing |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-09-14 | 2012-08-23 12:45 | -22 | 2012-08-17 | Civil - Civil Engineering General | 500 |  | System Defect | Rework |  | Complete |  | Completed |  | During a routine joint surveillance of the instrumentation and monitoring at Durward Street Shaft site (held on 17th August 12) it was noted that a schedule of all inspection, measuring and test equipment used for the works and associated calibration certificates was not being maintained.
| 02SL - Stations (LUL) | Cxxx-NCR-000351 | NCR | P16 - 42 hr Rule exceeded -DSS- BTL( 87) |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-09-28 | 2012-09-18 12:36 | -10 | 2012-08-20 | Structural Engineering - Diaphragm Walls | 500 |  | Equipment Breakdown | Use As-Is |  | Complete |  | Completed |  | The time passing during construction for P16 on DSS was 63:00h. Root Cause: Several factors contributed towards the panel construction time being delayed and therefore meaning the panel was extended to 44.7m. During excavation on the 30/07/12 at 16:00 the grab broke down causing a 1:30 hour delay.P16 is a closer panel, this involves two steel stop ends to be removed during the panel open time.
| 02SL - Stations (LUL) | Cxxx-NCR-000352 | NCR | P11 - 42 Hr rule exceeded -DSS ( __ - 88) |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-09-27 | 2012-08-29 08:14 | -29 | 2012-08-20 | Structural Engineering - Diaphragm Walls | 500 |  | Equipment Breakdown | Use As-Is |  | Complete |  | Completed |  | The time passing during construction for P11 on DSS was 64:29h. Root Cause: During excavation on the 19/07/12 there was slow progress due to equiptment breakdown on the HS 875 (Daily Report DSS_120719). Root Cause:
| 02SL - Stations (LUL) | Cxxx-NCR-000357 | NCR | DSS P09: Additional steel in P09 cage - ( BTL- 91) |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-09-30 | 2012-09-13 11:44 | -17 | 2012-09-04 | Structural Engineering - Diaphragm Walls | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The bottom cage (cage 1) of panel P09 has been fabricated and installed with an additional layer of reinforcement to those required in design intent drawing Cxxx-HYD-C-DDDD061_ WS105_Z-22282 . This additional reinforcement consists of 12 number 7.9m NF4 B40 bars as shown on the attached document. Root Cause: Reinforcement supplier possessed a surplus cage for panel P11 which was used with __'s agreement for panel P09. The panels were of similar dimensions, with panel P11 having more reinforcement.
| 02SL - Stations (LUL) | Cxxx-NCR-000360 | NCR | DSS Break Out for Capping Beam |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-09-27 | 2012-10-05 09:20 | 8 | 2012-08-23 | Civil - Structural Engineering | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | During the D-wall break out for the capping beam construction it was observed that over break was taking place below the cut off level. The over break was observed to have taken place over a significant length of the D-wall. See attached sketch and photographs.
| 02SL - Stations (LUL) | Cxxx-NCR-000362 | NCR | Sonic Reservation Tubes Grouting |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-09-07 | 2012-09-07 13:10 | 0 | 2012-08-24 | Structural Engineering - Grouting | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | ‘’__ Cement’’ has been accepted to be used for backfilling the sonic reservation tubes in MCR Cxxx-__-C-XDS-D061-50007 rev04, contractor observed on site using ‘’__Cement’’ instead of the accepted material
| 02SL - Stations (LUL) | Cxxx-NCR-000370 | NCR | D- Wall bentonite and Grout localized inclusions |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-10-05 | 2012-10-01 13:05 | -4 | 2012-09-18 | Structural Engineering - Diaphragm Walls | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | During __ works currently being undertake to break down the D-Wall at DSS, it was discovered, several instances where the structural concrete of the D-Wall ( P15/P16) has experienced grout and Bentonite inclusions.
| 02SL - Stations (LUL) | Cxxx-NCR-000400 | NCR | Capping Beam - Pour 1 -Coupler & Concrete Cover Issues - DSS |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-09-30 | 2012-10-01 13:20 | 1 | 2012-09-18 | Structural Engineering - Concrete Member | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | 1) NCR - Internal slab position couplers -__ have made an error in setting out of two slab couplers Bar Mark 10, as shown in the attached sketches. It was caused due to poor work man ship. Please see sketch attached. 2) NCR - Capping beam extended approx. 25 mm on the outer face/back face to get the required 50mm cover. The length of Bar mark 10 couplers was longer than shown on bending schedule. This resulted us to push the couplers backwards to get our front shutters right, which resulted in reduced cover on the outer face/back face of capping beam to 25 to 30mm instead of 50mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000406 | NCR | CxxxSurveillance exit note - Capping Beam |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-10-05 | 2012-10-05 09:32 | 0 | 2012-09-18 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | From review of the information provided in the surveillance exit notes the following items are to be addressed: Under item 4. The agreed method to achieve the unformed finish was not included in the method statement and when this was further challenged on site, a detailed answer could not be provided. Under item 6. Traceability of the steel reinforcement to be confirmed prior to the pour taking place, any traceability issues would be difficult to rectify post concrete placement.
| 02SL - Stations (LUL) | Cxxx-NCR-000409 | NCR | Capping Beam - Spacer bars Pour 2b Pour 2a - DSS |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-10-17 | 2012-10-05 09:37 | -12 | 2012-09-25 | Structural Engineering - Reinforcement | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | The steel fixers were not be able to install the spacer bars (BM44) to approx. 4 starter bars as there wasn't enough space ( Please see picture and Sketch attached). This means that BM 278 will sit close BM 222. Root Cause: The starter bars were not in one straight line i-e some of them have less cover than the rest. The following spacer bars will continue to be installed after the four starter bars as per design.
| 02SL - Stations (LUL) | Cxxx-NCR-000427 | NCR | Adjustment made to the steel - Couplers cut off in pour 3a - DSS |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-10-22 | 2012-10-15 12:08 | -7 | 2012-10-01 | Structural Engineering - Reinforcement | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | The couplers for pour 3a, have had there hoops cut off . Please see sketch attached for more details. Root Cause: the couplers had there hoops cut off so far in order for them to fit in pour 3a. This was a design issue.
| 02SL - Stations (LUL) | Cxxx-NCR-000428 | NCR | Repairs to surface of capping beam - DSS |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-10-31 | 2012-10-15 14:20 | -16 | 2012-10-02 | Structural Engineering - Finishes | 500 |  | Material | Repair |  | Complete |  | Completed |  | 1- Areas of honey comb. 2-Areas of suspected cold joint. 3-Discoloration to the concrete finish, monitor areas. 4- Areas where blow holes are visible. 5-Areas where protective foam to couplers has moved and caused a surface blemish outside of joint face with floor slab or drop beams. 6- Areas where protective foam to couplers has moved and caused a surface blemish on joint face to floor slab and drop beams.
| 02SL - Stations (LUL) | Cxxx-NCR-000429 | NCR | Damaged Hydrophilic Water Bar Pour 2b/3a/3b-DSS |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-10-31 | 2012-10-15 14:17 | -16 | 2012-10-02 | Civil - Civil Engineering General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | Damaged Hydrophilic Water Bar Pour 2b/3a/3b. Due to rain, the mastic below the water bar has swelled. The water bar is no longer in contact with the mastic.
| 02SL - Stations (LUL) | Cxxx-NCR-000430 | NCR | Incorrect Bars scheduled by __- Pour 2b |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-10-31 | 2012-11-05 08:47 | 5 | 2012-10-02 | Structural Engineering - Reinforcement | 500 |  | Design | Repair |  | Complete |  | Completed |  | C dimension for BM 229 is 960mm longer than BM 226, which makes it impossible to fit BM229 in the pour.
| 02SL - Stations (LUL) | Cxxx-NCR-000434 | NCR | Capping Beam Construction Pour 5a Cambridge Heath Shaft - Cxxx |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-11-01 | 2012-11-05 13:03 | 4 | 2012-10-04 | Civil - Civil Engineering General | 500 |  | Design | Rework |  | Complete |  | Completed |  | Cxxx contractor has installed bar mark 545 as a ‘straight bar’ as apposed to a ‘cranked bar’ which as per the design for the capping beam Pour 5a has the shape code 99 on both the reinforcement detail drawing and reinforcement schedule. Cxxx contractor have advised CRL that the design change to the reinforcement bar has been agreed with the contractor's detailer/designer (__) at a site/local level. CRL have not been formally notified of the change and are raising a NCR as Cxxx contractor propose to carryout remedial changes to the incorrect reinforcement type at a local / site level without formal notification to CRL.
| 02SL - Stations (LUL) | Cxxx-NCR-000435 | NCR | Excessive cover to capping beam reinforcing bars, Pour 5a at CHS |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-11-30 | 2012-11-19 09:19 | -11 | 2012-10-05 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Cover on the east facing vertical face of pour 5a of the Cambridge Heath capping beam is in excess of 80mm. __ have advised that the cover at the south west of pour 5a is in excess of 80mm. This is as per design as the construction joint runs through the node point between the concrete faces (or fa__s). The reason for the large amount of cover is that the reinforcement is curved however the concrete faces are fa__ed. Hence, in the middle of the fa__, the cover to the rebar will be 50mm. However, at the fa__ node points, the cover will be more than 80mm as the rebar curves away from the concrete face. This is clearly seen on Pour 5a plan on reinforcement drawing Cxxx-C08.090-DWG-RAM-0333. We presume that the problem of excessive cover and cracking on the internal faces of the capping beam over the shaft has been anticipated by providing mesh on the faces. However, no mesh is shown as required on the outside face of the capping beam on the approved reinforcement drawings. It is anticipated that cover will vary to similar amounts on the outside of the CHS capping beam for all the pours at CHS.
| 02SL - Stations (LUL) | Cxxx-NCR-000436 | NCR | Pour 2b- Slab Couplers / Soffit Couplers |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-11-05 | 2012-10-17 10:25 | -19 | 2012-10-05 | Structural Engineering - Reinforcement | 500 |  | Design | Repair |  | Complete |  | Completed |  | 1.Bobs cut on slab couplers.(Sketch attached) 2.Levels and spacing not right on the internal slab couplers (Sketch Attached) 3.Increased spacing between the couplers. (Sketch attached) 4.B dimension for soffit couplers BM 850-855 and 857-861 were cut (RAM-0319 Rev P03). Apparent Cause: 1.Due to congestion of steel the couplers could not be fitted in with the bobs( Refer to attached sketch) 2.Due to congestion of steel and bars in the way design levels and spacing could not be achieved. (Refer to attached picture and sketch) 3.The right number of bars could not be achieved in the specified spacing. (Refer to attached sketch) 4.Due to congestion of steel the U bars could not fit in as U bars.
| 02SL - Stations (LUL) | Cxxx-NCR-000437 | NCR | Pour 3a capping beam -Bar Marks 10 / couplers tolerances-DSS |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-11-05 | 2012-10-17 10:29 | -19 | 2012-10-05 | Structural Engineering - Reinforcement | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | 1 -All bar mark 10’s in pour 3a had to have their bobs removed, this was because of the resection of room on the far face of the panel not allowing the bars to be slide from the back as they normally would. To allow the bars to be slide in from the near face the bobs had to be removed because the amount of steel would not allow the past though otherwise. 2) Heights of couplers (BM10 and BM13), the accepted tolerance in levels of couplers in pour 3a is +/-10mm, the as build attached to this NCR show some couplers that fall out of this allowable range, this mainly occurred around the corner where the panel changes directions. Couplers that are out of tolerance are due to the amount of steel that is in the cage, which won’t allow for correct placement. Please see sketch attached
| 02SL - Stations (LUL) | Cxxx-NCR-000439 | NCR | Capping Beam - Pour 3a Bar Marks 6 - DSS |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-10-31 | 2012-11-05 09:14 | 5 | 2012-10-08 | Structural Engineering - Reinforcement | 500 |  | Design | Repair |  | Complete |  | Completed |  | Bar mark 6 in pour 3a is a u bar that is slid in from the side of the cage. Due to reinforcement congestion issues with the design the bar mark had to be cut.
| 02SL - Stations (LUL) | Cxxx-NCR-000440 | NCR | Capping Beam - Pour 4a B50 starter bars in Panel 5 - DSS |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-10-31 | 2012-11-05 09:24 | 5 | 2012-10-08 | Structural Engineering - Reinforcement | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | As seen in the attached drawing and photo a B50 starter bar in panel 5 had to be cut down by 150mm as it clashed with bar mark 190. If the bar was not reduced down it meant that bar mark 190 would have not been able to screw into the it coupler.
| 02SL - Stations (LUL) | Cxxx-NCR-000447 | NCR | Panel 04 - 32mm diameter starter bar -CHS |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-11-10 | 2012-11-05 12:54 | -5 | 2012-10-10 | Structural Engineering - Reinforcement | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | 1no 32mm diameter starter bar in panel 4 at CHS has broken off at the cut off level of the D-Wall.
| 02SL - Stations (LUL) | Cxxx-NCR-000448 | NCR | Pour 3b, Capping Beam |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-11-15 | 2012-11-12 09:52 | -3 | 2012-10-10 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | Waterproofing has been installed for the soffit of the capping beam as it extends beyond the diaphragm wall. Since installation, there has been heavy rain that has leaked under the waterproof membrane. Rebar has since been installed ontop of the membrane. Project Manager has requested several times (but not yet received) quality assurance documentation that the Contractor/Subcontractor has completed that verifies, for example, that the waterproofing has been installed as per the manufacturers' details
| 02SL - Stations (LUL) | Cxxx-NCR-000451 | NCR | Broken Rebar |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-10-15 | 2012-11-05 12:59 | 21 | 2012-10-11 | Structural Engineering - Structural Engineering - General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | 1no 32mm diameter starter bar in panel 4 at CHS has broken off at the cut off level of the D-Wall and 1 no 32mm diameter starter bar in panel 13 (in capping beam pour 2b) at CHS has been broken at 200mm above cut-off.
| 02SL - Stations (LUL) | Cxxx-NCR-000452 | NCR | Pour 4a capping beam -BM113.1 and BM113.2 -DSS |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-11-18 | 2012-11-19 09:21 | 1 | 2012-10-12 | Structural Engineering - Reinforcement | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | BM113.1 and BM113.2 in the bottom mat of the capping beam pour 4a had 300mm approx removed from their bobs, this was done so that the bars could be slid though the cages there was no other way to install them. Please see attached photo . This was due to poor design these obstacles where already known.
| 02SL - Stations (LUL) | Cxxx-NCR-000460 | NCR | Capping Beam - Pour 4a BM998 - DSS |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-11-16 | 2012-11-19 09:23 | 3 | 2012-10-17 | Structural Engineering - Reinforcement | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | 13 number Bar mark 998 had to have their bobs removed in order to slid them through the top mat of steel. See attached blown up drawing for the location of these bars. ( blown up drawing is taken from drawing Cxxx-__-C-DWG-D061-50276
| 02SL - Stations (LUL) | Cxxx-NCR-000467 | NCR | CHS Strain Gauges Damaged Cables |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-11-30 | 2012-12-05 09:41 | 5 | 2012-10-23 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | Damadged cables of P24 strain guage.
| 02SL - Stations (LUL) | Cxxx-NCR-000471 | NCR | CHS 4b - Finish not to specification on top face outside of kicker |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-11-22 | 2012-11-19 09:28 | -3 | 2012-10-29 | Civil - Structural Engineering | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Concrete was poorly compacted in 2 areas of Pour 4b at CHS causing a poor finish at the top and side of the capping beam. Poor finish occurs in 2no locations: over Panel 8 and Panel 5.
| 02SL - Stations (LUL) | Cxxx-NCR-000479 | NCR | BM304/305/383 - Bars incorrectly bent Pour 3b |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-11-23 | 2012-11-06 16:09 | -17 | 2012-10-31 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | A number of steel reinforcement bars for DSS Pour 3b, (bending schedule RAM-0320-P03) have been bent incorrectly and delivered to site. However due to the size and critical position of these bars, they cannot be used on site. BM304; 1No B40 bar with threaded end with coupler fitted BM305; 7No B40 bars with threaded end with coupler fitted BM383; 7No B50 bars with threaded end with coupler fitted. Root Cause: Bars been incorrectly bent by __ Reinforcement
| 02SL - Stations (LUL) | Cxxx-NCR-000481 | NCR | 5no. Bar mark 405 in pour 3b |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-11-23 | 2012-11-21 17:24 | -2 | 2012-10-31 | Structural Engineering - Reinforcement | 500 |  | Design | Rework |  | Complete |  | Completed |  | 5no. Bar mark 405 in pour 3b is a straight bar with coupler at one end and bob on the other end, positioned in the inside face of the capping beam. The bars bobs had to be removed in order for them to be placed as the bars where too long. Sufficient anchorage was left on the bar which was this was checked with __ from crossrail. Please see picture attached on the second page of the document. Root Cause: • Poor design these obstacle where already know.
| 02SL - Stations (LUL) | Cxxx-NCR-000482 | NCR | 2no. Bar mark 408 / 2no. Bar mark 990 - Pour 3b |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-11-23 | 2012-11-21 17:26 | -2 | 2012-10-31 | Structural Engineering - Reinforcement | 500 |  | Design | Rework |  | Complete |  | Completed |  | - 2no. Bar mark 408 in pour 3b is a straight bar with coupler at one end and bob on the other end, positioned in the face of the up-stand. Half the bars bobs had to be removed in order for them to placed as the cage had already been closed up. Sufficient anchorage was left on the bar which was checked with __ from __. - 2no. Bar mark 990 in pour 3b is a u bar with coupler for the starter bars are running up the face of the up-stand. The bar had to be cut in half in order for them to placed as the cage had already been closed up. Sufficient anchorage was left on the bar which was checked with __ from crossrail.
| 02SL - Stations (LUL) | Cxxx-NCR-000483 | NCR | Links Set pour 3b |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-11-30 | 2012-11-22 12:20 | -8 | 2012-10-31 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Links in the lower level of the capping beam in pour 3b where started in the wrong place which meant that 4 where out of position. This meant 4 no. Links sets did not have bm 369 to close the link set, refer to picture attached on document page 2. As there wasn't a correct number of links sets in the specified area of the capping beam __ (__) ran some calculation to verify that it would be strong enough. root cause: __ Not following the design details.
| 02SL - Stations (LUL) | Cxxx-NCR-000484 | NCR | Up - stand link sets - pour 3B |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-11-30 | 2012-11-22 12:31 | -8 | 2012-10-31 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The steel fixers fixed 2 extra link sets in the up-stand of pour 3b, see section D-D on drawing Cxxx-__-C-DWG-D061-50281 attached on the second page
| 02SL - Stations (LUL) | Cxxx-NCR-000485 | NCR | Surface Finish at pour 1 |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-11-30 | 2012-11-27 13:39 | -3 | 2012-10-31 | Structural Engineering - Finishes | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | Surface Finish Checks at pour 1 revealed low spots, refer to picture attached Root Cause: • Poor design these issues where already known.
| 02SL - Stations (LUL) | Cxxx-NCR-000489 | NCR | Concrete finishing of pour 5a - CHS |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-12-06 | 2012-11-27 13:43 | -9 | 2012-11-16 | Structural Engineering - Finishes | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The upper pour of 5a at the west side does not follow the same vertical alignment as the lower pour. The upper pour projects 30mm out compared to the lower pour, for a length of approximately 1m, starting from the curved part. The reason behind the projection is that the shutter was moved out to maintain suitable cover to the upper level reinforcement for the higher level pour. Please see photo and sketch attached.
| 02SL - Stations (LUL) | Cxxx-NCR-000494 | NCR | BM 465 bars -pour 4b - DSS |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-11-30 | 2012-11-22 12:17 | -8 | 2012-11-08 | Structural Engineering - Reinforcement | 500 |  | Design | Rework |  | Complete |  | Completed |  | 5 No. BM 465 bars located in the corner of 4b against the back blinding had to be cut in half to allow BM2450 to be slide in to the cage. Because of the BM 465 been located next to the back blinding it could not be spliced, __ from crossraill agreed that the bars could be cut and left as bobs without a splice. Root Cause: • Poor design these obstacle where already know.
| 02SL - Stations (LUL) | Cxxx-NCR-000498 | NCR | Industrial Waste in the Backfilling Material |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-11-24 | 2012-11-23 13:26 | -1 | 2012-11-10 | Civil - Fill | 500 |  | Material | Rework |  | Complete |  | Completed |  | Waste industrial material represented by Tensar Triax geo-grid fragments present in substantial quantities in the material used to backfill the area behind the DSS capping beam , specifically at the backside of pours 2b,1,2a,3a & 4a Photos attached to support this NCR
| 02SL - Stations (LUL) | Cxxx-NCR-000499 | NCR | Incorrect scheduling to pour 2b reinforcement bars |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-11-30 | 2012-11-30 12:07 | 0 | 2012-11-11 | Structural Engineering - Reinforcement | 500 |  | Design | Repair |  | Complete |  | Completed |  | No overlap between the top and bottom of both sides legs of BM 175 – 187 and BM 188-199, due to the incorrect scheduling to these rebars. Pour 2b reinforcement schedule shows the B&D lengths of BM 175-187 equal to 1125mm and the lengths of A&C BM 188-199 equal to 1000mm , the correct length for each side of these legs should be 1975mm. Please see attached drawing circled in red showing the required design arrangement and the actual reinforcement delivered to the site.
| 02SL - Stations (LUL) | Cxxx-NCR-000501 | NCR | Capping Beam -BM 456 - Pour 4b - DSS |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-12-06 | 2012-11-23 13:12 | -13 | 2012-11-13 | Structural Engineering - Reinforcement | 500 |  | Design | Rework |  | Complete |  | Completed |  | 18 No. BM 456 had to be cut in half, as they were unable to be slide in from the back due to back blinding been in the way. __ (__ Designer) advised that the bars cut in half did not need a splice on them where long enough. Please see attached bar sketch . Root Cause : Poor design these obstacle where already known
| 02SL - Stations (LUL) | Cxxx-NCR-000510 | NCR | Pour 4b -BM398 -DSS |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-12-09 | 2012-11-30 12:09 | -9 | 2012-11-19 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Due to BM398 From pour 3b sticking out too far from in pour 4b an step in the shutter for the capping beam had to be made. It was advised by __ that the step had to be a minimum of 300mm down from the top of the capping beam and the other dimensions to suit. Please see attached photo and drawing. Root Cause: Bar been set in the wrong position in pour 3b.
| 02SL - Stations (LUL) | Cxxx-NCR-000511 | NCR | CxxxLighting Boom Support ITP - PMI 077 |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-11-30 | 2012-11-22 12:11 | -8 | 2012-11-19 | Utilities Engineering - Electricity | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The offsite fabrication of the welded and galvanised steel supports for the lighting is now complete. Altough __ has submitted the first Revision for this ITP on the 22 nd of October, prior to the support steelwork installation start on site, the steel Fabrication works took place without an approved ITP. Root Cause: Because these TW were part of a PMI -077 the new ITP requirement wasn't identifyed by the approved document control for ITP's which is the ITP - Schedule.
| 02SL - Stations (LUL) | Cxxx-NCR-000519 | NCR | Damage to IE00056 at CHS |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-12-06 | 2012-12-10 13:09 | 4 | 2012-11-22 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | The inclinometer instrument numbered IE00056 at Cambridge Heath Site has not been functioning or transmitting data since 26th October 2012.
| 02SL - Stations (LUL) | Cxxx-NCR-000521 | NCR | Disturbance of In Ground Rod extensometer XR00002 |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-12-19 | 2012-12-20 09:15 | 1 | 2012-11-30 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Planning | Repair |  | Complete |  | Completed |  | Through readings and investigation, it has become apparent that XR2 has been damaged by adjacent works. This has caused the head of the instrument to tilt over, such that its readings have been affected. Root Cause: Lack of working space in the area. Adjacent work installing IPI cable protection ducting to 750mm below capping beam between Panel 12 and Panel 5. This involved a 5 ton 360 excavator, and a hand operated whacker plate.
| 02SL - Stations (LUL) | Cxxx-NCR-000522 | NCR | Installation of IPI in Panel 18 at CHS |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-12-20 | 2012-12-10 13:21 | -10 | 2012-12-03 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | It is understood that the bottom section of approximately 27m of IPI reference IE00053 in panel 18 has become stuck during installation and all attempts to retrieve the inclinometer rods to date have failed.
| 02SL - Stations (LUL) | Cxxx-NCR-000523 | NCR | Use of unapproved flexible conduit and deviation from approved MS |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-12-19 | 2012-12-10 13:50 | -9 | 2012-12-03 | Communications and Control Systems - Public Address Systems | 500 |  | Material | Rework |  | Complete |  | Completed |  | Contractor has deviated from approved WMS and installed __ which is not approved to LU 1-085 for Fire Safety Performance of materials.
| 02SL - Stations (LUL) | Cxxx-NCR-000525 | NCR | Pour 4b capping beam - Waterproofing |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-12-21 | 2012-12-17 09:02 | -4 | 2012-12-04 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The pre proof was damaged by the placement of shutter when building pour 4b there fore it was unable to be stuck to the wall with LM. The solution was to paint to wall with LM and run it across the top of the pre proof in a 200mm strip therefore creating a seal. This was suggested by Subcontractor, __ and __ (Crossrail designer) approved that it could be done.
| 02SL - Stations (LUL) | Cxxx-NCR-000526 | NCR | Pour 5a ( Upper level - Capping Beam-CHS) - Concrete minimum strength not achieved. |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-01-18 | 2013-01-07 08:33 | -11 | 2012-12-07 | Structural Engineering - Concrete Member | 500 |  | Damaged | Use As-Is |  | Complete |  | Completed |  | The concrete strength at 28 days for pour 5a ( upper level) was 37.4 N/mm2 ( please see summary report attached). Root Cause: Unknown . Please note that this was an one off ocurrance, all other cube results have achieved strengths above the minumum requirements.
| 02SL - Stations (LUL) | Cxxx-NCR-000527 | NCR | Protection for the DSS Instrumentation |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-01-11 | 2013-01-10 11:16 | -1 | 2012-12-15 | Surveying - Instrumentation and Monitoring | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Cables of the in-wall inclinometers laid on the ground without suitable protection, as shown on the attached photos. Protection required approximately form the area adjacent to IM0006 at the north side of the shaft up to the Data logger installed on the Swanlea school brick fence .
| 02SL - Stations (LUL) | Cxxx-NCR-000528 | NCR | Pour 3b - Chamfer on the upper outside edge of concrete- CHS |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-01-25 | 2013-01-10 11:48 | -15 | 2012-12-19 | Structural Engineering - Formwork | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | The concrete for 3b capping beam was poured without a 25 x 25mm chamfer on this outside edge. This was due to the __ installed on the inside of the shutters, which __ did not want to pierce while affixing the chamfer former. Instead, the subcontractor attempted to form the chamfer with a hand tool, however this did not produce as successful a result as if a chamfer former had been used.
| 02SL - Stations (LUL) | Cxxx-NCR-000529 | NCR | Pour 2a & 3a - Chamfer on the Upper outside edge of concrete |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-01-28 | 2013-01-10 11:57 | -18 | 2012-12-20 | Structural Engineering - Formwork | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The concrete for 2a and 3a capping beam was poured without a 25 x 25mm chamfer former on this outside edge. This was due to the __ installed on the inside of the shutters, which __ did not want to pierce while affixing the chamfer former. The subcontractor attempted to form the chamfer with a hand tool. This was partly successful, however this did not produce the same result as if a chamfer former had been used.
| 02SL - Stations (LUL) | Cxxx-NCR-000530 | NCR | CHS - Installation of IE00053 |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-01-15 | 2013-01-02 10:19 | -13 | 2012-12-20 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Damaged | Use As-Is |  | Complete |  | Completed |  | The Equipment has broken down during Installation and it couldn't been Installed at the rght designed depth .
| 02SL - Stations (LUL) | Cxxx-NCR-000531 | NCR | Protection for the DSS-In Wall Inclinometer Cables |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-01-21 | 2013-01-18 16:37 | -3 | 2013-01-07 | Surveying - Instrumentation and Monitoring | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Further to WHI-CRL NCR-Cxxx-00527 issued on 15-Dec-2012 The cables of the in-wall inclinometers laid on the ground and hanged on the scaffolding bars without suitable protection,as shown on the attached photos. Protection required for the cables between IE00004 and IM00003.
| 02SL - Stations (LUL) | Cxxx-NCR-000532 | NCR | Monitoring Prism regime for the Capping Beam |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-01-29 | 2013-01-09 13:28 | -20 | 2013-01-08 | Surveying - Instrumentation and Monitoring | 500 |  | Planning | Rework |  | Complete |  | Completed |  | It hasn't been possible to comply with the required ( Normally twice weekly) number of readings to be undertaken for the Capping Beam monitoring prisms over Christmas break.( 26/12/12). This was due to the keys for the tripod leg lockup being removed from the key press and not returned prior to Christmas shutdown.
| 02SL - Stations (LUL) | Cxxx-NCR-000533 | NCR | Incorporation or Monitoring Data into the UCIMS |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-01-31 | 2013-02-03 15:24 | 3 | 2013-01-08 | Surveying - Instrumentation and Monitoring | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | The data collected by the Contractor for the instrumentation and monitoring equipment at Durward Street Shaft site have not been incorporated into the UCIMS with the minimum of delay and in any event within 12 hours of the time of reading. The Project Manager lists below the Instruments and their corresponding dates of the latest data available on UCIMS: •Cxxx-XR000001 Up to 2012-12-17 is the latest data available on UCIMS •Cxxx-XR000003 Up to 2012-12-17 is the latest data available on UCIMS •Cxxx-IM000006 Up to 21/11/2012 is the latest data available on UCIMS •Cxxx-XR000002 Up to 2012-12-17 is the latest data available on UCIMS •Cxxx-IM000007 Up to 2012-12-17 is the latest data available on UCIMS •Cxxx-IM000008 Up to 2012-12-19 is the latest data available on UCIMS •Cxxx-IM000011 Up to 2012-12-19 is the latest data available on UCIMS •Cxxx-LP000005 Up to 2012-10-15 is the latest data available on UCIMS •Cxxx-LP000001 Up to 2012-12-20 is the latest data available on UCIMS •Cxxx-LP000002 Up to 2012-09-28 is the latest data available on UCIMS •Cxxx-LP000003 Up to 2012-12-20 is the latest data available on UCIMS •Cxxx-LP000004 Up to 2012-12-20 is the latest data available on UCIMS •Cxxx-LP000005 Up to 2012-10-15 is the latest data available on UCIMS •Cxxx-LP000009 Up to 2012-11-27 is the latest data available on UCIMS •Cxxx-LP000010 Up to 2012-12-17 is the latest data available on UCIMS •Cxxx-LP000011 Up to 2012-12-17 is the latest data available on UCIMS
| 02SL - Stations (LUL) | Cxxx-NCR-000534 | NCR | Concrete Testing for Sprayed Concrete In-Fill Wall B Temporary Works |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-01-31 | 2013-01-18 16:50 | -13 | 2013-01-08 | Civil - Geotechnical Engineering | 500 |  | System Defect | Rework |  | Complete |  | Completed |  | Following on-site inspections by Crossrail Field Engineers to undertake witness points for the construction of the in-fill panel 1 and panel 2 to wall B, Crossrail can confirm that no testing of the sprayed concrete has been undertaken or have any testing results been presented to Crossrail for review by Cxxx.
| 02SL - Stations (LUL) | Cxxx-NCR-000535 | NCR | Concrete Core Compressive Strength-Non Compliant Results- In-Fill Wall B |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-02-11 | 2013-02-03 15:40 | -8 | 2013-01-11 | Structural Engineering - Concrete Member | 500 |  | Material | Rework |  | Complete |  | Completed |  | Concrete strength for Panel 1/2 on Wall B didn't reach the compliant strengh ( 11.8 N/mm2) . Please see core results attached.
| 02SL - Stations (LUL) | Cxxx-NCR-000539 | NCR | D-Wall Protrusions - General Concrete Overbreak at DSS - ( __ 000093) |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-06-28 | 2013-04-17 09:18 | -72 | 2013-01-21 | Structural Engineering - Diaphragm Walls | 500 |  | Material | Repair |  | Complete |  | Completed |  | " Minor protrusions on inside face of DSS and CHS diaphragm walls exposed during bulk excavation. Grab removing obstructions which extended from the panel into the soil behind the inside face of the diaphragm wall. As obstructions cannot be cut through by the grab, they are pulled into the excavation which creates a local void in the excavation face. Typical obstructions are claystones, boulders,... Similar voids might also occur in poorly compacted ground, such as Made Ground".
| 02SL - Stations (LUL) | Cxxx-NCR-000540 | NCR | P11 - Concrete Overbreak - DSS( __ -NCR- 000094) |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-02-22 | 2013-02-04 16:09 | -18 | 2013-01-21 | Structural Engineering - Diaphragm Walls | 500 |  | Material | Rework |  | Complete |  | Completed |  | " A protrusion has been exposed on the diaphragm wall inside face of P11 at DSS. Approximate dimensions: - Level: Between 109.5 mATD and 108.5 mATD - Protruding: up to 500mm - Width: approx. 1500mm "Root Cause: Localised soild collapsed .
| 02SL - Stations (LUL) | Cxxx-NCR-000553 | NCR | Wall ‘A’ Infill panel 1/2 - Starter Bars |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-03-08 | 2013-02-20 16:44 | -16 | 2013-02-14 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | 3 No. Starter bars in panel 1 not driven into the ground to a sufficient length (500mm) due to old grout present in the ground, this resulted in an area of mesh in panel 2 not been able to be tied onto these 3 starter bars from panel 1. Please see attached NCR report with photo
| 02SL - Stations (LUL) | Cxxx-NCR-000558 | NCR | IM000008 -probe jammed |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-06-28 | 2013-06-27 12:59 | -1 | 2013-03-04 | Geotechnical Engineering - Geotechnical Engineering - General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | Inclinometer probe has become stuck in IM8 at Durward Street Site shaft. At the present moment we are unable to survey this tube until we recover the probe and survey for obstructions.
| 02SL - Stations (LUL) | Cxxx-NCR-000560 | NCR | Pour 4b - Damaged Waterproofing - DSS |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-07-01 | 2013-04-08 11:36 | -84 | 2013-03-18 | Civil - Civil Engineering General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | The water proofing material on the back side of capping beam has been damaged. Pictures attached. Root cause: this damage was caused due to the interface with construction / demolition works for the sprayed concrete infill panels wall B.
| 02SL - Stations (LUL) | Cxxx-NCR-000561 | NCR | Breach of 42 hour rule on P36 - DSS ( __ 000095) |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-03-26 | 2013-03-25 13:15 | -1 | 2013-03-19 | Structural Engineering - Diaphragm Walls | 500 |  | Equipment Breakdown | Use As-Is |  | Complete |  | Completed |  | The time passing during construction for P36 on DSS was 43:58h. 5h Rule relating to the panel key time was not breached. Root Cause: + The day after completion of excavation of Panel 36 the LR1600 service crane had a malfunction with its monitor rendering it out of action until fixed thus adding several hours of delay to the start of works. + During concreting of the panel the both bentonite removal pumps broke down causing delay to the concreting process.
| 02SL - Stations (LUL) | Cxxx-NCR-000563 | NCR | P38 -inadequate flushing of concrete during D-wall Lower Level construction. |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-06-28 | 2013-06-27 15:24 | -1 | 2013-04-08 | Structural Engineering - Diaphragm Walls | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | During phase 1 reduction of P38 D-wall concrete level to facilitate capping beam construction on Saturday 6th April 2013 it was noticed that the top 900mm of concrete contained some sand and water and was of lower quality than expected. This may have been a result of inadequate flushing of the panel. Please see photos attached.
| 02SL - Stations (LUL) | Cxxx-NCR-000564 | NCR | Lower Level D-Wall - P28 -5h, 42h & Sonic Reservation Tube -(__ 96) |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-05-22 | 2013-04-25 10:21 | -27 | 2013-04-10 | Structural Engineering - Diaphragm Walls | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | 1. The 5 hour rule was exceeded during the construction of panel 28 at Durward Street by 2h 28mins. The 5 hour rule starts from the insertion of the first section of reinforcement into the bentonite to the commencement of the concrete pour. 2. The 42 hour rule was exceeded during the construction of panel 28 at Durward Street by 9h 40mins. Crossrail D-wall Specification (Cxxx-HYD-Z-RSP-D061-00016 Rev6.0) specifies that the process from starting to excavate the portion of the panel within the strata providing primary vertical friction (defined as from a point 3m below the top of the London Clay to the toe of the wall) to completing concreting back up to a point 3m below the top of the London Clay shall not exceed 42h. 3. During the installation of the reinforcement 1 no. reservation tube was not fastened together. ROOT CAUSE: "The root causes of the NCR's stated above are as follows: 1. Sonic tubes were wire tied at one end and had to be cut during installation, this wasn't picked up during the site inspection of the reinforcement. 2. During the installation of the cage 1 no. sonic tube coupling did not fit together. 3. The concrete line to the panel blocked as the guillotine section wasn't cleaned properly after the previous concreting. 4. 2no. Complete links were missing from the bottom cage on delivery to site. These links had to be constructed and wire tired into place to the bottom cage during installation. 5. Cage delays moved concrete pour from nightshift to dayshift which resulted in lack of batching capacity and consequently slow supply rate."
| 02SL - Stations (LUL) | Cxxx-NCR-000565 | NCR | Dss Pour 6a Vertical Capping beam -Chamfer- |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-07-18 | 2013-07-08 09:07 | -10 | 2013-06-25 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | No chamfer fixed on SE corner for vertical capping beam DSS Pour 6a. (see attched photos)
| 02SL - Stations (LUL) | Cxxx-NCR-000566 | NCR | D-Wall Defects at CHS - P22 |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-05-31 | 2013-05-07 14:42 | -24 | 2013-04-19 | Structural Engineering - Diaphragm Walls | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | On excavation of the shaft at Cambridge Heath 1 no. inclusions was discovered next to pre-cast stop-end on panel 22. The exact start and finish levels of the inclusions is yet to be accurately recorded.
| 02SL - Stations (LUL) | Cxxx-NCR-000567 | NCR | DSS P39 - 42h Rule Overrun -( __ -000097) |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-05-17 | 2013-05-07 16:12 | -10 | 2013-04-17 | Structural Engineering - Diaphragm Walls | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The 42 hour rule was exceeded during the construction of panel 39 at Durward Street by 7h 30mins. Root Cause: "The root causes of the NCR's stated above are as follows: 1. Plant breakdown of excavation shovel set was encountered during excavation down and removal of concrete from the steel stop-end on P39. The heavy duty working requirements of this equipment can lead to heavy wear and subsequent breakdowns as it did in this instance. 2. Delays caused by plant break down moved concrete pour from nightshift to dayshift which resulted in lack of batching capacity and consequently slow supply rate."
| 02SL - Stations (LUL) | Cxxx-NCR-000568 | NCR | D-Wall Defects at CHS - P28 |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-05-31 | 2013-05-07 16:39 | -24 | 2013-04-19 | Structural Engineering - Diaphragm Walls | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | On excavation of the shaft at Cambridge Heath 1 no. inclusions was discovered next to pre-cast stop-ends on panel 28. The exact start and finish levels of the inclusions is yet to be accurately recorded.
| 02SL - Stations (LUL) | Cxxx-NCR-000569 | NCR | DSS P39 - 097 NCR DSS 42h Rule Overrun ( BTL-000098) |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-05-30 | 2013-05-29 17:10 | -1 | 2013-04-23 | Structural Engineering - Diaphragm Walls | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | 1-The 66 hour rule was exceeded during the construction of panel 40 at Durward Street by 07h 55mins. 2-Extension cage shear links marked on BTL-DSS-LL-SK2004 we cut during the cage installation. ( Please see attached). Root Cause: The root causes of the NCR's stated above are as follows: 1. Excessive over-concrete between 25m and 30m depth behind the P39/P40 stop-end extended the excavation time. The concrete is suspected to result from a sand lense or clay stone band whichwashed out/ broke out during excavation of P39. 2. The extension cage is narrower than the main cage and has been spliced with an approximate 100mm misalignment. This resulted in a clash with extension cage shear links and the tremie pipe. The cage had to be taken out and obstructing links removed, see attached sketch: Cxxx-DSS-LL-SK2004 REV 04 - NCR SHEAR LINK REMOVAL.
| 02SL - Stations (LUL) | Cxxx-NCR-000570 | NCR | P42 - P42 - BTL(101) NCR DSS 5hr Rule Overrun, Sonics cut, Main bar cut. |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-06-26 | 2013-06-12 10:07 | -14 | 2013-06-05 | Structural Engineering - Diaphragm Walls | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | During the construction of panel 42 the following NCR's were incurred: 1. 26m sonic tubes removed from one of P42 sonic tubes, due to damage caused during horizontal lifting. See attached photo "P42 Damaged Sonic" and sketch ref "P42 Sonic Location" section. 2. The 5 hour rule was exceeded by 12h 15min. Crossrail D-Wall Specification (Cxxx-HYD-Z-RSP-D061-00016 Rev 6.0) specifies the maximum time between the last turnover of the bentonite and the commencement of concreting is max. 5 hours. 3. One main bar and link were cut on Cage 2 Panel 42. See attached sketch ref "P42 Lifting Remedials" and photo " Shackle P42 Cage 2" for location. Root Cause: 1. Middle cage was pre-slung by __ in the correct design positions. During the horizontal lift the slings tightened and forced the sonics to bend. It is unknown when the damaged occured, whether in the fabrication process or during offloading onto to site. The sonics were removed for the following reasons: a) Possibility of falling during the tandem lift or cage splicing b) The sonic probe could get stuck during testing, resulting in an inability to grout the sonic tube up reliably c) The sonic tube no longer fitting together and thus resulting in delays during the cage installation process and potential partial concrete ingress during the concreting operation. 2. The cage installation of P42 commenced at 04:00am and was completed at 19:05pm on 03/05/2013. P42 is a corner cage and as a result requires extra time to lift and install. When the cages were tandem lifted, it became apparent that the shackles would catch on the a main bar and link when lifted to the vertical, thus preventing a safe lift. It was decided to cut the main bar and link to allow for the shackles during tandem lift. 3. The design of the cage for tandem lift did not consider the movement of the shackles during tandem lift. Approximately 150mm of main bar was cut off below the top of thread and 200mm of a link.
| 02SL - Stations (LUL) | Cxxx-NCR-000571 | NCR | P41- changes on the designed cage / 66 Hrs rule exceeded - details to follow |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-05-29 | 2013-05-29 16:53 | 0 | 2013-04-29 | Structural Engineering - Diaphragm Walls | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | 1-The 66 hour rule was exceeded during the construction of panel 41 at Durward Street by 08h 37mins. 2. The 5hour rule was exceeded by 06h 05min. 3. A section of P41 cage was removed prior to installation, see attached sketches "P41 cage trim elevation" and "P41 cage trim plan". Root Cause: Excessive over-concrete removal during P40 installation caused excavation face between P40/P41 to be irregular. Furthermore, a local sand lense or clay stone band is expected to be washed out/ broke out during excavation of P40. The overconcrete could not be removed and obstructed the P41 cage.
| 02SL - Stations (LUL) | Cxxx-NCR-000574 | NCR | D-Wall Piling Construction Records |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-05-30 | 2013-05-17 09:44 | -13 | 2013-05-07 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | During a joint surveillance carried out on 02-May 2013, it was noted that on reviewing the site records as per the ITP, it was found that there was a considerable delay in the records for each section of the Diaphragm Wall Construction being formally presented to the main contractor by the subcontractor. It was also noted the records reviewed which had not been released to the main contractor had no signatures on them, we were informed that the subcontractor signs them once he/she has reviewed them, the signatures for the intervention points by contractor and CRL are added retrospectively. Part 20.8 requires the Contractor (through the ITP process) to make clear who is responsible for implementing the planned arrangements, as well as who is responsible for certifying that compliance with requirements has been achieved in practice.
| 02SL - Stations (LUL) | Cxxx-NCR-000575 | NCR | D-Wall Construction - Clay deposit in found in panel 7 - Upper Ring Beam |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-07-02 | 2013-07-01 09:47 | -1 | 2013-05-22 | Civil - Civil Engineering General | 500 |  | Material | Repair |  | Complete |  | Completed |  | On 14th May during the ring beam construction at CHS a clay pocket was found in Panel 7 at CHS at upper ring beam level. (-21m bgl approx.). The clay pocket was approximately 100mm deep X 60mm X 80mm. - See attached photographs
| 02SL - Stations (LUL) | Cxxx-NCR-000579 | NCR | P41 - Tremie embedment ( __ 100) |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-07-11 | 2013-06-17 18:31 | -24 | 2013-06-07 | Structural Engineering - Diaphragm Walls | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Tremie embedment exceeded allowable tolerances of min 3m to max 10m stated in the D-wall ITP, in a double tremie pour in P41. At the end of concreting of P41 the concrete was flushed to the top and the double tremies removed. When the tremies were removed the tremie lengths were not as per the onsite concrete record. According to the concrete record being carried out on site during the pour, tremie embedment should have been 9m (3x3m sections) in both tremies. When the tremie were removed one tremie string was 6m (P40 side) and the other 9m, varying 3m in one of the tremie strings. Please see the attached concrete records showing tremie embedment as per original site record and record adjusted for a 3m shorter tremie string," P41 Original Concrete Record" and "P41 Visual Tremie Embedment" which shows the minimum embedment as 100mm at 15m depth. This is only shown as worse case scenario and does not necessarily reflect the sequence of events. Root Cause: The correct root cause could not be identified however the cause of less tremies found at the end could have been a cause of one of the following: 1) P41 was found to have a large concrete inclusion on the interface between P40 and P41 at a depth of approximately 33.3m. As a result it was planned to install a tremie string of 34m on P40 side and 39m on P42 side. Due to the inclusion of concrete underneath P40 stop-end the tremie string may not have been touched down correctly on the base to double check manual count. 2) Tremie assembly was checked by the supervisor with the installing operative but not witnessed by an engineer, which may have allowed for human error when recording and reporting the correct number of tremies. 3) A shift change occurred during the pour which may have resulted in confusion over the tremie lengths at handover. 4) During concreting operations the engineer was present near the concrete pump/tester at high level and communication with operatives and supervisor was made via radio. There is a likelihood of a misunderstanding/miscommunication on the number of tremies and from which string to be removed.
| 02SL - Stations (LUL) | Cxxx-NCR-000580 | NCR | P38 - (BTL-103 )-Top trapping band out of position. -DSS |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-06-28 | 2013-06-17 18:48 | -11 | 2013-06-07 | Structural Engineering - Diaphragm Walls | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | Top trapping band on top cage of Panel 38 was 225mm higher than its design position. Root Cause: The cage was fabricated to Cxxx-C08.090-DWG-BAU-0193 revision 6 after which the drawing was revised and the trapping band on the top cage was moved from 103.835mATD to 103.610mATD. The construction of the cage commenced on 18/09/2012 however the new revision was only approved on 26/09/2012. As a result the trapping band was built to revision 06 i.e 103.835 mATD.
| 02SL - Stations (LUL) | Cxxx-NCR-000582 | NCR | P41 - ( BTL-104 ) No Verticality Report- DSS |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-06-28 | 2013-06-12 10:18 | -16 | 2013-06-07 | Structural Engineering - Diaphragm Walls | 500 |  | Equipment Breakdown | Use As-Is |  | Complete |  | Completed |  | On P41 the grab computer failed to record the verticality during grab pass. Root Cause: The grab pass was completed and data recorded. However when the report was retrieved it was found the verticality had not been registered on the report due an unknown error. The root cause has been put down as Grab computer malfunction.
| 02SL - Stations (LUL) | Cxxx-NCR-000583 | NCR | P27- 5 hr Rule exceeded - __ 102 |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-07-18 | 2013-07-08 08:49 | -10 | 2013-06-27 | Structural Engineering - Diaphragm Walls | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The 5hour rule was exceeded during the construction of panel 27 at Durward Street by 15h 25mins. During the tandem lift of P27 middle cage, bending was witnessed in the lifting cathedral which resulted in deformation of the main bar. Please see photo " P27 Main bar bending" and location see sketch ref: " P27 Main bar bending location". ( Please see attached on 102 NCR DSS P27 doc) The root causes of the NCR's stated above are as follows: 1. The 5 hour rule was exceeded for the following reasons: Remedials to the main bar which was deformed during lifting, required additional rebar to be spliced to the cage. Secondly as the remedials delayed the concreting operation by a very long time, the concrete batcher was no longer able to supply the concrete at the time when cage was installed. This resulted in a wait of approx.. 7hrs after cage installation. 2. Bending Rebar: Inadequate cage design resulted in the bending of a main bar during tandem lift.
| 02SL - Stations (LUL) | Cxxx-NCR-000585 | NCR | DSS Pour 6a Lower level Capping Beam |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-06-24 | 2013-06-17 18:51 | -7 | 2013-06-10 | Structural Engineering - Reinforcement | 500 |  | Design | Rework |  | Complete |  | Completed |  | Description of non-compliance: 3 No starter bars cut (150mm) in Panel 42 (Picture attached) Describe apparent cause of non-conformance: The Steel fixers will not be able to fix BM 23 (RAM-0317) as the level of 3 No starter bars is 150mm to high.(Picture attached)
| 02SL - Stations (LUL) | Cxxx-NCR-000599 | NCR | Works not ready for inspection |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-07-25 | 2013-07-08 08:43 | -17 | 2013-06-26 | Structural Engineering - Concrete Member | 500 |  | Supervision/Management | Reject |  | Complete |  | Completed |  | Project Manager called for inspection for incomplete works. Having noted debris within formwork of capping beam (pour 7b/8) the Contractor noted that the operative blowing out the debris had gone on a break. The Project Manager notes that this does not comply with the correct procedure in that the work had not been completed, nor was it satisfactory, and yet the Contractor's engineer had accepted it and called the Project Manager to inspect the works.
| 02SL - Stations (LUL) | Cxxx-NCR-000600 | NCR | DSS Pour 5b Vertical Capping Beam - L Level |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-07-10 | 2013-07-08 09:04 | -2 | 2013-06-27 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | __ have cranked BM 592 to achieve cover on west side kicker 5b vertical capping beam. Only 35mm cover could be achieved on west side. (Picture and sketch attached) Root Cause Describe apparent cause of non-conformance: The starter bars BM 592 (6No) installed incorrectly during lower level capping beam 5b.
| 02SL - Stations (LUL) | Cxxx-NCR-000602 | NCR | Inclinometer Probe out of calibration |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-07-24 | 2013-07-16 16:02 | -8 | 2013-07-16 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | Inclinometers IE01, IE02, IM03, IE04, IE05 and IM06b At the time of installation of the above instruments the calibration of the inclinometer probe serial number DP805 had lapsed.
| 02SL - Stations (LUL) | Cxxx-NCR-000603 | NCR | P28 - S2 - CHS repairs concrete strength |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-08-09 | 2013-08-08 15:46 | -1 | 2013-08-02 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | two 28 days cubes crushed from grout used for the repair of P28 section 2 inclusion produced uncharacteristically low average 28 days strength of 48.7 and 49.5 N/mm2
| 02SL - Stations (LUL) | Cxxx-NCR-000604 | NCR | P22-S5 - CHS repairs - cuubes strength |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-08-09 | 2013-08-08 15:55 | -1 | 2013-08-02 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | 2 No's 28days cubes were crushed earlier than the 28 days due to an error in the cast date. the Spare cube from P22 section 5 was crushed at 28days and produced uncharacteristically low result of 46 N/mm2.
| 02SL - Stations (LUL) | Cxxx-NCR-000605 | NCR | D-Wall Installation |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2013-09-25 | 2013-09-16 09:21 | -9 | 2013-08-15 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During Cxxx SCL excavation works approaching the external face of the shaft it was noted that a number of reinforcement links were exposed from the recently installed d-wall panels indicatating there may be issues with maintaining the minimum cover. It is not clear if this is limited to this panel or if the issue is more wide spread.
| 02SL - Stations (LUL) | Cxxx-NCR-000057 | NCR | H&S Assurance competence of sub-contractors |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-07-20 | 2012-07-16 14:40 | -4 | 2012-07-03 | Construction Health & Safety - Construction Health & Safety General | 500 |  | System Defect | Rework |  | Complete |  | Completed |  | Two significant findings arose during the Health and Safety Surveillance undertaken, these related to the validation of sub-contractor / supplier competancies (HS & E policies, ISO9001/ISO14001/ OH__ 18001 registrations, EMAS and HSG65 Compliance). See attached report for further details.
| 02SL - Stations (LUL) | Cxxx-NCR-000095 | NCR | Temporary Bridge Access Deck – Incorrect Bolt Arrangement Installation |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-10-24 | 2012-10-19 09:40 | -5 | 2012-09-28 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | In carrying out the review of the pier arrangement connections to the header beam, the Contractor (Peter Doody) identified that the bolt connections between the RMD 2.7m Meagshor (vertical member) and the 305 x 97 UC Header Beam were incorrect. The bolt connections installed were 4 No. M20 bolts, where drawing number 0104-Whitehcapel-P4 states that bolt connections are to be 4 No. M24 Grade 8.8 Bolts C/W Nuts and Washers on 200 C/CTS (TYP. 4 Positions Each Header Beam). The attached photos (0647, 0649, 0650 and 0651) show the incorrect bolt arrangement which from the review identified the M20 bolts to be installed at each of the RMD Megashor interfaces across the full length of the header beam.
| 02SL - Stations (LUL) | Cxxx-NCR-000107 | NCR | Access Deck Base Slab to HCDL Disused Roads - Incorrect Drawing Revision |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-11-05 | 2012-10-26 09:12 | -10 | 2012-10-08 | Civil - Civil Engineering General | 500 |  | Design | Rework |  | Complete |  | Completed |  | NCR being raised retrospectively and as a follow up to PMC issued to the Contractor (Cxxx __) for the incorrect use of drawings which were not for construction and at revision P1 (Preliminary). The PMC issued to the Contractor (Cxxx-PMC-00734) highlighted that this was the second occurrence of the incorrect revision drawings being used.
| 02SL - Stations (LUL) | Cxxx-NCR-000129 | NCR | Temporary Works Bridge Over HCDL |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-11-30 | 2012-11-06 16:02 | -24 | 2012-10-19 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | Holding down bolts inspected on 16th October had no washers installed.
| 02SL - Stations (LUL) | Cxxx-NCR-000131 | NCR | Temporary Works Bridge Over HCDL |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-12-20 | 2013-01-02 10:00 | 13 | 2012-10-19 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | No welding procedure available to demonstrate that the Cxxx-__M-C-RGN-D061-50002 rev 2 reported stiffener plate weld crack repairs conformed to the above requirement.
| 02SL - Stations (LUL) | Cxxx-NCR-000142 | NCR | Temporary Hoarding Lighting |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-11-22 | 2012-11-22 09:25 | 0 | 2012-11-02 | Electrical - Lighting | 500 |  | Planning | Rework |  | Complete |  | Completed |  | No accepted ITP in place for Temporary Hoarding Lighting on the HCDL Worksite including Platform 1.
| 02SL - Stations (LUL) | Cxxx-NCR-000156 | NCR | Grout cubes for East Stair Shaft Temporary Piles |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-12-17 | 2012-12-17 09:13 | 0 | 2012-11-15 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | On the shift of 13-11-12 no grout cubes were taken for the grout batch that was used for piles 42, 57 and 61 (see attached sketch). This was a result of a mis-communication between the site supervisor and the UKAS accredited engineer to take the samples whereby all grouting had finished by the time the engineer was informed that cubes were ready to be taken. In accordance with our ITP we should have taken one sample (6 cubes) for the 3No. piles.
| 02SL - Stations (LUL) | Cxxx-NCR-000163 | NCR | Temporary diversion of Services on LO platforms - Post N7b to N8 distance |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-01-17 | 2013-01-15 17:29 | -2 | 2012-11-26 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | N7b is to be located as far north as possible (constraint by subway). Following LU union reps walk around, N8 is to be located as far north into platform corner as possible. This results in a 6.6m spacing i.e. 600mm to great.
| 02SL - Stations (LUL) | Cxxx-NCR-000164 | NCR | Temporary Diversion of London Overground Services - N7b post |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-01-15 | 2013-01-15 17:27 | 0 | 2012-11-26 | Civil - Civil Engineering General | 500 |  | Design | Rework |  | Complete |  | Completed |  | Abutment wall behind panel protudes into the space available and as such the free standing cannot be installed.
| 02SL - Stations (LUL) | Cxxx-NCR-000166 | NCR | LO temporary services diversions - Post N15 bolts |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-12-21 | 2012-12-21 12:04 | 0 | 2012-11-26 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The bolts were installed as per the original design not the marked up drawing.
| 02SL - Stations (LUL) | Cxxx-NCR-000167 | NCR | LO platforms temporary services diversion - N16 post bolts |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-12-21 | 2013-01-02 09:35 | 12 | 2012-11-26 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | The 2nr anchors closest to the platform edge have 150 mm embedment because steel obstruction (assumed reinforcement) encountered. Anchors tried to be installed in multiple locations unsuccesfully.
| 02SL - Stations (LUL) | Cxxx-NCR-000168 | NCR | HCDL East Stair Shaft Early Curing of Grout Cubes |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-02-07 | 2013-01-21 10:20 | -17 | 2012-11-26 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Three sets of grout cubes taken for the East Stair Shaft piles 70 and 58 have an average 28-day compressive strength below the required 40N/mm2 (ranging from 33.5-38.5N/mm2). These cubes were kept on site, in their moulds, but no record of early curing temperatures exist therefore we cannot be sure the initial cure took place within the required 15-25 degrees. The low strengths are a result of poor early curing, they are not representative of the piles. A review of cube results for samples taken with correct early curing procedures and records in place demonstrate the required strength gain has been achieved.
| 02SL - Stations (LUL) | Cxxx-NCR-000169 | NCR | Temporary Diversion of LO services - Base plate of post S5 and S6 |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-12-21 | 2013-01-02 09:37 | 12 | 2012-11-26 | Civil - Civil Engineering General | 500 |  | Design | Repair |  | Complete |  | Completed |  | Type E base plate is required to span ACO drain. Post S5 on site does not span ACO drain and therefore does not require type E baseplate. Post S6 on site does span ACO drain and therefore does require type E base plate.
| 02SL - Stations (LUL) | Cxxx-NCR-000183 | NCR | Platform 2 Worksite Hoarding Lighting |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-01-25 | 2013-01-24 12:46 | -1 | 2012-11-29 | Electrical - Lighting | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Check Sheet Cxxx/CL0015 SWA Cable Runs - No location details on check sheet and client listed as NR. Checksheet Cxxx/CL0019 Platform 2 Cable Tray details Cable Tray Overloaded - no explanation given. Checksheet Cxxx/CL0015 SWA Cable Runs had N/A status but no expalnations given. Checksheet Cxxx/CL009 Isolators and Fuse Switches not signed Checksheet Cxxx/CL0019 Cable Tray Platform 2 not signed
| 02SL - Stations (LUL) | Cxxx-NCR-000184 | NCR | Platform 2 Worksite Hoarding Lighting - DRA sign-off |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-01-25 | 2013-01-28 09:41 | 3 | 2012-11-29 | Electrical - Lighting | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Page 15 is the signature sheet - the copy in the file wasn't the signed version as on eB therefore could not be verified as the latest copy. The designers Risk Assessment had no __ signoff - A separate sheet which states that installation is in accordance with the CDS requirements with any deviations listed and signed off by __ needs to be incorporated into the file.
| 02SL - Stations (LUL) | Cxxx-NCR-000185 | NCR | Platform 2 Worksite Hoarding Lighting |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-12-13 | 2012-12-17 09:28 | 4 | 2012-11-29 | Electrical - Lighting | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Glands found to be only finger tight
| 02SL - Stations (LUL) | Cxxx-NCR-000186 | NCR | Platform 2 Worksite Hoarding Lighting - zinga coating |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-12-21 | 2012-12-20 11:04 | -1 | 2012-11-29 | Electrical - Lighting | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Cable Tray ends not zinga painted.
| 02SL - Stations (LUL) | Cxxx-NCR-000187 | NCR | Platform 2 Worksite Hoarding Lighting - Rotary Isolators |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-12-21 | 2012-12-20 11:01 | -1 | 2012-11-29 | Electrical - Lighting | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | 6 no. Rotary Isolators cables within showing too much copper at termination points and connector block needs to be removed.
| 02SL - Stations (LUL) | Cxxx-NCR-000188 | NCR | Platform 2 Worksite Hoarding Lighting - IP Rated Through Boxes |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-12-21 | 2012-12-20 11:22 | -1 | 2012-11-29 | Electrical - Lighting | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | 3x3 IP rated through boxes need flex checks for nicks etc. which were not carried out at the time of installation.
| 02SL - Stations (LUL) | Cxxx-NCR-000189 | NCR | Platform 2 Worksite Hoarding Lighting - Cable Distortion |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-12-21 | 2012-12-20 10:56 | -1 | 2012-11-29 | Electrical - Lighting | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | First Aid Box put in so that cable/box got distorted and stretched
| 02SL - Stations (LUL) | Cxxx-NCR-000210 | NCR | Platform 1 lighting non compliant cable |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-01-18 | 2013-01-15 17:04 | -3 | 2012-12-14 | Electrical - Lighting | 500 |  | Material | Rework |  | Complete |  | Completed |  | FP400 has been installed from BD2 to First Junction box, away from the JB outgoing circuits have been installed with non compliant material
| 02SL - Stations (LUL) | Cxxx-NCR-000211 | NCR | Platform 1 lighting cable shrouds |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-01-17 | 2013-01-15 16:54 | -2 | 2012-12-14 | Electrical - Lighting | 500 |  | Material | Rework |  | Complete |  | Completed |  | Cables have been installed using plastic glands and non low smoke shrouds
| 02SL - Stations (LUL) | Cxxx-NCR-000213 | NCR | Piling to Tower Crane 1 - Connection of Coupler Bars to Main Reinforcement |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-01-25 | 2013-01-02 09:40 | -23 | 2012-12-17 | Civil - Geotechnical Engineering | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Operatives observed attempting to torque coupler connector bolts to main reinforcement bar to pile 4, using a small ratchet wrench and length of scaffolding tube. The activity was being carried out in place of the correct tool being used, which in this case should have been a 'nut-runner' that shares off the coupler connector bolts to the correct torque. The actiity was stopped before coupler connection nut sheared off.
| 02SL - Stations (LUL) | Cxxx-NCR-000216 | NCR | TC1 pile 4 base collapse |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-01-31 | 2013-01-02 09:51 | -29 | 2012-12-20 | Civil - Geotechnical Engineering | 500 |  | Planning | Reject |  | Complete |  | Completed |  | Extended time to fix the tension bar due to plant breakdown of nut runners for M__ couplers resulted in pile 4 being left open for more than 12 hours. The pile could not be concreted at night as the Section 61 does not allow for this activity. As a result the base collapsed and the pile was only 22m in length. The T40 tension bars could not be removed due to their length (a crane would be required and the approval time would result in the pile being left open even longer). The pile was therefore poured being short of its designed length and with a collapsed base.
| 02SL - Stations (LUL) | Cxxx-NCR-000217 | NCR | TC1 pile 4 Wrong Concrete Delivery |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-12-21 | 2012-12-21 11:01 | 0 | 2012-12-20 | Civil - Geotechnical Engineering | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The first delivery of concrete for pile 4 was a mix for Cxxx contract and not Cxxx. This was identified by the __ engineer on site and the concrete was rejected and the correct batch sent. However the slump for the concrete was taken at the same time as the ticket was reviewed and this should have waited until after review of the ticket. To enable the slump to be taken part of the load was discharged in to the pump hopper. This was cleared through the line along with the grout to clear the line and did not enter the pile.
| 02SL - Stations (LUL) | Cxxx-NCR-000218 | NCR | Deformed Junction Box Due to Cable Stress |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2012-12-21 | 2012-12-21 10:55 | 0 | 2012-12-20 | Electrical - Lighting | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Junction box installed too low on unistrut leading to deformation of lower side.
| 02SL - Stations (LUL) | Cxxx-NCR-000222 | NCR | TC1 pile 4 auger extraction damage |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-01-31 | 2013-02-01 16:32 | 1 | 2012-12-21 | Civil - Geotechnical Engineering | 500 |  | Damaged | Reject |  | Complete |  | Completed |  | The slump of the concrete delivered was within the range of the design prior to pumping in to the pile. However the concrete within pile 4 cured faster than expected resulting in reduced workability. This meant that the reinforcement cage was difficult to insert although was inserted to full depth without the use of a poker as required. When the casings were extracted though the concrete within the pile lifted dragging the reinforcement cage with it. This has resulted in removal of the cage and significant damage to the top third of the pile concrete.
| 02SL - Stations (LUL) | Cxxx-NCR-000238 | NCR | TC1 piling - Pile nr 7 cage to low |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-02-20 | 2013-02-20 16:24 | 0 | 2013-01-17 | Civil - Civil Engineering General | 500 |  | System Defect | Repair |  | Complete |  | Completed |  | Cage below pile cut off level
| 02SL - Stations (LUL) | Cxxx-NCR-000239 | NCR | TC1 piling - Pile Nr 8. Pile left open over 12hrs |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-02-11 | 2013-02-11 15:41 | 0 | 2013-01-17 | Civil - Civil Engineering General | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | Possible reduction in friction resistence and factor of safety
| 02SL - Stations (LUL) | Cxxx-NCR-000245 | NCR | East Stair Shaft piles - exposed rebar bent over |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-01-31 | 2013-02-01 16:16 | 1 | 2013-01-16 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Damaged pile cage rebar
| 02SL - Stations (LUL) | Cxxx-NCR-000246 | NCR | East Stair shaft - Low grout strength Piles 79 and 56 |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-04-30 | 2013-03-06 15:55 | -55 | 2013-01-17 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Piles 79 and 56 (East Lift Shaft) The results from cube tests for the above referenced piles yielded an average compressive strength at 28 days of 34.0 N/mms which is below the specified 40.0 N/mm2
| 02SL - Stations (LUL) | Cxxx-NCR-000247 | NCR | Tower Crane pile Nr 8 - Cage dropped |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-02-20 | 2013-02-13 11:15 | -7 | 2013-01-17 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Cage is not at designed level
| 02SL - Stations (LUL) | Cxxx-NCR-000253 | NCR | TC1 pile Nr 8 - Faliure to bore to revised depth following revised toe level to take in to account longer than 12hrs |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-02-20 | 2013-02-20 16:37 | 0 | 2013-01-17 | Civil - Civil Engineering General | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | Pile could have insifficient friction resistence and subseqent reduced factor of safety
| 02SL - Stations (LUL) | Cxxx-NCR-000272 | NCR | Temporary CMS on ELL lack of room for cable installation |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-04-12 | 2013-04-08 10:52 | -4 | 2013-01-29 | Electrical - Cable Management | 500 |  | Design | Rework |  | Complete |  | Completed |  | As a result of the above technical detail, there is insufficent space for cable installation. Cables would be in-accessable / Impossible to install and therefore cannot be installed as shown.
| 02SL - Stations (LUL) | Cxxx-NCR-000275 | NCR | IRFs and ITP implementation |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-02-15 | 2013-02-06 09:45 | -9 | 2013-02-01 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Notification have not been served to the CRL to inspect the activities related to the brackets installation above pour 5b for the purpose of CHS Staircase Access construction. Activities of the ITP Cxxx-__M-C-ITP-D061-50032 rev01 from (4.1-4.5) listed below have been completed on site by the contractor with no IRF sent to CRL. 4.1 Ensure no one under load during lift. 4.2 Setting out line/level of support brackets and staircase. 4.3 Check depth of drilled anchor hole for support brackets. 4.4 Check depth of drilled anchor hole for staircase ties. 4.5 Bedding grout to be poured to correct depth and without air pockets.
| 02SL - Stations (LUL) | Cxxx-NCR-000276 | NCR | Damage to Waterproofing surrounding Capping Beam |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-02-18 | 2013-02-19 10:14 | 1 | 2013-02-04 | Civil - Civil Engineering General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | The initial edge protection didn’t comply with the temporary works drawing. The stubs were not cast vertically. During breakout of the slab for reinstallation the 5T excavator worked from the unprotected surface of the capping beam. The hydraulic braker attachment struck the capping beam during breakout causing damage to the waterproofing membrane.
| 02SL - Stations (LUL) | Cxxx-NCR-000277 | NCR | London Overground Temporary Support of Services - Installation of posts N7b |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-03-29 | 2013-03-25 09:19 | -4 | 2013-02-04 | Civil - Civil Engineering General | 500 |  | Design | Rework |  | Complete |  | Completed |  | Support N7b does not fit as planned behind the VE panels on the bridge abutment. This has occurred due to the design not taking into account some of the existing steel structures.
| 02SL - Stations (LUL) | Cxxx-NCR-000279 | NCR | London Overground Temporary Support of Services – Installation of posts N6 and N7a |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-03-29 | 2013-03-25 12:43 | -4 | 2013-02-04 | Civil - Civil Engineering General | 500 |  | Design | Rework |  | Complete |  | Completed |  | The bottom half has been installed but the top part could not be fitted as planned because of steel structures spanning across behind the VE panels. The post also clashes with existing cable trunking at high level.
| 02SL - Stations (LUL) | Cxxx-NCR-000280 | NCR | London Overground Temporary Support of Services – Orientation of Posts |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-04-10 | 2013-04-08 10:56 | -2 | 2013-02-04 | Structural Engineering - Steel Member | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | The following posts have been installed in the incorrect orientation i.e with the web perpendicular to the platform edge rather than with the web parallel to the platform edge (see attached sketch). N1, N2, N4, N5, N11, N12, S10, S11, S12, S13, S14. The non-compliance was identified during the shift and an on-site decision was taken to install all remaining posts in the same orientation to ensure consistency between the posts. Some of the posts carrying the heaviest load (like S5) are designed with the web perpendicular to the platform edge so it was assumed that this decision would not have an influence on the stability of the supports. The upper part of the posts formed by a unistrut welded on a plate is therefore now in an incorrect orientation and has been removed to be replaced
| 02SL - Stations (LUL) | Cxxx-NCR-000281 | NCR | London Overground temporary support of services – Location of post S14 and S13 |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-04-10 | 2013-03-25 08:57 | -16 | 2013-02-04 | Civil - Civil Engineering General | 500 |  | Planning | Rework |  | Complete |  | Completed |  | The bolts for the posts S13 and S14 were installed during the October possession. During that time, the setting out of the posts was done approximately, using the only constraint on the position of the posts - the spacing between them to be lower than 6m. Post S13 bolts were located in close proximity of the dry riser, which would have resulted in restricted access to the door. To ensure that access would not be restricted, S13 was moved towards S12, away from the door. In addition, S14 was moved towards S13 to maintain the spacings between posts to less than 6 m.
| 02SL - Stations (LUL) | Cxxx-NCR-000282 | NCR | London Overground temporary support of services – Base of post S14 |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-04-10 | 2013-04-08 11:05 | -2 | 2013-02-04 | Civil - Civil Engineering General | 500 |  | Design | Rework |  | Complete |  | Completed |  | The detail of the installation of S14 shows a base plate to be installed on to the top of a concrete slab located right below the paver slab and the screed. At the location for S14, the concrete slab was at a lower level than in other locations. This required the platform to be broken out to a lower level. This resulted in a reduced clearance to the level of the CMS from platform level.
| 02SL - Stations (LUL) | Cxxx-NCR-000291 | NCR | CHS Haki Staircase 1 Damage |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-02-20 | 2013-02-22 10:21 | 2 | 2013-02-08 | Civil - Civil Engineering General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | Haki staircase scaffold beam damaged by a 21T excavator during shaft excavation works.
| 02SL - Stations (LUL) | Cxxx-NCR-000292 | NCR | CHS Capping Beam Damage |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-02-22 | 2013-02-22 10:56 | 0 | 2013-02-08 | Civil - Civil Engineering General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | Capping beam damaged during excavation works. A 21T excavator struck the capping beam with the bucket while working in the area resulting in a section of capping beam being chipped off at the bottom corner.
| 02SL - Stations (LUL) | Cxxx-NCR-000293 | NCR | Lack of protection of split ducts surrounding Data logging cables |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-02-22 | 2013-02-22 10:45 | 0 | 2013-02-08 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | Split ducting containing data cables for strain gauges not adequately protected. Located in the walkway and exposed to potential damage due to being walked over, kicked, etc.
| 02SL - Stations (LUL) | Cxxx-NCR-000309 | NCR | Incorrect cement grout to plug TC7 coreholes |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-03-08 | 2013-03-08 15:40 | 0 | 2013-02-22 | Civil - Civil Engineering General | 500 |  | Material | Rework |  | Complete |  | Completed |  | Grout to be used to fill core holes in the TC7 barrette was not the same product as identified in the approved MCR and WMS.
| 02SL - Stations (LUL) | Cxxx-NCR-000334 | NCR | Concrete strewngth below specified strength |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-04-05 | 2013-04-05 15:33 | 0 | 2013-03-14 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Concrete pile under specified strength
| 02SL - Stations (LUL) | Cxxx-NCR-000364 | NCR | TC1 piling - Removal of reinforcing projections |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-04-11 | 2013-04-11 12:40 | 0 | 2013-03-21 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | In order to install a backblinding shutter between pile projections and the existing platform wall, while maintaining minimum backblinding thickness of 400mm. Cage reinforcing bars within a single pile (pile No. 7) insitu so as to project into the pile cap were removed as they clashed with shuttering.
| 02SL - Stations (LUL) | Cxxx-NCR-000375 | NCR | TC1 piles 1, 11 & 12 |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-05-08 | 2013-04-15 09:02 | -23 | 2013-03-28 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Pile cut-off level is such that 75mm remains within the cap itself. Following a pile breakdown operation it was observed that 3of the piles (1, 11 & 12) had been over broken such that less than 75mm remains. Generally across the three piles approximately 40mm remains
| 02SL - Stations (LUL) | Cxxx-NCR-000384 | NCR | CHS PR Well - PRW4 depth |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-05-08 | 2013-05-01 15:10 | -7 | 2013-04-02 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | - PRW4 driven to required depth initially using the open hole method (no casing or polymer used) - The hole collapsed back to a depth of 20.7m (69.3m ATD) - The well liner was installed to this level but sediment within the well screen rose up to c. 19.6m depth (c. 70.4m ATD). - An attempt was made to recover the well liner to allow redrilling. The liner was stuck tight and would not pull without risking breaking. - End result is that the well was terminated too shallow and not conforming to the tolerances specified.
| 02SL - Stations (LUL) | Cxxx-NCR-000385 | NCR | Concrete tolerance/reinforcement cover |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-04-26 | 2013-04-26 13:28 | 0 | 2013-04-02 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | TC1 back blinding walls have been surveyed for as-built purposes, from this exercise __ have learnt that over a limited area the two walls are approximately +10mm out of tolerance on the vertical plane. The consequence of this is that the TC1 pile cap reinforcement will not have sufficient, as designed cover.
| 02SL - Stations (LUL) | Cxxx-NCR-000408 | NCR | Damage to Diaphragm Wall cast in couplers during works to expose |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-06-28 | 2013-06-05 10:50 | -23 | 2013-05-29 | Shafts - Shafts General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | During works to expose the couplers within the CHS Diaphragm Wall it has become apparent that a number of box-outs for the couplers have been dislodged during Cxxx construction. This has resulted in a number couplers have to be broken out of concrete. During works to expose the couplers, a number have been found to be damaged, or have inadvertently been damaged during the process of exposing them. __ are in the process of completing the exposing works, and a full record of all damaged couplers is being compiled.
| 02SL - Stations (LUL) | Cxxx-NCR-000423 | NCR | TC1 Crane Base Concrete Placement |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-05-29 | 2013-05-14 10:51 | -15 | 2013-04-22 | Civil - Civil Engineering General | 500 |  | Equipment Breakdown | Rework |  | Complete |  | Completed |  | On the 18th April 2013, the placing concrete for TC1 Crane Base was interrupted leading to the unplanned cessation of the pour, blockages in the pipeline were cited as a potential reason by the Contractor . As a direct consequence of this the completion of the concreting activity could not be completed leading to the requirement of an unplanned construction joint in the crane base.
| 02SL - Stations (LUL) | Cxxx-NCR-000464 | NCR | TC7 Base Rebar |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-05-22 | 2013-05-23 10:17 | 1 | 2013-05-08 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Bar mark 02 (top layer) has been installed with 37no bars as opposed to the 38no specified. The reason for this was that the order was a bar short.
| 02SL - Stations (LUL) | Cxxx-NCR-000466 | NCR | TC7 Base pour concrete - Flow test failure |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-06-14 | 2013-06-12 17:28 | -2 | 2013-05-08 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | A spinner from __ (Silvertown) arrived with a batch of LC40/44 pump mix with an F5 consistance class. The flow test result was 720mm. See ticket attached.
| 02SL - Stations (LUL) | Cxxx-NCR-000492 | NCR | Non-use of __ PS1000 Rebar scanner resulting in over drilling to CHS Diaphragm Wall |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-06-05 | 2013-06-03 15:15 | -2 | 2013-05-29 | Shafts - Linings | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | During a routine site visit, it was noted by the __ Quality Site Inspector that the scanner was not being used and instead holes were being drilled into the wall on a trial and error basis. This practice has resulted in additional holes being drilled that are not suitable to anchor the shuttering ties.
| 02SL - Stations (LUL) | Cxxx-NCR-000517 | NCR | Ventilation Fan Support System |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-06-26 | 2013-06-14 10:32 | -12 | 2013-05-17 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | Due to the available concrete blocks on site, 4 No. scaffold tubes have been attached to the side of the block instead of on top as per design.
| 02SL - Stations (LUL) | Cxxx-NCR-000524 | NCR | __ Fixing Pullout Tests |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-06-19 | 2013-06-18 16:33 | -1 | 2013-05-17 | Civil - Civil Engineering General | 500 |  | Material | Rework |  | Complete |  | Completed |  | ITP Cxxx-__M-C-ITP-D061-50044 did not adequately address the requirement for pull-out testing of chemical anchors for Ring Beam shuttering. Additionally, to date the following anchors have failed to meet the required pull out test of 60kN as required by the temporary works design reference Cxxx-__M-C-CER-D061-50013. Date Location Details 10/05/13 Pour 1 – Panel P12 Failed pull-out test (reported by Cxxx) 13/05/13 Pour 1 – Panel P12 Failed pull-out test again 13/05/13 Pour 1 – Panel P13 Failed pull-out test at 20kN applied load, 13/05/13 Pour 1 – Panel P14 Failed pull-out test at 20kN 15/05/13 Pour 1 – Panel P13 Failed pull-out test failed at load of 45kN
| 02SL - Stations (LUL) | Cxxx-NCR-000525 | NCR | CHS Capping Beam _ Starter bars damaged |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-06-26 | 2013-06-05 09:10 | -21 | 2013-05-29 | Structural Engineering - Reinforcement | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | On 24th March 2013, the rear of a crane cab struck the rebar starter bars on the outer edge of the the CHS capping beam (photos attached). Several of the bars were bent and 4 were cut as they had became trapped within the under carriage below the crawler crane counter weights.
| 02SL - Stations (LUL) | Cxxx-NCR-000526 | NCR | CHS Water proofing behind upper ring beam - Pour 1 |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-06-28 | 2013-06-05 10:35 | -23 | 2013-05-29 | Structural Engineering - Diaphragm Walls | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | The shuttering ties were drilled and anchored after the water proofing had been applied to the diaphragm wall causing perforations in the water tight seal.
| 02SL - Stations (LUL) | Cxxx-NCR-000527 | NCR | Undertaking Works with a Generic Approved ITP |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-06-26 | 2013-06-26 16:02 | 0 | 2013-05-17 | Electrical - Cable Management | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | On Friday 17th May 13 it come to the attention of the Supervisor that the Contractor proceeded with the installation of CMS to the disused sides of the HCDL platform hoardings to enable diversion of lighting, LV, communications and fire services, without first ensuring the appropriate approved documentation. - The installation has taken place during planned night shifts on the station. A generic ITP was being used which should have been task specific to support the intended works. A revised CDS was in place, however it was still under review by LUL and was not accepted.
| 02SL - Stations (LUL) | Cxxx-NCR-000552 | NCR | Kempton court access road slab |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-07-02 | 2013-06-21 15:49 | -11 | 2013-05-22 | Civil - Civil Engineering General | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | Concrete not slumped prior to placement, only after discharge. Additional water was added to the concrete without the permission or knowledge of the supervising UKAS technician.
| 02SL - Stations (LUL) | Cxxx-NCR-000555 | NCR | CHS URB Incorrect steel unloaded |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-06-06 | 2013-06-03 16:26 | -3 | 2013-05-23 | Shafts - Shafts General | 500 |  | Supervision/Management | Reject |  | Complete |  | Completed |  | Delivery not inspected by Site Engineer => wrong steel unloaded
| 02SL - Stations (LUL) | Cxxx-NCR-000556 | NCR | Incorrect storage of grout cubes for P44 and P61 |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-07-01 | 2013-06-12 10:55 | -19 | 2013-05-31 | Geotechnical Engineering - Geotechnical Engineering - General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | On 4-5-13, it was decided that the grout cubes taken would be left to cure and store overnight in a safe and sheltered area on-site as access to the cube storage tank was not possible due to the erection of tower crane 1. This may cause the grout moulds to be unrepresentative samples of the piles installed.
| 02SL - Stations (LUL) | Cxxx-NCR-000587 | NCR | Upper Ring beam - Pour 1 Concreting |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-07-09 | 2013-06-12 11:13 | -27 | 2013-06-04 | Shafts - Shafts General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | On two occasions the spinner from __ (Silvertown) arrived with a batch of Line 31 concrete (which has an S3 consistency class), where the slump measurement exceeded the upper boundary of the S3 class. See ticket attached.
| 02SL - Stations (LUL) | Cxxx-NCR-000591 | NCR | GSM Roof Demo Scaffolding |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-06-28 | 2013-06-11 13:22 | -17 | 2013-06-10 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | Transom and ledger bracing installed incorrectly according to section B - B on drawing No. 5035-50-02-002. Transoms are installed below Ledgers.
| 02SL - Stations (LUL) | Cxxx-NCR-000594 | NCR | Calibration Certificates for measuring and testing equipment |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-07-09 | 2013-07-09 14:22 | 0 | 2013-06-06 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | On 27th May 2013 a Surveillance was carried out on the works associated with the construction of the upper ring beam and it was found that the Calibration Certificates for the measuring and test equipment used for the work were made available to review, but the Contractor did not maintain or have a schedule for measuring and test equipment which is required as part of the contract. Volume 2B – General Requirements Part 20 – Quality Management Clause 20.8 states “The Contractor is to maintain a schedule of all measuring and test equipment used for the works that includes records of the calibration to notionally recognised standards”
| 02SL - Stations (LUL) | Cxxx-NCR-000597 | NCR | URB Pour 1 - Early Striking of Stop End |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-06-28 | 2013-06-12 11:37 | -16 | 2013-06-07 | Shafts - Linings | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | The stop end shutters were struck on Pour 1 of the Cambridge Heath Shaft Upper Ring Beam not in accordance with the approved procedure. The Stop End was struck at approximately 15:00 the day after the pour had been completed, with the agreement of the TWC. According to the procedure Shutters, including Stop Ends, are not to be struck until 2N/mm2 has been achieved.
| 02SL - Stations (LUL) | Cxxx-NCR-000600 | NCR | MCR for grout mix on piling works |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-06-28 | 2013-06-14 10:33 | -14 | 2013-06-07 | Geotechnical Engineering - Geotechnical Engineering - General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | MCR was not submitted to client for acceptance (code 1 or code 1 decal). The grout mix was checked by __ material Engineers to ensure compliance with the design specification.
| 02SL - Stations (LUL) | Cxxx-NCR-000619 | NCR | Upper Ring beam - Pour 3 Concreting |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-07-18 | 2013-07-18 10:09 | 0 | 2013-06-11 | Shafts - Shafts General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | On two occasions the spinner from __ (Silvertown) arrived with a batch of Line 31 concrete (which has an S3 consistency class), where the slump measurement exceeded the upper boundary of the S3 class. See ticket attached.
| 02SL - Stations (LUL) | Cxxx-NCR-000632 | NCR | East Stair Shaft - no representative grout cubes taken |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-06-21 | 2013-06-14 10:10 | -7 | 2013-06-13 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | Representative samples on 6/5/13 (for piles 43, 81 and 83) were not taken. Pile logs written by piling site supervisor state the volume of materials used within the pile and these are similar to the mixes used for other piles and it is as per the grout mix design.
| 02SL - Stations (LUL) | Cxxx-NCR-000676 | NCR | ESS, Pile 52 bollard post out of tolerance |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-07-24 | 2013-07-22 09:39 | -2 | 2013-06-19 | Civil - Geotechnical Engineering | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Pile 52 bollard post was not installed within the centre of the reinforcement cage and is therefore out of tolerance.
| 02SL - Stations (LUL) | Cxxx-NCR-000682 | NCR | ESS, Pile 16 bollard post out of tolerance and reinforcement cover low |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-07-24 | 2013-07-22 09:23 | -2 | 2013-06-20 | Civil - Geotechnical Engineering | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Pile 16 bollard post was not installed within the centre of the reinforcement cage and is therefore out of tolerance. Pile 16 was inspected and it was observed that a reinforcing bar is exposed.
| 02SL - Stations (LUL) | Cxxx-NCR-000683 | NCR | Anchor Ties cast into Upper Ring Beam |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-07-18 | 2013-07-17 08:44 | -1 | 2013-06-22 | Shafts - Shafts General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | For a line of dywidag ties (4no bars) in Pour 5 the sleeves and cones are absent. As a result the ties have been cast into the pour.
| 02SL - Stations (LUL) | Cxxx-NCR-000685 | NCR | ESS: low top of projection levels |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-07-18 | 2013-07-18 10:30 | 0 | 2013-06-25 | Civil - Geotechnical Engineering | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The following piles were surveyed upon pile breakdown and are summarised below: P9 – 175mm low P20 – 189mm low P22 – 214mm low P25 – 153mm low P27 – 263mm low P28 – 132mm low P40 – 354mm low P42 – 337mm low P43 – 268mm low P48 - 232mm low P52 - 278mm low P54 – 325mm low P77 – 110mm low P82 – 182mm low
| 02SL - Stations (LUL) | Cxxx-NCR-000698 | NCR | ESS: high top of projection levels for piling works |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-07-31 | 2013-07-24 09:56 | -7 | 2013-07-03 | Civil - Geotechnical Engineering | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The following piles were observed to have high top of steel based on pile logs and surveyed upon pile breakdown: P19 – 347mm high P21 – 372mm high P24 – 220mm high P26 – 200mm high P29 – 157mm high P41 - 191mm high
| 02SL - Stations (LUL) | Cxxx-NCR-000699 | NCR | ESS: Piles out of positional tolerance |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-08-15 | 2013-08-02 16:02 | -13 | 2013-07-03 | Civil - Geotechnical Engineering | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The following piles have been surveyed as out of positional tolerance: P13 - 100mm (43mm East, 90mm North) P18 - 157mm (-157mm East, 8mm North) P20 - 142mm (32mm East, 138mm North) P56 - 87mm (-87mm East, 4mm North) P57 - 101mm (30mm East, 96mm North) P59 - 101mm (22mm East, 99mm North)
| 02SL - Stations (LUL) | Cxxx-NCR-000700 | NCR | ESS: Piles 88 - sampled grout cubes |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-08-07 | 2013-07-17 08:41 | -21 | 2013-07-03 | Civil - Geotechnical Engineering | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Pile 88, constructed on 02/03-07-13 (engineering hour shift) took four cube samples, therefore not having two cubes for reserve testing.
| 02SL - Stations (LUL) | Cxxx-NCR-000704 | NCR | Lack of Inspection Requests - East Stair Shaft |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-07-25 | 2013-07-25 23:24 | 0 | 2013-07-04 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Contractor has not identified the need for the inspection of the breaking down of piles within the East Stair Shaft (condition of starter bars and cut off level) in the associated ITP. The result is that the Contractor has continued with the work without inviting the Project Manager to inspect these necessary intervention points. Additionally, no IRF has been submitted for items 4.1, 4.2, 4.3, 4.4, 4.5, 4.6, 4.7 and 4.8, all of which have progressed - see attached photo. The Project Manager has requested on several occassions for IRFs to be submitted for this section of works.
| 02SL - Stations (LUL) | Cxxx-NCR-000705 | NCR | Adequate inclusion of activities within ITP for Western SME |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-07-31 | 2013-07-25 23:29 | -6 | 2013-07-04 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Contractor has not identified the need for intervention / inspection of the breaking down of platform 2 in the associated ITP. The result is that the Contractor has continued with the work without having an adequate inspection and testing regime in place along with necessary intervention points for the removal of the platform and associated works.
| 02SL - Stations (LUL) | Cxxx-NCR-000707 | NCR | Use of Concrete retarder on URB pours |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-07-19 | 2013-07-09 14:05 | -10 | 2013-07-08 | Shafts - Linings | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | This material has been used on every pour of the URB.
| 02SL - Stations (LUL) | Cxxx-NCR-000725 | NCR | Upper Ring beam - Pour 4 Concreting |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-08-20 | 2013-08-15 11:26 | -5 | 2013-07-12 | Shafts - Shafts General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | On two occasions the spinner from the supplier (__ Silvertown) arrived with a batch of Line 31 concrete (which has an S3 consistency class), where the slump measurement exceeded the upper boundary of the S3 class. See ticket attached.
| 02SL - Stations (LUL) | Cxxx-NCR-000738 | NCR | Upper Ring Beam |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-08-05 | 2013-07-24 10:25 | -12 | 2013-07-15 | Shafts - Shafts General | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | A section of Pour 4 Area measuring 2m long X1m wide been poured low. It is currently 0.150mm low i.e. TOC is 93.300.
| 02SL - Stations (LUL) | Cxxx-NCR-000742 | NCR | ESS: low top of projection level (P53) |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-07-24 | 2013-07-22 09:10 | -2 | 2013-07-16 | Civil - Geotechnical Engineering | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Pile 53 top of projection steel was found to be 650mm lower than design
| 02SL - Stations (LUL) | Cxxx-NCR-000743 | NCR | WSME Pile 121 |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-08-22 | 2013-08-16 16:39 | -6 | 2013-07-18 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Upon inspection of WSME pile 121 at 0800 18/7/2013, it was found that the concrete poured the previous day had yet to harden. The concrete was pumped into the pile approximately 16 hours previously and it would be expected to have cured to a solid state at this point. It would appear the concrete delivered was not batched as specified. An investigation as to the root causes is ongoing.
| 02SL - Stations (LUL) | Cxxx-NCR-000751 | NCR | Non IP Rated Enclosures |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-08-21 | 2013-08-15 11:00 | -6 | 2013-07-23 | Communications and Control Systems | 500 |  | Material | Rework |  | Complete |  | Completed |  | During the night shift commencing on 22nd July the newly installed power supply unit servicing platform 5 VID was leaking water, upon further inspection / investigation it was identified that the power supply box was of a mild steel housing and not IP rated and therefore was not fit for purpose in the intended environment. Additionally no quality related certification had been provided by the Contractor to demonstrate that the intended power supply unit was fit for purpose via the materials compliance process as detailed in Section 20.7 of WI volume 2B.
| 02SL - Stations (LUL) | Cxxx-NCR-000752 | NCR | MEP - Material Compliance Records |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-08-16 | 2013-08-15 14:51 | -1 | 2013-07-26 | Electrical - LV Equipment | 500 |  | Material | Rework |  | Complete |  | Completed |  | MEP MCRs are not being submitted for works that are occuring on site
| 02SL - Stations (LUL) | Cxxx-NCR-000757 | NCR | ESS: Compressive strength testing of grout. |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-09-11 | 2013-08-12 11:44 | -30 | 2013-07-24 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | ESS: A set of 4 cubes taken instead of a set of 6 cubes for piles P1, P3, P88 and P51
| 02SL - Stations (LUL) | Cxxx-NCR-000758 | NCR | ESS: Cube test results |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-08-13 | 2013-07-31 16:03 | -13 | 2013-07-24 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | 28 day results for cubes taken for piles cast on 19/11/2012, 02/02/2013, 20/02/2013 showed individual cube results greater than 15% of the mean.
| 02SL - Stations (LUL) | Cxxx-NCR-000761 | NCR | WSME Pile 122 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2013-09-11 | 2013-08-23 15:58 | -19 | 2013-07-25 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Upon delivery the concrete was spot sampled and found to be 250mm slump, 10mm outside of specification. The decision was taken to use the concrete and retest during the pour with a composite sample. The composite slump was 240mm approximately halfway through the load, also 10mm out of specification.
| 02SL - Stations (LUL) | Cxxx-NCR-000767 | NCR | Verification of Construction Records |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2013-08-30 | 2013-08-30 11:01 | 0 | 2013-07-29 | Civil - Civil Engineering General | 500 |  | System Defect | Rework | 4 (0.5-3k) | Complete |  | Completed |  | On 16/07/13 a surveillance of the CFA piling in Whitechapel station was undertaken. A review of the verification records was carried out, it was not clear if the contractor was able to fully comply with the contract requirement in respect of collation of records. Initially the findings were referred to the __ Quality Manager and an NCR was withheld until further details were understood. From the file that that was reviewed it was not clear if this was used as an activity folder or used for construction records deliverables as identified in the ITP. It was identified that reinforcement delivery notes were held separately in the commercial department, concrete pours were recorded on the piling records and cube results held digitally in the office.
| 02SL - Stations (LUL) | Cxxx-NCR-000768 | NCR | Weld Procedures |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-08-05 | 2013-08-05 13:01 | 0 | 2013-07-29 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | The Weld documents have not been reviewed and accepted by __, nor have they been submitted to CRL for approval. __ do not have a contractor in place to review the Welding documents prior to CRL submission. The props have been manufactured.
| 02SL - Stations (LUL) | Cxxx-NCR-000769 | NCR | WSME Pile 124 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2013-09-11 | 2013-08-23 16:13 | -19 | 2013-07-30 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Upon delivery the concrete was spot sampled and found to be 250mm slump, 10mm outside of specification. The decision was taken to use the concrete due to only being marginally outside of specification.
| 02SL - Stations (LUL) | Cxxx-NCR-000776 | NCR | Low steel level of WSME pile 124 |  | Contr |  | WHI - Whitechapel Station (Central) |  | 2013-09-02 | 2013-08-07 10:26 | -26 | 2013-08-01 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The as built level of the top of steel on Pile 124 Group 15b is 432mm low thus outside tolerance.
| 02SL - Stations (LUL) | Cxxx-NCR-000781 | NCR | WSME Pile 125 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2013-09-12 | 2013-08-23 16:15 | -20 | 2013-08-01 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Upon delivery the concrete was spot sampled and found to be 245mm slump, 5mm outside of specification. The decision was taken to use the concrete due to only being marginally outside of specification.
| 02SL - Stations (LUL) | Cxxx-NCR-000786 | NCR | Pile 131 (Pile Group 9) |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2013-08-22 | 2013-08-22 17:00 | 0 | 2013-08-08 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete |  | Completed |  | Pile 131 was drilled to depth on 07/08/2013 and due to problems with the quality of concrete the pile was aborted and backfilled to above casing level to comply with SPERW.
| 02SL - Stations (LUL) | Cxxx-NCR-000789 | NCR | Pl 5 & 6 ELL Diversion Works Construction Records |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2013-09-16 | 2013-08-23 16:17 | -24 | 2013-08-08 | Electrical - Electrical Engineering General | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Prior to the LO Platform Inspection scheduled for 08-08-13 between __ & CRL (__), a review of the construction records showed there were insufficient records available to complete a full inspection.
| 02SL - Stations (LUL) | Cxxx-NCR-000792 | NCR | Pile Group 9 - GSM Piles |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2013-09-27 | 2013-09-24 17:31 | -3 | 2013-08-09 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | The pile schedule issued to the site team details a cut off level of 108.425m to which the piles have been constructed. Consquently piles P130, P131 and P133 are 550mm high. Pile 132 is 900mm high.
| 02SL - Stations (LUL) | Cxxx-NCR-000813 | NCR | Adaptable Boxes Installed Over IP-Rated Trunking |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2017-03-31 | 2017-02-13 11:55 | -46 | 2013-08-15 | Electrical - Cable Management | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 100mm adaptable boxes have been installed flush to lid-side of incomplete IP-rated trunking. Manufacturer's lid cannot be installed along the length of trunking, no supplementary seal has been applied between rear of adaptable boxes and return flange of trunking to prevent water ingress once station roof removed.
| 02SL - Stations (LUL) | Cxxx-NCR-000821 | NCR | ITP Activities proceeding without an IRF |  | Crossrail | PDP | WHI - Whitechapel Station (Central) |  | 2013-09-17 | 2013-09-17 09:46 | 0 | 2013-08-16 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Contractor has not identified the need for the inspection of activities pertaining to the installation of the prop deflector (for prop 1 at level 4), as required by the ITP (Cxxx-__M-C-ITP-D061_WS105-50010).
| 02SL - Stations (LUL) | Cxxx-NCR-000822 | NCR | CW126 Mitigation Works |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2013-09-11 | 2013-09-10 16:35 | -1 | 2013-08-28 16:24 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Cxxx-__M-C-CCN-D061-50057 SNC : Construction of mass concrete beam details the design and method of construction of a mass concrete beam to retain the Sports Centre Wall while carrying out the excavation to expose Girders 2 to 6 for the CW126 Mitigation Works western abutment. The SNC specifies the compaction of the C8/10 S1 Mix in 150 mm layers with a plate compactor. The lean mix was compacted with the 3T excavator bucket instead.
| 02SL - Stations (LUL) | Cxxx-NCR-000823 | NCR | 2No missing washers on deflector 1 hanging bracket |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2013-10-07 | 2013-10-09 15:11 | 2 | 2013-08-23 17:17 | Shafts - Shafts General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 2No bolts were drilled and set too deep into the capping beam meaning that there was insufficient thread to add both a nut and washer whilst leaving 2No threads clear as stated in the NSSS 5th edition
| 02SL - Stations (LUL) | Cxxx-NCR-000825 | NCR | Use of __ EPR grout for end plates behind props at Durward Street Shaft |  | Crossrail | PDP | WHI - Whitechapel Station (Central) |  | 2013-09-27 | 2013-09-26 09:41 | -1 | 2013-08-29 11:12 | Civil - Structural Engineering | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | The __ EPR is a three-component system that consists of a base resin, liquid hardener and an inert filler. When grouting the west end of prop 1, level 4, several of the first batches only included 2 of the three componenets, omitting the filler.
| 02SL - Stations (LUL) | Cxxx-NCR-000826 | NCR | High Density Polystyrene between diaphragm wall panel and Level 4 Prop 4 concrete node |  | Crossrail | PDP | WHI - Whitechapel Station (Central) |  | 2013-09-27 | 2013-09-26 09:10 | -1 | 2013-08-29 12:04 | Civil - Structural Engineering | 2000 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The contractor has retained the high density polystyrene, that is used to protect the couplers that protrude from the diaphragm wall, between both the diaphragm wall and Level 4 prop 4 concrete node. As a consequence, there is now a compressible material that sits between the shaft's wall and its props.
| 02SL - Stations (LUL) | Cxxx-NCR-000827 | NCR | Inclinometer IM00702 Tube Protection |  | Crossrail | PDP | WHI - Whitechapel Station (Central) |  | 2013-09-19 | 2013-09-12 09:50 | -7 | 2013-08-29 17:08 | Surveying - Instrumentation and Monitoring | 0 |  | Design | Rework | 4 (0.5-3k) | Complete |  | Completed |  | No protection provided to inclinometer number IM00702 at the surface level as shown on the attached photo.
| 02SL - Stations (LUL) | Cxxx-NCR-000828 | NCR | Non-compliant angularity of threaded bars for deflector beam 3, DSS |  | Crossrail | PDP | WHI - Whitechapel Station (Central) |  | 2013-10-11 | 2013-10-18 07:59 | 7 | 2013-08-30 18:19 | Civil - Structural Engineering | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Contractor is installing threaded rods into the vertical face of the upper level capping beam at Durward Street Shaft in order to suspend the deflector beam cradle/hanger. The bolts were identified by the project manager to be non-compliant on 29th August 2013 as they sit more than 5mm from the horizontal and requested that an NCR be raised. The Contractor proceeded to cut the protruding section of the non-compliant bolt. It should be noted that the Project Manager was not invited to inspect the Witness Point associated with anchor installation, grouting or pullout tests (ITP items 4.1, 4.2, 4.3 and 4.4).
| 02SL - Stations (LUL) | Cxxx-NCR-000829 | NCR | Non issue of IRF |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2013-09-16 | 2013-09-11 14:52 | -5 | 2013-09-02 08:28 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | IRF not issued for drilling of upper capping beam for deflector 1
| 02SL - Stations (LUL) | Cxxx-NCR-000830 | NCR | Non issue of IRF for defelctor 1 A frame |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2013-09-16 | 2013-09-11 09:22 | -5 | 2013-09-02 09:11 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | IRF not issued for erecting A frame for deflector 1
| 02SL - Stations (LUL) | Cxxx-NCR-000831 | NCR | Not raising IRF for Grouting of prop 2 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2013-09-16 | 2013-09-11 14:48 | -5 | 2013-09-02 09:14 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | IRF not issued prior to completing the grouting of end plate 2 and deflector 1
| 02SL - Stations (LUL) | Cxxx-NCR-000832 | NCR | 3No dywidag bars through concrete waler incorrectly cut |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2013-09-16 | 2013-09-16 09:59 | 0 | 2013-09-02 09:25 | Civil - Civil Engineering General | 1000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Whilst attempting to tidy the site of hazards an operative mistakenly cut 3No dywidag bars protruding from the concrete waler.
| 02SL - Stations (LUL) | Cxxx-NCR-000833 | NCR | Non Issue of IRF - DSS Defector Beam 3 Bolts Installation |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2013-09-19 | 2013-09-11 08:22 | -8 | 2013-09-05 08:27 | Civil - Excavation | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | An IRF was not issued to the FE for the installation of the bolts for deflector beam 3 by the Durward Street Shaft constructino team
| 02SL - Stations (LUL) | Cxxx-NCR-000834 | NCR | Non Issue of IRF for bolt installation of DSS Deflector Beam 4 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2013-09-19 | 2013-09-11 09:24 | -8 | 2013-09-05 08:34 | Civil - Excavation | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | IRF not issued to the FE for the installation of the bolts for Deflector Beam for by the Durward Street Construction Team.
| 02SL - Stations (LUL) | Cxxx-NCR-000836 | NCR | Concrete cubes tested at incorrect age |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2013-09-24 | 2013-09-12 10:43 | -12 | 2013-09-10 11:49 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 14 concrete samples have from mixes Line 30 & Line 31 have been assesed for compliance using one compressive strength result at 56 days, not the mean of two. No other concrete mixes are affected.
| 02SL - Stations (LUL) | Cxxx-NCR-000839 | NCR | Prop Deflector 4 - Incorrect Connection Detail |  | Crossrail | PDP | WHI - Whitechapel Station (Central) |  | 2013-10-11 | 2013-10-02 08:49 | -9 | 2013-09-12 12:28 | Civil - Structural Engineering | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Connection between deflector beam cradle and capping is not as per the approved CAT III drawing. The bearing plate should be flush with the vertical face of the capping beam.
| 02SL - Stations (LUL) | Cxxx-NCR-000843 | NCR | Durward Street Shaft - Prop Phase 1 - Damaged Bolt |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2013-10-18 | 2013-09-24 12:06 | -24 | 2013-09-17 09:29 | Civil - Civil Engineering General | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | While breaking away the concrete blinding below the Level 4 - Phase 1 prop an exposed section of bolt was bent.
| 02SL - Stations (LUL) | Cxxx-NCR-000846 | NCR | Two hoarding posts have poor contact with concrete kentledge. |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2013-10-02 | 2013-09-23 09:07 | -9 | 2013-09-18 08:59 | Civil - Civil Engineering General | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Two base plates of the SHS posts for the removable hoarding have poor contact with their associated concrete kentledge, gap under the base plate approximately 10mm. This was caused by the finishing on the concrete and the natural fall across the line of the hoarding.
| 02SL - Stations (LUL) | Cxxx-NCR-000847 | NCR | DSS HAKI B Brackets |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2013-10-24 | 2013-10-24 08:21 | 0 | 2013-09-19 08:16 | Civil - Civil Engineering General | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | Design limitation meant the HAKI B brackets couldn't located as per design, due to mass rebar within the capping beam. The location achieved meant the baring plates are too close to the edge of the capping beam, additional support to the concrete perminant works is required.
| 02SL - Stations (LUL) | Cxxx-NCR-000848 | NCR | Wrong paint used on HCDL hoarding |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2013-10-07 | 2013-09-25 17:08 | -12 | 2013-09-23 16:11 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __ was used for painting maintenance on Platform 2 hoarding. This is the incorrect paint as it has a long drying time. __ water based gloss with 1 to 2 hour drying time is required for platform hoardings as detailed in Cxxx-__M-C-GMS-D061-50091. The paint used did not dry within the engineering hours shift and the platform had to be manned until it did.
| 02SL - Stations (LUL) | Cxxx-NCR-000849 | NCR | MEP - Comms Works proceeding without a LONO in place |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2013-11-23 | 2013-09-24 17:34 | -60 | 2013-09-24 08:44 | Communications and Control Systems - CCTV | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Comms installation works being undertaken by Cxxx Sub Contractor __ were found to be taking place without a letter of no objection (LONO) in place. Further investigation revealed that key supporting documentation had not been fully approved.
| 02SL - Stations (LUL) | Cxxx-NCR-000850 | NCR | ESS Pilecap - Faliure to take site cured cubes for compressive testing |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2013-10-15 | 2013-10-14 09:12 | -1 | 2013-10-01 19:16 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the first phase of the ESS pile cap pour on the 30/9/2013, contrary to items 5.6 and 5.7 on ITP Cxxx-__M-C-ITP-D061-50030 Rev 3.0 site cured (polystyrene) early strike cubes were not taken.
| 02SL - Stations (LUL) | Cxxx-NCR-000851 | NCR | CHS - Placement of Non-approved concrete mix |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2013-10-16 | 2013-10-04 10:54 | -12 | 2013-10-02 08:36 | Shafts - Shafts General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Temporary blinding was placed using C12/15 pumpmix This mix is not currently approved by CRL.
| 02SL - Stations (LUL) | Cxxx-NCR-000852 | NCR | Loosening of shutters on ESS pour without early strike data |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2013-10-16 | 2013-10-23 08:19 | 7 | 2013-10-02 09:08 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Further to NCR-00850 raised on the 1/10/2013 due the fact that early strike cubes were not produced the shutters on the ESS pilecap pour should not have been struck until it could be verified that the concrete with the pile cap had reach 2N/mm2 as per item 5.8 in Cxxx-__M-C-ITP-D061-50030.
| 02SL - Stations (LUL) | Cxxx-NCR-000853 | NCR | Installation of WSME back blinding not to designed depth |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2013-10-17 | 2013-10-21 07:39 | 4 | 2013-10-03 09:11 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As per detail in drawing 0332A-WHITECHAPEL-C1 the required dig level for back blinding sections 1-6 (section D of the drawing is incorrect) is required to be below 108.025m. Works carried out by the nightshift crew failed to reach the required depth prior to concreting.
| 02SL - Stations (LUL) | Cxxx-NCR-000854 | NCR | CHS Lower Ring Beam Reinforcement |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2013-10-30 | 2013-10-09 17:13 | -21 | 2013-10-07 14:03 | Civil - Civil Engineering General | 1500 |  | System Defect | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | During the inspection of the reinforcement prior to Pour 4 of the Lower Ring Beam, __s Quality Inspector, John Miller, noted that the reinforcement installed was not in accordance with the specification. This led to the cancellation of the concrete pour. Following a Root Cause Analysis (see Cxxx-__M-O4-RGN-D061-50033) it was found that the Inspection and Test Plan hold point had not been followed sufficiently.
| 02SL - Stations (LUL) | Cxxx-NCR-000855 | NCR | Low pile cut off P121 and P123 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2013-11-14 | 2013-11-14 09:03 | 0 | 2013-10-10 18:11 | Civil - Civil Engineering General | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Piles 121 and 123 have been cut down too low. Due to miscommunication between the site team and surveyor the pile has been cut 75mm lower than designed.
| 02SL - Stations (LUL) | Cxxx-NCR-000856 | NCR | Incomplete concrete to Pour 4 Area of LRB |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2013-11-28 | 2013-11-27 10:25 | -1 | 2013-10-11 13:51 | Shafts - Linings | 3000 |  | Planning | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The T.O.C. within the temporary section of the Lower Ring Beam at the location of VA4 has not been completed to the design level of 87.200. The lowest area within this section is 300mm below 87.200 at a length of 4m. The permanent concrete to either side of the tunnel has been completed to the design level.
| 02SL - Stations (LUL) | Cxxx-NCR-000857 | NCR | Pour 4 Area - Incomplete Concrete Pour to Lower Ring Beam |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2013-11-28 | 2013-11-26 16:20 | -2 | 2013-10-15 08:16 | Shafts - Linings | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Further to previous NCR Cxxx-NCR-000856 and following the removal of the Ring beam shutters further repair work has been identified. A ridge of concrete at the face of the pour within the temporary area of the LRB appears to be insufficiently compacted. The affected area is 300mm deep X 2.5m long.
| 02SL - Stations (LUL) | Cxxx-NCR-000858 | NCR | __ - use of subcontractor without ISO 9001 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2013-11-29 | 2013-10-18 12:06 | -42 | 2013-10-15 14:59 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Cxxx were instructed under PMI Cxxx-PMI-00045 to complete the waterproofing to the CHS capping beam, in order to maintain warranty arrangeemnts, Cxxx used __ who were previously employed by Cxxx. Cxxx decided to continue using __ for the waterpooing of the shaft to the Lower Ring Beam. In a recent review of our subcontractors it was discivered that __ do not have ISO 9001 certification.
| 02SL - Stations (LUL) | Cxxx-NCR-000859 | NCR | Strike of stop end prior to permit to strike being issued |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2013-11-21 | 2013-11-22 14:42 | 1 | 2013-10-15 20:39 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | The stop end for pour 1 of the level 6 liner wall was struck 13 hours after the pour had been completed by the site team. The permit to strike had not yet been issued.
| 02SL - Stations (LUL) | Cxxx-NCR-000860 | NCR | Fixing stop end for pour 2 level 6 liner wall DSS |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2013-11-29 | 2013-11-28 09:28 | -1 | 2013-10-17 18:44 | Civil - Civil Engineering General | 1500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In order to attach the stop end for pour 2 of the liner wall pour at level 6 concrete was broken back to allow a flat surface for the stop end support. This meant that some of the diapraghm wall was broken out
| 02SL - Stations (LUL) | Cxxx-NCR-000861 | NCR | Early strike of stop end prior to cube results beign obtained |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2013-11-26 | 2013-11-01 15:56 | -25 | 2013-10-22 13:40 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | The stop end for pour 5 was struck at 08:45, 30 mins prior to the cube results being obtained. 2kN is required for the permit to strike procedure. The cubes obtained 3.2kN and the permit to strike was issued at 09:55
| 02SL - Stations (LUL) | Cxxx-NCR-000862 | NCR | Incorrect Steel Reinforcement Not Quarantined |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2013-11-27 | 2013-11-26 16:24 | -1 | 2013-10-23 12:29 | Structural Engineering - Reinforcement | 2500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Straight 12mm bars were delivered instead of bent links for liner wall pour 3. Steel should have been quarantined in accordance with Cxxx-N1-STP-D061-50010 Acceptance and Transfer of Supplies Rev 2.0. Steel was subsequently bent on site and installed. This was identified during a reinforcement inspection.
| 02SL - Stations (LUL) | Cxxx-NCR-000863 | NCR | Non Compliant Cable - LU/LO Enabling Works |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-10-31 | 2013-11-26 16:27 | -339 | 2013-10-31 09:13 | Communications and Control Systems - CCTV | 5000 |  | Material | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 3.5km of non-approved __ and New Generation __ cable has been installed on Platforms 1, 2, 5 &6 by the Telecomms contractor __.
| 02SL - Stations (LUL) | Cxxx-NCR-000864 | NCR | E10/E10A Non Compliant Fire Stopping |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-02-28 | 2014-02-26 14:13 | -2 | 2013-10-31 09:26 | Fire - Compartmentation | 5000 |  | Supervision/Management | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Penetrations have been made through the E10 wall and fire stopped by non FIRAS Accredited persons using a material without an MCR
| 02SL - Stations (LUL) | Cxxx-NCR-000865 | NCR | Whitechapel Sports Centre-Access Ramp - Insufficent Concrete in Base Pour 4 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2013-11-28 | 2013-11-26 16:31 | -2 | 2013-10-31 15:04 | Civil - Civil Engineering General | 2500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Insufficient Concrete for the required area. Estimated Volume insufficient. Due to the Batcher being broken down temporarily, unable to get additional concrete to finish off the concrete works. Stop End installed to finished area. Remaining area to be concreted separately.
| 02SL - Stations (LUL) | Cxxx-NCR-000866 | NCR | DSS - Level 6 Liner Wall - Pour 4 Concrete Shortage |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2013-11-29 | 2013-11-28 08:37 | -1 | 2013-11-02 16:51 | Shafts - Linings | 3000 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Level 6 Liner Wall Pour 4 was carried out on Saturday 02/11/13. 42.5m3 of Concrete were poured using a concrete pump and 6 concrete lorries. The pour was about 3 m3 short (concrete required : 45.5 m3).
| 02SL - Stations (LUL) | Cxxx-NCR-000867 | NCR | Striking Stop End for Level 6 Liner Wall Pour 4 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2013-11-27 | 2013-11-20 17:09 | -7 | 2013-11-04 16:50 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The stop end for Level 6 Liner Wall Pour 4 was struck 13 hours after the pour had been completed by the site team on Sunday 03/11. The permit to strike had not yet been issued.
| 02SL - Stations (LUL) | Cxxx-NCR-000868 | NCR | Flexible Conduit - exceedance of limitations of use |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-10-20 11:14 | 112 | 2013-11-05 11:14 | Electrical - Cable Management | 20000 |  | Material | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | __ FPR PA6 nylon flexible conduit has been installed on Platforms 5&6 but has, ijn places, exceeded its limitations of use as stated in the approval letter available on the LU APR database.
| 02SL - Stations (LUL) | Cxxx-NCR-000870 | NCR | IP Rating to Lighting Junction Boxes |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-06-01 | 2015-06-01 15:55 | 0 | 2013-11-05 11:54 | Electrical - Lighting | 10000 |  | Material | Rework | 2 (6-60k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | Incorrectly sized cable has been used running power to the lighting on Platforms 5 & 6. 4mm instead of 2.5mm cable has been installed, causing the use of Junction Boxes as the larger cable does not fit into the lighting connections. The 26 Junction Boxes installed are not IP65.
| 02SL - Stations (LUL) | Cxxx-NCR-000871 | NCR | Wrong reinforcement bar lengths DSS level 6 liner pour 7 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2013-11-27 | 2013-11-14 09:28 | -13 | 2013-11-06 16:46 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Cxxx have received 48No reinforcement bars for pour 7 of the liner at level 6 at DSS. These bars are 40mm short so have a bar length of 1885 and 1460 respectively instead of 1925 and 1500. Instead of 675 with the coupler we have 635.
| 02SL - Stations (LUL) | Cxxx-NCR-000873 | NCR | East Stair Shaft piles cast too low |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2013-12-17 | 2013-12-18 08:21 | 1 | 2013-11-20 18:07 | Geotechnical Engineering - Concrete - Bored Pile | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Top of cages of the following piles were surveyed upon pile breakdown and are summarised below: Piles type D: P57 – 140 mm low P58 – 220 mm low P60 – 280 mm low P63 – 430 mm low P64 – 190 mm low P66 – 250 mm low P72 – 310 mm low P74 – 370 mm low P76 – 500 mm low
| 02SL - Stations (LUL) | Cxxx-NCR-000874 | NCR | Lux levels to platform 1 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-02-26 | 2014-02-25 10:45 | -1 | 2013-11-22 16:26 | Electrical - Lighting | 2500 |  | Design | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | The attached LUX readings for the platform 1 lighting indicate that grid A, grids E to H, girds J to M and grids Q1 to V1 have platform nosing lux levels below the required 150lux.
| 02SL - Stations (LUL) | Cxxx-NCR-000875 | NCR | Missing Dywidag In Node 4 Waler Pour |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-01-15 | 2013-12-04 08:49 | -42 | 2013-11-27 08:40 | Civil - Civil Engineering General | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During Node 4 infill pour (DSS Shaft level 6) a problem was identified. There was a missing or misplaced sleeve inside the waler pour. Due to missing sleeve it was impossible to find a sleeve and install the dywidag as per temporary works design drawings 0283 Whitechapel C3. Instead of connecting the dywidag and installing waler plate outside of the waler, an extra waler plate was installed inside the mass infill to still work for mass infill demolition sequence. There is a dywi missing inside the waler though as per sketches attached.
| 02SL - Stations (LUL) | Cxxx-NCR-000876 | NCR | IP Rating of Trunking Installed on the Platforms for VEID Relocation |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-11-27 | 2014-10-10 15:45 | -48 | 2013-11-27 15:30 | Electrical - Cable Management | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | The trunking installed for the VEID Relocation on Platforms 5 & 6 is currently IP 54 rated. The LUL standard for external CMS is IP65.
| 02SL - Stations (LUL) | Cxxx-NCR-000877 | NCR | Bracketry & components on platforms 5&6 are not exterior grade materials |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-12-09 | 2014-12-15 08:27 | 6 | 2013-11-28 10:46 | Electrical - Cable Management | 2500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The __ pre-galv channel bracketry, BZP drop rods, BZP Nuts & BZP Flat Washer installed on the LO Platforms 05 & 06 to support the comms CMS ( VEID's Relocation ) are not suitable for an external exposed enviroment. This does not comply to LU 1-069 Clause 3.9.5.
| 02SL - Stations (LUL) | Cxxx-NCR-000879 | NCR | ARCH 8 WALER CONCRETE REPAIR - LEVEL 6 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2013-12-17 | 2013-12-17 14:18 | 0 | 2013-12-02 17:59 | Shafts - Shafts General | 2500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Due to difficulties with installation of 1no jack used to prestress the prop group 4 on level 6 approx. 40mm of concrete had to be broken to allow it's installation.
| 02SL - Stations (LUL) | Cxxx-NCR-000880 | NCR | ESS Blinding Shutter |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2013-12-19 | 2013-12-16 14:08 | -3 | 2013-12-05 08:11 | Shafts - Grouting | 1500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | White grouting the face of the East Stair Shaft piles, expanding foam used to seal the joint between the shutter and the base blinding failed, causing approximately 1m3 of grout to be lost from the shutter.
| 02SL - Stations (LUL) | Cxxx-NCR-000881 | NCR | East Stair Shaft-Pile 77 Position |  | Crossrail | PDP | WHI - Whitechapel Station (Central) |  | 2014-02-11 | 2014-02-04 11:45 | -7 | 2013-12-16 16:25 | Geotechnical Engineering - Concrete - Bored Pile | 2000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Further to the issue of Cxxx-FCD-000828, it is apparent that the Contractors temporary works design as detailed in Cat. III Cert. - East Stairs Cofferdam & Piling submitted under Cxxx-CCM-02395 did not adequately address the co-ordination with the permanent works due to the clashes identified with pile 77 and the permanent works liner wall to the East Stair Shaft. This non-conformance is raised to capture the deficiencies in the Contractors temporary works design in accordance with Works Information Volume 2B Part 22. - Where the Contractor proposes that Temporary Works are not removed and remain in the permanent works, it shall demonstrate that the inclusion of the Temporary Works in the permanent works does not compromise the Employer’s design.
| 02SL - Stations (LUL) | Cxxx-NCR-000882 | NCR | East Stair shaft backblinding |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-01-22 | 2014-01-22 15:58 | 0 | 2013-12-18 14:12 | Civil - Civil Engineering General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A section of the back-blinding, identified in the attached sketch, in the East stair shaft, was cast out of line. In the worst place, the back-blinding protrudes approx 30 mm into the liner wall.
| 02SL - Stations (LUL) | Cxxx-NCR-000883 | NCR | Concrete finishing |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-02-06 | 2014-02-04 08:35 | -2 | 2013-12-19 08:29 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following the concrete pour to the base slab of the Western Secondary Means of Escape it has become apparent that the specified finish has not been achieved. The specification calls for a plain finish.
| 02SL - Stations (LUL) | Cxxx-NCR-000884 | NCR | Honeycomb in Concrete pockets for Handrails |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-01-17 | 2014-01-20 15:20 | 3 | 2013-12-20 10:05 | Civil - Civil Engineering General | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The concrete pockets cast for the Handrail base within the Sports Centre Ramp has honeycombing due to the small size of the pockets. See attached Photo. The Pockets were vibro pokered, however due to the size of the pockets the finish achieved is not satisfactory. The concrete plinths will be “made good”
| 02SL - Stations (LUL) | Cxxx-NCR-000887 | NCR | Concrete finish to WSME plinths |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-02-21 | 2014-01-28 10:49 | -24 | 2014-01-03 16:56 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Upon striking the shutters to the WSME plinths it became apparent that the concrete finish was not up to the required specification and featured surface defects such as honeycombing.
| 02SL - Stations (LUL) | Cxxx-NCR-000888 | NCR | Western SME holding down bolts |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-01-28 | 2014-01-28 15:37 | 0 | 2014-01-07 07:50 | Civil - Civil Engineering General | 2000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following as built surveys of steel holding down bolts, it has become apparent that the HD bolts are out of position by up to 20mm. Attached for infomation are the following: A copy of the initial hand drawn survey Photographs (2nr) identifying the positon of the bolts as they should be and spraymarks highligthing the position of reinforcement around the bolts
| 02SL - Stations (LUL) | Cxxx-NCR-000889 | NCR | CHS Base Slab Waterproofing |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2014-02-05 | 2014-01-23 12:09 | -13 | 2014-01-08 09:39 | Shafts - Linings | 10000 |  | Workmanship | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Contamination | Completed |  | The __ waterproofing membrane installed at the Base Slab level of CHS did not acheive the desired standard when inspected upon completion. It was evident that standing water was present between the substrate and the membrane causing the membrane to 'bubble' and the taped joints to detach. (See attached photographs)
| 02SL - Stations (LUL) | Cxxx-NCR-000890 | NCR | Breakout to Underside of Column Pour 4 - DSS |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2014-02-25 | 2014-02-25 10:47 | 0 | 2014-01-08 13:29 | Shafts - Shafts General | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | It has become apparent during the inspection of works in Durward street shaft that breakout of concrete to to column in liner wall pour 4. Has occured. - See attached photos along with scanned drawing showing location of the column. The exact timing of the non-conformance is not clear other than it appears to have taken place during week commencing 30th December 2013.
| 02SL - Stations (LUL) | Cxxx-NCR-000891 | NCR | Concrete finish WSME/E1 pit walls |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-02-20 | 2014-02-20 15:07 | 0 | 2014-01-09 16:16 | Civil - Civil Engineering General | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Further to striking shutters for the WSME/E1 pit walls, deficiencies in the quality of the concrete finish have been discovered. in particular honeycombing and exposed repair are evident around clay duct sections cast within the wall.
| 02SL - Stations (LUL) | Cxxx-NCR-000893 | NCR | WSME Phase 3 Steelwork Installation |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-03-05 | 2014-02-17 13:32 | -16 | 2014-01-13 17:46 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the installation of the Western SME, one of the legs of the Phase 3 Steelwork was installed 5mm out of tolerance. This was the base connection of steel element H105 at the gridline intersection of G3.2/gb1
| 02SL - Stations (LUL) | Cxxx-NCR-000894 | NCR | WSME Phase 2 Steelwork Bracing Misalignment |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-03-27 | 2014-03-26 08:28 | -1 | 2014-01-13 17:57 | Civil - Civil Engineering General | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the installation of the Western SME, the brace W102 is misaligned with the connection to column K108 on gridline GB preventing the installation of the 4no bolts.
| 02SL - Stations (LUL) | Cxxx-NCR-000895 | NCR | CHS Barrette Cut-off level |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-02-24 | 2014-02-12 15:20 | -12 | 2014-01-14 18:29 | Civil - Civil Engineering General | 4000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Barrettes were to be reduced to a level of 80.405m ATD by means of hydrodemolition prior to commencing with waterproofing and base slab installation to allow installation of loose B1 bars [Refer to Cxxx-__M-C-DWG-D061_WS107-50116 for typical section] . Upon inspection after waterproofing work completion it has been discovered that the barrettes have not been sufficiently reduced to the design level.
| 02SL - Stations (LUL) | Cxxx-NCR-000897 | NCR | DSS Level 7 liner wall pour 8 incorrect alternate bar arrangement |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-02-18 | 2014-02-17 12:41 | -1 | 2014-01-15 16:40 | Civil - Civil Engineering General | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In pour 8 the links connecting the front face and back face have been placed in the incorrect alternate bar arrangement in two locations. In one location instead of 1No 16mm followed by 1No 20mm bar there has been 2No 16mm and in one other location there have been 2No 20mm links. This is shown in the attached photos. This could not be corrected without removing all the steel fixed
| 02SL - Stations (LUL) | Cxxx-NCR-000898 | NCR | Links connecting near and far face |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-01-29 | 2014-02-03 16:52 | 5 | 2014-01-15 16:49 | Civil - Civil Engineering General | 1000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Due to the heavy density of steel detailed in the liner walls it is impossible to get some of the links (12mm and 20mm) completely horizontal as shown in the drawings(attached photos highlight the issue).
| 02SL - Stations (LUL) | Cxxx-NCR-000899 | NCR | DSS Level 7 pour 8 reduced cover at southern end |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-10-30 | 2015-10-23 16:56 | -7 | 2014-01-17 09:27 | Civil - Civil Engineering General | 2500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The bent bar at the southern end of pour 8 has been set incorrectly and reduced the cover at the southern end of the pour (300mm). The diameter of the coupler has not been taken into account and therefore reduced the cover to 20-25mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000900 | NCR | WSME Temporary Anchor Bolts in W177 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-02-27 | 2014-02-17 13:36 | -10 | 2014-01-17 18:40 | Civil - Civil Engineering General | 2000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the installation of the Western SME, the temporary anchor bolts in W177 were installed to short.
| 02SL - Stations (LUL) | Cxxx-NCR-000901 | NCR | B1 Cut panels |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-02-24 | 2014-01-30 11:14 | -25 | 2014-01-21 18:32 | Shafts - Shafts General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On 2 occasions there have been panels incorrectly cut to accommodate PR wells situated inside the footprint of these - In panel B1-19 (for PRW3) and B1-30 (for PRW4) this has occurred (photos attached).
| 02SL - Stations (LUL) | Cxxx-NCR-000902 | NCR | DSS Level 7 pour 5 to pour 6 joint |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-02-20 | 2014-02-21 11:45 | 1 | 2014-01-23 12:06 | Civil - Civil Engineering General | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Due to proximity of the construction joint between Pour 5 and 6 on level 7 DSS, 2no couplers cannot have L- bars installed in the d-wall (please see photographs attached).
| 02SL - Stations (LUL) | Cxxx-NCR-000903 | NCR | Lack of lap length for DSS level 7 pour 3 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-02-07 | 2014-02-07 14:33 | 0 | 2014-01-24 16:04 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | At DSS level 7 liner wall pour 3 there is a lap length problem on the bars lapping to the coupled bars in pour 4. The L bar is required to have a minimum of 1700mm lap. As the diaphragm wall, inherited from Cxxx, is further back than anticipated and the coupled L bars setting the line must witin the wall the whole cage is 20-30mm too far back. The implication of this, is the lapping bars cannot gain sufficient lap length. (see attached sketch for clarity)
| 02SL - Stations (LUL) | Cxxx-NCR-000904 | NCR | DSS Liner 7 Pour 9.1 - low cover on the near face |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-02-24 | 2014-02-20 11:54 | -4 | 2014-01-27 10:12 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As the result of low cover on DSS Liner 7 Pour 8 - low cover on the near face, the same problem occurs on Pour 9.1 approximately up to 3m from the construction joint. Cover varies between 22-30mm there on the top of the pour. There is no possibility of further adjustment as pour 8 is already finished. This issue was raised as: Cxxx-NCR-000899.
| 02SL - Stations (LUL) | Cxxx-NCR-000905 | NCR | Steel reinforcement |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-02-10 | 2014-02-06 10:48 | -4 | 2014-01-27 17:48 | Civil - Civil Engineering General | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The reinforcement bars marked B01 and B02 on the East Stair Shaft Temporary Prop 1 have been incorrectly placed. All 16 No bars have been fixed in the correct plane and orientation however they did not conform to the spacing’s prescribed on Drawing 029 Whitechapel (C03).
| 02SL - Stations (LUL) | Cxxx-NCR-000906 | NCR | DSS Level 7 - Liner Wall Pour 7/10 CJ damaged couplers |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-02-11 | 2014-02-06 15:23 | -5 | 2014-01-28 11:20 | Civil - Civil Engineering General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the scabbling of the construction joint between Pours 7 and 10 of the Liner wall, 3no. couplers were slightly damaged (as per photo attached).
| 02SL - Stations (LUL) | Cxxx-NCR-000907 | NCR | REINFORCEMENT East Stair Shaft Landing Slab |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-02-19 | 2014-02-11 10:22 | -8 | 2014-01-30 14:02 | Civil - Civil Engineering General | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Reinforcement bars marked (26 a-d) on Drawing Cxxx-__M-C-DWG-D061-50040 were spliced contrary to the design drawing which stipulated single whole length bars.
| 02SL - Stations (LUL) | Cxxx-NCR-000908 | NCR | Reinforcement East stair Shaft Landing Slab |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-02-27 | 2014-02-20 11:57 | -7 | 2014-01-30 14:16 | Civil - Civil Engineering General | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Couplers at the end of rebar (26 a-d) were extended beyond the Construction joint indicated on Drawing Cxxx-__M-C-DWG-D061-50040.
| 02SL - Stations (LUL) | Cxxx-NCR-000909 | NCR | Construction joint East stair Shaft Landing slab |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-02-25 | 2014-02-20 11:59 | -5 | 2014-01-30 14:26 | Civil - Civil Engineering General | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Soffit level for construction joint indicated on Plan ‘A’ of drawing Cxxx-__M-C-DWG-D061-50040 was 20 mm above design level .Subsequently FL for the landing Slab step is +20mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000910 | NCR | DSS missing tie bars waler level 7 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-03-04 | 2014-02-20 15:08 | -12 | 2014-02-03 09:57 | Civil - Civil Engineering General | 1500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In 2No locations the tie bars to support the waler have been missed when constructing the liner wall. In 1No location the tie is located out of line.
| 02SL - Stations (LUL) | Cxxx-NCR-000911 | NCR | DSS Level 7 - Dywidag out of line |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-05-20 | 2014-02-20 12:20 | -89 | 2014-02-03 15:44 | Civil - Civil Engineering General | 2500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | DSS Level 7 Node 2 dywidags were installed incorrectly. Their orientation clashes with the cut line. This means after the cut will be done during demolition the block will be supported only on 1no. dywidag which considering the weight there is not acceptable.
| 02SL - Stations (LUL) | Cxxx-NCR-000912 | NCR | Offsite Manufacture of Western SME Plate Dimension |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-02-25 | 2014-02-14 11:11 | -11 | 2014-02-04 15:03 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During a dimensional check of the Western SME at __'s factory it was discovered that the end plate P161 on the bracing connector 104 was 235mm in length rather than the 239mm length specified in the work shop drawings (Cxxx-__M-C-DWG-D061-50164). The permitted deviance in the NSSS is 2mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000913 | NCR | Surface preparation for paint on flame cut edges - Western SME |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-03-18 | 2014-02-20 15:11 | -26 | 2014-02-04 15:58 | Civil - Civil Engineering General | 2000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During a PTS inspection of the Western SME offsite manufacture it was noticed that the paint system had been applied to an incorrect steel surface profile on the flame cut edges of 2no P192 on element H105 from workshop drawings Cxxx-__M-C-DWG-D061-50164. The painting process was stopped and International Paint was contacted.
| 02SL - Stations (LUL) | Cxxx-NCR-000914 | NCR | East Stair Shaft landing slab reinforcement - modified arrangement |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-03-11 | 2014-03-06 14:39 | -5 | 2014-02-06 12:39 | Structural Engineering - Reinforcement | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | To comply with the approved construction sequence of the East Stair Shaft, recorded in Cat III check certificate Cxxx-__M-C-CER-D061-50114, an additional construction joint was agreed on via Cxxx-RFI-001281 and introduced at the interface between the lift shaft and landing slab. Due to the complex location of this joint (which interfaces with the lift shaft walls W2/W3 and the landing slab wall W1), 1 reinforcement bar, indicated by bar mark 41 NF2 on drawing Cxxx-__M-C-DWG-D061-50041 and highlighted on attached drawing was not installed as indicated (i.e. fixed during concrete pour of the landing slab).
| 02SL - Stations (LUL) | Cxxx-NCR-000915 | NCR | DSS missing tie behind node 4 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-06-07 | 2014-02-11 17:05 | -116 | 2014-02-07 09:13 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There has been 1No dywidag bar missed when installing the concrete waler. The tie protrudes from the liner wall but does not go through the waler
| 02SL - Stations (LUL) | Cxxx-NCR-000916 | NCR | DSS Waler level 7 - cover issues |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-03-11 | 2014-02-13 10:00 | -26 | 2014-02-11 12:36 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There are areas with too low and to high cover in relation to tolerance given by TWD on Whitechapel 282 C4 drawing. Please see attached 282 drawing indicating problematic areas.
| 02SL - Stations (LUL) | Cxxx-NCR-000917 | NCR | East Stair Shaft Liner Wall - Reinforcement bars omitted |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-02-26 | 2014-02-20 15:13 | -6 | 2014-02-12 12:53 | Structural Engineering - Reinforcement | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Bars marked 708 on Section 5-5 drawing Cxxx-__M-C-DWG-D061-50041 were omitted from the pour. A section of the pile cap (in the North side of ESS where Wall W2 interfaces with Wall 1 along Gridline ESA) was poured incorrectly (see attached marked up drawing for location). Therefore the south face of the pile cap interferes with the steelwork for liner wall W2 below.
| 02SL - Stations (LUL) | Cxxx-NCR-000918 | NCR | DSS prop end plates to be redriled |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-03-05 | 2014-02-21 16:17 | -12 | 2014-02-12 16:20 | Civil - Civil Engineering General | 2500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Error by manufacturer in shipping or marking | Completed |  | Due to small discrepancies within the end plates the welded studs are clashing with plate and not going through the designed opening
| 02SL - Stations (LUL) | Cxxx-NCR-000919 | NCR | Deviation from In-situ concrete specifications for ESS circular liner wall kicker |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-03-20 | 2014-02-17 15:37 | -31 | 2014-02-13 12:53 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The concrete pour for the circular liner wall on top of the intermediate landing slab (identified on drawing Cxxx-__M-C-DWG-D061-50042) was not covered with thermal blankets as stipulated in the approved Concrete Curing specifications, Cxxx-__M-C-GPD-D061-50003.
| 02SL - Stations (LUL) | Cxxx-NCR-000920 | NCR | CW126 Deck Extension Footings |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-03-04 | 2014-02-20 12:31 | -12 | 2014-02-13 15:35 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Deck Extension Footing Works: The western edge of the Eastern Footing for the deck extension is 15-20mm east of its proposed position. This results in an average thickness of 435mm instead of 450mm. The hold down bolts have been cast in the correct location and not in the centre of the footing.
| 02SL - Stations (LUL) | Cxxx-NCR-000921 | NCR | CW126 Deck Extension |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-02-27 | 2014-02-17 12:33 | -10 | 2014-02-13 15:35 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Width of blinding to the west abutment varies in dimension in the range of 1005mm, 964mm and 984mm which does not match what is shown on drawing number SUA/20000091/0003/032 C3 which states the width of the blinding to be 1050mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000922 | NCR | Damaged locating studs for prop set 3 level 7 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-03-25 | 2014-02-25 11:30 | -28 | 2014-02-14 15:36 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the installation of the prop highlighted in the sketch, DAM were trying to level and centre the prop and caused the locating studs welds to crack.
| 02SL - Stations (LUL) | Cxxx-NCR-000923 | NCR | __ SME Steelwork Surveillance Report |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2014-04-24 | 2014-04-02 13:00 | -22 | 2014-02-17 17:03 | Structural Engineering - Surface Treatment | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Further to the submission of the __ Western SME Fabrication-Paint Process Surveillance Report reference Cxxx-__M-O4-RGN-D061-50048 received under CCM-04683 on 31st January 2014, the Project Manager is concerned by the findings identified by the Contractors Inspector (PTS) during a random surveillance exercise. The findings detailed in the surveillance report should have been raised (notified) to the Project Manager in a timely manner. WI Volume 2B Part 20.8 states the following: 'Where a specified work activity has not been carried out in accordance with agreed procedural requirements, a NCR is raised. Unless otherwise accepted by the Supervisor, the Contractor shall enter each NCR, including sub-contractor NCR's in the PTR system.' - This did not happen.
| 02SL - Stations (LUL) | Cxxx-NCR-000924 | NCR | CHS base slab drainage - incorrect pipework level |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-02-25 | 2014-02-21 15:15 | -4 | 2014-02-18 14:05 | Civil - Drainage | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The pipework has been installed for the CHS base slab drainage network. The Fire Drain 1 pipe into the sump has been installed with the invert level at the sump = 81.140m ATD. This is 160mm low and increases the fall on the pipe to approx 1:20 (design is 1:35).
| 02SL - Stations (LUL) | Cxxx-NCR-000925 | NCR | Painting area not segregated from blasting area for Western SME |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-04-02 | 2014-04-03 08:11 | 1 | 2014-02-19 15:55 | Civil - Civil Engineering General | 2500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In __ shop in __ : Spraying carried out whilst open shot blasting was being carried out in the close vicinity. No control of the potential dust in the air.
| 02SL - Stations (LUL) | Cxxx-NCR-000926 | NCR | DSS TC2 Piling - Procedural errors during cage installation |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-03-26 | 2014-02-25 10:49 | -29 | 2014-02-19 15:56 | Civil - Civil Engineering General | 1000 |  | Planning | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | During pile number 29 installation process cage was installed without CRL inspection disregarding the ITP witness requirement. CRL Field Engineer was informed the inspection is required for 1500, but subcontractor carried on and cage was installed before that time. Cage installation started @1430 and finished @1500, when CRL Inspector arrived on site and witnessed just the end of installation.
| 02SL - Stations (LUL) | Cxxx-NCR-000927 | NCR | DSS TC2 piling - Pile 33 tremie pipe problem |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-03-12 | 2014-02-20 16:10 | -20 | 2014-02-19 16:25 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During concreting of Pile 33 tremie pipe could not reach the required depth and concrete was poured from the drop higher than 10m. This can cause aggregate segregation in the worst case scenario. The reason tremie pipe could not go down was the method of splicing the cage used at depth 8.140m causing a "bottle neck effect". Cage could not be retrieved to fix the problem.
| 02SL - Stations (LUL) | Cxxx-NCR-000928 | NCR | Deck Extension Positioning Cones for the Pre-Cast Concrete Slabs |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-03-18 | 2014-03-06 17:05 | -12 | 2014-02-24 14:12 | Civil - Civil Engineering General | 1000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The incorrect positioning cones were percured. The design stated a 15F 3073 positioning cone to be used, instead a 15F 3037 cone has been used. The 15F 3073 cone is secured by threaded bar, but the 15F 3037 is secured by dwyidag bar.
| 02SL - Stations (LUL) | Cxxx-NCR-000930 | NCR | Document Control |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2014-06-18 | 2014-06-11 12:55 | -7 | 2014-02-28 09:17 | Electrical - Electrical Engineering General | 1500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | 6 Findings with respect to document control • The Design Management Plan was not current • Acceptance Status of 2 Design Statements were not identifiable • Design Interface Management Plan partially filed under 2 different locations in eB • Interface Management Matrix & Minutes of Meeting issued with omissions • A superseded version of Works Information volume 2B tabled • The PMI Baseline Standards Document was not available
| 02SL - Stations (LUL) | Cxxx-NCR-000931 | NCR | Quality Support Procedure for Administration of Design |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2014-04-30 | 2014-04-28 08:46 | -2 | 2014-02-28 09:19 | Electrical - Electrical Engineering General | 1000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | 1 Finding with respect of no comprehensive quality support procedure for administration of design.
| 02SL - Stations (LUL) | Cxxx-NCR-000932 | NCR | Design Without an Accepted Design Statement |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2014-04-30 | 2014-04-28 08:50 | -2 | 2014-02-28 09:20 | Mechanical - Mechanical Engineering General | 1000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | 1 Finding for continuing with the design whist the design statement had not been accepted by the Project Manager
| 02SL - Stations (LUL) | Cxxx-NCR-000933 | NCR | Interface Control Document production timetable |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2014-04-30 | 2014-04-28 08:50 | -2 | 2014-02-28 09:23 | Mechanical - Mechanical Engineering General | 1000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | 1 Finding for no clear Interface Control Document production timetable
| 02SL - Stations (LUL) | Cxxx-NCR-000934 | NCR | Baseline Standards & Clause 8.2.1 of ISO 9001 (Customer Satisfaction) |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2014-04-30 | 2014-04-28 08:45 | -2 | 2014-02-28 09:24 | Mechanical - Mechanical Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | 1 Finding for no evidence to demonstrate ISO 9001 clause 8.2.1 ( Customer Satisfaction) implementation with respect of WI Vol 2B part 7.3 Contractors Design Duties that refer to Presentations)
| 02SL - Stations (LUL) | Cxxx-NCR-000935 | NCR | omission of MEP supports to permanent structure from 3D modelling |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2014-04-30 | 2014-04-28 08:52 | -2 | 2014-02-28 14:10 | Mechanical - Mechanical Engineering General | 1000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | 1 Finding for omission of MEP supports to permanent structure from 3D modelling 3D modelling of the GSM building was presented and reviewed during the visit The Contractor confirmed during the 3D presentation that the absence of details of supports for the MEP installations was in accordance with CRL requirements. This was checked post visit and found to be incorrect. CRL confirmation of MEP stage F design activities required before Gate 3 based on BSRIA Pro-forma 5a BG6/2012 requires bases, supports and structurally significant holes to be shown on 3D Model. Refer to technical requirements in this NCR.
| 02SL - Stations (LUL) | Cxxx-NCR-000936 | NCR | East Stair Shaft Temporary Access Bridge |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-04-09 | 2014-03-14 12:33 | -26 | 2014-02-28 10:11 | Structural Engineering - Bolted Connections | 2000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During installation of the East Stair Shaft Temporary Access bridge 1No. of the RMD baseplate propbolt connections has not achieved full embedment as per approved temporary works design Cxxx-__M-C-CER-D061-50159. The baseplate is the one installed in the North East Corner of the East Stair Shaft. 94mm embedment has been achieved instead of the manufacturers required 100mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000937 | NCR | Proceeding with Works without approved MCRs |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-04-14 | 2014-04-11 13:14 | -3 | 2014-02-28 17:31 | Electrical - LV Equipment | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | MCR for the __ Sockets installed during the possession dated 22/23 Feb 2014 has not been submitted to CRL for acceptance
| 02SL - Stations (LUL) | Cxxx-NCR-000938 | NCR | Proceeding with Works without approved MCRs |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-04-22 | 2014-04-26 07:46 | 4 | 2014-03-03 09:47 | Fire - Suppression | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | MCR for the Dry __ Hydrants installed during the possession dated 22/23 Feb 2014 has not been submitted to CRL for acceptance
| 02SL - Stations (LUL) | Cxxx-NCR-000939 | NCR | Proceeding with Works without an approved ITP |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-04-17 | 2014-03-05 12:07 | -43 | 2014-03-03 08:59 | Electrical - Electrical Engineering General | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | Cxxx-__M-E-ITP-D061-50017 Rev 2.0 was not submitted in advance of the Burnell FAT Test. This ITP was the controlling docuemnt. Rev 1.0 was at Code 1 but did not provide sufficient controls for the works it covered.
| 02SL - Stations (LUL) | Cxxx-NCR-000940 | NCR | Appointment of a Non ISO 9001 Certified Company |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-04-14 | 2014-04-09 07:33 | -5 | 2014-02-28 17:52 | Electrical - Switchgear | 2000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | __ have been employed to provide panels for the E51/E510A works but are not ISO 9001 certified.
| 02SL - Stations (LUL) | Cxxx-NCR-000941 | NCR | Proceeding with Works without approved MCRs |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-04-14 | 2014-04-09 07:37 | -5 | 2014-02-28 17:58 | Electrical - Switchgear | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | MCR for__ Panels has not been submitted to CRL for acceptance, but procurement has taken place
| 02SL - Stations (LUL) | Cxxx-NCR-000942 | NCR | CHS Base Slab - Top mat reinforcement levels |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-03-25 | 2014-03-26 08:27 | 1 | 2014-03-03 10:50 | Shafts - Shafts General | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The top mat of the base slab reinforcement has been installed with the level averaging 82.325mm ATD. This is 40mm lower than the design level and would give approx 115mm cover.
| 02SL - Stations (LUL) | Cxxx-NCR-000943 | NCR | Contractors Design Assurance |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2014-06-11 | 2014-06-11 16:08 | 0 | 2014-03-04 17:14 | Civil - Civil Engineering General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | The Contractor failed to implement an element of permanent works for the CHS base slab derived from an approved Contractor design (Issue For Construction) in accordance with the Contractors Design Management Process. This relates specifically to the Earthing and Bonding of CHS shaft.
| 02SL - Stations (LUL) | Cxxx-NCR-000945 | NCR | TC2 Piling Concrete - Out of Tolerance Concrete Used for Pile P177 |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2014-04-23 | 2014-04-03 16:32 | -20 | 2014-03-06 14:57 | Geotechnical Engineering - Concrete - Bored Pile | 2500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | TC2 bored pile concrete placed for pile number P177 despite the concrete not meeting the requirements of the ITP document number Cxxx-C-ITP-D061-50095 Rev 3.0 for the approved mix design. The ITP inspection number 6.2 under control document and clause KF11.2200 (BS EN 206-1:2000) states that the approved mix design for the TC2 piling allows for a class S4, which when tested is to achieve a slump of between 150mm - 230mm. The NCR is specific to the first concrete load used for pile P177, which when tested on site on two separate occasions exceeded the testing parameters of the ITP for class S4 and produced a slump of 256mm and 250mm respectively. The decision was taken on site by Cxxx to place the concrete for pile P177 despite the concrete not meeting the requirements of the ITP.
| 02SL - Stations (LUL) | Cxxx-NCR-000946 | NCR | CHS Lower Liner Wall Starters without A12 couplers |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-04-23 | 2014-03-27 15:55 | -27 | 2014-03-06 15:36 | Shafts - Shafts General | 5000 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | There are 25no liner wall starters panels 22 through 24 (13no bm08 and 12no bm09 from __ 50104) without threaded ends or A12 couplers. The bars installed with the correct embedments but would only provide a lap of approx 300mm if spliced.
| 02SL - Stations (LUL) | Cxxx-NCR-000947 | NCR | CHS Base Slab - W8-03NS Starter bars instead of A12 couplers |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-03-20 | 2014-03-11 16:26 | -9 | 2014-03-06 15:54 | Shafts - Shafts General | 2500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | For the Non-structural wall W8-03NS we have installed starter bars instead of the bars with A12 couplers at base slab level (80.440m ATD) specified in __ 50070. The bar lengths are 2.0m, with 1.05m embedded. The wall is not within a starter free zone as shown on drawing 50070.
| 02SL - Stations (LUL) | Cxxx-NCR-000949 | NCR | GSM Weld Procedure |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-04-05 | 2014-03-10 09:39 | -26 | 2014-03-06 21:26 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | The __ Weld Procedures for the GSM were not approved prior to the start of fabrication. The WPS for the WMSE is at Code 1, there have been no additional WPS requirements introduced with this section of construction.
| 02SL - Stations (LUL) | Cxxx-NCR-000950 | NCR | Use of non approved materials - earthing |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-05-05 | 2014-04-26 07:50 | -9 | 2014-03-06 22:08 | Electrical - Electrical Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The materials used in the earthing installation ahead of the base slab pour in CHS were not approved prior to installation.
| 02SL - Stations (LUL) | Cxxx-NCR-000951 | NCR | Works proceeding without an ITP in place |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-04-05 | 2014-04-07 08:20 | 2 | 2014-03-06 22:15 | Electrical - Electrical Engineering General | 5000 |  | System Defect | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There was no approved earthing ITP in place prior to the earthing activities undertaken ahead of the CHS base slab pour.
| 02SL - Stations (LUL) | Cxxx-NCR-000953 | NCR | TC2 Pile 173 & pile 21 out of tolerance |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-03-25 | 2014-03-24 11:53 | -1 | 2014-03-07 14:59 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | ITP numberCxxx-__M-C-ITP-D061-50095_Rev 3.0. Section 4.1, States the tolerance for piles positions to be within 75mm. The difference between the designed positions and as-built positions for piles 173 + 21 are both 77mm. this is 2mm out of tolerance.
| 02SL - Stations (LUL) | Cxxx-NCR-000954 | NCR | CHS Earthing - Works Constructed without Design Acceptance |  | Crossrail | PDP | WHI - Whitechapel Station (Central) |  | 2014-07-15 | 2014-07-21 08:22 | 6 | 2014-03-09 23:56 | Electrical - Electrical Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Elements of the earthing and bonding system cast into the Lower Ring Beam and Base Slab at CHS have not been assured at at a Design Gate 3 review and no Project Manager's Acceptance was obtained. No design submission and Gate 3 submission had been made for the cast-in elements in the Lower Ring Beam, the Mini-Gate 3 submission for that in the Base Slab (via CCM-05099 dated 28th February 2014) has been found inadequate and deemed not assured. Works Information Vol 2B 7.7.8 Acceptance of Design process has not been followed.
| 02SL - Stations (LUL) | Cxxx-NCR-000955 | NCR | CHS Earthing - Missing Earth Electrode Diaphragm Wall Connections |  | Crossrail | PDP | WHI - Whitechapel Station (Central) |  | 2014-07-15 | 2014-07-21 08:23 | 6 | 2014-03-09 23:56 | Electrical - Electrical Engineering General | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Earth electrode connections to diaphragm wall panels 3, 7, 24 and 30 are missing in the Lower Ring Beam at CHS (as indicated in RFI-000938 and 001221).
| 02SL - Stations (LUL) | Cxxx-NCR-000956 | NCR | DSS - Damage to Piezometer Cable |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-05-20 | 2014-05-20 12:41 | 0 | 2014-03-13 11:25 | Surveying - Geotechnical Surveys | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 11/03/14, Piezometer PV4 stopped producing monitoring information. 12/03/14, Piezometer PV3 2 nunmber of 4 sensors stopped producing monitiring information All other sensors are producing readings. The readings indicate the water table poses no immediate significant issues.
| 02SL - Stations (LUL) | Cxxx-NCR-000957 | NCR | Damaged East Stair Shaft Pile |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-04-29 | 2014-04-24 09:03 | -5 | 2014-03-13 17:28 | Geotechnical Engineering - Concrete - Bored Pile | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Type A Pile 2 on the attached Drawing 0251-Whitechapel –C3 has been damaged by the excavator bucket while undertaking the second stage of the ESS excavation. The damage is limited and reinforcement has not been exposed.
| 02SL - Stations (LUL) | Cxxx-NCR-000958 | NCR | Clash between GSM roof plate stiffener and lift shaft trimming steel |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-05-30 | 2014-05-28 15:32 | -2 | 2014-03-17 03:51 | Civil - Civil Engineering General | 1000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the installation of the GSM steelwork roof plates it was found that there was a clash betwen the roof plate stiffener and the lift shaft trimming steel on plates V1005 and V1013. To install the plates a section of the stiffener was removed, see photo attached. The cut edges will be touched up with the paint system.
| 02SL - Stations (LUL) | Cxxx-NCR-000959 | NCR | TC2: Breaking out of piles - Piles: 33; 37; 113; 189 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-04-02 | 2014-04-08 11:26 | 6 | 2014-03-19 23:08 | Geotechnical Engineering - Concrete - Bored Pile | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During pile cropping activities the concrete around 4no. Piles was chipped off at an angle reaching to a depth of approximately 200mm below design cut off level. Pile cropping was with hand breakers - not the jack hammer attachment of the excavator. Piles affected by the works are: 33, 37, 113, 189. Photo's are attached.
| 02SL - Stations (LUL) | Cxxx-NCR-000961 | NCR | CHS Base Slab - As-Built Top of Slab Levels |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-04-16 | 2014-04-16 14:38 | 0 | 2014-03-24 15:51 | Shafts - Shafts General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please find attached a sketch illustrating deviations on the top of slab levels from the design level (82.440 ATD). The maximum deviation is -32mm. This provides a cover to steel of 43mm in this local area.
| 02SL - Stations (LUL) | Cxxx-NCR-000962 | NCR | Void discovered in East Stair Shaft Pile |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-04-23 | 2014-04-09 07:38 | -14 | 2014-03-25 15:39 | Geotechnical Engineering - Concrete - Bored Pile | 1500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | It was proposed via Cxxx-RFI-000643 that the suitable method for determining the integrity of the piles was an inspection of the piles after excavation to formation level. Upon inspection of the East Stair Shaft piles, it was discovered that Pile No 85 indicated on the attached Drawing 0251-Whitechapel–C3 features a void. The __ TWC inspected the pile to assess its structural integrity and recommended the remedial actions below. Please also find attached pictures showing the location and dimensions of this void.
| 02SL - Stations (LUL) | Cxxx-NCR-000964 | NCR | GSM Steelwork Roof Non Installation of Bolts |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-05-21 | 2014-05-20 12:27 | -1 | 2014-03-27 18:53 | Civil - Civil Engineering General | 1500 |  | Equipment Breakdown | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A total of 48no countersunk bolts could not be installed on the GSM roof to connect the roof plate due to clashed with beam end plates and where drill bits have snapped in the holes. Locations shown in attached marked up drawing.
| 02SL - Stations (LUL) | Cxxx-NCR-000965 | NCR | CHS Lower Liner Wall - cut rebar between Pour 1 & Pour 3 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-04-29 | 2014-04-28 07:59 | -1 | 2014-04-08 16:55 | Shafts - Linings | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During installation of stop ends for Pour 1 of the Lower Liner Wall, an existing length of rebar was cut out to allow installation of the stopend between Pour 1 and 3.
| 02SL - Stations (LUL) | Cxxx-NCR-000966 | NCR | DSS L8 Barettes P45, P46 & P51 Lapped L-bars |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-04-09 | 2014-04-10 07:57 | 1 | 2014-04-08 16:48 | Shafts - Shafts General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | This NCR has been discussed and agreed with Cxxx(AW) and Cxxx(KK) on 07/04/2014 prior to raising. In the central pour there are 3no “Type C” barrettes which are either wholly or partially within the recess. As shown on drawing Cxxx-__M-C-DWG-D061_WS105-50196-C01, these barrettes have L-bars lapping with the existing tall vertical barrette bars installed by Cxxx. These L-bars should sit within either RT5 or RT6, depending on their orientation (bar marks 516 and 511 on drawing 50196 which shows P51, P45 & P46 are similar). These L-bars weren’t installed in the correct sequence. Bar marks 511/451/461 should have been installed following installation of RT6, before RT5 was installed and bar mark 516/456/466 should have been installed after RT5 but before T6 mats were installed. It was identified during the installation of T3 mats that these L-bars were missing. As such they have been installed form beneath the RT and T mats. In most cases they were installed in the correct layers (RT5 or RT6) but in some cases this wasn’t possible. In these cases the L-bars were installed in RT8 at the same level as the coupled L-bars (bar marks 512/452/462). The attached sketch “As Built sketch of lapped L-bar layers.pdf” shows the level of the installed lapped L-bars. On the plans, the high couplers which lap with the L-bars in question have been highlighted. Green indicates that the L-bar was installed within the design layer. Pink indicates that the L-bar was installed lower than the design layer, in which case the layer that the bar is installed in has been given. Note: where no highlighting is provided the bar is not affected, the L-bars will be installed in T layers.
| 02SL - Stations (LUL) | Cxxx-NCR-000967 | NCR | Cover |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-05-13 | 2014-05-07 11:23 | -6 | 2014-04-08 22:31 | Structural Engineering - Reinforcement | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The piles and their cap had to be built/installed at an awkward position to avoid a clash with existing piles. One corner of the proposed pile cap (including concrete cover) was 139mm away from an existing pile cap (west run pile cap). Due to the thickness of the formwork it was not possible to maintain the 75mm concrete cover at this corner – unless a vertical groove was cut into the existing west run pile cap in order to facilitate the formwork panels. Instead of cutting into the west run pile cap, the formwork panels were assembled as close and tight as possible to the design position, but the shuttering at the corner of concern was approx. 20-30mm short of the mark. As a result a small side wall section of the area of concern has 45mm concrete cover (at shallowest). This has caused the other sides to have cover of up to 95mm max. The top of the pile mat was to have 50mm concrete cover. The cover on top has been uniformly increased to 85mm. This is to allow the concrete to cover up to the 400mm below top of crane anchor mark.
| 02SL - Stations (LUL) | Cxxx-NCR-000968 | NCR | East stair Shaft linerwall reinforcement misallignment |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-05-20 | 2014-05-20 16:05 | 0 | 2014-04-29 12:01 | Civil - Geotechnical Engineering | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 1: 7No Bar mk 102 in the East stair shaft on Drawing Cxxx-__M-C-DWG-D061-50043 do not line up with corresponding rebar marked 102 as required to create a splice. This occurred in a few isolated locations on Wall "W3". It was advised by CRL ref Cxxx-FCD-00847 to bend the affected bars around the clashing piles. This was implemented and successful with all the horizontal reinforcement and most of the vertical reinforcement except for the 7 No bars. The location of these bars is shown on the attached sketch. 2: 3No Bars marked 704 were omitted from the preceding base slab pour in the North west corner of liner wall "W2B". These were additional bars as shown on section 13-13 of the attached sketch.
| 02SL - Stations (LUL) | Cxxx-NCR-000969 | NCR | East Stair shaft pile clash with liner wall |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-09-28 | 2018-10-26 09:56 | 28 | 2018-04-23 07:45 | Civil - Sub-base | 2000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The reverse blinding for the liner walls in the ESS projects into the liner wall in several locations. This is due to the temporary piles projecting into the back of the liner wall as shown in the attached as-built pile drawing.
| 02SL - Stations (LUL) | Cxxx-NCR-000970 | NCR | DSS L8 Central Pour - Welding Panel Spacing Tolerance |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-05-28 | 2014-04-15 10:57 | -43 | 2014-04-14 15:54 | Shafts - Shafts General | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During installation of the panels in the central pour, it has been identified that some bars within the panel have been welded out of tolerance. Attached are photos showing the western two bars of panel B3-19.2 which are at centres of 140mm rather than 150mm. This may cause difficulties when installing the ajoining mats in the north pour, resulting in cutting of rider bars to enable installation.
| 02SL - Stations (LUL) | Cxxx-NCR-000971 | NCR | DSS L8 Liner Wall FF Damaged Coupler |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-06-30 | 2014-05-30 11:00 | -31 | 2014-04-22 10:44 | Shafts - Shafts General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | This NCR has been discussed with Alex Woo (Cxxx) prior to raising. When installing base slab reiforcement in the central pour, it was identified that a coupler in the L7 Liner wall is damaged. A FF liner wall bar extending into the base slab pour should have been fitted into this coupler but couldn't be installed. See attached photos.
| 02SL - Stations (LUL) | Cxxx-NCR-000972 | NCR | DSS L8 Base Slab - bar set back from recess |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-06-17 | 2014-04-24 09:07 | -54 | 2014-04-22 11:01 | Shafts - Shafts General | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the pre-pour inspection for the central pour of the DSS base slab it was identified that in layer B3 bar mark 966 was installed approximately 50mm back from the recess stop end.
| 02SL - Stations (LUL) | Cxxx-NCR-000974 | NCR | Impact Board E510A |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-06-24 | 2014-06-09 12:48 | -15 | 2014-04-15 16:59 | Fire - Compartmentation | 2500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Outer impact board on E510A was cut due to an existing PA/VA conduit clash.
| 02SL - Stations (LUL) | Cxxx-NCR-000975 | NCR | DSS __ lap from north pour to central pour |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-05-28 | 2014-05-07 11:39 | -21 | 2014-04-16 12:28 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The __ in the north section of the shaft was joined to the serviseal on the northern slab construction joint with Bituthene LM. This was deemed not acceptable and rework was required.
| 02SL - Stations (LUL) | Cxxx-NCR-000976 | NCR | TTH Drainage and Ductwork Installation |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-07-01 | 2014-06-30 08:47 | -1 | 2014-04-22 15:27 | Civil - Utilities Engineering | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | RWP3 (Rain Water Pipe) is 127mm out of correct position. Survey and checks made prior to pouring the raft foundation showed that this pipe was in the correct position. However, as built survey post foundation pour, indicate that the pipe is 127mm out of position. It is likely that during the pouring of the raft foundation, the pipe was knocked out of alignment. A length of rigiduct, installed to carry a cable for a totem located on the Eastern edge of the TTH is 1289mm out of position. The setting out position was originally checked and signed off. However, once blinding was poured, the peg holding the duct in position was removed and the duct sunk in to the blinding, resulting in it being in the wrong location.
| 02SL - Stations (LUL) | Cxxx-NCR-000977 | NCR | DSS L8 B3-10 Panel |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-05-21 | 2014-05-14 10:56 | -7 | 2014-04-28 13:54 | Shafts - Shafts General | 1000 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | This NCR is raised following response to FCD-00846. During installation of panel B3-10 it was found that it has been fabricated incorrectly. The attached sketch shows the problem. Rather than alternating the 4no. “long” (bar mark 313a) and 4no. “medium” length bars (bar mark 113b) as shown on drg 50154, the bars have been welded as shown in the attached sketch “B3-10 Fabrication Error” which shows all the long bars, then the medium bars, then the short bars welded side by side. To resolve this, the 2no. bars that are too short were extended to the correct length with B40 bars lapping the welded "short" bars by a 2300mm (minimum required lao was 2240mm). The bars that are too long were left as they are. See attached sketch "B3-10 Solution".
| 02SL - Stations (LUL) | Cxxx-NCR-000978 | NCR | CHS - Formation of Voids between bottom of Upper Ring Beam and top of MIDDLE LEVEL LINER WALL |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-08-29 | 2014-08-28 09:10 | -1 | 2014-04-25 18:06 | Shafts - Linings | 2500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following the completion of the second scheduled pour (Area 3) which is located between EP2 and VA4 and adjacent to EP2, the concrete has not completely filled the space between the ring beams. Sections of the Middle Liner Wall Concrete have not reached the Upper Ring Beam therefore resulting in formation of fissures aprroxamateley 1m long and 4mm wide. See the attached photos.
| 02SL - Stations (LUL) | Cxxx-NCR-000980 | NCR | Construction without IFC Drawings in place - DSS Base Slab |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-06-10 | 2014-06-06 14:01 | -4 | 2014-05-02 09:37 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | DSS Level 8 Base Slab reinforcement installation has proceeded without IFC (C01) drawings in place. This has occurred in relation to the following. 1. Reinforcement chairs between the top layers at the recess (Cxxx-__M-C-DWG-D061_WS105-50233) 2. T4 layer (Cxxx-__M-C-DWG-D061_WS105-50180)
| 02SL - Stations (LUL) | Cxxx-NCR-000981 | NCR | CHS Level 8 Column and Wall Kicker Positions |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-05-27 | 2014-05-20 14:35 | -7 | 2014-05-02 12:17 | Shafts - Shafts General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | An as-built survey has been undertaken to confirm positions of the wall/column kickers cast as part of thr CHS base slab pour. It has identifed 2no columns that have been installed out of positional tolerance (+-10mm as per NSCS Cl 10.5.1). Deviations are: C8-47 eastern side, max 30mm C8-10 eastern side, max 20mm Please find attached the as-built survey diagram, including these columns
| 02SL - Stations (LUL) | Cxxx-NCR-000982 | NCR | TTH Pile P4 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-06-04 | 2014-06-04 08:54 | 0 | 2014-05-02 16:58 | Civil - Structural Engineering | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Pile design for TTH piles are 4No 450mm diamter piles with 300mm Cages and 400mm Thin-Walled Steel Liners. The Thin-Walled liners were coming out with the cases as they were extracted. The only way to extract the casings was to cut 3m off the liner and extract it first. Once the liner was extracted, the remaining cages were extracted and the liner was reinstalled. As 3m was cut off, only 4m of the 7m liner was installed in the pile. Also during the extracting of the liner concrete was pulled form the pile. On installation of the liner to 4m, the level of the concrete was approximately 300mm below cut off level.
| 02SL - Stations (LUL) | Cxxx-NCR-000983 | NCR | TTH Steelwork Fabrication without Approved Offsite ITP |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-05-16 | 2014-05-07 11:45 | -9 | 2014-05-02 18:45 | Civil - Civil Engineering General | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | The offsite ITP for the fabrication of the steelwork had not achieved code 1 or 2 status before fabrication works on the TTH commenced. The ITP did achieve Code 1 status during the fabrication process. Independent quality audit by __, CRL and PTS confirmed that the ITP process was being followed.
| 02SL - Stations (LUL) | Cxxx-NCR-000984 | NCR | TTH Fabricating Steelwork without Approved Weld Procedure Review |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-05-16 | 2014-05-07 11:53 | -9 | 2014-05-02 18:59 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Fabrication of the TTH commenced without Code 1 status on the weld procedure review document. Weld procedures used Subsubcontractor Oostingh were the same as the __ weld procedures used on the WSME and GSM to date which are approved. PTS have conducted a review of the TTH welds against __'s weld procedures and confirmed compliance. A quality audit in Holland workshop of Oostingh by __, CRL and PTS confirmed welder qualifications were in compliance with __'s weld procedures.
| 02SL - Stations (LUL) | Cxxx-NCR-000985 | NCR | Quality Support Procedure for Administration of Design |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2014-07-30 | 2014-07-21 15:14 | -9 | 2014-05-06 10:52 | Electrical - Electrical Engineering General | 1000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | 1 Finding with respect of no comprehensive quality support procedure for administration of design. This is a duplicate of Cxxx-NCR-000931 that was closed in error.
| 02SL - Stations (LUL) | Cxxx-NCR-000986 | NCR | Design Without an Accepted Design Statement. |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2015-08-31 | 2015-10-21 16:56 | 51 | 2014-05-06 10:59 | Mechanical - Mechanical Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | 1 Finding for continuing with the design whist the design statement had not been accepted by the Project Manager . This is a duplicate of Cxxx-NCR-000932 that was closed in error.
| 02SL - Stations (LUL) | Cxxx-NCR-000987 | NCR | Interface Control Document production timetable |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2014-05-20 | 2014-05-20 08:13 | 0 | 2014-05-06 11:02 | Mechanical - Mechanical Engineering General | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | 1 Finding for no clear Interface Control Document production timetable. This is a duplicate of Cxxx-NCR-000933 that was closed in error.
| 02SL - Stations (LUL) | Cxxx-NCR-000988 | NCR | Baseline Standards & Clause 8.2.1 of ISO 9001 (Customer Satisfaction) |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2014-06-11 | 2014-06-11 12:59 | 0 | 2014-05-06 11:07 | Mechanical - Mechanical Engineering General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | 1 Finding for no evidence to demonstrate ISO 9001 clause 8.2.1 ( Customer Satisfaction) implementation with respect of WI Vol 2B part 7.3 Contractors Design Duties that refer to Presentations) This is a duplicate of Cxxx-NCR-000934 that was closed in error.
| 02SL - Stations (LUL) | Cxxx-NCR-000989 | NCR | omission of MEP supports to permanent structure from 3D modelling |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2015-03-09 | 2015-03-02 15:41 | -7 | 2014-05-06 11:11 | Mechanical - Mechanical Engineering General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | 1 Finding for omission of MEP supports to permanent structure from 3D modelling 3D modelling of the GSM building was presented and reviewed during the visit The Contractor confirmed during the 3D presentation that the absence of details of supports for the MEP installations was in accordance with CRL requirements. This was checked post visit and found to be incorrect. CRL confirmation of MEP stage F design activities required before Gate 3 based on BSRIA Pro-forma 5a BG6/2012 requires bases, supports and structurally significant holes to be shown on 3D Model. Refer to technical requirements in this NCR. This is a duplicate of Cxxx-NCR-000935 that was closed in error.
| 02SL - Stations (LUL) | Cxxx-NCR-000990 | NCR | PV0002 Cable sever |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-06-25 | 2014-06-24 12:12 | -1 | 2014-05-06 13:26 | Surveying - Instrumentation and Monitoring | 0 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the nightshift of 30/04/2014, PV002 cable was severed.
| 02SL - Stations (LUL) | Cxxx-NCR-000991 | NCR | Offsite Fabrication - Steelwork - TTH - Discharging of Hold Points |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-06-18 | 2014-05-21 16:14 | -28 | 2014-05-07 08:55 | Civil - Civil Engineering General | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | It could not be demonstrated that __ have discharged their interventions in relation to the supervision of Oostingh Staalbouw (working in accordance with the agreed ITP hold points).
| 02SL - Stations (LUL) | Cxxx-NCR-000992 | NCR | Offsite Steel Fabrication - TTH - Visual Inspection Records |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-06-18 | 2014-05-21 16:15 | -28 | 2014-05-07 09:00 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | While visual inspection records of fit-up and weld inspections were available for review, of the sample undertaken (items 3032, 3008, 3014, 3015, 3019), visual inspection records were only available for 3019. The ITP requires a 100% visual inspection.
| 02SL - Stations (LUL) | Cxxx-NCR-000994 | NCR | PV0004 Cable Snagged |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-06-26 | 2014-05-30 16:45 | -27 | 2014-05-14 15:35 | Civil - Civil Engineering General | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | During day shift PV0004 cable was snagged on rebar within the southern base slab pour.
| 02SL - Stations (LUL) | Cxxx-NCR-000995 | NCR | Commencing work without approved MCR in place |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-06-25 | 2014-06-24 10:17 | -1 | 2014-05-14 15:58 | Shafts - Shafts General | 1000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Failure to follow status stamp | Completed |  | Base slab pour at CHS commenced with the __ Grating MCR [Cxxx-__M-C-LRC-D061-50100] @ Code 3 status.
| 02SL - Stations (LUL) | Cxxx-NCR-000996 | NCR | CHS Lower liner wall starters |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-06-24 | 2014-05-19 13:27 | -36 | 2014-05-15 18:17 | Shafts - Shafts General | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The CHS base slab was cast with 15no lower liner wall near face vertical coupled bars [bm08 from Cxxx-__M-C-DWG-D061_WS107-50104] situated such that the vertical bars [bm 401, 402 from Cxxx-__M-C-D061_WS107-50173] coupled into will clash with the radial lacer bars on the near face [for example bms 403, 433, 434, 444, from Cxxx-__M-C-D061_WS107-50173]
| 02SL - Stations (LUL) | Cxxx-NCR-000997 | NCR | TTH Sewer Vent Pipe Installation |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-06-25 | 2014-06-10 10:09 | -15 | 2014-05-16 18:13 | Civil - Civil Engineering General | 1500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | The Sewer Vent Pipe fabricated for the TTH was the wrong size. It has had to be cut down to size in order to be installed.
| 02SL - Stations (LUL) | Cxxx-NCR-000998 | NCR | DSS L8-7 Liner Wall Pour 3 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-06-24 | 2014-06-11 16:11 | -13 | 2014-05-20 11:07 | Shafts - Shafts General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | DSS Level 8 to 7 Liner Wall, Pour 3. 2no. 20mm A12 couplers are missing in the base slab for coupling BM316 bars in the near face. See attached sketch for locations.
| 02SL - Stations (LUL) | Cxxx-NCR-000999 | NCR | DSS Constructing Liner Wall Level 8 Under P03 Drawings |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-06-25 | 2014-06-16 08:03 | -9 | 2014-05-20 15:45 | Shafts - Shafts General | 1500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Level 8 Liner Wall rebar is currently being installed on site using P03 revision drawings.
| 02SL - Stations (LUL) | Cxxx-NCR-001000 | NCR | DSS L8-7 Liner Wall Pour 2 - Cover to NF Bars |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-06-17 | 2014-06-16 12:09 | -1 | 2014-05-22 15:55 | Shafts - Shafts General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Liner Wall Pour 2 the B40 NF2 bars from the base slab have a cover ranging from 85mm down to 35mm (worse case) (grading down along the length of the pour) please refer to sketch for more details. Where the cover is 35mm to the B40 NF2 bars we are unable to install all the NF1 bars on NF1 as there will be no cover.
| 02SL - Stations (LUL) | Cxxx-NCR-001001 | NCR | Non Approval of Weld Procedures |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-07-05 | 2014-06-23 08:33 | -12 | 2014-05-21 15:00 | Civil - Civil Engineering General | 1000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Approval of Weld Procedures were requried for the CHS & DSS sites relating to the offsite welding of the base slab reinforcement panels but was not obtained in line with the requirements of the ITP.
| 02SL - Stations (LUL) | Cxxx-NCR-001002 | NCR | DSS - Reinforcement exposed in Sump Base |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-09-30 | 2015-09-12 12:25 | -18 | 2014-05-22 10:34 | Shafts - Shafts General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During concreting to the South Pour Base Slab, the area beneath the drainage sump box was not compacted, resulting in an exposed void in the sump base. The void is approximately 1.1m x 0.7m x 0.4m deep (see attached photo).
| 02SL - Stations (LUL) | Cxxx-NCR-001003 | NCR | DSS - Couplers Installed in Wrong Location |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-06-18 | 2014-06-18 12:20 | 0 | 2014-05-22 15:36 | Shafts - Shafts General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Base Slab couplers for Liner Wall Level 8 Pour 5 within the recess have been installed in the incorrect location. Bar marks affected in Liner Wall Pour 5 are as follows: 535 - 541, 545, 546 and 509. Please refer to site photo for more details.
| 02SL - Stations (LUL) | Cxxx-NCR-001004 | NCR | Non Compliant earth cables installed in E510A |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-08-19 | 2014-08-08 12:21 | -11 | 2014-05-22 16:54 | Electrical - Cable Management | 5000 |  | Material | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Non compliant __ earth cables have been installed on Platform 6 E510A switchroom.
| 02SL - Stations (LUL) | Cxxx-NCR-001005 | NCR | TTH Pile Cut Off Levels |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-06-25 | 2014-06-11 10:51 | -14 | 2014-05-22 17:59 | Civil - Civil Engineering General | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | The TTH Pile Cut off levels were marked out using a datum set 100mm high. This resulted in the cut off levels being 100mm low. The Cut Off Levels of the piles are: P1 - 112.265mATD p2 - 112.265mATD P3 - 111.605mATD P4 - 111.605mATD P1 - P2 - P3 - P4 -
| 02SL - Stations (LUL) | Cxxx-NCR-001007 | NCR | DSS L8-7 Liner Wall Pour 8 Damaged Couplers |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-06-11 | 2014-06-04 15:28 | -7 | 2014-05-28 15:38 | Shafts - Shafts General | 1500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Prior to installing L8-7 liner wall pour 8 it has been identified that 2no 32mm A12 couplers (BM1017 on drg 50103) have been damaged on the underside of level 7 waler so the far face vertical bars projecting from the base slab (BM3022 on drg 50214) are not engaged in the couplers. See photos attached.
| 02SL - Stations (LUL) | Cxxx-NCR-001008 | NCR | TTH Paint Missing from Entrance PFC's |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-10-30 | 2014-10-08 09:01 | -22 | 2014-05-29 15:05 | Civil - Civil Engineering General | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Error by manufacturer in shipping or marking | Completed |  | During installation of the TTH steelwork it has been noticed that two PFCs P3247 and P3248 attached to beam 3020 in the TTH fabrication drawings Cxxx-__M-C-DWG-D061-50366 did not have the correct coating of paint as shown in the attached photographs.
| 02SL - Stations (LUL) | Cxxx-NCR-001009 | NCR | TTH Incorrectly Painted Top Flanges of Beams |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-10-30 | 2014-10-08 09:03 | -22 | 2014-05-29 15:32 | Civil - Civil Engineering General | 1000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Error by manufacturer in shipping or marking | Completed |  | During installation of the TTH it was noticed that some of the top flanges of the beams which are to receive metal decking welded studs have had paint applied. __ are to provide marked up drawings of which beams have had the top flanges painted where stud welding was required.
| 02SL - Stations (LUL) | Cxxx-NCR-001010 | NCR | DSS L8-7 Liner Wall Pour 1 tunnel trimmer starters |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-06-18 | 2014-06-04 14:27 | -14 | 2014-05-30 13:59 | Shafts - Shafts General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In DSS liner wall pour 1 it has been identified that the couplers (BM1070 FF on drg 50208) in the base slab have been installed in the wrong location. Rather than being installed in FF3, they have been installed in the centre of the liner wall. Photo attached.
| 02SL - Stations (LUL) | Cxxx-NCR-001011 | NCR | DSS Liner Wall 4 btw Base Slab & L7 Waler _ Cast In Cavity Drain without IFC drawings |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-06-16 | 2014-06-11 16:13 | -5 | 2014-06-02 17:22 | Shafts - Shafts General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | Due to design delays, the attached non-IFC drawing will be used to cast in the cavity drain in DSS Liner Wall 4 between base slab and L7 Waler (= Lower Liner Wall Pour 3).
| 02SL - Stations (LUL) | Cxxx-NCR-001012 | NCR | DSS - Liner Wall Level 8 Pour 8 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-06-17 | 2014-06-18 12:17 | 1 | 2014-06-03 12:39 | Shafts - Shafts General | 1500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Liner Wall Pour 8 the B40 NF2 (vertical) bars from the base slab have a cover ranging from 70mm - 40mm (worse case). Where the cover is 40mm to the B40 NF2 bars we are unable to install all the NF1 bars on NF1, as there will be no cover. Pour 8 Wall 1 (RFI-1633) the position of the couplers in the base slab also provide the same problem above.
| 02SL - Stations (LUL) | Cxxx-NCR-001013 | NCR | DSS L7-8 liner wall pour 8 tunnel trimer bars |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-06-27 | 2014-06-23 08:35 | -4 | 2014-06-03 17:12 | Shafts - Shafts General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | When installing reinforcement in the L7-8 liner wall pour 8 it has been found that the FF BM3076 bars in the base slab south pour were installed in FF2 rather than FF3. This means that the BM802 bars that couple into them clash with the FF2 lacers. BM802 are trimmer bars around tunnel PTE. The same has happened with 1no of the 3no BM802 in NF3. We intend to use the same solution in all cases.
| 02SL - Stations (LUL) | Cxxx-NCR-001014 | NCR | TTH P4 Concrete Strength |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-07-16 | 2014-06-11 10:53 | -35 | 2014-06-04 09:17 | Civil - Structural Engineering | 1500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 28 Day results for Cubes taken for P4, poured on 02/05/14 were 34.6N/mm2 and 33.0N/mm2. The Specified design strength is C32/40, therefore the concrete in the cubes have not achieved required strength.
| 02SL - Stations (LUL) | Cxxx-NCR-001015 | NCR | Internal wiring of E510a switch panel change over contactor incorrect |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-12-22 | 2014-08-26 08:12 | -118 | 2014-06-05 12:52 | Electrical - Power Distribution | 2500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | New interim switch Panel E510a has two electrical supplies (Primary supply LUL fed from E510 & Secondary supply DNO fed from E2), these supplies are operated by a change over panel. The panel is currently electrically biased to the DNO supply and internal supply present lights are wired incorrect.
| 02SL - Stations (LUL) | Cxxx-NCR-001016 | NCR | Utilities Diversion - Working to non IFC drawings |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-06-25 | 2014-06-26 08:02 | 1 | 2014-06-05 13:15 | Utilities Engineering - Utilities General | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Durward Street- Combined Services Trench Realignment drawings, are still not issued as IFC drawings. The works by the TTH area are substantially completed without these drawings in IFC status. The Drawings are currently with the project manager via Cxxx_CCM_06032. These drawings are to be issued for IFC through Projectwise/PMC by the Prokect Manager. Affected drawings: Cxxx-__M-C-DDA-D061_WS105_10-00001 Cxxx-__M-C-DDA-D061_WS105_10-00002 Cxxx-__M-C-DDA-D061_WS105_10-00003 Cxxx-__M-C-DDA-D061_WS105_10-00004 Cxxx-__M-C-DDA-D061_WS105_10-00005 Cxxx-__M-C-DDA-D061_WS105_10-00006 These drwaings needs to be in IFC status to produce Asbuilt information.
| 02SL - Stations (LUL) | Cxxx-NCR-001017 | NCR | Lack of Details on Approved ITP – for Carriageway Reinstatement works |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-10-08 | 2014-10-07 13:25 | -1 | 2014-06-09 08:43 | Civil - Base Course | 1000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | The approved ITP for Utility Diversion-Water main - Cxxx-__M-U-ITP-D061_WS105-50001_Rev 2.0 does not contain enough details for the Road pavement (carriageway) reinstatement works. The works are covered as part of the approved WMS - Cxxx-__M-U-GMS-D061_WS105-50001 Durward Street Combined Utility Diversion 2.0 The proposed reinstatement works on 02/06/14 was aborted until sufficient details and the Specification for the works was clarified.
| 02SL - Stations (LUL) | Cxxx-NCR-001018 | NCR | Durward street -Utilities Diversion - Working to non-approved MCR |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-06-23 | 2014-06-11 10:59 | -12 | 2014-06-09 08:55 | Utilities Engineering - Gas | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | The Type 1 and Sharp sand materials were used onsite prior to the MCR being approved officially by CRL. The Virgin Type 1 was used as the use of recycled Type 1 was temporarily suspended on site due to poor quality of the materials. Approved MCR for recycled type 1 was in place only. The Type 1 was used on 2/05/14 and the document submitted on the same day. MCR approved verbally. The Sharp sand was used as the supplier was unable to provide the necessary CE markings for Thanet sand which was requested by National Grid Gas (NGG) as it is their preferred material. However due to lack of approved suppliers and lack CE marking, the sharp sand materials was proposed to NGG and they approved the use of this material. However due to the progression of the works and delays in the documentation the sharp sand was used with verbal approval from NGG and CRL, with MCR documentation submitted as soon as practicable. The sand was used on 25/04/14, the MCR was officially submitted on the 2/05/14.
| 02SL - Stations (LUL) | Cxxx-NCR-001019 | NCR | DSS L8 Liner Wall Pour 1 Damaged Couplers in L7 Liner |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-07-15 | 2014-06-19 08:08 | -26 | 2014-06-10 15:42 | Shafts - Shafts General | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In L8-7 liner wall pour 1, 3no. 32mm A12 couplers are damaged in L7 liner wall. These couplers are on BM101 in drg 50095. Photos attached.
| 02SL - Stations (LUL) | Cxxx-NCR-001020 | NCR | DSS L8-7 Liner Wall Pour 7 BM747 & BM748 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-07-16 | 2014-06-26 08:37 | -20 | 2014-06-11 10:05 | Shafts - Shafts General | 2000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | When installing DSS L8-7 liner wall pour 7, in the thicker area along wall 3, there is insufficient cover to the NF bars in the region of the vertical BM728 32mm bars. When the NF1 horizontal bars are installed the cover in areas is 15/20mm. In other liner wall pours where a similar issue has occurred the NF1 bars have been moved to NF3. In this case, this cannot be done for all the bars. BM747 and BM 748 are ubars that sit in NF1 and FF2. The FF1 bars were cast in with the base slab so the ubars cannot be moved to FF0.
| 02SL - Stations (LUL) | Cxxx-NCR-001021 | NCR | DSS L8-7 Liner Wall Pour 7 missing NF couplers |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-07-30 | 2014-06-26 08:39 | -34 | 2014-06-11 15:43 | Shafts - Shafts General | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | When installing DSS L8-7 liner wall Pour 7, it has been found that couplers are missing in the base slab. These couplers are: - 3no. 32mm A12 couplers from BM2026 on drg 50211 - 2no. 40mm A12 couplers from BM3025 on drg 50214 Based on response to RFI-1633 the following work has been carried out: - 3no. 32mm bars drill and fixed into base slab with 200mm embedment - 2no. 40mm bars drill and fixed into base slab with 200mm embedment The locations of these bars are shown on the attached sketch. Please note that there are now 17no BM728 installed in the base slab rather than the 16no shown on the drawing. Photos are also attached.
| 02SL - Stations (LUL) | Cxxx-NCR-001022 | NCR | DSS L8-7 Liner Wall Pour 1 FF BM1063 missing |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-07-23 | 2014-06-16 12:11 | -37 | 2014-06-12 12:12 | Shafts - Shafts General | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 7no. 32mm bars BM1063(a-g) on drg 50208 have not been installed with the base slab.
| 02SL - Stations (LUL) | Cxxx-NCR-001023 | NCR | DSS L8-7 liner wall pour 1 NF bars drill and fix |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-07-22 | 2014-06-17 07:46 | -35 | 2014-06-13 12:07 | Shafts - Shafts General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In DSS L8-7 liner wall pour 1, 3no. couplers were missing for BM107 bars. The missing couplers were BM1026 on drg 50208. Locations are shown on attached sketch.
| 02SL - Stations (LUL) | Cxxx-NCR-001024 | NCR | GSM Column G1/GD Plate Re-Drilled |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-09-17 | 2014-09-11 09:42 | -6 | 2014-06-19 06:19 | Civil - Civil Engineering General | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the installation of the GSM canopy the column G1/GD bracket had to be re-drilled to accommodate the bolt through the column. The two bolt holes were not drilled perfectly straight leading to an error of approx 20mm between the fabricated plate L1516 and the exit holes on the east of the concrete column G1/GD. Subsequently the plate L1516 was re-drilled to accommodate the final bolt position (see photo attached). It was agreed by __ that this adaption to the connection is adequate and that __ Hit 200A resin was required to fill the void between the bolt and the drill hole in the concrete column. These remedial works were completed on the nightshift of 23/06/2014
| 02SL - Stations (LUL) | Cxxx-NCR-001025 | NCR | DSS - Liner Wall L8 Pour 1 Concrete Void |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-07-31 | 2014-07-08 09:25 | -23 | 2014-06-19 15:15 | Shafts - Shafts General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In the curved stop end of Liner Wall L8 Pour 1 a piece of polystrene was installed into the curve creating a void in the curve of the Liner Wall, please see site photo for more details.
| 02SL - Stations (LUL) | Cxxx-NCR-001027 | NCR | DSS L8-7 liner wall pour 7 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-07-22 | 2014-06-26 08:40 | -26 | 2014-06-23 11:38 | Shafts - Shafts General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In DSS L8-7 liner wall pour 7 there was 1no damaged 40mm A12 couplers in NF of L7 above. This coupler was on BM837 on drg 50111. Following response from previous NCRs (for example NCR-1019), the damaged coupler has been broken out and replaced. See photo attached.
| 02SL - Stations (LUL) | Cxxx-NCR-001028 | NCR | Damage to Mechanical Protection that house the PA cables during cill beam works |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-08-31 | 2014-09-08 09:07 | 8 | 2014-06-25 18:55 | Communications and Control Systems - Public Address Systems | 1500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | uring the Cill been installation work, a conduit which extends from the trunking to the speaker that we removed (during possession 20-23/05/14) was forced of the trunking by a third party (other work group during possession). This zone 5 PA speaker has been reinstated back into service on Sunday night shift 22/06/2014, Carried out test announcement successfully which was witnessed by Janet Reader of London underground. An Event Report Form (F127) has been filled out and a photo has been recorded of the damage, Station supervisor has been informed of the above details. Note: no damage has been observed to the PA cable To repair the mechanical protection (trunking to conduit flanged bush) of the PA zone 5 cables requires isolation of the zone by the asset maintainer. The speaker cables can be disconnected and pulled back into the trunking to allow repairs on the conduit flanged bush. On completion of the repairs cable to be reinstated and functional test of PA speaker to be carry out.
| 02SL - Stations (LUL) | Cxxx-NCR-001029 | NCR | DSS L6-7 Liner wall pour 1 2no damaged couplers |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-07-23 | 2014-06-27 08:36 | -26 | 2014-06-25 16:50 | Shafts - Shafts General | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | In DSS L6-7 liner wall pour 1 there are 2no damaged 25mm dwall couplers. 1no 25mm dwall coupler is in dwall panel P38. The female coupler is stuck in the male coupler. Efforts have ben made to remove it but this has lead to further damage of the male such that a bar cannot be installed in to it. See photos 491 & 492. 1no 25mm dwall coupler is in dwall panel P39. The male will not engage into the female. It will hold a bar but will cannot be torqued. A dwall starter has been installed into the male the coupler. See photo 493.
| 02SL - Stations (LUL) | Cxxx-NCR-001032 | NCR | D122b Subway Roof - Cut lines out of tolerance |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-07-10 | 2014-07-14 08:21 | 4 | 2014-06-26 17:04 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Approved ITP number Cxxx-__M-C-ITP-D061-50178 defines the location tolerance on the cut lines for the D122b subway roof at +/- 10mm. Whilst the horizontal cuts were on tolerance, the vertical saw cuts are out of the +10mm tolerance. The cuts were to be set out to allow for a 20mm vertical soft joint around the new roof slab. Due to the cuts being out of tolerance (too large), __ have poured high strength grout (Weber Five Star) to fill the extra gap.
| 02SL - Stations (LUL) | Cxxx-NCR-001034 | NCR | Level 8 Liner Wall Visual Imperfections |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-10-08 | 2014-08-14 08:37 | -55 | 2014-06-28 11:00 | Shafts - Shafts General | 3000 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Due to poor supply of self-compacting concrete during pouring of level 8 liner wall 5 and 8 visual imperfections are visiable on the surface of the wall. 100mm diameter cores were taken to a depth of 40mm into the cover zone to assess the depth off these imperfections. It appears they extend through the width of the pour.
| 02SL - Stations (LUL) | Cxxx-NCR-001035 | NCR | Void form at the far face top surface of Level 8 Liner wall 5 and 8 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-10-29 | 2016-09-30 14:38 | -29 | 2014-06-28 11:18 | Shafts - Shafts General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A void has formed at the far face of Level 8 liner wall pour 5 and 8 at the top level.
| 02SL - Stations (LUL) | Cxxx-NCR-001037 | NCR | TTH Steelwork Column Endplate Fabricated Out of Position |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-10-28 | 2014-10-28 12:14 | 0 | 2014-07-02 04:06 | Civil - Civil Engineering General | 1000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the installation of the TTH steelwork it was noticed that the plate P3119 on the PFC 3100 had been incorrectly fabricated in the workshop. The end plate has been fabricated approx 1m out of position as does not align with the top of the column on the intersection of gridlines G and 5 (See marked up drawings attached). Remedial works to be updated once discussed with __ and confirmed with __ designers.
| 02SL - Stations (LUL) | Cxxx-NCR-001038 | NCR | TTH Steelwork Eastern PFCs not in alignment column on gridline G-5 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-10-15 | 2014-10-10 15:52 | -5 | 2014-07-02 04:30 | Civil - Civil Engineering General | 1000 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the installation of the TTH steelwork it was noticed that 4no PFC (marks 3070, 3071 & 3073 x2) were installed out of alignment on the connection to column on gridline G-5. The PFCs are approximately 20mm out of position to the east (see attached photo). __ propose to redrill the beams/brackets to correct the alignment.
| 02SL - Stations (LUL) | Cxxx-NCR-001039 | NCR | Bracings installed incorrectly on GSM canopy |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-10-10 | 2014-07-23 09:55 | -79 | 2014-07-02 05:12 | Civil - Civil Engineering General | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the installation of the GSM canopy above platform 2 it was noticed that 3 braces were installed upside down where the friction paint is now not in contact with the beam fillet plate friction paint (see attached sketch). __ have checked the "use as is" option and have confirmed by calculation that this non conformance does not affect the structural integrity of the GSM canopy, see attached NCR 004. It is therefore proposed by __ to use as is.
| 02SL - Stations (LUL) | Cxxx-NCR-001040 | NCR | Incorrect Material Used for Drainage Surround |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-07-16 | 2014-07-07 08:42 | -9 | 2014-07-02 13:32 | Civil - Drainage | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The material that was excavated for for the drainage channel was used as a surround when backfilling. As per drawing Cxxx-__M-C-DWG-50132 and Cxxx-__M-C-DWG-50135, the surround for FO3 should be 4-10mm granaular aggregate (pea shingle).
| 02SL - Stations (LUL) | Cxxx-NCR-001041 | NCR | ESS - Pile Group 11B, Pile No.10 - Pile Casing Stuck |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-08-05 | 2014-08-04 10:35 | -1 | 2014-07-03 15:06 | Civil - Civil Engineering General | 1500 |  | Equipment Breakdown | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On 02/07/14 around 1500 hours, during pouring the concrete (Pile Group 11/ Pile No.10) managed to extract only one out of two temporary casings used (1m length), the other one was stuck in the ground and could not be retrieved. The temporary casing left in the ground is 508mm diameter/1 meter length, and the top of the casing is at 104.8mATD.
| 02SL - Stations (LUL) | Cxxx-NCR-001042 | NCR | GSM Roof Plates Phase 2 Missing Bolts |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-10-12 | 2014-07-31 08:23 | -73 | 2014-07-04 11:07 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As a follow up from Cxxx-NCR-000964 where 48 bolts could not be installed in the GSM roof plates, during phase 2 of the GSM roof plates (external plates) a further 24 bolts could not be installed due to clashes with beam end plates and beam stiffeners in the supporting beams, see attached marked up drawing. This leaves a total of 72 bolts not installed out of the approx 6600 bolts required on the GSM roof. This keeps the percentage of bolts not installed at appox 1%. This was confirmed as exceptable and was expected by __ after the completion of phase 1 installation, see attached __ NCR.
| 02SL - Stations (LUL) | Cxxx-NCR-001043 | NCR | GSM Incorrect Installation of Roof Beam mark 530 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-10-12 | 2014-08-04 07:39 | -69 | 2014-07-04 13:32 | Civil - Civil Engineering General | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | It has been noticed that the beam mark 530 on the GSM structural steel roof beams have been installed incorrectly during the GSM phase 1 steelwork installation. The beam has been installed incorrectly by 180 degrees. This does not affect the beam stiffener alignment with the roof purlins above but does however affect the pre drilled hole locations for the future canopy connections for the GSM SME canopy on the west of the building.
| 02SL - Stations (LUL) | Cxxx-NCR-001044 | NCR | Lack of Control of Materials and Storage |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-07-22 | 2014-07-21 13:18 | -1 | 2014-07-08 16:37 | Civil - Civil Engineering General | 500 |  | Material | Reject | 4 (0.5-3k) | Complete | Supervision - Supervisor not familiar with the work | Completed |  | 10No bags of Grout had been been incorrectly stored, resulting in the grout being in an unsatisfactory condition to be used. The grout has been disposed of.
| 02SL - Stations (LUL) | Cxxx-NCR-001045 | NCR | GSM access hatch in the wrong location |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-03-17 | 2014-12-03 11:22 | -104 | 2014-07-10 16:13 | Civil - Civil Engineering General | 10000 |  | Design | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | It has been raised to the Contractor by the Sub Contractor that the design of the steelwork trimming steel has been designed in the wrong location by one bay of steel. As shown in the marked up drawing, the access hatch should be in the bay nearest the GJ/G6 intersection however it is currently installed in the bay of GJ/G5. This means that the hatch does not align with the roof access room to be constructed inside the GSM.
| 02SL - Stations (LUL) | Cxxx-NCR-001046 | NCR | Steel column: SCP-8-6-01 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-07-30 | 2014-07-16 09:15 | -14 | 2014-07-10 18:49 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Drawing WS105-50463 is unclear as to the orientation and positioning of the Baseplate on SCP-8-6-01. A dashed line type was used on the drawing instead of a solid line type for the base plate.
| 02SL - Stations (LUL) | Cxxx-NCR-001047 | NCR | DSS Coupler Alignment for Beam CDB-6-04 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-07-25 | 2014-07-16 13:43 | -9 | 2014-07-11 16:43 | Shafts - Shafts General | 0 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The alignment of the couplers for beam CDB-6-04 within Liner Wall Level 6 - 7 Pour 5 are not in a perfect line, see site photo for details.
| 02SL - Stations (LUL) | Cxxx-NCR-001048 | NCR | Durward Street Utilities Diversion - Not raising an FCD related to __ duct installation |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-10-08 | 2014-09-26 14:06 | -12 | 2014-07-11 18:07 | Civil - Utilities Engineering | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | During the installation of __ duct work within Durward Street WC 07/07/14, a concrete obstruction was encountered. This obstruction has resulted in the cover of the ducting to be less than the minimum required by __. Where this has been encountered in previous phases of the utility diversions, a process has been greed with __ on how to provide extra protection to the ducting. Where minimum cover cannot be achieved within the carriageway and footpath, __ have agreed that a steel plate and thick rubber marker tape will provide adequate protection to their assets. An FCD is in the process of being produced and has not been approved. This FCD should have been approved prior to commencement of further works where the minimum cover could not be achieved.
| 02SL - Stations (LUL) | Cxxx-NCR-001049 | NCR | Cover issue with Liner wall 7-6 pour 7 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-07-28 | 2014-07-28 14:37 | 0 | 2014-07-14 13:17 | Shafts - Shafts General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On liner wall 7-6 pour 7 BM754 and BM748 have reduced cover of 5mm due to NF vertical bar couplers in the pour above being fixed too close to the edge. Inturn this has led to the vertical bars of the current pour to be too close to the edge and thus BM754 and BM748 left with reduced cover.
| 02SL - Stations (LUL) | Cxxx-NCR-001050 | NCR | CHS - Closure of FCD 00883 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-08-26 | 2014-07-23 12:12 | -34 | 2014-07-21 15:18 | Shafts - Shafts General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As described in FCD 00883 (please find attached): The couplers which connect the beam on the southern edge of CHS lift shaft 8 to the liner wall were installed in the incorrect orientation.
| 02SL - Stations (LUL) | Cxxx-NCR-001051 | NCR | Waterproofing |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-09-09 | 2014-09-01 16:37 | -8 | 2014-07-22 18:23 | Civil - Excavation | 1500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The ground was broken and excavated to expose the bottom of the precast concrete channels in preparation for their removal. Whilst exposing the channels some of the waterproofing was damaged. Further to Cxxx attendance this morning, it was agreed that the channels do not need to be removed – however, the waterproofing still must be rectified and made good.
| 02SL - Stations (LUL) | Cxxx-NCR-001052 | NCR | CHS Level 7-6 walls/columns concreting |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-08-27 | 2014-08-28 08:44 | 1 | 2014-07-29 16:23 | Shafts - Shafts General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On one occasion a concrete delivery from __ (Silvertown) arrived with a batch of Line 31 concrete (which has an S3 consistency class), where the slump measurement exceeded the upper boundary of the S3 class (215mm > 180mm)
| 02SL - Stations (LUL) | Cxxx-NCR-001053 | NCR | East Stair Shaft Waterproofing |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-10-05 | 2014-09-26 14:57 | -9 | 2014-07-29 18:59 | Civil - Structural Engineering | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During blinding work for the pile cap at Pile Group 14, a fault was noticed with a small section of waterproofing to the previously cast slab within the East Stair Shaft. After RFI numbers Cxxx-RFI-000892 and Cxxx-RFI-001013 had been raised, waterproofing specialist __ were used to provide the waterproofing as detailed in drawing Cxxx-HYD-S-DDB-D061_WS106_Z-75820. Horizontal installation of __ __ requires a 75mm lap with the previous sheet, as detailed within the attached specification. As shown in the attached photo, a small section (10%) of the previously poured slab did not have the __ membrane extend beyond the extent of the formwork. This has resulted in there being no lap available to continue the waterproofing for Pile Group 14 pile cap. __ have been contacted and they have provided Cxxx with a drawing on how to re-mediate the situation and ensure that the waterproofing of the slab is not compromised. Please find attached drawing D05088/1 from __ with a __ continuity detail. The blinding of the existing slab is to be undercut to find the installed __ membrane and then a Bituthene LM is applied to the underside of the __ layer and 75mm up the face of the existing slab. The waterproofing can then continue for the pile cap. Finally, Bituthene LM is then applied at this joint with the existing slab, lapping both the __ membrane layer and the face of the slab by 75mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001055 | NCR | TTH Level A Slab Finish |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-08-15 | 2015-06-20 15:43 | -56 | 2014-07-29 18:46 | Civil - Civil Engineering General | 450 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The specified finsh for the Level A Metal Decking Concrete slab for the TTH was 'Smooth Float Finish'. Due to the pace the concrete was setting, this finish was unacheivable and the slab level is out of tolerance. The level of the slab tolerances are +10mm/-5mm. The concrete was setting qucikly due to the high temperature on the day. Temperatures reached 29C which is still within the working temperature for the concrete, however, when placing the concrete on the metal deck, it began to set quicker due to the heat coming from both the metal deck and the sun.
| 02SL - Stations (LUL) | Cxxx-NCR-001056 | NCR | Incomplete Construction Records Level 6-7 Liner Wall construction |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-08-27 | 2014-08-28 08:46 | 1 | 2014-07-30 08:20 | Shafts - Shafts General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Incomplete construction records for Level 6-7 Liner Wall construction.
| 02SL - Stations (LUL) | Cxxx-NCR-001057 | NCR | CHS - over pour to wall W7-04S |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-03-05 | 2015-03-04 12:34 | -1 | 2014-07-31 12:26 | Shafts - Shafts General | 2000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the completion of the Level 7 slab a section of wall W7-04S was poured with the slab. During the completion of the pour the Southern shutter has been dislodge, by a maximum of 50mm. This has resulted in a 'belly' in the wall, tapering to nothing by the top of the kicker, see attached photos.
| 02SL - Stations (LUL) | Cxxx-NCR-001058 | NCR | CHS Liner Wall - Voids above SCC pours |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-06-08 | 2016-06-06 13:10 | -2 | 2014-08-01 13:27 | Shafts - Linings | 6000 |  | Material | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Further to NCR 978, this NCR is to highlight that voids, to varying extents, are present above all Liner Wall pours completed using self-compacting concrete.
| 02SL - Stations (LUL) | Cxxx-NCR-001059 | NCR | CHS - out of spec concrete load for Level 7-6 walls and columns 26 07 14 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-09-09 | 2014-09-16 16:28 | 7 | 2014-08-01 15:27 | Shafts - Shafts General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A load of concrete arrived at site that was not as per the specification. The load was Line 31 mix from __ which is a C40/50 S3 mix. The concrete was for Level 7 - 6 columns C7-07, C7-38, C7-41 & C7-47. The load slumped at 220mm first test and 195mm second test (allowable range for S3 mix 80 - 180mm). Due to this being the last load the concrete was used.
| 02SL - Stations (LUL) | Cxxx-NCR-001061 | NCR | Wall W7-05Ns Concrete Finish |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-09-09 | 2014-09-08 13:24 | -1 | 2014-08-13 13:30 | Shafts - Shafts General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Area of approximately 1m2 on W7-05NS has poor finish - honeycombing, blowholes, etc.
| 02SL - Stations (LUL) | Cxxx-NCR-001062 | NCR | TTH Water Main Connection Position |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-10-14 | 2014-10-10 15:53 | -4 | 2014-08-06 16:06 | Civil - Utilities Engineering | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Due to the location of the existing utilities in the TTH compound __ were unable ot install the Water main in the position as per Cxxx-__M-C-DWG-D061-50122. The Drawing Shows a centre of: 84937.4162 36489.5277 No exact Level required. Onsite the Connection has a centre of: 84937.3760 36489.6042 113.5020 This means that the connections is 86mm out of position.
| 02SL - Stations (LUL) | Cxxx-NCR-001063 | NCR | CHS - Flight 2 incorrectly cast starter bars |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-10-14 | 2014-08-29 16:16 | -46 | 2014-08-07 18:04 | Shafts - Shafts General | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As per FCD 000903, Cast into wall W8-04S the B16 pull out bars which become the stairwaist starter bars for flight 2 were cast in the incorrect position (see attached photo) Please refer to drawing Cxxx-__M-C-DWG-D061_WS107-50310. __ have broken out additional concrete and cranked these bars into position. This has however reduced the anchorage into the stairwaist to 420mm. The stairs are to be cast with C40/50 concrete and therfore the good bond minimum anchorage required for a full strength connection is 480mm. The reduced anchorage of 420mm reduces the strength of the connection to 420/480 = 0.875 capacity From RFI-001104 R the design forces for this connection are 25 kN/m vertical shear and 200kN/m horizontal tension. The capacity of B16@125mm centres exceeds the design shear by more than 4 times and the design tension by more than two times. Therefore a reduction in capacity of 12.5% is considered okay as the connection is still capable of resisting the design loads.
| 02SL - Stations (LUL) | Cxxx-NCR-001064 | NCR | TTH- TBS -Base |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-09-23 | 2014-09-12 10:44 | -11 | 2014-08-08 12:13 | Civil - Civil Engineering General | 2000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | When striking the Temporary Builders supply cabinet base, it was found that the concrete hadn’t properly cured . The base was not finished correctly - steel float flinsh required. No angle fillets installed.
| 02SL - Stations (LUL) | Cxxx-NCR-001066 | NCR | Material Compliance Records at Code 2 or 3 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-10-07 | 2014-10-07 14:05 | 0 | 2014-08-08 15:42 | Materials - Approval | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | During a review of the Not Yet Coded status of MCRs, 11 were found to be at Code 2 or 3 and past the 14 day period for reply
| 02SL - Stations (LUL) | Cxxx-NCR-001067 | NCR | Commencment of works without an agreed sub-contractor quality plan in place. |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2014-10-29 | 2014-10-23 08:35 | -6 | 2014-08-08 16:23 | Architectural - Walls | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | Ardent have sub-contracted the blockwork for the TTH to __ without an agreed sub-contractor quality plan in place.
| 02SL - Stations (LUL) | Cxxx-NCR-001068 | NCR | TTH Manhole Modification - Brickwork |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-09-05 | 2014-08-28 08:50 | -8 | 2014-08-08 17:19 | Civil - Utilities Engineering | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Personnel Error - Verbal communication problem | Completed |  | Nights shift did not understand engineers instructions from days. The engineer requested 2 courses of double skin bricks to reach a level of 113.350mATD. The engineer provided a datum of 113.600mATD to work from. Nights shift built 4 courses up to 113.600mATD. The next morning these works had to be remediated and rebuilt.
| 02SL - Stations (LUL) | Cxxx-NCR-001069 | NCR | Level 7 Pour 2 Missing Starter Bars |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-10-14 | 2014-08-29 16:17 | -46 | 2014-08-11 11:00 | Shafts - Shafts General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please refer to the attached sketch and drawing Cxxx-__M-C-DWG-D061_WS107-50338. BM 412 (a&b) and BM 438 (a&b) were not installed when Wall W7-04S was cast. These bars are required to tie Level 7 pour 2 into the wall.
| 02SL - Stations (LUL) | Cxxx-NCR-001070 | NCR | DSS - Columns C8-07, C8-08 and C8-12 poured too high |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-12-09 | 2018-07-06 12:22 | -156 | 2018-07-02 07:50 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Columns C8-07, C8-08 and C8-12 have been poured too high. The error occured as a result of a change in design which was misinterpreted by the engineers. Cxxx-FCD-000897 changes the level of the platform slab. On the drawing Cxxx-__M-C-DWG-D061_WS105-50278 section 3-3 shows the underside of the platform slab level with the underside of the beam. Therefore once the slab level changed it was thought that so too did the beam levels. This is in fact incorrect and was highlighted after the columns had been poured.
| 02SL - Stations (LUL) | Cxxx-NCR-001074 | NCR | TTH - North Slab Pour 1 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-10-11 | 2014-10-10 13:43 | -1 | 2014-08-22 13:59 | Civil - Civil Engineering General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | The TTH North Slab Pour 1 was poured withouth an MCR in place for __ TP70. The material was checked to achieve the same u value of 0.22w/m^2K as the sepcified insulaton, __ __. As this u value was satisfied it was decided by __ and CRL that it was acceptable to continue the works but raise an MCR for working without the correct MCR in place. On review of the slab and the __, it was pointed out by LU that __ is not compliant or fire rated. On LUs suggestion is was agreed that as the __ insulation is okay to be left in as it fully encased. This must be confirmed by the desinger.
| 02SL - Stations (LUL) | Cxxx-NCR-001075 | NCR | ESS- Self Comapcted Concrete Work - Flow Test Table |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-10-14 | 2014-10-13 11:00 | -1 | 2014-08-22 16:37 | Civil - Civil Engineering General | 1000 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | During the concrete pour portal frame central columns on ESS; The required flow test table could not be located prior to the pour, therefore no accurate slump test could be undertaken. A test using a standard slump kit plate was undertaken with a result of 670mm, within the required parameters. The standard plate was not big enough for the test and therefore limited its value
| 02SL - Stations (LUL) | Cxxx-NCR-001076 | NCR | CHS Level 6 Slab Lap Lengths |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-09-11 | 2014-09-04 11:10 | -7 | 2014-08-28 14:47 | Shafts - Shafts General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Some issues have been identified with regards to the lap lengths of the bars in the top mat of the level 6 slab. In a number of cases the lap was measure to be 1800-1830mm on one end and 1870-1900mm on the other, design requires a lap of 1850mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001077 | NCR | CHS Level 7 Column 47 out of plumb |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-09-11 | 2014-09-04 11:11 | -7 | 2014-08-28 15:22 | Shafts - Shafts General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Column 47 on level 7 at CHS is out of tolerance in terms of plumb on the west face and on the western side of the southern face. See attached plot for full as built details of the faces of the column.
| 02SL - Stations (LUL) | Cxxx-NCR-001078 | NCR | CHS Level 7 Column 41 out of plumb |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-09-11 | 2014-09-04 11:17 | -7 | 2014-08-28 15:26 | Shafts - Shafts General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Column 41 on Level 7 at CHS is out of plumb. The Eastern face and the East side of the Southern face is outside the design tolerance for plumbness. See attached plot for full as built data from the column.
| 02SL - Stations (LUL) | Cxxx-NCR-001079 | NCR | Out of date MCR for Line 292 Self compacting concrete |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-11-28 | 2014-11-24 09:45 | -4 | 2014-08-28 17:08 | Shafts - Shafts General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | The MCR for Line 292 self compacting concrete was not updated when the mix was changed from an SF2 to an SF3.
| 02SL - Stations (LUL) | Cxxx-NCR-001080 | NCR | TTH Water supply connection |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-08-10 | 2015-08-17 10:00 | 7 | 2014-08-29 08:56 | Utilities Engineering - Water | 2000 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | A connection was made to a __ main without following the __ approval process.
| 02SL - Stations (LUL) | Cxxx-NCR-001081 | NCR | Upper level liner wall dwidag pull out test |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-10-21 | 2014-09-03 13:57 | -48 | 2014-08-29 15:58 | Shafts - Shafts General | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 3No dwidag bars failed the pullout test for the upper level liner wall pour 4. Investigation into the failures of the 3 bars revealed; - 1No bar was embedded 120mm in to the D wall - 2No bars were embedded 50mm into the D wall
| 02SL - Stations (LUL) | Cxxx-NCR-001082 | NCR | Upper Level Liner Wall Pull out test failure |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-10-08 | 2014-09-04 11:19 | -34 | 2014-08-29 18:26 | Shafts - Shafts General | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | on 28/08/2014 19No dwidag bars were tested on for the Upper level liner wall at CHS, 5No of these bars did not reach the required 75kN pull out test limit therefore failed the test. Investigation found that the bars failed as they did not have sufficient embedment depth.
| 02SL - Stations (LUL) | Cxxx-NCR-001083 | NCR | Excess Cover on Upper Level Liner Wall Pour 4, CHS |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-10-21 | 2014-09-16 13:49 | -35 | 2014-09-03 18:08 | Shafts - Shafts General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Due to the position of the coupler bars for the front face steel on ULLW pour 4 at CHS there is excess cover on the front face reinforcement. The excess cover ranges from 90mm to 100mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001084 | NCR | Undertaking Works without an approved ITP in place |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-12-19 | 2014-12-18 08:24 | -1 | 2014-09-04 09:27 | Electrical - Electrical Engineering General | 1000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Earthing cable was required to be installed prior to backfilling activity. No approved ITP was in place prior to the works.
| 02SL - Stations (LUL) | Cxxx-NCR-001085 | NCR | Failed concrete cube results |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-10-08 | 2014-10-14 13:42 | 6 | 2014-09-05 08:01 | Utilities Engineering - Gas | 1000 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Supervision - Supervisor does not have sufficient experience | Completed |  | Concrete cubes taken for a road sub-base were cast in polystyrene moulds and have failed to meet the specified compressive strengths. See attached test results. The concrete was poured in a trench for gas diversion works near the south west corner of the sports center, see photo.
| 02SL - Stations (LUL) | Cxxx-NCR-001086 | NCR | TTH Steelwork - Incorrect bracket installed above the door post on Gridline B |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-12-04 | 2014-10-03 15:39 | -62 | 2014-09-05 12:05 | Civil - Civil Engineering General | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During completing the snagging works on the TTH steelwork, it has become apparent that the misaligned cladding rails on Gridline B have been caused by the incorrect bracket being installed above the PFC door column (K3021). This has resulted in the cladding rails and top of the door post being 30mm east of where their position should be. This has resulted in the 'bowed' look of the cladding between gridlines 3 and 5 as shown in the marked up sketches attached to this NCR.
| 02SL - Stations (LUL) | Cxxx-NCR-001087 | NCR | TTH cladding rail MC3062 on Gridline F installed incorrectly |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-10-25 | 2014-09-10 14:53 | -45 | 2014-09-05 15:57 | Civil - Civil Engineering General | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On gridline F of the TTH, the cladding rail MC3062 has been installed 180 degrees out of orientation due to the connection cleat on column K3022 being fabricated incorrectly (plese refer to attached photos).
| 02SL - Stations (LUL) | Cxxx-NCR-001088 | NCR | TTH Gridline G anti sag rod extension |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-10-25 | 2014-09-23 10:50 | -32 | 2014-09-05 17:26 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During installation of the anti sag rods on gridline G of the TTH, the sag rod TSA3017 closest to gridline 3 between gridlines 3 and 5 could not be located on site. There was a left over TSA3002 which was 40mm shorter than the required TSA3017. A M12 Grade 8 40mm long hex connector and M12 grade 8.8 threaded bar was installed to complete the anti sag rods in this bay.
| 02SL - Stations (LUL) | Cxxx-NCR-001091 | NCR | DSS - Wall W7-03s void |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-10-28 | 2014-10-28 11:13 | 0 | 2014-09-09 17:00 | Civil - Civil Engineering General | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Wall W7-03s has been cast with a large void forming in the base of the wall. We believe that the void was the result of two factors. 1. The pull out bars which were installed to act as the stair starter bars caused congetion amongst the reinforcement and restricted the flow of concrete to the bottom of the wall. 2. The concrete in this section of wall may not have been adequately pokered at this level as it is evident that there was a flow of concrete through the pull out bars along the remining section of wall.
| 02SL - Stations (LUL) | Cxxx-NCR-001092 | NCR | DSS - Wall W7-02s poured low |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-10-28 | 2014-09-30 11:35 | -28 | 2014-09-10 10:50 | Civil - Civil Engineering General | 1000 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Wall W7-02s has been poured 250mm too low. It was expected to be poured to 20mm above the level 6 slab soffit. The wall was cubed up at 7.5m3 and therefore one full wagon at 7.7m3 was expected to fill the wall. The concrete wagon did not arrive to site with the full 7.7m3 and therefore this left the wall short. As it ws poured on a Saturday evening it was not possible to get another load to site.
| 02SL - Stations (LUL) | Cxxx-NCR-001093 | NCR | DSS - Columns C8-07, C8-08 and C8-12 have been poured too high |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-10-28 | 2014-09-30 11:06 | -28 | 2014-09-10 11:43 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Columns C8-07, C8-08 and C8-12 have been cast too high. The non conformance occured due to mis-interpretation of the drawing. Drawing Cxxx-__M-C-DWG-D061_WS105-50278 has been subject to a number of Field Change Designs with the latest being FCD-000897 (see attached). In the FCD the platform slab which is adjacent to the columns on one side changed levels. It was interpretated from the marked up drawing that so too did the soffit of the drop beam as this was level with the soffit of the platform slab in the original IFC drawing. In fact the level of the drop beam did not change and so the columns were cast too high.
| 02SL - Stations (LUL) | Cxxx-NCR-001095 | NCR | DSS - Column C7-04, insufficient length splice bar |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-10-28 | 2014-09-30 16:03 | -28 | 2014-09-10 12:44 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Columns C7-04 was poured with insufficient splice to C8-04. The lap was measured at 1080mm but the design splice should have been 1250mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001096 | NCR | CHS - Upper level liner wall - starter bars cut short |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-09-26 | 2014-10-06 12:53 | 10 | 2014-09-12 13:11 | Shafts - Shafts General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 4no. starter bars in CHS - ULLW - pours 1 and 2have had to be cut short (from 1.2m to 200mm). This was due to the bars clashing with the stop end shutters for concrete pours 3 and 4. The RMD Walers had to be fixed to the wall where the starter bars were cast in. Two of the bars are type B32 and two are B25. Refer to photos attached
| 02SL - Stations (LUL) | Cxxx-NCR-001097 | NCR | DSS W7-08S connection to W7-02S & C7-04 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-09-26 | 2014-09-22 11:37 | -4 | 2014-09-12 15:44 | Shafts - Shafts General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During installation of W7-08S it was found that some couplers were missing in the ajoining W7-02S and C7-04. In W7-02S - 1no BM09 coupled ubar is missing towards the top of W7-08S, beneath L7 half landing. See attached sketch "missed coupled U bar". In C7-04 - 2no BM64 are missing at the bottom of C7-04. See attached sketch "C7-04 missing couplers".
| 02SL - Stations (LUL) | Cxxx-NCR-001098 | NCR | CHS - ULLW - Pour 3 drainage upstand incorrect |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-06-01 | 2015-06-01 11:09 | 0 | 2014-09-24 17:43 | Shafts - Shafts General | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The cast-in re-bar links for the drainage upstand to the southern end of pour 3 are incorrect. The upstand is a 150 x 150mm concrete box that runs around the circumference of the shaft. The links are 100mm high from the top of upper liner wall concrete level. At the southern end of the wall the last 1.5m of links kick off line, eventually reaching an error of 75mm. An as-built survey has been carried out and is attached to this NCR. __ propose the drainage upstand be modified to suit the location of the re-bar upstand links. Where the links are out of place, the box out should be extended so that there is adequate cover to the steel. The front line of the upstand can maintain its correct location and by extending the rear face will simply mean having an up-stand 225mm wide instead of 150mm locally. The current gap between the rear face of the up-stand and the D-wall is 330mm so with the new position of the upstand a clear gap of 255mm will still be present. See sketch attached showing location of proposed upstand modification.
| 02SL - Stations (LUL) | Cxxx-NCR-001099 | NCR | CHS - Upper level liner wall - pour 2 - cover too large |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-10-03 | 2014-09-26 10:08 | -7 | 2014-09-19 16:06 | Shafts - Shafts General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following a survey of the steel re-bar for CHS upper level liner wall - pour 2, it was found that the cover along a 5m length of cage was too large. Over the 5m section the cover gradually increased from the bottom and sides to a maximum of 100mm cover at the top of the wall. See attachment for survey of re-bar cage and photos of remedial measures.
| 02SL - Stations (LUL) | Cxxx-NCR-001100 | NCR | DSS L6 Stair 5 Starters Omitted |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-12-30 | 2016-11-23 12:20 | -37 | 2014-09-22 10:59 | Shafts - Shafts General | 1500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | DSS L6 slar stair 5 starters have have been omitted from the slab. The temporary void covers on L6 require cast in cones which were installed along the eastern edge of the void. This meant that the projecting starters BM481, BM482, BM485 & BM486 couldn’t be installed because they clashed with the cones and plates. See attached mark-up of 50376 showing which bars were omitted.
| 02SL - Stations (LUL) | Cxxx-NCR-001101 | NCR | LU/LO TTH Column on Gridline G/1 is not plumb |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-11-19 | 2014-11-18 15:25 | -1 | 2014-10-10 15:43 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Column K3017 on the gridline intersection G/1 of the TTH has a verticality difference of 18mm over the height of the TTH (1 storey) as shown in the attached survey drawing. As per section 423A of the TTH civil and structural specification Cxxx-__M-C-RSP-D061-50005, the tolerance for the verticality of a member is +/- 10mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001102 | NCR | DSS - Liner Wall damaged at W7-04s and W8-04s |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-09-27 | 2015-09-29 11:10 | 2 | 2014-09-22 10:58 | Civil - Civil Engineering General | 1500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | A section of liner wall which ties into lift shaft walls W7-04s and W8-04s has been damaged. The coupler bars which were installed in the liner wall to tie into the lift shaft walls were installed with difficulty due to the reinforcment congestion in this section of wall. As a result it wall difficult to expose the couplers in the two tie in points without damaging the thin section between them. (See attached photo)
| 02SL - Stations (LUL) | Cxxx-NCR-001103 | NCR | CHS - Wall W6-03S Incorrect Couplers |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-12-12 | 2014-12-03 13:34 | -9 | 2014-09-24 17:40 | Shafts - Shafts General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | 1) Flight 10's stairwaist stater bars on the north side of wall W6-03S were installed to the incorrect line (please see attched as-built survey). The line of the couplers starts at the low end in the correct position gradually moving out of the stairwaist towards the high end. Approximatley 2/3 of the couplers cannot be used. 2) On drawing Cxxx-__M-C-DWG-D061_WS107-50362 it details two coupler bars on the west end to act as starter bars for the half landing at 94.550m. The drawing shows 1 B20 in the B2 layer (Bm 07) and 1 B16 in the T2 layer (Bm 08). A B16 coupler was installed instead of a B20.
| 02SL - Stations (LUL) | Cxxx-NCR-001104 | NCR | CHS - Cut Starter Bars Column C6-08 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-10-09 | 2014-10-08 11:31 | -1 | 2014-09-25 14:19 | Shafts - Shafts General | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In order to install the Upper Liner Wall Pour 2 shutters, three of column C6-08 starter bars had to be cut. Aproximatley 500mm has been cut from the bar. The length of the starter bars is now 1.04m above the kicker. Please refer to the attached sketches for locations of the cut bars.
| 02SL - Stations (LUL) | Cxxx-NCR-001105 | NCR | CHS - Column C6-04 Incorrect Pour Height |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-10-13 | 2014-10-09 10:09 | -4 | 2014-09-29 08:41 | Shafts - Shafts General | 1500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Column C6-04 was poured to 96.320m instead of 96.620m. The column is currently 300mm low.
| 02SL - Stations (LUL) | Cxxx-NCR-001106 | NCR | Displacement of block wall tie channels on C6-03 and C6-41 at CHS. |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-10-29 | 2014-10-08 15:01 | -21 | 2014-09-29 09:58 | Shafts - Shafts General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | During pouring of columns C6-03 and C6-10 at CHS the 21/18 omega block tie channels have been displaced, see attached photographs.
| 02SL - Stations (LUL) | Cxxx-NCR-001107 | NCR | DSS - Level 6 slab thermal crack |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-06-30 | 2016-08-31 15:32 | 62 | 2014-10-01 10:20 | Civil - Civil Engineering General | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Concrete crack approximately 3m in length for full depth of level 6 slab identified in general location of grid references DSD/DS1
| 02SL - Stations (LUL) | Cxxx-NCR-001108 | NCR | CHS - ULLW - re-bar coming up through toc level |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-02-27 | 2015-02-25 17:14 | -2 | 2014-10-01 14:36 | Shafts - Shafts General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following the completion of pour 2 of the upper liner wall in CHS, it was found that a section of B32 re-bar was coming up out of the top of concrete level. See circled re-bar in attached photo. The bar had been used as gash steel to support the drainage channel being installed, however was not cut down to the correct level following its installation. It is proposed that the steel bar be exposed and cut to a level 50mm below toc level. The concrete surface will then be repaired as per procedure WS106-50002.
| 02SL - Stations (LUL) | Cxxx-NCR-001109 | NCR | CHS-ULLW-exposure of drainage channels damaging concrete |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-05-26 | 2015-04-09 14:24 | -47 | 2014-10-02 10:49 | Shafts - Shafts General | 1500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Drainage channels have been cast into the Upper liner wall in CHS. There is an opening above the wall behind the drainage upstand. The pipe then runs through the wall exiting around 1.5m below the TOC level. It was originally intended that the drainage pipes run through the shutters however it was found that a number of pipes clashed with the strong backs. It was therefore decided to wrap up the end of the pipe (such that a coupler can be fitted) and cast it into the pour. The pipes have then had to be broken out leading to the requirement for repairs on the concrete. See photos attached It is proposed that once the pipework is installed, the concrete will be repaired as per procedure WS106-50002
| 02SL - Stations (LUL) | Cxxx-NCR-001110 | NCR | CHS-ULLW-pour 1 L-bars drilled and fixed |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-11-27 | 2014-10-20 11:12 | -38 | 2014-10-02 14:15 | Shafts - Shafts General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Counterfeit Items | Completed |  | Further to RFI-001932, 11no. L-bars were drilled and fixed into the D-wall. The bars were fixed because a reply to the RFI had not been received. However the decision to install the bars by means of drilling and fixing was based on a very similar earlier RFI (RFI-001916) which specified the 7no. high couplers in pour 4 had to be drilled and fixed rather than omitted. The bars were installed as per the response from RFI-001916 __ propose the bars are left as is.
| 02SL - Stations (LUL) | Cxxx-NCR-001111 | NCR | Damage to New Earthing Cable During Demolition Works in ESS |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-11-26 | 2014-11-12 15:58 | -14 | 2014-10-07 11:16 | Electrical - Electrical Engineering General | 1500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During ESS abutment demolishing for the pile cap installation, the Excavator damage the earthing cable cover (Note: this is a new earthing cable part of ESS construction work)
| 02SL - Stations (LUL) | Cxxx-NCR-001112 | NCR | DSS - Reduced cover in W7-04s |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-12-10 | 2015-11-20 10:39 | -20 | 2014-10-08 12:09 | Civil - Civil Engineering General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There is reduced cover to the reinforcement in wall W7-04s at bthe interface with the liner wall. This was caused as a result of the coupler bars being installed in the liner wall out of position as a result of steel congestion. Corrective procedures for this had also been raised on RFI-Cxxx-002004, however this was not implemented on site.
| 02SL - Stations (LUL) | Cxxx-NCR-001113 | NCR | DSS L6 slab over wall W6-03S |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-11-25 | 2014-10-14 14:28 | -42 | 2014-10-08 17:29 | Shafts - Shafts General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The L6 slab over wall W6-03S has not been poured in pour 1 of L6 slab. The following reinforcement has not been installed: BM765 BM680A BM680B BM682 BM671 BM673 BM531 BM880A BM880B
| 02SL - Stations (LUL) | Cxxx-NCR-001114 | NCR | DSS - Level 6 slab recess out of line in liner wall pour |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-11-25 | 2014-10-14 14:25 | -42 | 2014-10-09 09:57 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A section of liner wall has been cast with the recess boxout out of position. The 1.8m long section was installed 30mm lower than the sections either side of it creating a step in the recess. On the discovery the coupler bars in the area were surveyed to ensure that they were in the correct position to which they were. As the coupler bars are in the correct position the level 6 slab can be cast without any remedial works required to the liner wall along with the 30mm step.
| 02SL - Stations (LUL) | Cxxx-NCR-001115 | NCR | CCTV Box on platform 2 for additional Camera |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-01-07 | 2016-08-09 07:06 | 215 | 2014-10-09 11:48 | Communications and Control Systems - CCTV | 5000 |  | Documentation and Records | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Box installed on East end of platform 2 without a MCR being approved, material is on the LU APR and is suitable for works / environment
| 02SL - Stations (LUL) | Cxxx-NCR-001116 | NCR | Cable Damage to SWA on platform 5 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-01-27 | 2014-12-15 08:31 | -43 | 2014-10-09 11:51 | Electrical - Power Distribution | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Cable damaged on platform 5 outer sheaving, unknown cause.
| 02SL - Stations (LUL) | Cxxx-NCR-001117 | NCR | Hole in Light Fitting case Platform 6 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-01-27 | 2014-10-13 09:44 | -106 | 2014-10-09 11:54 | Electrical - Lighting | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Light fitting on platform 6 has a hole drilled within the outer casing, IP rating of fitting has be compromised.
| 02SL - Stations (LUL) | Cxxx-NCR-001119 | NCR | DSS W8-03S BM28 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-04-01 | 2015-04-01 15:52 | 0 | 2014-10-13 15:42 | Shafts - Shafts General | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 2no BM28 (1no B2 and 1no T2) have been cut to allow installation of formwork. BM28 are starters for L7 landing.
| 02SL - Stations (LUL) | Cxxx-NCR-001120 | NCR | East Stair Shaft - Failure to Request Witness Inspection of Lightning Protection |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2014-11-20 | 2014-10-28 11:26 | -23 | 2014-10-14 14:24 | Electrical - Electrical Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | On Monday 13th October 2014, the contractor had planned a concrete pour to pile caps in the East Stair Shaft. In advance of this pour, main lightning protection earth tapes installed to steelwork would require testing, inspection and wrapping with denso tape. The contractor failed to raise an IRF or otherwise notify the Project manager of the requirement to inspect the integrity of bonding connections to the steelwork and witness satisfactory resistance testing of each earth tape, prior to the planned concrete pour, defined as Witness points in sections 4.1 and 5.5 of the approved ITP Cxxx-__M-E-ITP-D061_WS106-50009. The Contractor (__) subsequently presented the Project manager (Torrie) with photographic evidence of satisfactory resistance test results on Tuesday 14th October.
| 02SL - Stations (LUL) | Cxxx-NCR-001121 | NCR | CHS - Earthing cable around Column 08 |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2015-04-01 | 2015-02-09 11:35 | -51 | 2014-10-14 15:46 | Electrical - Electrical Engineering General | 500 |  | Planning | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The earthing cable at Level 8 has been installed wrapping around column 08. In all other other areas, i.e. Wall 06S, the Contractor has installed the earthing cable flush against the liner wall and / or cast it within the pour. Drawings Cxxx-__M-E-DDD-D061_WS107_8-30016 and Cxxx-__M-E-DDD-D061_WS107_Z-30018 provide typical earthing details. However as column 08 was cast before the earthing cable was installed the Contractor now requires a detail confirming how the earthing cable should pass around or through the column. (See attached photographs for further details). In addition, the Contractor failed to raise an IRF or otherwise notify the Project Manager of the requirement to inspect the installation of the earthing and bonding cable and fixings as defined as Witness points in section 4.1 in accordance with the approved ITP Cxxx-__M-E-ITP-D061-50005.
| 02SL - Stations (LUL) | Cxxx-NCR-001122 | NCR | Utilities Sub-contractor Construction Records |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-11-18 | 2014-10-28 11:28 | -21 | 2014-10-15 18:39 | Civil - Utilities Engineering | 1500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | Insufficient records relating to the concrete sampling for Utilities works. UKAS concrete sampling forms for the concrete road base was not produced bu Utiliies works sub-contractor.
| 02SL - Stations (LUL) | Cxxx-NCR-001123 | NCR | Commencment of works without an agreed sub-contractor quality plan in place |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-11-14 | 2014-11-13 07:52 | -1 | 2014-10-16 16:33 | Archaeology - General | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | __ have started work without an accepted Quality Plan in place
| 02SL - Stations (LUL) | Cxxx-NCR-001124 | NCR | CHS - Missing couplers wall W7-04S and Level 7 Slab |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-10-31 | 2014-10-31 10:53 | 0 | 2014-10-17 11:24 | Shafts - Shafts General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In wall W7-04S nineteen B16 couplers have been cast in the wrong location or have moved during the casting process, BM 03 (see attached sketch). In the Level 7 slab three couplers have been cast in the wrong location or have moved during the casting process BM 522, 523, 537 (see attached sketch).
| 02SL - Stations (LUL) | Cxxx-NCR-001125 | NCR | DSS L6 slab south - BM883 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-11-25 | 2014-11-25 08:40 | 0 | 2014-10-21 09:23 | Shafts - Shafts General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Drawing Cxxx-__M-C-DWG-D061_WS105-50379 rev C02 shows 38no BM697 installed into A12 couplers in the liner wall in B3. Only 35no A12 couplers were found in the liner wall, 1no of which was angled upwards and was unusable. Drawing Cxxx-__M-C-DWG-D061_WS105-50469 rev C02 shows 38no BM883 installed into A12 couplers in the liner wall in T3. Only 35no A12 couplers were found in the liner wall.
| 02SL - Stations (LUL) | Cxxx-NCR-001126 | NCR | DSS L6 slab south trimmer couplers missing |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-11-25 | 2014-10-28 11:34 | -28 | 2014-10-21 09:47 | Shafts - Shafts General | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Couplers for the following bars could not be found when installing reinforcement in the L6 slab south pour: - drg Cxxx-...-50379 C02 BM681b couplers in north pour missing - drg Cxxx-...-50379 C02 BM680b 1no coupler adjacent to void too close to corner of void and therefore unsable - drg Cxxx-...-50379 C02 BM692b couplers in north pour missing - drg Cxxx-...-50469 C02 BM881b couplers in north pour missing - drg Cxxx-...-50469 C02 BM880b 1no coupler adjacent to void too close to corner of void and therefore unsable See sketch attached.
| 02SL - Stations (LUL) | Cxxx-NCR-001128 | NCR | Project Managers acceptance of all individual responsible for undertaking design |  | Crossrail | PDP | WHI - Whitechapel Station (Central) |  | 2015-03-10 | 2015-03-12 18:19 | 2 | 2014-10-21 11:40 | Mechanical - Mechanical Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | There remains the requirement for all individuals responsible for undertaking design to have Project Manager acceptance- acceptance in place for only 2 personnel
| 02SL - Stations (LUL) | Cxxx-NCR-001129 | NCR | No MCR for Comms enabling equipement |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-08-15 | 2015-06-01 15:58 | -75 | 2014-10-26 15:19 | Communications and Control Systems | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | original NCR details The COMMs sub-contractor has not provided MCR for the following items prior to installation on site for the enabling works: Junction Boxes for PA / Dim Rail & Connector Blocks / Labels on Cable / Labels on equipment / Cable for PA / Cable for Cameras. revised NCR details as the installation of these materials were historic (works undertaken by previouse MEP department no longer on the project) further investigation for the full scope of materials is still ongoing. After further investigation these materials were subbmitted to CRL through Decal, it is though at this time that this was prior to the current MCR process being created (the following links to historic documents have been added Cxxx-__M-C-XDS-D061-50001, Cxxx-__M-C-XDS-D061-50002, Cxxx-__M-C-XDS-D061-50004). Since these documents were approved further MCR within the electronic eB format have been submitted and apporved, these links have also been added CRL-MCR-001025 __ Cable ID Labels, CRL-MCR-001026 __ Cable Markers Since these documents were approved further MCR within the electronic eB format have been submitted and are with CEG, These links have been added CRL-MCR-000977 __ - Coaxial Cable - H124C02 Does the project manager require all historic materials to be approved on the online eB format
| 02SL - Stations (LUL) | Cxxx-NCR-001131 | NCR | TTH Drainage Air Test Failure |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-08-31 | 2015-07-29 15:13 | -33 | 2014-10-24 12:52 | Civil - Drainage | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On completion of the TTH Drainage run an Air test was scheduled to be carried out as per 3.6 in the ITP, Cxxx-__M-C-ITP-D061-50144. Although tests have previously been carried out on the drainage and they passed, in this instance the system was unable to retain air pressure. On further insepction of the testing apparatus and run it was discovered that 2No Cracks were present in the vertical stacks of the drainage, which were resulting in the run failing the air test.
| 02SL - Stations (LUL) | Cxxx-NCR-001132 | NCR | TTH - Cladding Secondary Support Rails |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-01-14 | 2014-12-05 11:18 | -40 | 2014-10-24 12:59 | Architectural - General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On the North elevation , Grid 1 and 2, East elevation Grid G, the installation as detailed in drawing D512-__M-C-DWG-D061-50498 rev0.1 has been carried out by notching the secondary support rails in order to avoid clashing with the support flashing. Following investigation and the RFI C12-__-LKM-002 this method has been deemed unsuitable in this instance and corrective measures are required.
| 02SL - Stations (LUL) | Cxxx-NCR-001133 | NCR | TTH Rodding eye location |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-09-01 | 2015-08-24 17:31 | -8 | 2014-10-24 16:29 | Civil - Drainage | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Drawing Cxxx-__M-C-DWG-D061-50132 shows RE2 located 2m east of the ACO drain outside the TTH. The pipe for the rodding eye was installed at 45 degrees to allow easy access for drain clearing operations. As a result, the rodding eye now immediately adjacent to the TTH and will clash with a proposed ACO channel.
| 02SL - Stations (LUL) | Cxxx-NCR-001134 | NCR | TTH Installation of Roof Gutters |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-12-10 | 2014-11-27 15:35 | -13 | 2014-10-30 13:41 | Architectural - Roofing & Exterior Treatment | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On 22.10.2014 the installation of the square through wall outlets o the high level roof, grid line 3, internal parapet, has been carried out using the incorrect parts. As described in drawings Cxxx-__M-C-DWG-D061-50251/50260, the 100mm wall outlets should have been used.
| 02SL - Stations (LUL) | Cxxx-NCR-001135 | NCR | Error on NCR 001124 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-11-17 | 2014-11-03 12:56 | -14 | 2014-11-03 09:43 | Shafts - Shafts General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | NCR, Cxxx-NCR-001124 was raised and closed with the incorrect level referanced in the subject and text. The subject on NCR 001124 should read - CHS - Missing Couplers wall W7-04S and LEVEL 6 Slab. Where the Level 7 slab is referanced it should read Level 6.
| 02SL - Stations (LUL) | Cxxx-NCR-001136 | NCR | Utility wall breakout works commenced without Permit to Demolish |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-12-10 | 2014-12-10 16:26 | 0 | 2014-11-03 17:26 | Utilities Engineering - Utilities General | 1000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | A Permit to Demolish was not in place prior to works commencing as stated in ITP Cxxx-__M-C-ITP-D061-50132, item no 3.2. This is also a requirement of Works Information Vol 2B, Clause 19.7.9.6.
| 02SL - Stations (LUL) | Cxxx-NCR-001137 | NCR | Platform 2 :Pile Installation |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-04-01 | 2015-02-24 14:34 | -36 | 2014-11-05 11:58 | Civil - Civil Engineering General | 2500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Pile 86 was installed on 28/10/2014. The as built top of cage level is 109.5mATD 150mm below the required level of 109.65mATD. Pile 92 was installed on 30/10/2014. The as built top of cage level is 109.5mATD 150mm below the required level of 109.65mATD. The ITP states the tolerances are +150mm/-50mm Drawing Number: Cxxx-HYD-S-DDL-D061_WS106_Z-74004
| 02SL - Stations (LUL) | Cxxx-NCR-001138 | NCR | omission of angle filet to CHS C5-45 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-07-27 | 2015-06-15 16:03 | -42 | 2014-11-07 15:43 | Shafts - Shafts General | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Column C5-45 has been cast without angle filet on the Southern corners.
| 02SL - Stations (LUL) | Cxxx-NCR-001140 | NCR | Non-compliant Temp Works rebar cages ordered and delivered to site for WInthrop Street Bridge Piling Works |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-01-20 | 2014-12-05 15:56 | -46 | 2014-11-12 11:16 | Structural Engineering - Reinforcement | 12500 |  | Planning | Rework | 2 (6-60k) | Complete | Subcontractor Problems - Insufficient work planning by the subcontractors | Completed |  | The design intent for rebar cage for Winthrop Street Bridge Piles (Temporary Work Piles) was done by Bacsol and further reinforcement detailing were proposed by BacSol using a third party entity. The fabrication drawings were not sent to __ for approval and was ordered accordingly. Prior to install, the cages were checked onsite and discovered that the cages did not meet design intent of 1m splice length. The ordered cages only had 0.5m splice length. The existing cages is to be modified to cater for the 1m splice length, and extra cages to be ordered to accommodate the correct splice length.
| 02SL - Stations (LUL) | Cxxx-NCR-001142 | NCR | CHS - ULLW - Level 5 drainage upstand links incorrect |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-06-15 | 2015-06-15 13:03 | 0 | 2014-11-13 15:16 | Shafts - Shafts General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following a survey of a section of the drainage upstand links at the top of the upper Level Liner Wall (ULLW) in CHS, it was found a number of links were out of place. A full survey has been carried and is attached below. It may be seen in the survey that no links are out of place in the eastern side of the shaft. in the remaining two thirds of the shaft, a number of links are out of tolerance. it is proposed that in the Northern, Western, and Southern sections of the shaft the outer radius of the drainage upstand be changed to 13.775 (50mm larger than the original radius). This means there will be enough cover on all the links in their current locations. There is currently a 200-300mm gap between the back of the drainage upstand and the D-wall so increasing the outer radius of the upstand will not affect the channel behind. In areas where the cover is too great an extra reinforcing bar will be tied to the link to bring this back within tolerance.
| 02SL - Stations (LUL) | Cxxx-NCR-001143 | NCR | Pull out bars in the upper ring beam not inside pour area for W6-14NS |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-01-27 | 2014-12-03 11:24 | -55 | 2014-11-14 16:52 | Shafts - Shafts General | 4500 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 18no B12 pull out bars for W6-14NS from drawing Cxxx-__M-C-DWG-D061_WS107-50012 are missing. Area of wall has been scabbles and broken back and bars can not be located.
| 02SL - Stations (LUL) | Cxxx-NCR-001144 | NCR | Coupler bars missing on Stairs flight 7 in W6-03s and W6-02s |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-12-01 | 2014-12-03 08:31 | 2 | 2014-11-17 10:08 | Shafts - Grouting | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 1) There are 2 b16 couplers missing for the stair waste in flight 7 and 8 in W6-03, W6-04 and W6-02s kickers and slab. The couplers were missed out during the pouring of the wall kickers and slab. The number of couplers in the walls for stairs flight 7 is correct as per the drawings but there is excess spacing between couplers in the kickers, see attached drawing for location 2) 5 no couplers are have cover to that is outside of spec in the half landing for Flight 7, See attached drawing for location
| 02SL - Stations (LUL) | Cxxx-NCR-001145 | NCR | CHS - Concrete finish to walls W5-04S & W5-05S |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-08-07 | 2015-08-06 13:52 | -1 | 2014-11-19 10:31 | Shafts - Shafts General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following striking of the shutters to walls W5-04S and W5-05S it was discovered that ridges were present on the face of the walls in a couple of locations. On Wall W5-05S the ridges are on the East face of the wall. On Wall W5-04S the ridges are on the Southern face of the wall.
| 02SL - Stations (LUL) | Cxxx-NCR-001146 | NCR | Couplers for Level 5 slab pour 2 in cover zone |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-01-14 | 2015-01-15 14:01 | 1 | 2014-11-20 18:17 | Shafts - Shafts General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 4 no couplers in C5-03 for pour 2 of the level 5 slab are inside the cover zone. The couplers are B32 located in the T1 layer. See attached marked up drawing. The couplers are located on the north and south faces of C5-03.
| 02SL - Stations (LUL) | Cxxx-NCR-001147 | NCR | Southern void level 5 slab has incorrect dimensions |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-01-20 | 2014-12-05 15:50 | -46 | 2014-11-21 08:45 | Shafts - Shafts General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the pour of the level 5 slab the shutter on the Grid Line D beam in the southern void shifted. The shutter was refixed and replumbed but wall was found to be 20mm out at the worst position when the as built was completed, see attached as built and level 5 slab drawing for location and as buit details.
| 02SL - Stations (LUL) | Cxxx-NCR-001148 | NCR | HCDL Platform 2 Piles (PA85) - pile cage installed incorrectly (coupled out of the correct sequence) |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-01-30 | 2015-01-28 17:00 | -2 | 2014-12-01 13:15 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | Pile cage was installed incorrectly. The error was spotted by the CRL FE at the time and the error was rectified on site. The NCR has been raised relating to insufficient checking being undertaken by the Cxxx engineer in charge of the works and therefore not discharging the inspection hold point on the ITP.
| 02SL - Stations (LUL) | Cxxx-NCR-001149 | NCR | Concrete Testing Competence Records |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-01-15 | 2015-01-15 14:12 | 0 | 2014-12-01 16:20 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Improper resource allocation | Completed |  | During a surveillance of the East Stair Shaft Portal Frame concrete pour, the engineer undertaking the slump testing was found to have no docuemnted evidence in being trained to undertake slump testing for self compacting concrete.
| 02SL - Stations (LUL) | Cxxx-NCR-001151 | NCR | No IRF for __ Duct |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-12-17 | 2014-12-10 16:23 | -7 | 2014-12-03 12:13 | Utilities Engineering - Telecomms | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A 3m section of __ duct was installed without Crossrail being given the opportunity to inspect witness points 4.1-4.5.
| 02SL - Stations (LUL) | Cxxx-NCR-001152 | NCR | TTH Earthing – Works not covered by existing ITP |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-02-11 | 2015-01-15 15:36 | -27 | 2014-12-04 15:39 | Electrical - Electrical Engineering General | 2500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Exothermic was required on site. The revision of the ITP Cxxx-__M-E-ITP-D061_WS106-50006 at the time of the work did not have exothermic welding activities detailed.
| 02SL - Stations (LUL) | Cxxx-NCR-001153 | NCR | TTH Lighting Cable Installation - number of cables provided |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-01-19 | 2015-01-15 17:10 | -4 | 2014-12-04 16:23 | Electrical - Cable Management | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There are 10 light fittings identified on the drawing but 13 cables were installed.
| 02SL - Stations (LUL) | Cxxx-NCR-001154 | NCR | TTH Lightening Protection Cable MCR and Aluminium Tape |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-01-19 | 2015-01-08 16:05 | -11 | 2014-12-04 16:42 | Electrical - Electrical Engineering General | 2500 |  | Material | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | Cxxx-__M-E-LRC-D061-50070 Rev 2.0 is at Code 1. The scope of the MCR does not cover use in the LU/LO environment, However, the MCR - CRL-MCR-00478 that does cover LU/LO is yet to be approved before works was carried out. Additionally, the tape installed at the upper levels is alumimium, not copper - we do not currently have an MCR for aluminium tape.
| 02SL - Stations (LUL) | Cxxx-NCR-001155 | NCR | TTH Lighting Cable Installation |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-10-09 | 2015-10-15 18:09 | 6 | 2014-12-05 10:10 | Electrical - Electrical Engineering General | 1000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | The lighting cable installation to the north elevation of the Ticket Hall over the weekend 01-02 November was undertaken to a sketch detail that is not included in the current set of C01 drawings. There is no FCD in place to confirm whether the detail is acceptable.
| 02SL - Stations (LUL) | Cxxx-NCR-001156 | NCR | TTH Level A Slab Remedial Works |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-08-15 | 2015-06-20 10:53 | -56 | 2014-12-06 12:29 | Civil - Civil Engineering General | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Remedial works on Level A of the the TTH were damaged as they were not sufficiently protected.
| 02SL - Stations (LUL) | Cxxx-NCR-001157 | NCR | DSS - Void under bottom step of flight 2 Stair 2 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-09-20 | 2015-09-21 13:51 | 1 | 2014-12-08 14:20 | Shafts - Shafts General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | It was noticed during striking of flight 2 of stair 2 that a void is present under the bottom step.
| 02SL - Stations (LUL) | Cxxx-NCR-001158 | NCR | Damage lintel during trough installation |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2014-12-22 | 2014-12-17 07:49 | -5 | 2014-12-08 18:47 | Utilities Engineering - Utilities General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The existing utility appears to be located approximately 70mm further south than indicated by on DWG 60115. As a result, trough section 'D' clashed with the concrete lintel that had been cast into retaining wall W615. The lintel was damaged when operatives attempted to removed the section of lintel that was causing the obstruction.
| 02SL - Stations (LUL) | Cxxx-NCR-001159 | NCR | Works proceeding without approved FCD |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-01-23 | 2015-01-19 15:19 | -4 | 2014-12-09 17:55 | Utilities Engineering - Water | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | __ diversion works installed different to design without approved FCD.
| 02SL - Stations (LUL) | Cxxx-NCR-001161 | NCR | Incorrect Mix design used in DSS Level 5 slab North pour |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-02-23 | 2015-02-23 10:16 | 0 | 2014-12-15 18:29 | Shafts - Shafts General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Level 5 slab drawing Cxxx-__M-C-DWG-D061_WS105-50491 note C1 details a C40/50 concrete. The level 5 slab north pour was poured with a C32/40 (line 260).
| 02SL - Stations (LUL) | Cxxx-NCR-001162 | NCR | W5-03s poured high |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-02-23 | 2015-01-27 16:10 | -27 | 2014-12-16 10:09 | Shafts - Shafts General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Wall W5-03s was poured to high during the construction of level 5 walls and columns. The RL of the top of the wall is 101.830, this is 185mm higher than the design level of 101.645. This height difference means that there have been couplers for level 4 pour 2 that have been left out. See highlighted barmarks on attached drawing for missing couplers.
| 02SL - Stations (LUL) | Cxxx-NCR-001163 | NCR | CHS - Discrepancy between Cxxx and Cxxx drawings |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-02-23 | 2015-01-05 11:32 | -49 | 2014-12-17 12:47 | Shafts - Shafts General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please refer to the attached sketch and drawings Cxxx-HYD-C-DDL-D061_WS107_4-24205-C03 and Cxxx-__M-C-DWG-D061_WS107-50394-C01. After the completion of the level 4 slab it was dicovered that there was a discrepancy between the Cxxx drawing and the Cxxx drawing. On the Cxxx drawing it details a nib on the west side of the GL D beam south of GL 4 (see attached sketch). This nib was not detailed on the Cxxx drawings. The Cxxx drawings were reviewed by Cxxx and up reved to construction issue after the review process. The level 4 slab was then constructed to the code 1 Cxxx drawings.
| 02SL - Stations (LUL) | Cxxx-NCR-001164 | NCR | Utility Trough - Steel lid f__ent |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-01-22 | 2015-01-27 14:52 | 5 | 2014-12-23 13:28 | Utilities Engineering - Utilities General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Due to the exit angle of the water pipes in the utilities trough, lid sections H3 and H4 do not sit correctly on the trough.
| 02SL - Stations (LUL) | Cxxx-NCR-001165 | NCR | Finish on Wall W4-05s out of tolerance |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-08-10 | 2015-08-05 12:27 | -5 | 2015-01-07 17:02 | Shafts - Shafts General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Wall W4-05s has a lip in the finish of the wall where the two half shutters were fitted together on the western face of the wall. The lip is 10mm at the worst place, see attached photos
| 02SL - Stations (LUL) | Cxxx-NCR-001167 | NCR | DSS - W6-04S prepour inspection |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-12-10 | 2015-11-20 10:30 | -20 | 2015-01-06 18:41 | Shafts - Shafts General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the post pour inspection of W6-04S it was noticed in the south west corner of the lift shaft where it ties into the liner wall that the line of the wall was incorrect. The shutter was either installed incorrectly or moved during the concrete pour.
| 02SL - Stations (LUL) | Cxxx-NCR-001168 | NCR | Water main - failed pressure test |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-02-04 | 2015-01-19 07:44 | -16 | 2015-01-07 17:40 | Utilities Engineering - Water | 5000 |  | Workmanship | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the pressure test carried out on the new installed water main, the pipework has failed its pressure test which was witnessed by __ (Jan Pretorius). The Leak is suspected to be on the D/I bolted connection.
| 02SL - Stations (LUL) | Cxxx-NCR-001169 | NCR | DSS - Internal line of W6-04S out of tolerance |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-09-09 | 2016-09-06 14:46 | -3 | 2015-01-08 08:49 | Shafts - Shafts General | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During construction of the kickers for W6-04S it was noticed that the top of W7-04S was out of line at Level 6. W6-04S was poured in the correct location but as a result a lip is present between W7-04S and W6-04S.
| 02SL - Stations (LUL) | Cxxx-NCR-001170 | NCR | Works Proceeding without an approved ITP - Sub Mains from Substation to E51 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-03-06 | 2015-03-05 14:18 | -1 | 2015-01-08 11:01 | Electrical - Cable Management | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | The CMS works for the cabling commenced without the ITP in place
| 02SL - Stations (LUL) | Cxxx-NCR-001171 | NCR | CCTV ITP - Insufficient activities detailed |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-03-27 | 2015-03-30 15:02 | 3 | 2015-01-08 11:05 | Communications and Control Systems - CCTV | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | The ITP Cxxx-__M-R3-ITP-D061_WS106-50001 Rev 1.0 does not contain the CCTV FAT Test scheduled for 08/01/14. The FAT procedure has subsequently not been issued to CRL for approval prior to the activity. At the time of the activity, the ITP status is Code 3.
| 02SL - Stations (LUL) | Cxxx-NCR-001172 | NCR | Reduced cover on C6-16 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-01-22 | 2015-01-27 16:12 | 5 | 2015-01-08 15:11 | Shafts - Shafts General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There is reduced cover on C6-16 on the eastern face
| 02SL - Stations (LUL) | Cxxx-NCR-001176 | NCR | Couplers for stairs flight 11 and 12 not installed in kicker |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-01-27 | 2015-01-29 15:49 | 2 | 2015-01-13 11:28 | Shafts - Shafts General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Couplers for the stairs flight 11 and flight 12 were not installed in the kicker of W5-03, W5-04 and W5-02. The number of couplers in each flight of stairs is correct as per the drawing however there is a gap of 400mm where there are no couplers installed. See attached highlighted drawing for location details.
| 02SL - Stations (LUL) | Cxxx-NCR-001177 | NCR | LU/LO Area 1 beam top flanges unpainted |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-06-22 | 2015-02-09 15:00 | -133 | 2015-01-23 16:09 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In meeting the metal decking ITP requirements of item 3.2, the top flanges of the beams in the Area 1 steelwork were not painted during fabrication. This now implies that potentially the steelwork does not comply with Annex D of the Materials and Workmanship Specification for Steelwork KM10.
| 02SL - Stations (LUL) | Cxxx-NCR-001178 | NCR | LU/LO Omitted Mild Steel Plate Under Truss 1 and 2 at the Platform 5 Cill Beam |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-02-21 | 2015-02-05 10:56 | -16 | 2015-01-22 15:41 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In compiling the QA package for the Area 1 steelwork, it has been noticed that the 650 x 400 mild steel packing plates have not been installed under the trusses on the platform 5 cill beam. This was required under dwg Z_76007 detail 29 and also Cxxx-RFI-001367. The steelwork subcontractor has designed this connection as having a grout base which has been installed on site. This is reflected in the approved Area 1 CATIII connection design and also the approved CATIII shim design referenced to this NCR. The grout has achieved the minimum strength of 40N/sq.mm as is in the construction records for the area.
| 02SL - Stations (LUL) | Cxxx-NCR-001180 | NCR | LU/LO Use of non approved material to seal metal decking |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-05-01 | 2015-03-16 09:22 | -46 | 2015-01-22 14:27 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Material used on site without an approved MCR in place on Area 1 metal deck, TTH metal deck and Western SME metal deck. MCR was submitted on 11/12/2014 and is now coded as code 3 but no PMC has been received to date. It is noted that there are no approved sealants on the LU-APR suitable for sealing the metal decking required in the works information drawings. This product seals the decking and is then ultimately buried in concrete. In the majority of places the sealing is over a joint above a beam where the beam will also receive fire protection fully isolating this product from any fire for the duration of the fire protection in that area. 1-085 clause 3.4.1 g) is ambiguous is defining a total area in which the product is limited to 100g and 0.2 sq.m. MCR reference: Cxxx-__M-C-LRC-D061_WS106-50027
| 02SL - Stations (LUL) | Cxxx-NCR-001181 | NCR | DSS - W7-04S out of tolerance |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-02-06 | 2015-02-09 12:14 | 3 | 2015-01-23 11:13 | Shafts - Shafts General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The walls of W7-04 are out of tolerance by up to 66mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001182 | NCR | TTH - Staircase Stub Installed in the wrong location |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-02-06 | 2015-02-10 10:27 | 4 | 2015-01-23 17:16 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The TTH stub S3602 was installed at the incorrect height on site due to the wrong existing holes being used to measure off and drill the new holes due to a design change on the TTH staircase. On the following nightshift this stub was removed, the column redrilled and then the stub re-installed at the correct height. A level survey carried out confirmed with stub was within position to the nearest millimetre.
| 02SL - Stations (LUL) | Cxxx-NCR-001183 | NCR | CHS - Level 4 Pour 2 West couplers cast incorrectly |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-02-27 | 2015-02-16 09:28 | -11 | 2015-01-26 08:04 | Shafts - Shafts General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please refer to the attached sketches. During the construction of the level 4 slab BM 274, 275 and 1 of BM 297 were installed at the incorrect level. The couplers were installed to low therefore there would be insufficent cover to the reinforcement.
| 02SL - Stations (LUL) | Cxxx-NCR-001184 | NCR | LULO - ESS Lift Shaft - cold joint in Pour 3a |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-03-20 | 2015-02-25 17:24 | -23 | 2015-01-29 11:25 | Structural Engineering - Concrete Member | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Due to slow concrete supply from __ during the completion of pour 3a to the ESS Lift shaft, a cold joint has formed. NOTE: THIS WAS A SELF COMPACTING CONCRETE POUR.
| 02SL - Stations (LUL) | Cxxx-NCR-001185 | NCR | TTH Roof - Waterproofing/Insulation Damage |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-07-01 | 2015-06-20 11:47 | -11 | 2015-01-29 14:42 | Architectural - Roofing & Exterior Treatment | 40000 |  | Damaged | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The roofing works to the TTH have been damaged during installation. The waterproofing system was interrupted due to inclement weather meaning the system was incomplete. The incomplete works were not protected and access was not restricted to the roof. The primer subsequently was cracked an has allowed water to penetrate the insulation. The damaged roof has been exposed to further inclement weather which has been detrimental to the condition.
| 02SL - Stations (LUL) | Cxxx-NCR-001186 | NCR | TTH External Windows |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-06-24 | 2015-05-30 13:54 | -25 | 2015-01-29 14:45 | Architectural - Glazing | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient surveillance of subcontractors | Completed |  | 3 No. External window frames were installed on Grid Line 3 of the TTH without approved documents or a LONO for the associated works and without providing a sample.
| 02SL - Stations (LUL) | Cxxx-NCR-001187 | NCR | Use of Non Approved Materials on Site TTH |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-06-24 | 2015-05-30 14:09 | -25 | 2015-01-29 14:52 | Civil - Civil Engineering General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient surveillance of subcontractors | Completed |  | Materials have been installed in the TTH prior to receiving approval of the MCR. The materials include: __ 600 __ __ K 301 Self Levelling Compound
| 02SL - Stations (LUL) | Cxxx-NCR-001188 | NCR | LU/LO Area 1 metal decking edge trim |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-10-21 | 2015-09-21 08:59 | -30 | 2015-02-03 15:27 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | An as-built survey has been undertaken on the Area 1 metal decking of the permanent edge trims installed to date. The attached drawing shows the edge trim offset values as sruveyed (highlighted green for within tolerance and red for out of tolerance). Taking into account the causes below, it was proposed to use as is. However the architect __ has now confirmed that this slab detail needs to remain as designed. Therefore __ will move the walkway scaffold in engineering hours to accomodate the design line of the metal deck edge trim and then the metal edge trim will be moved into the correct position.
| 02SL - Stations (LUL) | Cxxx-NCR-001189 | NCR | Winthrop Ground Retention Solution - Pile and Pile Cap Issues - East Abutment |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-03-10 | 2015-03-04 12:24 | -6 | 2015-02-10 14:39 | Civil - Geotechnical Engineering | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 3 Short piles omitted, Nos P19, P20 and P49 due to existence of mass concrete. Pile 26 moved to aovid clash with protective measures to live HV and LV cables. Pile 27 poured to piling platform level and bled after casing extraction ending approx 1.1m below piling platform level. Raking piles R08, R09, R10, R11, R12, R13 & R14 installed approximately 270mm out of position due to set out error. Pile 22 bored to depth of 14.1m and 6 x B25 cage installed as the foundation was not encountered.
| 02SL - Stations (LUL) | Cxxx-NCR-001190 | NCR | DSS - Level 5 South pour concrete out of spec. |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-04-29 | 2015-05-01 14:20 | 2 | 2015-02-04 09:46 | Shafts - Shafts General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 5No concrete wagons were out of the specified S3 slump specification. The ticket numbers were 617454 (220), 617455 (220), 617461 (230), 615508 (60), 615507 (60)
| 02SL - Stations (LUL) | Cxxx-NCR-001191 | NCR | TTH Concrete Slab Interface GL G |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-08-15 | 2015-08-14 08:00 | -1 | 2015-02-10 13:18 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The TTH ground floor slabs have been cast. There are two locations where the slab is cast incorrectly; GL 3G and GL 5G, see attached photographs. At GL 3G the slab should have been boxed out around the steel column to facilitate the construction of a brick plinth. Please see attached drawing, detail 6. Cxxx-__M-A-DWG-D061-50045 C01 At GL 5G the slab level should have been cast at +113.345 and then built up using a 130mm thick screed to FFL. The collapsible gate track was to be cast in this screed. Please see attached drawings: Cxxx-__M-C-DWG-D061-50167 Cxxx-__M-C-DWG-D061-50122 Cxxx-__M-A-DWG-D061-50051 C01
| 02SL - Stations (LUL) | Cxxx-NCR-001192 | NCR | TTH Drainage RE2 Location |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-10-31 | 2015-10-28 09:24 | -3 | 2015-02-11 10:09 | Civil - Drainage | 6000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The TTH drainage has been installed in the incorrect location. The sub-contractor __ installed the drainage run without setting out as per drawing Cxxx-__M-C-DWG-D061-50132.
| 02SL - Stations (LUL) | Cxxx-NCR-001194 | NCR | Unapproved Material Used on Site - Tack Coating |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-03-20 | 2015-03-03 13:44 | -17 | 2015-02-16 10:43 | Civil - Roadworks Formation | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | Tack coat applied before asphalting works. Tack coat does not have an MCR, although an MCR number was generated on EB.
| 02SL - Stations (LUL) | Cxxx-NCR-001195 | NCR | West Stair Shaft Pile # 5 toe level and steel level installed low |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-05-30 | 2015-06-02 10:06 | 3 | 2015-02-17 15:32 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Pile 5 was the first pile to be installed on the West Stair Shaft. The design toe level is 100m and the top level of the projecting steel into the pile cap is 112.440. Casings were installed to a depth of 107.5m and the pile was drilled to a depth of 100m. (as per drawing Cxxx-HYD-C-DDB-D061_WS105_Z-23041, the casing should have been installed to 103.5) The augurs were removed however, prior to installing the rebar cage the bottom section of the pile collapsed inwards. Water was also present. Two more attempts were made to drive casing deeper and bore the pile. Finally, casings were installed to a depth of 99m with the toe of the pile extending to 97.8m. The rebar cage was install in chaired on feet to the correct level. During the concrete operation however it was noticed that the case had settled approximately 250mm Since this first pile was installed, 6 more piles have been drilled. All casing have been installed to the intended level of 103.5 with no issues of water or the base of the pile collapsing.
| 02SL - Stations (LUL) | Cxxx-NCR-001196 | NCR | DSS L6 _ Damage to coupler in C6-38 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-03-20 | 2015-03-05 16:10 | -15 | 2015-02-17 17:08 | Civil - Civil Engineering General | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Upon compiling the Quality pack for the level 6-7 liner wall, it has been discovered that an NCR was not raised at the time of the non-conformance and has not been raised since. PLs see the details below which relate to non-conformance on the 5/8/14 Further to ‘Cxxx-NCR-000885’ and ‘Cxxx-NCR-000889’ pls see the remedial action for column C6-38 The coupler circled in red on drawing ‘Cxxx-__M-C-DWG-D061_WS105-50361, NCR Sketch’ was damaged during the excavation stage. The coupler was found to be un-usable . BM 844 and BM 877 (an straight and an L bar) were supposed to be installed in this coupler which project into the column. The adjacent coupler circled in blue on drawing ‘Cxxx-__M-C-DWG-D061_WS105-50361, NCR Sketch’ was supposed to have a straight bar (BM 844) protruding from it (Originator: __)
| 02SL - Stations (LUL) | Cxxx-NCR-001197 | NCR | DSS L6-L7 Lwall _ Incorrect reinforcement check sheet used |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-03-03 | 2015-02-25 11:32 | -6 | 2015-02-17 17:25 | Shafts - Shafts General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Upon compiling the information for the Quality Handover pack for the DSS level 6-7 liner walls, it has become apparent that the reinforcement check sheet used is not as per the check sheet referenced in the ITP ITP # Cxxx-__M-C-ITP-D061-WS105-50031 section 5 ‘Reinforcement references check sheet D3-39. Pours 1-7 have been filled out using check sheet D3-26, Pour 8 has used the correct check sheet D3-39 All the non-conforming check sheets are signed by both CRL, __ and IDI and contain the same information as the conforming check sheets. All pours have also had IRF completed for the reinforcement signed by both CRL and IDI (Originator: __)
| 02SL - Stations (LUL) | Cxxx-NCR-001199 | NCR | Non-confirming 1:1 sand cement cube results for Winthrop St. Bridge Ground Retention Solution |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-03-05 | 2015-02-20 12:14 | -13 | 2015-02-19 19:41 | Civil - Geotechnical Engineering | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | A number of grout cube compressive strength results for the Winthrop Street Bridge temporary works ground retention solution piles have been found to be lower than required design strength of 35MPa, although the indication is that the low strength may be as a result of poorly prepared and maintained grout cubes. The details of the ground retention solution can be found in Cxxx-__M-C-CER-D061-50424. Details of the cubes and corresponding piles are detailed in the attached file title - Winthrop Grout Cube Information.pdf.
| 02SL - Stations (LUL) | Cxxx-NCR-001200 | NCR | TTH Blockwork Mastic |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-08-20 | 2015-08-03 16:16 | -17 | 2015-02-24 12:16 | Architectural - Brickworks/Blockworks | 2000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There are locations within the TTH ground floor blockwork where the intumescent mastic seal has been damaged. The damage has been caused due to water ingress as a result of the external envelop not being weather tight.
| 02SL - Stations (LUL) | Cxxx-NCR-001201 | NCR | TTH External Boarding |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-11-01 | 2015-10-10 16:57 | -22 | 2015-02-24 12:38 | Architectural - General | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Due to the on-going issues with the TTH roof, there are areas of external boarding (both Aqua Panel and __) located on the accommodation level, external parapets. Some boards show evidence of water damage and others have been damaged as a result of earthing tape installation and scaffold installation.
| 02SL - Stations (LUL) | Cxxx-NCR-001202 | NCR | TTH Blockwork – Collapsible Gate Housing Interface |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-05-28 | 2015-04-13 16:16 | -45 | 2015-02-27 13:12 | Architectural - Brickworks/Blockworks | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The blockwork to the TTH power entry riser (room 1-02) approximate location GL 5/G; has been constructed incorrectly, reference drawings: Cxxx-__M-A-DWG-D061-50004 C01 Cxxx-__M-A-DWG-D061-50051 C01 Cxxx-__M-C-DWG-D061-50503 10240596-XKA-0164 rev C - TTH Builders work holes The blockwork wall has been extended level with the adjacent riser blockwork (1-03, 1-04), and a lintel installed above door D1/04 with blockwork completed to the soffit above. The section of wall above the door was designed to be a partition wall. By extending the wall, the blockwork clashes with the collapsible gate housing and PFC support column. See attached photo.
| 02SL - Stations (LUL) | Cxxx-NCR-001205 | NCR | TTH Switchboard Dimensions |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-05-03 | 2015-05-01 15:25 | -2 | 2015-03-04 15:34 | Electrical - LV Equipment | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | While undertaking the FAT at __ for the TTH Switchboards, a dimensional check identified that all three were 45mm too tall
| 02SL - Stations (LUL) | Cxxx-NCR-001206 | NCR | __ESL Management of NCRs |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-06-30 | 2015-06-30 16:50 | 0 | 2015-03-04 15:47 | Electrical - LV Equipment | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | During a Quality Surveillance at __ (__), the NCR procedure was reviewed. The procedure was found to be insufficiently implemented.
| 02SL - Stations (LUL) | Cxxx-NCR-001207 | NCR | DSS - Void in Concrete in W5-01NS Non-Structural Wall |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-07-30 | 2015-07-30 15:00 | 0 | 2015-03-09 11:13 | Shafts - Shafts General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Whilst striking the shutters for W5-01NS non-structural wall a void in the concrete was noticed under the door way opening for the half landing.
| 02SL - Stations (LUL) | Cxxx-NCR-001208 | NCR | Work completed without approved ITP in place |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-06-25 | 2015-06-18 14:53 | -7 | 2015-06-11 12:54 | Shafts - Shafts General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | 5no. LED lights were installed around CHS prior to final CRL approval of the ITP. The lights have been signed off by a temporary works supervisor and are in a stable condition. It is proposed that final approval of the ITP be achieved and any amendments be made to the lights as required.
| 02SL - Stations (LUL) | Cxxx-NCR-001209 | NCR | DSS - Grout Loss in W5-06S Internal Wall |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-10-16 | 2015-10-06 15:02 | -10 | 2015-03-09 16:31 | Shafts - Shafts General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Grout loss occurred during the construction of W5-06S Internal Wall, causing a localised increase in cover of approximately 10 - 15mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001210 | NCR | Nominated ITP not covering the works being undertaken |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-04-23 | 2015-04-21 14:51 | -2 | 2015-03-09 20:55 | Electrical - Electrical Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | During a site visit by CRL it was found that the TTH electrical external services works being undertaken on site were not covered by the nominated ITP.
| 02SL - Stations (LUL) | Cxxx-NCR-001211 | NCR | Non-submission of formal IRF's |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-03-24 | 2015-03-19 15:09 | -5 | 2015-03-10 14:49 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | No official IRF's have been submitted for the installation of Temporary piles for the Durward Street bridge demolition. Please note that throughout the temporary work installation (Piling) for Durward Street Demolition, the contractor has informally keep the client up to date with inspection requests and piling process. Therefore this is a procedural NCR.
| 02SL - Stations (LUL) | Cxxx-NCR-001212 | NCR | E51 room Earthing Tape Damged |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-06-20 | 2015-06-01 11:33 | -19 | 2015-03-10 15:48 | Electrical - General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | The recently installed earthing tape within the E51 switch room has been damaged by scaffold works. The earthing tapes protective layer has been torn and damged. See attached Photographs.
| 02SL - Stations (LUL) | Cxxx-NCR-001213 | NCR | TTH External Window Installation |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-01-07 | 2015-12-08 09:53 | -30 | 2015-03-30 14:13 | Architectural - Glazing | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The TTH external windows have been installed out of tolerance. The sill detail to the window is detailed to be flush with the cladding, however has been installed at an offset as per the sill above the doors. After discussion with __, for this system the sill should be offset, this is something that needs to be addressed on the design drawings. The sill to window (W/01) has been installed out of level. The joints between the window frame and the cladding system have been installed out of tolerance and there is swarf/debris visible in the joints.
| 02SL - Stations (LUL) | Cxxx-NCR-001214 | NCR | TTH Brickwork/Blockwork Mortar |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-06-22 | 2015-04-17 09:45 | -66 | 2015-03-24 14:10 | Architectural - Masonary | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | The TTH Blockwork/Brickwork is complete. Upon inspection there is a variation in the mortar colour (see attached photographs). The blockwork specification is detailed with Cxxx-__M-A-RSP-D061-50078 clause F10 and references clause Z21 for cement gauged mortar.
| 02SL - Stations (LUL) | Cxxx-NCR-001215 | NCR | Couplers out of cover zone in Level 3 pour 2 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-04-03 | 2015-03-30 15:06 | -4 | 2015-03-11 11:33 | Shafts - Shafts General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 2No B32 couplers and 5No B16 couplers for the level 3 slab pour 2 are outside of cover zone. See attached marked up drawing for details. The couplers have a cover of approximatly 20mm which is outside of the specification which requires 50mm. __ propose to Drill and fix bars to replace couplers: - For the B32 couplers a 40mm hole will be drilled 350mm deep and replacement bar will be fixed using __ Hit 200. - For the B16 couplers a 20mm hole will be drilled 250mm deep and replacement bars will be fixed using __ Hit 200.
| 02SL - Stations (LUL) | Cxxx-NCR-001216 | NCR | DSS - L5 Slab Drainage Pot Location |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-08-28 | 2015-08-25 15:04 | -3 | 2015-03-12 11:04 | Shafts - Shafts General | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Drainage Pot within L5 Slab (Level 5 / P / 13) was installed out of position, please see attached photos and drawing of drainage pot location.
| 02SL - Stations (LUL) | Cxxx-NCR-001217 | NCR | DSS - Liner Wall above L6 Waler Pour 1 / 3 Reduced Cover |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-10-28 | 2015-10-14 17:27 | -14 | 2015-03-13 14:37 | Shafts - Shafts General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Liner Wall above L6 Waler Pour 1 / 3 localised reduced cover to bar highlighted in attached drawing, approximately 10mm cover. Bar is located in the bottom of the key of the Liner Wall. Reduced cover extends approximately 6 metres.
| 02SL - Stations (LUL) | Cxxx-NCR-001219 | NCR | Works proceeding without IRFs being submitted – Utilities Work |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2015-04-02 | 2015-04-02 13:50 | 0 | 2015-03-19 16:07 | Utilities Engineering - Utilities General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | __ have started the excavation (about 1m deep currently) for the manhole works relating to ITP Cxxx-__M-U-ITP-D061_WS106-50001. CRL have not been contacted regarding these works starting and have not been invited to witness points stated on the ITP, notably 4.1 and 4.2. Works Information 20.8 states “Inspections and tests during construction shall be notified by the Contractor to the Supervisor utilising the Inspection Request Form (IRF) identified in Appendix 20D.” CRL requested Cxxx to raise an NCR for this issue on the date of the incident (11/03/2015)
| 02SL - Stations (LUL) | Cxxx-NCR-001220 | NCR | CHS - Low cover on connection between CUB1-01 and CDB1-01 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-04-07 | 2015-04-08 12:38 | 1 | 2015-03-24 13:41 | Shafts - Shafts General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Counterfeit Items | Completed |  | Due to steel congestion in the connection between CUB1-01, CDB1-01 and column 23 starter bars there was low cover between the southern U- Bar for CDB1-01 and the corner of the shutter. See attached photo and drawing for location details. To gain cover on the steel a 40mm x 40mm angle had to be cut from the corner of the shutter, this gave 50mm of cover to the steel. See photo attached
| 02SL - Stations (LUL) | Cxxx-NCR-001221 | NCR | TTH - Grid Line 5 __ |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-06-22 | 2015-06-20 15:12 | -2 | 2015-03-24 12:48 | Architectural - Roofing & Exterior Treatment | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Counterfeit Items | Completed |  | The __ was installed to GL 5 in November 2014 as per approved design and documentation, as part of the TTH firebarding works completed by __. The rain screen cladding on this elevation has been delayed due to the louvres and the lamatherm installation to W177. Both of these items have been delayed awaiting document approval and LONO to proceed. The louvres have also been subject to a design change so that the mechanical ventilation damper can be installed internally and not within the wall to assist future maintenance and not compromise the fire rating of the wall. Due to these delays, the __ has been exposed in excess of 4 months, this exceeds the warrantee for the product regarding exposure to UV.
| 02SL - Stations (LUL) | Cxxx-NCR-001222 | NCR | TTH Concourse Paving/Manhole/Gate Line Slab interface |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-06-22 | 2015-06-25 09:42 | 3 | 2015-03-24 13:55 | Architectural - Flooring | 1500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The TTH concourse paving has been installed as per 10240596-XKA-0281 rev C. The paving installation has an interface with the previously installed civil’s works including the gate line slab and the existing manhole. The manhole was previous installed under Cxxx-__M-C-ITP-D061-50148. This NCR is to record that the position of the manhole was altered on site to suit the existing location, therefore the position is -69mm (N-S) and +57mm (E-W), proposal to use as is. The corner level of the manhole was surveyed: N/E 113.489, E/S-113.496, W/S-113.516, N/W-113.516, meaning that the east edge has a difference in level of 7mm. This is within the tolerance of the civil’s specification, but does not correlate for the lower tolerances of the architectural specification. Sketch 10240596-XKA-0281 rev C has amended the paving from being a continuous fall across the concourse (west to east) to areas of level paving connected by paving on a gradient. The levels and position of these level/inclined breaks have not been coordinated with the existing civil work. The gate line slab level is +133.530 and the FFL is +113.626, providing a maximum 96mm depth for paver and bedding. As the break from level/graded does not coincide with the edge of slab, there is insufficient bedding. This has been captured in RFI Cxxx-__-221, please see attached sketches and photos. The concrete slab has also been poured high, please see attached levels survey. The result of both the as built slab and the design levels means that the bedding layer is reduced to below 30mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001223 | NCR | Cast Iron Drainage CHS - Working to non IFC drawings |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2015-08-25 | 2015-08-06 09:29 | -19 | 2015-03-24 | Mechanical - Public Health Engineering | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Cast Iron drainage for the Cambridge Heath Shaft. The drawings being used to install the drainage are not issued at IFC status. The drainage has been started on level 6. These drawings are listed below: Cxxx-__M-P-DDA-D061_WS107_1-10280 Cxxx-__M-P-DDA-D061_WS107_1-10281 Cxxx-__M-P-DDA-D061_WS107_1-10282 Cxxx-__M-P-DDA-D061_WS107_3-10280 Cxxx-__M-P-DDA-D061_WS107_3-10281 Cxxx-__M-P-DDA-D061_WS107_4-10280 Cxxx-__M-P-DDA-D061_WS107_4-10281 Cxxx-__M-P-DDA-D061_WS107_5-10280 Cxxx-__M-P-DDA-D061_WS107_5-10281 Cxxx-__M-P-DDA-D061_WS107_6-10280 Cxxx-__M-P-DDA-D061_WS107_6-10281 Cxxx-__M-P-DDA-D061_WS107_7-10280 Cxxx-__M-P-DDA-D061_WS107_7-10281 Cxxx-__M-P-DDA-D061_WS107_8-10280 Cxxx-__M-P-DDA-D061_WS107_8-10281 Cxxx-__M-P-DDA-D061_WS107_A-10280 Cxxx-__M-P-DDA-D061_WS107_A-10281 Cxxx-__M-P-DDA-D061_WS107_B-10280 Cxxx-__M-P-DDA-D061_WS107_B-10281 Cxxx-__M-P-DDA-D061_WS107_C-10280 Cxxx-__M-P-DDA-D061_WS107_C-10281 Cxxx-__M-P-DDD-D061_WS107_Z-10502 Cxxx-__M-P-DDE-D061_WS105_Z-35910 Drawings are required to be at IFC prior to any works onsite.
| 02SL - Stations (LUL) | Cxxx-NCR-001224 | NCR | Durward Street Temporary works Piling - Non-conforming 1:1 Sand cement Cube results for Durward Street Bridge Piling |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-04-02 | 2015-04-08 12:28 | 6 | 2015-04-01 12:38 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | A number of grout cube compressive strength results for the Durward Street Bridge temporary works ground retention solution piles have been found to be lower than the required design strength of 40MPa at 28 day testing. The details of the ground retention solution can be found in Cxxx-__M-C-CER-D061_WS106-50042. Details of the cubes and corresponding piles are detailed in the attached files. Please note : extra cubes will be crushed and these will be submitted to the PFE as they are recieved. Details of the cubes and corresponding piles can be found in the attached file titled Durward Grout Cube Information.pdf
| 02SL - Stations (LUL) | Cxxx-NCR-001225 | NCR | Use of Non Approved Materials – Dry __ |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-08-10 | 2015-07-21 15:11 | -20 | 2015-03-26 14:00 | Materials - Approval | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | During a review of the Construction Certificate for the Dry __, a number of materials used for the Dry __ works were found to be without MCRs in place.
| 02SL - Stations (LUL) | Cxxx-NCR-001226 | NCR | Non Approved Material - UTX Troughing |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-11-01 | 2015-10-29 16:23 | -3 | 2015-03-26 14:18 | Materials - Approval | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | The UTX Troughing Material __ has been installed in site without an approved MCR in place. The MCR was on the eB MCR system but was not approved
| 02SL - Stations (LUL) | Cxxx-NCR-001227 | NCR | UKAS Testing |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2015-05-10 | 2015-05-06 11:03 | -4 | 2015-03-27 08:35 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Whilst carrying out a planned surveillance, It was stated that the Contractor and Crossrail have agreed that site based staff can under take testing, it was further stated that this was agreed during a Quality Forum Meeting (QFM) with all parties present. However on review it was identified that although agreed in the QFM, no formal agreement had been given by Crossrailas required by Works Information Volume 2B Part 20.,
| 02SL - Stations (LUL) | Cxxx-NCR-001230 | NCR | LULO ESS - Cast in steel paints installed with no corrosion protection |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-09-01 | 2015-05-19 11:08 | -105 | 2015-04-01 12:24 | Structural Engineering - Steel Member | 2000 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Steel plates have been cast into the reinforced concrete walls within the ESS to take steel members in accordance with drawings Cxxx-HYD-S-DDL-D061_WS106_2-75053 and Cxxx-HYD-S-DDD-D061_WS106_Z-76004. These steel plates have not had any corrosion protection applied to them. All other steel members within the ESS have had an epoxy coating applied to them as required within the Materials and Workmanship Specification for Structural Steel (Cxxx-HYD-S-RSP-D061-00003). To ensure that the steel plates achieve the correct corrosion protection, __ propose to use a surface tolerant epoxy called Interseal 670HS; the use of which has been approved within MCR Cxxx-C-LRC-D061-50184. This product is suitable for hand prepared steel work. All non cast in steel members will arrive on site with the CIRIA E-2 system applied, i.e. a 75 micron primer layer and a 100-125 micron intermediate layer. So in total a minimum of 175 microns of paint. The site applied Interseal 670HS has to be applied typically between 100-200 microns. Therefore, we would propose that 175-200 microns minimum of the Interseal 670HS is applied. To prepare the steel prior to application, concrete will be removed from the face of the steel and the steel will be brushed by hand or power tool using a dry bristle brush. The Interseal 670HS will be mixed and applied as per manufacturer instructions and left to cure prior to steelwork installation. Please confirm that this method is acceptable.
| 02SL - Stations (LUL) | Cxxx-NCR-001231 | NCR | LO SME extension camera |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-06-22 | 2015-04-27 17:04 | -56 | 2015-04-03 15:36 | Communications and Control Systems - CCTV | 1000 |  | Material | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | The CCTV secondary back box installed for LO SME __ camera is not the type specified in the MCR. A metal back box was required under the MCR however a plastic back box was installed.
| 02SL - Stations (LUL) | Cxxx-NCR-001232 | NCR | DSS - __ Damage on C5-13 and C5-9 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-05-30 | 2015-05-29 11:29 | -1 | 2015-04-10 09:01 | Shafts - Shafts General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Counterfeit Items | Completed |  | __ channel has come away from column (C5-13, C5-9) whilst striking the shutters. Please see attached site photo for more details.
| 02SL - Stations (LUL) | Cxxx-NCR-001233 | NCR | TTH/WSME Drawings |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-08-20 | 2015-08-18 19:26 | -2 | 2015-04-10 12:55 | Architectural - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | __ have issued construction drawings C01, Crossrail have reviewed these drawings and sub-contractors are completing works on site. The sub-contractor design (namely cladding - __) has been revised/developed to capture all site details, __ have stamped their approval of the sub-contractor drawings which are now being worked to on site. __ are yet to revise their drawings to C02 meaning that certain design details being constructed on site are not visible to Crossrail who do not have access to sub-contractor drawings.
| 02SL - Stations (LUL) | Cxxx-NCR-001234 | NCR | LO SME illuminated emergency exit signs |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-07-15 | 2015-07-15 18:56 | 0 | 2015-04-16 09:16 | Electrical - Lighting | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Two LU approved Design plan __ emergency exit light fittings (M1977/1PL11LHF/S12F/EM3) have been installed inside the LO SME extension tunnel with out an MCR being composed
| 02SL - Stations (LUL) | Cxxx-NCR-001235 | NCR | Platform 5 Damage to CMS trunking |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-05-11 | 2015-05-05 13:35 | -6 | 2015-04-13 12:17 | Civil - Demolition/Site Clearance | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Some temporary CMS trunking (not cabling) underneath Winthrop Street bridge on platform 5 South, recieved some minor damage during the demolition of Winthrop street bridge (21-22nd Feb, 2015). This damage occured when the remaining section of bridge arch was demolished.
| 02SL - Stations (LUL) | Cxxx-NCR-001237 | NCR | Installation of wrong camera back box within the LO SME |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-04-30 | 2015-04-27 16:11 | -3 | 2015-04-16 09:45 | Communications and Control Systems - CCTV | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | During installation of CCTV cameras withing the LO SME a camera back box was installed that did not have an MCR.
| 02SL - Stations (LUL) | Cxxx-NCR-001238 | NCR | Pile Grout Strength Failures |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-06-15 | 2015-06-16 11:52 | 1 | 2015-04-16 16:59 | Civil - Civil Engineering General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | Further to Cxxx-NCR-001209 and Cxxx-NCR-001238, the most recent report from the Cxxx UKAS Lab shows further failures in the piling grout.
| 02SL - Stations (LUL) | Cxxx-NCR-001239 | NCR | CHS - B20 Coupler in the cover zone for Half landing at 109.400 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-05-10 | 2015-05-05 13:42 | -5 | 2015-04-16 16:10 | Shafts - Shafts General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | CHS - B20 coupler for the half landing at 109.400 is located in the cover zone. The coupler was cast in column C1-04. __ propose to drill and fix a 20mm bar to replace coupler. A 25mm hole will be drilled 300mm deep, bar will be fixed with with __ Hit 200.
| 02SL - Stations (LUL) | Cxxx-NCR-001240 | NCR | TTH - Use of non Approved Material On Site - Naylor Lintels |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-10-01 | 2016-08-10 15:22 | -782 | 2015-04-17 14:32 | Architectural - Brickworks/Blockworks | 1000 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Counterfeit Items | Completed |  | Naylor lintels have been installed as part of the TTH blockwork. The MCR is at Code 3.
| 02SL - Stations (LUL) | Cxxx-NCR-001241 | NCR | Concrete works to lift 6 - lipping greater than 3mm |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-07-16 | 2015-08-19 08:02 | 34 | 2015-04-20 08:58 | Structural Engineering - Concrete Member | 2500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A post-pour concrete inspection to Lift 6 completed by a __ Engineer, an IQI and a Crossrail Field Engineer has identified al non-conformance related to specification Cxxx-HYD-A-RSP-D061-00007 Finishes to in Situ Concrete – Architectural Requirements. All in situ external concrete elements of Lift 6 are to be cladded. Whilst Cxxx-HYD-A-RSP-D061-00007 Part JE20.1101a states ‘this section specifies the requirements for architectural finishes for in situ concrete elements where exposed to view’, there are still items of workmanship that do not comply with this specification. Steps at joints between concrete pours exceed the limit of 3mm. These gaps between formwork and the previously poured structure have also resulted in grout runs. ‘Making good’ works as per the accepted works procedure Cxxx-__M-C-GPD-D061_50017 will reduce the lips to less than 3mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001242 | NCR | Concrete works to Lift 6 - cast-in plates for steel connections |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-06-01 | 2015-04-30 16:36 | -32 | 2015-04-20 08:59 | Structural Engineering - Concrete Member | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Counterfeit Items | Completed |  | A post-pour concrete inspection to Lift 6 completed by a __ Engineer, an IQI and a Crossrail Field Engineer has identified al non-conformance related to specification Cxxx-HYD-S-RSP-D061-00002 Materials and Workmanship Specification In Situ Concrete. There are eight cast in steel plates for steel work connections within the East Stair Shaft. Whilst the plates have been cast in the correct position, one plate is out of plumb in the ‘Z’ axis. The bolt hole locations have been surveyed and accepted by the Steelwork contractor __, however the plate is outside of the +/- 6mm tolerance as stated within Cxxx-HYD-S-RSP-D061-00002.
| 02SL - Stations (LUL) | Cxxx-NCR-001243 | NCR | Benchmark |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2015-06-24 | 2015-05-22 10:23 | -33 | 2015-04-28 11:04 | Architectural - Masonary | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Contractor was asked to supply evidence for the inspection and acceptance of the blockwork benchmark in the Temporary Ticket Hall. The evidence supplied was made up of two number Notification for Works Ready for Inspection (NOWRI) process, first dated 08/08/2014, document number Cxxx-NOWRI-000049, subject; Inspection and acceptance of Temporary Ticket Hall blockwork wall benchmark gridline 1, the document was signed off by the Contractor 08/08/2014, CRL 03/12/2014 and the Architects representative 10/12/2014. The second document dated 02/09/2014 was also numbered Cxxx-NOWRI-000049 but was for Inspection and acceptance of Temporary Ticket Hall brickwork wall benchmark gridline 1, the document was signed off by the Contractor 02/09/2014, CRL 03/12/2014 and the Architects representative 10/10/2014, also supplied were three number __-Form-D3 Brick and Blockwork check sheets; two dated and signed off 29/07/2014 by the Contractor for gridline 1 blockwork, third signed off 20/08/2014 by the Contractor for gridline 1 brickwork. On reviewing the above documentary evidence the Contractor has proceeded with the installation of blockwork in the Temporary Ticket Hall without an accepted benchmark in place as the above evidence shows.
| 02SL - Stations (LUL) | Cxxx-NCR-001244 | NCR | Construction Records - CFA Mini Piling, ESS |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-05-29 | 2015-05-06 11:51 | -23 | 2015-04-29 10:57 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the compilation of the construction records for the CFA Mini Piles for the East Stair Shaft works, the QA review revealed the reinforcement checksheets required by the ITP were found to be incomplete in terms of signatures missing, some data not available. The works date back to 2012-2013, the engineer responsible for the work has left the project 18 months ago. __ have no one who can counter sign.
| 02SL - Stations (LUL) | Cxxx-NCR-001246 | NCR | CHS - Level A pour 3 steel unable to be installed due to Wall 04 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-05-19 | 2015-05-19 12:01 | 0 | 2015-05-05 14:19 | Shafts - Shafts General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | CHS The reinforcement for Level 1 pour 3 drawings number Cxxx-__M-C-DWG-D061-WS107-50445 cannot be installed due the pouring of W3-04s. See attached marked up drawing and Sketches for details of reinforcement that need to be installed in the end of W3-04. __ propose to saw cut and break out concrete for the area of W3-04s that effects the Level 1 pour 3 slab. Concrete will be broken out to expose the rebar and then steel fixing in the area can commence. Prior to pouring a steel inspection will be carried out by Crossrail and __ IQI to confirm that reinforcment in acceptable. Volume of wall to be broken out is 0.4m*0.74m*0.45m.
| 02SL - Stations (LUL) | Cxxx-NCR-001247 | NCR | Delivery tickets not provided for materials being used in the TTH to provide assurance of traceability to the approved MCRs. |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2015-10-30 | 2015-08-11 18:54 | -80 | 2015-05-05 15:06 | Materials - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Lack or improper material identification and traceability | Completed |  | During a planned Crossrail surveillance on 02nd April 2015 which looked at TTH materials compliance, five materials being used to construct the works were selected for post surveillance traceability review. Following multiple requests, __ was only able to provide the delivery tickets for the __, and not the other materials sampled, which were requested to enable traceability to the documented MCRs. It was stated that these, where applicable, are held by sub-contractors Ardent and __ who on request were not providing the information. As the information was not made available, it could not be determined whether the materials being used on site, in particular the __ __ and __ board, were that as detailed in the documented MCR, as both products had no identification markings. Additionally the supplier/ manufacturer could not be verified with the information detailed in the MCR. Works Information Volume 2B parts 20.2, 20.7 and 20.8 state respectively, “The Contractor shall make available for audit all records necessary to demonstrate that the works have been executed in accordance with the contract….”; “Verification of the quality and material traceability of each element of the works shall be the responsibility of the Contractor….” and “The Contractor’s verification is accomplished by examinations, tests, measurement and inspection and by verifying records including those of his Subcontractors and suppliers”. Additionally BS EN ISO 9001:2008 ‘Quality Management Systems – Requirements’ clause 4.2.4 Control of Records states “The organization shall establish a documented procedure to define the controls needed for the identification, storage, protection, retrieval, retention and disposition of records. Records shall remain legible, readily identifiable and retrievable”. As the records were not made available for all the requested materials an NCR was raised resulting from the surveillance.
| 02SL - Stations (LUL) | Cxxx-NCR-001249 | NCR | Whitechapel Camera 9 - Damaged Cable - SSL1680052 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-05-28 | 2015-05-20 15:11 | -8 | 2015-05-12 17:15 | Communications and Control Systems - CCTV | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Damaged cable found for Camera 9. Fault on Camera 9 cable found, the cable had been trapped in temporary trunking behind the hoarding on platform 2.
| 02SL - Stations (LUL) | Cxxx-NCR-001250 | NCR | CHS Surface damage to C1-25 and C1-28 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-12-10 | 2015-12-16 10:13 | 6 | 2015-05-13 14:35 | Shafts - Shafts General | 1500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Columns C1-25, C1-28, C1-34, C1-35 and C1-40 were poured on 22/04/15. A Permit to strike was raised on the 24/04/15 and the shutters were removed. During the removal of the shutters the face of the column and the __ channel was removed on column C1-25 and the channel removed on C1-28 (please see attached photos).
| 02SL - Stations (LUL) | Cxxx-NCR-001251 | NCR | Concrete works to ESS Wall W2a/W2b |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-09-15 | 2015-09-09 12:39 | -6 | 2015-05-15 14:08 | Structural Engineering - Concrete Member | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A post-pour concrete inspection to Wall W2a/W2b in the East Stair Shaft completed by a __ Engineer, an IQI and a Crossrail Field Engineer has identified a non-conformance related to specification Cxxx-HYD-A-RSP-D061-00007 Finishes to in Situ Concrete – Architectural Requirements. All in situ concrete elements of Wall W2a/W2b are to be cladded. Whilst Cxxx-HYD-A-RSP-D061-00007 Part JE20.1101a states ‘this section specifies the requirements for architectural finishes for in situ concrete elements where exposed to view’, there are still items of workmanship that do not comply with this specification. Steps at joints between concrete pours exceed the limit of 3mm. These gaps between formwork and the previously poured structure have also resulted in grout runs. ‘Making good’ works as per the accepted works procedure Cxxx-__M-C-GPD-D061_50017 will reduce the lips to less than 3mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001252 | NCR | CHS - C1-01 couplers missing from construction |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-06-15 | 2015-06-18 12:34 | 3 | 2015-05-18 09:56 | Shafts - Shafts General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Couplers for surrouding elements were missed from the construction of C1-01. See attached Marked up drawing for details. -20No B12 couplers were missed for W1-21s -4No B20 couplers were missed for Half landing slab __ propose to drill and fix replacement bars: - Missing B12 couplers - A 16mm hole wll be drilled 200mm deep, a B12 replacement bar will be fixed into the hole using HILTI HIT 200. - Missing B20 couplers - A 25mm hole will be drilled 250mm deep, a B20 replacement bar will be fixed into the hole using HILTI HIT 200.
| 02SL - Stations (LUL) | Cxxx-NCR-001253 | NCR | CHS - W8-12NS, liner wall coupler spacing |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-06-16 | 2015-06-15 12:53 | -1 | 2015-05-19 14:03 | Shafts - Shafts General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Spacing between the couplers at the top of W8-12NS is larger than the design spacing of 500mm. __ propose to drill and fix a 25mm bar into the Liner wall where the spacing is above the required 500mm. 1No bar will need to be drilled and fixed. Hole will be 250mm deep and bar will be fixed with __ Hit 200
| 02SL - Stations (LUL) | Cxxx-NCR-001254 | NCR | Ardent – Insufficient Supervision Levels for Fire Stopping Works TTH |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-07-24 | 2015-07-30 17:29 | 6 | 2015-05-25 14:19 | Architectural - General | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Insufficient levels of FIRAS supervision and FIRAS certified operatives have been observed. During the fire stopping surveillance by __ Quality there were 3 untrained operatives on site. The FIRAS card later emailed is blurred (name illegible) and relates to __ Contracts Ltd, Not Ardent. There is insufficient evidence to show __/Ardent have provided sufficient levels of supervision for the __ mastic work.
| 02SL - Stations (LUL) | Cxxx-NCR-001255 | NCR | TTH - Maintenance of Construction records – Fire Stopping |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-08-13 | 2015-08-07 08:19 | -6 | 2015-05-25 14:28 | Architectural - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The brickwork and Mastic work was finished several months ago. During a surveillance of fire stopping works by __ Quality Dept, the records received were insufficient a) no photographs of the fire stop labels b) no competence records During the surveillance, no checksheets could be found for fire stopping for works undertaken in 2015, despite evidence found on site (E9, Pl 6). The checksheets that have been provided are not those listed in the controlling ITP. There is nowhere to record __ or CRL inspection of the works and therefore no evidence that the works have ever been offered up for inspection.
| 02SL - Stations (LUL) | Cxxx-NCR-001256 | NCR | WSME Panel Fire Boarding Damage |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-01-25 | 2015-12-08 09:42 | -48 | 2015-05-25 15:39 | Architectural - General | 17878 |  | Damaged | Repair | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The WSME cladding panels have been pre-fabricated at Barking comprising the complete cladding build-up of studwork, boarding, __, brackets and zinc; ready for lifting on to the WSME steelwork, to minimise working over the HCDL tracks and overcome access issues. The fire protection design for these panels has recently been queried due to the detail of abutting panels not having a staggered joint and the proposed mastic having longevity concerns. As a result of these issues with quality assurance the panels have been re-worked, stripping back to the secondary steelwork with a single layer of fire board. Access will be provided to complete the cladding in situ once the panels are lifted into position. By unscrewing the second layer of fire boarding, the first layer has been damaged where the screws and joints were fixed; mastic has been used as a remedial to this. The re-work on the panels has meant they have been regularly handled, stacked, un-stacked and transported back and forth from site to the yard in Barking. The extra, unforeseen lifting and movement of the panels has led to further damage to corners, edges and the face of the board as the attached photographs show.
| 02SL - Stations (LUL) | Cxxx-NCR-001257 | NCR | TTH Level A Roofing; VCL Damage |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-11-12 | 2016-08-04 07:35 | -100 | 2015-05-25 15:48 | Architectural - Roofing & Exterior Treatment | 8000 |  | Damaged | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Further to NCR 1055 and 1156, the TTH level A concrete slab was confirmed to have sufficient cover to the reinforcement and the roofing sub-contractor confirmed that the level variance could be accommodated within the roofing system. To close these existing NCR’s the non-compliant levelling screed was fully removed. The Level A roofing works are now on-going and the VCL has been installed. The VCL is becoming damaged where there is a change in level and where debris has not been fully removed before application, when the roof is trafficked this is resulting in tears in the VCL. Please see attached photographs.
| 02SL - Stations (LUL) | Cxxx-NCR-001258 | NCR | DSS: Procedural NCR for missing construction records for Level 4 Waler/Propping works |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-06-15 | 2015-06-04 09:04 | -11 | 2015-06-01 16:52 | Shafts - Shafts General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | Following the compilation of construction records for the DSS Level 4 Props and Walers Install and Remove Sub Construction Certificate - Cxxx-__M-C-CER-D061-50191 several historic records are not available. These records relate directly to Construction Records Cxxx-__M-O4-LRC-D061_WS105-50034 and Cxxx-__M-O4-LRC-D061_WS105-50036. The missing records are deliverable items as stated in the associted ITP's Cxxx-__M-C-ITP-D061-50056 Rev 3 and Cxxx-__M-C-ITPD061_WS105-50010 Rev 2 respectively. Please see attached lists highlighting missing records.
| 02SL - Stations (LUL) | Cxxx-NCR-001259 | NCR | DB33 emergency lighting Key switch |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-07-01 | 2015-06-02 12:24 | -29 | 2015-06-01 16:30 | Electrical - Lighting | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | Within switch room to house new DB33 (Room 2/412) a '__ 12 gang key light switch' is to be installed for the emergency enabling works battery pack fitting. Prior to the __ back box and accessories arriving on site a 12 way non compliant MK alternative (for site temps) was installed, it should be noted that site teams (nights) asked (days) if this MK accessories was compliant before proceeding further, it should also be noted that this area is currently within the __ disused area prior to becoming part of the station.
| 02SL - Stations (LUL) | Cxxx-NCR-001260 | NCR | LULO Temporary Ticket Hall Staircase missing soffit |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-11-10 | 2015-10-29 18:11 | -12 | 2015-06-02 09:42 | Structural Engineering - Steel Member | 2000 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | In the TTH staircase, the lowest soffit plate has not been installed.
| 02SL - Stations (LUL) | Cxxx-NCR-001261 | NCR | East Stair Shaft - Procedural NCR for CFA Mini Piles Lab results relating to Piles No. 48 & 73 low compressive strength observed post construction records submission |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-06-23 | 2015-07-01 17:55 | 8 | 2015-06-09 10:57 | Civil - Structural Engineering | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following the compilation and submission of historic Construction Records for the East Stair Shaft CFA Mini Piles Lab results_Cxxx-__M-O4-LRC-D061-50008, it has been highlighted that two Piles (48 and 73) out of 90 temporary grout piles had not reached the compressive strength of 40n/mm2 required within the 28 day period as stated in the associated ITP for the works: Cxxx-__M-C-ITP-D061-50012_ CFA Mini Grout Piles. The results inidicate Pile No. 48 reached an average of 37.2 N/mm2 within 28 days and 42.1 N/mm2 after 56 days whilst Pile No. 73 reached an average of 38.8 N/mm2 within 28 days and 42.4 N/mm2 after 57 days. This was not highlighted by the construction team during the construction phase and missed during final review & compilation of the Construction Records. However was noted post submission to CRL. These construction records are contained within Plie Group 11 Sub Construction Certificate_Cxxx-__M-C-CER-D061-50171 and relates directly to the following Construction Records: Cxxx-__M-O4-LRC-D061-50005_ESS CFA Mini Piles Setting Out Checksheets Cxxx-__M-O4-LRC-D061-50006_ESS CFA Mini Piles Construction Checksheets Cxxx-__M-O4-LRC-D061-50007_ESS CFA Mini Piles Reinforcement Cage Checksheets Cxxx-__M-O4-LRC-D061_WS106-50046_Pile Group 11 - Platform Level Piling Moreover a total of 6 Piles (48, 56, 58, 70, 73 & 79) achieved low strength. 2 NCR's were raised Cxxx-NCR-000246: East Stair shaft - Low grout strength Piles 79 and 56 and Cxxx-NCR-000168: HCDL East Stair Shaft Early Curing of Grout Cubes covering Piles 70 & 58. No other NCR's were raised.
| 02SL - Stations (LUL) | Cxxx-NCR-001262 | NCR | Working to non-IFC drawings |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2015-08-10 | 2015-08-06 12:18 | -4 | 2015-06-04 14:46 | Mechanical - Public Health Engineering | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | Cast Iron drainage for the Durward Street Shaft. The drawings being used to install the drainage are not issued at IFC status. The drainage has been started on level 5 and level 6. These drawings are listed below: Cxxx-__M-P-DDA-D061_WS105_3-10270 Cxxx-__M-P-DDA-D061_WS105_3-10271 Cxxx-__M-P-DDA-D061_WS105_4-10270 Cxxx-__M-P-DDA-D061_WS105_4-10271 Cxxx-__M-P-DDA-D061_WS105_5-10270 Cxxx-__M-P-DDA-D061_WS105_5-10271 Cxxx-__M-P-DDA-D061_WS105_6-10270 Cxxx-__M-P-DDA-D061_WS105_6-10271 Cxxx-__M-P-DDA-D061_WS105_7-10270 Cxxx-__M-P-DDA-D061_WS105_7-10271 Cxxx-__M-P-DDA-D061_WS105_8-10270 Cxxx-__M-P-DDA-D061_WS105_8-10271 Drawings are required to be at IFC prior to any works onsite.
| 02SL - Stations (LUL) | Cxxx-NCR-001263 | NCR | WHI-interim-DB33 - Room 2/412 Fire Compartmentation Door |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-06-22 | 2015-06-30 08:13 | 8 | 2015-06-04 19:34 | Architectural - Doors | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Not Defined | Completed |  | __ FD60 fire door has been installed and inspected as part of the fire compartmentation works for room 2/412 on 04/06/2015 (associated IRF Cxxx-__M-E1-IRF-D061-50001 attached). This material has not been approved for use through the CRL MCR process. The associated MCR (Cxxx-__M-A-LRC-D061_WS106-50200 (attached to this NCR)) is currently pending review with CRL and was submitted to on the 26/03/2015 Contractors Communication Cxxx-CCM-09367 (Attached to this NCR). It should be noted that this product is fit for purpose on LU sub surface station on LU-APR-1944 and is therefore compliant for use in current location.
| 02SL - Stations (LUL) | Cxxx-NCR-001266 | NCR | Location of 4no. holes required in ESS concrete pedestal |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-12-01 | 2015-11-29 12:52 | -2 | 2015-06-12 09:45 | Civil - Concrete Pavement | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A new reinforcement beam is being poured around the East Stair Shaft lift shaft. When pouring the eastern section of the beam, the recesses designed for the cladding panels fixing details have been missed. Therefore these 4no. holes need to be cored through the RC beam. To illustrate this issue, please find attached an indicative sketch showing the location of the 4 missing holes.
| 02SL - Stations (LUL) | Cxxx-NCR-001267 | NCR | TTH Staircase risers |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-09-30 | 2015-09-22 10:42 | -8 | 2015-06-12 13:19 | Civil - Structural Engineering | 2000 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In the TTH staircase, the bottom riser of each stair flight is missing. To address this issue, we propose to fabricate, and install bolted risers, as per design sent by email to __ (Attachement: "Grating and kick plates details", detail: "KICKPLATE TREADS").
| 02SL - Stations (LUL) | Cxxx-NCR-001268 | NCR | TTH Staircase grating |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-01-25 | 2015-11-15 13:54 | -71 | 2015-06-12 14:31 | Civil - Structural Engineering | 4000 |  | Manufacturing Defect | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The TTH staircase top landing/grating is not level. It also does not allow for railings to be installed. We propose to amend approved design to address these 2 issues.
| 02SL - Stations (LUL) | Cxxx-NCR-001270 | NCR | East Stair Shaft Precast Stairs - Incorrect installation level |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-07-01 | 2015-07-06 11:23 | 5 | 2015-06-12 13:44 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The East stair Shaft precast stairs were installed on top of the ESS landing at an incorrect level. The reason for this non conformance is an irregularity in the level of the RC landing slab. After installation of the stairs, __ surveyed the level of the stairs and noticed this disparity.
| 02SL - Stations (LUL) | Cxxx-NCR-001271 | NCR | POMS/Clerk Office Blockwork - Door Lintel |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-08-07 | 2015-08-05 16:19 | -2 | 2015-06-16 08:07 | Architectural - Brickworks/Blockworks | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Due to improper supervision of sub-contractors the lintel for the door to the Ground Floor Security Lobby leading to POMs and Ticket Clerk Office, has been installed at an incorrect height. This is due to some discretion on which direction the door opened into and the change in floor level from Security Lobby to POMs Office. The lintel has been installed at a doors height from the lower floor level of the Security Lobby instead of the higher level. The lintel for the door on the same wall has been installed at the correct height and this is the height that the other should be installed to. Please see photo attached showing the difference in lintel height.
| 02SL - Stations (LUL) | Cxxx-NCR-001272 | NCR | West Lift Lobby - Piling |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-06-26 | 2015-06-23 13:11 | -3 | 2015-06-12 14:08 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Top pile cage installed with 900mm lap length, minimum lap length should be 1000mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001273 | NCR | TTH - Incorrectly Fitted __ Level A |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-09-15 | 2015-08-24 18:35 | -22 | 2015-06-17 08:13 | Architectural - Ceilings & Soffits | 1800 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __ in TTH Level A ceiling is not level and not parralell as per design. Design specifies instilation at 600mm centres and is installed at 1200mm centres instead. Tape was used to measure out each __. __s became unleveled.
| 02SL - Stations (LUL) | Cxxx-NCR-001274 | NCR | Works Proceeding without an approved ITP - Offsite Steelwork Fabrictaion |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-07-31 | 2015-08-06 17:38 | 6 | 2015-06-16 21:23 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | Works associated with the Off Site Fabrication of Structural Steelwork (Area 3a & 3b) Cxxx-__M-C-ITP-D061_WS106-50083 (Rev 1.0) proceeded without an approved ITP in place.
| 02SL - Stations (LUL) | Cxxx-NCR-001275 | NCR | Works Proceeding without an approved ITP - East Stair Shaft Pre Cast Stairs |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-07-31 | 2015-08-19 07:35 | 19 | 2015-06-16 21:29 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | The Stair 23 pre cast stairs have been installed without an approved ITP in place. Works relate to Cxxx-__M-C-ITP-D061-50075 Rev 9.0
| 02SL - Stations (LUL) | Cxxx-NCR-001276 | NCR | DSS - Missing drainage Level 4 to 3 Liner Wall |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-09-30 | 2015-09-30 17:16 | 0 | 2015-06-23 15:39 | Civil - Drainage | 1500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The first section of Liner wall between Level 4 and Level 3 slab was poured to the top of Level 3 slab (SSL +106.540) as per design. A drainage pipe is to be installed as detailed on drawing Cxxx-__M-P-DDD-D061_WS107_Z-10502 OPTION detail D-1 or D-2. The pipe has not been cast-in the concrete pour.
| 02SL - Stations (LUL) | Cxxx-NCR-001278 | NCR | TTH Fire, Comms, PAVA & Electrical Drawings |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-05-01 | 2016-04-27 10:46 | -4 | 2015-06-23 15:27 | Communications and Control Systems - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | __ installed primary cable management services (CMS) for Fire, Comms, PAVA and Electrical disciplines within the TTH without approved issued for construction (IFC) drawings. The works were constructed to the following Cxxx-__M-E-DWG-D061-50006 P04 Cxxx-__M-E-DWG-D061-50007 P04 Cxxx-__M-E-DWG-D061-50008 P03 Cxxx-__M-E-DWG-D061-50009 P03 Cxxx-__M-E-DWG-D061-50011 P04 Cxxx-__M-E-DWG-D061-50012 P05 Cxxx-__M-E-DWG-D061-50015 P04 Cxxx-__M-E-DWG-D061-50025 P03 Cxxx-__M-E-DWG-D061-50026 P03 All drawings have achieved C01 status
| 02SL - Stations (LUL) | Cxxx-NCR-001279 | NCR | Damaged Heat Recovery Unit |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-10-21 | 2015-10-20 09:59 | -1 | 2015-06-23 15:31 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Damaged | Reject | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Damage to the heat recovery unit LHRV02 while in transit. While the damage appears to be superficial it will not be known until commissioning if the damage sustained has affected the performance. Close out date September
| 02SL - Stations (LUL) | Cxxx-NCR-001281 | NCR | LULO Use of non approved material |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-08-08 | 2015-08-06 17:49 | -2 | 2015-06-23 18:13 | Civil - Civil Engineering General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | The metal decking for the ESS has started to be installed on site. Before concrete is poured it is a requirement to seal gaps larger than 3mm. There is currently no approved 1-085 material that is suitable to fulfil this criteria. This issue was raised previously under Cxxx-NCR-001180 for the Area 1 metal decking. The outcome of this NCR was to supply drawings for approval showing where the sealant will be applied prior to installation of the decking. This however is not practicable as the use of the sealant cannot be determined until the decking is installed on site. Going forward, the suggested practical approach is that the sealant in Cxxx-__M-C-LRC-D061_WS106-50027 is applied and then allowed to cure. Prior to pouring concrete the cured foam will be trimmed back to the minimum requirement to provide a seal. The D3-115 metal decking sign off form will be updated to add an additional check that this has occurred, the new rev 2.0 is attached to this NCR.
| 02SL - Stations (LUL) | Cxxx-NCR-001282 | NCR | CHS - Level A pour 5 northern and eastern stopend movement |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-02-14 | 2016-02-14 20:54 | 0 | 2015-06-25 08:55 | Shafts - Shafts General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the pour of the Level A slab pour 5 the 600mm high stopends on the eastern and northern edge moved up to 20mm out of position due to the weight of the concrete. See attached marked up drawing for location detials. __ propose 2 alternate solutions depending on the area of the overpour. 1) in areas where side of slab is not covered by cladding the face will be scabbled to required depth and repaired as per concrete making good procedure Cxxx-__M-C-GPD-D061_50017. 2) in areas where slab is covered in exterior cladding, any lips will be smoothed and made good as per Cxxx-__M-C-GPD-D061_50017.
| 02SL - Stations (LUL) | Cxxx-NCR-001283 | NCR | DSS - Honeycombs and holes on the Underside of level 4 slab |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-08-20 | 2015-08-07 16:47 | -13 | 2015-06-24 12:48 | Civil - Civil Engineering General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In between Walls W5-04S and W5-01NS the concrete finish of the underside of Level 4 slab is not up to standard. Honeycombs and openings are visible on the surface of the concrete (see attached photo)
| 02SL - Stations (LUL) | Cxxx-NCR-001284 | NCR | LULO ESS Non-Conforming Bracing |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-10-20 | 2016-10-25 08:36 | 5 | 2015-06-29 16:34 | Civil - Civil Engineering General | 2000 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Due to a fabrication error of the connection plate to BC 403 (__ Mark 4014) in the ESS connecting the steel girder to the concrete lift shaft, the bracing BC 386 (__ Mark 4046) does not connect as indended via the two M24 Grade 10.9 HSFG bolts, see photo attached to this NCR (Cxxx-JV00030-NCR-0024 (Binded).pdf).
| 02SL - Stations (LUL) | Cxxx-NCR-001285 | NCR | CHS - Level A pour 5 North east corner underside concrete finish |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-12-04 | 2015-12-03 16:06 | -1 | 2015-06-30 12:21 | Shafts - Shafts General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The finish on the concrete on the underside of the slab in the north eastern corner of level A pour 5 does not meet the specification requirements. See attached photos and marked up drawings for detials. __ propose to repair the section that does not meet the requirements using 'RC Remedial Works' WMS doc number Cxxx-__M-C-CCN-D061_WS107-50010.
| 02SL - Stations (LUL) | Cxxx-NCR-001286 | NCR | E51 floor opening - Trimming of Fin Plate |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-09-23 | 2015-09-21 09:59 | -2 | 2015-07-02 10:54 | Civil - Structural Engineering | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please see attached sketches. The 2no openings highlighted in the attached sketches should be 500mm. The as built opening was measured at 485mm. To gain an extra 10mm, BM4 needed to have the fin plate fixed on the inside of the beam. For this to happen 5mm had to be trimmed at the top and the bottom of all 4no fin plates on BM1, it would not fit otherwise. Due to late change in design some the Beams were fabricated additionally as add on to reflect the changes. This may have resulted in the misalignment of the beams. Therefore the reduced opening could not be picked up at earlier inspections. Due to programme reasons the work had to be done immediately as the delivery/installation of switch gear was imminent. There for the correct FCD processes could not be followed.
| 02SL - Stations (LUL) | Cxxx-NCR-001287 | NCR | E51 Swichboards Weight |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-08-17 | 2015-07-07 06:46 | -41 | 2015-07-03 14:37 | Electrical - LV Equipment | 1000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Error by manufacturer in shipping or marking | Completed |  | E51 Switchboards design was submitted as an approximation of 250kg in weight. Upon delivery, it was identified that the weight of each Switch Board exceeded the manufacturers predicted design weights substantially. Hence, this raised a question of E51 structural flooring loading capability.
| 02SL - Stations (LUL) | Cxxx-NCR-001288 | NCR | Works commencing prior to code 1 ITP - Winthrop - Durward Retaining walls |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-07-20 | 2015-07-20 15:34 | 0 | 2015-07-06 14:13 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | Works commenced on Winthrop and Durward street abutments prior to Code 1 ITP being accepted
| 02SL - Stations (LUL) | Cxxx-NCR-001289 | NCR | LULO - ESS stair 23 - hairline and larger fractures to the stair soffits |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-01-15 | 2016-01-14 15:00 | -1 | 2015-07-09 15:57 | Architectural - General | 2500 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Cracks have appeared in the stair soffit as per the attached photograph.
| 02SL - Stations (LUL) | Cxxx-NCR-001290 | NCR | DSS Level 5 Blockwork - Laying of Mortar to vertical jolints |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-08-23 | 2015-08-26 09:18 | 3 | 2015-07-09 16:34 | Architectural - Brickworks/Blockworks | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the Supplier Appraisal Quality Site Inspection, the vertical joints between blocks were inspected. From the sample undertaken, insufficient mortar between the vertical joints was discovered.
| 02SL - Stations (LUL) | Cxxx-NCR-001291 | NCR | East Stair Shaft - As-built Steel Deviations |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-08-01 | 2016-03-24 16:56 | -130 | 2015-07-15 19:07 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | East Stair Shaft - As-built Steel Deviations, Please refer to the enclosed marked-up as built of the East stair shaft steel structure, we note that the structure has deviated slightly beyond the permitted deviations of the NSSS Section 9: Accuracy of Erected Steelwork. The affected structural deviations comprise of the: horizontal alighnment of the columns, and minor deviations to the sloping & verticle alignment of the floor beams.
| 02SL - Stations (LUL) | Cxxx-NCR-001292 | NCR | TTH - Incorrectly installed lintel in OLBI room level A |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-10-11 | 2015-08-03 16:31 | -69 | 2015-07-13 09:42 | Architectural - Brickworks/Blockworks | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Due to issues with the datum being too far away from the door lintel being fitted for the quality of equipemnt used the height was measured off the floor for the door height and lintel fitting. The lintel was installed level but due to slightly uneven/damaged screed below the door lintel is too close to the ground on one side. This size would not fit in the door and the frame.
| 02SL - Stations (LUL) | Cxxx-NCR-001293 | NCR | CHS - CA-25 column poured 50mm larger than design |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-07-28 | 2015-07-22 14:29 | -6 | 2015-07-14 13:21 | Shafts - Shafts General | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As per discussion between __, Cxxx and __ on 14/07/2015 column CA-25 will be poured at a size of 600mm x 450mm, this differs from design by 50mm. The increase in the column size is in the northern direction. See attached Level A plan for column CA-25 location. - The increase in size of the column will be to maintain nominal cover on the column starters. - __ will cut and bend new links to fit size of column size increase, see attached __ extract. - As kicker is currently 500mm x 600mm, kicker will be cut to size 450mm x 600mm - __ will increase the set on the column main bars (BM37 on attached __ extract) to ensure starter bars are in the correct position for CB-25 above.
| 02SL - Stations (LUL) | Cxxx-NCR-001294 | NCR | HCDL-Western Platforms- Working to Non-IFC Drawings |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-09-30 | 2015-09-09 10:33 | -21 | 2015-07-14 14:44 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | The HCDL western platforms construction works have proceeded without IFC drawings. This has not been instructed or agreed formally by the Project manager via CCM/PMI to proceed with works without IFC drawing in place. However the project manager is aware of the ongoingoing works. The HCDL Western Platforms works are currently progressing. The works are covered by the list of drawings attached in RIR 58 and RIR 69. The drawings are currently in P0x revisions awaiting CO1 status. All the drawings in the attached list has been through the Mini Gate process, however the formal approval of these drawings and issue of IFC status drawing is with the Desin Team/Project Manager. The works are being progressed in order to meet the Interim Station programme date.
| 02SL - Stations (LUL) | Cxxx-NCR-001295 | NCR | Blockwork CHS level 6 - Wall out of plumb |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-11-15 | 2015-10-21 11:11 | -25 | 2015-07-15 16:37 | Architectural - Brickworks/Blockworks | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | CAMBRIDGE HEATH SHAFT LEVEL 6 BLOCK WORK WALL WHICH FORMS CER2 & FCR ROOMS THE DOUBLE SKIN OF .90mm BLOCKWORK OUT OF TOLERANCE IN PLUMB BY 28mm over 4.5m height.
| 02SL - Stations (LUL) | Cxxx-NCR-001296 | NCR | CHS Blockwork Level 6 - wall out of level tolerance |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-11-15 | 2015-10-21 13:29 | -25 | 2015-07-15 16:44 | Architectural - Brickworks/Blockworks | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Level difference between 2 walls in Staircase 41 is out of tolerance - over 11mm between two walls corner. Maximum tolerance in plane for fire stopping installation is 2mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001297 | NCR | E51 Flooring |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-11-01 | 2015-10-29 17:42 | -3 | 2015-07-16 15:22 | Architectural - Flooring | 4000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Accidental damage has been made to one of the steel floor beams. It appears that someone was cutting something over the steel beam and had cut through part of it. The cut is approx. 2-3mm wide and runs from the top flange to the web. The damaged was caused sometime after the IRF inspection for the floor beam installation. i have attached photo graphs and DWG showing which beam is damaged.
| 02SL - Stations (LUL) | Cxxx-NCR-001298 | NCR | Offsite Steel Fabrication - Phase 3, 4 and 5. Winthrop and Durward Street bridges |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-08-30 | 2015-08-28 16:07 | -2 | 2015-07-16 15:27 | Civil - Structural Engineering | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the 25% fabrication surveillance undertaken by PTS (on behalf of __) on 18 July 2015, welding actvities were observed outside of the electrical current parameters of the supporting Weld Procedure Specification (WPS).
| 02SL - Stations (LUL) | Cxxx-NCR-001299 | NCR | Offsite Steel Fabrication - Phase 3, 4 and 5. Winthrop and Durward Street bridges - Welder Quals |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-08-30 | 2015-09-03 17:25 | 4 | 2015-07-16 15:38 | Civil - Structural Engineering | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the 25% fabrication surveillance undertaken by PTS (on behalf of __) on 18 July 2015, it was observed that the welder approval test certificate had expired and had not been revalidated for a welder carrying out welding in the fabrication workshop. Welder name: R.Sijpenhof, Certificate number: 267835/RTV/032 Rev.0
| 02SL - Stations (LUL) | Cxxx-NCR-001300 | NCR | 6No. Termporary Grout Piles to re-build up to cut-off level on WLL |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-09-29 | 2015-09-29 16:58 | 0 | 2015-07-17 14:56 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 6 of the temporary reinforced grout piles for the West Lift Lobby contiguous piled wall were built at a lower level than the design pile cut-off level (+110.125m). NCR re-work on 21/07/2015. Responses to additional queries: - What are the achieved pile levels? R: Level of top of reinforcement cages: Pile no. 2: +110.194m; Pile no. 9:+110.235m; Pile no. 27: +110.215m; Pile no. 31:+110.195m; Pile no. 34: +110.159m; Pile no. 44:+110.247m. The pile cutoff level (for all piles) is +110.125m (under top of cage for all aforementionned piles) but when breaking the piles to the cutoff level as the grout is very unstable and cracks easily and the piles were broken down below cutoff level. This is the reason to re-build the mentioned piles. - If you are proposing a different grout what is the spec? R: The proposed grout to re-build the piles has the same strength as the grout used to build the piles. The suitability of 5 Star Grout has been agreed with the __ Temporary Works Designer who detailed these works. - How will the interface between the existing and new grouts be managed? R: Existing grout is not to be scabbled as there is no requirement for it and as it would easily break and make the situation worse (lower the break down level even more). - Is there a requirement to extend reinforcement (starter bars) and if so what is the spec/detailing? R: On the original pile design there are female couplers on the top of the pile reinforcement and these couplers are to be fitted with B25 threaded tapered bars (525 length) to the same level of the capping beam reinforcement. The levels achieved at the top of piling cages (see levels above) allow to do so and guarantee the correct anchor length. There are no issues/design deviations regarding reinforcement.
| 02SL - Stations (LUL) | Cxxx-NCR-001301 | NCR | Damage to CMS on London Overground during the July 4/5th possession |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-10-22 | 2018-09-19 12:39 | -33 | 2018-05-15 08:01 | Electrical - General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Damage to CMS on Platform 6 beside Durward Street abutment wall
| 02SL - Stations (LUL) | Cxxx-NCR-001302 | NCR | Not installed cast in items inside Lift 6 (ESS) |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-03-31 | 2017-05-30 21:39 | 60 | 2015-07-21 14:12 | Civil - Civil Engineering General | 12000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Cast in items not installed on the inside face of the western wall of Lift 6 (ESS). Please see orange highlighted items on the attached drawings. Lifting eyes not cast in, hence will require post fixed lifting eyes.
| 02SL - Stations (LUL) | Cxxx-NCR-001303 | NCR | TTH Drawpit 4 Distance between Ducts and Highway Level |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-10-19 | 2015-08-11 08:58 | -69 | 2015-07-21 16:24 | Civil - Utilities Engineering | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | See attached drawing Cxxx-__M-E-DWG-D061-50018 for reference. As per the drawing the distance between the top of duct and highway level was required to be 450mm. Due to site circumstances and achieving the distance between duct and bottom of chamber the as built distance between duct and highway level is in fact 545mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001304 | NCR | Packing/shimming of the Insulation to the level A roof. |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-11-14 | 2016-08-10 09:10 | -96 | 2015-07-21 17:19 | Architectural - Roofing & Exterior Treatment | 30000 |  | Incorrect Installation | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Works not done in accordance with design. Due to slab previously being and uneven finish (captured as NCRs 1055 and 1156) the insulation could not be laid with flat edges and the desired fall without packing underneath. To get the fall as per design thin strips of rockwool was packed unerneath areas that were more uneven. The fall is now correct despite the floor being uneven. Kemperol have informally said that this is a valid solution to the even floor and will not jepordise the integrity of the roofing product. There is a report from kemperol we are awaiting on to be able to close this NCR. Insulation installed on top of VCL prior to VCL NCR being closed out.
| 02SL - Stations (LUL) | Cxxx-NCR-001305 | NCR | Galvanising protection to weld on vent stack in Bin Stores room TTH has failed |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-10-20 | 2015-10-04 15:25 | -16 | 2015-07-22 11:43 | Civil - Sewage/Water services | 1200 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The galvanising protection to a joining weld on the vent stack in the bin stores has failed as it has begun to rust. This is thought to be due to improper prepartion of the welding surface.
| 02SL - Stations (LUL) | Cxxx-NCR-001306 | NCR | The brick piers along grid line G do not align, causing a mis-alignment with the cladding. |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-11-27 | 2015-12-01 09:24 | 4 | 2015-07-22 12:10 | Architectural - Brickworks/Blockworks | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The brick piers either side of the main entrance to the TTH are mis-aligned along the wall on GL G. This affects the allignment of the exterior cladding slightly. It does not affect the cladding abve the gateway. The mis alignment is in the realm of about 20-30mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001307 | NCR | Offsite Steelwork Fabrication - Area 3 Steelwork Link Beam Stud Bolts |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-11-05 | 2015-10-28 15:54 | -8 | 2015-07-23 15:02 | Civil - Structural Engineering | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Stud Bolts on the link beams have been welding in a straight line.
| 02SL - Stations (LUL) | Cxxx-NCR-001308 | NCR | Use of Unapproved Material in Winthrop West Abutment |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-09-21 | 2015-09-22 07:57 | 1 | 2015-07-24 15:12 | Civil - Structural Engineering | 1500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A MCR was drafted and submitted (Cxxx-__M-C-LRC-D061-50195) on 26/06/15 for __ 2 Soft Joint after it was noticed that it was approved only on the disused roads/D122b subway. It had passed it's period of reply (14 days) and __ proceeded to use the material to stay ahead of a tight programme. The location that it is used is on the southern end of Winthrop West (refer to plan detail in drawing Cxxx-HYD-S-DDD-D061_WS106_Z-79050). The material is fully enclosed in the structure (refer to attached mark up), as it acts as a movement joint except the edge of the material as detailed in the attached sketch.
| 02SL - Stations (LUL) | Cxxx-NCR-001309 | NCR | CHS - Cover to reinforcement on drainage upstand on Level 3 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-08-27 | 2015-08-21 15:25 | -6 | 2015-07-23 18:51 | Shafts - Shafts General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Cover to the reinforcement on the drainage upstand on level 3 did not meet minimum requirements. In addition to the cover issue a communication breakdown occured and a small section, approx 2m was poured. When identified that the pour was taking place the pour was stopped immediately. As the quality in the area that was poured was fine, this decision was made to leave the concrete in place. __ propose to: - Cut off upstand steel that has insufficient cover, break down concrete around the bars and ensure that bars are cut below the concrete level. - Drill and fix B12 bars to replace any links that are without cover. Bars will be fixed with __ Hit 200 and all drilling will be done in accordance with the __ guidelines - leave poured area as is as quality was acceptable
| 02SL - Stations (LUL) | Cxxx-NCR-001310 | NCR | CHS - Column C1-26 out of plumb |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-08-11 | 2015-08-11 09:04 | 0 | 2015-07-28 09:24 | Shafts - Shafts General | 1500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Column C1-26 was cast out of plumb. This has put column C1-26 at the top 23mm to the north of designed position. This positional error will transfer up to CA-26 which will be 23mm too far north and the portion of WA-21 at GL4 will be 23mm to the north. As discussed with Cxxx and __ (see attached email correspondance): - Structurally C1-26 is satisfactory - Positionally 23mm north for C1-26, CA-26 and WA-21 (at GL4) is satisfactory __ propose to: - Cast CA-26 and W1-21 vertical to the underside of the CDB-B-01 at which time the positional error can be reduced without any lipping or protrusions in the wall or column. - W1-21 will be put to the correct location at column CA-19, the 23mm to the north will be reduced to 0 over the 6.45m from GL4 to GL3
| 02SL - Stations (LUL) | Cxxx-NCR-001311 | NCR | DSS C4-13 BM 49 installed at the incorrect level |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-08-14 | 2015-08-06 14:55 | -8 | 2015-07-31 10:38 | Shafts - Shafts General | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | BM 49 on 50853 was installed at the incorrect level, this was identified when attempting to fix CDB-3-02.
| 02SL - Stations (LUL) | Cxxx-NCR-001312 | NCR | Cabling in TTH |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-10-11 | 2015-09-21 15:03 | -20 | 2015-08-02 16:50 | Electrical - Cable Management | 0 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Cabling in the TTH has commenced prior to inspection and approval of the CMS. Fire Alarm, Comms and PA/VA cabling has been installed to meet programme dates prior to the CMS being inspected and signed off by Crossrail.
| 02SL - Stations (LUL) | Cxxx-NCR-001313 | NCR | LULO Durward Street Bridge Upper Deck Reinforcement Mesh |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-10-30 | 2015-09-09 13:22 | -51 | 2015-08-03 15:43 | Structural Engineering - Reinforcement | 750 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The A393 mesh laid to the top of Durward Street Bridge upper deck slab was placed in orientation approximately 14 degrees out of that specified on the ‘For Construction’ issue RC drawing Cxxx-__M-C-DWG-D061_WS106-50438-C02. It is noted on the current issue drawing that the mesh shall be laid on B2 with orientation of T1=B1 and in the direction of the deck span. However the mesh was laid as T2=B2, and while being generally in the direction of the span, T1 is oriented approximately 14 degrees out of parallel with B1. Details of the as-built A393 mesh orientation are shown on the attached “Sketch20150803 – NCR to mesh orientation at Durward Street Bridge upper deck”, photo attached within the PDF.
| 02SL - Stations (LUL) | Cxxx-NCR-001314 | NCR | Durward St. Utilities trough land drain access shaft |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2016-10-01 | 2016-09-26 13:11 | -5 | 2015-08-04 14:56 | Utilities Engineering - Utilities General | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | RFI-2264 was raised on 12/12/2014. This RFI requested clarification on how to terminate the land drain which was part of the utilities trough over the LO platforms which was to be used for the Durward street utility diversions. Subsequently an FCD was submitted with the appropriate termination as agreed at a workshop between CRL and Cxxx. FCD-964 was initiated on 23/01/2015, and approved on 28/01/2015. The diversions have since taken place, and the area backfilled. However Crossrail have not been invited to inspect any element specific to this element prior to backfill and are not aware of any access shaft being installed as agreed within FCD-964 or what form of termination the land drains have been left in.
| 02SL - Stations (LUL) | Cxxx-NCR-001315 | NCR | Phase 3 and Durward St Upper Deck Steelwork - As Built Steel Deviations |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-05-13 | 2016-05-16 11:30 | 3 | 2015-08-04 18:34 | Structural Engineering - Steel Member | 3000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | For Phases 3, 4 & 5 we note that the structure has deviated slightly beyond the permitted deviations of the NSSS Section 9: Accuracy of Erected Steelwork. The survey was conducted by __'s surveyor, Longline during the time of installation of the beams. __ are undertaking a survey of the steelwork to produce a check on the setting out. Phase 3 Please refer to the enclosed marked-up as built of the Phase 3, Winthrop & Durward St Lower Beams. For Winthrop St, the affected structural deviations comprise of the beam location being greater than tolerance. For Durward St, the affected structural deviations comprise of beam level, beam slope and beam location. Durward St Upper Deck Please refer to the enclosed marked-up as built of the Upper Deck, the affected structural deviations comprise of beam level, beam slope, relative beam level, beam location and beam spacing.
| 02SL - Stations (LUL) | Cxxx-NCR-001316 | NCR | Reaming of the Connection Detail for Durward St Upper Deck |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-09-13 | 2015-09-27 15:35 | 14 | 2015-08-04 19:02 | Structural Engineering - Steel Member | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the installation of the Durward St Upper Deck, the West-middle column connection did not align with the connection to the upper deck in that location. __ reamed out the holes to allow for the connection to be fully bolted.
| 02SL - Stations (LUL) | Cxxx-NCR-001317 | NCR | TTH ESUB Foundation Location |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-11-03 | 2015-08-24 18:36 | -71 | 2015-08-05 17:19 | Civil - Sub-base | 1000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | (Further to Cxxx-FCD-001095) There was an indiscrepancy in drawings for the location of the ESUB foundation within the TTH. Drawing Cxxx-__M-A-DWG-D061-50004 showed the location of the ESUB as sitting directly above the GLE ground beam, it was not possible to cast the slab in this location. The ESUB foundaion was therefore cast in the location shown on Cxxx-__M-C-DWG-D061-50122. However after casting in this location, it was determined that the foundation located here would cause a clash between the ESUB and CBS advertisement board. The ESUB foundation then had to be cast again in the location in attached RFI 077 and sketch 10240596-IKV-0025.
| 02SL - Stations (LUL) | Cxxx-NCR-001318 | NCR | CHS - Missing starter bars WA-18NS |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-08-20 | 2015-08-25 10:10 | 5 | 2015-08-06 08:03 | Shafts - Shafts General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Starter bars (BM11 on drawing attached) for WA-18ns were missed during the construction of W1-18s. __ proposed to replace BM11 with a B16 L-bar that will be embedded into the level A slab at 115.350. The L-bar will be 1.3m long with the bottom of the L-bar sitting in the B3 layer of the slab. Bars will run in the centerline of the WA-18ns.
| 02SL - Stations (LUL) | Cxxx-NCR-001319 | NCR | TTH External Cladding - Detailing and Damage |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-07-15 | 2016-07-14 15:32 | -1 | 2016-01-19 17:38 | Architectural - Roofing & Exterior Treatment | 2500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The following details/locations have been installed by __ to complete the external cladding; these details were reviewed on site and are primarily required to close gaps in the cladding and interfaces between materials. This is on request from LU regarding concern of finger traps and possible concealed areas. None of these details compromise the rain screen system as the weather proof building line is set behind this at the __ breather membrane. TTH Column Capping’s TTH Door and Window head cill sitting proud of cladding line, weep holes incorporated TTH MEP penetration – weather shroud (GLE) TTH GL E beam penetration TTH-Court Street bridge interface TTH brick pier flashing TTH external stair soffit TTH finger traps <2.4m height – __ foam (Photographs attached) These details have been reworked following the inspection between __, CRL and LU (Cxxx-NOWRI-000051) and these observations have been recorded on the DOWL (DOWL-LULO-917 – 977). This NCR should also record a number of areas where the cladding has minor damage including dents, scratches, hair-line cracks and markings.
| 02SL - Stations (LUL) | Cxxx-NCR-001320 | NCR | TTH BWIC - Design Coordination |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-05-31 | 2016-05-25 17:15 | -6 | 2016-01-21 11:17 | Architectural - Brickworks/Blockworks | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Further to Cxxx-FCD-001009, sketch 10240596-XKA-0164 was submitted following amendments to the BWIC for the TTH blockwork walls; this was required due to clashes between MEP routes and structural elements. The M+E design was not fully coordinated with the architectural design meaning that we continued to observe clashes, these were resolved on site with __ and __ on the understanding that as long as the opening size and bearing width of the lintel, this is documented in the attached email chain and following agreement: “Additional penetrations have been installed through blockwork and partition walls on both level 1 and A of the TTH to facilitate M+E and third party routes, these will be captured in the relevant mechanical and electrical packages. Regarding the final as built record of the wall penetrations, the fire stopping identifies every penetration as this has been asset tagged as part of fire stopping, package Cxxx-__M-A-CER-D061-50014. Please see attached copy of these records. __ confirmed during on site meetings that the change to the penetrations to accommodate M+E was acceptable assuring that the penetration were supported with a lintel bearing in accordance with specification clause F30-735A. The attached email chain is evidence of this agreement.” The final fire stopping register including locations plans and photographs will be attached in closure of this NCR for completeness.
| 02SL - Stations (LUL) | Cxxx-NCR-001322 | NCR | WSME Cladding - Non Approved Materials |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-03-20 | 2016-02-25 17:04 | -24 | 2016-01-20 15:15 | Architectural - Roofing & Exterior Treatment | 2500 |  | Material | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | In constructing the WSME, there have been non-compliant materials trapped within the fabric, the reason for this is construction sequence (i.e. lifting pre-fabricated panels/requirements to keep blockwork dry whilst awaiting permanent roof). Such materials include lifting strops and tarpaulin. This NCR should also capture that __ foam initially installed above E51 door was removed and replaced with __ C144, photographs attached. These materials have been moved as much as physically possible without damaging the permanent works, cutting back and disposed of. The materials trapped in the structure have subsequently been encased within fire protection and pose no concern as they are fully encapsulated.
| 02SL - Stations (LUL) | Cxxx-NCR-001323 | NCR | TTH Drawpits 1/2/3 Distance Between Highway and Duct Level |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-08-24 | 2015-09-03 14:57 | 10 | 2015-08-10 11:39 | Civil - Utilities Engineering | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Further to Cxxx-NCR-001303. For all 4 drawpits shown in drawing Cxxx-__M-E-DWG-D061-50018, the distance between highway level and top of duct should be 450mm. However due to site conditions for drawpits 1, 2 and 3, the distance falls somewhere in the range of 545mm-585mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001324 | NCR | TTH Drawpits 1/2/3/4 Rectangular Cuts |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-01-13 | 2016-12-20 12:40 | -24 | 2015-08-10 11:48 | Civil - Utilities Engineering | 4000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | All 4 draw pits in drawing Cxxx-__M-E-DWG-D061-50018 are required to have holes drilled with a hole saw to facilitate the ducts being installed into circular holes. Instead, in all 4 draw pits these holes have been cut rectangular, leaving much larger gaps between ducts.
| 02SL - Stations (LUL) | Cxxx-NCR-001325 | NCR | Steel preparation and paint to Court Street Bridge Beams |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-02-11 16:06 | -140 | 2015-08-10 15:47 | Structural Engineering - Surface Treatment | 6000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | This NCR relates to painting to the existing steel Bridge beams on Court Street Bridge. Our specification calls for Abrasive vacuum blast cleaning to Sa2½ for life to first maintenance of 25 years. Since award of the contract our Subcontractor has suggested, and had approval from __, that if a suitable paint adhesion test is passed then the blasting can be omitted, any exposed surfaces prepared to ST3 and a 25 year guarantee still given. Unfortunately, the paint adhesion tests have failed and in carrying out the tests the Subcontractor has now raised concerns that blasting may further damage the bridge due to its existing condition and relative age. The Adhesion Report states that the paint manufacturer will guarantee the system for ‘5 to 10 years’. In addition, __ subcontractor also proceeded with application of primer and first coat prior to reciept of Adhesion test results.
| 02SL - Stations (LUL) | Cxxx-NCR-001326 | NCR | TTH Ground Floor Slab Changes |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-12-03 | 2015-11-15 11:57 | -18 | 2015-08-12 15:38 | Civil - Concrete Pavement | 12000 |  | Design | Use As-Is | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | All changes recorded on this NCR are deviations from original construction drawing Cxxx-__M-C-DWG-D061-50122. 1. Matwell Extension: As per RFI-120, the matwell slab had to be extended in order to give a platform to which the blockwork wall tying the existing LU garage and new blockwork wall together could be built on. The extension needed to be an addition 700mm to the East, across the doorway and entrance to the LU garage (see photo DSCF1081 for clarification). The south matwell slab was already cast and already had reinforcement to tie the extended part into. In order to obtain the required cover over the ground beam on Gridline 5, the area south of the entrance to the cupboards (see photo DSCF1098) were poured at a level of +113.395 (50mm higher than the rest of the Matwell slab). 2. POMs Plinth; Due to the change in levels of the finished floor; the safe plinth has changed from 175mm deep to 235mm deep to suit FFL +113.710. The change in height has been captured in 10240596-XKA-0281 Rev 0. There has also been an addition of a 100mm high plinth for the ticket machines, also captured in 0281. Both plinths were dowelled at 600mm centres, 100mm embedment and received a layer of mesh before being poured with C32/40 concrete as per RFI-162. 3. Screeded Areas; Section 9-9 and 10-10 on Cxxx-__M-C-DWG-D061-50122 show a build up of 130mm thick screed with a mesh reinforcement. These area have not been built up with screed. Section 10-10 was cast in concrete during matwell slab pour 1 (see Cxxx-FCD-000915) and then broken out locally to facilitate gate track install (see Cxxx-NCR-001191). Section 9-9 has not yet received anything in this area but we propose to use concrete here as this will tie into the adjacent North Slab which is also concrete and receives only a floor sealer finish.
| 02SL - Stations (LUL) | Cxxx-NCR-001328 | NCR | Permeter Wall joint/ junciton not constructed to drawing |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-08-04 | 2018-06-12 12:40 | -53 | 2018-04-06 11:50 | Architectural - Brickworks/Blockworks | 1200 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The appearance of the wall perimeter wall joint at Level 6 grid line 4-D is not consistent with how this junction is shown on the layout plan Cxxx-__M-A-DDA-D061_WS107_6-20661
| 02SL - Stations (LUL) | Cxxx-NCR-001329 | NCR | Level 4 & 5 Structural Ties Missing In Vertical/Horizintal Direction |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-02-01 | 2016-01-29 09:27 | -3 | 2015-10-01 10:50 | Architectural - Brickworks/Blockworks | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Structural ties missing in vertical and horizontal direction with the nearest tie being 1200mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001331 | NCR | TTH - Hot & Cold Water Pipework - Brackets Hanging from Electrical CMS Bracket |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-12-03 | 2015-11-09 16:08 | -24 | 2015-10-08 17:36 | Mechanical - Hot & Cold Water Supplies | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Setting out of pipework differs from drawing due to coordination with electrical services. __ rings hang from electrical support due to location of run and access for other services. Additional weight on CMS support considered to be negligible
| 02SL - Stations (LUL) | Cxxx-NCR-001332 | NCR | TTH SSO - Mechanical Plant Clash with Electrical CMS |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-10-28 | 2015-10-20 09:55 | -8 | 2015-10-14 12:21 | Mechanical - Mechanical Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | There has been concern raised that the maintanence of the mechanical plant above the ceiling in the TTH SSO will be inhibited by the Electrical CMS and associated bracketery. The mechanical plant requires filters to be changed and electrical terminations to be accessible.
| 02SL - Stations (LUL) | Cxxx-NCR-001333 | NCR | TTH - Mechanical / Electrical Segregation |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-10-23 | 2015-10-13 12:17 | -10 | 2015-08-31 07:53 | Mechanical - Mechanical Engineering General | 5500 |  | Design | Use As-Is | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Throughout the TTH there are a number of clashes between the mechnaical and electrical services. The specified distance between services should be 150mm. This has not been adhered to in a number of places due to the lack of available space above the ceiling. A 3D model of the TTH building would have picked up some of these clashes had this been carried out.
| 02SL - Stations (LUL) | Cxxx-NCR-001334 | NCR | Addition of Water to Apply a Brushed Finish to Area 1 Slab on Metal Decking |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-01-01 | 2017-12-15 14:38 | -17 | 2015-08-26 11:39 | Civil - Concrete Pavement | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Pour no. 3 of Area 1 Metal Decking was completed during the engineering hours and subsequently cured. As with the rest of the pours, it was allowed to go off slightly prior to applying a brushed finish as per requirement during the early hours of the day shift. During this process, the Operatives attempted to apply the brushed finish whilst the concrete was still too wet. They left it and returned to complete later on, at this point – the concrete had hardened at the surface so they added water to make it workable enough to apply a brushed finish. __ are now speaking with our materials technicians and an investigation is underway.
| 02SL - Stations (LUL) | Cxxx-NCR-001337 | NCR | WSS - Pile out of tolerance |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-10-20 | 2015-09-14 14:04 | -36 | 2015-09-01 14:32 | Shafts - Shafts General | 1500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Upon completing the 2nd stage of excavation (+109.4m to +104.55m) at the West Stair Shaft down to base blinding level (+104.65m), it has become apparent that 2no. piles are out of vertical tolerance and protrude out of the back blinding over part of their height •Pile no. 30 protrudes approximately 90mm out of the back blinding at level 104.65m. It is back flush with the back blinding at level of 106.45m therefore is protruding into the back blinding over a height of 1.8m •Pile no. 22 protrudes approximately 40mm out of the back blinding at level 104.65m. It is back flush with the back blinding at level of 106.65m therefore is protruding into the back blinding over a height of 2m Both piles were within tolerance following the 1st stage excavation (112.6m to 109.4m) and construction of the upper level liner walls. __ have confirmed that in both piles, there is currently 125mm cover to the main reinforcement at the location in question. This additional cover is a result of using a casing to construct the piles. __ plant to scabble 50mm off both piles in the location where they protrude out of the back blinding. This will result with 75mm cover on each pile which is the minimum required. By removing 50mm from both piles; •Pile 22 will be within the back blinding and the back blinding will be cast over the pile as usual •Pile 30 will still however protrude 40mm out of the back blinding over a height of 900mm from the base slab bliding level. The surface of the pile will be made smooth in this location and the __ waterproofing layer will be installed directly to the face of the pile. The liner wall / base slab reinforcement may need to be moved slightly in this location to ensure the minimum cover is maintained Please confirm this is acceptable
| 02SL - Stations (LUL) | Cxxx-NCR-001338 | NCR | Fire Main - Work Commencing Prior to an Approved ITP Cxxx-__M-E1-ITP-D061-50004 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-09-16 | 2015-09-15 09:57 | -1 | 2015-09-02 13:59 | Fire - Suppression | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Work commenced by __ sub contractor __ on the Fire Main installation without an approved ITP Cxxx-__M-E1-ITP-D061-50004 . The installation works for the Fire mian at the bottom of the WSME / disused road commenced before the signed decal sheet had been issued. __ had been made aware the document would proceed to Code 1 verbally but were not in possesion of the written document.
| 02SL - Stations (LUL) | Cxxx-NCR-001340 | NCR | Platform 2 Drawpit Concrete Cube Results |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-10-14 | 2015-09-09 14:46 | -35 | 2015-09-02 15:42 | Civil - Utilities Engineering | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | C40 bagged concrete was used to cast the surround of the steel beams and platform infill to the drawpit. Cubes where taken and tested at 7, 28 and 56 days. The maximum compressive strenght achieved was 39.5N/mm2. The design states that the compressive strenght should reach 32/40N/mm2. Although the results have not met the manufacturers strenght they have met the deisgns strenght as per Cxxx-__M-C-CER-D061-50509 - CAT III HCDL Platform 2 MEP Chamber.
| 02SL - Stations (LUL) | Cxxx-NCR-001341 | NCR | DSS Level 8 Drainage - heads cast too low |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-01-29 | 2018-11-02 15:20 | -88 | 2018-10-01 13:55 | Civil - Drainage | 4000 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | DSS Level 8 has been cast lower than specification so drainage caps can't be fitted. Heads have been cast into finished slab level, not finished floor level
| 02SL - Stations (LUL) | Cxxx-NCR-001342 | NCR | Weld Procedures for Area 3, 4, 5 Fabrication - submission prior to fabrication |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-11-26 | 2015-11-09 18:04 | -17 | 2015-09-03 10:48 | Civil - Structural Engineering | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | During a Surveillance by PTS at __'s factory, welding was found to be undertaken without prior submission and approval of the weld procedures for review and acceptance. "__ welding procedure specification 403 for stud welding was submitted for review after stud welding had begun being carried out in the fabrication workshop. This WPS however is not supported by pre-production tests to prove the mechanical properties of the weld as required by BS EN ISO 14555:2014 10.3.1. This documentation will need to be submitted by __ to ensure that the requirements of BS EN ISO 14555 are adhered to. Also, it was noted in the fabrication shop that some manual (138) fillet welding had been carried out on stud welds on beam no 1039 that had not achieved full visible fusion (see photographs). __ were unable to produce a supporting WPS for this stud weld repair and no WPS to cover such welding had been submitted in the original welding documentation.
| 02SL - Stations (LUL) | Cxxx-NCR-001345 | NCR | TTH drainage - Clay pipe above ground |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2016-02-11 | 2016-02-04 16:38 | -7 | 2015-09-08 12:09 | Mechanical - Public Health Engineering | 3000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The clay drainage used as part of the TTH below ground drainage has been cast through the foundation and ground slab and protrudes above ground. This is noncompliant to the TTH Mechanical and Public Health Services specification.
| 02SL - Stations (LUL) | Cxxx-NCR-001346 | NCR | Blockwork CHS Level 5 - Wall out of tolerence |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-10-31 | 2018-11-30 08:32 | 30 | 2018-04-06 11:52 | Architectural - Brickworks/Blockworks | 1500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Cambridge heath shaft level 5 IWS621 wall between grid line A/4,3 - has a number of cuts out of tolerence as well as not being straight in any 5m length.
| 02SL - Stations (LUL) | Cxxx-NCR-001349 | NCR | Level 6 Builders Opening built with 180° orientation (mirrored on elevation) |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-08-04 | 2018-05-31 17:23 | -65 | 2018-04-06 11:53 | Architectural - Brickworks/Blockworks | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Builders opening elevation D-D built with 180° orientation (mirrored on elevation)
| 02SL - Stations (LUL) | Cxxx-NCR-001352 | NCR | CHS - CDB-B-04 bottom couplers damaged |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-09-30 | 2015-09-18 09:14 | -12 | 2015-09-14 11:11 | Shafts - Shafts General | 800 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The position of the bottom coupler (west side) in CDB-B-04, on Column 38, part of the level B slab B3, has moved and is un-usuable (see attached photo). Position of CDB-B-04 and CA-38 are shwon on drawing Cxxx-__M-C-DWG-D061_WS107-50557 (attached). Position of coupler is shown on reinforcement drawing Cxxx-__M-C-DWG-D061_WS107-50561 (attached). __ propose: 1. The beam CDB-B-04 is satisfactory with 2 B25 bottom couplers, see attachement for details. 2. To drill and fix 1no bar in to CA-38. Hole will be 32mm and drilled to a depth of 200, bar will be fixed using __ Hit 200.
| 02SL - Stations (LUL) | Cxxx-NCR-001354 | NCR | CMS (Conduit) Clash with Ceiling Grid |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-10-14 | 2015-10-14 16:04 | 0 | 2015-09-16 16:16 | Electrical - Cable Management | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | TTH Level A - Corridor Conduit had been installed and clashed with the ceiling grid installation.
| 02SL - Stations (LUL) | Cxxx-NCR-001355 | NCR | TTH Level A Corridor -Mounting Height of Speakers |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-10-14 | 2015-10-14 16:06 | 0 | 2015-09-16 16:32 | Communications and Control Systems - Public Address Systems | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | TTH Level A Corridor. PA / VA Speakers mounted in corridor at incorrect height.
| 02SL - Stations (LUL) | Cxxx-NCR-001356 | NCR | DSS Blockwork Missing Ties hatch openings |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-02-11 | 2016-02-10 16:00 | -1 | 2015-09-17 10:04 | Architectural - Masonary | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Missing wall ties in cavity openings identified on level 5 in different locations where ties must be installed every course of blocks. The tie is usually missed is the one in the first course.
| 02SL - Stations (LUL) | Cxxx-NCR-001357 | NCR | DSS Blockwork Discolouration of Materials |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-10-29 | 2015-10-27 10:09 | -2 | 2015-09-17 10:14 | Architectural - Masonary | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Discolorations of Blocks and Mortar seen throughout the shaft on different levels.
| 02SL - Stations (LUL) | Cxxx-NCR-001358 | NCR | Phase 4 & 5 - Lift shaft Beam 6541 clash |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-12-14 | 2015-11-05 17:37 | -39 | 2015-09-21 20:17 | Structural Engineering - Steel Member | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Phase 4 & 5 steelworks, Beam [6541] is connected at both ends using web cleats. Connection of [6541] to lower lift shaft frame [Frame] is via a flange plate located at beam soffit. Installation of [Frame] required lifting down into triangular trusses (Cantilever truss, South end truss & HCDL truss) and brought back upwards to connect to the soffit of the South end truss & corner of Frame bearing onto the lower flange of cranked beam Winthrop St Bridge. Design of [6541] web cleats resulted in [6541] to be installed prior to [Frame] connection. Temporary support angles on both longitudinal sides of [6541] forms a recess with beam lower flange which the [Frame] connection plate would be inserted into from below. This detail formed a clash as the connections for the web cleats could not allow rotation and lateral movement along the horizontal plane of the beam if the lower [Frame] is installed prior. Remedial action of removing 600mm of temporary support angle along one side of [6541] allowed the installation to follow. Please refer to enclosed marked photos.
| 02SL - Stations (LUL) | Cxxx-NCR-001359 | NCR | E51 - Underfloor CMS |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-10-17 | 2016-08-05 11:15 | -438 | 2015-11-17 17:12 | Electrical - Cable Management | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Containment Management System (CMS) for underneath the E51 floor was not on the drawings as part of the E51 early works submission SDR / mini gate process. The contractor has progressed with the under floor CMS to meet the need of interim station. Redline drawing have been created showing the additional CMS under the floor since 'survey date', this is to be given to the designer to incorporate into the permanent works design. The CMS has been inspected by the __ and CRL and relevant check sheets filled in, the work is of a high standard of work and is fit for purpose for interim station cabling.
| 02SL - Stations (LUL) | Cxxx-NCR-001360 | NCR | TTH - Public Health - Works Constructed without an Approved Design |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-11-12 | 2015-10-19 18:58 | -24 | 2015-09-29 10:31 | Mechanical - Public Health Engineering | 3000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | Works have been constructed within the TTH without an Approved FCD being in place. The Redlines of the Public Health works have been captured by the Contractor's Specialist Sub Contractor __ and reviewed by the Designer (__) via a PTR. The PTR is attached and indicates the Designer is satisfied with the changes.
| 02SL - Stations (LUL) | Cxxx-NCR-001361 | NCR | TTH - DX Air Con - Works Constructed without an Approved Design |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-10-27 | 2015-10-21 17:04 | -6 | 2015-09-29 10:50 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | Works have been constructed within the TTH without an Approved FCD being in place. The Redlines of the DX Air Con works have been captured the Contractor's Specialist Sub Contractor __ and reviewed by the Designer (__) via a PTR. The PTR is attached and indicates the Designer is satisfied with the changes.
| 02SL - Stations (LUL) | Cxxx-NCR-001362 | NCR | TTH - Ventilation - Works Constructed without an Approved Design |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-11-19 | 2015-10-20 09:25 | -30 | 2015-09-29 10:57 | Mechanical - Heating Ventilation & Air Conditioning | 1500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | Works have been constructed within the TTH without an Approved FCD being in place. The Redlines of the Ventilation works have been captured the Contractor's Specialist Sub Contractor __ and reviewed by the Designer (__) via a PTR. The PTR is attached and indicates the Designer is satisfied with the changes.
| 02SL - Stations (LUL) | Cxxx-NCR-001363 | NCR | TTH - Hot & Cold Water - Work Constructed without an Approved Design |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-11-12 | 2015-10-19 19:10 | -24 | 2015-09-29 11:09 | Mechanical - Hot & Cold Water Supplies | 1000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | Works have been constructed within the TTH without an Approved FCD being in place. The Redlines of the Hot & Cold Water works have been captured the Contractor's Specialist Sub Contractor __ and reviewed by the Designer (__) via a PTR. The PTR is attached and indicates the Designer is satisfied with the changes.
| 02SL - Stations (LUL) | Cxxx-NCR-001364 | NCR | TTH - CMS Installation - Works Constructed without an Approved Design |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-10-27 | 2015-10-20 09:23 | -7 | 2015-09-29 11:22 | Electrical - Cable Management | 1500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | Works have been constructed within the TTH without an Approved FCD being in place. The Redlines of the CMS works have been captured the Contractor's Specialist Sub Contractor __ and reviewed by the Designer (__) via a PTR. The PTR is attached and indicates the Designer is satisfied with the changes.
| 02SL - Stations (LUL) | Cxxx-NCR-001366 | NCR | CHS - Level B slab B4 CDB-B-07 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-11-10 | 2015-10-27 09:00 | -14 | 2015-10-02 15:54 | Shafts - Shafts General | 2000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | CDB-B-07 requires an alternate design due to a number of issues: - Reinforcement detail drawing Cxxx-__M-C-DWG-D061_WS107-50585 shows the beam resting on non structural wall, WB-30NS. This has the beam at a length of 2.7m. The beam would be required to rest on structural wall WA-15S, this requires the beam to be 4.8m in length. - The beam cannot be built to 600mm deep the whole of 4.8m as wall WB-30ns is cast 150mm too high, meaning the original design depth of 600mm of CDB-B-07 cannot be met. See attachments for details. Following discussion with Cxxx, __ propose to construct a 600mm wide by 450mm deep beam with 5no B32 bars on top and 5no B32 bars on bottom, see attached section for details.
| 02SL - Stations (LUL) | Cxxx-NCR-001367 | NCR | DSS Level 8 Drainage Out of Position |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-01-02 | 2015-11-16 17:18 | -47 | 2015-10-06 16:37 | Civil - Drainage | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Drain CWD3 on Level 8 South has been cast out of position. It should be located within the cavity yet sits within the upstand.
| 02SL - Stations (LUL) | Cxxx-NCR-001368 | NCR | CHS - Level issue with CDB-B-11 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-10-30 | 2015-10-26 09:28 | -4 | 2015-10-06 12:49 | Shafts - Shafts General | 1000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | Beam CDB-B-11 is a transfer beam between wall WA-11S and column CA-28. This beam was not shown on Cxxx’s design intent . Through telephone conversations and email the design intent for this beam was agreed between __ and Cxxx. However in this time column CA-28 had already been cast . The column has been cast to suit a 600mm dp beam. Hence BM 42 will clash with the top of the column. See Sketch 1
| 02SL - Stations (LUL) | Cxxx-NCR-001369 | NCR | HCDL Platform Ducting- Installation without approved drawing and MCR |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2015-11-18 | 2015-11-17 14:30 | -1 | 2015-10-07 13:02 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | The IRF (IRF-LULO-621) referenced drawing Cxxx-__M-C-DDA-D061_WS106_2-12501 rev P05, this is not an approved drawing (revision C01 has been approved and issued) There is no MCR in place for the ducts installed (Cxxx-__M-C-LRC-D061_WS106-50006) See observation CRL-OBS-06064 for further information
| 02SL - Stations (LUL) | Cxxx-NCR-001370 | NCR | DSS Blockwork/Liftshaft Joint |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-11-30 | 2015-11-13 12:37 | -17 | 2015-10-21 15:56 | Architectural - Brickworks/Blockworks | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The joint between IWS-602 and Lift Shaft 2 (W6-04(D)) has varying thickness (maximum of ˜50mm) and is therefore out of tolerance of the spec. Initial tolerance of the spec is 10mm but has been extended for wall-to-column joints to 20mm (RFI - Cxxx-__-PTR-455). The plumb of the liftshaft that the blockwork has been built against was built out of tolerance causing the varying width against a plumb blockwork wall.
| 02SL - Stations (LUL) | Cxxx-NCR-001371 | NCR | IRF-LULO-582 - Court Street Formation Inspection |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2016-02-07 | 2016-01-15 15:58 | -23 | 2015-10-13 13:02 | Civil - Sub-base | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Procedure violation that may render permanent works item to be nonconforming. While carrying out IRF-LULO-582 - Court Street Formation Inspection, the following item was missing: 1. Signed check sheet 04 September 2015 09:00-09:30
| 02SL - Stations (LUL) | Cxxx-NCR-001372 | NCR | Procedure violation - IRF-LULO-572 - Court Street D.O.T Type 1 Placement |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2016-01-15 | 2016-01-15 15:59 | 0 | 2015-10-13 13:11 | Civil - Sub-base | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Procedure violation that may render permanent works item to be nonconforming. While carrying out IRF-LULO-572 - Court Street D.O.T Type 1 Placement Inspection, the following items were missing: 1. Signed check sheet 2. Evidence of material compliance. 27 August 2015 09:00-09:30
| 02SL - Stations (LUL) | Cxxx-NCR-001373 | NCR | HCDL Platform Paving -Incorrect Paving Laid |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-11-30 | 2015-11-29 11:37 | -1 | 2015-10-13 16:14 | Architectural - Flooring | 9510.98 |  | Material | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | Incorrect Paving slabs delivered to site by Manufacturer. Subcontractor laid the wrong slabs without checking the correct slab were delivered.
| 02SL - Stations (LUL) | Cxxx-NCR-001374 | NCR | TTH - Level A Partitions Deflection Head |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2018-05-31 | 2018-02-16 08:17 | -104 | 2015-10-15 10:30 | Architectural - Partitions | 3000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After receiving Cxxx-FCD-001102 (TTH Level A Partitions Deflection Head) CRL have observed that the head details have not been constructed as per the proposed detail. Please provide evidence from __ that will support the current wall configurations which will assist in closing out the change control.
| 02SL - Stations (LUL) | Cxxx-NCR-001376 | NCR | Use of non approved materials - PCC Cladding |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-02-01 | 2016-01-25 16:28 | -7 | 2015-10-16 07:42 | Architectural - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | PCC Cladding has been procured and installed in the TTH without an approved MCR. The MCR Cxxx-__M-C-LRC-D061_WS106-50168 is on eB as a placeholder only
| 02SL - Stations (LUL) | Cxxx-NCR-001377 | NCR | TTH - Works proceeding without an accepted ITP - Install of Switchboards |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-11-30 | 2015-11-09 16:05 | -21 | 2015-10-16 07:55 | Electrical - Switchgear | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The installation of the CEPS and Non CEPS Swicthboards and the OLBI have been completed without activities listed in the corresponding ITP Cxxx-__M-E-ITP-D061_WS106-50005 Rev. 4.0. The ITP details the assets in the MCR section and has FATs listed as activities but there are no activities for the initial SAT (on arrival to site), the installation or secondary SAT.
| 02SL - Stations (LUL) | Cxxx-NCR-001378 | NCR | Court Street Type 1 Installation- without approved MCR |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2016-01-15 | 2016-01-15 16:05 | 0 | 2015-10-16 10:20 | Civil - Sub-base | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | The type 1 on Court Street was installed without an approved MCR, as witnessed during IRF-LULO-627. The ITP lists MCR document number Cxxx-__M-C-LRC-D061_WS106-50151 which has no MCR attached to it. The site team were also unable to provide evidence from the supplier to confirm the material specification.
| 02SL - Stations (LUL) | Cxxx-NCR-001379 | NCR | No evidence of inspections prior to IRF - : IRF-LULO-626 – WSME RC Slab |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-11-30 | 2015-11-18 08:04 | -12 | 2015-10-16 11:12 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | IRF-LULO-626 – WSME RC Slab – ITP checksheets had not been completed prior to the IRF activity on site. __ could not demonstrate that an internal inspection had taken place as required by the Contractor Intervention ITP Hold Point.
| 02SL - Stations (LUL) | Cxxx-NCR-001380 | NCR | TTH - Roofing & Guttering - ITP does not contain activities for the entire scope of works |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-01-07 | 2016-01-07 19:49 | 0 | 2015-10-19 08:30 | Architectural - Roofing & Exterior Treatment | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | .Cxxx-__M-C-ITP-D061-50180 Rev 4.0 does not contain activities for the rain water pipe installation. IRF-LULO-606 was raised for RWP inspection, listing this ITP as the Quality control document
| 02SL - Stations (LUL) | Cxxx-NCR-001381 | NCR | TTH - Use of non approved materials - Rain Water Pipe Installation |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-02-04 | 2016-01-14 10:38 | -21 | 2015-10-19 09:20 | Architectural - Roofing & Exterior Treatment | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Cxxx-__M-C-ITP-D061-50180 Rev 4.0 lists 4 MCRs. During the document review as part of IRF-LULO-606, 3 of the 4 MCRs had not been submitted to CRL for acceptance. During the initial review of the nonconformance, it has been identified that the internal rainwater pipe installed is not on the LU APR and evidence has not been produced to confirm the product meets the fire performance requirements of the LU Standard LU1085. Kemperol 2K Put Waterproofing System Cxxx-__M-A-LRC-D061-50110 – Code 1 Aluminium rain water pipes Cxxx-__M-A-LRC-D061_WS106-50046 – This product has not been used. Zinc has been used and is covered under the main __ Zinc Cladding MCR - Cxxx-__M-A-LRC-D061-50003 Rev 2.0, Code 1 Internal rain water pipes Cxxx-__M-A-LRC-D061_WS106-50048 – not submitted. Product installed is __ SML Cast Iron Drainage, not LU approved. Pipe brackets Cxxx-__M-A-LRC-D061_WS106-50049 – brackets are included a part of the __ product system and do not require a separate MCR
| 02SL - Stations (LUL) | Cxxx-NCR-001382 | NCR | CMS Pull Out Testing |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2015-11-16 | 2015-11-05 16:39 | -11 | 2015-10-19 09:54 | Electrical - Cable Management | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | Concrete fixings have not been tested to the required standards specified within the ITP. Works Information Volume 2B – Part 20.8 “The Contractor…shall maintain ITPs appropriate for the services they provide that are accepted by the Supervisor. These accepted ITPs shall stipulate the necessary level and frequency of tests and inspections for each aspect of the works.” The pull out test specification as detailed within the CMS ITP (Cxxx-__M-E-ITP-D061_WS106-50002) specifies the need to test a random sample of 10% of the fixings to a pass criteria of 3.5kN (masonry) or 5kN (concrete). The test record (Cxxx-__M-E-ITP-D061_WS106-50002) states that the pull out test was passed to the ‘required loading’ of 3kN. This is below the required pass criteria detailed within the ITP. It is unclear whether a random sample of 10% of fixings was taken because the test frequency and locations are not stated within the provided documentation.
| 02SL - Stations (LUL) | Cxxx-NCR-001383 | NCR | DSS - Level 5-4 Walls and Columns - Concrete Cube test results missing |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-11-04 | 2015-11-04 11:52 | 0 | 2015-10-21 14:55 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | On the 9th and 11th of February 2015, 2 concrete pours occured, during the 2 pours concrete cube samples were taken, load docket number 617748 on the 9/02/15 and 617918 on the 11/02/15, as per concrete pour records attached. However the laboratory has no recolection of the cube tests and therefore there is no results showing that the concrete reach the design compressive strength after 56 days. The concrete used to pour the walls and columns these dates is C40/50 Line 31 from __ and the elements poured were: - 09/02/15 Columns C5-08, 10 & 13 and Wall W5-04S - 11/02/15 Columns C5-03, 04, 11 & 16 and Wall W5-02S
| 02SL - Stations (LUL) | Cxxx-NCR-001384 | NCR | LULO Steelwork - Phase 4 & 5 Lift Shaft Doorway Threaded Bolts |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-12-15 | 2015-11-02 15:15 | -43 | 2015-10-20 18:28 | Structural Engineering - Bolted Connections | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Insufficient quantity of material to do the job | Completed |  | The bolts for two connections between the lift shaft doorway (6549) and the South End truss (6530) were not on site. To prevent delay to the installation on the possession, 4 no. threaded bars M24 x 140mm Grade 8.8 were installed instead of 4 no. M24 x 110mm Grade 8.8 bofts in the connections (2 no.) of mark 6549 to mark 6530. Please refer to attachment Cxxx-JV00030-NCR-0031_rev01.pdf (__ NCR-0031.pdf is an old revision but cannot be removed)
| 02SL - Stations (LUL) | Cxxx-NCR-001386 | NCR | TTH - Works proceeding without an accepted ITP - Vinyl Floors Installation |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-12-05 | 2015-11-25 13:58 | -10 | 2015-10-21 20:01 | Architectural - Flooring | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient surveillance of subcontractors | Completed |  | Works have proceeded without an accepted ITP in place for the vinyl flooring
| 02SL - Stations (LUL) | Cxxx-NCR-001387 | NCR | TTH - Use of non approved materials - __ Safety Flooring |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-12-05 | 2015-11-29 09:53 | -6 | 2015-10-21 20:12 | Architectural - Flooring | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | __ Safety Flooring has been procured and installed in the TTH without an approved MCR. The MCR Cxxx-__M-A-LRC-D061_WS106-50179 Rev 1.0 was returned Code 3. Revision 2 has been submitted but has not been returned by CRL. It should be noted that the comments raised against the Rev 1.0 submission did not directly relate to the technical compliance of or performance of the material, th Code 3 status is not proportional to the comments raised
| 02SL - Stations (LUL) | Cxxx-NCR-001388 | NCR | TTH - Court Street - Use of non approved materials - Ultrascape Flowpoint |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-01-15 | 2016-01-14 17:06 | -1 | 2015-10-21 20:37 | Civil - Street Architecture | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | __ has been procured and installed in Court Street without an approved MCR. The ITP states __ is to be used.
| 02SL - Stations (LUL) | Cxxx-NCR-001389 | NCR | DSS - Level 5 Slab - D-wall couplers not connected |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-11-06 | 2015-11-03 12:22 | -3 | 2015-10-23 12:12 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 2 rows of couplers in the D-wall were installed at the same level resulting in 2Nos B32 re-bars, connecting the D-wall reinforcement with Level 5 slab, not being installed. On the attached mark-up drawing 50498, the 2 couplers marked "B" were left empty because the 2 bars installed in the couplers marked "A" were in front.
| 02SL - Stations (LUL) | Cxxx-NCR-001390 | NCR | DSS - C3-04 Alignment Alteration |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-11-06 | 2015-11-03 12:23 | -3 | 2015-10-23 15:19 | Shafts - Shafts General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Column 04 Level 3-1 is off the design alignment, please refer to attached survey drawings.
| 02SL - Stations (LUL) | Cxxx-NCR-001391 | NCR | WSME - Cladding - Works proceeding without approved FCD |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-12-06 | 2015-11-15 11:58 | -21 | 2015-10-23 14:52 | Fire - Compartmentation | 4000 |  | Documentation and Records | Repair | 3 (3-6k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | WSME cladding works: Works have proceeded before the FCD regarding the Fireboard/Blockwork detail was approved. FCD has now been raised Cxxx-FCD-001214.
| 02SL - Stations (LUL) | Cxxx-NCR-001392 | NCR | Works proceeding without an approved ITP - Pl 2 Trimmer Steel - Interim Station |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-12-11 | 2015-11-12 10:59 | -29 | 2015-10-27 11:01 | Civil - Structural Engineering | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | Works have proceeded without an approved ITP in place for the offsite fabrication on the platform 2 trimmer steel.
| 02SL - Stations (LUL) | Cxxx-NCR-001393 | NCR | Interim Station - Works proceeding without an approved Weld Procedure - Pl 2 Trimmer Steel |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-03-01 | 2016-02-18 15:14 | -12 | 2015-10-27 11:20 | Civil - Structural Engineering | 1000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Fabrication of the Platform 2 trimmer steel has been completed without a Code 1 Weld Procedure in place. The Code 3 comments are considered minor and do not affect the physical performance of the welds
| 02SL - Stations (LUL) | Cxxx-NCR-001394 | NCR | DSS - L1 Slab East Pour 2 Crack |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-08-10 | 2016-08-11 12:45 | 1 | 2015-10-27 12:26 | Shafts - Shafts General | 1500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Full depth crack in the north corner of L1 Slab East Pour 2, please refer to site photos for more details.
| 02SL - Stations (LUL) | Cxxx-NCR-001395 | NCR | LULO - Sub-subcontracting of works without prior acceptance by __ |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-12-12 | 2015-11-05 16:34 | -37 | 2015-10-28 15:08 | Civil - Structural Engineering | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Error by manufacturer in shipping or marking | Completed |  | __ have sub-sub contracted the painting for the permanent steelwork Central concourse, roof, upper lift shaft and stairs fabrication package. It should be noted that PTS undertook a surveillance of the paint process at the subcontractors facilities and found the work to be of a good standard and all applicable processes being followed. There is no perceived risks to the physical works. See Cxxx-__M-O4-RGN-D061_WS106-53002 for full Surveillance Report
| 02SL - Stations (LUL) | Cxxx-NCR-001396 | NCR | TTH – CMS Works to non-IFC drawings |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2015-11-17 | 2015-11-12 17:21 | -5 | 2015-11-03 08:03 | Electrical - Electrical Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | NCR has been raised for failure to install the CMS to the correct construction drawings (IFC). For details refer to surveillance report Cxxx-XRL-O4-RGN-CR001-50032.
| 02SL - Stations (LUL) | Cxxx-NCR-001397 | NCR | WSME - Clay pipe drainage above ground level |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-02-01 | 2016-01-28 23:03 | -4 | 2015-11-03 09:56 | Civil - Drainage | 4000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | In the WSME, the cast iron rain water pipe is connected to the below ground drainage clay pipe approx. 0.5m above concrete level. This is not in line with the specification. However, this downpipe is enclosed inside the WSME wall and the clay is not at risk of behing damaged, there are also no performance concerns, as discussed on site with __ (Crossrail). Use As-Is is in this case acceptable.
| 02SL - Stations (LUL) | Cxxx-NCR-001398 | NCR | Use of non approved materials - Mechanical Pipework, TTH |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-12-18 | 2015-11-18 10:50 | -30 | 2015-11-03 16:49 | Materials - Approval | 3000 |  | Material | Reject | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | __ have installed mechanical pipework in the TTH that is not the same as the material specified in the MCR referenced in the ITP Cxxx-__M-P-ITP-D061_WS106-50001 Rev. 3.0. The material installed does not meet the requirements of the LU Standard 1-085.
| 02SL - Stations (LUL) | Cxxx-NCR-001399 | NCR | Use of non approved materials - __ CFS- SL Fire Resistant Sleeve |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-01-01 | 2016-01-07 20:01 | 6 | 2015-11-03 21:08 | Materials - Approval | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | __ CFS- SL Fire Resistant Sleeve installed to accommodate the leakey feeder without an approved MCR.
| 02SL - Stations (LUL) | Cxxx-NCR-001400 | NCR | DSS - W1-10S Reduced Cover |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-02-01 | 2016-01-22 16:49 | -10 | 2015-11-05 13:50 | Shafts - Shafts General | 1500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During pre pour inspection it was noticed that both ends of the eastern face (shaft side) of the wall had less than the required cover. See attached plan and photos.
| 02SL - Stations (LUL) | Cxxx-NCR-001401 | NCR | TTH - Sanitary Ware Fixing Detail |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-02-11 | 2016-02-11 16:19 | 0 | 2015-11-06 13:23 | Mechanical - Public Health Engineering | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | TTH Male WC - Wash hand basin were found to be insufficiently fixed during an inspection. Further investigation found that the toggle fixing had not opened out to its correct final position. See attached picture which illustrates the fixing and the installation fault.
| 02SL - Stations (LUL) | Cxxx-NCR-001402 | NCR | DSS - W6-01NS Void |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-03-01 | 2016-01-22 16:46 | -39 | 2015-11-09 09:49 | Shafts - Shafts General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Void at the top of W6-01NS.
| 02SL - Stations (LUL) | Cxxx-NCR-001403 | NCR | Compliance Submission document update |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2016-02-16 | 2016-01-15 15:34 | -32 | 2015-11-09 13:55 | Communications and Control Systems | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Procedure Problem - Not Defined | Completed |  | NCR has been raised to ensure that the ‘Temporary Ticket Hall Compliance Submission’ doc. ref. no. Cxxx-__M-C-RGN-D061-50055 is updated to reflect the final London Underground’s decision on the installation of heat pump system that is non compliant with their standard 1-085. For details refer to surveillance report no. Cxxx-XRL-O4-RGN-CR001-50032
| 02SL - Stations (LUL) | Cxxx-NCR-001404 | NCR | Lack of commissioning schedule or programme |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2015-12-18 | 2015-11-28 12:54 | -20 | 2015-11-09 14:04 | Mechanical - Mechanical Engineering General | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | This NCR has been raised to ensure that the contractor will produce a commissioning programme with the appropriate works sequencing and estimated dates prior to the commissioning activities as required by WIv2B clause 28.1.7. since at present there is no commissioning programme. For further details refer to doc. ref. no. Cxxx-XRL-O4-RGN-CR001-50033
| 02SL - Stations (LUL) | Cxxx-NCR-001405 | NCR | Phase 4 & 5 Fabrication Error - Piece 6531 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-01-12 | 2015-12-21 16:47 | -22 | 2015-12-01 11:56 | Civil - Structural Engineering | 5000 |  | Manufacturing Defect | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Phase 4 & 5 Link beam [6531] Memeber connection of [6531] to secondary beam member [6508] was fabricated incorrectly. Connection is at site measure of 720mm offset towards the centre of the beam. (refer to sketch enclosed)
| 02SL - Stations (LUL) | Cxxx-NCR-001406 | NCR | TTH Door D2/10 - Threshold detail |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-01-14 | 2016-01-13 10:25 | -1 | 2015-11-12 18:17 | Architectural - Doors | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | This NCR follows up on Cxxx-NCR-001268. The 2 issues the Cxxx-NCR-001268 was raised for have now been resolved by replacing the TTH staircase level A grating. Cxxx-NCR-001268 can consequently be closed. However the replacement of the grating has impacted the door threshold. Also, Crossrail has expressed there disagreement against a 12mm threshold plate being fitted to an internal door (trip hazard). This NCR is consequently raised to capture the change of the door threshold detail.
| 02SL - Stations (LUL) | Cxxx-NCR-001407 | NCR | TTH - MEP - OLBI FAT Calibration Records |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-01-28 | 2016-01-28 13:12 | 0 | 2015-11-16 10:20 | Electrical - Power Distribution | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | During the OLBI FAT undertaken at __, 25 November 2014, calibration records for various test equipment were taken as part of the surveillance evidence. The Calibration Record for the elcometer used to measure the paint thickness of the cabinet could not be traced back to the calibration certificate offered.
| 02SL - Stations (LUL) | Cxxx-NCR-001408 | NCR | DSS Blockwork - Walls out of tolerance on Level 8 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-12-16 | 2015-12-01 11:41 | -15 | 2015-11-18 14:02 | Architectural - Brickworks/Blockworks | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Two structural blockwork walls have been found out of tolerance due to the incorrect setting out on Level 8 See location of walls attached
| 02SL - Stations (LUL) | Cxxx-NCR-001409 | NCR | As built position of Central Concourse Steelwork |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-12-03 | 2015-12-03 12:07 | 0 | 2015-11-19 12:03 | Civil - Structural Engineering | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | As-built position of the Phase 4 & 5 Steelworks of the central concourse over LO platforms 5 & 6 of Whitechapel station are noted to be out of tolerance. The deviation of the steelworks is beyond that stipulated within the NSSS 5th Edition sections 9.
| 02SL - Stations (LUL) | Cxxx-NCR-001410 | NCR | Platform 2 COMMs Migration CMS |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-02-07 | 2016-02-05 14:29 | -2 | 2015-11-20 19:57 | Communications and Control Systems - General | 9000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Other | Completed |  | On platform 2 existing lighting Column CMS route an IP65 2 compartment trunking has been installed for the PA/VA & CCTV systems. This trunking is for the COMMs migration and temporary safe route installation. This has been installed under the Electrical Safe Route CATII design, within this CAT II there is no specific assurance details for securing the trunking to the existing lighting column and no detailed showing the position of the CMS on a drawing.
| 02SL - Stations (LUL) | Cxxx-NCR-001411 | NCR | DSS - W1-05S (Lift Shaft 5) |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-04-28 | 2017-04-24 11:06 | -4 | 2015-12-03 11:36 | Shafts - Shafts General | 2500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Between the top pour of W3-05S and the bottom pour of W1-05S it was noticed that the finished internal wall location of W3-05S was not exactly were it should be. To make this correct in the pour of W1-05S the internal shutter was packed out to bring the lift shaft internal walls into the correct position. This is going to leave a noticeable join between the pours of W3-05S and W1-05S. See attached mark up showing the locations to be corrected.
| 02SL - Stations (LUL) | Cxxx-NCR-001412 | NCR | LULO Steelwork - Link Beam (6531) Fabrication Error |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-12-23 | 2015-12-21 16:46 | -2 | 2015-11-23 17:11 | Structural Engineering - Steel Member | 5000 |  | Manufacturing Defect | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | A connection plate between 6531 and 6508 and the stub on 6531 have been fabricated approximately 720mm out of position.
| 02SL - Stations (LUL) | Cxxx-NCR-001413 | NCR | TTH Level A Switchroom - Duct |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-02-01 | 2016-01-25 12:40 | -7 | 2015-11-25 12:20 | Architectural - Brickworks/Blockworks | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Further to Cxxx-FCD-001041 the Level A Switchroom internal walls have been changed to blockwork. The blockwork followed the line of the boxed steel column (GL 3/E) and therefore reduced the width of the louvre. The lintel above the top row of louvres was also installed too high meaning the structural opening was not 315x315 introducing a gap above the duct.
| 02SL - Stations (LUL) | Cxxx-NCR-001414 | NCR | LULO Steelwork - Roof 5 Connection Plate Fabrication |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-01-07 | 2016-01-04 09:23 | -3 | 2015-11-25 17:21 | Structural Engineering - Structural Engineering - General | 7500 |  | Manufacturing Defect | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The connection plate on Roof Assembly 5 (7324, 7326, 7418, 7299, 7346, 7300) to the East Virendeel is not aligned with the other Virendeel connection plate.
| 02SL - Stations (LUL) | Cxxx-NCR-001416 | NCR | WSS Precast Permanent Props Coupler Issue |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-01-14 | 2016-01-14 09:39 | 0 | 2015-11-26 13:08 | Structural Engineering - Concrete Member | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Precast props (2 no.) arriving on site from __ have been found to be fitted with incorrect __ couplers and with 10 (no.) of the 24 (no.) couplers fitter in the incorrect orientation. The incorrect couplers are EL20S13-M22 as opposed to EL20S13 as specified in the drawings meaning M22 bolts are required for the connection as opposed to M24. With regards to the incorrectly orientated couplers they are located as follows: Prop 1 - 6 at one end, 2 at other end, Prop 2 - 1 at each end.
| 02SL - Stations (LUL) | Cxxx-NCR-001418 | NCR | Western HCDL RC Slabs |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-01-13 | 2015-12-07 13:11 | -37 | 2015-11-26 15:32 | Civil - Civil Engineering General | 1000 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | Prior to pouring the last plaform slab for the iterim station it was noted that some of the DPM following throught from the adjacent slabs has been damaged/missing. Where this was the case we were not able to achieve our 150mm continuation lap through to the new slab. please see highlighted drawing of the missing DPM lap.
| 02SL - Stations (LUL) | Cxxx-NCR-001419 | NCR | TTH - Concourse Lighting |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-05-31 | 2016-06-28 11:05 | 28 | 2015-11-26 14:58 | Electrical - Lighting | 3000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | TTH Concourse Lighting has been installed surface as opposed to recessed as per the original design.
| 02SL - Stations (LUL) | Cxxx-NCR-001420 | NCR | Cold Weather Concrete - LO Concourse |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-02-01 | 2016-01-29 10:05 | -3 | 2015-11-26 16:32 | Structural Engineering - Concrete Member | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | On the week 35 possession, the LO concourse deck was poured at GL7-9 & GL17-HCDL. Frost blanket was not placed to the finished concrete surface prior to handback. The decision was made to not place the frost blanket as the concrete was not set enough such that walking on it may have damaged the surface finish. This is in contradiction of the agreed/approved cold weather concreting procedure.
| 02SL - Stations (LUL) | Cxxx-NCR-001421 | NCR | Western HCDL Platfrom 1 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-02-01 | 2016-01-20 12:11 | -12 | 2015-11-26 17:35 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The lid on LDP2 (Platform 1) was set in the wrong orientation. This will need lifting and turning around so that the lids within the frame run east to west rather than north to south.
| 02SL - Stations (LUL) | Cxxx-NCR-001422 | NCR | LULO Steelwork - Roof Beam (7289) Fit |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-01-26 | 2015-12-21 16:49 | -36 | 2015-11-27 18:07 | Structural Engineering - Structural Engineering - General | 1000 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The Roof Beam (7289) on the East side between GL 11 & 12 was installed however due to a tight fit only two bolts (out of 8) could be installed with the connection to the GL 12 column (7337) and three bolts (out of 4) in the connection with the stub on the vierendeel. An MDC was produced during the possession and the beam was stable with the number of bolts installed.
| 02SL - Stations (LUL) | Cxxx-NCR-001423 | NCR | LULO Steelwork - Roof Beam (7286) Fit |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-02-21 | 2016-02-21 15:43 | 0 | 2015-11-27 18:13 | Structural Engineering - Steel Member | 10000 |  | Manufacturing Defect | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | The roof beam (7286) on the East side between GL 13 & 14 did not fit and was not installed.
| 02SL - Stations (LUL) | Cxxx-NCR-001424 | NCR | LULO Steelwork - Link Beam (6532) End Plates |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-02-25 | 2016-02-18 17:48 | -7 | 2015-11-27 18:32 | Structural Engineering - Steel Member | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The West link beam (6532) has a gap large than specified in the NSSS at each end of the beam between the connection plates and 2 number threaded bolts in the North end (connected to the vierendeel) are too long.
| 02SL - Stations (LUL) | Cxxx-NCR-001425 | NCR | LULO Steelwork - GL 18 West Walkway Connection Plate |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-02-25 | 2016-02-21 16:06 | -4 | 2015-11-27 18:59 | Structural Engineering - Bolted Connections | 1000 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The connection plates between the West walkway and the West vierendeel have a gap larger than the tolerence in the NSSS.
| 02SL - Stations (LUL) | Cxxx-NCR-001426 | NCR | LULO Steelwork - Roof Columns Threaded Bolt |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-02-25 | 2015-12-21 16:50 | -66 | 2015-11-27 19:25 | Structural Engineering - Bolted Connections | 500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | One bolt (out of 6) could not be installed in the threaded hole of the connection between the top flange of the top chord of Vierendeel West and the roof columns marks 7273, 7272, 7333, 7332 & 7331 (row 10, 11, 13, 14 & 15 respectively).
| 02SL - Stations (LUL) | Cxxx-NCR-001428 | NCR | Lack of fit of pre-assembled Roof 5 (Mark 7324 & 7326) |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-07-27 | 2018-07-16 08:00 | -11 | 2018-04-25 14:17 | Structural Engineering - Steel Member | 3000 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Clash of endplate of Mark 7324 with the connection plate welded to Vierendeel Girder East prevents installation of pre-assembled Roof 5.
| 02SL - Stations (LUL) | Cxxx-NCR-001429 | NCR | CHS - Level B Wall 11 to Wall 15 connection |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-01-22 | 2016-01-14 16:28 | -8 | 2015-12-04 09:40 | Shafts - Shafts General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Due to damage to the P13 couplers cast into WB-15s for the connection to WB-11s pour 2 15no couplers are unusuable. As per conversation between Cxxx and __ replacement bars will be drill a fixed. A 16mm hole will be drilled 100mm from the edge of wall 15 to a depth of 250mm. B12 bars will be fixed in with __ Hit 200.
| 02SL - Stations (LUL) | Cxxx-NCR-001430 | NCR | TTH-WSME Lightening Tape-Roofing Interface |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-02-01 | 2016-01-28 23:22 | -4 | 2015-12-10 12:08 | Architectural - Roofing & Exterior Treatment | 1000 |  | System Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Due to the sequence of construction and the requirement for the lightening tape to run external across the roof and tapping on to the structural steel columns as down conductors, it meant that the tape had to penetrate the buildings weather membrane. This requirement was apparent on the TTH and WSME roof. The MEP drawings did not provide detail for how these penetrations are sealed as the line arbitrarily passes through the building envelope. __ confirmed with the cladding sub-contractor and the relevant manufacturers that penetration details through various membranes were typical and could be applied. The installation has subsequently been completed on site, and the lightening tape and roofing have both passed the relevant test for conductivity as per the approved ITP. __ have endorsed the lightening tape route and connection details, this is captured in the electrical construction package.
| 02SL - Stations (LUL) | Cxxx-NCR-001431 | NCR | W177 Heritage Brickwork |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2021-07-08 19:47 | 373 | 2015-12-10 13:56 | Architectural - Brickworks/Blockworks | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Further to LULO_743-W177 Brickwork inspection, the following non-conformance is to be recorded. Wall W177 had a section demolished to facilitate the TTH/WSME construction, the demolition was to the nearest pier to ensure the wall was structurally stable, consequently there are two infill’s east and west to be reinstated. The east received a temporary wind post and panel infill, the west had to be brickwork to facilitate the riser cabinet servicing the platforms. The history of this is recorded in Cxxx-FCD-001115, Cxxx_RFI_002201, Cxxx_RFI_002618, Cxxx_RFI_002879. It was critical to install the west infill wall/cabinet to facilitate mechanical works and the interim station programme. Due to access issues, the wall construction was possession critical. Materials, detail and methodology was lacking before the reconstruction due to late consultation with heritage architects. The wall was reconstructed using existing bricks from the east London line bridge demolition, the mortar used was hydraulic lime (data sheet attached). Following an inspection with __ heritage architects the workmanship and appearance of the wall was rejected due to the following; incorrect brick bond, mortar joints, corbelling, cracking, incorrect material, concern with mortar, line, level and general appearance from a heritage point of view.
| 02SL - Stations (LUL) | Cxxx-NCR-001433 | NCR | Use of non approved materials - __floor 155 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-01-28 | 2016-01-15 15:56 | -13 | 2015-12-14 10:10 | Materials - Approval | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | __floor 155 has been used on site without n approved MCR in place
| 02SL - Stations (LUL) | Cxxx-NCR-001434 | NCR | Use of non approved materials - Court Street Urban Realm - Bagged Site Mix Concrete |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-07-15 | 2016-07-15 10:44 | 0 | 2015-12-14 10:19 | Materials - Approval | 1000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Bags of site mixed 40kN concrete was used for the Court Bridge southern ramps. There is no MCR that covers the material to be used in this area
| 02SL - Stations (LUL) | Cxxx-NCR-001435 | NCR | Use of non approved materials - Court Street Urban Realm - __lastic Waterproofing System |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-01-28 | 2016-01-15 15:57 | -13 | 2015-12-14 10:29 | Materials - Approval | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Works requiring the use of __ Waterproofing System Court Street Bridge proceeded without an approved MCR in place. The MCR is currently at Code 3.
| 02SL - Stations (LUL) | Cxxx-NCR-001436 | NCR | Use of non approved materials - TTH - Durastreel Access Hatch |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-03-31 | 2016-02-25 15:37 | -35 | 2015-12-14 10:40 | Materials - Approval | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | __ Access Hatch has been installed to the north face of the WSME, without an approved MCR. The hatch gives access to the underside of the WSME.
| 02SL - Stations (LUL) | Cxxx-NCR-001437 | NCR | Use of non approved materials - TTH / W177- __ Lime Mortar |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-10-28 | 2016-09-21 16:53 | -37 | 2015-12-14 10:45 | Materials - Approval | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | __Lime Mortar has been used on W177 without an approved MCR.
| 02SL - Stations (LUL) | Cxxx-NCR-001438 | NCR | TTH - Nominated ITP not covering the works being undertaken - Collapsible Gate |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-01-28 | 2016-01-20 08:06 | -8 | 2015-12-14 10:59 | Architectural - Doors | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Cxxx-__M-C-ITP-D061-50183 Rev 2.0 did not have an activity identified specifically for the installation of the Gate Housing
| 02SL - Stations (LUL) | Cxxx-NCR-001439 | NCR | TTH SSO Windows – East window |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-01-28 | 2016-01-29 07:56 | 1 | 2015-12-14 16:53 | Architectural - Glazing | 15000 |  | Damaged | Use As-Is | 2 (6-60k) | Complete | Material/Preservation Problems - Insufficient quantity of material to do the job | Completed |  | During the installation of the SSO windows on the SSO Room, the west window was successfully fitted, whereas the east window cracked when the last screw was being fitted to secure the window. Apparently the middle of the glass was protruding 1 or 2mm and caught on a screw which caused the glass to shatter. CRL also raised their concern with regards to the insufficient expansion gap around the SSO window. This gap permits the window to expand in a fire situation. __ is to confirm if the expansion gap is enough to accommodate the expansion of the window in the event of a fire.
| 02SL - Stations (LUL) | Cxxx-NCR-001440 | NCR | TTH SSO Windows – West window |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-01-28 | 2016-01-20 08:18 | -8 | 2015-12-14 17:05 | Architectural - Glazing | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Insufficient quantity of material to do the job | Completed |  | The SSO west window cracked when the capping trim was being fitted. The trim has to be forced on due to the screws at the top of the head. The defective window (with the blemish around) was refitted and an assessment will be done by the window manufacture to assess if the blemish affects the integrity of the window and if it needs to be replaced or not. CRL also raised their concern with regards to the insufficient expansion gap around the SSO window. This gap permits the window to expand in a fire situation. __ is to confirm if the expansion gap is enough to accommodate the expansion of the window in the event of a fire.
| 02SL - Stations (LUL) | Cxxx-NCR-001441 | NCR | __ on TTH/WSME junctions GL5 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-11-14 | 2016-10-01 13:11 | -44 | 2015-12-14 17:11 | Fire - Compartmentation | 4789 |  | Material | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | The __ (compressible material) installed on TTH/WSME junctions is not approved on the LU APR. The __ was not removed from the junctions. As an alternative solution the junctions were encapsulated within a 60min compartment as shown in __ sketch below. The strips cannot be removed due to access restrictions on GL 5. Removal from the inside was not carried out as this would have left an exposed gap to the railway.
| 02SL - Stations (LUL) | Cxxx-NCR-001442 | NCR | WSME Cladding - Change to KME/Zinc interface detail |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-02-15 | 2016-02-10 09:03 | -5 | 2015-12-15 02:39 | Architectural - Roofing & Exterior Treatment | 2000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Cxxx-__M-C-DWG-D061-50375 WSME Cladding Zinc / KME interface detail shows an aluminium flashing. This was changed on site to a zinc flashing, as built drawing is attached.
| 02SL - Stations (LUL) | Cxxx-NCR-001443 | NCR | Non Issue of IRFs - Week 35 Possession |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-02-13 | 2016-02-02 09:22 | -11 | 2015-12-15 07:17 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | IRF’s not sent to CRL during the possession for the following activities CSB- Installation of mesh panels CSB- paving in front of SME (this included excavation down to formation level and backfill with CBM) ESS- fixing of panels to landing ESS- paving LULO- concreting of concourse
| 02SL - Stations (LUL) | Cxxx-NCR-001444 | NCR | Non Issue of IRFs - Week 37 Possession |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-02-13 | 2016-02-02 09:24 | -11 | 2015-12-15 07:20 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | IRF’s not sent to CRL during the possession for the following activities Area 1 Remedial Works Inspection of painting to beams Metal decking Area 4 & 5 Link beam installation Stair installation Upper lift shaft Roof steel Metal decking of link beams East Stair Shaft Installation of new emergency escape onto platform 6 (who will sign this into use from __?) HCDL Platform 1 paving TTH External cladding & bird wire
| 02SL - Stations (LUL) | Cxxx-NCR-001445 | NCR | Storgae of Concrete Cubes in the GSM |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-01-29 | 2016-01-28 13:14 | -1 | 2015-12-15 07:30 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Insufficient controls have been applied to the storage of concrete cubes in the GSM area. The following was noted. 1. None of the cubes present were correctly marked to identify 7 day, 14 day, 28 day or spare. 2. Several of the cubes being stored were blank 3. There was a curing tank present but none of the cubes were being stored inside it. 4. 2 of the cubes stored were marked '20.10.15 Area 1'. These had already exceeded the 28 day testing period.
| 02SL - Stations (LUL) | Cxxx-NCR-001446 | NCR | WSME entrance from Platform Level – Door reveal |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-04-15 | 2016-04-15 16:44 | 0 | 2016-01-20 13:41 | Architectural - Doors | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The external door flashing (door reveal) on the main entrance door of the WSME is detailed for the permanent case with doors D2-20, D2-21. These doors are not installed until the permanent station opens and the WSME becomes an escape stair. The design drawings Cxxx-__M-C-DWG-D061-50457, 50396 have been superseeded by the attached sketch for the interim station. This change will be recorded and included in the redline drawings and re-addressed in the permanent case when the doors are installed.
| 02SL - Stations (LUL) | Cxxx-NCR-001447 | NCR | Pull off adhesion testing procedure not followed on Court St bridge |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-12-29 | 2016-01-06 17:23 | 8 | 2015-12-15 09:30 | Structural Engineering - Testing | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not qualified | Completed |  | As per __floor -155 WN MDS the concrete substrate the material is applied to needs to have a tensile strength of 1.5N/mm2. A pull of adhesion test determines the tensile strength of the concrete substrate to confirm sikafloor -155 WN can be applied. The pull off adhesion tests carried out recorded values of 1.0 meaning they failed, however upon discussions with the waterproofing subcontractor they advise they were confident in the concrete substrate to continue applying the __floor -155 WN. Upon further discussions with __ they advised that the minimum value of the pull off adhesion tests is 1.0N/mm2. Further pull off tests were carried out on the concrete substrate as well as the primed surface with all values exceeding 2.9KN which is a pass.
| 02SL - Stations (LUL) | Cxxx-NCR-001448 | NCR | Misaligned lateral joints on Court St south paving |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2015-12-29 | 2016-01-06 17:26 | 8 | 2015-12-15 11:15 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As per specification Cxxx-__M-C-RSP-D061-50006 paving setts need to be installed to ensure the pattern is consistent through all lateral and longitudinal joints (every second row must line up with each other). The specification also stipulates that the joints between paving setts is 10-12mm on all sides of the setts. Due to irregularities in the sizes of the paving setts supplied (difference in lengths, widths, thickness of up to 5mm) as well as the minimal tolerance in joint widths areas of laid setts do not have consistent lateral lines. This is compounded the further down a paving run the setts are laid. This has meant some lateral joints are out to approx 20mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001449 | NCR | Area 4 & 5 Metal Decking |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-01-26 | 2016-01-12 08:33 | -14 | 2015-12-15 16:59 | Structural Engineering - Concrete Member | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | With reference to Cxxx-__M-C-DWG-D061_WS106-50437 'Metal Deck floor layout + details', at Grid Lines 19 & H - Z', the metal decking sections 1630 and 736 were not installed due to a site-fit issue stemming from the inability to fix the initial metal deck section (easternmost) as per the design detail.
| 02SL - Stations (LUL) | Cxxx-NCR-001450 | NCR | Court St Bridge - Testing on concrete substrate by non UKAS accredited personnel |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-09-28 | 2019-02-07 09:26 | 132 | 2018-04-06 12:08 | Civil - Civil Engineering General | 1000 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As per design Court St Bridge was to have a DPM applied to the concrete deck, to protect the structural steel underneath from water ingress. The process before the Primer/DPM was applied required pull out tests on the concrete substrate to be carried out. The pull out tests were carried out by __ who were trained in the equipment (Hydrajaws 2000) however they are not UKAS accredited.
| 02SL - Stations (LUL) | Cxxx-NCR-001452 | NCR | ESS temporary handrial support fixings on mid landing |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-03-01 | 2016-01-27 14:50 | -34 | 2015-12-18 15:22 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 4no hilti HST stud anchors installed to support the temporary handrail connections around the midlanding were found to be improperly installed. 3no anchors were not fully tightened while 1no anchor did not have a minimum of 3 threads protruding.
| 02SL - Stations (LUL) | Cxxx-NCR-001453 | NCR | DSS Blockwork - Level 4 Mezz Blockwork Quality |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-04-13 | 2016-02-19 12:09 | -54 | 2016-01-04 12:36 | Architectural - Brickworks/Blockworks | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Quality of blockwork generally of a poor standard, with the following points noted: - Inconsistency in mortar joint thickness. Upper two mortar joints are thicker than the joints below despite the top course block cut down in height. - Top block course installed proud of the block work beneath to the front face and top of wall - Bed course cambers inward from the external face
| 02SL - Stations (LUL) | Cxxx-NCR-001454 | NCR | E51 Flooring - Adjacent Floor Panels Differnt Lengths |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-02-24 | 2016-01-29 08:25 | -26 | 2016-01-07 12:26 | Architectural - Flooring | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Counterfeit Items | Completed |  | There is a 10mm difference in floor panel lengths between the two floor panels that sit East of the switchboards. The panels match up at the kickplate on the East but are short on the West (next to the panel). Please see attached PDF.
| 02SL - Stations (LUL) | Cxxx-NCR-001455 | NCR | E51 - Interim Station Lighting Lux Levels |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-06-30 | 2016-06-30 16:40 | 0 | 2016-01-08 18:05 | Electrical - Lighting | 2000 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | E51 lux levels have been taken and reviewed (see attached mark up site readings sheet) and completed LUX Level sheets. The levels expected by the DIALux have not met the required levels (the DIALux design plan 277901 has been attached for information). It should be noted that as part of the interim station the permanent luminaires cannot be installed due to no OLBI (emergency) supply not being available.
| 02SL - Stations (LUL) | Cxxx-NCR-001456 | NCR | West Lift Lobby Lift Pit Walls (Lift 5) Reduced Width |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-02-22 | 2016-02-02 10:06 | -20 | 2016-01-08 15:55 | Civil - Structural Engineering | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Personnel Error - Inattention to detail | Completed |  | The setting out of the concrete back blinding for the West Lift Lobby Lift 5 Pit hasn't been properly executed, resulting in the area being too small to fit the full width of the pit as designed. In order to maintain enough space in the pit to fit the lift's mechanical elements as well as to maintain the location of the face of the lift pit walls that are linked to the structural steelwork of the concourse at higher level, the width of the Southern and Eastern walls of the lift have to be reduced in width by 120mm, bringing them from a design width of 400mm to a width of 280mm. This allows to maintain the setting out of the internal and external faces of the Lift 5 Shaft as per original intent.
| 02SL - Stations (LUL) | Cxxx-NCR-001457 | NCR | WSME Stair Remedials |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-04-17 | 2016-03-04 12:04 | -44 | 2016-01-08 18:28 | Architectural - Flooring | 3500 |  | Workmanship | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The WSME remedial works to level the stair treads and achieve a consistent 170mm rise were not within tolerance
| 02SL - Stations (LUL) | Cxxx-NCR-001458 | NCR | TTH - Interim Station Lighting Lux Levels |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-06-30 | 2016-06-30 07:36 | 0 | 2016-01-08 19:46 | Electrical - Lighting | 3000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | TTH lux levels have been taken and reviewed (see attached mark up site readings sheet) and completed LUX Level sheets (3 of). The areas that require attention are marked up on the attached file ‘__ Proposal for upgrade of TTH lighting’ these areas are: - Front of non paid concourse Level 1 - Back of CER Level 1 - Back of the store Level 1 - Front of CER/Store corridor Level 1 - External stair case level 1 & Level A - Male locker room Level A - External plant area Level A The levels expected by the DIALux have not met the required levels as per the approved design.
| 02SL - Stations (LUL) | Cxxx-NCR-001459 | NCR | TTH - Lighting within rooms that require a secondary supply |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-12-30 | 2016-11-16 13:06 | -44 | 2016-01-27 16:25 | Electrical - Lighting | 50000 |  | Design | Repair | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Within the TTH certain room (listed below) luminaires have only been supplied with 1 light and/or 1 circuit from the DNO/OLBI supply. A power loss to the DNO will result in no lighting available within certain room and therefore a risk to station staff safety. This is because the OLBI will only be brought online if there is a loss of power to the LU and DNO supply simultaneously.
| 02SL - Stations (LUL) | Cxxx-NCR-001460 | NCR | TTH - Mechanical Installation Pull Test Requirements |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-10-31 | 2016-09-28 11:50 | -33 | 2016-01-11 15:17 | Mechanical - Heating Ventilation & Air Conditioning | 2000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Following a review of the certification records for the TTH Mechanical works it was found there were insufficient pull test records to meet the 10% minimum requirement of the controlling ITPs. Pull tests were only found for the MPIP (Cxxx-__M-M-ITP-D061_WS106-50003) and Public Health (Cxxx-__M-P-ITP-D061_WS106-50001) works.
| 02SL - Stations (LUL) | Cxxx-NCR-001461 | NCR | Construction to P Rev Drawings - Cast in Earthing and Bonding |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-12-10 | 2016-11-04 09:20 | -36 | 2016-01-12 21:47 | Electrical - Electrical Engineering General | 2000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | Cast in earthing for CHS and DSS were constructed to P rev drawings, not Crev as is required. The drawings in question are Cxxx-__M-E-DDA-D061_WS105_8-30015 & 30016 and Cxxx-__M-E-DDD-D061_WS107_8-30015 & 30016
| 02SL - Stations (LUL) | Cxxx-NCR-001462 | NCR | CHS - Cover to starter bars cast in CHS capping beam |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-02-28 | 2016-01-28 11:24 | -31 | 2016-01-14 11:09 | Shafts - Shafts General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Previous Construction - Interfacing issues | Completed |  | CHS - Cover to the starter bars that were cast in the capping beam by contractors who completed works prior to __ on Cxxx. See attached image for details. 1) 2no B16 starter bars have 30mm cover 2) 1no B16 starter bar has 40mm cover 3) 1no B16 starter bar has 10mm cover 4) the back face of the raidius wall has 120mm cover. __ propose to: 1) cut off at kicker level bars with 30mm cover and make good 2) Use bar with 40mm cover, cover will be 40mm at the kicker level and bar will be bent back to have 50mm cover as wall continues up. 3) Cut off at kicker level bar with 10mm cover and make good 4) use bars with 120mm cover
| 02SL - Stations (LUL) | Cxxx-NCR-001463 | NCR | TTH - Additional Speakers Required SSO and BOH |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-04-15 | 2016-04-12 14:45 | -3 | 2016-01-15 17:08 | Communications and Control Systems - Public Address Systems | 4000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The TTH design did not include speakers in the following locations: - Station Supervisors Office (Level 1) - Bin Stores (Level 1) - Bin Stores (marked up on drawing as lobby) (Level 1) Areas identified on hand marked Sound Presure Level testing drawing attached
| 02SL - Stations (LUL) | Cxxx-NCR-001464 | NCR | CHS - Couplers in C1-07 for W1-23 with low cover |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-02-12 | 2016-02-02 10:01 | -10 | 2016-01-15 15:07 | Shafts - Shafts General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Couplers cast into column C1-07 for W1-23 connection are outside of the cover zone. See attached photo. 21no couplers are unusable due to having 20-30mm cover. __ propose to drill and fix replacement B12 bars. A 16mm hole will be drilled 150mm deep and a B12 bar cast into the column with __ Hit HY200 to replace each coupler.
| 02SL - Stations (LUL) | Cxxx-NCR-001465 | NCR | CHS - Edge of C2 slab |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-10-01 | 2016-10-01 13:33 | 0 | 2016-01-25 11:01 | Shafts - Shafts General | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | CHS - The edge of C2 slab is out of position. The eastern edge of the C2 slab is 29mm out of position in an isolated area. Attached is an asbuilt survey of the eastern edge of the C2 slab. The slab is surveyed at the top of Wall WB-11(RL 128.400), at the C2 pour 1 level (RL 129.000) and at the C2 pour 2 level (RL129.500). From the as built survey it can be seen that: - The position of the top of WB-11 is within 4mm of design. - The position of C2 slab pour 1 is within 16mm of design - the position of C2 slab pour 2 is within 29mm of design The positional changes are steps in the concrete, see attached photos. __ propose to scabble/ break back the lips in the concrete and make good as per the CHS RC Making Good Procedure
| 02SL - Stations (LUL) | Cxxx-NCR-001466 | NCR | stairs 23 nosing |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-03-02 | 2016-01-29 18:13 | -33 | 2016-01-19 13:11 | Architectural - Flooring | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | As showing on Drawing Cxxx-__M-A-DDD-D061_WS106_z-10520 C01 detail 3 and 4 precast concrete treads and HDLT nosing are bedded into reinforced concrete on-site or the whole units are to be cast off-site with 35mm paves inset. As previously confirmed 35mm paves cannot be used and 50mm paves as an alternative are being utilised. It is not possible to construct this detail on-site in prefabbed condition or in-situ and the 50mm paver eliminates the possibility of utilising this detail. As an alternative please see attached detail TRI-7179-00001_P02. Precast nosings reduce in size to allow for 50mm paves and risers was placed on-site.
| 02SL - Stations (LUL) | Cxxx-NCR-001467 | NCR | Court St - Staircase contrasting nosing strips |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-09-01 | 2016-09-01 16:49 | 0 | 2016-01-20 08:20 | Civil - Streets & Highways | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As per drawing Cxxx-__M-A-DDD-D061_WS106_1-14030 detail 4, the granite risers are to have a contrasting nosing strip on the front edge. This nosing strip is shown to start on step 1 and finish on step 10. It also shows the very bottom step at ground level to have no contrasting strip at all. The bottom step (ground level) has been installed with a contrasting nosing strip on the front edge which runs along the edge of the corduroy pavers.
| 02SL - Stations (LUL) | Cxxx-NCR-001468 | NCR | TTH Internal PPC Cladding |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-08-07 | 2016-07-29 14:28 | -9 | 2016-01-21 11:10 | Architectural - Walls | 875 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Following procurement, design and fabrication issues with the PPC internal cladding to the TTH and WSME, the interim station has been opened to the public with a number of temporary installation to facilitate the time to produce the necessary replacements. These include: 1. Door D1/16 – Replace panel above door. Edge between panel and door frame to be sealed with a grey mastic (LU approved). Door Head reveal panel to be lowered to finish to top of door frame (as per all other doors). 2. POM – Replace all cladding infill’s between the POM machines and along the top of the POM machine and bottom panel covering column with a stainless steel channel to be flush all round. There will be a requirement to step the s/s channel from approx. 300mm to f.f.l. 3. Door D1/13 –Stainless steel trim missing. 4. Skirting between Door 1/12 and Door 1/13 – missing 5. Door D1/10 Key pad has been relocated – install a stainless steel finger plate with rounded corners to cover extended cut out underneath the key pad. 6. Replace skirting on corner adjacent to D1/09 7. WSME/TTH Movement Joint – movement plate to be installed behind panel (to both walls). 8. 2 panels with 4 no. handrail roses holes to be replaced in WSME 9. Skirting to Service Duct in corner of WSME to be replaced and facing angle panel to be replaced. 10. Skirting on corner of corridor is set proud of cladding panels – reconfigure angle of skirting 11. Cladding panel located behind the gate line is protruding further out than all other panels – remove and adjust and refit. 12. Door D1/05 – double panel above door to be replaced with single panel to match all panels above doors. 13. Infill strips to be replaced as a result of damages, bent, paint removed by plier/mould grips. 14. Large panel above door D1/04 to be replaced
| 02SL - Stations (LUL) | Cxxx-NCR-001470 | NCR | HCDL Platforms Installation of platform end barriers with no approved material compliance record in place. |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-03-03 | 2016-01-27 16:15 | -36 | 2016-01-20 14:27 | Architectural - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Procedural NCR- Bespoke platform end barriers were installed on the HCDL platforms without an approved material complience record in place. This was
| 02SL - Stations (LUL) | Cxxx-NCR-001471 | NCR | TTH Location of Fire Extinguishers / Fire Point Signs on Concourse and Level A |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-04-30 | 2016-05-25 17:11 | 25 | 2016-01-20 14:30 | Architectural - Signage | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Due to space constrains and clashes with conduits / assets within the TTH rooms, 6no. Fire Extinguishers / Fire Point Signs were relocated to the nearest wall on the room. The aforementioned relocated Fire Extinguishers and Fire Point Signs are installed on: - OLBI Room - LU Switchroom - DNO Switchroom - POM’s Ticket Office - Bin Store - SCR Room Please see attached marked up drawing for clarification of the final location of all (14no.) Fire Extinguishers and Fire Point Signs on TTH Concourse and Level A.
| 02SL - Stations (LUL) | Cxxx-NCR-001472 | NCR | TTH POMs room infill between ticket machines |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-09-30 | 2016-09-26 08:31 | -4 | 2016-01-21 09:34 | Architectural - Walls | 4000 |  | Design | Use As-Is | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | There are gaps between the ticket machines installed by __. To achieve station opening, these were temporarily covered using site cut support mullions, fire board, stainless steel and mastic. The internal elevation of the ticket machines has similar gaps which again require filling to prevent maintenance issues. A permanent detail and solution is required. Please see attached drawings and comments. There are issues regarding structural support due to congestion between architectural and MEP elements. The head and bottom restraint are obstructed largely by service routes. Due to the quantity of CMS within the ceiling, the soffit is not readily available for fixing, unless the CMS/ceiling unistrut was utilised? There is also insufficient working room between adjacent machines (75-80mm). Clearly any partition will impact the existing MEP/ceiling arrangement, including lighting design. Further consideration is required and to be coordinated between disciplines. The permanent detail will be finalised and issued to CRL through the FCD system prior to installation to ensure LU operatives accept the solution.
| 02SL - Stations (LUL) | Cxxx-NCR-001473 | NCR | TTH concourse Insulation |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-05-13 | 2016-05-13 14:15 | 0 | 2016-01-21 09:44 | Architectural - Walls | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | There is insulation missing to the internal cladding in the TTH concourse, the location of this is on Grid Line 3, specifically to the elevation of the SSO. The insulation was previously installed and completed, however this has been damaged by others, as MEP have required various penetration drilling through the SSO blockwork. To complete this the internal cladding panels have been removed and the insulation damaged/not replaced as required.
| 02SL - Stations (LUL) | Cxxx-NCR-001474 | NCR | HCDL Platform Paving out of tolerance - Platform 2 South wall of WSME. |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-12-04 | 2018-07-12 13:42 | 220 | 2016-01-26 10:15 | Architectural - Flooring | 5500 |  | Workmanship | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During possesion weekend of 16 and 17 Jan 2016, paving was required to infill areas previously taken up by platform hoarding and columns. Paving was laid in accordance with the ITP and checked by __ engineer. Several days later it was noticed that the recently laid pavers have lifted and caused cracking in the grout joints.
| 02SL - Stations (LUL) | Cxxx-NCR-001475 | NCR | HCDL Platform 1 paving against western de train ramp not installed in accordance with design drawings. |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-09-30 | 2016-09-06 16:09 | -24 | 2016-01-26 15:27 | Architectural - Flooring | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | As per Detail 7 on Cxxx-__M-A-DDD-D061_WS106_Z-19050, there was a requirement for a 150x100 retaining angle to be installed at the interface of the platform paving and the existing concrete detraining ramp on platform 1. Once temporary concrete was broken out in this area during the possesion of 16 and 17 Jan 2016, it was apparent it was not possible to install this plate as there were too many undulations on the surface. Please see attached reponse from __.
| 02SL - Stations (LUL) | Cxxx-NCR-001476 | NCR | TTH Level A - Ceiling Level |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-02-18 | 2016-02-03 09:38 | -15 | 2016-01-21 12:37 | Architectural - Ceilings & Soffits | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Record of ceiling level change to Level A rooms south of corridor, as agreed between __, __, CRL/CEG
| 02SL - Stations (LUL) | Cxxx-NCR-001477 | NCR | TTH POM Ceiling Level |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-02-18 | 2016-02-03 09:46 | -15 | 2016-01-21 13:02 | Architectural - Ceilings & Soffits | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | POM ceiling level changed to accomodate M+E, see RFI to __ attached - agreed on site
| 02SL - Stations (LUL) | Cxxx-NCR-001478 | NCR | TTH - Use of non approved materials - Collapsible Gate |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-05-31 | 2016-05-16 16:28 | -745 | 2016-01-22 14:06 | Architectural - Doors | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Further to Cxxx-NCR-001438; TTH - Nominated ITP not covering work undertaken, the gate housing installed does not have an approved ITP, this NCR is to record a non-conformance for the procedure as per Works Information 2B Cl 13.3.8. Post installation, the contractor is yet to receive full assurance that the materials installed have the required certification. The sub-contractor has been notified of this inadequacy (see attached)
| 02SL - Stations (LUL) | Cxxx-NCR-001479 | NCR | TTH - POMs room - Infill between ticket machines (inside) |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-03-11 | 2016-03-07 14:25 | -4 | 2016-01-26 10:30 | Architectural - Flooring | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Cxxx-NCR-001472 "TTH POMs room infill between ticket machines" has been raised and will cover the concourse side of the infill. This NCR is raised to cover the POMs side of the infill, which will be easily resolved. As discussed with __, CRL, and LU, the contractor is proposing to fabricate __ boxes to suit the gaps between the machines, which will then be slid in position. __, has been used throughout the TTH for __ furniture. These boxes will be made with a fall towards the inside of the room, and fitted with a pull ring. Sketch is attached.
| 02SL - Stations (LUL) | Cxxx-NCR-001480 | NCR | HCDL Platforms- New platform end barriers interface with existing, platform 1 side. |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-03-04 | 2016-02-16 15:39 | -17 | 2016-01-25 15:35 | Architectural - General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | The new platform end barriers installed on platform 1 side of the HCDL platforms does not tie in vertically to the existing barriers.
| 02SL - Stations (LUL) | Cxxx-NCR-001481 | NCR | TTH VE Signage Relocation, Emergency Exit Signage, Poster Frames Relocation, Additional Signage to be Installed |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-06-09 | 2016-06-07 16:35 | -2 | 2016-01-25 16:58 | Architectural - Signage | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The below items have been relocated due to clashes with existing assets. This was agreed on site with __ and __ on 22/12/2015. - Sign 08 – the frame sign was too wide to be fitted as per drawing and the right hand side fixings were not able to be fitted. - Sign 09 – the sign was to be fitted where a fire call point was already installed. The below items have been substituted due to the size of the signs and the restricted space to fit them. Instead of VE suspended signs there were installed Photoluminascent signs. This was agreed on site with __ and __ on 01/12/2015. - Sign 07a (Lobby 1/085 – above Door D1/17, Corridor 1/242 – above Door D1/18, Corridor A/237 – above Door D2/10, CER 1/572). 2no. additional signs were also requested by __ and __ for the Mechanical Plant Area A/776 and Roof A/551 above doors D2/0 and D2/16. There is no mention to these signs on the approved drawings but this is part of the Fire Exit Route from the Roof. - Sign 07b (TTH External Stairs A/578 – bottom landing) The below items have been also relocated. This was agreed on site with Olaf Haitink on 04/12/2015. - RVP – from the left hand side of the main station entrance to the right hand side of the station entrance. This was due to the relocation of the LFB Box. - CCTV – the standard sign was too wide to go on the external cladding so it was agreed to be moved to the left hand side of the station entrance (where the RVP previously was) Additional SID numbers were also requested by LUL (__ and __) to be fitted on D2/01, D2/10, D2/16, D1/09, D1/10 and D1/12. These signs are in addition to those shown on the approved construction drawings All the aforementioned changes will be captured on the red line drawings.
| 02SL - Stations (LUL) | Cxxx-NCR-001482 | NCR | WSME Interim CMS Route - Cladding Penetration |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-01-01 | 2018-03-05 16:29 | -302 | 2016-01-26 10:24 | Architectural - Walls | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | To achieve the interim station and the associated migration of electrical/communication systems, A temporary CMS route has been installed on the Platform 1 and 2 temporary canopy, connecting existing switch rooms with the TTH. To connect this CMS route with the WSME trunking it has been necessary to cut a penetration in the external cladding on the east elevation above the platform entrance (see attached photographs). This penetration has been formed through the external envelop, the detail has been made weather tight using the typical __ detail for penetrations and it has subsequently been fire stopped. In the temporary condition, this penetration has received a trim to cover the exposed cut edges of the cladding panel. This NCR is to record that the external and internal cladding panels have been cut and will require replacing upon opening of the permanent station when the WSME reverts to an escape stair.
| 02SL - Stations (LUL) | Cxxx-NCR-001483 | NCR | LDP11 unable to be installed in design location- HCDL platforms |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-03-31 | 2016-01-29 08:20 | -62 | 2016-01-26 14:53 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | PTR was raised to __ highlighting the issue that LDP11 could not be installed in the design location-15/9/2015 . The completed PTR was not issed on EB for CRL review. Details Below: 'Please view drawing Cxxx-__M-C-DDA-D061_WS106_2-12501. Drawpit LDP11 cannot be installed between the existing bridge column foundation and the existing switchroom. There is a mass foundation for this bridge column that covers the area in towards the switchroom. Can you please relocate this drawpit where it can installed? Also can you advise if there is to be a brickwork switchroom constructed around this drawpit as on drawing Cxxx-__M-A-DDA-D061_WS106_2-12501 it shows the outline of brickwork and a door.Please provide more information on the cover that is required for drawpit as it states it is a Helling & Neuhaus bespoke cover.
| 02SL - Stations (LUL) | Cxxx-NCR-001485 | NCR | TTH - External Cladding Weatherproof Test Results |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-11-14 | 2016-08-31 14:09 | -75 | 2016-01-28 14:27 | Architectural - Roofing & Exterior Treatment | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Inspection points not adequate | Completed |  | The TTH External Cladding Spary Bar Test does not fully confirm that the building is sufficiently weatherproof as the internal face of the cladding could not be observed as it was covered.
| 02SL - Stations (LUL) | Cxxx-NCR-001488 | NCR | WSME HCDL Platform Drainage invert levels varying from design. |  | Contr | BFK | WHI - Whitechapel Station (Central) |  | 2016-04-04 | 2016-04-04 09:58 | 0 | 2016-02-04 16:18 | Civil - Drainage | 6000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Below details taken from Cxxx-__-PTR-460 The manholes and relating box culverts on drawing no Cxxx-__M-P-DDA-D061_WS106_2-12501 Rev C01 were installed. A survey was carried out which shows the levels higher that design. The direction of the flow is still as per the deign. The concrete culvert pipes were not laid to the correct grade as a result, the invert level of MH03 is +56mm above design. Please advise on level of next Manhole and the following manholes and drainage going East.
| 02SL - Stations (LUL) | Cxxx-NCR-001489 | NCR | Durward St Bridge Concrete Infill out of specified slump |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-04-01 | 2016-03-30 21:18 | -2 | 2016-02-01 17:55 | Civil - Fill | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The concrete infill was poured at the Durward Street Bridge deck on the morning of 25th Jan 2016, during engineering hours. Upon arrival of the concrete load, the ticket was checked by the engineer for to ensure compliance. Concrete was then discharged into a bucket to enable the slump to be assessed and the temperature taken. Once confirmed by the engineer, discharge of the concrete commenced. The concrete was then taken to the 'specified area' where 4 no cubes were made and stored. The concrete was out of slump for all 3 loads but a decision was made to continue with the pour. The concrete sample taken for the slump test displayed good cohesion (there was very little segregation between the constituent materials) therefore the potential risk of under-strength concrete was extremely low. This process was repeated for the 2 subsequent loads (minus the cubes which were not required). See results below (target slump S3 [80-180mm]) Load 1 Slump = 220mm Load 2 Slump = 220mm Load 3 Slump = 200mm
| 02SL - Stations (LUL) | Cxxx-NCR-001491 | NCR | TTH - 2 Slave Clocks were installed wrong voltage |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-04-26 | 2016-04-19 13:34 | -7 | 2016-02-08 09:53 | Communications and Control Systems - General | 2500 |  | Material | Repair | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | During the installation of the 2 slave clocks within the TTH (POMs & SSO room) the wrong voltage clocks were accepted onto site by the COMMs subcontractor. These were installed within their final location. The clocks installed were 24V dc and were meant to be 230V AC as per small power drawings.
| 02SL - Stations (LUL) | Cxxx-NCR-001492 | NCR | CHS - BM38 not installed in C1-02 for connection to W1-24s |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-02-19 | 2016-02-17 12:51 | -2 | 2016-02-05 15:23 | Shafts - Shafts General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | No coupler bars, Bar mark 38 (drg Cxxx-__M-C-DWG-D061_WS107-50376 C02) were installed in C1-02 when it was cast. These couplers provide a connection into W1-24s. __ propose BM18 bars on drg. Cxxx-__M-C-DWG-D061_WS107-50458 C02 are drilled and fixed into C1-02 with hilti-hit 200
| 02SL - Stations (LUL) | Cxxx-NCR-001493 | NCR | TTH - RCD or RCBO Electrical Protection Required |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-04-08 | 2016-03-17 08:46 | -22 | 2016-02-08 15:27 | Electrical - LV Equipment | 2000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | RCD/RCBO protection has been specified on Drawing ‘Temporary Ticket Hall Final Distribution Board Layouts / Cxxx-__M-E-DWG-D061-50039 / C01’ (file attached). The installation was completed to the design however this did not meet the requirement of the LU standard 1-069 as specified in ‘Technical Requirement’. This was brought to the contractors / subcontractors attention during the NORWI inspection. Attached is an email from LU advising of their observation after the NORWRI highlighting the issue and further correspondence. Also attached is a redline drawing ‘Temporary Ticket Hall Final Distribution Board Layouts / Cxxx-__M-E-DWG-D061-50039 / X01’ showing the extent of the circuitry that requires RSBO protection; the __ to be changed for RCBO’s has also been identified below: E50 TTH – DNO 1L2 / 1L3 / 2L3 / 4L3 E59 TTH – NCEPS 8L2 / 10L3
| 02SL - Stations (LUL) | Cxxx-NCR-001494 | NCR | CHS Blockwork Level 6 - block out of tolerance |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-04-24 | 2016-04-13 08:25 | -11 | 2016-02-08 12:42 | Architectural - Brickworks/Blockworks | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 1no block deviates off plumb by 4mm, blockwork parameters for straightness is 5mm in any 5m length. In addition block work is within vertical plumb (within 14mm). In addition the block does not form part of any builders work holes. Please see attached drawing highlighted in red of location.
| 02SL - Stations (LUL) | Cxxx-NCR-001500 | NCR | CHS - Level 1 - W1-24S - Starter Bars Drill and Fix |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-03-27 | 2016-02-28 10:35 | -28 | 2016-02-11 15:03 | Shafts - Shafts General | 1500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Due to 4 No B25 starter bars (BM 7) in W1-24S clashing with form work of the adjacent wall W1-23S the bars were cut to allow shutter installation. See attached reinforcement drawing Cxxx-__M-C-DWG-D061_WS107-50458-C02. __ propose that the 4 No starter bars are replaced with 4 No B25 bars drilled and fixed in location adjacent to original bars. Embedment depth of 250mm. Depth and cleanliness will be checked prior to installation. The replacement bars will be the same length as the original bars. The starter bars were originally installed by Cxxx and their position did not take account of the temporary works or construction sequence required to pour W1-23S.
| 02SL - Stations (LUL) | Cxxx-NCR-001501 | NCR | Internal Mortar Testing |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-05-19 | 2016-04-18 13:35 | -31 | 2016-02-16 09:07 | Architectural - Brickworks/Blockworks | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate resources | Completed |  | The ITP states that mortar testing should be done monthly per batch of CPI batch testing, and that this should be supported by __s monthly cube result verifications. __ have successfully received all CPI batch test results in line with JF10.2200 in conjunction to BS EN 1052 and BS EN 772 which have not highlighted any issues to date. However __ have only conducted verification cube testing for 2months April 2015 and May 2015, therefore we have fallen outside our ITP requirements.
| 02SL - Stations (LUL) | Cxxx-NCR-001502 | NCR | CHS Blockwork Level 4 missing FCD |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-03-23 | 2016-03-01 13:59 | -22 | 2016-02-12 09:20 | Architectural - Masonary | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | MEP design completion supersedes blockwork design information. __ reviewed the blockwork layout and builtders work openings. The revised sizes/locations are confirmed on for CHS Level 4 PTR-381 and attached marked up plans
| 02SL - Stations (LUL) | Cxxx-NCR-001503 | NCR | CHS Blockwork Level 5 missing FCD |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-03-23 | 2016-03-01 09:24 | -22 | 2016-02-12 09:29 | Architectural - Masonary | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | MEP design completion supersedes blockwork design information. __ reviewed the blockwork layout and builders work openings. The revised sizes/locations are confirmed on for CHS Level 5 PTR-373
| 02SL - Stations (LUL) | Cxxx-NCR-001504 | NCR | CHS Blockwork Level 6 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-03-23 | 2016-03-01 14:16 | -22 | 2016-02-12 09:51 | Architectural - Masonary | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | MEP design completion supersedes blockwork design information. __ reviwed the blockwork layout and builders work openings. The revised sizes/locations are confirmed on for CHS Level 6 PTR-373 and attached marked up plans
| 02SL - Stations (LUL) | Cxxx-NCR-001505 | NCR | Lightning installation - no FDC for the changed instalaltion detail |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2016-06-30 | 2016-06-30 15:37 | 0 | 2016-02-12 10:41 | Electrical - General | 2500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Not Defined | Completed |  | NCR has been raised since there was no evidence provided that the lightening protection detail drawings were available on site during the surveillance as required by WIv2B part 13.3.6. Also, although the new detail was installed over a year ago there was no red line drawing showing the change nor a FCD had been raised for the above change. To close out the NCR the Contractor should ensure that all the required documentation is formally submitted. For details refer to surveillance report ref. no. Cxxx-XRL-O4-RGN-CR001-50035
| 02SL - Stations (LUL) | Cxxx-NCR-001506 | NCR | CHS - Shutter movement at East end of A5 slab |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-09-16 | 2016-07-29 15:04 | -49 | 2016-02-12 15:15 | Shafts - Shafts General | 1500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | This is a follow-on NCR from NCR-1282 (See attached) In NCR-1282 it stated "Instead of scabbling the entire face of the concrete member, structurally it is preferred to undertake corrective measure only at the joint where they 'lipped'. The corrective measure can be undertaken in accordance with concrete making good procedure Cxxx-__M-C-GPD-D061_50017 - Section 7.1.3 - Lipping. " This was taken to mean the East face of slab A5 would be scabbled back where it meets wall 5, however where there were openings (later to be blockwork walls), remedial works were not carried out. This was shown in the original sketch attached to NCR1282. Upon closing out the NCR the original response was questioned as the new concrete location was not checked against Cxxx's drawings for clashes with steelwork and fan systems. __ propose: 1) The as-built for the A5 slab is compared with Cxxx's fabrications drawings for their fan systems. If no clash is found, it is proposed to leave the concrete as is. 2) If a clash occurs, the concrete will be scabbled back to removed the lip and made good as per concrete making good procedure Cxxx-__M-C-GPD-D061_50017 - Section 7.1.3 - Lipping. In the event of proposal 1, any alterations to required fire-stopping details will be covered under an RFI/ MDC.
| 02SL - Stations (LUL) | Cxxx-NCR-001507 | NCR | ESS Hoarded Tunnel Construction - Flashing |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-05-15 | 2016-04-04 17:55 | -41 | 2016-02-15 15:43 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As per construction drawing (Hewson) H204/62/009 section X ubiflex flashing should be installed into steel column. On site for vertical junction flashing fendalite not removed and ubiflex fashing installed on top. Also in few locations flashing not sealed correctly as showing on attached photos.
| 02SL - Stations (LUL) | Cxxx-NCR-001508 | NCR | TTH - OLBI Battery __le/Unit within switch room A/661 - Damage to Equipment |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-09-15 | 2016-07-20 13:34 | -57 | 2016-02-15 16:06 | Electrical - General | 1899 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | During an inspection within TTH it was noticed that Damage to Equipment display screen was cracked on OLBI Battery __le/Unit within switch room A/661.
| 02SL - Stations (LUL) | Cxxx-NCR-001509 | NCR | CHS - No couplers in C1-12 for W1-22 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-04-12 | 2016-02-28 11:15 | -44 | 2016-02-16 15:43 | Shafts - Shafts General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | No couplers (BM37) were installed in C1-12 to connect to W1-22 (See drg 50378 attached) It is proposed the 14no. BM15 threaded bars are drilled and fixed in place.
| 02SL - Stations (LUL) | Cxxx-NCR-001511 | NCR | DSS - Vertical Mastic Joints Debonding |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-05-18 | 2016-04-12 15:57 | -36 | 2016-02-18 08:04 | Archaeology - General | 6000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Areas of vertical mastic joint required re-word due to either pour workmanship or mastic de-bonding to cut blocks, concrete face or smooth surfaces. the joints and there reason are listed below; The joints as per the following ref. numbers require rework due to workmanship; • 321531 • 321571 • 321574 • 321530 • 367515 • 321523 • 261865 • 261864 • 261856 • 321565 • 357780 • 357780 • 357782 • 357789 • 341635 • 341636 • 321518 • 318594 • 318586 • 321552 The joints as per the following ref. numbers required rework due to de-bounding; • 321526 • 321525 • 261867 • 261868 • 321526 • 357729 • 321563 • 357783 • 318582 • 318589 • 318583 • 321554
| 02SL - Stations (LUL) | Cxxx-NCR-001512 | NCR | DSS Level 6 IWS-602 DR II Wall |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-05-17 | 2016-04-11 10:09 | -36 | 2016-02-17 14:59 | Architectural - Brickworks/Blockworks | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | IWS-602 perimeter wall has been built alongside DR II with no detail shown for a blockwork wall in drawings Cxxx-__M-A-DDA-D061_WS105_6-20561 and Cxxx-__M-A-DDA-D061_WS105_6-20562.
| 02SL - Stations (LUL) | Cxxx-NCR-001513 | NCR | TTH - __ Vinyl Floors Discoloration |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-03-28 | 2016-03-07 09:08 | -21 | 2016-02-17 18:49 | Architectural - Flooring | 1000 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | __ Vinyl Floor has been installed in the Temporay Ticket Level 1 and level A. See Cxxx-FCD-001220. Following removal of the floor protection, discoloration of the floor was be observed in the following rooms: 2-07 Female lockers 2-01 Corridor 2-11 Mess room 2-02 Male lockers A investigation was consequently carried out by the supplier __. The outcome of this investigation and various conversations with __ specialists are attached to this NCR. In short: - The discoloration cannot be remediated - It is assumed that this discoloration is due to the wrong product being used to clean the floor - Other explanation is that this is due to water/chemical product being trapped between the floor and the floor protection - Slip resistance tests have been carried out on the discoulored floor and the outcome was that the slip resistance was 4 points higher than the normal __ vinyl floor - At the moment, there is no concern regarding the overal performance of the material Consequently, __'s position is as follows: - Given the fact that the product is currently safe to use; - Given the extensive amount of works that replacing the damaged floors would involve; __ is proposing to regularly inspect the floor for further deterioration. Should the condition of the floor worsen, the situation will be reassessed and the floor potentially replaced. In the meantime it will be used as-is despite the above noted defects.
| 02SL - Stations (LUL) | Cxxx-NCR-001514 | NCR | TTH - Door Ironmongery schedule |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-11-30 | 2018-02-08 09:31 | -295 | 2016-02-29 12:08 | Architectural - Doors | 1550 |  | Incorrect Installation | Reject | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | This NCR is about the Temporary Ticket Hall Door Ironmongery Schedule included, document number Cxxx-__M-A-DWG-D061-50029. Up to revision 5.0 of the document, the door closer types were as followed: C6/10 for doors D1/08 D1/09 D1/10 D1/12 D1/13 D1/16 D1/18 C7/10 for doors D1/01 D1/14 D1/17 D1/19 D2/01 D2/10 D2/14 D2/15 D2/16 Revision 6.0 of the document introduced a change to types C10/10 and C11/10 respectively. The changes introduced in revision 6.0 are not reflected on site, as door closers are as per revision 5.0, except for door D2/16 which has a C11/10 door closer.
| 02SL - Stations (LUL) | Cxxx-NCR-001515 | NCR | HCDL Platforms - Working to P revision Drawings |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-06-30 | 2016-04-20 08:09 | -71 | 2016-02-22 11:19 | Civil - Civil Engineering General | 1000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | During IRF-777 it was noted that the construction drawings produced onsite, of which the draw pit work was constructed to, were P revision drawings. This means the drawings have not gone through the CRL gate assurance process exposing __ and CRL to increased risk during construction. P revision drawings were used as construction drawings due to the delays the __ delivery team were experiencing with the formal issue of IFC drawings. The IFC drawings associated with these works were to be issued at the beginning of January and as of today 19/02/2016 they have still not been issued. To prevent any standing time onsite it was agreed within the design team to construct to the P revision drawings under a CRL PMI. The PMI had not been formally issued before the works started onsite.
| 02SL - Stations (LUL) | Cxxx-NCR-001516 | NCR | DSS & CHS - Lightening Protection - Works proceeding without a completed design |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-02-24 | 2017-02-07 08:54 | -17 | 2016-02-22 09:55 | Electrical - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Lightening Protection installation has been installed prior to the design being assured
| 02SL - Stations (LUL) | Cxxx-NCR-001517 | NCR | CHS Level B - MEP - Use of non approved materials - __ |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-05-20 | 2016-05-19 14:51 | -1 | 2016-02-22 10:10 | Mechanical - Public Health Engineering | 2000 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | __ insulation material has been installed around pipework in CHS Level B. __ is a non-approved product for the project.
| 02SL - Stations (LUL) | Cxxx-NCR-001518 | NCR | Platform Tunnels - Pressure Relief Drainage - Ch10470-Ch10500 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-04-03 | 2016-03-07 14:43 | -27 | 2016-02-23 16:50 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Pressure Relief Drainage was installed 4 dimples wide rather than 6 dimples wide at the tunnel invert - wing wall interface, as shown on marked up drawing Cxxx-HYD-C4-DDA-D061_WS106_7-20578.
| 02SL - Stations (LUL) | Cxxx-NCR-001519 | NCR | Area 3 Slab - Concrete Finishing |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-12-01 | 2016-11-11 10:43 | -20 | 2016-02-24 14:56 | Civil - Civil Engineering General | 5000 |  | Workmanship | Use As-Is | 3 (3-6k) | Complete | Supervision - Other | Completed |  | On Sunday 14th Feb, the slab on metal decking at Area 3 was poured. Following the pour, operatives walked across the finished surface in an attempt to secure frost blankets to the surface for cold weather protection during curing. The concrete was not sufficiently cured and as a result deep footprints were left in the concrete surface. Once the problem was identified by the supervisor and engineer, it was raised to the __ Works Manager, Construction Manager, Crossrail and Cxxx. The slab was inspected by the above and it was agreed that the concrete was still workable and the slab was re-worked. Frost blankets were once again placed, this time without walking on the fresh concrete surface.
| 02SL - Stations (LUL) | Cxxx-NCR-001520 | NCR | DSS - WA-12S Missing Couplers |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-04-04 | 2016-03-24 16:16 | -11 | 2016-02-24 12:24 | Shafts - Shafts General | 2000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 11no missing couplers within Level A Slab for starters for WA-12S, across the length of the wall.
| 02SL - Stations (LUL) | Cxxx-NCR-001521 | NCR | DSS - WA-12S Reduced Cover |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-04-14 | 2016-04-12 08:22 | -2 | 2016-02-25 10:22 | Shafts - Shafts General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Reduced cover between CA-06 and WA-12S, please refer to attached site photos.
| 02SL - Stations (LUL) | Cxxx-NCR-001522 | NCR | DSS - CA-32 Cover Issue |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-03-31 | 2017-03-30 15:25 | -1 | 2016-02-25 17:35 | Shafts - Shafts General | 2000 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Reduced cover on CA-32 on North Eastern side.
| 02SL - Stations (LUL) | Cxxx-NCR-001523 | NCR | LO SME - Electrical works without approved design |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-04-09 | 2016-03-17 15:35 | -23 | 2016-02-29 11:08 | Electrical - Electrical Engineering General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | London Overground Secondary Means of Escape Electrical works was carried out without an approved design or Project Manager Instruction.
| 02SL - Stations (LUL) | Cxxx-NCR-001524 | NCR | TTH - DNO Metering Cupboard 6 way earth bar |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-09-10 | 2016-09-07 15:13 | -3 | 2016-03-29 06:48 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | This NCR has been raised to cover the fact that an FCD should have been raised to cover the fitting, on-site, of a 6 way earth bar instead of the 12 way, as specified in the design. Earthing Schematic Drawing Cxxx-__M-E-DWG-D061-50063 specifies 12 way earth bar.
| 02SL - Stations (LUL) | Cxxx-NCR-001525 | NCR | DSS - Level 3-1 Cube Results |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-04-10 | 2016-03-23 10:46 | -18 | 2016-03-01 10:23 | Shafts - Shafts General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Insufficient quantity of material to do the job | Completed |  | Extract of cube results in the table attached for Line 31 concrete poured within DSS in Level 3-1 have not achieved the required 56 day compliance strengths.
| 02SL - Stations (LUL) | Cxxx-NCR-001526 | NCR | DSS - Concrete Cube Results Level 1-A |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-04-10 | 2016-03-23 10:47 | -18 | 2016-03-01 10:42 | Shafts - Shafts General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Insufficient quantity of material to do the job | Completed |  | Extract of cube results in the table attached for Line 31 concrete poured within DSS in Level 1-A have not achieved the required 56 day compliance strengths.
| 02SL - Stations (LUL) | Cxxx-NCR-001527 | NCR | TTH - Lack of FCD for Ventilation Damper Size Change |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-09-24 | 2016-07-15 14:57 | -71 | 2016-04-27 07:05 | Mechanical - Heating Ventilation & Air Conditioning | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | This NCR is raised to cover the fact that an FCD should have been issued for a change to the Smoke Damper size fitted on site. The specification states that the wall duct sleeve for MAP smoke damper SD-F16 is to be 600mm (width) x 350mm (height). Owing to the restricted space between the structural steel and the ceiling the specified damper will not fit. Subcontractor __ proposed changing the size of the damper be to 850mm (width) x 250mm (height) to allow the damper to fit and to maintain the cross sectional area of the damper. Owing to this change the width of the opening will need to be 870mm – the current height is adequate.
| 02SL - Stations (LUL) | Cxxx-NCR-001528 | NCR | DSS - WA-19NS Cover Issue |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-03-28 | 2017-03-28 07:32 | 0 | 2016-03-02 08:45 | Shafts - Shafts General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Reduced cover between West end of WA-19NS and CA-24 and concrete cracking around localised coupler. Please refer to attached site photos.
| 02SL - Stations (LUL) | Cxxx-NCR-001529 | NCR | DSS - Stair 3 Temporary Finishes |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-06-20 | 2016-06-18 08:58 | -2 | 2016-03-03 16:31 | Shafts - Shafts General | 50000 |  | Incomplete Works | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As part of the Construction Phase Fire Strategy, Stair 3 in the Durward Street Shaft will be used as the temporary SME route from the London Overground, Platform 6. This is to allow the current SME over London Overgound to be removed to facilitate the installation of the new Permanent Concourse above London Overground. When the temporary SME route is in place through stair 3, the permanent finishes (approx 85mm build-up of paving and nosing’s) will not been installed. Prior to concreting the stairs, it was hoped the concrete finish would have been such that the stairs could have been used in a temporary case without needing to carry out any additional works to get them to conform with the relevant standards. However, due to the tolerances required with the specification, it has not been possible to do this. To enable the stairs to bough into use, a temporary finish / detail will need to be installed to the concrete treads __ propose a similar solution to that used on the stairs at the Western SME. A 3000mm wide x 160mm high x 3mm think steel plate will be fixed to the front of all the stair risers. These will then be levelled. Any concrete on the tread above the height if the steel plate will be scabbled back. Once steel plates have been checked, ‘Contar ‘ will be installed and level over the whole tread providing a level finish and a constant rider height between all the stairs The plate will be fixed to the concrete with 2no. rows (staggered) of 6no. __ M10 countersunk HUS-CR concrete fixings, equally spaced. See attached sketch. The out hoes will be slotted to enable movement when setting the treads into position. The contar will be installed by a specialist subcontract Pls confirm this detail is acceptable
| 02SL - Stations (LUL) | Cxxx-NCR-001530 | NCR | DSS - Level A Central Pour 400mm Upstand |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-04-21 | 2016-04-13 09:09 | -8 | 2016-03-02 12:47 | Shafts - Shafts General | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The reinforcement for Level A Central Pour 400mm Upstand has been installed outside the concrete line of the upstand.
| 02SL - Stations (LUL) | Cxxx-NCR-001532 | NCR | TTH - SSO Room sink position. No FCD raised. |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-08-24 | 2016-07-26 11:58 | -29 | 2016-04-26 10:42 | Mechanical - Hot & Cold Water Supplies | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | The sink unit in the SSO has been installed in a position, rotated through 180 degrees, compared to the original IFC drawing. The pipework to the sink has been modified to suit. No FCD was raised at the time
| 02SL - Stations (LUL) | Cxxx-NCR-001533 | NCR | TTH - Fire Rated Ductwork Lagging |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-08-25 | 2016-07-21 16:03 | -35 | 2016-04-27 07:16 | Mechanical - Heating Ventilation & Air Conditioning | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | NCR to cover the lack of an FCD for Fire-rated ductwork not lagged, due to fire compartmentation alteration
| 02SL - Stations (LUL) | Cxxx-NCR-001534 | NCR | Platform 5&6 SME Fire Hoardings Materials |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-04-12 | 2016-04-07 15:56 | -5 | 2016-03-03 16:24 | Architectural - Partitions | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | The Specialist sub-contractor who are installing the Fire Hoarding as part of the Platform 5&6 SME route through DSS installed a different plasterboard than what they had specified. The hoarding makeup calls for ‘12mm plasterboard’ overlaid by ‘__’, which provides the fire separation. The specialist sub-contractor advised they would use ‘12mm __ Fireline’ as the plasterboard. An MCR was generated by __ for that material and it was noted that ‘__ Fireline’ was on the LU approved materials register. However, during the installation of the fire hoardings in DSS, It was discovered by the __ Engineer that ‘12mm __ Fireboard’ was being used as the plasterboard layer in place of the __. ‘12mm __ Fireboard’ is not on the LU approved Materials Register Works were immediately stopped and CRL were advised. __’s Consultant Fire Engineer, __ was contacted and advised that the alternative material would provide adequate protection and the design intent is met with the substituted board. Additionally, there were no issues with regards to its suitability. Similar views were noted by Crossrail’s Fire Engineer __, however he noted that until an MCR was approved, installation of the board would be at the contractor risk. Works have since continued An MCR will be raised for the alternate materials pending acceptance of this NCR. The email string containing the responses from both fire engineers is attached with this NCR
| 02SL - Stations (LUL) | Cxxx-NCR-001535 | NCR | DSS - WA-19NS Missing Bar |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-04-12 | 2016-03-23 11:06 | -20 | 2016-03-03 17:16 | Shafts - Shafts General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 1no BM04 Near Face is missing in CA-24.
| 02SL - Stations (LUL) | Cxxx-NCR-001536 | NCR | Platform 5&6 SME Hoarding Fixings |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-04-21 | 2016-04-21 15:29 | 0 | 2016-03-03 17:46 | Architectural - Partitions | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During an inspection of the Platform 5&6 SME hoardings in DSS between __ and CRL, it was noted a small number of the M12 fixing between adjoin steel frames were loose. Additionally, a small number of the washers were not central to the holes in which the M12 studs were installed meaning they were not bearing sufficiently or evenly on either side of the holes. At the time of the inspection, level 4 hoarding was complete (cladding fixed to both sides of the steel frames meaning no access to the fixings) however Level 3 and 4 only had 1 side of the facing installed (meaning full access to all the bolts). As a precaution, all works on the hoarding installation were stopped, and the contractor installing the hoarding instructed to change ALL the washers on Level 1 and level 3 to oversized washer and re-torque all bolts. A new check sheet was implemented as part of the ITP to cover the torqueing of the bolts which was completed by __ and witnessed by the CRL night shift Engineer (check sheets attached) The Works were re inspected the following morning by __ and CRL day shift
| 02SL - Stations (LUL) | Cxxx-NCR-001537 | NCR | DSS - WA-19NS Alignment |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-08-06 | 2016-07-25 09:36 | -12 | 2016-03-09 12:51 | Shafts - Shafts General | 895 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | WA-18S and WA-19NS are out of alignment, please refer to attached asbuilt.
| 02SL - Stations (LUL) | Cxxx-NCR-001538 | NCR | DSS - W1-08S Alignment Issue |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-04-13 | 2016-04-07 07:46 | -6 | 2016-03-04 09:13 | Shafts - Shafts General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | W1-08S the southern end of the wall has been poured out of alignment, please see attached survey of the wall.
| 02SL - Stations (LUL) | Cxxx-NCR-001539 | NCR | Crossrail Platforms - Low cover in localised area on top steel of the Track bed W/B T/B bay 212 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-05-31 | 2016-04-22 09:20 | -39 | 2016-03-07 19:18 | Track - Track Bed | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On track bed W/B T/B bay 212 there is low cover at the eastern end construction joint to bay 213. The cover issue is localised to the stop end area. Cover to the B10 top reinforcement in the worst place is 20mm, see attached photos.
| 02SL - Stations (LUL) | Cxxx-NCR-001540 | NCR | CHS - Level 1 - W1-24S Pour 1 Couplers for Stair 42 flight 2 out of position |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-04-17 | 2016-04-13 07:10 | -4 | 2016-03-08 16:11 | Shafts - Shafts General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | At level 1 of the Cambrige Heath Shaft, couplers were installed in W1-24S (Dwg:50458) to receive screw in bars BM31 (Dwg:50480) from Stair 42 Flight 2. When the reinforcement was being fixed it was discovered that the couplers had been installed in the bottom 1 position, however the drawing (Dwg:50480) shows that the couplers for BM31 should be installed in the B2 layer. If the reinforcement was to be installed in the position shown on the drawing the cover to the B1 reinforcement BM16a-e and BM20 would be reduced below the required 50mm. __ propose BM31 will be installed in the B1 layer to ensure the nominal cover would be the required 50mm. Therefore, all the reinforcement in the B2 position will be swapped with the B1 reinforcement. Please see attached drawings; Cxxx-__M-C-DWG-D061_WS107-50458-C02 and __ Cxxx-__M-C-DWG-D061_WS107-50480-C02 and __
| 02SL - Stations (LUL) | Cxxx-NCR-001541 | NCR | CHS Blockwork Level 6 - Wall Out Of Tollerance |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-05-01 | 2016-04-26 08:10 | -5 | 2016-03-08 18:31 | Architectural - Brickworks/Blockworks | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Level 6 IWS-621 wall was not constructed straight and therefore the line of blockwork went off set from setting out position. Blockwork wall was taken down and placed back in line of setting out position. See attached drawing for reference.
| 02SL - Stations (LUL) | Cxxx-NCR-001542 | NCR | Insufficient concrete to complete the pour - Tunnel platforms - WB - TB213 - Cxxx-__M-C-CER-D061-50471 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-04-28 | 2016-04-15 10:25 | -13 | 2016-03-09 05:49 | Civil - Civil Engineering General | 1500 |  | Planning | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Due to supply difficulties not enough concrete was delivered to the westbound tunnel to complete pour of Track Bed 213 WB. As the effect concrete levels on approx. 20% of the slab area were too low providing only a couple of mm of cover. At 18:20 the decision was made to clean the lines and install temporary stop ends. Due to retarder ingress from finished sections of the pour it was left for a few hours to achieve workability and then temporary stop ends were installed to cover a minimum 150mm of concrete depth and provide squared up concrete joint. Slab concrete at 100mm below steel was levelled and left for construction joint preparation (jetwashing/scabbling). Affected area of track bed is shown in attached marked up drawing, and is between chainage 10503.607 and 10494.894.
| 02SL - Stations (LUL) | Cxxx-NCR-001544 | NCR | DSS Level 5 - DR II Doorway Cracked Lintel |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-05-10 | 2016-04-12 08:13 | -28 | 2016-03-11 08:16 | Architectural - Brickworks/Blockworks | 2500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Concrete lintel above Doorway D5 006 into the DR II Room has been chipped on the bottom corner as shown in attached photos.
| 02SL - Stations (LUL) | Cxxx-NCR-001545 | NCR | DSS Blockwork - Stair 5/DR I incorrect installation |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-06-18 | 2016-04-13 08:21 | -66 | 2016-04-04 08:51 | Architectural - Brickworks/Blockworks | 3500 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The return section of blockwork between Stair 5 and DR I has been built incorrectly in position shown in the attached mark up.
| 02SL - Stations (LUL) | Cxxx-NCR-001546 | NCR | Crossrail Platforms - Shrinkage cracking in the W/B track bed pours- Cxxx-__M-C-CER-D061-50476 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-09-01 | 2016-09-01 09:22 | 0 | 2016-04-11 15:15 | Civil - Track | 8000 |  | Material | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Other | Completed |  | Shrinkage cracks are located in the track bed pours, see attached crack report detailing size and locations of cracks that have been identified. More investigation into the cracks is required.
| 02SL - Stations (LUL) | Cxxx-NCR-001547 | NCR | TTH - Lack of FCD for Additional Power supplies for GLAP and Door Contacts |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-09-02 | 2016-09-06 12:52 | 4 | 2016-04-26 06:38 | Electrical - General | 2000 |  | Design | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | An FCD should have been raised at the time of installation for an additional power supply to the GLAP in the concourse area of the Temporary Ticket Hall. Also an additional power supply was required for door-entry contacts, due to late changes in the door-entry design.
| 02SL - Stations (LUL) | Cxxx-NCR-001548 | NCR | TTH - Earthing Schematic Drawing. Additional details added for three switchrooms |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-09-23 | 2016-07-20 10:31 | -65 | 2016-04-26 06:57 | Electrical - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | Subcontractor __ had not been issued with a C01 drawing showing the earthing arrangement within three of the TTH switchrooms. They were issued with a P05 drawing detailing the earthing requirements in the three switch rooms. The C01 drawing was subsequently updated with the P05 information relating to the three switchrooms. The NCR has been raised as work started without a C01 drawing.
| 02SL - Stations (LUL) | Cxxx-NCR-001549 | NCR | DSS - WB-12S Cover Issue |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-05-14 | 2016-04-13 08:22 | -31 | 2016-03-15 17:05 | Shafts - Shafts General | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Reduced cover on the southern side of WB-12S at the vertical construction joint at CB-06.
| 02SL - Stations (LUL) | Cxxx-NCR-001550 | NCR | Twin wall system - concrete instead of bentonite |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-04-29 | 2016-03-30 21:24 | -30 | 2016-03-16 15:15 | Civil - Civil Engineering General | 10000 |  | Material | Rework | 2 (6-60k) | Complete | Personnel Error - Inattention to detail | Completed |  | As per of the design, a twin wall system was required to be set up on Pile group 18. The twin wall system was supposed to be made of: permanent casing, then bentonite, then Wells Type 3C duct, then bentonite. Concrete has been poured instead of bentonite on the outside of the Wells Type 3C duct (for 3 piles out of 6).
| 02SL - Stations (LUL) | Cxxx-NCR-001551 | NCR | LULO - West Stair Shaft - Fabrication undertaken without an pre start documentation approval (ITP, WPS, MCR) |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-08-17 | 2016-10-12 15:23 | 56 | 2016-03-17 13:59 | Civil - Civil Engineering General | 2000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Procurement and fabrication of the steel staircase for the West Stair Shaft proceeded without key pre start documents accepted by CRL and with no prior discussion with the client to agree
| 02SL - Stations (LUL) | Cxxx-NCR-001552 | NCR | LULO - LO SME Hoarding - Works proceeding without pre start document approvals (ITP, Design) |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-06-10 | 2016-06-10 13:38 | 0 | 2016-03-17 14:05 | Civil - Civil Engineering General | 2000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Works have proceeded on site without an ITP or design in place for the RJC Fire Hoarding associated with the LO SME works
| 02SL - Stations (LUL) | Cxxx-NCR-001553 | NCR | Grouting of joints between Paving slabs and ACO Channel. HCDL Platform |  | Contr | BFK | WHI - Whitechapel Station (Central) |  | 2016-06-30 | 2016-04-12 15:59 | -79 | 2016-03-18 12:55 | Architectural - Flooring | 2000 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Approval of Design Change Notice (FCN/FCR) in CTI excessive | Completed |  | As this change was not captured by way of FCD, an NCR required to be raised. The soft joint infill to the __ channel on the HCDL platforms to __'s understanding was requested by London Underground for the purpose of aiding in removal of the __ channel should this be required in the future. The shape of the__ is flared at the base, there is also a significant ammount of concrete haunching around the __ Channel base. Should the __ be removed, several paving slabs wide either side of the __ would have to be removed also. The joint to the 150mm __ nearest platform 1 is also works that cant be undertaken to the weekend of the week 43 possesion due to raking props and hoarding restricting paving slabs being installed. the __ 600 and __ MP20 will have not cured to significant strength to allow foot traffic once station is opened Monday 18 Jan 2016. the __ also has a curing time of 4 weeks.
| 02SL - Stations (LUL) | Cxxx-NCR-001554 | NCR | LULO - Pile Group 18 - Pile 112 Reduced Projection Length into Headstock |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-05-31 | 2016-04-05 11:11 | -56 | 2016-03-21 19:13 | Civil - Structural Engineering | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | After pile break back activities were completed it was discovered that main bars on Pile 112, in Pile Group 18, do not reach the required projection. Drawing Cxxx-HYD-S-DDL-D061_WS106_Z-74003 (attached) calls for 800mm projection into the headstock, all 6(no.) bars of Pile 112 have 700mm projection. It should be noted all other piles have reached (and exceeded) the required projection (7no.)
| 02SL - Stations (LUL) | Cxxx-NCR-001556 | NCR | DSS Level 5 DR I/Stair 5 Blockwork - Incorrect return location |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-05-23 | 2016-04-11 10:22 | -42 | 2016-03-24 16:25 | Architectural - Brickworks/Blockworks | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Subcontractor constructed blockwork incorrectly (shown in attached mark up) to sit on upstand instead of as per the drawing.
| 02SL - Stations (LUL) | Cxxx-NCR-001557 | NCR | CHS - stairs 42B wedge wall couplers in wrong location |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-05-30 | 2016-05-04 14:46 | -26 | 2016-03-24 19:23 | Shafts - Shafts General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The couplers cast into W1-23s (BM-07 and 08 drg. 50456) for the stairs 42B wedge wall were cast out of place so that the cover to the south side of the wedge wall was around 120mm It is proposed that the 8no. threaded bars be installed as per the drawing (50516) but a further 4no. bars be drilled and fixed to make up for the lack of reinforcement in the southern side of the wedge wall. These bars will be drilled to an embredment depth of 200mm and fixed with hilti hit 200.
| 02SL - Stations (LUL) | Cxxx-NCR-001558 | NCR | CHS - missing couplers into A4 slab |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-05-12 | 2016-05-04 10:50 | -8 | 2016-04-02 08:27 | Shafts - Shafts General | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 2no. couplers are missing from the south East side of the A4 slab. (BM-18). See drawing attached. As per attached communication, the missing bars were drilled and fixed to depth of 200mm with hilti-hit 200A resin. See photo attached.
| 02SL - Stations (LUL) | Cxxx-NCR-001559 | NCR | DSS Level 6 Blockwork Builders Work alterations |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-05-10 | 2016-04-12 08:59 | -28 | 2016-03-31 11:22 | Architectural - Brickworks/Blockworks | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | PTR-395 was issued for DSS Level 6 Builders Works - as the latest design information at the time of construction. This PTR should have been issued to CRL on an FCD prior to commencing works and was not. These works are now substantially complete.
| 02SL - Stations (LUL) | Cxxx-NCR-001560 | NCR | E5 to CER Submain Replacement; no FCD raised to cover installation of new earth bar |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-07-30 | 2016-08-02 11:10 | 3 | 2016-04-01 15:28 | Electrical - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | This NCR has been raised to cover the fact that an FCD should have been issued regarding the fitting of an additional earthbar in switchroom E5. (Room 1/665). The existing main-earth terminal (MET) in E5 was specified to be used, but is of insufficient size to accept the new Earth Bonding Conductors to be installed, as detailed in the Earth Management Plan stage 6, Cxxx-__M-E-STP-D061-50009. (Page 3 of the CDS, Cxxx-__M-E-XST-D061_WS106-50010 also details a 95mm Earth Bonding Conductor size). A 12 way earth bar has now been fitted in E5 to accomodate the specified Earth Bonding Conductors.
| 02SL - Stations (LUL) | Cxxx-NCR-001561 | NCR | CHS - A4 slab coupler bars at wrong angle |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-05-12 | 2016-04-27 08:02 | -15 | 2016-04-02 10:16 | Shafts - Shafts General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | To the NW corner of the A4 slab, 2no. bars had to be bent to suit the line of the shutter. The coupler was a P13-35 however the bars were detailed to be cranked. On drawing 50497 attached, it can be seen that these bars should have been curved to match the shutter. __ propose the bent bars to be left as is, as they were only bent a single time and no cover or adjacent bars were affected by the modification.
| 02SL - Stations (LUL) | Cxxx-NCR-001562 | NCR | DSS - W1-16NS Shrinkage |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-04-12 | 2016-04-12 08:07 | 0 | 2016-04-04 09:46 | Shafts - Shafts General | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There is a 30mm void between the top of W1-16NS and Level A Slab Soffit.
| 02SL - Stations (LUL) | Cxxx-NCR-001563 | NCR | LULO - Pile 97 - Inclination Tolerance not achieved |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-06-03 | 2016-05-26 10:10 | -8 | 2016-04-04 21:02 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Inclination of Pile 97 out of tolerance - 1:40 achieved
| 02SL - Stations (LUL) | Cxxx-NCR-001564 | NCR | LULO - Concrete Testing by non UKAS trained engineers |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-06-03 | 2016-05-27 08:15 | -7 | 2016-04-04 21:13 | Civil - Civil Engineering General | 2000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Training Deficiency - No training provided | Completed |  | Concrete slump testing and cube making has been undertaken by the LULO team using engineers who have not been trained by the Cxxx laboratory.
| 02SL - Stations (LUL) | Cxxx-NCR-001566 | NCR | CRL Platforms - Shrinkage Crack in Wall |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-12-01 | 2016-11-30 16:26 | -1 | 2016-04-07 09:10 | Civil - Civil Engineering General | 5065 |  | Material | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | In the Westbound tunnel a shrinkage crack has been noticed in the inner wall of bay 014. See attached drawing for location, the approximate Track Centre Line Chainage is 10483.300. The crack is located adjacent to a crack which runs through the trackbed lower / upper pours in bays 212/222. The crack is approximately 0.5mm wide and appears to run through the whole wall. More investigation into the crack is required and investigation into whether this is occurring in other poured track beds which still have shutters blocking view. The Contractor is currently reviewing the concrete mix design in light of this new crack.
| 02SL - Stations (LUL) | Cxxx-NCR-001567 | NCR | DSS - CB-44 Bolt Holes |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-04-11 | 2016-04-13 09:15 | 2 | 2016-04-07 14:02 | Shafts - Shafts General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Bolt holes for CB-44 for the bracket for Cxxx Beam are out of position.
| 02SL - Stations (LUL) | Cxxx-NCR-001568 | NCR | LO Platform 5 and 6 SME - No IRF offered for the MEP Installation |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-09-02 | 2016-09-05 08:56 | 3 | 2016-04-08 11:36 | Electrical - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Inspection and Request Form not issued to the CRL FE for the inspection of the activities detailed in the ITP for Platform 5 and 6 LO Secondary Means of Escape (Cxxx-__M-E-ITP-D061_WS106-50012)
| 02SL - Stations (LUL) | Cxxx-NCR-001569 | NCR | LO SME Platform 5 and 6 - lack of snagging |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-09-02 | 2016-09-05 09:19 | 3 | 2016-05-05 16:02 | Electrical - General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Reporting of Defective and Outstanding Works ("snags") has not been carried out on the LO SME MEP works.
| 02SL - Stations (LUL) | Cxxx-NCR-001570 | NCR | LULO - LO SME Works - Floor Installation - Lack of cleaning prior to opening |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-06-07 | 2016-06-07 16:05 | 0 | 2016-04-08 13:15 | Architectural - Flooring | 2000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | The station was opened up prior to a final clean of the false floors being carried out within the DSS and WSS SME routes. Works on the false floors commenced 3 days prior to opening the SME and took 3 days to complete meaning they were completed on the day we handed back. There was saw dust and stains present on the floors when the station was opened which required additional works during engineering hours after opening
| 02SL - Stations (LUL) | Cxxx-NCR-001571 | NCR | CHS - low cover to upstand on A4 slab |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-05-18 | 2016-05-16 09:14 | -2 | 2016-04-08 14:25 | Shafts - Shafts General | 3000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There is around 25mm cover to BM-32 in CUB-A-12 on the south side of the A4 slab. See attached sketch for location and photo of the cover. __ propose to leave the cover as is due to the difficulties in adjusting the reinforcement. This is as per communication with Cxxx attached.
| 02SL - Stations (LUL) | Cxxx-NCR-001572 | NCR | LULO - LO SME Works - Temporary Handrail Installation |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-06-03 | 2016-06-02 15:50 | -1 | 2016-04-08 13:20 | Architectural - Handrail | 3000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient surveillance of subcontractors | Completed |  | The installation of the handrail took approximately 4 weeks to complete from start to finish. During this time there were various other trades carrying out works in the SME route the same time. The handrails were in semi complete state for most of the installation at which time they were left unprotected due to the works not being complete. During this time, the handrails sustained damage and scuff marks due to the other works happening in the SME at the same time. Once the handrails were near complete, they were inspected by CRL, __ and LU. This inspection identified the damage caused from the handrails being left unprotected as well as a considerable amounts of snags and defects over the entire length of the handrail which required reworks. Again, the handrails were left unprotected to enable the snagging / rework to be completed during which time additional damage may have been sustained
| 02SL - Stations (LUL) | Cxxx-NCR-001573 | NCR | Storage of Concrete Cubes in the GSM Storage Room |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-06-10 | 2016-07-06 08:18 | 26 | 2016-04-08 13:24 | Civil - Civil Engineering General | 1000 |  | Material | Rework | 4 (0.5-3k) | Complete | Training Deficiency - Not Defined | Completed |  | P2 Piling, week 52 possession (cast 20/03/16) struck from cubes and being stored in room. 16 days old (as of Tuesday) P2 Piling, week 52 possession (cast 20/03/16) placed in bath still in mould. Should have been struck 14 days ago. 16 days old (as of Tuesday) P6 Pile cap , cast 28/03/16, still in mould. These should have been struck 6 days again, 7 day test overdue. 8 days old (as of Tuesday) P5 PG17, date cast unknown. Still in mould.
| 02SL - Stations (LUL) | Cxxx-NCR-001574 | NCR | LULO - Platform 1 Resurfacing |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-09-16 | 2016-07-25 09:38 | -53 | 2016-04-08 13:28 | Civil - Fill | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Platform 1 resurfacing - No N__ testing undertaken on sub-grade during possession works (Week 3)
| 02SL - Stations (LUL) | Cxxx-NCR-001575 | NCR | LULO - LO SME - Door Frame Installation on P6 SME Entrance |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-06-07 | 2016-06-04 20:44 | -3 | 2016-04-08 13:32 | Architectural - Doors | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Clear opening of the door frame prior to installing the doors was supposed to be 2130mm as per the ITP. When this was measured onsite, clear distance between the door frame was measured at 2130mm however bolt fixings on either side projected into the clear openings reducing it to 2120mm. This was highlighted to the specialist door installer who confirmed the door opening was satisfactory and the protruding bolts would not affect the door installation. This turned out to be correct
| 02SL - Stations (LUL) | Cxxx-NCR-001576 | NCR | LULO - LO SME Works - DSS temporary handrail out of Tolerance |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-06-07 | 2016-06-04 20:48 | -3 | 2016-04-08 13:36 | Architectural - Handrail | 3000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Gaps between adjoining sections of the temporary handrail in the LO SME route through DSS are >2mm throughout the route
| 02SL - Stations (LUL) | Cxxx-NCR-001577 | NCR | LULO - LO SME Works - Platform 5 & 6 End Barrier - Pull Test Requirement |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-06-07 | 2016-06-04 20:53 | -3 | 2016-04-08 13:40 | Architectural - Balustrade | 3000 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | No pull testing undertaken on platform end barriers installed at the end of Platform 5 & 6
| 02SL - Stations (LUL) | Cxxx-NCR-001578 | NCR | LULO - LO SME Works - Platform 6 End Barrier Installation |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-06-07 | 2016-06-09 14:05 | 2 | 2016-04-08 13:44 | Architectural - Balustrade | 5000 |  | Incomplete Works | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | During the installation of the end barrier on platform 6, not all the fixings could installed in the base plates which fix the barrier to the platform. This is due to the holes in the base plates being directly below the bottom steel member on the end barrier and preventing access with a drill.
| 02SL - Stations (LUL) | Cxxx-NCR-001579 | NCR | LO SME Platform 5 and 6 - Materials used not covered in the MCR list on the ITP |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-08-01 | 2017-08-02 12:53 | 1 | 2016-05-26 15:12 | Electrical - Electrical Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Work was commenced on new Fire System call-points for the LO SME on Platforms 5 and 6, using Firecel SR114E SWA cable which is not on the MCR register of approved materials. The cable is approved for LU use and the MCR application is currently in process.
| 02SL - Stations (LUL) | Cxxx-NCR-001580 | NCR | LO SME Platform 5 and 6 - Fire ITP records not compiled progressively |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-09-02 | 2016-09-05 09:03 | 3 | 2016-05-05 13:39 | Fire - Fire Systems & General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Construction Records have not been fully completed with all the required signatures, as the work progressed.
| 02SL - Stations (LUL) | Cxxx-NCR-001582 | NCR | LO SME - Lack of MCR for Door Alarm System |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-09-30 | 2016-11-07 08:44 | 38 | 2016-05-10 14:21 | Communications and Control Systems - General | 1000 |  | Material | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | A Door Alarm system has been installled in the LO SME without an Materials Compliant Record (MCR) being approved for the materials and prior to work commencing. Materials are: 1) __ Elite 88 - Door Alarm Panel, 2)__ Elite SMK - Keypad, 3) __ - Door Contacts
| 02SL - Stations (LUL) | Cxxx-NCR-001583 | NCR | LO SME - Lack of MCR for __ Termination Box |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-09-07 | 2016-09-27 11:56 | 20 | 2016-05-10 15:15 | Electrical - General | 1000 |  | Material | Rework | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | A __ Termination Box has been used on site without a Materials Compliance Record being approved for use.
| 02SL - Stations (LUL) | Cxxx-NCR-001584 | NCR | LO SME - Lack of MCR for Wall Mounted Rittal Cabinet EL7706 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-09-07 | 2016-10-18 07:30 | 41 | 2016-05-10 15:53 | Electrical - General | 0 |  | Material | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | No MCR in place for a Wall Mounted Rittal Cabinet EL7706 used on the LO SME.
| 02SL - Stations (LUL) | Cxxx-NCR-001585 | NCR | LO SME - Lack of MCR for Cat6 __ Cables |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-09-07 | 2016-10-05 13:22 | 28 | 2016-05-10 16:29 | Communications and Control Systems - General | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | No MCR in place for Cat6 __ Cables used on the LO SME. CRL-MCR-001089 applies.
| 02SL - Stations (LUL) | Cxxx-NCR-001586 | NCR | LO SME Platform 5 and 6 - Lux Levels Test Failure |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-09-02 | 2016-09-02 12:42 | 0 | 2016-05-05 09:29 | Electrical - Lighting | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Installed lighting on Platform 5 and 6 failed to reach the Lux levels specified in the LU Baseline standard LU 1-066. These works fall under Sub-construction certificate Cxxx-__M-E-CER-D061-50052 Lighting and Small Power.
| 02SL - Stations (LUL) | Cxxx-NCR-001588 | NCR | DSS Blockwork - Level 5 DR II IWS-622 ghosting |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-04-12 | 2016-04-13 09:19 | 1 | 2016-04-08 16:07 | Architectural - Brickworks/Blockworks | 1500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | Blockwork stained by concrete
| 02SL - Stations (LUL) | Cxxx-NCR-001589 | NCR | Lack of FCD prior to changing specified cable route from E5 to Back of House |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-09-02 | 2016-09-08 12:37 | 6 | 2016-04-26 10:43 | Electrical - Cable Management | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | This NCR has been raised to cover the lack of an FCD which should have been raised before proceeding with the work. This is for a change of cable route to that specified in the published CDS, owing to scaffolding installed blocking the proposed cable route. CDS Reference Cxxx-__M-E-XST-D061_WS106-50018. The cable in question is a 25mm SWA cable running from switchroom E5 to the distribution board in corridor 1/236 Back of House.
| 02SL - Stations (LUL) | Cxxx-NCR-001590 | NCR | LULO - LO SME Works - Gap > 10mm beween GRP Floor Sheet |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-06-12 | 2016-06-10 15:55 | -2 | 2016-04-13 12:28 | Architectural - Flooring | 3000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | During the installation of the GRP false floor in the DSS SME route, it was noted that in some locations, small gaps were present between adjoining GRP sheets. The worst location was a gap of 10mm
| 02SL - Stations (LUL) | Cxxx-NCR-001591 | NCR | LULO - LO SME - Incorrect fixings centres on first fix of fire hoarding |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-08-09 | 2016-07-15 10:48 | -25 | 2016-06-10 14:01 | Architectural - Partitions | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | The fire hoarding in the DSS SME route comprised of __ plasterboard overlaid with __. The ITP noted the fixings centres were to be 600 c/c in the plasterboard and 300 c/c in the __. During the installation of the __, it was noted that a section of the plasterboard had been installed with fixing centres of 685 cc
| 02SL - Stations (LUL) | Cxxx-NCR-001592 | NCR | DSS - W3-03NS |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-03-28 | 2017-03-28 07:33 | 0 | 2016-04-14 14:25 | Shafts - Shafts General | 4000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Personnel Error - Inattention to detail | Completed |  | Reduced cover on couplers/lacers as per attached document. Cover is on stair 1 and 2 side of C3-04.
| 02SL - Stations (LUL) | Cxxx-NCR-001593 | NCR | DSS - Level A Wall WA-07S Cover issues |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-03-28 | 2017-03-28 07:35 | 0 | 2016-04-14 14:24 | Shafts - Shafts General | 4000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Cover issues in wall WA-07S Level A.
| 02SL - Stations (LUL) | Cxxx-NCR-001594 | NCR | DSS - Level B Slab South Parapet Wall Allignment |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-07-21 | 2016-07-21 08:57 | 0 | 2016-04-15 13:21 | Shafts - Shafts General | 2000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | The highlighted parapet within Level B South Slab is out of alignment and is thinner than designed. Please see attached sketches and asbuilts.
| 02SL - Stations (LUL) | Cxxx-NCR-001595 | NCR | LULO - MEP LO SME Platform 5 & 6 lighting. FCD not raised for the change of lighting positions |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-09-01 | 2016-08-17 07:53 | -15 | 2016-04-15 11:30 | Electrical - Lighting | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | This NCR covers the fact that an FCD hasn't been raised to capture a design change. Luminaires (light fittings) have been installed in a position contrary to that stated in the approved design.
| 02SL - Stations (LUL) | Cxxx-NCR-001598 | NCR | DSS - W1-12NS Coupler and Cover Issue |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-11-21 | 2016-11-23 14:18 | 2 | 2016-04-15 16:37 | Shafts - Shafts General | 4000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Supervision - Insufficient supervision | Completed |  | W1-12NS couplers missing and reduced cover within the southern section of the wall.
| 02SL - Stations (LUL) | Cxxx-NCR-001599 | NCR | LULO-MEP LO SME Emergency Exit Signage |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-09-07 | 2016-07-22 15:49 | -47 | 2016-05-10 17:26 | Electrical - Lighting | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | This NCR has been raised because 4 No. Emergency Light Fittings have been installed of a type not specified in the ITP. They should be dual-fed from two separate supplies.
| 02SL - Stations (LUL) | Cxxx-NCR-001600 | NCR | LULO-MEP LO SME Adaptable Boxes not as per MCR type listed in ITP |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-09-07 | 2016-05-16 08:40 | -114 | 2016-05-10 17:07 | Electrical - General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | A non-compliant adaptable box has been fitted on the Platform 5 and 6 in 12 places. The ITP calls for Metpro ABxxG type with a CRL-MCR-001679 approval which is in process and not approved.
| 02SL - Stations (LUL) | Cxxx-NCR-001601 | NCR | Level 6 Blockwork Wall Built In Wrong Position |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-06-07 | 2016-05-25 14:12 | -13 | 2016-04-18 13:01 | Architectural - Brickworks/Blockworks | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | IWS621 wall has been set out incorrectly by 200mm thus reducing the size of lobby 2. Please see attached drawing for reference.
| 02SL - Stations (LUL) | Cxxx-NCR-001603 | NCR | LULO-MEP LO SME luminaires not fitted with a __ Plug and Socket |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-09-08 | 2016-07-06 09:32 | -64 | 2016-05-11 07:40 | Electrical - Lighting | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Insufficient quantity of material to do the job | Completed |  | Luminaires (approx 12 No.) have been hard-wired and not fitted with a __ plug and socket as per the Conceptual Design Statement.
| 02SL - Stations (LUL) | Cxxx-NCR-001604 | NCR | DSS Level 8 - Cleanliness of Structural Blockwork |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-05-29 | 2016-05-05 06:41 | -24 | 2016-04-19 10:22 | Architectural - Brickworks/Blockworks | 1500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Staining from mortar has been removed from blockwork and a result has left residual marking on blocks as shown in photos.
| 02SL - Stations (LUL) | Cxxx-NCR-001605 | NCR | LULO-MEP LO SME Platform 6 Emergency Exit Signage - Hard wired |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-09-08 | 2016-07-05 13:59 | -65 | 2016-05-11 09:23 | Electrical - Lighting | 1200 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Insufficient quantity of material to do the job | Completed |  | The Emergency Exit sign on Platform 6 has been hard-wired instead of being wired-in with __ connectors. See detail 1. on drawing 17868-E03
| 02SL - Stations (LUL) | Cxxx-NCR-001606 | NCR | LULO-MEP LO SME Incorrect SWA glands fitted in open areas |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-09-08 | 2016-07-26 10:03 | -44 | 2016-05-11 09:33 | Electrical - Electrical Engineering General | 4000 |  | Material | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | SWA glands have been fitted with BW type and require to be CW type to ensure the cable gland meets the specified IP rating.
| 02SL - Stations (LUL) | Cxxx-NCR-001607 | NCR | LULO-MEP LO SME SWA Cable rippling in outer sheath in a variety of areas and cable sizes |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-10-31 | 2016-09-19 15:04 | -42 | 2016-05-11 07:16 | Electrical - Cable Management | 2000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | SWA cable in a variety of areas and cable sizes has been installed with a bend-radius within that specifed for the cable type and diameter. However ripples appear in the outer sheath, which could comprise the fire-rating integrity of the sheath.
| 02SL - Stations (LUL) | Cxxx-NCR-001609 | NCR | LULO-MEP LO SME Luminaires on Platforms 5 and 6 have been installed incorrectly. |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-09-07 | 2018-08-14 05:33 | -24 | 2018-05-10 07:32 | Electrical - Lighting | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Superseded by Cxxx-NCR-001586
| 02SL - Stations (LUL) | Cxxx-NCR-001611 | NCR | GSM - Builders Holes - Setting out error on site |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-02-01 | 2017-01-30 09:45 | -2 | 2016-04-21 18:24 | Structural Engineering - Steel Member | 6000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | GSM Building: 2no Builders Holes Works have been set out incorrectly and then cut. As per Cxxx-HYD-S-DDL-D061_WS106_Z-70762 rev P14.1, communicated under PMI 764, 2no holes were to be made in the steel beam along gridline GF, between gridlines G4 and G5. See holes H3 and H4. Setting out information was provided by __ in sketch 10240596-XKA-0612_Rev.3 - attached. There was a setting out mistake as a result of which the holes have been cut in the wrong location. As built survey has been carried out, please see attachments.
| 02SL - Stations (LUL) | Cxxx-NCR-001612 | NCR | LULO-MEP LO SME Incorrect __ current rating fitted |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-09-06 | 2016-08-11 08:54 | -26 | 2016-05-09 09:51 | Electrical - Electrical Engineering General | 1000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | The supplies to the two circuits 110/5 and 110/6 feeding 110v SME socket outlets, have been fitted with 32A __s instead of 16A as specified in the design. There is a conflict of information in the Cat III document as regards to the correct rating of __ to be installed.
| 02SL - Stations (LUL) | Cxxx-NCR-001613 | NCR | Passenger Routeways- Interim Station Works Calibration & Competency Certifcate missing |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-12-18 | 2016-11-29 08:14 | -19 | 2016-10-19 15:28 | Architectural - General | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Training Deficiency - No training provided | Completed |  | Following the compilation of construction records for the Passenger Route ways (Temporary Works - East Stair Shaft Hoarded Tunnels and Platform 1 & 2 Cross Passage) for the Interim Station Works Sub- Construction Certificate - Cxxx-__M-A-CER-D061-50389, it has been identified that calibration & competency certificates are not available for the pull tests conducted. These records relate directly to Construction Records Cxxx-__M-O4-LRC-D061_WS106-50215 (Construction Records – Interim Station Temporary Routeways) and Cxxx-__M-O4-LRC-D061_WS106-50256 (Construction Records – Y-Configuration Works). The missing certificates are deliverable items as stated in the associted ITP's Cxxx-__M-C-ITP-D061_WS106-50093 Rev 2.0 and Cxxx-__M-C-ITP-D061_WS106-50087 Rev 1.0 respectively.
| 02SL - Stations (LUL) | Cxxx-NCR-001614 | NCR | Concrete Cubes lost after LO piling |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-06-24 | 2016-04-26 09:34 | -59 | 2016-04-22 09:10 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper storage of material | Completed |  | 4 cubes were taken while the last pile on LO Platform was poured (Pile P107) on Friday night shift (19/02/2016-20/02/2016). 3 of the cubes had been lost on their way to the lab.
| 02SL - Stations (LUL) | Cxxx-NCR-001616 | NCR | TTH - IRF not raised to invite CRL for inspection of works in the CER Room |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-09-02 | 2016-09-15 10:20 | 13 | 2016-04-27 09:40 | Electrical - Cable Management | 2500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | New CMS has been installed in the TTH CER as part of works required for the Platform 5 and 6 Comms, CCTV and PAVA installation. There was no Inspection Request Form (IRF) raised inviting Crossrail to inspect the works, as specified in the ITP
| 02SL - Stations (LUL) | Cxxx-NCR-001617 | NCR | Omission of Drawpit LPD1-HCDL Platforms |  | Contr | BFK | WHI - Whitechapel Station (Central) |  | 2017-03-31 | 2017-03-29 08:15 | -2 | 2016-04-29 08:35 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | Drawpit LDP1 and the 4 no. ducts were not connected to LDP2 during a possession due to time constraints.
| 02SL - Stations (LUL) | Cxxx-NCR-001619 | NCR | CRL Platforms - GFRP bars installed at incorrect spacings in Platform 014 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-10-01 | 2016-09-16 07:20 | -15 | 2016-04-25 10:30 | Civil - Civil Engineering General | 55000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Contractor is currently constructing the reinforced concrete elements in the Crossrail Platforms. It has been found that the GFRP U bars (Bar Mark 401) in Platform 14 have been installed at 200mm centres rather than the required 100mm centres. Please see marked up detail drawing Cxxx-__M-C-DWG-D061_WS106-53051 which highlights the incorrectly installed bars and location of Platform 014.
| 02SL - Stations (LUL) | Cxxx-NCR-001620 | NCR | CHS - Cantilever Beam No. 5 Reinforcement congestion |  | Contr | MRG | WHI - Whitechapel Station (Central) |  | 2016-07-25 | 2016-05-05 07:23 | -81 | 2016-04-26 15:06 | Civil - Civil Engineering General | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Cantilever Beam No. 5 on the North East Corner of the CHS has had couplers installed in a manner that does not allow reinforcement to be fixed as per Cxxx-__M-C-DWG-D061_WS107-50519-C01.
| 02SL - Stations (LUL) | Cxxx-NCR-001624 | NCR | CHS - A9 slab issues |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-06-06 | 2016-06-01 16:04 | -5 | 2016-04-27 12:42 | Shafts - Shafts General | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | There are several areas of non-conformance with the A9 slab in CHS (See sketches attached): 1) The 4no. BM-37 threaded bars due to be screwed into female __ A12 couplers had to be drilled and fixed, as the couplers were installed too low and the cover would be out of tolerance. It is proposed these bars be drilled and fixed at the correct level. 2) 7no. BM-E07 bars due to be screwed into B16 __ A12 couplers can not be installed as the couplers are located out of position and there will not be enough cover to the edge of the up-stand. It is proposed these bars be drilled and fixed in the correct position. 3) 2no. BM-E24 bars due to be screwed into A12 couplers in the wall can not be installed as the couplers are out of position and will clash with the links of the beam CUB-A-02. It is proposed these two bars are drilled and fixed in the correct position inside the beam. 4) Due to a number of the couplers cast in the Bottom mat of the wall being cast in quite deep, as they were exposed, the edge of the wall was damaged. This has led to some gaps between the edge of the wall and the soffit of the A9 slab. It is proposed that the decking be extended underneath the wall in these locations and the slab poured to fill these gaps. Following the pour, it will be ensured that this joint is tidy and within specified tolerances. Andy remedial works will be carried out as per the making good procedure - Cxxx-__M-C-GPD-D061_50017.
| 02SL - Stations (LUL) | Cxxx-NCR-001625 | NCR | Pile 102 Toe Level & Casing |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-06-27 | 2016-06-18 09:03 | -9 | 2016-04-28 15:06 | Civil - Geotechnical Engineering | 10000 |  | Equipment Breakdown | Use As-Is | 2 (6-60k) | Complete | Subcontractor Problems - Other | Completed |  | The augers were removed from pile 102 due to water being in the bore, prevented material from being flighted and restricting piling progress. Augers removed at 20m (pile design length from PPL = 25.6m). All augers removed at 16:15. Rig breakdown occurred at 16:30. No more piling took place. The borehole was backfilled with type 1 material. The casing was left in position but the top was burnt off to allow LU platform reinstatement. Pile construction timescales: Pile start: 05:50 28/03/16 7.5m of casing installed: approximately 12:00 29/03/16 Pile bored to 20m from PPL of 110.5m : 14:15 29/03/16 Augers removed: 16:15 29/03/16 Rig breakdown: 16:30 all piling work stopped Pile backfilled with type 1 material 30/03/16 Proposed Pile re-commencement 25/06/2016
| 02SL - Stations (LUL) | Cxxx-NCR-001626 | NCR | TTH - SSO Hatch Change From Trespa to Aluminium |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-06-08 | 2016-06-03 08:21 | -5 | 2016-04-29 07:58 | Architectural - Finishes | 4000 |  | Design | Use As-Is | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Due to the hatch in the SSO being too heavy to lift when constructed from __, __ instructed __ to fabricate a further hatch made out of aluminium. This had not been recorded formally.
| 02SL - Stations (LUL) | Cxxx-NCR-001627 | NCR | TTH - CER Room. Non-compliant installation of CMS as a part of Platform 5 and 6 Comms, CCTV and PAVA installation |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-08-27 | 2016-09-15 11:09 | 19 | 2016-04-29 14:20 | Electrical - General | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Non-compliant installation of CMS as a part of Platform 5 and 6 Comms, CCTV and PAVA installation. CMS has been installed as detailed in Cxxx-FCD-001416. This was found to be non-compliant, upon inspection, with the standards specified in the ITP Cxxx-__M-E-ITP-D061_WS106-50020. Also failed to meet the LU standards for cable management and trunking. See attached documents.The attached photographs and comments show the specific failures to comply. Note that the Sub-construction Certificate Cxxx-__M-A-CER-D061-50389 applies to this. (It is an architectural certificate - this is not a typo)
| 02SL - Stations (LUL) | Cxxx-NCR-001628 | NCR | LULO - WSME Civils - Incomplete QA Records - UKAS Certificates |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-06-28 | 2016-06-27 12:30 | -1 | 2016-04-29 10:42 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | UKAS Certificates for the retaining wall works associated with the construction records Cxxx-__M-O4-LRC-D061_WS106-50241 Platform Infill checksheet is missing for works associated with the construction records for Cxxx-__M-O4-LRC-D061_WS106-50242
| 02SL - Stations (LUL) | Cxxx-NCR-001629 | NCR | TTH - Omitted FFE Units |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-06-08 | 2016-05-25 17:29 | -14 | 2016-04-29 16:32 | Architectural - Finishes | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Due to a clash with the SSO Store Room door, LUL/CRL requested __ remove the unit.
| 02SL - Stations (LUL) | Cxxx-NCR-001630 | NCR | TTH - Signage changes |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-06-08 | 2016-05-26 16:49 | -13 | 2016-04-29 16:45 | Architectural - Signage | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Door sign D1/09 says 'Fire Exit Keep Clear' this has been changed to 'Private' at the request of M Roddy and D Stranger so as not to confuse passengers in the event of a fire.
| 02SL - Stations (LUL) | Cxxx-NCR-001631 | NCR | TTH - CER Room. Non-compliant installation of Power Supply for LO SME CCTV Half-rack |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-08-27 | 2016-09-15 15:14 | 19 | 2016-04-29 16:15 | Electrical - General | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Non-compliant installation of the Power Supply and CMS within the TTH CER, as a part of Platform 5 and 6 Comms, CCTV and PAVA installation. Detailed in Cxxx-FCD-001418. This was found to be non-compliant, upon inspection, with the standards specified in the ITP Cxxx-__M-E-ITP-D061_WS106-50005. Also failed to meet the LU standards for cable management and trunking. See attached documents.The attached photographs and comments show the specific failures to comply. Note that the Sub-construction Certificate Cxxx-__M-E-CER-D061-500012 applies to this.
| 02SL - Stations (LUL) | Cxxx-NCR-001632 | NCR | LULO SME MEP Fire Call Point relocated to the wrong location on Platform 1 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-09-13 | 2016-09-14 15:10 | 1 | 2016-05-16 15:26 | Fire - Fire Systems & General | 4000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Personnel Error - Inattention to detail | Completed |  | A Fire call-point was recently moved from a location on the side of the stairs (being demolished in week 3) on Platform 1, to a new location on a hoarding, at the top of the stairs leading to the LO Platform. This position was incorrect (See photograph and this NCR has been raised to cover this non-conformance).
| 02SL - Stations (LUL) | Cxxx-NCR-001634 | NCR | TTH - Floor coating material __ 3M |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-08-18 | 2016-09-08 14:42 | 21 | 2016-05-09 11:49 | Architectural - Flooring | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | TTH: Floor sealing works have been carried out with a code 2 MCR for __ 3M XF 895 Cxxx-__M-A-LRC-D061_WS106-50301. Since then, the MCR has not been resubmitted and acceptance of the product not formally recorded. Please find attached __ endorsement of the product. Following closure of this NCR, the MCR will be resubmitted.
| 02SL - Stations (LUL) | Cxxx-NCR-001635 | NCR | DSS - Transfer Drain Pipes |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-09-09 | 2016-08-02 10:31 | -38 | 2016-05-09 11:05 | Architectural - Brickworks/Blockworks | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | Stainless steel transfer pipe material and installation not included within Blockwork ITP.
| 02SL - Stations (LUL) | Cxxx-NCR-001636 | NCR | Interim Station E12 to E51 Tunnel Transformer Power Distribution Migration |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-09-06 | 2016-09-02 11:44 | -4 | 2016-05-09 16:52 | Electrical - General | 3000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | New CMS and SWA cabling has been installed as part of the works required for the E12 to E51 Tunnel Transformer Migration. There was no Inspection Request Form (IRF) raised inviting Crossrail to inspect the works, as specified in the ITP at the respective Hold and Witness Points. Sub Construction certificate Cxxx-__M-E-CER-D061_WS106-50100 refers.
| 02SL - Stations (LUL) | Cxxx-NCR-001637 | NCR | TTH CER Half-rack CCTV/Door Alarm incorrect cable routing |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-09-07 | 2016-09-06 12:40 | -1 | 2016-05-10 12:47 | Electrical - Electrical Engineering General | 1500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | It has been found that the power supply to the LO CCTV wall rack is also feeding the Door Alarm equipment via the CCTV PSU. The power cable to the Door Alarm equipment is routed through the Comms CMS trunking. Regulations state that power cables are to be segregated from Communications cables.
| 02SL - Stations (LUL) | Cxxx-NCR-001638 | NCR | HCDL Platform - Change in Direction of Aco Drain Connection Pipework into MH04 |  | Contr | BFK | WHI - Whitechapel Station (Central) |  | 2016-09-30 | 2016-07-19 13:29 | -73 | 2016-05-10 13:45 | Civil - Drainage | 3000 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | This NCR was raised due to a change in pipework direction was not captured with an FCD during the construction phase. While constructing the Aco Drainage back drop pipework connection into MH04 the orientation was changed. This was due to the existing site layout and limited clearance due to close proximity of retaining platform wall and hoarding line.
| 02SL - Stations (LUL) | Cxxx-NCR-001639 | NCR | ETH Front of House Compound - Gantry Frame Fabrication Error |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-06-21 | 2016-06-10 15:58 | -11 | 2016-05-12 09:07 | Civil - Civil Engineering General | 3000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Construction of the gantry frame outside the Existing Ticket Hall (ETH) has nearly been completed. Whilst reviewing the structure it was noticed that the splice on the runway beam was not in the location stipulated on the original CATIII design. It has been fabricated and therefore constructed 1 metre out of position leaving one section cantilevered. Further to this, one beam has no connection detail and durbar plates have been welded within their surface area. The fabrication drawings produced by the manufacture Environmental Fabrications Ltd. also show the error, meaning this was due to incorrect replication of the original CATIII drawings. These fabrication drawings were reviewed by members of Environmental Fabrications, __ and the __ Temporary Works Team, but the mistake was not spotted.
| 02SL - Stations (LUL) | Cxxx-NCR-001640 | NCR | CHS - A8 slab issues |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-06-20 | 2016-06-15 08:34 | -5 | 2016-05-11 16:12 | Shafts - Shafts General | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The are several reinforcement issues with the A8 slab in CHS: All proposals are as per previous email correspondence with Cxxx. 1) BM-21 in CUB-A11 is 400mm high in a 550mm high beam. This means there is 100mm cover to the top. It is proposed that we lay some extra bars on top to make up the extra 50mm. 2) There is 1no. coupler missing in the bottom mat, half way along W1-25s. It is proposed this bar (BM-19) is drilled and fixed to a depth of 200mm with __-hit 200 3) There is not enough cover on the Eastern face of CUB-A-08 (around 25mm). It is proposed that this face be coated with Intercrete 4841 once the concrete has cured and the side shutters are struck. See MCR-Cxxx-__M-C-LRC-D061_WS106-50169 attached.
| 02SL - Stations (LUL) | Cxxx-NCR-001641 | NCR | Blockwork Lintel Schedule/Specification Discrepancy |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-11-15 | 2021-10-14 12:08 | -32 | 2021-10-06 14:52 | Architectural - Brickworks/Blockworks | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Subcontractor orders lintels as per Blockwork Opening Schedule Cxxx-__M-C-TSC-D061_WS105-50001. The lintel schedule that is used by the Subcontractor has detailed __ Doorway Lintels to have a __ Type reference of 'Type 33'. __ Type 33 dimensions are 215 x 140mm with a 140 minute fire rating. The Blockwork Specification details a __ to a__ Type 32S lintel with a cross section of 200x215mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001642 | NCR | DSS - CB-38 Honeycombing |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-11-12 | 2016-11-11 15:32 | -1 | 2016-05-16 14:41 | Shafts - Shafts General | 4000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Honeycombing of the concrete has occurred at the base of CB-38.
| 02SL - Stations (LUL) | Cxxx-NCR-001643 | NCR | DSS - C1-08 Kicker Alignment |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-11-12 | 2016-08-04 07:19 | -100 | 2016-05-16 15:03 | Shafts - Shafts General | 3500 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Personnel Error - Not Defined | Completed |  | Column C1-08 kicker was poured out of designed alignment.
| 02SL - Stations (LUL) | Cxxx-NCR-001644 | NCR | Interim Station MEP - Junction boxes installled without an approved MCR |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-10-23 | 2018-05-29 17:04 | -147 | 2018-05-16 08:47 | Electrical - General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Junction Boxes have been installed on the Tunnel Transformer Power to E51 Switch Room circuit, without an approved MCR.
| 02SL - Stations (LUL) | Cxxx-NCR-001645 | NCR | NCR - Damage to existing CMS cable tray in the disused road |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-09-15 | 2016-08-10 07:49 | -36 | 2016-05-18 16:25 | Electrical - Cable Management | 2000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | Existing CMS, comprising a cable-tray and 2 no. conduits have been damaged by a plant operator, whilst moving bulk bags underneath the GSM. The incident was not reported to the MEP Team Leader or the team leader of the operative at the time of the occurrance. This NCR has been raised because of the failure to follow procedures and report the incident at the time it happened.
| 02SL - Stations (LUL) | Cxxx-NCR-001646 | NCR | LULO - __ - Upper Concourse Steelwork - Welding being carried out without an approved weld procedure specification (C-50289) |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-09-01 | 2017-01-03 13:39 | 124 | 2016-05-19 11:40 | Civil - Structural Engineering | 4000 |  | Documentation and Records | Rework | 3 (3-6k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | During a Surveillance activity undertaken by __ at __s's factory in __ the following was found. Beam no. 20536 has a butt weld connecting the three RHS sections together. On the drawing this weld is detailed as being a single bevel butt weld with no backing, however on the shop floor the weld was being fitted up using a steel backing strip. __ does not have a CRL approved weld procedure specification this weld detail with a backing strip.
| 02SL - Stations (LUL) | Cxxx-NCR-001647 | NCR | Temporary Ticket Hall Drainage-Combined Sewer Relocation |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-11-14 | 2016-11-14 21:41 | 0 | 2016-06-08 10:23 | Civil - Drainage | 1500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | The Combined Sewer Manhole positioned on the east side of the Temporary Ticket Hall was relocated onto Court Street as per drawing Cxxx-__M-C-DWG-D061-50132 C02 (attached). __ raised a PTR to __ who accepted the relocation of the manhole (see PTR 046 attached) however failed to communicate this information to CRL via the correct procedure by raising the relevant Project Technical Request (PTR) to CRL. Moreover the drawing had not been submitted onto eB and therefore was not available to CRL. Please note drawing since uploaded to eB.
| 02SL - Stations (LUL) | Cxxx-NCR-001649 | NCR | LO SME - CCTV Blind Spot on Platform 6 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-06-10 | 2016-06-10 07:34 | 0 | 2016-05-23 11:25 | Communications and Control Systems - CCTV | 2000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | NCR raised because on LO Platform 6 SME entrance, there is a CCTV blind spot created by the erection of hoarding. The SME blind spot measures 2.1m x 2.7m which exceedes the LU specified area of 4m sq.
| 02SL - Stations (LUL) | Cxxx-NCR-001650 | NCR | CHS Level 8 Wall W8-01s |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-07-03 | 2016-05-31 16:16 | -33 | 2016-05-24 08:07 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Insufficient quantity of material to do the job | Completed |  | This NCR is in regards to the CHS concrete pours down at level 8. Wall W8-01s has been poured with a C32/40 mix, however the specification requires a C40/50 concrete mix. The wall has been poured from 82.44 SSL to 84.9 SSL From data received of this concrete, it has already achieved a 43.8 compressive strength at 28 days. It would be our proposal to leave this as it is. For further works, the correct concrete mix will be used.
| 02SL - Stations (LUL) | Cxxx-NCR-001651 | NCR | CHS Level 8 Cranked Slab Couplers |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-07-02 | 2016-06-30 09:58 | -2 | 2016-05-23 13:39 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | This NCR is in regards to the cranked slab reinforcement at level 8. Having broken down the exterior concrete to expose couplers within column C8-06, there is one coupler that has been installed into the western face. The attached drawing and __ for cranked slab and the column requires 2 couplers in place at this location. To resolve this issue I would like to propose a drill and fix solution at this location.
| 02SL - Stations (LUL) | Cxxx-NCR-001653 | NCR | Riser 4 CHS Square washer Packers |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-08-04 | 2016-07-28 15:40 | -7 | 2016-05-23 16:22 | Electrical - Cable Management | 6000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Previous Construction - Problems based on previous construction errors | Completed |  | Used square washers to pack out unistrut Channel on uneven wall.
| 02SL - Stations (LUL) | Cxxx-NCR-001655 | NCR | DSS & CHS MEP Works - CMS Installation - use of chemical anchors in soffits |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-01-19 | 2016-12-14 08:48 | -36 | 2016-05-23 21:36 | Electrical - Cable Management | 20000 |  | Material | Repair | 2 (6-60k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | __ have installed chemical anchors to the concrete slab soffits in CHS and DSS in a number of locations
| 02SL - Stations (LUL) | Cxxx-NCR-001656 | NCR | Y Configuration Works proceeding without LONO or Cat III document |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-09-21 | 2016-09-05 14:53 | -16 | 2016-05-24 13:21 | Electrical - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Installation works has commenced on platform 1 WB of CMS for the Y configuration walkways, however, the documentation required to carry out the works is not current. A LONO, and CAT III document are still required from LU before work commences.
| 02SL - Stations (LUL) | Cxxx-NCR-001657 | NCR | Crossrail Platforms - PLAT 015 Westbound Trackbed Wall Penetrations |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-07-04 | 2016-06-29 09:06 | -5 | 2016-05-25 13:22 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 2 No. Trackbed Wall Penetrations are installed 25mm too low. See sketch attached which details penetrations impacted.
| 02SL - Stations (LUL) | Cxxx-NCR-001659 | NCR | Platform 5 and 6 Temporary LO SME works - Missing cube results |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-08-27 | 2016-08-25 13:16 | -2 | 2016-07-18 10:05 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | During the week 53 Possession, some concrete was placed for the temporary works on platform 5 and 6. This included the infill ramp and concrete infills following the SME removal. The concrete records were taken, but the cubes taken have since been misplaced and no results have been recieved. Note, these works are temporary and will be replaced at a later date
| 02SL - Stations (LUL) | Cxxx-NCR-001660 | NCR | CHS - Cast in items at level 1 (Cxxx-__M-C-CER-D061-50235) |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-02-15 | 2018-02-07 16:07 | -8 | 2016-05-27 15:43 | Shafts - Shafts General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A number of cast in items have been erroneously omitted from some RC elements at level 1 in CHS. These include the following: 1) Wall ties cast into W1-23 to enable the glazed blockwork to be ties to the outside of the wall. 2) 5no. __ 21/18 channels cat into W1-23 and W1-22 to enable blockwork walls to be tied to the RC structure. 3) __ 28/15 channels cast into a 4m length of W1-23 at the NE end. 4) 3no. __ HD anchor pulling points cast into the fin slab. See sketch attached for location of channels. An RFI has been raised to __ to propose alternative installation methods for each of the above items. Once the response is received, this NCR will be updated with the proposed solutions. The RFI has been received (See attached) and the response is as follows: 1) Use __ SDB cramps, fixed with __ M6 single expansion bolts 2) Use __ SDV cramps 3) Use __ SDV cramps 4) Install post drilled and fixed pulling point as per drg. no. 10506 (attached) Following discussions with CRL, to enable close out of this NCR, the ITP for blockwork must be revised to include these new fixings. These works are scheduled for March 2017.
| 02SL - Stations (LUL) | Cxxx-NCR-001661 | NCR | CHS - Level A - CUB-A-07 out of tollerance |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-09-02 | 2016-08-31 13:52 | -2 | 2016-06-02 08:58 | Shafts - Shafts General | 1000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | At Cambridge Heath Shaft Level A, the upstand beam on slab A9 (CUB-A-07) is out of tollerance. The survey shows the that the beam is out of positional tollerance in 3 areas (see attached). __ propose to use as is. Conformation from __ will be sought to ensure no sucessive works will be affected. 18/08/2016 Please see __ response to RFI-1419 and marked up sketch __ have confirmed the CUB-A-07 upstand can remain as is, as long as the following changes are made to the architectural works. 1. Where deviation is up to 37mm outwards, the cavity width can be reduced to 50mm minimum, and the SS angle under coping reduced in width from 65mm to 50mm. 2. Where deviation is upto 27mm inwards, the bullnose coping to be increased in width to 500mm and this width to be maintained along the full length of the parapet. 3. Cavity wall tie lengths to be adjusted to suit reduced or increased cavity widths. 4. External curved appearance of the glazed wall to be maintained at a constant radius throughout, as per the design setting-out requirements.
| 02SL - Stations (LUL) | Cxxx-NCR-001663 | NCR | Interim Station MEP - Cable installed with non-compliant bend radius |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-10-22 | 2019-04-03 14:07 | 163 | 2018-05-15 08:03 | Electrical - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | SWA cables have been installed in E51 Switch Room feeding the Tunnel Power Supply with a bending radius smaller than that recommended by the manufacturer.
| 02SL - Stations (LUL) | Cxxx-NCR-001664 | NCR | CHS Wall W8-06s missing couplers for starter bar |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-09-30 | 2016-07-25 09:09 | -67 | 2016-06-03 13:18 | Civil - Civil Engineering General | 1539 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | This NCR is in relation to the level 8 Wall W8-06s. For the W8-06s wall at level 8, 20 couplers are required to be pre cast into the base slab to allow for the wall starter bars to be correctly installed, see attached drawing and mark ups. When breaking out the base slab concrete, 12 couplers were found on the north and east faces however the 8 on the west face (close to the liner wall) have not been found to be installed. To correct this, it is proposed for a drill and fix solution of B16 bars at the same spacing (250mm) of the original couplers to an embedment depth of 320mm using __ HY200.
| 02SL - Stations (LUL) | Cxxx-NCR-001665 | NCR | CHS - voids between liner walls and ring beams |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-08-01 | 2017-08-22 09:13 | 21 | 2016-06-03 14:38 | Shafts - Shafts General | 10000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In CHS, during excavation of the shaft 3no. ring beams were poured to support the diaphragm walls. Liner walls were then poured between these ring beams using self compacting concrete. Since the SCC was poured to the underside of the ring beams a small void was left where it didn't quite reach fill the whole area. NCR-1058 was originally raised to cover this non-conformance however following access constraints due to programme requirements and a number of extensions NCR-1058 was required to be closed. Two areas of liner wall were closed out at this time. This NCR (NCR-1665) was raised to cover the remaining areas of voids still requiring to be made good as per the original NCR. It is proposed these on-going remedial works will be completed as per the method outlined in the original NCR (see attached)
| 02SL - Stations (LUL) | Cxxx-NCR-001668 | NCR | DSS - Offsite Fabrication - __ Pre Start Documentation - Precast Concrete Cladding (__) |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-10-14 | 2016-10-07 07:54 | -7 | 2016-06-20 08:37 | Architectural - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | A number of key control documents required for the fabrication of the DSS precast concrete cladding panels were not in place prior to fabrication. The are as follows 1. Inspection Test Plan - Offsite fabrication of the brackets (__) 2. Weld Procedures - __ 3. Material Compliance Record - __ Brackets
| 02SL - Stations (LUL) | Cxxx-NCR-001669 | NCR | DSS - Offsite Fabrication - Pre Start Documentation (CFS) - Precast Concrete Cladding (__) |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-10-14 | 2016-10-07 08:51 | -7 | 2016-06-20 08:47 | Architectural - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | A number of key control documents required for the fabrication of the DSS precast concrete cladding panels were not in place prior to fabrication. The are as follows 1. Inspection Test Plan - Offsite fabrication of the brackets (CFS) 2. Weld Procedures - CFS 3. Material Compliance Record - CFS
| 02SL - Stations (LUL) | Cxxx-NCR-001670 | NCR | Lack of an approved ITP for Earthing and Bonding on the Concourse Steelwork |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-12-30 | 2016-12-15 10:09 | -15 | 2016-06-22 15:27 | Electrical - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | The main station Concourse steelwork structure is required to have individual bonding straps fitted between adjacent sections of steel. This is to provide a satisfactory conductive path for earth bonding. The work has commenced without an approved ITP for the works
| 02SL - Stations (LUL) | Cxxx-NCR-001671 | NCR | Lack of MCR for Earthing Pins fitted to Concourse Steelwork |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-04-30 | 2017-02-09 15:53 | -80 | 2016-06-20 13:06 | Electrical - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Not Defined | Completed |  | __ fixings have been used for earthing and bonding the concourse steelwork, without an approved MCR being place prior to works commencing.
| 02SL - Stations (LUL) | Cxxx-NCR-001672 | NCR | LO SME - NCR for lack of replacement CCTV Camera to cover Platform 6 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-08-28 | 2016-08-11 07:13 | -17 | 2016-06-21 13:54 | Communications and Control Systems - CCTV | 3000 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | A CCTV Blind Spot on LO Platform 6 was corrected using a new camera. ( Cxxx-NCR-001649) .This new camera utilised the existing Camera 59 network connection (with the actual Camera 59 being taken out of service) to bring the new camera into operation quickly. The withdrawn camera 59 was to be replaced within one week, but this hasn't taken place within the specified time so this NCR has been raised.
| 02SL - Stations (LUL) | Cxxx-NCR-001673 | NCR | DSS - Western Elevation Level 1 Brackets |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-11-25 | 2016-11-14 12:01 | -11 | 2016-06-23 14:46 | Shafts - Shafts General | 8659 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Grid Line 4 Wall is out of tolerance. Affecting the installation of PCC Panels.
| 02SL - Stations (LUL) | Cxxx-NCR-001674 | NCR | __ finish exceeding thickness tolerance on section of benchmark above platform 6 and above LO tracks |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-09-01 | 2016-08-25 13:22 | -7 | 2016-06-27 02:29 | Architectural - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The tolerance specified in Cxxx-__M-A-RSP-D061-50079 states "the finished surface shall avoid sudden irregularities and be +/-1mm in any 2000mm". Prior to the spraying of the benchmark, __ raised this as unachievable and a -0 / +10mm was agreed upon and signed off in the ITP for the works (this topic is covered in Cxxx-FCD-001522). However, the __ finish on the section of the benchmark that was sprayed with __ on the 18th and 19th of June (i.e. above platform 6 and above LO tracks) has exceeded this. Attached measurement sheets show thicknesses in excess of 30mm were measured in some locations.
| 02SL - Stations (LUL) | Cxxx-NCR-001675 | NCR | DSS - Pier 6 Kicker Error |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-12-10 | 2016-12-01 09:48 | -9 | 2016-06-27 11:37 | Shafts - Shafts General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Pier 6 kicker was installed and cast incorrectly.
| 02SL - Stations (LUL) | Cxxx-NCR-001676 | NCR | DSS - Pier 6 Additional Construction Joint |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-08-06 | 2016-07-25 09:13 | -12 | 2016-06-27 12:16 | Shafts - Shafts General | 3059 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During stage 3 concrete pour of Pier 6, the pier was poured low.
| 02SL - Stations (LUL) | Cxxx-NCR-001677 | NCR | Interim Station MEP - Phase 9, Y Configuation, FCD not raised for relocation of Cameras and PAVA Speakers |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-09-02 | 2016-09-08 08:11 | 6 | 2016-06-28 07:40 | Communications and Control Systems - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | This NCR covers the fact that an FCD should have been raised to cover the change of CCTV camera and PAVA Speaker locations within the Y Configuration (Phase 9) of the Interim Station works, owing to the Cross-Passage remaining open.
| 02SL - Stations (LUL) | Cxxx-NCR-001678 | NCR | Crossrail Platforms - Low cover in localised area on top steel of Track Bed Eastbound TB 214/5 construction joint |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-08-16 | 2016-08-15 15:08 | -1 | 2016-06-29 15:16 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | At the construction joint of Eastbound trackbed 214/5 there is a localised area of low cover to the top steel. Cover to the top mat in the worst place is 25mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001679 | NCR | PES Plenum - Westbound West End Condition |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-11-17 | 2016-11-17 16:29 | 0 | 2016-06-28 13:41 | Architectural - General | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The PES was assured as part of the Platforms Early Assurance Package, Gate Pass Certificate Reference Cxxx-XRL-O-CER-CRG02-50026. Drawing Cxxx-__M-A-DDA-D061_WS106_7-22009 was part of the package and shows the Westbound tunnel diverging at the West end of the PES. The IFC drawing shows the standard PES module and the dimension to the tunnel structure. At the time of issue it was assumed that this was sufficent information for the F2 design, however when undertaking the detailed F2 design more information was required. The PES should be aligned to the tunnel showing the dimension that each module is to be extended by, this also requires structural verification by Cxxx before the F2 design can be completed.
| 02SL - Stations (LUL) | Cxxx-NCR-001680 | NCR | LULO – Phase 8 Steelwork – GL 22, Fin Plates Welded Incorrectly on Upper Concourse |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-11-01 | 2016-11-01 13:09 | 0 | 2016-07-04 14:22 | Structural Engineering - Steel Member | 3000 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | This NCR is written on behalf of __ In the main cross beam (BM 20501) on GL 22, the 6no fin plates in the middle section of the main beam have been welded to an incorrect slope. A minor design change has been produced to enable a revised connection to be used. The 6no. end connection for the longitudinal plan roof bracing members have been modified to fit the incorrectly welded fin plates in the main cross beam Pls conform this is acceptable
| 02SL - Stations (LUL) | Cxxx-NCR-001683 | NCR | DSS - Pier 2, 3 & 5 incorrect Height |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-08-08 | 2016-07-25 13:09 | -14 | 2016-06-29 13:01 | Shafts - Shafts General | 1350 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The height of piers 2, 3 & 5 is incorrect.
| 02SL - Stations (LUL) | Cxxx-NCR-001684 | NCR | Platform Tunnels, PES __ fixings - incorrect drilling locations GL5 and GL13 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-08-21 | 2016-08-18 14:55 | -3 | 2016-06-29 14:23 | Civil - Structural Engineering | 6000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The PES head bracket fixings are drilled in sets of 4 using a drilling jig to correctly set out location and spacings. The centre of each set of fixings is marked on the platform nosing, and a laser is set out, which beams a crosshair onto the tunnel crown. This is used to align the drilling jig and drill the holes for the fixings. For WB GL5 and GL13 (setting out drawing 53113), the sets of holes have been drilled incorrectly at 54mm and 60mm respectively along the tunnel chainage to full depth (195mm).
| 02SL - Stations (LUL) | Cxxx-NCR-001685 | NCR | Platform Tunnels - Position of internal wall penetration platform 006 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-08-22 | 2016-07-19 15:11 | -34 | 2016-07-05 10:14 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The penetration in internal wall platform 006 is out of position by 125mm in chainage. Level is within allowable tolerances. The penetration is at: Chainage 10343.960 to 10344.860 as opposed to: Chainage 10344.084 to 10344.984
| 02SL - Stations (LUL) | Cxxx-NCR-001686 | NCR | LULO - MEP - Y Configuration Lux Levels failed to meet LU standard A2 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-11-02 | 2016-07-06 09:20 | -119 | 2016-07-05 09:14 | Electrical - Lighting | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Platform 1 lux levels for the Y configuration have failed in places, to reach the baseline standard of LU standard 1-066 A2 and the design. They meet the requirements of revision A4 of this standard, but the design is to revision A2 and hence non-compliant. CRL Observation CRL-OBS-10906 refers.
| 02SL - Stations (LUL) | Cxxx-NCR-001687 | NCR | ETH - Front of House Compound Concrete Testing Results |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-09-05 | 2016-09-05 13:51 | 0 | 2016-07-07 15:30 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | On the 20/02/2016 concrete was poured to form the last section of the front of house compound slab. The cubes were taken for the pour, but no record of them can be found at the testing facility or on site meaning there are no crush test results. The full compound slab was poured in 3 stages. The first two reached 50.5N/mm2 and 40.7N/mm2 respectively. The area is not under the hoists area for potential drop load (see attachment).
| 02SL - Stations (LUL) | Cxxx-NCR-001688 | NCR | LO RC infill - incorrect rebar diameter |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-07-25 | 2016-07-20 14:15 | -5 | 2016-07-11 03:59 | Civil - Structural Engineering | 1500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Not Defined | Completed |  | With reference to Cxxx-RFI-003392 & Cxxx-RFI-003493: - The LO infill at Grid Line 1 is 540mm deep (wall thickness), all others are 680mm deep. - This difference in as-found condition was queried in Cxxx-RFI-003493, with the response instructing that the wall reinforcement change from B16@150 to B20@150 (corbel and shear key rebar to remain as is). - When marking up the BSS for the supplier for the different wall dimensions, the engineer failed to change the B16s to B20s. This mistake was only noticed after the infill had been poured.
| 02SL - Stations (LUL) | Cxxx-NCR-001689 | NCR | TTH - Mechanical Plant Interface Panel (MPIP) failed to meet the published performance specification |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-03-31 | 2017-03-24 09:03 | -7 | 2016-07-15 10:57 | Mechanical - Heating Ventilation & Air Conditioning | 5900 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | The Mechanical Plant Interface Panel (MPIP) has been installed in the TTH, but doesn't show the correct information from the mechanical plant it monitors as specified in Temporary Ticket Hall (TTH) Mechanical & Public Health Services Specification.
| 02SL - Stations (LUL) | Cxxx-NCR-001691 | NCR | LULO - MEP Y Configuration Phase 9 - lux levels non-compliant on platform 1 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-08-28 | 2016-07-22 13:11 | -37 | 2016-07-19 08:16 | Electrical - Lighting | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Platform 1 lux levels for the Y configuration have failed in places, to reach the baseline standard of LU standard 1-066 A2 and the design. They meet the requirements of revision A4 of this standard, but the design is to revision A2 and hence non-compliant. (Note that there is another similar NCR, Cxxx-NCR-001686 (now closed) for Y Config Lux levels)
| 02SL - Stations (LUL) | Cxxx-NCR-001692 | NCR | CHS Riser CMS Clash |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-02-23 | 2016-12-22 15:04 | -63 | 2016-07-20 08:37 | Electrical - Cable Management | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Riser steel and CMS clash. CMS installed prior to Riser steel from scaffolding to mitigate delay caused by late riser floor installation. CMS set out to the C rev CMS drawings and checked against the riser penetrations shown on steel drawings. Clash caused by the CMS drawings do not include for support unistrut brackets and steel work drawings did not include angle support brackets for beams.
| 02SL - Stations (LUL) | Cxxx-NCR-001693 | NCR | DSS - Level 5 - Blockwork - SRLV I joint out of tolerance |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-09-30 | 2016-09-30 16:18 | 0 | 2016-07-25 10:21 | Architectural - Brickworks/Blockworks | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Corner joint of perimeter and IWS-621 of Riser A has been constructed out of specified tolerance. Joint starts at the bottom at 10mm, increasing to a maximum of 45mm before reverting at the soffit to 15mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001694 | NCR | LULO Steelwork Installation- Phase 6 Cranked Beam |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2016-09-14 | 2016-11-17 13:31 | 64 | 2016-07-21 15:02 | Structural Engineering - Steel Member | 5000 |  | Manufacturing Defect | Repair | 3 (3-6k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | The western base plate of the cranked beam (mark 11214) clashes with the base plate of the already installed northern crank beam of Durward Street Bridge. The base plate (P11235) was trimmed by 15mm to enable installation of the cranked beam. This change was captured by MDC Cxxx-__M-C-CER-D061_WS106-53169, which provided assurance for temporary stability.
| 02SL - Stations (LUL) | Cxxx-NCR-001697 | NCR | LULO- GSM Building Internal Blockwork |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2016-12-09 | 2016-12-02 12:10 | -7 | 2016-07-21 16:36 | Architectural - Brickworks/Blockworks | 20000 |  | Supervision/Management | Rework | 2 (6-60k) | Complete | Management Problem - Other | Completed |  | As per Cxxx-HYD-S-DDB-D061_WS106_Z-70752, and Cxxx-HYD-S-DDB-D061_WS106_Z-70753, the East, South, and West facade walls of the GSM building were to be retained. The wall tiles which to be stripped off the walls were taken off using power tools, not hand tools as required. This has led to significant damage to the blocks. As per site walk 20.07.16 (between CRL, Cxxx & __), Cxxx have identified which blocks are to be replaced. Other blocks may be retained pending survey post removal of damaged blocks.
| 02SL - Stations (LUL) | Cxxx-NCR-001698 | NCR | CRL Platforms - Wesbound TB203 pour |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-08-31 | 2016-08-24 11:41 | -7 | 2016-07-22 15:55 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Due to an incident with the concrete pump the lower track slab pour TB203 in the Westbound tunnel had to be abandoned and is therefore incomplete. It is proposed that the pour is left as in from Chainage 10314.264 to approximately Chainage 10328. Steel in the upper track slab pour will be constructed as per design. Additional dowels will be fixed into the slab to ensure the steel can be installed to the correct height. A stop end will be installed at approximately Chainage 10328 and the remaining track slab TB203 will be poured with TB202. Any loose concrete will be removed and the area jet washed. The concrete will be stepped and scabbled accordingly. A dowel will be installed on every step at 1m spacings. The upper track slab steel will be installed as per design. An as-built survey and photographs will be included in the close out of this NCR.
| 02SL - Stations (LUL) | Cxxx-NCR-001699 | NCR | West Stair Shaft- Non UKAS accredited lab used for testing concrete poured for props installation |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-09-30 | 2016-09-29 15:36 | -1 | 2016-08-01 10:42 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | As part of the West Stair Shaft works two 400mm diameter permanent precast props were fabricated off site by __ to be installed in the upper level of the West Stair Shaft by __. During the compilation of the Construction Records as part of the Self Certification process, it has been observed that the records for the Compressive Strength results of the concrete used to cast the respective props has been produced by __ who do not have a UKAS accredited laboratory. __ was contracted to have the tests carried out by an independent UKAS accredited laboratory. The cubes were tested by __ in their own lab using calibrated testing equipment and all results achieved satisfactory results of 66N/mm2 (average) after 28 days. The mix requirement is 50N/mm2.
| 02SL - Stations (LUL) | Cxxx-NCR-001700 | NCR | TTH - CER Room. Drawings, in rack cabinet, don't reflect what is installed |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-10-31 | 2016-09-13 14:00 | -48 | 2016-07-25 13:27 | Communications and Control Systems - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The schematic diagram affixed on the inside door of the PAVA cabinet doesn't represent the current installation of equipment and cabling.
| 02SL - Stations (LUL) | Cxxx-NCR-001701 | NCR | TTH - CER. Cables within CCTV rack need to be dressed |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-09-03 | 2016-09-07 14:48 | 4 | 2016-07-25 10:59 | Communications and Control Systems - General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Cables within the CCTV racking in the TTH CER Room, are not dressed and hanging loose in the back of the cabinet.
| 02SL - Stations (LUL) | Cxxx-NCR-001702 | NCR | DSS - P1 & P2 sockets cast out of position |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-10-24 | 2016-10-07 08:56 | -17 | 2016-07-26 14:40 | Shafts - Shafts General | 1589 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | M16 sockets in base of units should be set at 140 mm from front face of PCC unit, sockets have been cast 75 mm from face as earlier revision drawing detailed before corbel was added to the drawing
| 02SL - Stations (LUL) | Cxxx-NCR-001703 | NCR | DSS - P52, P53, P54A, P61A and P62C |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-05-30 | 2017-05-20 08:56 | -10 | 2016-07-26 16:07 | Shafts - Shafts General | 7000 |  | Design | Repair | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Cast in sockets used to restrain panels back to RC walls have been designed in the wrong location
| 02SL - Stations (LUL) | Cxxx-NCR-001704 | NCR | Incorrect depth for phase 7 steelwork anchor on Winthrop Street |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-10-14 | 2016-09-13 08:53 | -31 | 2016-07-27 02:02 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | The northernmost of the four anchors of the easternmost of the four phase 7 columns in Winthrop street could not be drilled to depth. Depth of the anchor is 125mm instead of the required 250mm. Please see attached drawing with mark-up.
| 02SL - Stations (LUL) | Cxxx-NCR-001706 | NCR | DSS - Fire Main Bracket |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-12-30 | 2016-11-06 20:35 | -54 | 2016-07-27 11:42 | Shafts - Shafts General | 2085 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Fire Main Brackets have not been installed with two no rows as per CAT III design due to hitting reinforcement.
| 02SL - Stations (LUL) | Cxxx-NCR-001708 | NCR | DSS - Piers 1 - 6 Special Finish Specification Issues |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2021-11-05 17:12 | 493 | 2016-07-27 12:27 | Shafts - Shafts General | 14000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Counterfeit Items | Completed |  | Plywood formwork joints not aligned through on front and adjacent sides of the piers, also on some of the piers the angle fillet (chamfer battens) have some gaps / discrepancies along the edges / corners of the piers.
| 02SL - Stations (LUL) | Cxxx-NCR-001709 | NCR | CHS-Lift shaft walls out of tollerance level 7 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-11-25 | 2016-08-07 11:00 | -110 | 2016-07-28 08:45 | Shafts - Shafts General | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In Cambridge Heat Shaft on Level 7, two walls which form the lift shaft (W7-13 and W7-06) have been found to be out of tollerance. As-built survey shows that part of the wall is out of tollerance. See attached as-built drawings. __ propose to use it as it is. Confirmation from __ and lift designer will be required to insure that it will not effect lift installation.
| 02SL - Stations (LUL) | Cxxx-NCR-001710 | NCR | DSS - ITP Torque Values Incorrect |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-10-25 | 2016-08-30 10:47 | -56 | 2016-07-27 16:01 | Shafts - Shafts General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | Torque value on DSS Bracket Support and Restarint Fixing for Cladding Panel is incorrect. Value states 6kN for M12 and M20 fixings.
| 02SL - Stations (LUL) | Cxxx-NCR-001711 | NCR | DSS - Drainage Channel Waterproofing ITP |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-09-06 | 2016-08-02 10:20 | -35 | 2016-07-28 15:23 | Shafts - Shafts General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | Incomplete revision of DSS Drainage Channel Waterproofing ITP document submitted to eB and put in use.
| 02SL - Stations (LUL) | Cxxx-NCR-001712 | NCR | DSS - DSS/LO Pl 6 Wall - All Purpose Band - Use of Non Approved Material |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-04-05 | 2017-03-16 15:31 | -20 | 2016-07-28 13:41 | Electrical - Cable Management | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | All Purpose Band used to fix flexible conduits to DSS external west elevation wall.
| 02SL - Stations (LUL) | Cxxx-NCR-001713 | NCR | LULO - GSM - Incorrect Primer to Secondary Steel Beams |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-10-20 | 2016-10-11 15:22 | -9 | 2016-07-28 14:24 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | 3no secondary beams had been painted with __ Epigrip C400V3 instead of Interseal 670HS. This was then painted over with Interseal 670HS when touch dry.
| 02SL - Stations (LUL) | Cxxx-NCR-001715 | NCR | CRL Platforms - Westbound Nosing __ Channel Position |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-09-29 | 2017-09-13 07:35 | -16 | 2016-07-29 16:14 | Civil - Civil Engineering General | 3000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please see attached the final Platform Screen Door (PSD) __ channel survey for the platform nosing. The survey has been done in the locations of the fixings. The spread sheet attached highlights the out of tolerance areas. The survey has found the following; • 15 locations where the halfen channel is out of tolerance • 7 locations where the spacing between the halfen channel is out of tolerance
| 02SL - Stations (LUL) | Cxxx-NCR-001716 | NCR | CRL Platforms - TB201 Lower pour |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-09-10 | 2016-08-25 11:34 | -16 | 2016-08-01 06:22 | Civil - Civil Engineering General | 3000 |  | Equipment Breakdown | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Due to __'s batching plant breaking down on Saturday 30th July 2016, Track bed pour TB201 (lower pour) had to be abandoned after 3 loads. The pour is therefore incomplete. Attached are photographs of the pour once the remedial works were completed on Saturday nightshift. The horizontal construction joint has been scabbled and dowels installed at 1m spacing's. Attached is a sketch showing the finish levels of the concrete.
| 02SL - Stations (LUL) | Cxxx-NCR-001717 | NCR | DSS - PCC Cladding ITP Incorrect Torque Values |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-10-30 | 2016-08-30 10:43 | -61 | 2016-08-01 16:19 | Shafts - Shafts General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | Torque values shown on the ITP and check sheet are incorrect
| 02SL - Stations (LUL) | Cxxx-NCR-001718 | NCR | Low reinforcement to piles 102 and 103 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-09-30 | 2016-09-29 14:51 | -1 | 2016-08-01 20:32 | Civil - Geotechnical Engineering | 2700 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | When carrying out pile breakdown works in order to construct Pile Cap 2D, the piles were broken down to cut-off level. The starter bar reinforcement was not visible, so __ were required to continue breaking the pile until the reinforcement was found. Pile 102 reinforcement was found set at 108.000, Pile 103 reinforcement was set at 108.195.
| 02SL - Stations (LUL) | Cxxx-NCR-001719 | NCR | Modification of Gusset Plate for Phase 6 Structural Steelwork |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-09-11 | 2016-09-09 14:38 | -2 | 2016-08-02 11:19 | Civil - Civil Engineering General | 3000 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Please refer to Cxxx-__M-C-CER-D061_WS106-53196 Extract as follows: North Concourse – Modification of gusset plate for CHS114.3x 6.3 strut on grid line 3 During the pre-assembly of main frame for grid line 4 the CHS114x 6.3 strut (mark11168) could not be connected to the gusset plate of column UC356x 368x 220 (mark 11144), because gusset plate is incorrectly positioned.
| 02SL - Stations (LUL) | Cxxx-NCR-001720 | NCR | DSS - Level 5 - Stair 5 Strucutural IWS-602 Wall |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-09-11 | 2016-08-15 14:46 | -27 | 2016-08-02 16:01 | Shafts - Shafts General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Structural IWS-602 (140mm wall) shown on attached mark up has been built as a structural IWS-621 (200mm) wall.
| 02SL - Stations (LUL) | Cxxx-NCR-001721 | NCR | Phase 6 Steelworks - Platform 6 (East Side) Piers 1 & 3 Remediation works |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-09-12 | 2016-09-09 10:32 | -3 | 2016-08-03 10:50 | Civil - Civil Engineering General | 2000 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Phase 6 Steelwork - Eastern Side (DSS// LO Platform 6) Site inspection revealed that the bearing connections along the Eastern Side of the Phase 6 steelwork were damaged/ contained defects in 2nos. of Piers. Pier 1 - 4nos. of couplers under the bearing plate were offset from the bolt holes of the bearing plate Pier 3 - 1nos. of couplers had thread damage 50% of the length down.
| 02SL - Stations (LUL) | Cxxx-NCR-001722 | NCR | Pile cubes not produced as per the ITP |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-10-28 | 2016-11-01 13:12 | 4 | 2016-08-03 13:00 | Civil - Civil Engineering General | 1000 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Training Deficiency - Not Defined | Completed |  | During the installation of Piles 116 and 113, 4no. 75mm grout cubes were made to provide a quality check of the grout used to install the pile.
| 02SL - Stations (LUL) | Cxxx-NCR-001723 | NCR | Phase 6 Steelwork - GL7 - Shoulder beam to Column, Lack of fit |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-11-03 | 2016-11-03 16:16 | 0 | 2016-08-03 17:36 | Civil - Civil Engineering General | 2000 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Lack of fit in connection of shoulder beam west [11096] to column [11153] only the lower 4 no M27-8.8 bolts could be installed.
| 02SL - Stations (LUL) | Cxxx-NCR-001724 | NCR | Missing Records for Combined Sewer Manhole in Durward Street |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-11-15 | 2016-11-14 21:45 | -1 | 2016-08-04 08:49 | Civil - Drainage | 1500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | There are missing records and checksheets for the construction of the combined sewer Manhole from drawing Cxxx-__M-C-DWG-D061-50132 outside the TTH. This also includes the back drop connection detail into the combined sewer on Durward Street.
| 02SL - Stations (LUL) | Cxxx-NCR-001725 | NCR | No PSK101 thickness measurements on several locations in area 4/5 steelwork above LO tracks |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-09-13 | 2016-09-12 13:58 | -1 | 2016-08-04 11:30 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient surveillance of subcontractors | Completed |  | Fire protection works have been carried out during engineering hours on the area 4/5 steels above the LO tracks. These steels have been completed primed and meshed. However, only a couple of measurements of PSK101 thickness have been taken by __. They have been allowed to proceed with the meshing without these measurements being taken beforehand. It is not possible to take precise measurements anymore because this requires measuring the thickness of the __ paint before the PSK101 is applied. Because this was carried out during engineering hours on small widths of steel, __ applied the PSK101 with the roller instead of the spray. This avoided putting protection up on the holorib decking, which would have taken a long time. When applying with the roller, the thickness cannot be less that the required thickness, which is why __ discontinued their measurements. The couple of measurements taken show very high values of total thickness, giving confidence that the thickness of the PSK101 is sufficient. __ have asked __ to carry out additional measurements to confirm this before spraying the beams with __. Available measurements are attached to the NCR. This area was also primed and meshed without CRL signing-off the beams once they had been cleaned. However __ engineers signed them off as clean.
| 02SL - Stations (LUL) | Cxxx-NCR-001726 | NCR | Over Excavation of pile P81 in 2/392 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-09-28 | 2016-09-28 12:50 | 0 | 2016-08-05 09:02 | Civil - Civil Engineering General | 1800 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | A trial hole was dug in 2/392 post discovery of a potential power cable (picked up by CAT scanning of the area). This trial hole was extended over the pile pocket location of pile P81, as per attached photo.
| 02SL - Stations (LUL) | Cxxx-NCR-001727 | NCR | Measurements for __ thickness on area 1 were not taken |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-09-14 | 2016-08-25 13:44 | -20 | 2016-08-05 15:15 | Civil - Base Course | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | __ thicknesses for beams that were sprayed on the 02/08 and the 03/08 were not taken and recorded immediately after spraying. This was a concern as the ITP states that measurements are to be taken as the beams are sprayed. This was raised with __. They acknowledge that measurements needed to be taken while explaining that because the __ is sprayed on in two coats and involves moving the GRP towers between locations, it is not always possible to get measurements of the full thickness while it is still fresh. __ reacted by calling in a quality engineer who is trained to take the measurements through the hard surface of the __. He was active taking measurements on the 04/08 afternoon and the 05/08 afternoon. His measurements were very numerous and he recorded only a fraction of them, which was already more than we needed. See attached measurements sheet signed off by Crossrail. We agreed with __ that the sprayer would carry on measuring the thickness as he sprays, to check that the desired thickness is achieved while the quality engineer will measure systematically and record his measurements once the works are finished. When questionned, he confirmed that if the __ is found to be not thick enough, it can be sprayed again to a thin layer even when the surface has hardened by dampening it.
| 02SL - Stations (LUL) | Cxxx-NCR-001728 | NCR | Tunnel Platforms - Westbound Platform 018 Slab |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-09-28 | 2016-09-14 08:44 | -14 | 2016-08-11 12:27 | Civil - Civil Engineering General | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Counterfeit Items | Completed |  | Concrete compliance cubes have failed to achieve the required strength of 40N/mm2. 7 Day strength: 26.8 N/mm2 28 Day strength cube 1: 39.7 N/mm2 28 Day strength cube 2: 39.8 N/mm2 The fourth cube, for intended 56 day testing, was made onsite but didn't reach the concrete testing lab. ================== UPDATE 26/08/16: ====================== The lab has two sets of 4 No. cube results for the PLAT 018 pour. Only 1 set of 4 No. cubes were made. Therefore one set of cubes have been incorrectly linked to pour PLAT 018. o One set of 3 No. cubes failed (Reference: CW 1248). In the belief that these cubes were the set for PLAT 018 this NCR was raised. o One set of 4 No. cubes passed (Reference: CW 1239). CW numbers are issued by the lab on receipt of cubes and therefore give a good indication of pour date. The lab believes CW 1239 are the correct set for PLAT 018 for the following reasons: o It gained strength in line with our usual mix. o The reference number CW 1239 corresponds perfectly with the pour date. o There were four number cubes. The lab believes CW 1248 (that this NCR is raised for) are not for this pour: o It’s strength gain does not correspond to the usual mix. o The higher CW reference number corresponds to a later date than that of the pour. o There are only 3 No. cubes, which implies they are not quality assurance ones, of which 4 always exist. The failed cubes are not thought to be for any of the Crossrail Platforms pours as there are no other missing cube results. Factors in this error include the following 1. Incorrect paperwork (sample certs) delivered to the lab 2. Technician mix up with marking on cubes 3. Error in booking in of cube sets at the laboratory This is the first administrative error with concrete cubes, after roughly 500 or so delivered from the Crossrail Platforms team to the lab, there is not thought to be an issue with the procedure. CW 1239 proves PLAT 018 did in fact achieve 69.1 N/mm2 avg 28 day strength, and therefore this NCR is can be cancelled.
| 02SL - Stations (LUL) | Cxxx-NCR-001730 | NCR | LULO East Stair Shaft - Procedural NCR for CFA Mini Pile #51 Compressive Strength test average |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-10-21 | 2016-09-19 09:06 | -32 | 2016-08-11 12:16 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Upon CRL review for resubmission of Construction Records for Piles cast in 2012 - CFA Mini Piles (HCDL) East Stair Shaft: Compressive Strength Laboratory Results Cxxx-__M-O4-LRC-D061-50008 Rev 2.0, CRL have highlighted a non compliance with respect to the compressive strength results for 1of 90 Piles - pile #51. According to the ICE Specification for piling and embedded retaining walls 2nd edition 2007 edition Clause B19.8.3 Sampling for compressive strength testing of the results is not compliant with the Specification for piling and embedded retaining walls which states "The cubes shall be made, cured and tested in accordance with the appropriate parts of BSEN 12390.... The mean of two cube results at 28 days shall constitute a test result provided the difference of the individual cube results is not greater than 15% of the mean". The results obtained for Pile #51 is in conflict with this clause. Please see the attached UKAS Concrete & Grout Cube testing form Conc005 Sample ref CW0011 who shows the 28 days to be 37.3 N/mm2 and 46.3 N/mm2 respectively with an average of 41.8 N/mm2. The difference of the 2 values is 9N/mm2. 15% of the mean (41.8 N/mm2) = 6.27 N/mm2. To conclude the individual cube results difference of 9N/mm2 is greater than 6.27 N/mm2 which is not acceptable.
| 02SL - Stations (LUL) | Cxxx-NCR-001731 | NCR | LULO - WSS - Concrete Storage Facility - LaCK OF Management |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-09-16 | 2016-09-16 14:48 | 0 | 2016-08-11 07:12 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Improper resource allocation | Completed |  | Further to CRL-OBS-11407, this NCR records the lack of management of the new LULO concrete storage unit. 1. No water tank present to store the cubes in. Concrete cubes should be stored within the mould for more than 16 hours but less than 3 days. Once removed from the mould they should be stored in water at a temperature of 20 °C ± 2 °C, until immediately before testing. 2. Paperwork was missing from several sets of cubes which would help to identify them. 3. No means of testing the room temperature (i.e. thermometer), and no log book was present at the time of inspection.
| 02SL - Stations (LUL) | Cxxx-NCR-001733 | NCR | CHS Level 8 Blockwork Setting Out |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-09-10 | 2016-09-10 10:19 | 0 | 2016-08-15 14:56 | Architectural - Brickworks/Blockworks | 895 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Wall to Lobby 3 (8/083) and Stair 40 has been set out incorrectly. The blockwork was set out from the wrong side of the RC wall, and approx. 5 courses of blockwork laid. This was not picked up by __ Engineer.
| 02SL - Stations (LUL) | Cxxx-NCR-001734 | NCR | CHS - As-built survey Level C |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-10-29 | 2016-10-28 12:20 | -1 | 2016-08-16 12:11 | Shafts - Shafts General | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please see attached as built survey of CHS - level C There are a number of areas that are out of tolerance (highlighted in green). 1) The area within the purple bubble shows the extent of NCR-1465 regarding the movement of the shutter when pouring the C2 slab. 2) The area in the Southwest corner is another are out of tolerance by up to 12mm. There are grills required to be installed here however this, or another as-built survey will be completed prior to installation and fabrication will take account of the minor discrepancies. As such, other than the area already raised as an NCR, it is proposed that all remaining areas are left as is.
| 02SL - Stations (LUL) | Cxxx-NCR-001735 | NCR | DSS - Additional construction joint C1-16 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-09-25 | 2016-08-31 14:13 | -25 | 2016-08-16 15:05 | Shafts - Shafts General | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | C1-16 poured to an incorrect level
| 02SL - Stations (LUL) | Cxxx-NCR-001736 | NCR | CHS - As-built survey Level 8 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-10-29 | 2016-10-28 10:54 | -1 | 2016-08-16 14:19 | Shafts - Shafts General | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please find attached the as-built survey for CHS - Level 8 walls and columns Any points that exceed the allowable of tolerance of 10mm (as per NSCS), have been highlighted in green. __ propose that these areas be left as is
| 02SL - Stations (LUL) | Cxxx-NCR-001738 | NCR | CHS - Blockwork L8 Stair 40 - Out of Tolerance |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-12-20 | 2016-09-10 09:05 | -101 | 2016-08-31 18:09 | Architectural - Brickworks/Blockworks | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The wall dividing Stair 40 and 8/083 has been constructed out of tolerance. At the top of the wall the deviation from vertical is 22mm, as surveyed by __ Engineer. This is believed to be due to the top 5.5 courses being out of plumb.
| 02SL - Stations (LUL) | Cxxx-NCR-001739 | NCR | CHS - Level 8 Blockwork - Discrepancy in Drawings |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-12-07 | 2016-12-07 17:17 | 0 | 2016-08-31 18:14 | Architectural - Brickworks/Blockworks | 1500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | There exists a discrepancy between blockwork drawings Cxxx-__M-A-DDD-D061_WS107_8-19080 P04 and Cxxx-__M-A-DDA-D061_WS107_8-20682 P05. The result of this discrepancy is that a windpost has been ordered that is too long, as shown in drawing 19080.
| 02SL - Stations (LUL) | Cxxx-NCR-001741 | NCR | CHS - Firestopping - Provision of an accepted Benchmark |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-10-01 | 2016-12-12 15:50 | 72 | 2016-08-22 19:51 | Fire - Compartmentation | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | During a firestopping surveillance of CHS & DSS, evidence of an accepted benchmark was requested. While it was stated that "mastic was initially level 6, later changed to level 5 large “FAN ROOM” due to de-bonding issues on level 6", there is no benchmark identified on site with a label, no entry in the benchmark register and no readily available documented evidence of acceptance.
| 02SL - Stations (LUL) | Cxxx-NCR-001742 | NCR | CRL Platforms - EP1 - Short Wall Position |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-10-29 | 2016-10-05 09:17 | -24 | 2016-08-24 10:34 | Civil - Civil Engineering General | 2900 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Contractor has found that the return to the short wall in EP1 has been constructed 240mm out of line. See sketch attached for details.
| 02SL - Stations (LUL) | Cxxx-NCR-001743 | NCR | Lost casing in piles 105 and 106 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-12-01 | 2016-12-01 16:21 | 0 | 2016-08-30 11:18 | Civil - Civil Engineering General | 1500 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Whilst removing the casing from Pile 105 after pouring the concrete, the casing joint on the final section of casing spilt whilst still in the bore. 1.2m of casing (1no. 1m casing section and a 0.2m cutting head) have been left in the bore. The top of the casing left around the pile is located approximately 106.8m AOD (approximately 1.1m below pile cut off level). Whilst removing the casing from Pile 106, the rig was unable to remove all the casing, leaving 7.2m (7no. 1m sections and 1no. 0.2m lead section) of casing in the ground. The top of the casing is located at 109.8m AOD (approximately 1.9m above cut off level)
| 02SL - Stations (LUL) | Cxxx-NCR-001744 | NCR | CRL Platforms - Westbound Tunnel - Plat 02 - Columns poured to the incorrect height at the platform slab step |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-10-09 | 2016-09-14 11:12 | -25 | 2016-08-30 16:58 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Two columns highlighted in the attached sketches have been poured 150mm too high. The columns are located in Platform Bay 02. The columns are located in the 150mm step in the slab between the main platform and the platform ends. Cxxx-NCR-001744 Sketch 01 details the location of the columns. The front short column are detailed in drawing Cxxx-__M-C-DWG-D061_WS106-53133_REV C01. See Cxxx-NCR-001744 Sketch 02 for further information. The back tall column is detailed as a column 'C01' on drawing Cxxx-__M-C-DWG-D061_WS106-53048 REV C01
| 02SL - Stations (LUL) | Cxxx-NCR-001745 | NCR | CRL Platforms - Eastbound - Track slab wall bay TB212 / 213 poured to the wrong level |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-10-13 | 2016-09-17 11:35 | -26 | 2016-09-01 14:00 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A section of the track slab wall in bays EB TB212 / 213 has been poured 75mm too high. Section of track slab wall in question - Chainage 10412.571 to Chainage 10428.359 See marked up GFRP drawing which shows the level the wall has been poured to. This level clashes with the GFRP U-bars (BM 401) and lower GFRP lacers to be installed in the platform nosing.
| 02SL - Stations (LUL) | Cxxx-NCR-001746 | NCR | DSS - Stainless Steel Cladding Bracket Weld Cleaning |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-12-14 | 2016-10-24 07:38 | -51 | 2016-09-05 12:51 | Shafts - Shafts General | 7600 |  | Manufacturing Defect | Use As-Is | 2 (6-60k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Post weld cleaning was not completed on stainless steel cladding support brackets. This has potentially introduced additional corrosion factors and therefore potentially affect the lifecycle of the product.
| 02SL - Stations (LUL) | Cxxx-NCR-001747 | NCR | Crossrail Platform Tunnels - As-built tolerances |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-10-29 | 2016-09-26 09:35 | -33 | 2016-09-05 16:43 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As-built survey Cxxx-__M-C-RGN-D061_WS106-53056, "Crossrail Platforms RC As-Built surveys Chainage 10356 to 10447" has identified the following areas outside of construction tolerances. The as-built survey has been taken at 5m intervals. In each instance the two sides of the wall is offset further from the track centre line by the following amounts: PLAT 007 === Trackbed wall === DWG 53069 @ CH 10360m - 14mm and 17mm @ CH 10370m - 08mm and 17mm PLAT 008 === Trackbed wall === DWG 53071 @ CH 10375m - 19mm and 18mm PLAT 009 === Internal wall === DWG 53074 @ CH 10395m - 17mm and 19mm @ CH 10400m - 10mm and 17mm
| 02SL - Stations (LUL) | Cxxx-NCR-001748 | NCR | DSS - WB-09S Kicker Out of Alignment |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-03-31 | 2017-03-10 11:19 | -21 | 2016-09-07 09:00 | Shafts - Shafts General | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Level B Slab section where WB-09S kicker should be was poured out of alignment, as per the attached asbuilt.
| 02SL - Stations (LUL) | Cxxx-NCR-001749 | NCR | DSS - W1-09S Out of Alignment |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-12-15 | 2016-12-01 09:50 | -14 | 2016-09-07 11:05 | Shafts - Shafts General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | W1-09S has been poured out of alignment, please refer to attached asbuilts.
| 02SL - Stations (LUL) | Cxxx-NCR-001750 | NCR | DSS - Level 1 - C1-14 - Concrete lip out of tolerance |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-01-31 | 2017-01-31 10:27 | 0 | 2016-09-07 12:00 | Shafts - Shafts General | 3500 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Counterfeit Items | Completed |  | 15mm lip in concrete C1-14 poured out of tolerance
| 02SL - Stations (LUL) | Cxxx-NCR-001754 | NCR | LULO ETH E6 incorrect fuse size in fuse switch |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-11-30 | 2016-11-02 09:31 | -28 | 2016-09-08 16:08 | Electrical - Power Distribution | 1000 |  | Planning | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Insufficient quantity of material to do the job | Completed |  | Saturday night during the E6/ E14 changeover works it was noted that the Fuse Switch which had a label on it stating protection by 63A fuses actually contained 100A fuses. This is in conflict with the CATII document amtech design which states the overcurrent protective device as 63A rated.
| 02SL - Stations (LUL) | Cxxx-NCR-001755 | NCR | DSS - P52 Corbel Cast Out of Position |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-11-09 | 2016-11-05 13:10 | -4 | 2016-09-07 16:56 | Shafts - Shafts General | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Corbel cast on panel P52 where there is an RC structure clash with corbel
| 02SL - Stations (LUL) | Cxxx-NCR-001756 | NCR | LULO - TTH - Slip Test Results Failure |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-10-19 | 2019-03-12 13:01 | 144 | 2016-09-08 07:53 | Architectural - Flooring | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Slip Test Values recorded in Cxxx-__M-A-RGN-D061_WS106-50027 by __ during the post installation survey have failed in a number of locations. Details are held within the report
| 02SL - Stations (LUL) | Cxxx-NCR-001757 | NCR | Crossrail Platform Tunnels - As-built Tolerances Platform 15 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-01-19 | 2016-11-10 18:26 | -70 | 2016-09-12 15:39 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As-built survey Cxxx-__M-C-RGN-D061_WS106-53058, "Crossrail Platforms RC As-Built surveys Chainage 10491 to 10573" has identified the following areas outside of construction tolerances. The as-built survey has been taken at 5m intervals. The following describe the as built conditions for platform 15 PLAT 015 === Internal Wall === DWG 53085 @ CH 10495m – 14mm and 7mm @ CH 10500m – 14mm and 10mm PLAT 015 === Track Bed Wall === DWG 53085 @ CH 10510m – 11mm PLAT 015 === Drainage Channel Base === DWG 53085 @ CH 10505m – 14mm It is proposed to use as is.
| 02SL - Stations (LUL) | Cxxx-NCR-001758 | NCR | GSM Building - Gaps in new and existing steel connections |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-11-04 | 2016-11-02 10:11 | -2 | 2016-09-12 11:52 | Structural Engineering - Bolted Connections | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Upon inspection of the GSM roof steelwork, gaps have been identified by __ between existing steel and new steel in 4no locations. Gaps were in the corners of the building (intersections of gridlines GD and G7, GL and G7, GL and G1, G1 and GD). The Contractor notified the subcontractor __, who was able to attend site the following nightshift to install the required shim plates. 5mm and 8mm Shim plates were used as shown in attachment.
| 02SL - Stations (LUL) | Cxxx-NCR-001759 | NCR | GSM Building - Defect in new steelwork coating |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-10-22 | 2016-09-29 15:10 | -23 | 2016-09-12 12:44 | Civil - Civil Engineering General | 1000 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Upon inspection of the recently installed coating of the GSM first floor steelwork, a defect in appearance of the coating was identified on the beam along gridline GJ, between gridlines G4 and G5. Upon further inspection it was identified that loose materials had been painted in. This caused the defect in appearance, a discontinuity in the coating, and reduced adhesion.
| 02SL - Stations (LUL) | Cxxx-NCR-001760 | NCR | Crossrail Platform Tunnels - As-built Tolerances Platform 16 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-10-22 | 2016-09-17 12:50 | -35 | 2016-09-12 16:01 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As-built survey Cxxx-__M-C-RGN-D061_WS106-53058, "Crossrail Platforms RC As-Built surveys Chainage 10491 to 10573" has identified the following areas outside of construction tolerances. The as-built survey has been taken at 5m intervals. The following describe the as built conditions for platform 16 PLAT 016 === Internal Wall === DWG 53087 @ CH 10515m – 11mm PLAT 016 === Slab === DWG 53087 @ CH 10530m – 13mm
| 02SL - Stations (LUL) | Cxxx-NCR-001761 | NCR | Crossrail Platform Tunnels - As-built Tolerances Platform 17 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-01-19 | 2016-12-12 09:56 | -38 | 2016-09-12 16:26 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As-built survey Cxxx-__M-C-RGN-D061_WS106-53058, "Crossrail Platforms RC As-Built surveys Chainage 10491 to 10573" has identified the following areas outside of construction tolerances. The as-built survey has been taken at 5m intervals. The following describe the as built conditions for platform 17 PLAT 017 === Top of Upstand === DWG 53089 @ CH 10540m – 11mm and 7mm PLAT 017 === Side of Upstand === DWG 53089 @ CH 10545m – 14mm PLAT 017 === Track Bed === DWG 53089 @ CH 10545m – 11mm and 14mm PLAT 017 === Drainage Channel Base === DWG 53089 @ CH 10535m – 16mm
| 02SL - Stations (LUL) | Cxxx-NCR-001762 | NCR | DSS - W8-14S, 13S Poured Low |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-12-13 | 2016-09-27 08:23 | -77 | 2016-09-14 09:07 | Shafts - Shafts General | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As per the attached sketch W8-14S and a section of W8-13S have been poured low. The wall is a maximum of 30mm low and runs into the correct level as indicated on mark up. The steel metal deck will be fixed between the RC wall and structural blockwork wall and poured at correct level (86.950 SSL). Level 8 soffit in this location will therefore be a maximum of 30mm low.
| 02SL - Stations (LUL) | Cxxx-NCR-001763 | NCR | LULO - WSS - S25 Temporary Stairs - Welding of Bolts |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-11-25 | 2016-11-25 15:44 | 0 | 2016-09-20 10:05 | Civil - Structural Engineering | 3000 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | S25 Temporary Stairs have welded bolt connections as part of their fabrication. McNeally Brown are unable to provide a statement confirming that their Weld Procedures are sufficient for welding bolts.
| 02SL - Stations (LUL) | Cxxx-NCR-001764 | NCR | DSS - Panel Restraint Misalignment P8-P13-P21RR |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-12-23 | 2016-10-23 16:41 | -61 | 2016-09-14 09:11 | Shafts - Shafts General | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Precast Concrete panels P8, P13 and P21RR have restraint fixings cast in wrong locations
| 02SL - Stations (LUL) | Cxxx-NCR-001765 | NCR | Crossrail Platform Tunnels - As-built Tolerances, remaining Doc 53058 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-01-19 | 2016-12-12 09:57 | -38 | 2016-09-14 09:12 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As-built survey Cxxx-__M-C-RGN-D061_WS106-53058, "Crossrail Platforms RC As-Built surveys Chainage 10491 to 10573" has identified the following areas outside of construction tolerances. The as-built survey has been taken at 5m intervals. The following describe the as built conditions for remaining structures between 10491 and 10573 chainage with relation to NCR 001756, 001760 and 001761. Upstands: PLAT 018 === Side of Upstand === DWG 53091 @ CH 10555m – 12mm @ CH 10560m – 11mm @ CH 10565m – 13mm PLAT 019 === Top of Upstand === DWG 53091 @ CH 10570m – 12mm PLAT 019 === Side of Upstand === DWG 53091 @ CH 10575m – 29mm Trackbed: PLAT 018 === Track Bed === DWG 53091 @ CH 10560m – 16mm and 13mm @ CH 10565m – 11mm PLAT 019 === Track Bed === DWG 53091 @ CH 10570m – 11mm @ CH 10575m – 19mm Drainage Channel: PLAT 018 === Drainage Channel Base === DWG 53092 @ CH 10565m – 18mm PLAT 019 === Drainage Channel Base === DWG 53091 @ CH 10570m – 22mm
| 02SL - Stations (LUL) | Cxxx-NCR-001766 | NCR | Crossrail Platform Tunnels - As-built Tolerances for remaining structures in between 10356 and 10447 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-10-24 | 2016-10-06 15:24 | -18 | 2016-09-14 11:25 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Counterfeit Items | Completed |  | As-built survey Cxxx-__M-C-RGN-D061_WS106-53056, "Crossrail Platforms RC As-Built surveys Chainage 10356 to 10447" has identified the following areas outside of construction tolerances. The as-built survey has been taken at 5m intervals. This NCR is in addition to NCR 001747 fopr this chainage section. The following show the structures out oif as built tolerences and their locations. Wall: PLAT 007 === Internal wall @ CH 10370m - 12mm and 8mm PLAT 009 === Internal wall @ CH 10405m - 11mm and 0mm Platform Slab: PLAT 007 === Slab @ CH 10360m – 17mm @ CH 10365m – 11mm @ CH 10370m – 15mm PLAT 008 === Slab @ CH 10375m – 11mm PLAT 009 === Slab @ CH 10400m – 16mm PLAT 010 === Slab @ CH 10425m – 14mm PLAT 011 === Slab @ CH 10435m – 14mm and 12mm and 11mm @ CH 10440m – 15mm and 11mm @ CH 10445m –15mm UPE Benching (between walls): PLAT 007 === UPE Benching @ CH 10360m – 19mm @ CH 10370m – 11mm PLAT 010 === UPE Benching @ CH 10420m – 25mm PLAT 010 === UPE Benching @ CH 10425m – 14mm CMS Benching (between wall and SCL): PLAT 007 === CMS Benching @ CH 10365m – 11mm (top) and 13mm (side) PLAT 008 === CMS Benching @ CH 10380m – 12mm (top) PLAT 008 === CMS Benching @ CH 10385m – 23mm (top), 20mm (top) and 11mm (side) PLAT 008 === CMS Benching @ CH 10390m – 16mm (side) PLAT 009 === CMS Benching @ CH 10395m – 12mm and 14mm (top) PLAT 009 === CMS Benching @ CH 10405m - 14mm (top) PLAT 010 === CMS Benching @ CH 10415m – 13mm and 7mm (top) PLAT 010 === CMS Benching @ CH 10420m – 23mm (top) PLAT 010 === CMS Benching @ CH 10425m – 28mm (top) Platform Nosing: PLAT 009 === Nosing @ CH 10395m – 11mm PLAT 011 === Nosing @ CH 10440m –12mm @ CH 10445m –12mm Upstands: PLAT 008 === Upstand Top @ CH 10380m – 14mm PLAT 008 === Upstand Top @ CH 10385m – 15mm PLAT 008 === Upstand Top @ CH 10390m – 15mm PLAT 009 === Upstand Top @ CH 10395m – 14mm and 2mm PLAT 009 === Upstand Side @ CH 10400m - 11mm @ CH 10410m - 16mm PLAT 010 === Upstand Top @ CH 10415m – 12mm and 6mm PLAT 010 === Upstand Side @ CH 10415m – 16mm and 9mm @ CH 10420m – 11mm @ CH 10430m – 11mm and 12mm PLAT 011 === Upstand Side @ CH 10445m –15mm and 5mm Track Bending Pour (mass pour): PLAT 007 === Track Benching Pour @ CH 10360m – 21mm and 9mm @ CH 10370m – 13mm PLAT 008 === Track Benching Pour @ CH 10375m – 13mm Track Bed: PLAT 007 === Track Bed @ CH 10360m – 16mm @ CH 10370m – 16mm PLAT 008 === Track Bed @ CH 10375m – 13mm @ CH 10380m – 16mm @ CH 10385m – 11mm PLAT 009 === Track Bed @ CH 10395m – 15mm and 4mm @ CH 10405m – 18mm PLAT 010 === Track Bed @ CH 10415m – 12mm @ CH 10425m – 17mm @ CH 10430m – 13mm PLAT 011 === Track Bed @ CH 10440m –11mm @ CH 10445m –15mm and 7mm Track Drainage Channel: PLAT 008 === Drainage Channel Base @ CH 10380m – 15mm PLAT 008 === Drainage Channel Base @ CH 10385m – 42mm PLAT 009 === Drainage Channel Side @ CH 10395m – 11mm and 10mm PLAT 009 === Drainage Channel Base @ CH 10395m – 15mm PLAT 010 === Drainage Channel Base @ CH 10415m – 11mm @ CH 10425m – 11mm Corbel: PLAT 011 === Corbel @ CH 10445m –11mm
| 02SL - Stations (LUL) | Cxxx-NCR-001767 | NCR | DSS - Western Elevation - Panel P19 Colour Inconsistancy |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-08-01 | 2017-09-29 14:05 | 59 | 2016-09-15 12:10 | Shafts - Shafts General | 500 |  | Material | Reject | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | The first panel to the right of grid line 2.1 is darker than adjacent panels
| 02SL - Stations (LUL) | Cxxx-NCR-001768 | NCR | Crossrail Platform Tunnels - As-built Tolerances For Chainages 10253-10356 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-10-26 | 2016-10-06 15:00 | -20 | 2016-09-16 15:53 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As-built survey Cxxx-__M-C-RGN-D061_WS106-53055, "Crossrail Platforms RC As-Built surveys Chainage 10253 to 10356" has identified the following areas outside of construction tolerances. The as-built survey has been taken at 5m intervals. Below is a summary of all outside tolerences. • Drainage channel PLAT 004 === Drainage Channel Base @ CH 10300m – 12mm PLAT 006 === Drainage Channel Base @ CH 10335m – 12mm • Upstands PLAT 001 === Upstand Top @ CH 10260m – 15mm PLAT 004 === Upstand Top @ CH 10300m – 11mm PLAT 004 === Upstand Side @ CH 10300m – 14mm and 16mm @ CH 10310m – 11mm PLAT 005 === Upstand Side @ CH 10325m – 11mm @ CH 10330m – 11mm PLAT 006 === Upstand Side @ CH 10345m – 20mm PLAT 006 === Upstand Top @ CH 10335m – 17mm PLAT 007 === Upstand Side @ CH 10355m – 12mm • Track side wall PLAT 002 === Track Side Wall @ CH 10285m – 12mm PLAT 004 === Track Side Wall @ CH 10300m – 13mm @ CH 10310m – 20mm PLAT 005 === Track Side Wall @ CH 10315m – 15mm @ CH 10320m – 14mm @ CH 10325m – 13mm and 18mm @ CH 10330m – 12mm and 18mm PLAT 006 === Track Side Wall @ CH 10335m – 11mm • Internal wall PLAT 005 === Internal @ CH 10315m – 12mm @ CH 10325m – 11mm • Platform Slab PLAT 001 === Platform Slab @ CH 10265m – 12mm and 19mm @ CH 10270m – 12mm PLAT 002 === Platform Slab @ CH 10280m – 11mm, 16mm and 21mm PLAT 004 === Platform Slab @ CH 10295m – 12mm PLAT 005 === Platform Slab @ CH 10320m – 12mm @ CH 10325m – 15mm @ CH 10330m – 11mm PLAT 006 === Platform Slab @ CH 10335m – 12mm, 14mm and 15mm • Track Bed PLAT 002 === Track Bed @ CH 10280m – 13mm PLAT 005 === Track Bed @ CH 10320m – 17mm @ CH 10325m – 20mm PLAT 006 === Track Bed @ CH 10345m – 12mm and 13mm PLAT 007 === Track Bed @ CH 10355m – 15mm • CMS Benching PLAT 004 === CMS Benching @ CH 10305m – 13mm • Track slab benching PLAT 002 === Track Slab Benching @ CH 10280m – 16mm @ CH 10285m – 11mm PLAT 004 === Track Slab Benching @ CH 10300m – 16mm @ CH 10295m – 15mm PLAT 006 === Track Slab Benching @ CH 10345m – 13mm PLAT 007 === Track Slab Benching @ CH 10355m – 15mm and 20mm • Nosing PLAT 002 === Platform Nosing @ CH 10285m – 11mm PLAT 005 === Platform Nosing @ CH 10315m – 12mm @ CH 10325m – 11mm @ CH 10330m – 11mm PLAT 006 === Platform Nosing @ CH 10345m – 11mm PLAT 007 === Platform Nosing @ CH 10355m – 11mm
| 02SL - Stations (LUL) | Cxxx-NCR-001769 | NCR | LULO - Reinforcement Concrete - WLL - Lift 10 Base |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-10-29 | 2016-10-27 12:42 | -2 | 2016-09-19 08:39 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | The works have started without an approved ITP.
| 02SL - Stations (LUL) | Cxxx-NCR-001770 | NCR | Crossrail Platforms - WB Plat 011-012 Central Wall remedial |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-01-17 | 2016-11-23 14:07 | -55 | 2016-09-19 10:45 | Civil - Civil Engineering General | 1500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In the Westbound tunnel, during striking of the central wall shutter below platform 012, damage was inflicted on the adjoining wall. A piece of concrete approximatly 500x100mm was broken off, exposing some reinforcement (See attached Photo).
| 02SL - Stations (LUL) | Cxxx-NCR-001771 | NCR | Crossrail Platform Tunnels - As-built Tolerances for remaining structures in between 10447-10491 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-10-31 | 2016-10-06 13:12 | -25 | 2016-09-21 15:01 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Counterfeit Items | Completed |  | As-built survey Cxxx-__M-C-RGN-D061_WS106-53057, "Crossrail Platforms RC As-Built surveys Chainage 10447 to 10491" has identified the following areas outside of construction tolerances. The as-built survey has been taken at 5m intervals. • Drainage channel PLAT 013 === Drainage Channel Base @ CH 10470m – 12mm PLAT 014 === Drainage Channel Base @ CH 10485m – 24mm • Upstands PLAT 012 === Upstand Side @ CH 10455m – 12mm PLAT 012 === Upstand Top @ CH 10450m – 14mm PLAT 013 === Upstand Side @ CH 10460m – 14mm @ CH 10470m – 15mm • Internal wall PLAT 013 === internal Wall @ CH 10470m – 10mm and 13mm • Platform Slab PLAT 012 === Platform Slab @ CH 10450m – 12mm PLAT 013 === Platform Slab @ CH 10470m – 20mm • Track Bed PLAT 013 === Track Bed @ CH 10470m – 11mm PLAT 014 === Track Bed @ CH 10475m – 14mm @ CH 10480m – 13mm • Nosing PLAT 012 === Nosing @ CH 10450m – 11mm PLAT 013 === Platform Nosing @ CH 10460m – 14mm • Corbel PLAT 013 === Corbel @ CH 10460m – 13mm @ CH 10470m – 15mm
| 02SL - Stations (LUL) | Cxxx-NCR-001773 | NCR | ETH - DNO Duct Bracket Fixing |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-10-30 | 2016-10-26 14:39 | -4 | 2016-09-20 11:01 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | The bracket system under CAT I design Cxxx-__M-E-CER-D061_WS106-50147 to support the steel duct which would house the new DNO supply into switch room E2 was installed prior to Crossrail sign off on the documentation. The works were undertaken on 13th September with the document uploaded to eB to be issued to Crossrail on the 16th September. This was not as per Crossrail procedure.
| 02SL - Stations (LUL) | Cxxx-NCR-001774 | NCR | ETH - Pad Foundation on TL151 Tunnel Top Landing |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-11-18 | 2016-11-02 10:12 | -16 | 2016-09-20 12:24 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Pad Foundation FP3A was poured without the 4 nos. B12 dowel bars cast into the landing below as shown in drawing Cxxx-HYD-S-DDB-D061_WS106_Z-75861.
| 02SL - Stations (LUL) | Cxxx-NCR-001775 | NCR | CHS - Level 8 - Waterproofing Detail |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-03-01 | 2017-02-28 09:12 | -1 | 2016-09-27 10:53 | Architectural - General | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | The wateproofing detail below blockwork walls is insufficient to provide a water-resistant boundary when used with the waterproofing layer incorporated into screed works. Due to the in-blockwork drainage detail, as per Cxxx-__M-A-DDD-D061_Ws107_8-19123, this membrane is warped. It can also be seen in the attached photograph that the membrane has been fixed up to the blockwork, which has introduced perforations. Furthermore, there are tears which have not yet been repaired.
| 02SL - Stations (LUL) | Cxxx-NCR-001776 | NCR | DSS - Stair 1 Flight 17 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-11-10 | 2017-10-16 09:47 | -25 | 2017-07-14 07:07 | Shafts - Shafts General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 16mm A12 lenton couplers were installed at the incorrect heights along the section of wall W3-03S (below CDB-1-09). Couplers are approx. 50mm below the underside of the stair waist.
| 02SL - Stations (LUL) | Cxxx-NCR-001777 | NCR | DSS - Level 6 Walls & Columns Asbuilts |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-01-05 | 2017-01-05 17:40 | 0 | 2016-09-27 12:55 | Shafts - Shafts General | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Level 6 asbuilts of walls and columns which are out of tolerance, __ have been notified, please refer to attached PTRs and Asbuilts
| 02SL - Stations (LUL) | Cxxx-NCR-001778 | NCR | DSS - Level 5 Walls & Columns Asbuilts |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-01-05 | 2017-01-05 17:39 | 0 | 2016-09-27 13:33 | Shafts - Shafts General | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Level 5 asbuilts of walls and columns which are out of tolerance, __ have been notified, please refer to attached PTRs and Asbuilts
| 02SL - Stations (LUL) | Cxxx-NCR-001779 | NCR | Blocked and incorrectly cast UTX in westbound tunnel |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-07-01 | 2017-06-08 08:16 | -23 | 2016-09-28 14:55 | Civil - Civil Engineering General | 4000 |  | Damaged | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In the westbound tunnel there are three UTX's. This NCR has been raised to cover defects in the east end UTX and the west end UTX. East End UTX (see attached sketches): The location that the Cxxx OHLE ducts emerge from the upstand is not as shown on dwg Cxxx-__M-E-DDA-D061_WS106_7-1000. They currently emerge on the edge of the upstand. The draw cord is easily pulled through these ducts. One of the Cxxx Signal ducts is currently blocked with what we assume is concrete. Please note there are 8 spare ducts in this location. West End UTX (see attached sketches): One Cxxx Earthing duct is currently blocked with what we assume is concrete. Please note there are 8 spare ducts in this location.
| 02SL - Stations (LUL) | Cxxx-NCR-001782 | NCR | RIR-828 Conflicting Information |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-11-07 | 2016-11-07 17:28 | 0 | 2016-09-28 10:26 | Architectural - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | RIR-828 has been issued with several errors, as a result of this the document in its current for cannot be issued to site teams, or to subcontractors to obtain the drawing for use to undertake the site works, the document also in its current for is an incomplete/ incorrect record of issue for these versions of the drawings. __ should be issuing out RIRs that we are confident are correct to the subcontractors as they are issued at IFC. If we are to issue this RIR in its current form to a subcontractor, we would have received back an EWN informing us of the error on the RIR. The Site Team similary at risk of not being armed with the most up to date information as this RIR does not detail this correctly This item was identified on the 5th September to __ doc control and Design Management teams. At present the subcontractor/ site teams have not been issued with the drawings associated with this RIR due to the discrepancy in the document and the resulting confususion this would cause on site. The issues with RIR-828 are as below, See below the issues with this particular RIR: - Title of RIR – Is GIA IFC, emphasis on the ‘IFC’ - not all drawings have corresponding C rev/ IFC issue drawing - some are still at P. - Drawing Cxxx-__M-A-DDD-D061_WS107_Z-19120 has 2 different titles between the number. - The RIR has drawing WS107_Z-19120 and Z-19210 both with the same title ‘seepage drainage details’ both at C01, neither on Eb – both links fail. - The Cxxx-__M-A-DDD-D061_WS107_Z-19120 Seepage Drainage Details drawing C01 does not exist on EB - The drawings Z-19121 P09 and Z-19122 P05 do not have a corresponding C/ IFC drawing - There is no IFC for Cxxx-__M-A-DDD-D061_WS107_Z-19120 – Blockwork details – therefore last approved blockwork details drawing we have to work to is the MCG01 - Drawing Z-19123 C02, the Eb link doesn’t work
| 02SL - Stations (LUL) | Cxxx-NCR-001783 | NCR | DSS - Level 4 Walls & Columns Asbuilts |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-01-06 | 2017-01-06 09:59 | 0 | 2016-09-28 11:04 | Shafts - Shafts General | 1500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Level 4 asbuilts of walls and columns which are out of tolerance, __ have been notified, please refer to attached PTRs and Asbuilts
| 02SL - Stations (LUL) | Cxxx-NCR-001784 | NCR | Crossrail Platform Tunnels - EP2 slab concrete finish |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-12-07 | 2016-12-07 16:26 | 0 | 2016-10-28 15:29 | Civil - Civil Engineering General | 1000 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The brush finish to the slab in EP2 is incomplete. Day shift began applying the brush finish but stopped as the remaining concrete was too wet. Night shift were unable to apply the brush finish as the concrete was too hard. A section of ~3.25m from the construction joint remains incomplete.
| 02SL - Stations (LUL) | Cxxx-NCR-001785 | NCR | DSS - __ PCC Cladding Cube Results 08/06/16 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-01-07 | 2016-12-23 07:59 | -15 | 2016-09-29 14:49 | Shafts - Shafts General | 1000 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __ Concrete PCC Cladding concrete cubes on 8/06/16 reached 47.4N after 56 days.
| 02SL - Stations (LUL) | Cxxx-NCR-001786 | NCR | DSS - __ PCC Cladding Cube Results 14/07/16 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-01-07 | 2016-12-23 07:56 | -15 | 2016-09-29 15:49 | Shafts - Shafts General | 1000 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Concrete cubes for precast concrete cladding reached 48.7N after 28 days
| 02SL - Stations (LUL) | Cxxx-NCR-001787 | NCR | DSS Level 6 - Blockwork Wall Abuts Concrete With No Movement Joint In Place |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-12-04 | 2016-11-11 17:52 | -23 | 2016-09-30 10:46 | Architectural - Brickworks/Blockworks | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Blockwork wall abuts concrete with no movement joint in place.
| 02SL - Stations (LUL) | Cxxx-NCR-001788 | NCR | DSS - Level 5 Blockwork Joint Discrepancy |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-12-15 | 2016-12-07 08:19 | -8 | 2016-09-30 15:24 | Architectural - Brickworks/Blockworks | 1750 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Blockwork wall joint discrepancy could not be achieved due mitre joint. __ to confirm via PTR if a mastic joint is practical. PTR-1697 has been sent to __ for clarification.
| 02SL - Stations (LUL) | Cxxx-NCR-001789 | NCR | Colour matching Wall 11 on C1 to C2 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-09-15 | 2017-09-19 09:51 | 4 | 2016-09-30 17:28 | Architectural - Walls | 6000 |  | Workmanship | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following closure of NCR 1465 __ indicated colour match is necessary in order to make the wall fit for use. This colour match is required on the band of rememdials carried out in the centre of the wall as indicated in the attached photos of Wall 11.
| 02SL - Stations (LUL) | Cxxx-NCR-001790 | NCR | CHS - Cutting steel members in Riser 2 Level 7 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-05-25 | 2018-06-15 13:51 | 21 | 2016-10-18 14:20 | Architectural - Flooring | 3500 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Management Problem - Other management problem | Completed |  | There was a clash with the installed dry riser in Riser 2 at Level 7 at CHS. In order to allow the steel work to proceed the steel members were notched as per the drawings and photos attached. Additionally the decking was also notched to allow installation.
| 02SL - Stations (LUL) | Cxxx-NCR-001791 | NCR | Phase 7 - Disused Roads Incorrectly fabricated connection holes of beam mark [15542] |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-02-14 | 2017-03-02 17:06 | 16 | 2016-10-06 14:35 | Civil - Civil Engineering General | 10000 |  | Manufacturing Defect | Rework | 2 (6-60k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | The drilled holes in both ends of beam 15542 (610 x 305 UB 238) do not match the existing holes in the steel beam previously erected marked 15508 (610 x 305 UB 113) and the integral lift shaft beam marked 15216 (610 x 305 UB 149). The beam [15542] was site drilled and fitted temporarily to ensure stability of the structure until further checks were made. Following site dimensional and stability checks it was determined that the holes in beam 15542 were incorrect and it was confirmed it was acceptable to remove the beam.
| 02SL - Stations (LUL) | Cxxx-NCR-001792 | NCR | LULO Steelwork - Phase 7 - Beam [15510], incorrect setting out of shear studs |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-12-02 | 2016-11-09 09:36 | -23 | 2016-10-07 13:35 | Civil - Civil Engineering General | 3500 |  | Manufacturing Defect | Repair | 3 (3-6k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | LULO Steelwork - Phase 7 - Beam [15510] The setting out of the 'double row' shear studs along beam [15510] were observed to be incorrect. With the metal decking installed, it is observed that the shear studs are located in line with the apex of the deck profile and not at the trough. Attached (word document) is the fabrication drawing of the beam and a site photograph (.jpeg) of the top flange of beam 15510 showing the shear studs as they are. The photograph is marked with yellow arrows of where the studs should have been, the yellow arrows are indicative of the position that the shot fired studs will be attached to the beam in line with the deck trough.
| 02SL - Stations (LUL) | Cxxx-NCR-001795 | NCR | CHS - Cast-in Drainage |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-08-31 | 2017-10-24 06:33 | 54 | 2016-10-10 14:33 | Civil - Utilities Engineering | 15000 |  | Damaged | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Reduction of cast-in drainage capacity due to cementitious build up, as per attached report.
| 02SL - Stations (LUL) | Cxxx-NCR-001796 | NCR | LULO - Steelwork - Phase 2 - Gap between end plate and column and end plate |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-03-01 | 2017-02-28 08:46 | -1 | 2016-10-11 10:47 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There's a gap between the end plate of floor beams, mark 9113, 9119, 9120 & 9137 and the column flange of lift shaft 7, mark 9116. [Refer to attachment for mark up locations]
| 02SL - Stations (LUL) | Cxxx-NCR-001797 | NCR | CHS - Blockwork - L7 Missing __ I-I |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-02-01 | 2017-02-01 14:28 | 0 | 2016-10-12 10:18 | Architectural - Brickworks/Blockworks | 5000 |  | Workmanship | Rework | 3 (3-6k) | Complete | Personnel Error - Inattention to detail | Completed |  | On Level 7, __ I-I, which is between Rooms 7/668 and 7/663, has been missed. The wall was constructed out of fair faced blockwork, omitting the __. These rooms are now inaccessible due to use of the hoist void for material movement L7 -> L8.
| 02SL - Stations (LUL) | Cxxx-NCR-001798 | NCR | CRL Platforms - Westbound - Ch 10382 Manhole out of position |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-11-21 | 2016-11-14 13:56 | -7 | 2016-10-12 14:46 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | A Builders Work Hole, in the westbound platform at chainage 10382, has been cast in the incorrect position. The correct position of the centre of the __ is 4.926m from the track centre line. The centre of the __ has been cast at 5.376m from the track centre line, therefore is 450mm out of position. The most likely cause is a calculation error when calculating the offset of the box out corners.
| 02SL - Stations (LUL) | Cxxx-NCR-001799 | NCR | CHS - Riser 3 Level 6 Installed at Incorrect Level |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-07-31 | 2017-08-29 07:38 | 29 | 2016-10-18 14:08 | Architectural - Flooring | 4750 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The riser floor steel and metal flooring in Riser 3 Level 6 has been installed 150mm below design FFL
| 02SL - Stations (LUL) | Cxxx-NCR-001800 | NCR | Crossrail Platform Tunnels - Westbound __ locations |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-11-26 | 2016-11-23 10:23 | -3 | 2016-10-17 13:28 | Civil - Civil Engineering General | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | This NCR details incorrect builders works holes in the westbound platform.
| 02SL - Stations (LUL) | Cxxx-NCR-001801 | NCR | LULO Interim Station - FCD not raised for CCTV Camera Blind Spot |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-11-27 | 2016-11-07 10:36 | -20 | 2016-10-18 07:31 | Communications and Control Systems - CCTV | 0 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Due to a planned hoarding move on platform 2, a CCTV blind spot was created. An additional CCTV camera is required to cover the blind spot. This NCR has been raised, due to the fact that an FCD had not been raised to cover the design and acceptance of the new camera's location and specification.
| 02SL - Stations (LUL) | Cxxx-NCR-001802 | NCR | LULO GSM Drop Bolts drilled in incorrect location |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-12-09 | 2016-12-08 14:18 | -1 | 2016-10-18 09:19 | Architectural - Ceilings & Soffits | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | There has been a number of drop bolts drilled at the incorrect location according to Cxxx-FCD-001635 'FCD GSM Drop Bolt Setting Out Grid'.
| 02SL - Stations (LUL) | Cxxx-NCR-001803 | NCR | CHS - Pre-Cast Stairs - Fabrication without Sample Acceptance Form |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-01-07 | 2016-12-30 08:34 | -8 | 2016-10-19 12:47 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Pre-cast stairs, Stair 42 and Stair 43, have been fabricated without an approved Sample Acceptance Form for finish to the units. The sub-cert will be Cxxx-C-CER-D061-53022, and will be added when available on eB.
| 02SL - Stations (LUL) | Cxxx-NCR-001804 | NCR | LULO - East Stair Shaft Cores For Cladding dowels |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-12-05 | 2016-12-01 14:03 | -4 | 2016-10-26 09:46 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The design for the __ Pre-cast concrete panels requires a dowel fixing at the base of each panel as previously detailed in Cxxx-RFI-002547. To facilitate the dowel a number of 50 mm cores need to be drilled 150mm deep into the ESS ground beam. In 2015 the Contractor has cored 4 of these locations on the East side of the lift shaft however following a recent survey it appears that the cores were set out in the wrong location.
| 02SL - Stations (LUL) | Cxxx-NCR-001805 | NCR | Timescale for primer application on Fireproofing exceeded |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-12-15 | 2016-12-09 12:55 | -6 | 2016-10-27 13:58 | Structural Engineering - Surface Treatment | 1500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | __ PSK 101 is a single pack, multi purpose synthetic latex, water based emulsion for use as a sealer and keycoat as a component of the __ __ integrated fire protective coating system. __ PSK 101 application guide (attached) states maximum over coating time is 2 months with either more __ PSK 101 or __ __ MII. The beams on the Phase 4/5 steelwork above LO were sprayed with CAFO PSK 101 in July 2016. All of the beams, except 3, were sprayed the next month, meaning they are currently still exposed with the first single layer of __ PSK 101. Specification Cxxx-__M-A-RSP-D061-57009
| 02SL - Stations (LUL) | Cxxx-NCR-001806 | NCR | CRL Platforms - Eastbound Blocked UTX duct` |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-07-01 | 2017-06-08 08:17 | -23 | 2016-10-27 15:23 | Civil - Civil Engineering General | 4000 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In the eastbound tunnel there are three UTX's. This NCR has been raised to cover a defect in the east end UTX. One of the Cxxx Signal ducts is currently blocked with what we assume is concrete (See attached sketch). The blockage is located 3.6m from the northern side of the duct. Please note there are 8 spare ducts in this location.
| 02SL - Stations (LUL) | Cxxx-NCR-001807 | NCR | LULO - WLL - Lift Shaft 5 - Missing Concrete Records for Pit Slab |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-01-06 | 2017-01-03 13:00 | -3 | 2016-10-28 14:27 | Civil - Civil Engineering General | 2000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | The Pit Slab for the West Lift Lobby Lift Shaft (Lift 5) was poured on the 08/01/2016. Concrete cubes were taken at the stage of the pour however the cubes were lost onsite and not sent to TUCA to be tested.
| 02SL - Stations (LUL) | Cxxx-NCR-001808 | NCR | LULO - WLL - Lift Shaft 5 - Concrete Records for Liner Walls (1st Pour) - Concrete cubes crushed on wrong dates |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-11-10 | 2016-11-09 15:44 | -1 | 2016-10-31 11:09 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | WLL Lift Shaft 5 was completed in several pours at different heights. The Liner Walls were poured on the 19/03/2016 (1st pour) and on the 29/03/2016 (2nd pour). The test dates for the 1st pour were wrong and the cubes were older than they should have been. Concrete cubes were crushed at 2, 10, 11, 17, 17, 38, 38 and 66, 66 days. However, all cubes crushed for this pour achieved the minimum required for a C40/50 concrete mix.
| 02SL - Stations (LUL) | Cxxx-NCR-001809 | NCR | CHS - Pre-Cast Stairs - Provision of Accepted Sample |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-09-07 | 2018-05-29 16:54 | -101 | 2018-05-10 07:43 | Structural Engineering - Pre-cast | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Duplicate of Cxxx-NCR-001803
| 02SL - Stations (LUL) | Cxxx-NCR-001810 | NCR | Platform Tunnels - CP3 Incorrect __ Channel Installation |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-02-23 | 2017-02-01 15:59 | -22 | 2016-11-21 16:30 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | The incorrect type of halfens have been installed on the western face of the CP3 North Central Wall. HTA-CE 40/25 halfens have been installed instead of the HTA-CE 49/30 halfens that were detailed (PTR-1095 attached).
| 02SL - Stations (LUL) | Cxxx-NCR-001811 | NCR | GSM - Welding of Web Stiffeners to main beams without accepted WMS, ITP, and F2 drawings |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2017-01-19 | 2017-01-18 17:02 | -1 | 2016-11-03 13:20 | Structural Engineering - Welding | 2500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Installation was commenced for the steel web stiffeners to the existing main beams to the underside of the GSM building on night shift of 02/11/2016 (see attachment "Att 01 - Web Stiffeners") . This work was commenced without the following accepted documentation; ITP (Cxxx-__M-C-ITP-D061_WS106-53060) - Rev 1.0 Code 3. - Rev 2.0 submitted to CRL on 02/11/16. Not yet coded. Works Method Statement (Cxxx-__M-C-GMS-D061_WS106-53055) - Rev 1.0 excluded welding operations therefore N/A to this NCR. - Rev 2.0 submitted to include welding operations. Submitted to CRL 31/10/16 and forwarded to LU for No Objection on 01/11/2016. Document currently under review by LU and has therefore not received a Code 1 from CRL. F2 Drawings (RIR Cxxx-__M-C-LRG-D061-50007 Rev. 893.0) - 4x F2 drawings submitted on the above RIR on 06/10/16. Drawings not yet approved. - F2 drawings highlighted a discrepancy between location of service penetrations made known to Cxxx based on previous __ design information and revised information used for setting out on site that had not been formally communicated to CRL/Cxxx. Further information provided by __ on 26/10/16 to facilitate Cxxx review (see attachment "Att 02 - Further Info"). - The discrepancy necessitated Cxxx to carry out a further set of calculations justifying the relocation of the penetrations in the beams. This is currently underway.
| 02SL - Stations (LUL) | Cxxx-NCR-001812 | NCR | Upper Concourse - Slot erroneously cast as __ |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-12-15 | 2017-01-09 11:58 | 25 | 2016-11-03 15:33 | Civil - Structural Engineering | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | With reference to Cxxx-FCD-001655 _ LULO Station Entrance and Concourse _Final Cast In Slots, Cxxx-RFI-004172 R _ LULO Slab Penetrations _ Best available info,SW&RF trimmers and Cxxx-__M-E-DDA-D061_WS106_1-31601 slot NCR markup, it is noted that the 35mm deep slot shown on the markup was cast as a Builder’s Works Hole. Rebar trimmers were installed as per detail ‘1a’ on drawing Cxxx-HYD-S-DDL-D061_WS106_A-77739. The underlying metal decking remains in place.
| 02SL - Stations (LUL) | Cxxx-NCR-001813 | NCR | GSM Building - Modification of trimmers brackets |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-01-20 | 2017-01-20 12:50 | 0 | 2016-11-04 18:32 | Structural Engineering - Steel Member | 5000 |  | Workmanship | Rework | 3 (3-6k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | 3no clashes have been identified between existing GSM stiffeners and new trimmer steel brackets. To overcome these clashes 2no options were envisaged: - Offset the trimmers structures - Modify the brackets The preferred option was to be submitted for Cxxx approval via an FCD. __ site team decided to modify the brackets in 2no locations on site. This was done after consulting with __ design team to confirm modified brackets would be acceptable. But it was done without __ agreement and before an FCD was submitted to CRL/Cxxx for approval. Brackets have been installed 03/11 nightshift.
| 02SL - Stations (LUL) | Cxxx-NCR-001815 | NCR | GSM LULO mortar joints to exterior wall remedials |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-01-08 | 2017-01-06 17:41 | -2 | 2016-11-09 18:36 | Architectural - Brickworks/Blockworks | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | It has come to the attention of __ that areas of the exterior wall remedial blockwork have not been sufficiently jointed full depth with mortar. The attached photos and marked up drawing show areas which were inspected on 09/11/2016.
| 02SL - Stations (LUL) | Cxxx-NCR-001817 | NCR | LULO - MEP - ITP not resubmitted within the period for reply |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-02-01 | 2017-01-10 15:56 | -22 | 2016-11-10 11:16 | Electrical - Electrical Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The LU/LO Earthing & Bonding ITP
| 02SL - Stations (LUL) | Cxxx-NCR-001818 | NCR | DSS - MEP - Works proceeding without an ITP - 2nd & 3rd fix electrical installation |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-01-09 | 2017-01-05 10:48 | -4 | 2016-11-10 11:22 | Electrical - Electrical Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | DSS – Level 1, Transformer Rooms TR1 & TR2. Lighting has been installed without an ITP in place
| 02SL - Stations (LUL) | Cxxx-NCR-001819 | NCR | CHS - MEP - Works Starting without an ITP - Distribution Board Installation |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-01-09 | 2017-01-05 10:47 | -4 | 2016-11-10 13:20 | Electrical - Electrical Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Distribution Boards have been installed in CHS with no ITP in place
| 02SL - Stations (LUL) | Cxxx-NCR-001821 | NCR | GSM Building - Dry packing between trimmer and slab |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-01-13 | 2017-01-13 11:15 | 0 | 2016-11-10 20:05 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Through Cxxx-RFI-004101, it has been agreed to install dry-packing between steel trimmers and GSM slab. The agreed depth of dry packing was 10-20mm. In 1no location in the GSM building, the gap between trimmer and slab is between 50 and 60mm. It is not possible to modify the trimmer to reduce this gap, and so the thickness of dry packing will be increased in this instance.
| 02SL - Stations (LUL) | Cxxx-NCR-001822 | NCR | LULO-MEP TTH UPS installed in CER without approved MCR |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-03-14 | 2017-01-03 12:44 | -70 | 2016-11-14 11:21 | Electrical - General | 1500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other management problem | Completed |  | UPS (quantity 2) have been installed in the TTH CER room, without an approved MCR being in place prior to the works commencing .
| 02SL - Stations (LUL) | Cxxx-NCR-001823 | NCR | LULO-MEP TTH POM room - Cable uncontained |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-03-14 | 2016-12-07 14:49 | -97 | 2016-11-14 12:57 | Communications and Control Systems - General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | TTH POM room has an uncontained coaxial cable running from dado trunking to the CCTV monitor. See attached photographs IMAG2830 and IMAG2831
| 02SL - Stations (LUL) | Cxxx-NCR-001824 | NCR | LULO-MEP TTH SSO room - Cable uncontained |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2016-12-15 | 2016-11-28 08:45 | -17 | 2016-11-15 13:04 | Communications and Control Systems - General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | A coaxial cable is uncontained and incorrectly terminated to a junction box under the desk in the SSO.
| 02SL - Stations (LUL) | Cxxx-NCR-001825 | NCR | LULO-MEP TTH CCTV Matrix Table incorrect |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-03-15 | 2016-11-28 09:03 | -107 | 2016-11-15 10:37 | Communications and Control Systems - Crossrail Data Network | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Management Problem - Other management problem | Completed |  | The CCTV cables were re-terminated after being severed during demolition of bridge. However the Excel matrix of installed cameras did not not agree with the actual installation
| 02SL - Stations (LUL) | Cxxx-NCR-001826 | NCR | CRL Platform Tunnels - EB PLAT 014 - Hole in nosing |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-01-15 | 2017-01-08 13:43 | -7 | 2016-11-16 14:08 | Civil - Civil Engineering General | 1250 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The platform nose contains 2 No. ~60mm voids at the construction joint between two adjacent slabs [CJs as per Cxxx-FCD-001743]. This has occurred where silicone has been used to seal the formwork, and excess has not been removed prior to the pour. As this is a construction joint in the slab, these voids do not clash with GFRP U bar (50mm cover). Other deeper GFRP in this location is not visible in the voids.
| 02SL - Stations (LUL) | Cxxx-NCR-001827 | NCR | Phase 7A - Lack of fit in the connection of canopy beam, mark 16024 to column, mark 15535 on grid line DF. |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-01-20 | 2016-12-20 10:40 | -31 | 2016-11-17 16:47 | Civil - Structural Engineering | 3500 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Because of lack of fit in the connection of canopy beam, mark [16024] to column, mark [15535] on grid line DF the 4 no. M20-8.8 bolts cannot be installed.
| 02SL - Stations (LUL) | Cxxx-NCR-001828 | NCR | CRL Platforms - EB - Platform 012 - Concrete mix with the incorrect aggregate |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-03-09 | 2016-12-11 20:04 | -88 | 2016-11-17 13:19 | Civil - Civil Engineering General | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Whilst the concrete gang was finishing Platform slab 012 in the Eastbound tunnel it was noticed that the aggregate was ‘floating’ to the surface of the pour. After investigations on site and spot samples of the concrete mix it was confirmed that the aggregate found ‘floating’ in the mix was Lytag. The sketch attached shows the section of platform slab affected. It is approximately 20m in length. Four loads were received from __, all of which passed flow tests on arrival and showed no signs of segregation. The delivery tickets (all attached) all confirm that the concrete supplied was the approved mix, Line 422, C32/40, 10mm Limestone. The email attached shows __’s response to the concerns raised by __. They believe that the contamination occurred only in the last delivery. Further investigation is required to confirm this, which is detailed in the remedial actions. Please find attached the following: • Photographs of the platform slab 012 with the aggregate 'floating' to the surface • Photographs of the aggregate washed out of surplus concrete. • Scanned copies of the concrete delivery tickets • Scanned copy of the concrete pour record • Email correspondence between __ and Marcus Stevens of __
| 02SL - Stations (LUL) | Cxxx-NCR-001829 | NCR | LULO GSM Head Restraint Connections Drilled In Wrong Location |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-02-03 | 2017-02-01 18:31 | -2 | 2016-12-05 10:22 | Structural Engineering - Steel Member | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | Connections for head restraint steelwork drilled to wrong offset in overhead beam. This affects the beam on gridline G3 between GK and GL - photo attached to this NCR.
| 02SL - Stations (LUL) | Cxxx-NCR-001830 | NCR | PG13 Pile cap - concrete cubes failing at 56 days |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-01-13 | 2016-12-20 12:17 | -24 | 2016-11-22 12:55 | Civil - Civil Engineering General | 2000 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Cubes were taken while pouring pile cap of PG13. The last cubes were crushed at 56 days, the results are: 42 and 43.2 N/mm2, i.e. an average of 42.6 N/mm2. The concrete used was a C40/50 concrete. therefore the cubes are failing the compressive strenght test.
| 02SL - Stations (LUL) | Cxxx-NCR-001831 | NCR | CHS - L8 - Screed & M&E Interface |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-08-04 | 2018-12-11 10:44 | 129 | 2018-04-06 12:22 | Mechanical - Public Health Engineering | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Under Cxxx-__-PTR-1778 (attached), an additional area of screed was defined, under Riser 3 and areas shown. A collar connecting the lift-pit drain pipe to the cast-in drainage was not considered in this design change. A cast-iron sleeve was placed around the collar, as shown in the attached, and screeded-in.
| 02SL - Stations (LUL) | Cxxx-NCR-001832 | NCR | LU Cross Passage - LUX Level Failure (Emergency lighting) and Failure to report prior to Handback |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2017-01-31 | 2017-02-08 09:51 | 8 | 2016-11-21 16:25 | Electrical - Lighting | 3000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The relocated LU Cross Passage between Platform 1 and 2 of the HCDL was opened to the public on the morning 21/11/16 following the Week 34 possession. This was done without evidence in place of compliant LUX levels from newly installed luminaires within the cross passage. 1. LUX plots for both normal and emergency lighting were received by CRL @ approx. 11:00 on 21/11/16 - these are attached to this NCR (Att 01 & Att 02). 2. The LUX levels for emergency lighting were non-compliant with LU Standard S1066. Two luminaires were not functioning on emergency mode meaning lux levels were non-compliant (in emergency mode) where the cross passage joins Platform 2. Following site investigations during the afternoon of 21/11/16 it was found that this was due to the designated emergency luminaires not having been properly connected, therefore the emergency lighting was not operational at time of handback. 3. The above issues were not communicated to CRL or LU at any point prior to handback and only became apparent upon receiving the plots mid-morning. This the seventh NCR raised on Cxxx relating to LUX level failures as well as Cxxx-EWN-01846. The previous NCRs are linked below.
| 02SL - Stations (LUL) | Cxxx-NCR-001833 | NCR | CHS - Level 7 - Section B-B - Fire Main Installed Outside __ |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-10-11 | 2018-09-14 06:53 | -27 | 2018-07-03 07:50 | Fire - Fire Systems & General | 2000 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Fire main installed outside of a designed __. Blockwork has been left short to accommodate unplanned service. A new builders work hole have been assigned for this and will be labelled accordingly
| 02SL - Stations (LUL) | Cxxx-NCR-001834 | NCR | CHS - Riser 4 Level 3 UKB203x102x23 fabricated incorrectly |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-03-06 | 2017-03-14 17:22 | 8 | 2016-11-22 15:14 | Architectural - General | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The main primary member (UKB203x102x23) highlighted in the attached drawing of Riser 4 Level 3 has been fabricated incorrectly. The flange plate at the southern end of the beam has been welded at the incorrect centres (87mm NOT 132mm). This means that the UKA80x80x6 highlighted is installed in the incorrect orientation and is out of design tolerance.
| 02SL - Stations (LUL) | Cxxx-NCR-001835 | NCR | DSS - Track slab and W08-03NS / W08-04NS setting out |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-01-03 | 2017-01-03 15:59 | 0 | 2016-11-24 12:06 | Civil - Civil Engineering General | 1000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | The Contractor is currently constructing the trackslab and walls through DSS. Due to the inconsistencies in the drawings the line of the track slab / walls has been set out and cast incorrectly on site. Please see the document attached which details the NCR.
| 02SL - Stations (LUL) | Cxxx-NCR-001836 | NCR | GSM Building - Trimmers - On site deviations |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-03-10 | 2017-03-10 12:37 | 0 | 2016-11-23 14:15 | Structural Engineering - Steel Member | 1000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | This NCR captures 2no site adaptations, decided during installation, of the GSM trimmers. None of these changes have a knock-on effect on MPSPS design. 1. Trimmer located between gridlines G6-G7/GJ-GK. Due to the proximity with the retaining wall it was not possible to install the beam mark 2646 closer to the retaining wall, this beam was moved approximately 100mm. 2. Trimmer located between gridlines G2-G3/GK-GL. There was a clash between the intended location of the trimmer, and an existing stiffener. Existing stiffeners were not shown on __/Cxxx drawings. To overcome the clash, the whole trimmer was moved 100mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001837 | NCR | LULO_ESS___ PCC Cladding Cube Results |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-02-28 | 2017-03-24 17:05 | 24 | 2016-11-25 11:24 | Structural Engineering - Pre-cast | 35000 |  | Manufacturing Defect | Rework | 2 (6-60k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | __ PCC panels for ESS have achieved a concrete strength equivalent to a grade C30/37 concrete rather than the specified C40/50. Reviewed structural calculation under MDC Cxxx-__M-C-CER-D061_WS106-53260 (referenced) demonstrates that reduction in concrete compressive strength has no structural capacity implications. Implications relating to durability has been addressed under MCR Cxxx-__M-A-LRC-D061_WS106-50492 (referenced) which consists in coating the external face of the panel with __, also provides an extended design life of 120 years. The email attachment “FW_ Vetrofluid Q & A” contain information stating that Anti-graffiti coat can be applied on top of __. The __ will be applied prior to installation on __'s site. All concrete cubes results received from __ are attached. Please Note: PTR raised to __ under number Cxxx-PTR-2005 (attached) contains __ response which states that structural capacity of PCC panels has to be reviewed by sub-contractor (__) which actually is covered under MDC Cxxx-__M-C-CER-D061_WS106-53260
| 02SL - Stations (LUL) | Cxxx-NCR-001838 | NCR | LULO-MEP Cross Passage. Comms works not completed before end of possession |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-01-04 | 2016-12-16 13:34 | -19 | 2016-11-25 14:45 | Communications and Control Systems - General | 500 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other management problem | Completed |  | Quantity 2 CCTV cameras and Quantity 2 PAVA Speakers were not fully functional at the station handback to LU on 21 November after the possession. The CCTV cameras were fitted and electrically working, but neither was displaying a compliant image. The PAVA speakers were not functional and required terminating.
| 02SL - Stations (LUL) | Cxxx-NCR-001839 | NCR | CHS & DSS - MEP - Use of Non Approved Material - Fire Main Pipework |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-06-06 | 2017-02-21 13:01 | -105 | 2016-11-28 09:53 | Materials - Approval | 10000 |  | Material | Rework | 2 (6-60k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | During a surveillance undertaken by the Quality Team, a non-approved materials was found to have been installed in CHS & DSS. Temporary Pipework installed between level 6 up to Level 1 (aprox 60m between both) is not compliant with the approved MCR (MCR 001437). The current MCR approved is for __ Install Plus Pipework however part of the pipework has been provided by different manufacturer. It is not clear whether the replacement pipework is CE marked.
| 02SL - Stations (LUL) | Cxxx-NCR-001840 | NCR | CRL Platforms - EP1 As-built Tolerances |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-01-07 | 2016-12-12 10:06 | -26 | 2016-11-28 12:44 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The asbuilt survey has been carried out on EP1 and shows two areas to be out of the required tolerance. The EP1 slab will be covered by 150mm of screed, as shown in Cxxx-__M-A-DDB-D061_WS106_Z-10409. __ have been contacted regarding the walls (Please see attached email response from __ MEP Design manager) EP1 Slab Chainage 05: +0.012m EP1 Wall Chainage 15: -0.018m
| 02SL - Stations (LUL) | Cxxx-NCR-001841 | NCR | RJS installing Blockwork on GSM Level 1 (SE Corner – Plant Room) using ‘historic’ drawings (P06 & P01) and not the ‘current’ and ‘approved’ versions (P08 & P02) |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2017-02-28 | 2017-02-28 10:56 | 0 | 2016-11-28 13:55 | Architectural - Brickworks/Blockworks | 1000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | A planned Crossrail surveillance was undertaken on 25th November 2016 to look at __’s adherence to their Control of Drawings Procedure Cxxx-__M-O4-GPS-D061-50002. Activities in progress were inspected during the site visit where the drawings were checked for currency and acceptance. One of the activities witnessed was the installation of Blockwork at GSM Level 1 (SE Corner – Plant Room) being undertaken by RJS. The RJS operatives provided the drawing pack they were using for installation. Two drawings were checked appropriate to the installation with the revisions as detailed (and shown in the attached photos); ‘Setting Out Plan Level 1’ Cxxx-__M-A-DDA-D061_WS106_1-10252 (P06) and ‘Plant Room 1/769’ Cxxx-__M-A-DDC-D061_WS106_1-17129 (P01). The __ engineer also attended the site visit where drawings were presented from the __ site folder. On checking the drawings in the folder, *10252 was at revision P07 and *17129 was at revision P02. Following subsequent review on eB, it was identified that the ‘current’ and ‘approved’ revision of *10252 was P08, which was incorporated within RIR revision 904 which was Code 1 2nd November 2016. As such RJS were working to a drawing that was two revisions old, and to a drawing that formed RIR revision 766 which was Code 3 16th May 2016. In addition, the __ engineer also had the incorrect drawing within the site folder. Moreover, it was also identified that the ‘current’ and ‘approved’ revision of *17129 was P02; however this formed RIR revision 766 which was Code 3. RJS were again working to a drawing that was ‘historic’ and not ‘current’. Control of Drawings procedure section 6.7 ‘Control of Drawings on Site’ states “Only the latest accepted drawings are allowed on site. The engineer responsible for an area of work is responsible for ensuring that works are constructed to the correct revision. Regular reviews of site files against the latest RIR will be undertaken to ensure compliance.” In both instances, the process for controlling drawings had failed; including those processes for ensuring new revisions of drawings are disseminated to site engineers and specialist sub contractors.
| 02SL - Stations (LUL) | Cxxx-NCR-001844 | NCR | CHS - Installation of kick flats in risers without an approved design |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-02-28 | 2018-02-23 12:54 | -5 | 2016-11-29 18:44 | Architectural - General | 3367.5 |  | Design | Rework | 3 (3-6k) | Complete | Management Problem - Other | Completed |  | Kick flats have been installed in Risers 1, 3 and 4 at Cambridge Heath Shaft without a CRL accepted design.
| 02SL - Stations (LUL) | Cxxx-NCR-001845 | NCR | CHS - MEP - Works Commencing without an approved ITP - fibre cable install |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-01-28 | 2017-01-10 09:22 | -18 | 2016-11-29 15:49 | Communications and Control Systems - Fibre Optic Network | 1500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Fibre Cable Install has commenced without an accepted ITP in place
| 02SL - Stations (LUL) | Cxxx-NCR-001846 | NCR | DSS - Coupler installation track slab & PTE corbel |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-02-08 | 2017-02-06 08:57 | -2 | 2016-12-01 12:50 | Civil - Civil Engineering General | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Refer drawing: Cxxx-__M-C-DWG-D061_WS105-51566-C01 The PTE Corbel reinforcing detail shows the requirement for B20 threaded bars and A12 couplers to be used to join the Track slab and PTE corbel. Refer highlighted section in the Attachment. The DSS track slab has been poured without installation of couplers at the Eastern edge adjoining the PTE Corbel.
| 02SL - Stations (LUL) | Cxxx-NCR-001847 | NCR | __ - used without approved MCR |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-01-08 | 2017-01-04 17:23 | -4 | 2016-11-29 17:07 | Architectural - Flooring | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | __ ES5 Perimeter flanking strip. (spec ref: JM10.1215) was used on site in advance of the MCR approval. The use of __ within the shafts was not fully identified as required until the PTR-1805 issued on FCD-001688 was recieved. __ MCR rev 1 was rejected in august with no action taken to resubmit
| 02SL - Stations (LUL) | Cxxx-NCR-001848 | NCR | CRL West Platform Invert_ Work commenced without an approved ITP- fibre cable install |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-02-01 | 2017-01-26 07:57 | -6 | 2016-11-30 07:46 | Communications and Control Systems - Fibre Optic Network | 2000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Fibre Cable Install has commenced without an accepted ITP in place.
| 02SL - Stations (LUL) | Cxxx-NCR-001849 | NCR | DSS - CRL Platforms - Eastbound - Track slab interface |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-04-01 | 2017-03-23 17:30 | -9 | 2016-11-30 11:47 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Contractor is currently constructing the trackslab at the DSS – Platform Tunnel Eastbound interface. It has been found that the Construction Joint of bay TB201 has been located 300mm to the East of the design position. The sketches attached detail the position.
| 02SL - Stations (LUL) | Cxxx-NCR-001850 | NCR | DSS - WA-03S Coupler Installed Incorrectly |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-03-01 | 2017-03-01 17:00 | 0 | 2016-12-01 13:54 | Shafts - Shafts General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Couplers (Bar Mark 06 on drawing Cxxx-__M-C-DWG-D061_WS105-51390) have been installed at the incorrect height.
| 02SL - Stations (LUL) | Cxxx-NCR-001851 | NCR | CRL Platforms - CP3 and EP2 As built tolerances |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-01-11 | 2016-12-12 10:02 | -30 | 2016-12-02 16:30 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The asbuilt survey has been carried out on CP3 and EP2. It shows some areas to be out of the required tolerance. Please see list below and attached asbuilt survey. The CP3 slab will be covered by 150mm of screed, as shown in Cxxx-__M-A-DDB-D061_WS106_Z-10409. The benching does not have any applied finishes Cxxx-__M-A-DDB-D061_WS106_Z-10409. __ have been contacted regarding the walls (Please see attached email response from __ MEP Design manager) CP3 Asbuilts Chainage 07 Wall 2 = -0.016mm and -0.018m Chainage 10 Wall 2 = -0.020mm and -0.018m Chainage 15 Benching between walls = +0.016mm Chainage 20 Slab = +0.012m Chainage 25 Slab = +0.016m Chainage 30 Benching = +0.020 and +0.021 Chainage 35 Slab = +0.012 and +0.015 Benching = +0.033 and +0.031 Chainage 40 Slab = +0.012 and +0.016 Benching = +0.037 EP2 Asbuilts Chainage 10 Wall 7= +0.019 and +0.012 Chainage 15 Wall 7= -0.015
| 02SL - Stations (LUL) | Cxxx-NCR-001852 | NCR | Pile Group 20 - Lost casings within pile 111 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-03-07 | 2017-03-07 14:58 | 0 | 2016-12-05 13:32 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | During grouting of pile 111 the grout level was brought up to the piling platform. The temporary casings were then removed. The Rig operator rotated the casing out clockwise, which caused them to undo. This resulted in 4 m of casing being left in the ground. This also meant the grout could not be topped up to the required level after slumping. The final grout level was recorded as approximately 108.95 m AOD, 400 mm below the pile cut off level. The top of the 4 m length of casing left in the ground was approximately 106.150 m AOD, 3.2 m below the pile cut off level. The reinforcement was installed to the required tolerance.
| 02SL - Stations (LUL) | Cxxx-NCR-001853 | NCR | GRC components arrived on site on pre delivery inspection prior to unloading the items it was noted that 2 items had been damaged in transit. |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-08-04 | 2018-04-25 07:10 | -101 | 2018-04-06 12:26 | Architectural - General | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | Prior to unloading the __ tusk plinths the logistics Manager undertook a pre-delivery inspection. During the inspection found 2 areas of damage. These were subsequently photographed and the items safely unloaded.
| 02SL - Stations (LUL) | Cxxx-NCR-001855 | NCR | Use of non-accepted drawing in carrying out the works |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-02-06 | 2017-02-06 08:50 | 0 | 2016-12-08 10:52 | Civil - Geotechnical Engineering | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | To allow for the construction of Piles P110-P116 for Pile Group 20, __ have used a 3rd Party pile cage fabrication drawing (Cxxx-__M-C-DWG-D061_WS106-53210) which was not approved by CRL. The original P01 revision was reviewed by CRL and Cxxx, and approval for uprev to C01 was provided. The drawing revision was updated to C01 and uploaded to EB on 26/07/2016, via Transmittal Cxxx-INT-0015013. This was not however submitted via a CCM by __ Doc Control to CRL. The drawing was then subsequently used in the construction of the piles in two phases, between the dates of 27/07/2016 and 02/08/2016 and 28/11/2016 and 02/11/2016. The non-approved status of the drawing was spotted until IRF-LULO-1000 was submitted to the CRL Field Engineer.
| 02SL - Stations (LUL) | Cxxx-NCR-001857 | NCR | DSS - Level 8 - Wall W08-04NS and W08-03NS L bar installation |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-01-22 | 2017-01-17 09:37 | -5 | 2016-12-13 12:35 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please see the marked up RC drawings and photographs attached which detail the incorrectly installed L-bars in wall W08-03Ns and W08-04NS. One L-bar has been installed rather than two.
| 02SL - Stations (LUL) | Cxxx-NCR-001859 | NCR | CHS - All Levels - Fire Stopping - Mastic Joint Cracking |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-11-30 | 2018-02-06 13:38 | 68 | 2016-12-13 13:36 | Fire - Compartmentation | 2000 |  | System Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Horizontal __ head joints luff coat is splitting, vertical movement mastic joints cracking and delaminating. Multiple locations within the shaft. The will be no project costs associated with this NCR as these works will be undertaken as subcontractor rework
| 02SL - Stations (LUL) | Cxxx-NCR-001860 | NCR | DSS - All Levels - Fire Stopping - Mastic Joint Cracking |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-08-24 | 2017-11-08 14:14 | 76 | 2016-12-13 13:42 | Fire - Compartmentation | 24500 |  | System Defect | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Horizontal __ head joints luff coat is splitting, vertical movement mastic joints cracking and delaminating. Multiple locations within the shaft. There will be no costs to the project associated with this NCR as these works will all be subcontractor rework. As MEP installation is currently ongoing there will be minimal program implications with access and sequencing for reworks - this is the same for NCR-001859 at CHS
| 02SL - Stations (LUL) | Cxxx-NCR-001861 | NCR | GSM Building - __ Spraying in cold weather |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-03-17 | 2017-03-09 09:08 | -8 | 2016-12-15 19:00 | Fire - Compartmentation | 3000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | This NCR captures the shortfall in checking ITP parameters when carrying out Fire protection spraying activities in the LULO section - GSM Building. - On the night of Sunday 04/12/2016, air temperatures were fluctuating between 2-4 degrees, i.e. very close to the limit were spray cannot go ahead - for precise parameters, please refer to ITP C-53040. - The __ tool, used to check substrate temperatures / air temperature / due point / relative humidity was being calibrated and not used. This means that 3no ITP parameters (substrate temperature / due point / relative humidity) were not checked. - Air temperature, was reportedly checked throughout the night but these checks have not been recorded. - In spite of the above spraying activities went ahead, and so did PSK 101 primer application activities. 'Works.pdf' is a location plan showing works carried out on that shift.
| 02SL - Stations (LUL) | Cxxx-NCR-001862 | NCR | Comms & BMS SLD Handover |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-04-20 | 2017-03-14 09:33 | -37 | 2016-12-14 07:52 | Electrical - General | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | __ did not inspect the works before offering to CRL.
| 02SL - Stations (LUL) | Cxxx-NCR-001863 | NCR | Wrong Conduit Used |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-02-20 | 2017-02-21 09:11 | 1 | 2016-12-14 09:28 | Electrical - Cable Management | 20000 |  | Material | Rework | 2 (6-60k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Sub-contractor installed conduit not on the MCR system for Whitechapel
| 02SL - Stations (LUL) | Cxxx-NCR-001864 | NCR | Failure to adhere to ITP witness points |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2017-01-23 | 2017-01-23 17:59 | 0 | 2016-12-14 16:35 | Fire - Detection | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | This NCR refers to cabling installation works commencing within CHS in the CER and FCR rooms to the Fire Alarm system without prior inspection made to the installed conduit as per the attached ITP. (Item 4.1-4.2) Witness points are an integral part of the quality assurance process and as such should be treated accordingly.
| 02SL - Stations (LUL) | Cxxx-NCR-001865 | NCR | Final Dressing of Fibre Optics Incomplete |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-06-07 | 2017-06-06 13:04 | -1 | 2016-12-14 17:26 | Communications and Control Systems - Fibre Optic Network | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Fibre optic cables not installed as per standard issued.
| 02SL - Stations (LUL) | Cxxx-NCR-001866 | NCR | FOSC Cabinets |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-02-24 | 2017-02-21 09:40 | -3 | 2016-12-15 08:17 | Communications and Control Systems - Fibre Optic Network | 1500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | FOSC Cabinets offered up for inspection but failed to produce the paperwork.
| 02SL - Stations (LUL) | Cxxx-NCR-001867 | NCR | DSS & CHS - Failed Inspection - CER Cabinet Installation |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-04-21 | 2017-03-10 14:34 | -42 | 2016-12-15 09:06 | Communications and Control Systems - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | CER Cabinet installation had not started when the IRF was issued, the room was not ready for cabinet installation to proceed. The IRF was not cancelled in advance.
| 02SL - Stations (LUL) | Cxxx-NCR-001869 | NCR | BMS Conduit Install. |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-02-21 | 2017-02-21 09:49 | 0 | 2016-12-16 06:50 | Mechanical - Heating Ventilation & Air Conditioning | 10000 |  | Documentation and Records | Rework | 2 (6-60k) | Complete | Management Problem - Inadequate supervision | Completed |  | Inspection did not commence.
| 02SL - Stations (LUL) | Cxxx-NCR-001870 | NCR | West Lift Lobby Pit Level |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-02-10 | 2017-02-09 12:22 | -1 | 2016-12-20 10:52 | Civil - Civil Engineering General | 2500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The West lift lobby pit level has been cast 25mm too high. In the __ drawing Cxxx-__M-M-DWG-D061_WS106-50038 the level of the pit should be 103.970 however the as-built survey gave an average reading of 103.995m. Following discussions with __ __ have been informed that it is a statutory requirement ( En81-1 / En81-20 ) that the depth of the pit should be 1.6m. Whilst coring the slab for NCR 1807 it was identified that there is 102mm, this was also confirmed with a __ survey (see attached).
| 02SL - Stations (LUL) | Cxxx-NCR-001871 | NCR | HCDL East stair shaft Dowel Holes |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-02-24 | 2017-02-23 14:56 | -1 | 2016-12-20 17:35 | Civil - Civil Engineering General | 2000 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The dowel holes required for the external cladding panels on the east and south side of the East Stair Shaft have been cast in the wrong location. __ have recently cored the new locations using __ drawing Cxxx-__M-A-DWG-D061_WS106-53379 however it has been identified by __' surveyor that these locations do not match the manufacturing drawings.
| 02SL - Stations (LUL) | Cxxx-NCR-001872 | NCR | Damaged Fibre Optics Riser 4, level 6, CHS |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-03-10 | 2017-03-13 10:45 | 3 | 2016-12-20 15:27 | Communications and Control Systems - Fibre Optic Network | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | Fibre optics damaged as they passed through floor penetration from level 6 to level 7.
| 02SL - Stations (LUL) | Cxxx-NCR-001873 | NCR | DSS Level 3 Blockwork - Windpost in incorrect location |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-04-21 | 2017-04-19 10:31 | -2 | 2016-12-22 16:13 | Architectural - Brickworks/Blockworks | 4500 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Windpost highlighted in the attached markup was installed 2.4m out of position (also shown in the mark up) for the sequence of build to allow for the installation of M&E cabinets for SLD dates. The new windpost location clashes with builders work hole BW3 029.
| 02SL - Stations (LUL) | Cxxx-NCR-001874 | NCR | DSS - North Elevation Wall Alignment |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-04-13 | 2017-04-13 12:24 | 0 | 2017-01-03 11:54 | Shafts - Shafts General | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On the North Elevation of Durward Street Shaft two sections of the wall listed below will require scabbling to allow the installation of Precast Concrete Cladding Stainless Steel Support Brackets - 1. Level B between DS3 and DS4 2. Level 1 to Level A at Grid DS1.5
| 02SL - Stations (LUL) | Cxxx-NCR-001875 | NCR | DSS - Level 4 Wall W4-05S Out of Tolerance |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-09-16 | 2017-05-20 09:05 | -119 | 2017-01-09 15:08 | Shafts - Shafts General | 1500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Level 4 asbuilt of wall W4-05S shows the wall is out of tolerance. __ have been notified, please refer to attached PTRs and Asbuilts.
| 02SL - Stations (LUL) | Cxxx-NCR-001876 | NCR | PES Precast Concrete Panels Benchmark |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-06-28 | 2017-06-15 15:39 | -13 | 2017-01-04 17:23 | Civil - Civil Engineering General | 1500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Under clause KH10.2102 of the Cxxx specification Cxxx-ATK-N2-RSP-CR002-00001 Rev 11, there is a requirement to produce a benchmark for acceptance in the form of the first panel produced of each type. This was not carried out prior commencing installation of the panels.
| 02SL - Stations (LUL) | Cxxx-NCR-001877 | NCR | LULO Steelwork - Accommodation Blocks - Lack of Access to the bolts for mark 17047. Proposal to not install this mark. |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-04-22 | 2017-04-07 13:40 | -15 | 2017-01-06 11:44 | Civil - Civil Engineering General | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | Because of a lack of access for bracing mark 17047 the bolts cannot be installed.
| 02SL - Stations (LUL) | Cxxx-NCR-001878 | NCR | LULO Steelwork - Accomodation Blocks - Lack of fit in the connection of beam, mark 17085 to column, mark 17707 on grid line D1/D5. |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-03-28 | 2017-03-28 15:49 | 0 | 2017-01-06 11:51 | Civil - Civil Engineering General | 4000 |  | Manufacturing Defect | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Error by manufacturer in shipping or marking | Completed |  | Because of a lack of fit in the connection of beam, mark [17085] to column, mark [17077] on grid line D1/D5 not all 4 no. M20-8.8 bolts can be installed.
| 02SL - Stations (LUL) | Cxxx-NCR-001879 | NCR | LULO Steelwork - Connection of beam mark 17130 to beam mark 17136 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-02-28 | 2017-02-21 15:36 | -7 | 2017-01-09 17:12 | Civil - Structural Engineering | 4000 |  | Manufacturing Defect | Rework | 3 (3-6k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Because of a lack of fit in the connection of beam mark 17130 to beam mark 1736 on grid line D4, the beam mark 17130 cannot be installed
| 02SL - Stations (LUL) | Cxxx-NCR-001880 | NCR | LULO Steelwork - Lack of fit in the connection of beam mark 16529 and bracing mark 16514 to beam mark 16504 on grid line DH/DA |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-02-28 | 2017-02-27 12:53 | -1 | 2017-01-09 17:34 | Civil - Structural Engineering | 4000 |  | Manufacturing Defect | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Because of lack of fit in the connection of beam mark 16529 and bracing mark 16574 to beam mark 16504 on grid line DH/DA, these members cannot be installed.
| 02SL - Stations (LUL) | Cxxx-NCR-001881 | NCR | LULO Steelworks - Lack of fit in the connection of beam mark 16006 to column mark 16102 on grid line DC/D3 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-02-28 | 2017-02-27 12:57 | -1 | 2017-01-09 17:48 | Civil - Structural Engineering | 2500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Because of a lack of fit in the connection of beam mark 16006 to column mark 76102 on grid line DC/D3, the 3 nos. M20-8.8 bolts cannot be installed.
| 02SL - Stations (LUL) | Cxxx-NCR-001882 | NCR | Fire rated ductwork insulation fixing detail |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2017-02-21 | 2017-02-22 11:56 | 1 | 2017-01-12 07:56 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | The current installation method of fixing thermal insulation to fire rated ductwork is by using self-tapping screws. This method does not accord with the proposals in the MCR which implies rivets and washers
| 02SL - Stations (LUL) | Cxxx-NCR-001883 | NCR | Maintainability/replacement of fire damper |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2017-03-22 | 2017-02-22 10:18 | -28 | 2017-01-12 08:08 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Fire damper will be difficult to remove and replace due to the duct being very close to the structural ceiling and adjacent wall without any special clearance. The removal/replacement of mezz flange bolts and mezz clips are precluded as the duct is tight against the ceiling and the adjacent wall.
| 02SL - Stations (LUL) | Cxxx-NCR-001884 | NCR | LULO GSM Lift Shaft 9 Steel Not Plumb |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-05-01 | 2017-04-27 09:09 | -4 | 2017-01-12 10:11 | Structural Engineering - Steel Member | 2500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Historical NCR-973 was raised to capture the lift shaft steelwork installation out of plumb tolerance, however this was subsequently cancelled on account of it being within NSSS tolerance specs. There is a carry over effect now where the out of plumbness affects installation of the blockwork and possibly the lift internal installations. More information needs to be gathered through the as-built drawings and a detailed survey to make an assessment, but for now blockwork to the lift shaft has been suspended awaiting close out advice on this NCR.
| 02SL - Stations (LUL) | Cxxx-NCR-001885 | NCR | LULO GSM wind posts on Level 2 does not align with header beam cleat |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-12-20 | 2017-12-01 15:57 | -19 | 2017-01-12 12:14 | Architectural - Brickworks/Blockworks | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Subcontractor Problems - Interfacing problems | Completed |  | Wind posts WP8, WP7 and WP11 (reference taken from __ drawing Cxxx-__M-A-DWG-D061_WS106-53523) do not quite align with the pre-installed header beam cleat once installed.
| 02SL - Stations (LUL) | Cxxx-NCR-001886 | NCR | DSS - Missing waterproof checksheets - Sub construction Packages Slab, Walls and Columns Level 6-5 and Level 5-4 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-04-28 | 2017-04-27 16:24 | -1 | 2017-01-13 11:50 | Civil - Drainage | 1500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - No evidence of program review from Contractor's Quality Manager or Management | Completed |  | Missing __-1 waterproofing checksheet for Level 6-5 and level 5-4 Slabs, walls and column. These are required for the submission of Cxxx-__M-O4-LRC-D061_WS105-50049 and Cxxx-__M-O4-LRC-D061_WS105-50050.
| 02SL - Stations (LUL) | Cxxx-NCR-001887 | NCR | Stair 9 Flight 19 Mising Concrete |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-05-18 | 2017-05-16 10:04 | -2 | 2017-03-10 10:35 | Shafts - Shafts General | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Missing concrete on the top eastern side of Stair 9 Flight 19.
| 02SL - Stations (LUL) | Cxxx-NCR-001888 | NCR | DSS Proceeding past witness points |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2017-02-22 | 2017-02-13 10:22 | -9 | 2017-01-13 12:08 | Electrical - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | Installation works continued past hold and witness points without the appropriate inspection's offered or carried out by Crossrail (CRL) in accordance with the accepted Inspection and Test Plan (ITP) procedure. Secondary Cable Management System (CMS) had been installed to non inspected primary CMS, additionally wiring had been carried to secondary CMS that had been installed to primary CMS.
| 02SL - Stations (LUL) | Cxxx-NCR-001889 | NCR | Cable Pulling Lubricant |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-02-22 | 2017-02-16 14:35 | -6 | 2017-01-13 15:25 | Fire - Fire Systems & General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | Incorrect lubricant used for pulling in fire alarm cabling.
| 02SL - Stations (LUL) | Cxxx-NCR-001890 | NCR | CHS Proceeding past witness points |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2017-02-22 | 2017-02-13 10:16 | -9 | 2017-01-13 13:02 | Electrical - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | Installation works continued past hold and witness points without the appropriate inspection's offered or carried out by Crossrail (CRL) in accordance with the accepted Inspection and Test Plan (ITP) procedure. Secondary Cable Management System (CMS) had been installed to non inspected primary CMS, additionally wiring had been carried to secondary CMS that had been installed to primary CMS.
| 02SL - Stations (LUL) | Cxxx-NCR-001891 | NCR | DSS - East Elevation Wall Alignment |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-04-27 | 2017-04-27 17:22 | 0 | 2017-01-17 08:06 | Shafts - Shafts General | 6000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On the East Elevation of Durward Street Shaft three sections of the wall as shown on the attached mark-up will require scabbling to allow the installation of Precast Concrete Cladding Stainless Steel Support Brackets.
| 02SL - Stations (LUL) | Cxxx-NCR-001893 | NCR | CRL Platforms - Eastbound - TB 204-205 Lytag contamination |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-02-27 | 2017-02-27 11:35 | 0 | 2017-01-18 14:07 | Civil - Civil Engineering General | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Whilst the concrete gang was finishing the TB 204-205 upper trackslab pour in the Eastbound tunnel it was noticed that there was some Lytag contamination on the surface. The sketch and photos attached detail the location of the contamination.
| 02SL - Stations (LUL) | Cxxx-NCR-001894 | NCR | CHS - Pre-cast stair dowel locating voids misaligned with dowel bar in corbel |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-08-11 | 2017-08-17 08:09 | 6 | 2017-01-26 15:50 | Civil - Civil Engineering General | 1000 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | When installing the pre-cast concrete (PCC) stairs it was found that units C43/F3 and C43/F6 both contained cast in voids in the incorrect location. This is likely due to movement of the void former during casting of the stair units.
| 02SL - Stations (LUL) | Cxxx-NCR-001895 | NCR | LULO_ESS___ PCC Cladding Panels 2E-09 and 2E-10 Geometric Side Pattern |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-08-01 | 2017-08-01 07:05 | 0 | 2017-01-23 13:25 | Architectural - General | 6000 |  | Manufacturing Defect | Repair | 3 (3-6k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | __ PCC Cladding Panels 2E-09 and 2E-10 were cast without the Geometric Side Pattern in two locations (JH42.1218 - Type EWS-413 Precast Concrete Cladding. Textured flat and curved concrete panels with geometric pattern.a) Location: HCDL Stair 23 (eastern end) external face of external wall). Panel 2E-09 was not cast with the geometric side pattern on a small return (north side - 150mm width) - Please see drawing Cxxx-__M-A-DWG-D061_WS106-53379. Panel 2E-10 was not cast with the geometric side pattern on a small return (south side - 150mm width) - Please see drawing Cxxx-__M-A-DWG-D061_WS106-53379.
| 02SL - Stations (LUL) | Cxxx-NCR-001896 | NCR | CRL Platforms - Eastbound Asbuilt tolerances Ch 10385-10475 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-07-23 | 2017-02-28 09:40 | -145 | 2017-01-24 11:40 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The asbuilt survey has been carried out in Eastbound between chainage 10385 and 10475. Please see attached file for highlighted survey drawings showing the areas which are out of tolerance. The locations outside the required tolerance are summarised below: Chainage 10385m Trackbed wall +0.013m Chainage 10390m Benching between walls +0.016m Platform Slab level +0.012m Trackbed drainage channel +0.016m Trackbed wall +0.011m Trackbed upstand SCL side +0.011m Chainage 10395m Platform Slab +0.014m Trackbed drainage channel +0.024m Trackbed upstand level SCL side +0.011m Chainage 10400m Platform Slab +0.011m, +0.013m, +0.016m Trackbed drainage channel +0.013m Trackbed upstand SCL side -0.012m Trackbed upstand platform side +0.011m Trackbed lower +0.011m Chainage 10405m Platform Slab +0.014m Trackbed upstand platform side level +0.011m Trackbed drainage channel +0.011m Chainage 10410m Benching between walls +0.015m Platform Slab +0.014m and +0.011m Chainage 10415m Trackbed upstand SCL side +0.014m Trackbed upstand Platform side +0.016m Chainage 10420m Trackbed upstand SCL side +0.014m Trackbed wall +0.018m and +0.016m Drainage channel in benching +0.012m Chainage 10425m Trackbed upstand SCL side +0.016m Track drainage channel level +0.014m Trackbed wall +0.024m and +0.013m Benching drainage channel level -0.016m Benching drainage channel +0.012m Platform level +0.012m Chainage 10430m Benching drainage channel level +0.012m Trackbed level +0.012m Chainage 10435m Track bed +0.012m Chainage 10445m Track bed level +0.024 Chainage 10450m Trackbed upstand SCL side -0.011m Trackbed level +0.015m Trackbed upstand +0.015m Platform nosing +0.014m Platform level +0.011m and +0.011m Chainage 10455m Platform nosing +0.015m Chainage 10460m Platform nosing +0.016m Trackbed +0.018m Chainage 10470m Trackbed drainage channel +0.012m Platform Level Chainage 10475m Trackbed upstand -0.014m Trackbed level -0.025m The platform slab will be covered by 150mm of screed, as shown in Cxxx-__M-A-DDB-D061_WS106_Z-10409. The benching does not have any applied finishes Cxxx-__M-A-DDB-D061_WS106_Z-10409. The area between the trackbed upstands will be filled with concrete by Cxxx therefore the small discrepancies/ position in level will not have an effect.
| 02SL - Stations (LUL) | Cxxx-NCR-001898 | NCR | Platform Tunnels - EB halfen omission |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-05-04 | 2017-04-25 12:39 | -9 | 2017-01-24 12:13 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 2 No. halfen channels 7.8m long were omitted in the internal wall, platform 004, Eastbound. The omitted halfens were the two horizontal halfens, in the cable recess, as per Cxxx-RFI-003545 [diagram attached]. Vertical halfens were installed to design.
| 02SL - Stations (LUL) | Cxxx-NCR-001899 | NCR | PES WB Truss T224 incorrect SHS stub height and bolt holes height |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-04-24 | 2017-04-20 15:32 | -4 | 2017-01-24 17:06 | Civil - Civil Engineering General | 2500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | LW Internal NCR 008/17. A SHS stub has been welded at the incorrect height on Truss T224 in the Westbound tunnel. LW Internal NCR 009/17. Truss T224 has two holes at the incorrect height on the bottom of the main splice joint hanger. This means the lower grille bottom bracket fixed to the truss with these holes will be too low if installed as is. See attached LW Internal NCRs containing: • Drawing of Truss to show position of errors on T224 • Overall plan drawing to show position on the Westbound Platform • Photos of correct and incorrect positions
| 02SL - Stations (LUL) | Cxxx-NCR-001901 | NCR | LULO GSM - 2/135 Lift Control Room head restraint beam misalignment |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-04-15 | 2017-03-07 10:43 | -39 | 2017-01-25 11:30 | Architectural - Brickworks/Blockworks | 3500 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The head restraint PFC beams installed to the southern wall of 2/135 Lift Control Room do not align with where the future blockwork wall is to be constructed.
| 02SL - Stations (LUL) | Cxxx-NCR-001902 | NCR | Platform Tunnels - CP1 and EB __s to be cored |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-06-30 | 2017-06-12 08:36 | -18 | 2017-01-31 13:38 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | This NCR details 2 No. __s that do not exist through constructed platform slab. 1) A 250x50mm __ in CP1 This __ was an addition between issue of the IFC drawing [Cxxx-__M-C-DWG-D061_WS106-53146_REV C01] and construction. 2) A 500x300mm __ in the Eastbound platform. This __ was an addition after issue of the IFC drawing [Cxxx-__M-C-DWG-D061_WS106-53122_REV C01] and after construction. Please find attached 2 sketches showing the location of these bwhs.
| 02SL - Stations (LUL) | Cxxx-NCR-001903 | NCR | CRL Platforms - Shrinkage Crack in Wall |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-08-13 | 2017-08-09 12:40 | -4 | 2017-01-30 13:00 | Civil - Civil Engineering General | 4000 |  | Material | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | In the Eastbound tunnel shrinkage cracks have formed on the inner wall in multiple locations between bay 012 and 014. See the attached report for locations and chainages The cracks range in size from approximately 0.3mm to 1.3mm wide and appear to run through the whole wall. This is a repeat from the Westbound tunnel which was captured in NCR-001566
| 02SL - Stations (LUL) | Cxxx-NCR-001904 | NCR | CRL Platforms - CP1 Walls Damage |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-05-30 | 2017-05-15 08:49 | -15 | 2017-01-30 17:00 | Civil - Civil Engineering General | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In the crossrail tunnels - CP1, damage was sustained during striking of walls 5 North and South. The wall has been cracked in four locations.In location one, reinforcement has been exposed. Please see attached marked up drawing and photos.
| 02SL - Stations (LUL) | Cxxx-NCR-001905 | NCR | CRL Platforms - Low Cover on Trackbed |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-04-07 | 2017-03-14 09:06 | -24 | 2017-02-01 17:04 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On track bed E/B T/B bay 205/206 an area of the track bed was poured out of tolerance. The track bed has been surveyed and a sketch showing the difference from design level and the location has been attached to this NCR. The level of top of concrete varies from -38mm to +21mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001906 | NCR | LULO Steelworks - Northern Concourse crossover to DSS - Lack of fit in the connection of DSS floor beams to concrete wall on GL 3.2 and 3.3 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-03-31 | 2017-03-31 15:47 | 0 | 2017-02-02 12:10 | Civil - Structural Engineering | 4000 |  | Design | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Because of a lack of fit in the connections of the lower level beams of the Northern Concourse crossover to DSS, the M30 bolts of floor beams marks 12702 and 12703 on grid lines 3.2 and 3.3 cannot be installed
| 02SL - Stations (LUL) | Cxxx-NCR-001907 | NCR | DSS - Level 1 - Lift 2 structural opening |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-08-25 | 2017-08-15 07:05 | -10 | 2017-02-02 16:54 | Shafts - Shafts General | 2000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | A difference in design from drawing Cxxx-HYD-C-DDB-D061_WS105_Z-23018 C03 to the __ lift design has resulted in the constructed structural opening of liftshaft 2 on level 1 being the incorrect height. The __ drawings require an opening of 2250mm whereas the RC design specified it as 2330mm. The result is that the positioning of the __ Channels that would support the landing door headers and top tracks will be 80mm too high. A full as built site survey is required in order to determine and produce a post fix solution for the positioning of these fixing points for the landing door headers and top tracks
| 02SL - Stations (LUL) | Cxxx-NCR-001908 | NCR | LULO_ESS___ PCC Cladding Panel 2E-13 – Installation Clash |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-05-19 | 2017-05-20 08:15 | 1 | 2017-03-03 08:55 | Architectural - General | 2000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The proposed fixing detail of panel 2E-13 does not work. Unlike previous details the bracket in this location is adjacent to a steel column. This column prevents the plate washer from slotting over the threaded bar thus securing the panel.
| 02SL - Stations (LUL) | Cxxx-NCR-001909 | NCR | LULO_ESS___ PCC Cladding Panel 2E-14 – Installation Clash |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-09-22 | 2017-11-09 10:18 | 48 | 2017-03-03 09:18 | Architectural - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The design of panel 2E-14 did not incorporate a section of the East Stair Shaft portal frame. As a result the panel clashes with this structure therefore a new panel will need to be designed and cast.
| 02SL - Stations (LUL) | Cxxx-NCR-001910 | NCR | LULO_ESS___ PCC Cladding Panels – Packers Installation |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-10-12 | 2019-03-13 12:50 | 152 | 2018-04-06 12:28 | Architectural - General | 2500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | __ have installed packers on the underside of the precast concrete panels that sit on top the existing concrete upstand around ESS Stair 23. A double layer of mastic and backing rod is still required to be installed between the underside of the precast concrete panels and the DPM and in several locations this cannot be installed due to the packers installed to close to the edge.
| 02SL - Stations (LUL) | Cxxx-NCR-001911 | NCR | DSS/CHS RC Works - Lack of notification of defects and as-built survey information |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2017-04-21 | 2017-04-07 15:32 | -14 | 2017-02-08 18:33 | Structural Engineering - Finishes | 2000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Previous Construction - Failure to follow close out process | Completed |  | Extensive portions of the completed RC works in DSS and CHS have not been surveyed for as-built comparison to specification tolerances. This issue largely relates to the slabs, floor finishes, stairs and landings within both DSS and CHS. Some of these areas were completed in 2014. As such the Contractor has not demonstrated that these works meet the Works Information requirements in a timely manner. In lieu of objective as-built survey data, the Contractor has failed to manage the quality and assurance of these works. The absence of as-built survey information increases the likelihood of defects being present within the works that have not been raised and rectified via the NCR process. The risks associated with late and outstanding as-built survey information includes; - Impact to application of architectural floor finishes - Impact to installation of MEP/Comms equipment - Impact to handover of rooms/routes to C6xx contracts - Increase of rework to RC finishes and additional risk to programme The Contractor is to provide the following as a matter of urgency; - Schedule of as-built survey information completed for RC works in DSS and CHS formally submitted to CRL date and those areas outstanding as-built survey to the Project Manager. - Programme for completion of outstanding as-built surveys, submission of surveys to the Project Manager and raising of all required NCRs for agreement of remedial action with the Project Manager. - Mitigation measures to remediate areas that fall outside of specified tolerances and a programme of remedial works to mitigate any impact to future handovers and follow-on trades. - Proposals for preventing reoccurrence of this issue i.e. large-scale lack of progressive assurance.
| 02SL - Stations (LUL) | Cxxx-NCR-001912 | NCR | DSS - Level 5 Floor Out of Tolerance |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-07-23 | 2017-07-28 06:43 | 5 | 2017-02-13 15:56 | Architectural - Brickworks/Blockworks | 19000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | CER 1 and TV MCC Room on Level 5, Durward Street is out of tolerance at points shown on the attached asbuilt.
| 02SL - Stations (LUL) | Cxxx-NCR-001913 | NCR | LULO Concourse Slab Level |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2017-12-13 | 2018-04-03 07:57 | 111 | 2017-02-14 09:57 | Structural Engineering - Structural Engineering - General | 234000 |  | Incorrect Installation | Rework | 1 (>60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As-built survey information is outstanding for the concourse slab. As such, the Contractor is yet to suitably demonstrate that the Works in question have been constructed in accordance with the Works Information. Cxxx-__M-C-RGN-D061_WS106-53070 (issued to CRL 30.01.17) states the following as-built slab levels (SSL) GL02 = 109.593 (+18 mm) GL03 = 109.587 (+ 12 mm) GL06 = 109.600 (+25 mm) GL10 = 109.590 (+15 mm) GL19 = 114.499 (+24 mm) GL20 = 114.720 (+245 mm, assumed typo?) NSCS 10.9.1 states the following tolerances: Permitted global deviation = 12 mm Permitted local deviation = 5 mm The Contractor is yet to confirm the impact of any areas of the concourse out of tolerance, nor provide a full survey of the works. Any remedial works which may be required must be approved by the FDC prior to commencing. Furthermore, the Contractor has informally discussed with the Project Manager deviations outside of the allowable tolerances on the slab.
| 02SL - Stations (LUL) | Cxxx-NCR-001914 | NCR | Platform Tunnels - EB Damage to benching |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-05-20 | 2017-03-30 07:38 | -51 | 2017-02-09 12:20 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | EB benching mass fill concrete was damaged during striking of the benching drainage channel. A section of concrete ~100mm x 500mm has broken away from the pour. Please see attached sketch containing location and photos.
| 02SL - Stations (LUL) | Cxxx-NCR-001915 | NCR | GSM Building - Core not lined up with trimmer steel |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-04-07 | 2017-04-07 14:44 | 0 | 2017-02-20 15:18 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Activity: coring of __ in GSM building level 1. Issue: On 08-02-17 it was noted that 1no trimmer steel did not line up with the __ above. The __ had been set out from GSM level 1. Upon further investigation it appeared that: - Setting out of the hole was correct - The trimmer had been installed in the wrong position - The subcontractor (__) had not clearly understood the purpose of ITP inspection 3.4 (pilot hole). The purpose is to confirm that the trimmer and the hole are both properly set out before coring. The following shift, site team proceeded to modify the trimmer steel to suit the location of the __. Dry packing was also reinstated. Steel coating was not damaged by the coring (as it was protected by the dry packing) and did not require remedial works.
| 02SL - Stations (LUL) | Cxxx-NCR-001916 | NCR | DSS Level 6 OHLE Room __ Door Install |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-11-20 | 2017-11-17 11:34 | -3 | 2017-02-17 11:24 | Architectural - Doors | 2480.76 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | First door install on the project. Originally intended as benchmark door. After install it became evident that there are a number of scratches and imperfections on the door leaves and frame. These are detailed on the attached photos.
| 02SL - Stations (LUL) | Cxxx-NCR-001918 | NCR | LULO Steelworks - Northern Concourse Stair 29 - Clash of bottom of Stair 29 support beam mark 11202 with DSS pre-cast concrete cladding panel |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-03-27 | 2017-03-27 10:16 | 0 | 2017-02-15 11:48 | Civil - Structural Engineering | 4500 |  | Design | Repair | 3 (3-6k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | There is a clash between the bottom of Stair 29 support beam, mark 11202 (RHS400/200/16.0) and the T-piece bracket, mark 11257 (PL15) with the pre-cast concrete cladding panel installed on DSS wall.
| 02SL - Stations (LUL) | Cxxx-NCR-001919 | NCR | LULO Steelworks - South Accommodation Block - Clash between floor beam mark 19021 with existing vertical cables on OLOD wall near Grid Line 22 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-03-27 | 2017-03-27 13:37 | 0 | 2017-02-15 11:45 | Civil - Structural Engineering | 4500 |  | Incomplete Works | Repair | 3 (3-6k) | Complete | Management Problem - Other | Completed |  | Due to a clash between the floor beam mark 19021 (UC203x46+PL260x10) and existing cables on OLOD wall near Grid Line 22, the floor beam cannot be installed.
| 02SL - Stations (LUL) | Cxxx-NCR-001920 | NCR | LULO Steelworks - East Stair Shaft - Angled sections used as supports for pre-cast concrete panels were welded on the wrong side of the roof frame mark 4541 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-03-28 | 2017-03-27 09:24 | -1 | 2017-02-16 12:40 | Civil - Structural Engineering | 4000 |  | Manufacturing Defect | Repair | 3 (3-6k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Angled section L80/8 used as support for the pre-cast concrete panels was welded to the wrong side of the roof frame mark 4541
| 02SL - Stations (LUL) | Cxxx-NCR-001921 | NCR | HCDL Platform Paving - Cracked Grout Joints and Lifted Paving Slabs |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-06-30 | 2017-06-20 17:14 | -10 | 2017-02-15 12:41 | Architectural - Flooring | 4000 |  | Supervision/Management | Rework | 3 (3-6k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Paving was installed on HCDL Platform 1 during a possession. 1 week later cracks started appearing in a small section of this paving and some of the paving slabs lifted by 3mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001922 | NCR | CHS - Level 6 CER room floor level out of tolerance |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-07-23 | 2017-07-19 12:50 | -4 | 2017-02-15 19:40 | Civil - Civil Engineering General | 7000 |  | Workmanship | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | CER room floor level is out of tolerance as per attached as-built survey
| 02SL - Stations (LUL) | Cxxx-NCR-001923 | NCR | LULO Steelworks - Upper Concourse Roof - Missing gusset plates in roof beam mark 21543 for 2nos roof bracings mark 20589 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-03-29 | 2017-03-29 09:46 | 0 | 2017-02-17 18:02 | Civil - Structural Engineering | 4000 |  | Manufacturing Defect | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Upper Concourse Roof - 2nos gusset plates are missing in roof beam mark 21543. These gusset plates connects the roof beam mark 21543 with the roof bracings mark 20589
| 02SL - Stations (LUL) | Cxxx-NCR-001924 | NCR | Stair 28 - Floor beam mark 11065 is 100mm long |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-03-29 | 2017-03-29 11:51 | 0 | 2017-02-17 18:26 | Civil - Structural Engineering | 4000 |  | Manufacturing Defect | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Stair 28 - Floor beam mark 11065 is 100mm long. Floor beam cannot be installed, it has to be modified
| 02SL - Stations (LUL) | Cxxx-NCR-001925 | NCR | LULO Steelworks - Northern Concourse - DSS floor beam mark 12901 clashes with the side of the concrete DSS wall near grid line 5 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-03-29 | 2017-03-29 12:44 | 0 | 2017-02-17 18:51 | Civil - Structural Engineering | 4000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Top plate of DSS floor beam mark 12901 clashes with the side of the concrete DSS wall in the Southern crossover near grid line 5 Top plate needs to be locally cut to be able to install the beam
| 02SL - Stations (LUL) | Cxxx-NCR-001926 | NCR | GSM Building - __ cored in wrong location |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-04-21 | 2017-04-21 17:33 | 0 | 2017-02-20 16:22 | Civil - Civil Engineering General | 4000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Activity: Coring of __ in GSM building level 1 Issue: 1no 150mm diameter core __ was cored in the wrong location. This hole now requires to be infilled, and then cored again in correct location. It was envisaged to use as is (and modify the trimmer steel to suit), but this would introduce a clash with a door on level 1.
| 02SL - Stations (LUL) | Cxxx-NCR-001928 | NCR | Incorrect Washers installed to CMS Brackets |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2017-04-04 | 2017-03-30 12:33 | -5 | 2017-02-23 13:39 | Electrical - Cable Management | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Installation to the CMS brackets at Level 8 Cable transit route has been carried out using inappropriately sized washers allowing the washer to be partly pulled through and incorrectly seating against the bracket. This in turn negates the effect of the split washer also installed.
| 02SL - Stations (LUL) | Cxxx-NCR-001930 | NCR | Control of Drawings - Incorrect Revision of Drawing used on Site, Drawing Not Issued for Construction |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-04-05 | 2017-04-25 07:05 | 20 | 2017-02-24 06:19 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Reject | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | On 22/02/2017 it was noticed that an incorrect revision of drawing Cxxx-__M-C-DWG-D061_WS106-50525 was being used on site. Whilst inspecting the small section of reinforcement for the South Accommodation Block slab pre-pour checks, the Crossrail FE identified that the drawing being used was revision C04 whilst the current approved revision on eB was C03. After investigation, Crossrail stopped the Contractor from pouring this section of works until the drawing status was investigated and confirmed.
| 02SL - Stations (LUL) | Cxxx-NCR-001931 | NCR | CRL Tunnel PES Black CMS |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-05-28 | 2017-04-12 10:44 | -46 | 2017-02-27 14:05 | Electrical - Cable Management | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | CMS has been procured, and installed on the Westbound PES. MCR covers CMS supplied by __ however the CMS on the PES has a Black finish which is detailed in MCR as Products can be powder coated using LUL approved coatings
| 02SL - Stations (LUL) | Cxxx-NCR-001932 | NCR | Stair 24 - PCC cast in slip bearing plate levels |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-04-29 | 2017-04-28 15:09 | -1 | 2017-02-28 12:23 | Structural Engineering - Pre-cast | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | As per drawing Cxxx-__M-C-DWG-D061-50768, the PCC stair units are to have slip bearing plates cast into the connection between the top flight and bottom flight of the staircase. During a pre-installation inspection carried out at the __ precast yard it was found that the bearing plates were cast flush with the concrete surface on both the top and bottom flight units leaving no part of the bearing pad exposed to allow for movement.
| 02SL - Stations (LUL) | Cxxx-NCR-001933 | NCR | DSS-Level 5. CIR-PL2/CER1 Loddy. Tolerance for fire stopping not allowed for. |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-04-29 | 2017-04-20 10:32 | -9 | 2017-02-28 08:21 | Electrical - Cable Management | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | Containment passing through penetration too close to wind post fire cladding.
| 02SL - Stations (LUL) | Cxxx-NCR-001934 | NCR | DSS - Late Design Change to Column C1-30 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-05-26 | 2017-05-25 08:31 | -1 | 2017-03-15 16:03 | Shafts - Shafts General | 2000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Column on level 1 of C1-30 on Eastern elevation of Durward Street Shaft was constructed to C01 drawing. The profile of column C1-30 between level 1 to level A is different to the profile of column C1-30 between level A to C. Precast concrete cladding between the east and south west (service yard) has a defined line based on the C1-30 profile between Level A to C.
| 02SL - Stations (LUL) | Cxxx-NCR-001935 | NCR | LULO - Peeling of PSK 101 Primer within Level 3 Plant Room |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-08-15 | 2017-08-22 12:38 | 7 | 2017-03-03 12:20 | Civil - Civil Engineering General | 2000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | ITP Ref. Cxxx-__M-C-ITP-D061_WS106-53040, inspection number 4.4. Upon Crossrail inspection of the PSK 101 Primer application to Truss 4, it was noticed that part of the primer on a section of the truss had bubbled and peeled. Whilst the primer was applied within a dry environment, heavy rainfall following the application caused damage to the primer. After identifying this defect, the follow-on meshing activity did not occur.
| 02SL - Stations (LUL) | Cxxx-NCR-001936 | NCR | LULO ETH - Missing Concrete Cubes for Lift 7 Base and Raft Slab A2 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-05-06 | 2017-05-05 12:24 | -1 | 2017-03-07 13:06 | Civil - Civil Engineering General | 2500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | On 08/11/16, the base of Lift 7 and Raft Slab A2 of the Level 3 Plant Room were poured using Line 31 C40/50 concrete. Sampling took place as per the approved ITP and 100mm cubes were stored on site. During the period from striking the cubes and delivery to the testing laboratory, the cubes have been misplaced and can no longer be located and crushed. As a result, the compressive strength of the concrete is unknown.
| 02SL - Stations (LUL) | Cxxx-NCR-001937 | NCR | Staircase 24 PCC Units - Damage to units during installation |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-04-28 | 2017-04-26 09:15 | -2 | 2017-03-03 15:37 | Civil - Civil Engineering General | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | As per drawing Cxxx-__M-C-DWG-D061-50768, Staircase 24 is constructed of 12 no. PCC units. During the installation of units C24/F1A & C24/F3A, there has been a clash during placement which caused damage to the staircase nosings (photos attached).
| 02SL - Stations (LUL) | Cxxx-NCR-001938 | NCR | Out of tolerance areas of installed steelwork on the Northern Concourse, the Central (lower) Concourse and the Upper Concourse Roof |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-08-31 | 2017-09-05 07:46 | 5 | 2017-03-03 18:49 | Civil - Structural Engineering | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Reference attached __ internal NCRs [NCR-0067, NCR-0068, NCR-0069]. This information is presented as received from __. These documents report deviations of representative points on the constructed steel frame from their design locations in (x, y, z) axes expressed in millimetres. The data used is __ As Built survey information. The table demonstrates how __ has interpreted the requirements of NSSS to determine the applicable steel location tolerance at each point. Locations shown in red on the table are areas where __ has determined that the steel location is out of tolerance. Detailed tables for each out of tolerance point indicate the surveyed deviation, the allowable deviation and the out of tolerance value
| 02SL - Stations (LUL) | Cxxx-NCR-001939 | NCR | CHS Level 5 FAN room floor level out of tolerance |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-08-01 | 2017-08-01 07:30 | 0 | 2017-03-07 08:31 | Civil - Civil Engineering General | 19000 |  | Workmanship | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | FAN room floor level is out of tolerance as per attached as-built survey
| 02SL - Stations (LUL) | Cxxx-NCR-001940 | NCR | CHS Lift shaft openings out of tolerance |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-05-05 | 2017-05-09 08:54 | 4 | 2017-03-07 09:07 | Civil - Civil Engineering General | 8000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The lift shaft openings are out of tolerance as per attached survey data
| 02SL - Stations (LUL) | Cxxx-NCR-001941 | NCR | LULO Steelworks - Anchors for Columns on Grid Lines 1, 1.1, 2 & 2.1 on Platform 5 are too short |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-04-17 | 2017-03-27 13:43 | -21 | 2017-03-08 12:58 | Civil - Structural Engineering | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Anchors for the Columns mark 11206 (Grid Line 1), 11207 (Grid Line 2), 11208 (Grid Line 1.1) and 11209 (Grid Line 2.1) regarding Stairs 26 & 27 are too short. Therefore, the columns cannot be installed
| 02SL - Stations (LUL) | Cxxx-NCR-001942 | NCR | LULO Steelworks - Anchors for Columns on Grid Lines 1, 1.1, 2 & 2.1 on Platform 5 are too short |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-04-07 | 2017-04-26 09:20 | 19 | 2017-03-09 11:38 | Civil - Structural Engineering | 4000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Anchors for the Columns mark 11206 (Grid Line 1), 11207 (Grid Line 2), 11208 (Grid Line 1.1) and 11209 (Grid Line 2.1) regarding Stairs 26 & 27 are too short. Therefore, the columns cannot be installed
| 02SL - Stations (LUL) | Cxxx-NCR-001943 | NCR | LU West Lift Lobby - Missing Cube Results for Temporary Piles |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-04-18 | 2017-03-14 15:29 | -35 | 2017-03-09 17:23 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | 50 no. grout piles were cast to form a contiguous wall and allow the construction of the West Lift Lobby. There are cube results missing for 6 no. piles. The pile numbers are P6, P13, P18, P21, P34 and P49.
| 02SL - Stations (LUL) | Cxxx-NCR-001944 | NCR | DSS - Level A Walls and Columns As Built |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-08-25 | 2017-09-04 08:11 | 10 | 2017-03-13 15:40 | Shafts - Shafts General | 1250 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Level A As-Builts of walls and columns which are out of tolerance, __ have been notified, please refer to attached PTRs and As-Builts
| 02SL - Stations (LUL) | Cxxx-NCR-001945 | NCR | LULO Concourse - Area 2 Concrete Slab cas too low |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-05-12 | 2017-05-11 13:29 | -1 | 2017-03-11 19:34 | Civil - Civil Engineering General | 4000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Part of the concrete slab for Area 2 of the LO concourse was cast on 02/03/17. After completion of the pour, it was noticed that a 150mm step was required within this location. The current level of the concrete is 114.175m and requires increasing by 150mm to 114.625m.
| 02SL - Stations (LUL) | Cxxx-NCR-001946 | NCR | Level B-C Civils As-Built out of Tolerance |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-11-30 | 2017-11-20 12:26 | -10 | 2017-03-28 12:18 | Shafts - Shafts General | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Level B - C As-Builts of walls, columns and parapet which are out of tolerance. Please see 'Reference Document' for the as built Survey
| 02SL - Stations (LUL) | Cxxx-NCR-001947 | NCR | CRL Platforms - Eastbound Asbuilt Tolerances Ch 10195 - 10265 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-05-19 | 2017-05-15 08:53 | -4 | 2017-03-16 16:11 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The asbuilt survey has been carried out in Eastbound between chainage 10195 and 10265. Please see attached highlighted survey drawings showing the areas which are out of tolerance. The locations outside required tolerance are detailed below: Chainage 10195 Trackbed drainage channel level -0.015m Trackbed upstand line (platform side) -0.014m Trackbed upstand level (platform side) -0.014m Chainage 10200 Trackbed upstand level (SCL side) -0.012m Chainage 10205 Trackbed upstand level (platform side) -0.012m Benching +0.018m Chainage 10210 Benching drainage channel level +0.019m Benching drainage channel line +0.014m Benching +0.013m Benching +0.014m Chainage 10215 Platform nosing line -0.011m Chainage 10220 Trackbed level (platform side) -0.022 Chainage 10230 Trackbed wall -0.014m and -0.019m Chainage 10240 Trackbed level (platform side) -0.011m Benching between walls +0.018m Platform slab +0.011m Chainage 10245 Platform slab +0.015m and +0.020m Benching +0.031m and +0.019m Chainage 10250 Trackbed upstand line (Platform side) -0.011m Trackbed wall -0.011m Chainage 10255 Trackbed upstand level (SCL side) +0.019m Chainage 10260 Trackbed upstand level (SCL side) +0.028m Trackbed level (SCL side) +0.012m Chainage Trackbed upstand level +0.033m Trackbed level (SCL side) +0.013m Trackbed level (platform side) -0.013m Corbel line -0.012m and -0.013m
| 02SL - Stations (LUL) | Cxxx-NCR-001948 | NCR | CHS - Pre Cast Stairs (Stair 43) dowel locating voids misaligned with corbel thread |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-09-30 | 2017-09-25 09:12 | -5 | 2017-03-24 15:23 | Architectural - Finishes | 1500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Stair 43 dowel locators in pre cast unit C43/F2 do not align with the dowel threads in the corbel. This is likely due to movement of the Well's Tube void former during casting of the stair units.
| 02SL - Stations (LUL) | Cxxx-NCR-001949 | NCR | CHS - Pre Cast Stairs (Stair 42 and 43) Final As Built Survey |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-07-28 | 2017-10-17 11:09 | 81 | 2017-03-24 15:31 | Architectural - Finishes | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | All pre cast units for stair 42 and stair 43 are installed and a final as built inspection has been conducted by a CHS engineer to show any discrepancy against the construction drawings. Please refer to item 8.0 in the approved ITP and CHS as built of exterior staircase. An additional area that was not mention in the mark up prior to the inspection has now been added with photo attached.
| 02SL - Stations (LUL) | Cxxx-NCR-001950 | NCR | DSS - North Elevation PCC Panel Colour Inconsistency |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-09-30 | 2017-10-09 13:17 | 9 | 2017-03-20 17:11 | Architectural - General | 1500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | Precast Panels on the Northern Elevation of Durward Street Shaft appear to be exhibiting some efflorescence that can form white patches on the surface giving an overall lightening of the product.
| 02SL - Stations (LUL) | Cxxx-NCR-001951 | NCR | Trunking joining screws |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-05-02 | 2017-03-29 12:57 | -34 | 2017-03-23 11:30 | Electrical - Cable Management | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Supervision - Other | Completed |  | Trunking joining screws were too long
| 02SL - Stations (LUL) | Cxxx-NCR-001952 | NCR | Lift 5 and 6 concrete lift shaft remedial works |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-09-22 | 2017-09-22 16:50 | 0 | 2017-04-03 08:33 | Civil - Structural Engineering | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Lift 6 shaft was poured in Q2 of 2015 in accordance with the approved Cxxx and Cxxx reinforcement drawings at the time. The control panel in lift 6 was cast in the correct location according to the approved drawings at the time, as noted above. However the current architectural and __ drawings show the control box being located on the opposite side to the lift shaft entrance, please see referenced Cxxx-HYD-S-DDB-D061_WS106_Z-75820 and Cxxx-__M-C-DWG-D061-50047 showing current box location, and __ drawing Cxxx-__M-M-DWG-D061_WS106-50052 showing the required box location. During construction of WLL Lift shaft 5 it has been assumed that a setting out error was made when setting out the top and bottom landing of the lift and remedial works will be required on top and bottom landing. Please see attached “Lift 5 Remedial Works”.
| 02SL - Stations (LUL) | Cxxx-NCR-001953 | NCR | Fire Alarm Conduit through Fire Ductwork Insulation |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2017-06-08 | 2017-06-07 14:18 | -1 | 2017-03-24 12:24 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | 1. Surveillance on Fire rated Ductwork was carried out at Cxxx Whitechapel Station. As part of the surveillance Cambridge Heath and Durward Street Shafts were visited and it was found that Fire Alarm Conduits had been installed through both sides of Fire rated Ductwork Insulation in various areas (See Photos attached). Additionally a CMS support bracket threaded rod has been encapsulated as part of the Ductwork insulation (See photo attached).
| 02SL - Stations (LUL) | Cxxx-NCR-001954 | NCR | No MCR for __ sealant |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2017-04-21 | 2017-04-20 12:28 | -1 | 2017-03-24 12:50 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Lack or improper material identification and traceability | Completed |  | Surveillance on Fire rated Ductwork was carried out at Cxxx Whitechapel Station. As part of the surveillance Cambridge Heath and Durward Street Shafts were visited. During the site visit it was noted by RDS that they are applying __ sealant to Flange sections of the Fire Rated Ductwork. This is additional to the manufacturing process. The contractor made available a paper based MCR Cxxx-__M-A-LRC-D061-50022. On checking this was for Cxxxv temporary Ticket hall (TTH) and not for Fire Rated Ductwork.
| 02SL - Stations (LUL) | Cxxx-NCR-001956 | NCR | CHS - Level 8 622 Wall DR1 - Lobby 2 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-08-12 | 2018-07-26 16:33 | -17 | 2018-07-03 07:32 | Architectural - Brickworks/Blockworks | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | A large chip was found in the blockwork at level 8 Lobby 2 - DR1 area. This was just in the doorway and the block needed to be replaced.
| 02SL - Stations (LUL) | Cxxx-NCR-001957 | NCR | DSS - Stair 4 / W1-11NS As-built NCR - Out of tolerance pour |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-12-08 | 2017-12-19 15:36 | 11 | 2017-03-25 11:51 | Shafts - Shafts General | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Stair 4 (Level 3 to 1) and dividing wall (W1-11NS) in Durward Street has been poured out of tolerance (as-builts attached)
| 02SL - Stations (LUL) | Cxxx-NCR-001958 | NCR | DSS - Blockwork - Level 1 - DR II IWS 621 overhanging soffit |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-11-28 | 2017-11-23 16:13 | -5 | 2017-03-25 12:17 | Architectural - Brickworks/Blockworks | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As a result of out of tolerance wall W1-11NS (captured in Cxxx-NCR-001957) IWS-621 wall has been constructed to overhand DR II void as shown in mark ups and attached photos
| 02SL - Stations (LUL) | Cxxx-NCR-001959 | NCR | LULO Failure to notify inspection |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2017-05-08 | 2017-05-05 16:45 | -3 | 2017-03-29 08:11 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | __ failed to notify Crossrail of inspections during the week 52 possession, for the following works 1. Concourse break out 2. P5/6 brickwork __ to provide details on how to prevent reoccurrence.
| 02SL - Stations (LUL) | Cxxx-NCR-001960 | NCR | Slab Pour at north end of the concourse |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-08-25 | 2017-08-22 12:58 | -3 | 2017-03-28 14:04 | Civil - Civil Engineering General | 1000 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Slab at the north end of the concourse was poured with a known concrete level issue. The slab was cast too high because the steel work is installed too high. From design level, the concrete slab should be poured to top of the flange. Pouring to design level, we would not achieve enough cover for the concrete. Furthermore, the thickness of the slab will change and may effect loading on this area. Concrete was poured on night 25/26 /02/2017 and concrete cube results in attachment Compressive strength after 7 days 42.6 Compressive strength after 28 days 56 Braking out concrete was on weekend possession 25-26/03/2017 after 28days of curing
| 02SL - Stations (LUL) | Cxxx-NCR-001961 | NCR | DSS - Level 6 Void in OLHE room |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-05-19 | 2017-05-20 09:34 | 1 | 2017-03-30 09:59 | Shafts - Shafts General | 2000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | On level 6 in the OLHE room there is a void in the slab (__6/P/04) that is no longer required. This is to be filled in.
| 02SL - Stations (LUL) | Cxxx-NCR-001962 | NCR | LULO - - Missing Records |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-06-02 | 2017-06-14 13:57 | 12 | 2017-03-30 09:47 | Civil - Civil Engineering General | 1000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - No evidence of program review from Contractor's Quality Manager or Management | Completed |  | Infill works have been completed but records of the material used are not currently available
| 02SL - Stations (LUL) | Cxxx-NCR-001963 | NCR | DSS - Level C Slab Exposed Reinforcement |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-08-01 | 2017-08-25 07:27 | 24 | 2017-05-09 15:55 | Shafts - Shafts General | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | At DSS level C North slab there is one No. Reinforcement bar exposed
| 02SL - Stations (LUL) | Cxxx-NCR-001964 | NCR | DSS - Level 3 Stairs adjacent to C3-15 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-09-29 | 2017-10-18 07:53 | 19 | 2017-03-30 15:41 | Shafts - Shafts General | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In DSS level 3 stairs adjacent to column C3-15 were poured to the incorrect height on all risers (See attached asbuilt)
| 02SL - Stations (LUL) | Cxxx-NCR-001965 | NCR | DSS - Western Elevation Upper - PCC Cladding Brackets |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-08-21 | 2017-09-26 14:12 | 36 | 2017-03-30 14:40 | Shafts - Shafts General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On the upper Western Elevation of Durward Street Shaft two sections of the wall listed below will require scabbling to allow the installation of Precast Concrete Cladding Stainless Steel Support Brackets - 1. Level A between DS1 and DS3 2. Level A between DS4 and DS5
| 02SL - Stations (LUL) | Cxxx-NCR-001967 | NCR | CMS installed incorrectly |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-05-10 | 2017-04-18 12:38 | -22 | 2017-03-31 10:08 | Electrical - Cable Management | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | CMS crossing over through __
| 02SL - Stations (LUL) | Cxxx-NCR-001968 | NCR | HCDL Platform - Concrete slab box out missing starter bars |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-08-30 | 2020-12-08 17:18 | 100 | 2020-04-27 08:26 | Civil - Civil Engineering General | 2050 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | During week 52 possession concrete slab on the HCDL platform 2 which encompasses the subway staircase was constructed. To maintain access to the dry riser pipe underneath the platform 2 slab a box out was formed within the slab. Due to access issues starter bars/flying ends were not able to be left in the box out. Please find attached photos.
| 02SL - Stations (LUL) | Cxxx-NCR-001969 | NCR | 1DN - Wrong locations of MEP penetrations |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-11-01 | 2017-11-15 08:30 | 14 | 2017-04-24 10:34 | Civil - Base Course | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Since raising Cxxx-FCD-001653, Cxxx-FCD-001655, Cxxx-FCD-001799, Cxxx-RFI-004067, Cxxx-RFI-004068 & Cxxx-RFI-004172, __ have cast the slab to the North Accommodation Block. Following an as-built survey a number of penetrations have been cast in the wrong location. See attached an as-built drawing with the yellow penetrations indicating the as-built locations, the red penetrations as the current design locations and the green the proposed new locations.
| 02SL - Stations (LUL) | Cxxx-NCR-001970 | NCR | 1DN - concrete slab out of tolerance |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-05-21 | 2017-05-09 09:10 | -12 | 2017-04-11 08:17 | Civil - Base Course | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On the North edge of the Accommodation block, the as built of the edge of the slab is 30mm South to the design (see sketch attached).
| 02SL - Stations (LUL) | Cxxx-NCR-001971 | NCR | LULO Steelworks - Northern Concourse Stair 28 - Beam mark 11123 at upper landing is too short to support the Eastern upper stringer |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-05-13 | 2017-05-12 12:05 | -1 | 2017-04-03 13:11 | Civil - Structural Engineering | 6000 |  | Manufacturing Defect | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Northern Concourse Stair 28. The beam mark 11123 at the upper landing is 200mm too short to support the Eastern upper stringer mark 13017
| 02SL - Stations (LUL) | Cxxx-NCR-001973 | NCR | DSS - Pull out bars for Stair 1&2 Flight 4 are out of alignment |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-06-04 | 2017-05-16 12:07 | -19 | 2017-04-05 12:38 | Shafts - Shafts General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Approximately 1m of pull out bars for stair 1&2 Flight 4 in Wall W7-02S are out of alignment
| 02SL - Stations (LUL) | Cxxx-NCR-001974 | NCR | DSS - Level 3-1 Slab Walls and Columns Out of Alingment |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-07-30 | 2017-08-29 07:09 | 30 | 2017-04-21 11:31 | Shafts - Shafts General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Level 3 As-Builts of walls and columns which are out of tolerance, As-Builts
| 02SL - Stations (LUL) | Cxxx-NCR-001975 | NCR | 1DN - SMD metal deck details not as per drawing |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-05-16 | 2017-05-05 16:37 | -11 | 2017-04-06 13:12 | Civil - Structural Engineering | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __ and Crossrail completed an inspection of the Accommodation Block SMD metal deck of 1DN. It was identified that a number of details constructed on site were different to the drawing or not detailed.
| 02SL - Stations (LUL) | Cxxx-NCR-001976 | NCR | CHS - Riser 3 out of tolerance gaps between riser floor panels |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-02-28 | 2018-03-28 14:22 | 28 | 2017-04-10 13:33 | Architectural - General | 3367.5 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | This NCR captures the following issues throughout all levels of Risers at CHS: - Gaps between finished concrete and PCP floor panels >10mm - Gaps between PCP panel and PCP Panel >5mm - Gaps between PCP panel and kickflat >10mm
| 02SL - Stations (LUL) | Cxxx-NCR-001977 | NCR | CHS - Riser 2 out of tolerance gaps between riser floor panels |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-02-28 | 2018-03-28 14:19 | 28 | 2017-04-10 12:43 | Architectural - General | 3105 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | This NCR captures the following issues throughout all levels of Risers at CHS: - Gaps between finished concrete and PCP floor panels >10mm - Gaps between PCP panel and PCP Panel >5mm - Gaps between PCP panel and kickflat >10mm
| 02SL - Stations (LUL) | Cxxx-NCR-001978 | NCR | CHS - Riser 1 out of tolerance gaps between riser floor panels |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-02-28 | 2018-03-28 14:10 | 28 | 2017-04-10 12:45 | Architectural - General | 3460 |  | Design | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | This NCR captures the following issues throughout all levels of Risers at CHS: - Gaps between finished concrete and PCP floor panels >10mm - Gaps between PCP panel and PCP Panel >5mm - Gaps between PCP panel and kickflat >10mm
| 02SL - Stations (LUL) | Cxxx-NCR-001979 | NCR | CHS - Riser 4 out of tolerance gaps between riser floor panels |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-03-30 | 2018-03-28 14:24 | -2 | 2017-04-10 13:35 | Architectural - General | 870 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | This NCR captures the following issues throughout all levels of Risers at CHS: - Gaps between finished concrete and PCP floor panels >10mm - Gaps between PCP panel and PCP Panel >5mm - Gaps between PCP panel and kickflat >10mm
| 02SL - Stations (LUL) | Cxxx-NCR-001980 | NCR | LULO ETH - Stair 21 tread level out of tolerance |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-09-29 | 2017-11-13 08:36 | 45 | 2017-04-11 15:59 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During construction of the upper flight of Stair 21, a discrepancy was identified between the detailed reinforcement and the finished concrete level on drawing Cxxx-__M-C-DWG-D061_WS106-53410. The nominal cover to reinforcement of 40mm could not be achieved to bar mark 28 if the design level of 113.490m was to be achieved. The step design was to be 125mm, and if a cover of 39mm and 40mm is applied to the reinforcement as detailed, this leaves a remaining 45mm of space for reinforcement. However, the bending schedule detailed bar mark 28 to be 75mm deep (see attached sketch). As a result, it was discussed and agreed on site with CRL (__) that the finished concrete level to be raised in order to maintain cover to the reinforcement. Upon surveying the finished Stair 21 structure to generate an as-built, it can be confirmed that the level of the first tread on the upper stair is 113.515, 25mm higher than the design.
| 02SL - Stations (LUL) | Cxxx-NCR-001981 | NCR | DSS - __ Pre Cast Panels Offsite Fabrication Records submission |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-06-02 | 2017-07-04 10:18 | 32 | 2017-04-11 14:52 | Architectural - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Difficulty to obtain offsite fabrication records for the Pre Cast Panels at Durward Street Shaft from __.
| 02SL - Stations (LUL) | Cxxx-NCR-001982 | NCR | Site Wide - Offsite Fabrication Records - Insufficient collation and submission |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-10-27 | 2017-10-03 19:59 | -24 | 2017-04-11 16:03 | Materials - General | 2000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Other | Completed |  | The results from an internal surveillance of offsite fabrication records across a number of packages and disciplines has shown insufficient contemporaneous record keeping/submission in line with the various ITP requirements
| 02SL - Stations (LUL) | Cxxx-NCR-001983 | NCR | DSS - PCC East North Elevation P83A Cast Out of Tolerance |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-07-28 | 2017-10-10 07:10 | 74 | 2017-04-13 14:58 | Architectural - General | 5000 |  | Manufacturing Defect | Repair | 3 (3-6k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Panel P83A on the Eastern North elevation has been cast with a out of tolerance chamfer.
| 02SL - Stations (LUL) | Cxxx-NCR-001984 | NCR | CHS - Lift 8 Capping Slab Concrete Cover |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-06-02 | 2017-05-15 08:56 | -18 | 2017-04-20 11:56 | Civil - Structural Engineering | 3000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During install of the steel for the lift 8 capping slab at Cambridge Heath Shaft, it was noted that the concrete cover to steel at the top of the slab was lower than the 50mm required. This was due to where the top steel was fixed to couplers in the existing Level A-1 Slab and the fact that the finished concrete level had to tie in with existing slab level. From the pre-pour cover survey attached, the lowest concrete cover is 23mm - for the steel located above the lifting beam (photo 6 in attachment). The remaining areas have concrete cover ranging from 25-40mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001985 | NCR | DSS - Level B Earthing plate DC01 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-07-20 | 2017-08-09 15:39 | 20 | 2017-04-21 10:11 | Electrical - General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Earthing plate DC01 has been cased into the parapet by circa 25mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001986 | NCR | DSS - Missing __ waterproof checksheets - Slabs, walls and Columns - Level 3-1 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-06-30 | 2017-07-06 10:45 | 6 | 2017-04-21 13:03 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - No evidence of program review from Contractor's Quality Manager or Management | Completed |  | Missing __-1 waterproofing checksheet for Level 3-1 slabs, walls and column. These are required for the submission of Cxxx-__M-C-LRC-D061_WS105-50080 from ITP Cxxx-__M-C-ITP-D061_WS105-50065.
| 02SL - Stations (LUL) | Cxxx-NCR-001987 | NCR | LULO Steelworks - Platform Extension - Beam marks 17701 and 17723 clash with the existing LU West Bound rail bridge beam |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-05-31 | 2017-05-31 15:00 | 0 | 2017-04-21 16:37 | Civil - Structural Engineering | 4000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Due to a clash between the beam marks 17701 and 17723 with the existing LU West Bound rail bridge beam, these beams cannot be installed.
| 02SL - Stations (LUL) | Cxxx-NCR-001988 | NCR | GSM Building - Weld Inspection Missing |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-07-28 | 2017-07-13 11:19 | -15 | 2017-05-31 11:14 | Structural Engineering - Testing | 1000 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - No evidence of program review from Contractor's Quality Manager or Management | Completed |  | As part of the GSM web stiffeners welding works, the agreed weld testing regime was as per Cxxx-RFI-004155: 100% visual testing and 30% MPI testing. The Subcontractor has not carried out visual inspections of 2no Stiffeners on gridline GJ, between gridlines G5 and G6, and 1no angle on gridline GH. The Contractor was only informed that some inspections had not been carried out several days later, when the weld inspection reports were received. In the meantime, the stiffeners had been fire protected.
| 02SL - Stations (LUL) | Cxxx-NCR-001989 | NCR | DSS - Stair 1&2 Flight 8 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-06-15 | 2017-06-13 10:59 | -2 | 2017-04-26 12:57 | Shafts - Shafts General | 1500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In-Situ starter reinforcement form Level 6 slab have been cast out of stair 1&2 Flight 8
| 02SL - Stations (LUL) | Cxxx-NCR-001990 | NCR | DSS - Change in builders work hole location |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-07-14 | 2017-07-10 14:01 | -4 | 2017-04-25 13:18 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Please refer to the attached sketches and photos. The builders work hole that allows the CMS from below the platform to enter the FOSC cabinet in the DSS back of house room has been cast in the incorrect location. The hole clashes with a wall for the back of house rooms. The hole was cast correctly to the DSS code 1 drawings however the location of the hole changed and this was not picked up on the DSS RC drawings.
| 02SL - Stations (LUL) | Cxxx-NCR-001991 | NCR | CRL Platforms - Eastbound Asbuilt Toilerances 10270 - 10380 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-08-31 | 2017-08-14 11:07 | -17 | 2017-05-10 15:13 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The asbuilt survey has been carried out in Eastbound between chainage 10270 and 10380. Please see attached file for highlighted survey drawings showing the areas which are out of tolerance. The locations outside the required tolerance are summarised below: Chainage 10270m Trackbed drainage channel line +0.016m Chainage 10275m Trackbed level +0.013 / -0.015m Trackbed wall (trackside) +0.016m Trackbed wall (platform side) +0.014m Chainage 10280m Trackbed drainage channel level -0.014m Trackbed wall (trackside) +0.018m Trackbed wall (platform side) +0.013m Chainage 10285m Trackbed level -0.031m Trackbed wall (trackside) +0.015m Platform slab +0.013m, +0.013m, +0.012m Chainage 10290m Trackbed wall (trackside) +0.015m Trackbed wall (platform side) +0.016m Internal wall (SCL side) +0.013m Chainage 10295m Trackbed wall (trackside) +0.019m Trackbed line +0.012m Platform slab +0.013m, +0.014m Chainage 10300m Trackbed wall (trackside) +0.011m Benching drainage channel level -0.011m Chainage 10305m Trackbed wall (trackside) +0.012m Benching drainage channel level -0.014m Chainage 10310m Trackbed wall (platform side) +0.013m Trackbed line +0.020m, +0.018m Benching drainage channel level -0.030m Chainage 10315m Trackbed wall (platform side) +0.015m Trackbed line +0.011m Corbel -0.015m Chainage 10320m Lower trackbed wall +0.011m, +0.012m Chainage 10325m Benching (lower) level +0.018m Benching (higher) level +0.015m Chainage 10330m Trackbed wall line +0.012m, +0.011m Platform slab level +0.012m Chainage 10335m Benching drainage channel level -0.014m Platform slab level +0.012m Chainage 10340m Platform slab +0.012m Chainage 10345m Trackbed wall +0.015m Platform slab level +0.012m, +0.016m, +0.015m, +0.014m Chainage 10350m Lower trackbed level -0.011m Corbel line -0.032m Chainage 10355m Upstand level (platform side) -0.011m Benching level -0.012m, -0.017m Chainage 10360m Trackbed wall line +0.011m Platform Slab +0.016m Chainage 10365m Trackbed wall line +0.011m, +0.014m Benching level (lower) 0.011m Benching (upper) +0.023m Platform slab +0.011m Chainage 10370m Trackbed (SCL Side) +0.014m Trackbed drainage channel level +0.017m Chainage 10375m Internal wall line +0.011m Corbel line +0.012m The platform slab will be covered by 150mm of screed, as shown in Cxxx-__M-A-DDB-D061_WS106_Z-10409. The benching does not have any applied finishes Cxxx-__M-A-DDB-D061_WS106_Z-10409. The area between the trackbed upstands will be filled with concrete by Cxxx therefore the small discrepancies/ position in level will not have an effect.
| 02SL - Stations (LUL) | Cxxx-NCR-001992 | NCR | LULO GSM - Non-tissue faced thermal insulation installed to GSM soffit (type INS-401) |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-11-15 | 2017-11-17 17:32 | 2 | 2017-04-27 15:08 | Architectural - Ceilings & Soffits | 2500 |  | Material | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | It has been realised that the type INS-401 thermal insulation installed to the GSM soffit is without black tissue face as per the Specification.
| 02SL - Stations (LUL) | Cxxx-NCR-001993 | NCR | LULO GSM - Missing drop rod installation through floor soffit |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-12-22 | 2017-12-20 12:39 | -2 | 2017-04-27 09:07 | Architectural - Ceilings & Soffits | 1500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | This NCR has been raised to capture missed drop rod installations through the GSM floor soffit. The M12 threaded drop rods were installed through the floor between PCC planks prior to screeding to support insulation and suspended MEP/ ceiling tiles below. 3no. locations where rod installations have been missed have been discovered.
| 02SL - Stations (LUL) | Cxxx-NCR-001994 | NCR | Installation clashes between FA conduit and ductwork |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-12-22 | 2018-02-02 08:33 | 42 | 2017-04-27 10:05 | Mechanical - Heating Ventilation & Air Conditioning | 14000 |  | Planning | Repair | 2 (6-60k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | In some instances there has been a clash between the fire alarm conduit installation and the ventilation installation. This has occurred in both shafts.
| 02SL - Stations (LUL) | Cxxx-NCR-001995 | NCR | LULO Steelwork- Use of unapproved drawing |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2017-08-02 | 2017-07-24 15:22 | -9 | 2017-04-27 12:34 | Structural Engineering - Structural Engineering - General | 1000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | Works have taken place without an approved drawing. Drawing Cxxx-__M-C-DWG-D061-WS106-53500 P01 was issued to Crossrail for acceptance 24.04.17, works commenced the same day without acceptance from Crossrail.
| 02SL - Stations (LUL) | Cxxx-NCR-001996 | NCR | LULO Stair 21 joint omitted |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2017-11-17 | 2017-12-05 09:20 | 18 | 2017-04-27 12:59 | Civil - Civil Engineering General | 1750 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Stair 21 sub-construction cert (Cxxx-__M-C-CER-D061-50273) was issued to Crossrail for acceptance, however there was no evidence of the required stair 21 joint to upper concourse included. RFI-003828 highlighted that an aerofil joint was to be installed. This was omitted from the MCR list, construction records and red-line drawings.
| 02SL - Stations (LUL) | Cxxx-NCR-001997 | NCR | DSS-Damaged Precast Concrete Cladding Panel P73-PTN 90 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-07-07 | 2017-07-06 09:21 | -1 | 2017-04-28 15:10 | Shafts - Shafts General | 500 |  | Workmanship | Reject | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | During the slinging procedure of off loading panel P73-PTN 90,damage was incurred on the panel.
| 02SL - Stations (LUL) | Cxxx-NCR-001998 | NCR | DSS - Level 7 Slab As-Built |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-07-23 | 2017-08-02 16:29 | 10 | 2017-05-24 08:37 | Shafts - Shafts General | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The slab level on Level 7 Has been poured out of tolerance.
| 02SL - Stations (LUL) | Cxxx-NCR-001999 | NCR | LULO_ESS___ PCC Cladding Panels and __ Secondary Steel Installation |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-11-01 | 2017-12-04 10:58 | 33 | 2017-04-28 16:18 | Architectural - General | 9500 |  | Planning | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | In order to proceed with the installation of the PCC external cladding panels and the secondary steel on the ESS, the sprayed __ had to be broken in some primary steel columns at height and low level to allow the installation of the panels and the secondary steel over the main brackets and columns. __ is due to provide a sketch highlighting the local areas where the __ was exposed after the cladding panels and secondary steel works finished. __ intend to clean, re-primer and re spray the areas that were exposed in order to repair what was exposed.
| 02SL - Stations (LUL) | Cxxx-NCR-002000 | NCR | LULO_ESS___ Blockwork Installation - Lintels on Switchrooms E10A, E10 and LAN Equip Room |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-07-15 | 2017-07-14 16:20 | -1 | 2017-05-16 09:40 | Architectural - Brickworks/Blockworks | 5000 |  | Supervision/Management | Rework | 3 (3-6k) | Complete | Personnel Error - Other human error | Completed |  | Drawing Cxxx-__M-A-DDB-D061_WS106_Z-10328, Elevation K-K, shows 4no. lintels to be installed above doors and builders work holes. __ have provided setting out datum to the subcontractor from SSL however this datum was misunderstood by the subcontractor due to the scaffold that was installed in front of the levels marked. The subcontractor have used a different datum that was in place from a previous requirement and all the 4 lintels and associated blocks were installed 150mm height.
| 02SL - Stations (LUL) | Cxxx-NCR-002001 | NCR | DSS - Level 8 - 6 Walls and columns Aligment out of tolerance |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-10-26 | 2017-11-10 12:48 | 15 | 2017-05-24 09:52 | Shafts - Shafts General | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Elements between Level 8 and Level 6 have been poured out of tolerance.
| 02SL - Stations (LUL) | Cxxx-NCR-002002 | NCR | LULO_ESS___ PCC Cladding Panels and __ Steel Installation_Panel 2E-15 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-08-31 | 2017-08-24 08:40 | -7 | 2017-05-02 09:42 | Civil - Civil Engineering General | 5500 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | In order to achieve the installation of panel 2E-15 by __ on the ESS Stair 23, the support angles welded to the solid box section on the __ primary steel had to be moved to the other side of the beam. This was covered under Cxxx-NCR-001920. The 2no. shelf support angles were bolted to the correct side of the __ primary steel however they will have to be turned up side down (as per Cxxx-__M-C-DWG-D061_WS106-53504), packed out by 50mm and holes / slots will have to be drilled to bolt __ angle through. __ can then install the concrete panel 2E-15 achieving the correct alignment.
| 02SL - Stations (LUL) | Cxxx-NCR-002003 | NCR | CRL Platforms - Back of house cabinets - Wind post recess missing |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-08-31 | 2017-08-30 10:51 | -1 | 2017-05-03 12:05 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On the CRL Platforms, following the casting of the back of house cabinet plinths it was noted that some of the box outs required to create a recess in the plinths had not been installed. The recess has been missed in 3 positions - 1 No Westbound West, 1 No Eastbound East and 1 No Eastbound West (Please see attached marked up drawings for locations). The recess in the plinth is required so the wind post base can be fixed to the structural slab. The recess will be saw cut and broken out. The plinth is reinforced with a single layer of mesh. Exposed reinforcement will be painted with __ __ Zinc rich paint, to prevent corrosion. Following installation of the wind post the baseplate and windpost will be cast in with __ GP to the same level as the plinth.
| 02SL - Stations (LUL) | Cxxx-NCR-002004 | NCR | LULO - GSM Building - Incorrectly Installed Lintel D2/015 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-09-04 | 2017-08-21 13:34 | -14 | 2017-05-05 07:13 | Architectural - Brickworks/Blockworks | 4000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The lintel above door D2/015 does not achieve the 150mm bearing at each end as stated in the lintel schedule and specifiaction. Lintel bearing has been checked by __, and deamed sufficient, however the construction of the nib wall is an issue. __ have proposed 2no remedial options detailed in the attachment 'Response to PTR-3230'. Option 1 - Post drill rebar into the nib wall with __ HY270 resin Option 2 - Fix an equal angel post with __ HY270 resin anchors Option 3 - Fully bond the nib wall into the eastern wall by toothing out and reworking.
| 02SL - Stations (LUL) | Cxxx-NCR-002005 | NCR | DSS - PCC - Western Elevation - P52, P53A, P54 and P55A - incorrect cavity dimension in PCC design |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-09-05 | 2017-09-05 09:06 | 0 | 2017-05-08 11:35 | Shafts - Shafts General | 50000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | P52, P53A, P54 and P55A panels designed for 125mm cavity instead of 25mm due to an error in structural/architectural design coordination.
| 02SL - Stations (LUL) | Cxxx-NCR-002006 | NCR | DSS - W8-06NS Extension and New Construction joint on Level 7 Platform Slab (West) |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-07-28 | 2017-07-20 08:18 | -8 | 2017-05-09 15:52 | Shafts - Shafts General | 2000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Level 7 Platform slab on the western end has not been designed to be a canter leaver. Wall W8-06NS has been install as per design and fall approximately 2.2m from the designed edge of platform.
| 02SL - Stations (LUL) | Cxxx-NCR-002007 | NCR | DSS Riser A Level B - Blockwork walls incorrectly built |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-01-18 | 2018-11-30 20:54 | -49 | 2018-09-20 08:36 | Architectural - Brickworks/Blockworks | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Wall construction was started but built to wrong offset.
| 02SL - Stations (LUL) | Cxxx-NCR-002008 | NCR | DSS - Level 1 Escalator Slab 600mm Thick Wall (Step in Slab) Coupler Alignment |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-07-13 | 2017-07-27 07:43 | 14 | 2017-05-09 15:44 | Shafts - Shafts General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The kicker for the Level 1 Escalator Slab 600mm Thick Wall has been poured out of alignment. The retaining __ blocks that support the 200Ton crane mat intrudes onto the wall.
| 02SL - Stations (LUL) | Cxxx-NCR-002009 | NCR | LULO Steelworks - North Concourse Stairs 26, 27, 28 and 29 - Metal decking support |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-06-18 | 2017-06-15 15:33 | -3 | 2017-05-09 16:36 | Civil - Structural Engineering | 2000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On stairs 26 & 27 (LO Platform 5) no side support for the metal decking was given in Cxxx design on the West side of the stair landing platform. On stairs 28 & 29 (LO Platform 6) no side support for the metal decking was given in Cxxx design on the East side of the stair landing platform. Therefore no support was detailed in the __ Steelwork Model.
| 02SL - Stations (LUL) | Cxxx-NCR-002010 | NCR | CRL EB Tunnel Cxxx CMS quality |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-12-22 | 2017-10-20 12:16 | -63 | 2017-08-24 10:57 | Electrical - Cable Management | 2000 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | The CRL Tunnel Cxxx 450mm 3 compartment tray dividers do not touch the tray throughout its length. The welds fixing the dividers to the tray are spaced at approximately 300mm and the post hot dip galvanising process has distorted the tray leaving gaps between the tray and the dividers in some instances.
| 02SL - Stations (LUL) | Cxxx-NCR-002011 | NCR | LULO Steelworks - Missing MDC documents related to Area 3, 4 & 5 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-06-29 | 2017-06-14 14:02 | -15 | 2017-05-10 13:45 | Civil - Structural Engineering | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | Several MDC documents related to the steel installation on Area 3, 4 & 5 were never issued to CRL for approval.
| 02SL - Stations (LUL) | Cxxx-NCR-002012 | NCR | LULO GSM - Isolation of dissimilar metals used in soffit insulation |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-11-15 | 2017-11-21 16:08 | 6 | 2017-05-11 12:46 | Architectural - Ceilings & Soffits | 8000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | __ PTR-2833 was submitted and accepted for installation of the soffit thermal insulation and boarding (only) as the details were in accordance with F1 design drawing Cxxx-__M-A-DDD-D061_WS106_Z-11014 rev C02. On the back of this acceptance installation of the soffit insulation commenced. The F1 design drawings and Specification call on stainless steel threaded drop rods through the soffit, to support hot dip galvanised __. Therefore the impression was that this had been considered as compatible metals. Within the attachments to B-H PTR-2833, soffit designer Fairhurst provided a statement that bimetallic corrosion between the two dissimilar metals would be low risk. As the reply from B-H in PTR-2833 did not directly address this stance on bimetallic corrosion, subsequent B-H PTR-2958 was raised to confirm. B-H replied to PTR-2958 late, and with a differing view to Fairhurst's evaluation after corresponding with the Galvaniser's Association. The Subcontractor installing the works was subsequently stopped from further installation until the issue is resolved.
| 02SL - Stations (LUL) | Cxxx-NCR-002013 | NCR | LULO GSM - Level 2 failed blockwork inspection |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-08-14 | 2017-08-11 12:01 | -3 | 2017-05-11 15:35 | Architectural - Brickworks/Blockworks | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | NCR raised to capture failed and abandoned inspection of blockwork on GSM level 2 (IRF-LULO-1186). This was a re-inspection of IRF-LULO-1173 from 04/05/2017.
| 02SL - Stations (LUL) | Cxxx-NCR-002014 | NCR | CRL Platforms - EB and WB platform ends - __'s without reccesses |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-10-18 | 2017-10-17 14:10 | -1 | 2017-06-06 12:33 | Civil - Civil Engineering General | 4500 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Please see the __ PTR attached which details the __'s in the CRL Platforms which have been constructed without recesses. The proposed remedial measures are detailed in the attached PTR response document. Please can the Project Manager confirm if these proposals are acceptable structurally.
| 02SL - Stations (LUL) | Cxxx-NCR-002015 | NCR | CHS - Missing __ Level 1 Section D-D |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-10-22 | 2018-07-16 07:45 | -98 | 2018-05-15 08:08 | Architectural - Brickworks/Blockworks | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | On Level 1, __ D-D, which is between rooms 1/669 and 1/237 has been missed. The wall was constructed out of fair faced blockwork, omitting the __. RDS plan to put a transfer air duct through the __.
| 02SL - Stations (LUL) | Cxxx-NCR-002017 | NCR | LULO Area 3, 4 & 5 - Drawing Code 2 - Cxxx comments not incorporated in the drawing |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-07-13 | 2017-07-11 12:41 | -2 | 2017-05-13 11:40 | Civil - Structural Engineering | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Failure to follow status stamp | Completed |  | The drawing Cxxx-__M-C-DWG-D061_WS106-50441 C01 was coded 2, however the works on site continued despite Cxxx comments were not incorporated to the drawing. The works on site were not directly affected by the comments made by Cxxx.
| 02SL - Stations (LUL) | Cxxx-NCR-002019 | NCR | Intumescent paint damage under top hat |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-08-04 | 2017-08-10 11:30 | 6 | 2017-05-18 13:45 | Fire - Fire Systems & General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Intumescent paint has been applied to roof arches as part of fire protection. __ to install top hat has been stopped because of damage to the intumescent paint during fixing of top hats. Shot fire gun has been used to fix top hats with recommended power to allow fix nail on minimum depth and that create damage to intumescent paint. __ agreed with __ to change type of fixing top hats from fire shot to tek screw
| 02SL - Stations (LUL) | Cxxx-NCR-002020 | NCR | DSS Submarine Door - Contradiction between Cxxx and __ drawings |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-11-10 | 2017-11-09 07:35 | -1 | 2017-05-19 10:43 | Architectural - Doors | 1500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The attached Cxxx and __ drawings at DSS Level B show differing details for the structural opening of the "Submarine Door" As-built is currently as per the Cxxx drawing.
| 02SL - Stations (LUL) | Cxxx-NCR-002022 | NCR | LU/LO - East Stair Shaft - Missing grout pour records and cube results |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-08-31 | 2017-08-29 07:46 | -2 | 2017-05-19 13:03 | Civil - Structural Engineering | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - No evidence of program review from Contractor's Quality Manager or Management | Completed |  | Missing pour records and cube results of the grout poured underneath the base plate of the perimeter columns at the East Stair Shaft area.
| 02SL - Stations (LUL) | Cxxx-NCR-002023 | NCR | CHS Trunking Screws Protruding into Trunking |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2017-06-21 | 2017-06-28 14:29 | 7 | 2017-05-22 08:22 | Electrical - Cable Management | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | The Multi Compartment Trunking run installed within riser 1 has the trunking joiner screws protruding into the trunking body potentially leaving any cables installed liable to damage against them.
| 02SL - Stations (LUL) | Cxxx-NCR-002024 | NCR | LULO GSM - Level 2 small cuts to blockwork around builder's work holes |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-10-31 | 2017-09-21 11:39 | -40 | 2017-05-22 10:20 | Architectural - Brickworks/Blockworks | 6000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | It has been identified that some of the smaller builder's work holes on GSM level 2 have been constructed with a number of small cuts to the underside of the lintel and also around the base of the openings. Stack bonding has also been used to avoid “L” shaped cuts and further small cuts in some instances. These builder's work holes are identified to the following rooms: DNO/ Switch Room - BW2/109, BW2/110, BW2/111 Mist Suppression Room - BW2/114, BW2/115, BW2/116, BW2/117, BW2/127 CER 4/ OPO Room - BW2/143, BW2/129
| 02SL - Stations (LUL) | Cxxx-NCR-002025 | NCR | HCDL Platforms Manhole MH00 wrong clear opening size |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-07-31 | 2017-07-24 12:17 | -7 | 2017-05-22 12:56 | Civil - Drainage | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During installation of Manhole 00 cover slab with clear opening 600 mm x 750 mm was installed.
| 02SL - Stations (LUL) | Cxxx-NCR-002026 | NCR | DSS HV Route Inspection & CMS Removal |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2017-07-01 | 2017-07-14 13:12 | 13 | 2017-05-22 12:39 | Electrical - Cable Management | 5000 |  | Incomplete Works | Rework | 3 (3-6k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Inspection to re inspect works previously removed from Riser B2 was halted due to the installation further along the cable run having been removed. All works post inspection and sign off should not be altered in any way unless CRL have been informed, the work then will be required to be re inspected. This particular route is due to be handed over to Cxxx in its complete form. The complete route should now be re inspected.
| 02SL - Stations (LUL) | Cxxx-NCR-002027 | NCR | LULO - Lift Shaft 6 & Stair 23 Portal Frame - Missing Records |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-08-25 | 2017-09-12 07:00 | 18 | 2017-05-22 12:53 | Civil - Civil Engineering General | 2000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | The ITP folder for Lift Shaft 6 and Stair 23 Portal Frame cannot be found. __ do not have records of any of the concrete pour inspections for the works.
| 02SL - Stations (LUL) | Cxxx-NCR-002028 | NCR | DSS / Platform Tunnels - Level 6 Wedge - Asbuilt NCR |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-09-19 | 2017-08-18 08:49 | -32 | 2017-05-22 16:15 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | DSS Level 6 - Reinforced Concrete Wedge has been poured out of tolerance as per attached asbuilt survey.
| 02SL - Stations (LUL) | Cxxx-NCR-002029 | NCR | LULO - Platform 1 and 2 Missing Pile Records |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-12-15 | 2017-12-15 14:57 | 0 | 2017-08-29 20:00 | Civil - Civil Engineering General | 3000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | Platform 1 and 2 piling works have been completed however there are a number of concrete piling records that are not currently available. 29/08/17 Update. A review of the construction records for Platform 1 and 2 has been conducted and the results are tabled within the attached ITP Records Tracker. To summarise, the following records are missing: - __ Form D3-45 Pile Cage Check Sheet for pile groups 1, 2b, 2c, 2e, 2f, 3c, 3d and 5 - Cube results for Pile 49 and Pile 57/52 - Integrity tests for pile groups 3a, 4a/2j, 4b/2k and 5 __ Form D3-45 is an additional checksheet used upon arrival to site to check that the cages are of the correct type and as per design. An additional pile cage check is completed prior to installation on __ Form D3-44 and full records of this checksheet for all piles have been provided. The 13 piles missing cube and integrity test results were constructed by __ and __ in November and December of 2014. These piles were constructed using Cased Segmental Flight Auger methodology, where temporary casings are sealed into the clay acting as a support through the unstable strata and segmental augers were used to advance the bore to the required depth. __’s proposed disposition is that these identified piles are satisfactory and fit for purpose based on historic data of over 200 other similar piles completed by __ on the Cxxx project. Statistics show that these piles completed by the same drilling crew and supervision have satisfactory strength and integrity results (yielding 100% pass rate) which would suggest that these 13 piles are also satisfactory. Integrity of each pile will have been maintained by controlled drilling for the cased SFA construction; the augers and casings will have prevented any material falling into the excavation. Each pile is measured for depth prior to concrete pour; foreign material at the bottom of the pile will have been detected if the depth was not achieved. The concrete was placed using a tremie pipe to prevent segregation of the material and also guarantee the integrity of the structure. Only once the concrete was poured, the temporary casings were removed. This pile construction methodology minimises the risk of any anomalies within the pile shaft. Please see attached email from __ to confirm this statement. The piles are no longer available for inspection due to the construction of pile caps and floor finishes on top. Furthermore, the piles are now loaded with a steel canopy structure. As a result, it would have been noticeable by this stage if the piles were not of satisfactory construction. Whilst the specification Cxxx-HYD-Z-RSP-D061-00031 states non-destructive pile integrity testing shall be carried out on all piles, The Specification for Piling and Embedded Retaining Walls references the Federation of Piling Specialists Handbook on Pile Load Testing (section C15.1) which states that the strategy for pile testing needs to be established at the time the piles are being designed. During the design period, appropriate factors of safety were used in the design such that static testing was not specified for these piles due to access difficulties (see Cxxx-RFI-000392).
| 02SL - Stations (LUL) | Cxxx-NCR-002032 | NCR | LULO_WLL___ Columns Installation - Missing Grout Cube Results |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-02-20 | 2018-02-12 15:10 | -8 | 2018-01-11 18:03 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | Missing cube results of the grout poured underneath the base plate of the __ columns on top of Pilecap 2c, 2d, 2h and Lift 10 walls in the WLL area.
| 02SL - Stations (LUL) | Cxxx-NCR-002033 | NCR | LULO - LO Concourse Concrete Structural Damage |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-08-23 | 2017-08-22 12:42 | -1 | 2017-05-25 17:45 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Whilst completing the lower concourse remedial works outlined within Cxxx-RFI-004373 (as a result of Cxxx-NCR-001913), damages to the concourse concrete structure have occurred. Sketch 01 details the original agreed area of concrete to be removed to accommodate the floor trunking. This NCR has been raised to agree the proposed remedial work to all areas of breakout. Since these breaking works, Cxxx-FCD-002072 has been raised to cover the revision of finish floor levels along the length of the LO concourse. To summarise, the FFL has been increased by 20mm from Gridline 1 to Gridline 6.1. As a result, the new FFL for this area only is 109.745 for the main concourse and the landings to staircases 25, 26, 27, 28 and 29. This 20mm increase accommodates for the steel and concrete installation to be on average 20mm high, as detailed within Cxxx-NCR-001913. The levels for the remaining concourse remain unaltered. This 20mm increase also maintains the original structural depth of 310mm and removes the requirement to substantially reduce the level of the concrete to incorporate the primary CMS trunking routes within the floor finishes. Between Gridline 1 and 6.1, the new SSL will be 109.595 which reflect the current average concrete levels, as shown on the attached as-built drawing. The upper concourse SSL remains the same as per original design, and a 175mm deep slab has been maintained. Please see the attached sketch 02 to explain the new levels and location of the floor CMS trunking. The majority of the primary CMS route has previously been reduced as agreed within Cxxx-RFI-004373. At these locations, the concrete slab shall be reinstated to the new SSL of 109.595. The repair method for reinstatement will utilise a minimum 10mm thick layer of Weber Five Star Repair Concrete as recommended by VINCI Technology Centre and Weber Saint-Gobain. Please see attached emails from both VINCI and Weber approving the use of the Five Star Repair concrete. As a result of the previous concrete breaking works, areas of the concrete slab have been removed to reveal the metal decking below. Please see attached photographs. This is due to a minimal concrete cover of 85mm from top of concrete to the top of the decking; breaking the concrete in these locations has caused the concrete to shatter the full depth. To rectify, a Weber epoxy bonding aid shall be applied to the areas of exposed decking and reinforcement mesh prior to the concrete repair mix to guarantee a good bond. This will guarantee the reinstatement of a monolithic structure. After application of the repair concrete to all areas of the concourse, a cover survey shall be completed. The following two scenarios shall be encountered: 1. If the concrete cover is greater than the design 25mm, the repair concrete layer is a sufficient repair. 2. If the concrete cover is less than the design 25mm, the repair concrete layer is not sufficient and requires a 2mm layer of Flexcrete cementious coating 851 applied on top. If the layer of reinforcement mesh is above the desired SSL, this will require removal. The mesh shall be cut and a __ corrosion spray applied to the ends of the steel. A 25mm layer of Five Star Repair Concrete shall then be applied to the vertical edge to achieve the design cover of the steel. The remaining remedial work can then be completed as per the above methodology. To summarise, the following repairs will be utilised throughout the LO concourse: 1. Repair method 1 – Apply a layer of Weber Five Star Repair Concrete to the areas of concrete removed for the CMS trunking route to the underside level of the trunking. 2. Repair method 2 – If the layer of Weber Five Star Repair Concrete does not achieve the required 25mm cover to the reinforcement mesh, a 2mm layer of Flexcrete cementitious coating 851 must be applied on top. 3. Repair method 3 – if the layer of reinforcement mesh is above the level of the desired SSL, this will require removal. The mesh shall be cut, the remaining ends protected with a __ corrosion coating and then a 25mm thick layer of Weber Five Star Concrete applied to the vertical edge to achieve the design cover. Repair method 1 shall then be utilised afterwards. 4. Repair method 4 – at some locations along the concourse, the metal decking has been exposed. Where this occurs, a Weber epoxy bonding aid shall be coated to the decking and then the Weber Five Star Repair Concrete placed whilst the epoxy is still tacky, as per repair method 1.
| 02SL - Stations (LUL) | Cxxx-NCR-002034 | NCR | CHS - L7 __R/SER Room Floor Level Out Of Tolerance |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-08-18 | 2017-09-05 07:45 | 18 | 2017-06-07 15:41 | Civil - Civil Engineering General | 1200 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __R and SER room floor level is out of tolerance as per attached as-built survey
| 02SL - Stations (LUL) | Cxxx-NCR-002035 | NCR | Code 3 MCR |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2017-08-31 | 2017-09-01 09:55 | 1 | 2017-05-30 10:01 | Materials - Approval | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | A planned Surveillance was carried on the Evens PCC installation, A review of the MCR’s associated with the installation, found that Precast Concrete Panel MCR Cxxx-__M-A-LRC-D061_WS106-50165 (Rev 1) had been at Code 3 since 27/03/15.
| 02SL - Stations (LUL) | Cxxx-NCR-002036 | NCR | DSS - Stair 9 Stringers and risers out of Tolerance |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-01-18 | 2018-01-04 11:14 | -14 | 2017-05-31 15:26 | Shafts - Shafts General | 927.6 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In Stair 9 Flight 19-21 There are some risers out of tolerance.
| 02SL - Stations (LUL) | Cxxx-NCR-002037 | NCR | CRL tunnel invert earthing zonal gapping in CMS |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-08-18 | 2017-08-25 07:48 | 7 | 2017-05-30 13:11 | Electrical - Cable Management | 10000 |  | Design | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Insufficient quantity of material to do the job | Completed |  | The CMS has been installed in the platform inverts without the GRP section being installed for earth gapping proposes
| 02SL - Stations (LUL) | Cxxx-NCR-002038 | NCR | Cxxx signal CMS compartment size in DSS and Inverts |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-08-19 | 2017-09-01 07:16 | 13 | 2017-05-31 15:23 | Electrical - Cable Management | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other management problem | Completed |  | Cxxx tray is indicated as being 450mm x 80mm c/w 2 number rigid dividers which has been installed. The Invert drawings went from C rev back to P rev changing the size of tray fro 300mm to 450mm c/w two dividers. To allow installation to progress we raised Cxxx-FCD-001659. the response cam back changing the compartments to 150, 100, 150mm which we were able to incorporate in the manufacture of the tray. DSS tray had already been purchased/installed at this stage.
| 02SL - Stations (LUL) | Cxxx-NCR-002039 | NCR | Removing signed off CMS |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-07-10 | 2017-06-12 09:05 | -28 | 2017-05-31 11:48 | Electrical - Cable Management | 1000 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | A 450mm tray bend was uninstalled so operatives had more room to install some trunking
| 02SL - Stations (LUL) | Cxxx-NCR-002040 | NCR | DSS - Level 7 Platform Slab - As-built tolerance CH 10170 to 10190 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-08-24 | 2017-09-18 08:00 | 25 | 2017-06-05 10:05 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The asbuilt survey has been carried out in at Durward Street Shaft Level 7 Platform Slab - between chainage 10170 and 10190. Please see attached file for highlighted survey drawings showing the areas which are out of tolerance. The locations outside the required tolerance are summarised below: Chainage 10170m Platform Nosing -0.017m Platform Slab -0.014m Chainage 10175m Platform Nosing -0.017m Platform Slab -0.016m Platform Slab -0.016m Chainage 10180m Platform Nosing -0.015m Chainage 10190m Platform Nosing -0.014m Platform Slab +0.015m Trackbed (DSS North Side) 0.014m Trackbed (DSS South Side) -0.031m Benching +0.016, +0.013m
| 02SL - Stations (LUL) | Cxxx-NCR-002041 | NCR | DSS L8-6 Construction records- cubes did not reach required compressive strength |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2017-09-03 | 2017-08-31 14:05 | -3 | 2017-06-06 12:10 | Civil - Civil Engineering General | 1200 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Construction records for DSS L8-6 was submitted to CRL for review. During this the following non-conformances were identified: 1. Sample CW0472 (04.09.14) 56 day cubes reached an average compressive strength of 48.5N/mm^2 2. Sample CW0478 (06.09.14) 56 day cubes reached an average compressive strength of 48.1N/mm^2 3. 3 x cube results were missing from the records, dated 08.05.15, 13.08.16 & 10.01.17. 4. Upon further investigation, sample CW1411 (13.08.16) 56 day cubes reached an average compressive strength of 48.7N/mm^2 The required compressive strength for the concrete used is 50N/mm^2 __ to provide tracker of concrete testing and how non-conformant test results are identified & communicated
| 02SL - Stations (LUL) | Cxxx-NCR-002042 | NCR | LULO Steelworks - Missing MDC documents related to Area 2 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-07-11 | 2017-06-15 13:46 | -26 | 2017-06-01 12:38 | Civil - Structural Engineering | 1500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | 2no. MDC documents related to the steel installation on Area 2 were never issued to CRL for approval.
| 02SL - Stations (LUL) | Cxxx-NCR-002043 | NCR | CHS - Level 7 __R D7/015 Structural Opening Out of Tolerance |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-01-29 | 2019-05-23 14:55 | 114 | 2017-06-02 12:36 | Architectural - Brickworks/Blockworks | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The structural opening for the door (D7/015) in the __R room has an issue with the lintel level and structural slab level. This is likely due to the local deviations on the slab when laying blocks with an additional of the architectural blockwork tolerances. See elevation K-K mark up with survey points shown
| 02SL - Stations (LUL) | Cxxx-NCR-002044 | NCR | DSS - Level 7 Slab - Missing UKAS records |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-07-12 | 2017-06-12 08:45 | -30 | 2017-06-02 12:53 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | Missing UKAS records for DSS Level 7 slab pours taken on - 25/01/17 and 02/02/17, CW1667 CW1664
| 02SL - Stations (LUL) | Cxxx-NCR-002045 | NCR | CHS - Level 8 Screed Angle Upstand |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-10-18 | 2018-10-24 17:03 | 6 | 2017-06-08 09:51 | Architectural - Finishes | 1300 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | A concrete upstand is shown in (Cxxx-__M-A-DDD-D061_WS107_8-19081) and (Cxxx-__M-A-DDA-D061_WS106_8-10281) drawing relating to structural opening D8/010 between DR2 8/792 and CIR-S (Escape Corridor) 8/084. This is also apparent of the structural opening D8/012 between unused room and CIR-S and structural opening D8/008 between Riser 3 8/788 and CIR-S 8/084. The concrete upstand has been missed from Cxxx drawing (Cxxx-HYD-A-DDA-D061_WS107-11660) but shown on the architectural detail drawings to be an interface. A steel angle has been installed in its place.
| 02SL - Stations (LUL) | Cxxx-NCR-002046 | NCR | LULO Steelworks - Area 2 - Gable Wall installation |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-01-15 | 2018-03-02 09:36 | 46 | 2017-06-05 15:47 | Civil - Structural Engineering | 1000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Previous Construction - Other | Completed |  | The wall behind the Gable Wall truss was not at the location given in Cxxx-RFI-004256. 3 no. props mark 22119 and 3 no. props mark 22120 cannot be installed.
| 02SL - Stations (LUL) | Cxxx-NCR-002047 | NCR | LULO Steelworks - Roof deck bearing width on the Western Canopy (Entrance Steel) |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-07-16 | 2017-07-12 13:41 | -4 | 2017-06-06 08:31 | Civil - Structural Engineering | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On the West Canopy of the station entrance steel, there is insufficient deck bearing onto the steel (45mm) on the Northern sheet (along grid line 23 + 1.8m. and between grid lines A-A1).
| 02SL - Stations (LUL) | Cxxx-NCR-002048 | NCR | DSS - Stair 5 Cast out of Tolerance |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-12-07 | 2017-12-20 13:32 | 13 | 2017-06-07 14:32 | Shafts - Shafts General | 4107 |  | Workmanship | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Steps have been pour out of tolerance through out Stair 5 Flights.
| 02SL - Stations (LUL) | Cxxx-NCR-002050 | NCR | DSS - PCC - East/East North Elevation Panels installed out of tolerance |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-11-04 | 2017-10-26 09:21 | -9 | 2017-06-07 21:36 | Shafts - Shafts General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As per clause JH42.3216 of Architectural Specification the maximum deviation from design position for PCC panels is 6mm. A number of panels on East/East North elevations were installed 1-3mm out of tolerance.
| 02SL - Stations (LUL) | Cxxx-NCR-002051 | NCR | DSS - Lift 2 (Wall 4) Missing Builder work hole |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-07-19 | 2017-08-03 07:56 | 15 | 2017-06-09 16:15 | Shafts - Shafts General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | An additional Builders Work hole is required in Lift 2.
| 02SL - Stations (LUL) | Cxxx-NCR-002053 | NCR | HCDL platforms- change to SSL levels |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-07-28 | 2017-07-17 12:35 | -11 | 2017-06-08 13:26 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - No evidence of program review from Contractor's Quality Manager or Management | Completed |  | At the completion of HCDL concrete slab works as-built survey was carried out. As a rule of thumb SSL level = FFL- 125 mm. (for example if FFL= +110.125 m then SSL= 110.000 m). This means that the designed SSL levels shown on drawings Cxxx-HYD-S-DDA-D061_WS106_2-75714 and Cxxx-HYD-S-DDA-D061_WS106_2-75716 are raised by approximately 50 mm to 60 mm. Thickness of the slab didn’t change (175 mm thick) and FFLs of the platforms didn’t change. Also GSM building SSL slab didn’t change SSL= +109.925 Reason for the change was to reduce depth of the screed under the paving (from approx. 160-220 mm to 75 mm) this helped significantly reduce the cost of paving works (by both saving amount of material, time and labor required) Assessment on various drawings (including pile caps, foundations, GSM building, Lift 5, Lift 10 skirting and threshold details, stair 24 drawings, ACO drainage) was made to establish if raising SSL by 50 mm to 60 mm will affect any other works. There is no negative impact observed or design changes required due to aforementioned SSL changes. Cxxx-RFI-003029 (attached) was raised by __ to Crossrail regarding this matter on 15/07/2015. Crossrail response is that acceptance from __/__ has to be obtained for proposed change. This was never properly and formally communicated to __/BH and CRL approval wasn't obtained. Cxxx-__-PTR-3398 was raised to __ for approval of mentioned changes
| 02SL - Stations (LUL) | Cxxx-NCR-002054 | NCR | LULO - Concourse Concrete Quality |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-09-07 | 2017-09-20 12:56 | 13 | 2017-06-09 12:25 | Civil - Civil Engineering General | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Whilst completing remedial works on the lower concourse, there have been a number of defects discovered related to the quality of workmanship when casting the concrete slab. Attached photographs show three locations where concrete has failed to reach areas of decking and as a result have impacted the structural integrity of the concourse structure. Plywood used to cast a slot/recess within the surface of the concrete resulted in the restricted flow of concrete to the areas below and prevented compaction of the concrete. These slots/recesses are detailed n drawing Cxxx-__M-E-DDA-D061_WS106_3-31601 and the areas requiring repair are highlighted on the attached drawing.
| 02SL - Stations (LUL) | Cxxx-NCR-002055 | NCR | LULO GSM - Variance in lintel heights to level 2 blockwork northern elevation |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-02-28 | 2018-02-28 17:58 | 0 | 2017-06-20 09:19 | Architectural - Brickworks/Blockworks | 2130.76 |  | Design | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | It has been identified that lintel heights for doorways D2-014, D2-026, D2-019 on the northern elevation of GSM level 2 do not align at the same height. Drawing Z-10410 depicts these door openings at the same consistent level for the finished construction. A site survey of the 3no. doorways has produced the following as-built heights to the underside of the lintels: D2-014 +112.100 D2-026 +112.110 D2-019 +112.150 Upon further analysis of the IFC drawings (marked up copies of which are attached to this NCR), there appears to be discrepancy between drawings showing the setting out point of the internal 50mm step within the room. This affects doorways D2-014 and D2-019. Please refer to the marked up drawings attached to this NCR for further details, where you can see the level 2 setting out plan drawing does not agree with the internal elevation drawings. Further to this, between the plan view on the internal elevation drawing and the cross section of the door structural opening, there is a discrepancy. Having analysed the drawings, I believe the installation of the lintels is correct to the drawings that have been provided for blockwork setting out. The permitted variance in doorway structural opening height is +/- 5mm as per the Specification and BS 8000 Part 3.
| 02SL - Stations (LUL) | Cxxx-NCR-002056 | NCR | CHS - Stair 40 and 41 Cast out of tolerance |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-01-31 | 2018-01-11 11:01 | -20 | 2017-06-12 14:23 | Shafts - Shafts General | 5631.2 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Riser have been poured out of tolerance in Stair 40 and 41
| 02SL - Stations (LUL) | Cxxx-NCR-002057 | NCR | LULO - HCDL Infill, Testing for Material Characterisics |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-03-01 | 2017-10-24 08:42 | -128 | 2017-06-13 10:36 | Civil - Fill | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Testing has been carried out by the supplier off the 6N and Type 1 at the time of the MCR submittals. However these have not been carried out on the material delivered to site for index properties other than material gradings
| 02SL - Stations (LUL) | Cxxx-NCR-002058 | NCR | DSS - PCC - Torque Calibration Cert Out of Date |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-08-25 | 2017-08-22 09:27 | -3 | 2017-06-13 17:47 | Shafts - Shafts General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | The calibration cert for the the torque wrench used for torque of the nuts of the fixings on Lower Western, East North, East and North elevations of PCC cladding was out of date by the time the works were completed.
| 02SL - Stations (LUL) | Cxxx-NCR-002060 | NCR | Stair 24 underside - concrete spalling due to MEP __ fixings too close to concrete edge |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-08-11 | 2017-08-08 06:55 | -3 | 2017-06-13 15:33 | Electrical - General | 2000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The unistrut fixings on the underside of stair 24 have been installed too close to concrete edge. This has led to large sections of concrete spalling as per the attached photos. There is also several instances of drilled holes no longer in use not being repaired as per the approved procedure.
| 02SL - Stations (LUL) | Cxxx-NCR-002062 | NCR | LULO - Area 1 Upper Deck Missing Concrete Check Sheet |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-08-13 | 2017-08-16 07:27 | 3 | 2017-06-14 10:23 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | The Concreting Check Sheet (Pre Pour, Pour Record & Post Pour) is missing or mislaid
| 02SL - Stations (LUL) | Cxxx-NCR-002063 | NCR | CHS - FLOORS OUT OF TOLERANCE MULTIPLE LOCATIONS |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-03-14 | 2018-04-03 11:08 | 20 | 2017-06-23 10:12 | Architectural - Finishes | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On completion of floor surveys to finished floor levels in multiple locations within the CHS shaft om multiple levels it was determined that in distinct locations the finished floor level (FFL) was found to be out of tolerance. the variance is from 1 mm within 1 meter of adjacent survey points to 10 mm within 1 meter of adjacent survey points.The allowable tolerance is +/- 5 mm. the exact variance and locations are as follows: Level B Chiller room. 2 locations. .002 to .010 = + 3 mm & .003 to .009 = + 1 mm. Level A PFR room (A/779 MCC2)multiple locations ranging from +1mm + 3mm(2 locations), +6mm (3 locations) , +7mm, +8mm, +10mm, +11mm. Level A Smoke extract room. (A/777 MCC4) +2mm(2 locations , +4mm, +5mm, +14mm(2 locations , +15mm(3 locations , +16mm (4 locations
| 02SL - Stations (LUL) | Cxxx-NCR-002064 | NCR | LULO Concourse repair works commenced without approved design & ITP |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2017-09-29 | 2017-09-21 11:54 | -8 | 2017-06-15 09:52 | Civil - Civil Engineering General | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Works commenced on the lower concourse without an approved design or ITP. The works in question were as a result of a previous non-conformance. FCD-20272 was raised 06.06.17, and reworked back 12.06.17 for further information. Works on-site commenced 14.06.17
| 02SL - Stations (LUL) | Cxxx-NCR-002066 | NCR | CRL Platforms - CP1-EPW1-ES1 Asbuilt Toilerances |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-08-25 | 2017-08-24 07:19 | -1 | 2017-06-16 14:55 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The AsBuilt survey has been carried out in CP1, EPW1 and ES1. Please see attached files for highlighted survey drawings showing the areas which are out of tolerance +/- 10mm. The locations outside the required tolerance are summarised below: CP1 Chainage 20m Platform Slab +0.014m to +0.019m Chainage 25m Platform Slab +0.011m to +0.017m Chainage 30m Internal Wall -0.011m EPW1 Chainage 05m Platform Slab +0.012m Internal Wall +0.011m Chainage 15m Internal Wall -0.012m Escalator Stairs (Location is given between horizontal setting information points going from bottom of stairs to top of stairs) Setting Information 0.000 to 8.851 Bottom of Stairs +0.016m to +0.018m Setting Information 8.851 to 15.673 Stair Level -0.012m Stair Level -0.011m Setting Information 16.680 to 24.508 Stair Line +0.018m Stair Line +0.015m Stair Line +0.020m Stair Line +0.017m Stair Line +0.019m Stair Line +0.019m Stair Line +0.014m Stair Line +0.026m Stair Level -0.014m Stair Level -0.015m Stair Level -0.011m Top Of Stair Slab -0.025m to 0.022m Escalator Plinths 1no plinth +0.014m and -0.013m
| 02SL - Stations (LUL) | Cxxx-NCR-002067 | NCR | DSS - Level 3 Column C3-38 and C3-39 Shrinkage |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-04-30 | 2018-02-23 10:03 | -66 | 2017-10-03 08:20 | Shafts - Shafts General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The concrete shrunk from the soffit of the capping slab.
| 02SL - Stations (LUL) | Cxxx-NCR-002068 | NCR | Platform Tunnels - GRC - Bay 1a skirting kerb |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-11-23 | 2017-09-12 14:24 | -72 | 2017-06-26 11:49 | Architectural - General | 1000 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | A slight manufacture error in baseplate [A-01-S01-A-B01-50519-103] has resulted in the contractor being unable to correctly install the skirting kerb support infill strut. It has been possible to install the passenger panel support infill strut directly above. This confirms it is not a setting out / installation issue.
| 02SL - Stations (LUL) | Cxxx-NCR-002069 | NCR | South Accommodation Block Slab Thickness Out Of Tolerence |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-08-22 17:26 | 2017-08-22 17:36 | -365 | 2017-06-22 11:31 | Civil - Structural Engineering | 2500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | It has been identified that the slab in the South Accommodation block is out of tolerance. Drawing Cxxx-HYD-S-DDL-D061_WS106_1-74063 specifies that the slab should be 175mm thick however in a localised area (1m2) the slab is reduced to 153mm thick (see attached document for location and details). __ identified this issue whilst installing the secondary steel fixings.
| 02SL - Stations (LUL) | Cxxx-NCR-002070 | NCR | DSS - Transformer Room 1 - Removal of Signed Off Conduit |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-08-21 | 2017-09-11 07:29 | 21 | 2017-06-22 12:10 | Electrical - Cable Management | 2500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Installed and inspected conduit has been removed without prior notification to CRL.
| 02SL - Stations (LUL) | Cxxx-NCR-002072 | NCR | DSS - Missing waterproof checksheets - Sub construction Packages Slab, Walls and Columns Level 4-3 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-08-25 | 2017-08-22 09:18 | -3 | 2017-06-22 15:58 | Civil - Drainage | 1000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | Missing __-1 waterproofing checksheet for level 4-3 Slabs, walls and column. These are required for the submission of Cxxx-__M-C-LRC-D061_WS105-50094
| 02SL - Stations (LUL) | Cxxx-NCR-002073 | NCR | DSS - Level 4 - 3 Slab walls and Colums RC Items Pour out of Tolerance |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-03-26 | 2018-02-21 13:36 | -33 | 2017-06-28 09:49 | Shafts - Shafts General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | RC Items in Level 4-3 Slab walls and columns have been poured out of Tolerance.
| 02SL - Stations (LUL) | Cxxx-NCR-002074 | NCR | DSS - Lvl C parapets around lvl B Service Courtyard cast out of aligmnent |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-12-25 | 2017-10-11 08:44 | -75 | 2017-06-28 17:02 | Architectural - General | 4000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The lvl C parapets around Lvl B service area of DSS have been cast out of alignment causing a step to the walls underneath. The differences in alignment are up to 35mm This does not allow to install the __ render over these walls to the specified tolerances.
| 02SL - Stations (LUL) | Cxxx-NCR-002075 | NCR | Incorrect installation of metal deck |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-08-06 | 2017-09-05 15:04 | 30 | 2017-06-27 15:51 | Architectural - Roofing & Exterior Treatment | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During not official site inspection by __ engineer on R10N was identify that installation of metal deck on R10N centre roof by __ is not as per drawings. Fixings of the metal deck were too close to the edge of top hat without minimum bearing. Works were stopped and __ designer were invited for inspection to provide repair solution. (attached photos with incorrect installation)
| 02SL - Stations (LUL) | Cxxx-NCR-002076 | NCR | LULO Steelworks - Northern Concourse - Connection of roof beam West (11149) to column (11090) on Grid Line 2.2 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-08-07 | 2017-07-17 14:24 | -21 | 2017-06-28 12:22 | Civil - Structural Engineering | 1500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Because of a lack of fit in the connection between the cantilever roof West beam (mark 11149) and the column (mark 11090) on Grid Line 2.2, only 5 no. instead of 6 no. M36-8.8 bolts can be installed.
| 02SL - Stations (LUL) | Cxxx-NCR-002077 | NCR | LULO Steelworks - Northern Concourse - Connection of floor beam (mark 11134) to column (mark 11207) |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-08-07 | 2017-07-17 15:13 | -21 | 2017-06-28 12:58 | Civil - Structural Engineering | 2000 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Because of a lack of fit in the connection between the beam mark 11134 and the column mark 11207 on Grid Line 2, the beam mark 11134 cannot be installed. M24 nuts have been tag welded instead of M20. Therefore the wholes have to be reamed.
| 02SL - Stations (LUL) | Cxxx-NCR-002078 | NCR | Plant room Level 3 concrete plinth |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-08-12 | 2017-08-31 08:43 | 19 | 2017-07-03 08:19 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | A PTR was raised to __ for clarifiation regarding the plinth shown on the Cxxx drawing and sketch was sent back with more details. On 01/07/2017 the three plinths were poured without sending a RFI to Cxxx to approve the __ sketch . SUB CONSTRUCTION CERTIFICATE - Cxxx-__M-A-CER-D061_WS106-50077 Drawing Numbers - Cxxx-__M-A-DDC-D061_WS106_3-17332 - Cxxx-__M-A-DDC-D061_WS106_3-17329 - Cxxx-__M-A-DDC-D061_WS106_3-17327
| 02SL - Stations (LUL) | Cxxx-NCR-002079 | NCR | Platform Tunnels - GRC - PT4 - CP1/EB Incorrect SCL fixing |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-02-05 | 2017-09-05 07:46 | -153 | 2017-07-20 12:28 | Architectural - General | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | At P-T4 junction CP1-Eastbound the contractor had an one instance on each plinth (1 of 4 fixings on LHS and 1 of 4 on RHS) where the tolerance to the SCL required Detail D on DWG [Cxxx-__M-A-DWG-D061_WS106-53111 C01]. i.e. gap between SCL and back of plinth <80mm. 3 No. detail A fixings were used on each plinth for the other plates. For 1 No. fixing on each plinth the contractor then incorrectly installed 20mm threaded rod with __ Hit HY 200A, 200mm embedment into SCL, instead of the __ M12 plus 200 screw anchor detailed in Detail D. Note: In the final state this threaded rod is left with nuts / washers loose. Please find attached __ acceptance of the incorrect fixing in the form of Cxxx-GRC-014 [attached].
| 02SL - Stations (LUL) | Cxxx-NCR-002080 | NCR | CHS - Reinforce Concrete Items Poured out of Tolerance |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-05-11 | 2018-02-21 13:43 | -79 | 2017-07-06 08:21 | Shafts - Shafts General | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | CHS As-Built survey of the slab walls and Columns show elements out of tolerancee. Please see 'Reference Document' for the as built Surveys
| 02SL - Stations (LUL) | Cxxx-NCR-002081 | NCR | PES lights |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-03-25 | 2018-08-31 08:33 | -206 | 2018-04-09 08:47 | Electrical - Lighting | 60000 |  | Manufacturing Defect | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Other | Completed |  | PES lights have not been manufactured in line with benchmark fitting and have dark spots exact details to be provided by Design Plan. Note this is a site wide issue with all of this manufactures fittings affected.
| 02SL - Stations (LUL) | Cxxx-NCR-002082 | NCR | DSS - Stair 1 and 2 - Failed UKAS Results |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-11-07 | 2017-11-02 12:16 | -5 | 2017-07-10 13:34 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | CW1070 Flight 11 CW1056 Flight 12 CW1465 Flight 15 CW1472 Flight 17 Line 31 concrete poured within DSS in Stair 1 and 2 have not achieved the required 56 day compliance strengths.
| 02SL - Stations (LUL) | Cxxx-NCR-002083 | NCR | DSS - Stairs 1&2 Cast out of Tolerance |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-01-05 | 2018-01-04 10:59 | -1 | 2017-07-10 15:46 | Shafts - Shafts General | 750 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Steps have been pour out of tolerance through out Stairs 1&2 Flights.
| 02SL - Stations (LUL) | Cxxx-NCR-002084 | NCR | CHS - Level 4 DR1 Acoustic Blockwork - Knocked Blocks |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-08-20 | 2017-09-01 13:24 | 12 | 2017-07-11 08:15 | Architectural - Brickworks/Blockworks | 2500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | On the acoustic blockwork at level 4, approximately 8no. blocks have been knocked out of position cause the mortar to crack and crumble away.
| 02SL - Stations (LUL) | Cxxx-NCR-002085 | NCR | PES Plenum Lining - PFC Channel Paint |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-09-08 | 2017-09-05 07:48 | -3 | 2017-07-13 16:16 | Civil - Civil Engineering General | 1200 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As shown in the Cxxx F1 Specification - Rev 12 section JH11.1203 part d. "d) All visible ductwork and trunking or other cable containments, device, equipment or fixing behind PES grilles shall be finished Matt Black RAL 9011. If it is not deemed possible to achieve this finish for specific components the Contractor shall submit proposed finish for Project Manager's approval." The PES Plenum Lining materials are painted offsite. The onsite installation requires 2 no vertical Parallel Flange Channels (PFCs) to be installed to the PES, then a __ panel in between and so on. During installation of the PFCs to the Westbound Plenum lining; 4 no unpainted channels were installed, which are now showing galvanised steel. The channels sit just behind the galvanised steel truss hangers of the PES. Therefore from the platform level it is not obvious that the channels are not black. The rework to remove and reinstall these channels would be significant. The majority of the plenum lining installation is now complete. The __ panels on either side of the channel would need to be removed, including Corafil, Luff and __. In various locations, dampers and CMS would also need removing. To then reinstate the __ panels would require working in a confined space inside the plenum.
| 02SL - Stations (LUL) | Cxxx-NCR-002086 | NCR | Fireproofing Damage on North Accommodation Block Primary Steel (South Face) |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-08-21 | 2017-08-18 13:14 | -3 | 2017-07-12 14:01 | Civil - Civil Engineering General | 500 |  | Workmanship | Reject | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During installation of 6mm plate/removal of scaffolding grab locks, the fireproofing build up has been damaged. Topcoat and intumescent paint layer has been scraped back to primary steel, compromising the fireproofing system (see attached picture) and requires remedial work.
| 02SL - Stations (LUL) | Cxxx-NCR-002087 | NCR | Cast in __ inserts out of tolerance in concrete lift shafts Station wide |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-12-12 | 2017-12-14 10:46 | 2 | 2017-07-13 12:36 | Civil - Civil Engineering General | 20000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The __ deisgn requires __ Channels to be cast into the concrete lift shaft walls to enable fixing of the lift equipment in place by __ within the lift shafts ( See example drawing attached Cxxx-__M-M-DWG-D061_WS105-50008 ). It has been found that in ALL the concrete lift shafts site wide ( lifts 1,2,3,5,6 and lift 8 ), that a large amount of the halfens have been cast in to the contrete lift shafts are positionally out of tolerance to __'s requirements.
| 02SL - Stations (LUL) | Cxxx-NCR-002088 | NCR | Crossrail Platforms- Shrinkage Cracks in Internal Platform Wall (Eastbound) |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-10-27 | 2017-09-06 08:49 | -51 | 2017-07-13 15:19 | Civil - Civil Engineering General | 2500 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Shrinkage Cracks 0.3mm and larger in width have been identified in 27 locations along the Reinforced Concrete Internal Wall in the Eastbound Platform UPE between chainages 10377.55 and 10222.70. Attached Report shows locations and photos of these cracks. Note that these cracks (numbered 09 to 35) are additional to the 8 cracks identified in Cxxx-NCR-001903.
| 02SL - Stations (LUL) | Cxxx-NCR-002089 | NCR | CHS Proceeding past witness points |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2017-08-23 | 2017-09-13 07:25 | 21 | 2017-07-14 07:55 | Electrical - Cable Management | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Following an Inspection to Primary CMS within SR2 and ESR a number of snags were identified resulting in installation works being rejected until such time the snags were rectified. These snag still exist in the install and the Contractor has commenced wiring within an unacceptable installation. Additionally CMS works installed into TR1 and 2 have been carried out with no inspection offered to CRL. This installation has now also had Fire cabling installed but the installation remains unfinished. To further enhance the problem the Transformers have been installed making it necessary for the works to be carried above them.
| 02SL - Stations (LUL) | Cxxx-NCR-002090 | NCR | LULO GSM - Water ingress and potential damage to completed works |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-08-02 | 2018-09-03 16:22 | 32 | 2018-04-24 12:59 | Architectural - Ceilings & Soffits | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Significant rainfall was experienced overnight between the afternoon of Tuesday 11th July and Wednesday morning 12th July, which has lead to water ingress to the GSM Building. A record of the ingress locations and photos has been recorded on Wednesday 12th July by the __ site team as well as the Subcontractor whose completed works may have sustained damage. These records are attached to this NCR.
| 02SL - Stations (LUL) | Cxxx-NCR-002091 | NCR | Maintenance issue DSS level 4 CIR-PL 4/238 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-08-26 | 2017-09-13 07:31 | 18 | 2017-07-17 12:17 | Electrical - Cable Management | 4800 |  | Planning | Repair | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Clash of services namely maintenance of dampers was being hampered by CMS in the way level 4 DSS CIR-PL 4/238 outside the battery room
| 02SL - Stations (LUL) | Cxxx-NCR-002092 | NCR | CHS Lift 8 __s out of Tolerance |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-10-31 | 2019-01-15 21:53 | 76 | 2018-04-23 07:54 | Shafts - Shafts General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __ channels in Lift 8 have been cast out of tolerance.
| 02SL - Stations (LUL) | Cxxx-NCR-002093 | NCR | LULO Steelwork - North Accommodation Block - Connection of beam mark 11024 to beam mark 17018 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-08-28 | 2017-08-21 08:23 | -7 | 2017-07-19 16:41 | Civil - Structural Engineering | 4000 |  | Manufacturing Defect | Repair | 3 (3-6k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | The fin plate for the connection of beam UB254x146x31 (mark 11024) to curved beam UB533x210x82 (mark 17018) has been welded in the wrong position. Therefore, the beam UB254x146x31 (mark 11024) cannot be installed.
| 02SL - Stations (LUL) | Cxxx-NCR-002096 | NCR | DSS - Lift 2 __s out of tolerance |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-08-21 | 2018-07-09 07:50 | -43 | 2018-04-23 07:55 | Shafts - Shafts General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Details of the areas of non-conformances can be found in the As Built Survey Cxxx-__M-C-RGN-D061_WS105-50047.
| 02SL - Stations (LUL) | Cxxx-NCR-002098 | NCR | LULO GSM - Cracking to level 1 brick/blockwork in external wall |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-12-23 | 2017-12-20 17:12 | -3 | 2017-07-26 13:53 | Architectural - Brickworks/Blockworks | 5750 |  | Design | Rework | 3 (3-6k) | Complete | Previous Construction - Other | Completed |  | Cracks propagating through new blockwork construction have been recorded to several locations in the exterior cavity wall to GSM level 1. Locations as noted below: (1) Eastern elevation: Inner leaf on gridline GL between G4 and G6. [Photos #1, #2]. (2) Southern elevation: Inner leaf on gridline G1 between GH and GI. [Photo #3]. (3) Western elevation: 2no. locations to outer leaf on gridline GD between G3 and G4. [Photos #4, #5, #6, #7]. (4) Western elevation: Inner leaf on gridline GD between G4 and G5 above door D1/091. [Photo #8].
| 02SL - Stations (LUL) | Cxxx-NCR-002099 | NCR | CHS-level 06-lobby to CER-tray removal for firestopping |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-09-27 | 2017-09-22 07:10 | -5 | 2017-07-28 12:38 | Electrical - Cable Management | 1000 |  | Planning | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | cambridge heath shaft level 06 - removal of a 2m section of 600mm comms tray to allow fire stopping to proceed then reinstating. tray section previously signed off by cross rail. drawing file = Cxxx-__M-E-DDA-D061_WS107_6-31940
| 02SL - Stations (LUL) | Cxxx-NCR-002100 | NCR | CHS-LEVEL 04 RISER 03 BENT LVB TRAY DUE TO TEMP SUPPLY ENTERING SWITCHROOM SR-LV-2 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-09-27 | 2017-09-20 14:26 | -7 | 2017-07-28 13:13 | Electrical - Cable Management | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | CHS-LEVEL 04 RISER 03 - Reworks on LV'B' 450mm cable tray in riser 3 level 4 due to installation of tempoary supply through riser 3 to switchroom SR-LV-2. drawing ref - Cxxx-__M-E-DDA-D061_WS107_4-31940
| 02SL - Stations (LUL) | Cxxx-NCR-002102 | NCR | LULO-STH L3 Plantroom- Fireboarding to windposts on Truss 3 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-10-13 | 2017-10-09 08:07 | -4 | 2017-08-18 13:48 | Fire - Suppression | 750 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | While installing the fireboarding to the Windposts in the plantroom it was noticed that the fireboarding on WP 1 and WP 5 on Truss 3 was not flush with the blockwork. The fireboarding sits proud of the face of the blockwork. Construction of the blockwork and steel windposts both have independent installation tolerances. Therefore the tolerances for blockwork setting out, and blockwork vertical construction tolerances, when against the windpost installation with its own setting out and vertical tolerances can be magnified with up to a permissible 20mm misalignment between the blockwork and steelwork installations. This acceptable tolerance installation misalignment is visually compounded when the required fire rated protection to the steel work is achieved by a 20mm fireboard to be cladded over the windpost in to a designed 20mm vertical recess as per drawing WS106_Z-19270 detail 8. The permissible construction tolerances can therefore increase and/or decrease up and down the vertical face of the steelwork/ blockwork interface and result in a fireboard construction that is proud of the wall, or recessed further into the wall - dependent on the direction of misalignment.
| 02SL - Stations (LUL) | Cxxx-NCR-002104 | NCR | LULO – West Lift Lobby – Incorrect installation of wall ties |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-09-11 | 2017-09-08 15:16 | -3 | 2017-08-02 08:44 | Architectural - Brickworks/Blockworks | 1200 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the installation of the blockwork for the West Lift Lobby the wall ties have not been installed correctly in to the mortar, see attached marked up photograph. As a result the ties are loose and are not suitable for use.
| 02SL - Stations (LUL) | Cxxx-NCR-002105 | NCR | LULO - LO Concourse - Quality Control Failures |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-11-21 08:57 | 2017-12-05 09:40 | 14 | 2017-08-04 14:06 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Electrical or instrument noise | Completed |  | Following on from CRL-OBS-17599, CRL-OBS-17623 and Cxxx-PMC-16062, this NCR is to record failings in quality control whilst completing remedial works on the LO concourse. The Contractor acknowledges that protection measures to date have been inadequate and this has resulted in damage to the repair concrete at a location between gridline 22 and 23. The ITP shall be briefed to the site team and Engineers to ensure protection measures are in place and that the importance of these is understood. The defect shall also be rectified. The Contractor also acknowledges that storage of concrete cubes after pours dated 19th July and 26th July 2017 were not in accordance with the correct procedure. The correct arrangement for storage of concrete cubes is to deliver these to the Contractor’s testing facility the following day of the pour. A quality briefing shall be presented to the engineering team to reiterate the importance of the correct procedure for storing concrete samples. Please see attached the briefing that shall be delivered.
| 02SL - Stations (LUL) | Cxxx-NCR-002106 | NCR | DSS LVMSB/A Switchboard Multifunction Display Damaged |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-09-18 | 2017-09-20 12:44 | 2 | 2017-08-09 11:02 | Electrical - Switchgear | 1500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | A multifunction display unit on LVMSB/A has been damaged to a point where it will need to be replaced.
| 02SL - Stations (LUL) | Cxxx-NCR-002107 | NCR | LULO - GSM Building - Wall Out of Plumb |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-10-05 | 2017-09-01 14:24 | -34 | 2017-08-10 17:24 | Architectural - Brickworks/Blockworks | 4500 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Wall panel between corridor and DNO Switchroom has been installed out of tolerance vertically, please see attached photographs. The panel bows in the top half of the wall, starting approximately 1.5m from the slab and deviating 13mm at the worst point rectifying itself at the head of the wall. These measurements have been taken using a plumb line with __ supervisor present, and later verified using a total station measuring from the nearest gridline.
| 02SL - Stations (LUL) | Cxxx-NCR-002108 | NCR | Crossrail Platforms - GRC - EB bay 85 pull testing failure |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-11-30 | 2017-08-29 08:08 | -93 | 2017-08-09 10:17 | Architectural - General | 1010 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __ has so far tested a minimum of 60% of fixings __ Plus M12 150mm screwbolts onsite. These are used for the GRC crown SCL bracket as per drawing [Cxxx-__M-A-DWG-D061_WS106-50098] and Cxxx-FCD-001973 . This is well in exceedance of the 25% specified in the agreed ITP [Cxxx-__M-A-ITP-D061_WS106-50153]. On 08/08/17 __ (a company with UKAS pull testing accreditation) attended Whitechapel and pull tested 35 No. screwbolts. During this survey 1 No. screwbolt was found to fail the pull testing. This is the first fixing found to fail after a total of approx. 450 No. installed. The SCL hanger plate has redundant holes intended for use due to clash with steel in the concrete. __ installed another fixing in the adjacent hole. This was pull tested by __ and found to pass the 20kN test load. __ are currently preparing a report of the pull testing conducted 08/08/17.
| 02SL - Stations (LUL) | Cxxx-NCR-002109 | NCR | LULO - Missing offsite testing records for __ |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-09-01 | 2017-11-10 13:00 | 70 | 2017-08-09 12:00 | Civil - Civil Engineering General | 1000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | The preparation for __ activity (inspection number 4.7) in the ITP for LULO Steelwork Fire protection (Cxxx-__M-C-ITP-D061_WS106-53040) states that dry bulk density test to be carried out by an independent UKAS testing laboratory. Records for the dry bulk density test cannot be provided for the duration of the __ works on the LULO works.
| 02SL - Stations (LUL) | Cxxx-NCR-002110 | NCR | LULO - Missing calibration certificates for __ testing equipment |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-09-01 | 2017-10-20 11:31 | 49 | 2017-08-10 08:29 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | Contractor is unable to provide the calibration certificate for the scales used during the density measurement as part of the __ testing for the LULO works.
| 02SL - Stations (LUL) | Cxxx-NCR-002111 | NCR | CHS - level 07 - sesr - c620 isolator |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-09-18 | 2017-09-13 07:36 | -5 | 2017-08-09 14:04 | Electrical - LV Equipment | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | c620 isolator located sesr room on level 07 has a damaged handle and will result in replacement.
| 02SL - Stations (LUL) | Cxxx-NCR-002112 | NCR | LULO - Lack of onsite testing records for __ |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-09-01 | 2017-11-10 12:53 | 70 | 2017-08-09 16:46 | Civil - Civil Engineering General | 1000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There are a number of missing test record sheets for density measurement and slump tests for the LULO __ works ranging from start of works in June 2016 to January 2017.
| 02SL - Stations (LUL) | Cxxx-NCR-002114 | NCR | Westbound - Cxxx - OHLE - CMS installed to P rev Drawings |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-09-20 | 2017-09-26 14:08 | 6 | 2017-08-11 09:12 | Electrical - Cable Management | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | OHLE and Cxxx CMS to tunnel mouth area. Cxxx did not provide CMS requirements in a timely manor to allow Cxxx design team to complete the design and have drawings approved. To enable the installation to progress and mitigate delays to Cxxx installation team a site meeting was held with CRL Cxxx and Cxxx where Cxxx confirmed actual requirements. Cxxx were to install the CMS in the reduced platform area in Cxxx air space however Cxxx were unable to achieve in their own time spans. Cxxx therefore progressed the installation however a by exception review has not been carried out. FCD 2167 has now been started but not completed.
| 02SL - Stations (LUL) | Cxxx-NCR-002115 | NCR | Minor damage to LO Platforms 5&6 precast planks |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-10-23 | 2017-10-25 08:33 | 2 | 2017-09-13 14:58 | Structural Engineering - Pre-cast | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | As per drawings Cxxx-__M-C-DWG-D061_WS106-53601 & Cxxx-__M-C-DWG-D061_WS106-53602, the LO Platforms 5&6 extension consist of 56 precast planks. During the installation of planks P5/S13A, P5/S18A, P5/S21A, P5/S23A, P6/S7A, P6/S9A, P6/11, P6/S12A, P6/13A, P6/S15 & P6/17A, there was minor damages ('chips') to the edges/corners (photos attached).
| 02SL - Stations (LUL) | Cxxx-NCR-002116 | NCR | LULO Concrete cube storage |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2018-04-30 | 2019-07-04 11:27 | 430 | 2017-08-14 15:32 | Civil - Civil Engineering General | 2000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | CRL-OBS-17713 highlighted that the current cube storage area serving the LULO section is non-conformant. The following issues were identified: 1. 5 no unmarked cubes stored inside room 2. Above cubes being stored incorrectly (i.e. not in curing task) 3. No temperature control within room 4. No curing tank present. __ to provide cube storage room as per the relevant standards. __ lab to be contacted to provide comment on lack of correct cube storage. __ to provide process map/flow diagram for concrete testing, detailing each stage of the process and relevant competency (to undertake that task)
| 02SL - Stations (LUL) | Cxxx-NCR-002117 | NCR | LULO GSM - Staff Lobby CIR-S blockwork wall alignment |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-12-15 | 2017-11-30 18:29 | -15 | 2017-08-31 12:03 | Architectural - Brickworks/Blockworks | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | On level 2 of the GSM, the line of the Staff Lobby CIR-S north wall is difficult to align due to cumulative global tolerances accruing across Lift 9 steelwork installation and the Platform Cleaning Machine Room doorway D2/013. A redline markup of the situation is provided as an attachment to this NCR. There are 3no. concrete lintel support brackets to align (doorway D2/013 and Lift 9 entrance), as well as fireboarding to the lift 203UC columns to satisfy and the blockwork nib which has already been constructed to the first lift (7 courses). Generally, each individual element is within its own respective tolerance for installation but when accumulated there is difficulty aligning the blockwork when drawing a line. NCR-1884 raised for Lift 9 out of verticality on level 2 does not play much of a factor, as the verticality of the blockwork wall is not the issue. However, it was picked up when surveying the steelwork that the south-west column is slightly off line toward gridline G3 - this now plays a part as the design line of the wall should be 48mm from this column to the face whereas with the as-built column position this is reduced to 35mm.
| 02SL - Stations (LUL) | Cxxx-NCR-002118 | NCR | DSS - PCC - Damage to Panels P107 and P112 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-03-12 | 2018-03-19 16:25 | 7 | 2017-08-19 12:07 | Architectural - General | 7500 |  | Damaged | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the adjustment of panel P107 the installers damaged the corner of the panel as well as the face of the panel and panel P112 underneath. The damage to the faces of the panels is superficial and can be repaired in situ but the damage to the corner of panel P107 is more severe showing clear 'scaring' around the corner of the panel of total length of over 300mm and as the damage cannot be assessed properly there is a possibility of the corner coming off at some point.
| 02SL - Stations (LUL) | Cxxx-NCR-002119 | NCR | LULO - HCDL Platforms - Pile Caps - Waterproofing check sheets not signed by IDI |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-11-17 | 2017-11-21 07:48 | 4 | 2017-08-15 13:20 | Civil - Civil Engineering General | 1500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | For the following Pile Caps the Waterproofing check sheets have not been signed by the __ IDI. Pile Cap 2H Pile Cap 2B Pile Cap 2G Lift 10 Pile Cap Pile Cap 2D
| 02SL - Stations (LUL) | Cxxx-NCR-002120 | NCR | LO platform extension - Grout cubes |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-02-28 | 2018-01-17 14:59 | -42 | 2017-09-29 11:27 | Structural Engineering - Grouting | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | The number of grout cubes taken was not as per ITP for the LO platform 5&6 extension works (Cxxx-__M-C-ITP-D061_WS106-53066)
| 02SL - Stations (LUL) | Cxxx-NCR-002121 | NCR | E51- Blockwork - Missing Mortar cube Results |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-10-22 | 2018-08-14 05:31 | -69 | 2018-05-15 08:08 | Architectural - Brickworks/Blockworks | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | Mortar Cube results were not provided as part of the QA documents as part of the subcontract package handover.
| 02SL - Stations (LUL) | Cxxx-NCR-002122 | NCR | CHS- works commencing without approved ITP |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2017-10-21 | 2017-10-06 08:53 | -15 | 2017-08-17 15:28 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | CHS drainage works have commenced without an approved ITP. ITP was issued rev 1.0 09/08/17 and returned code 3.0 15/08/17. Works have commenced on site as of 16/08/17.
| 02SL - Stations (LUL) | Cxxx-NCR-002125 | NCR | LULO HCDLstair 24 top brackets not installed |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-02-07 | 2017-11-23 10:00 | -76 | 2017-10-10 14:20 | Civil - Structural Engineering | 1500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | On the drawings: Cxxx-__M-C-DWG-D061_WS106-53506 and Cxxx-__M-C-DWG-D061-50768 there are anchors shown connecting angle bracket and stair precast unit. At the time of installation of the stairs units, bracket detail and anchors type to be used weren't known and it was decided they will be installed at later date. In effect steel beam (supporting top flight of the stairs) was concrete sprayed before brackets installation. Please see photos of the brackets where sprayed concrete fire protection was removed. Actions: 1. Brackets to be fixed to precast units 2. Concrete fire protection was removed locally to fix the brackets and needs to be reinstated.
| 02SL - Stations (LUL) | Cxxx-NCR-002126 | NCR | GSM Building - Crack in New Lintel |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-11-03 | 2017-11-02 14:17 | -1 | 2017-08-22 18:13 | Architectural - Brickworks/Blockworks | 3000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | On GSM level 2, a hairline crack has appeared on a Type 16 140x140mm Kingstone precast lintel. Lintel is located above door D2/011. After consulting with __ structural engineer, and with the lintel manufacturer, __ proposes to remove and replace the lintel. See attached emails.
| 02SL - Stations (LUL) | Cxxx-NCR-002127 | NCR | non painted drilled holes |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-01-05 | 2018-03-21 06:56 | 75 | 2017-08-22 17:56 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Holes in RHS steel stringers had been drilled on a different shift and had not been painted to seal the holes. The installation of __ channels proceeded without the holes being painted using Holobolts (which cannot be removed) on a different shift with new operatives who were unaware of the painting procedure. 1) Please see attached DWG ;Stair 27' holes drilled without application of zinga localised to box beam as shown in attachment 2) plese see pics attached 3) Please see e-mail from hollandia that proposal is acceptable 4) MCR for __ attached - is suitable for Galvanised ferrous Construction certificates in reference documents
| 02SL - Stations (LUL) | Cxxx-NCR-002129 | NCR | LULO - Existing Ticket Hall - Ductwork Mandrel Test |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-06-19 | 2018-03-28 09:27 | -83 | 2018-03-21 15:31 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Within clause JP30.2201 of the Civil Engineering Technical Specification Cxxx-__M-C-RSP-D061_WS106-50003, there is no specific requirement for mandrel testing of pipe ducts for electriacal and data cables.
| 02SL - Stations (LUL) | Cxxx-NCR-002130 | NCR | CHS-RISER 2-cms removal due to ductwork lagging |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-10-23 | 2017-10-17 07:53 | -6 | 2017-08-24 07:11 | Electrical - Cable Management | 5000 |  | Planning | Repair | 3 (3-6k) | Complete | Management Problem - No evidence of program review from Contractor's Quality Manager or Management | Completed |  | Due to access problems within riser 2 levels 3-7. bbmv have removed sections of cms to install an access scaffold for lagging to ducting. once completed we will re-issue for inspection.
| 02SL - Stations (LUL) | Cxxx-NCR-002131 | NCR | DSS - Stair 2 Level 4.5 - Drawings Discrepancy |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-11-09 | 2018-10-10 19:11 | -30 | 2017-09-04 08:19 | Shafts - Shafts General | 4000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | __ drawing of Stair 1 & 2 (Cxxx-__M-A-DDD-D061_WS105_Z-10560) GA plan shows a concrete wall to segregate the staircase from Riser B2 & B3 (on level 5). However the RC detail drawing (Cxxx-__M-C-DWG-D061_WS105-50692) doesn`t show any wall but a void instead with annotation of blockwork to be built within the opening.
| 02SL - Stations (LUL) | Cxxx-NCR-002133 | NCR | CHS - Level 08 - Riser 03 - SWA'S installed without following ITP procedure |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-10-08 10:11 | 2017-09-29 12:09 | -9 | 2017-08-25 10:47 | Electrical - Cable Management | 5000 |  | Planning | Repair | 3 (3-6k) | Complete | Management Problem - Inadequate administrative control | Completed |  | cable pulling has commenced within the cambridge heath shaft. we currently have swa's for the sump pump room and OHLEDB entering from riser 3 were the cms is missing due to removal for ducting and lagging. also the cms located in the lobby area is complete but without sign off.
| 02SL - Stations (LUL) | Cxxx-NCR-002134 | NCR | Pipe sleeves not concentric in fire stopping |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2017-10-08 | 2017-10-06 08:32 | -2 | 2017-08-29 11:04 | Civil - Structural Engineering | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | pipe sleeves are left pipes passing through fire break walls for the following fire stopping trades to fit concentrically in around the pipe to obtain the correct fire stopping gap. there are instances throughout the site where the pipe sleeve has not been installed concentrically by the fire stopping contractor.
| 02SL - Stations (LUL) | Cxxx-NCR-002135 | NCR | DSS - Lift 2 Level 6 Control Panel Remedial |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-12-15 | 2017-12-09 09:52 | -6 | 2017-09-04 07:53 | Shafts - Shafts General | 1200 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The control panel on level 6 for lift 2 has been poured 35mm to low
| 02SL - Stations (LUL) | Cxxx-NCR-002136 | NCR | CHS - Wall hatch interface with blockwork |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-03-05 | 2018-03-07 18:13 | 2 | 2017-09-20 17:10 | Architectural - Brickworks/Blockworks | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The radius wall at level 6 holds hatch (Number: AH6/001) and adjacent wall does have enough room to place the frame around the hatch. The wall hatch has already been prefabricated and adapting the blockwork is the most practical solution. Current bearing on lintel is 150mm.
| 02SL - Stations (LUL) | Cxxx-NCR-002137 | NCR | DSS - Missing Test Results for CPI __ Mortar |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2017-12-15 | 2017-12-09 09:57 | -6 | 2017-08-31 08:17 | Architectural - Flooring | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | The quality surveillance for the block work installation in the DSS (CRL-OBS-17768) highlighted a lack of CPI __ mortar test results. Activity 5.3 in ITP Cxxx-__M-C-ITP-D061_WS105-50063 Rev. 3.0 states a frequency of a minimum of 4 cubes should be tested for each silo delivery or refill. This does not correspond with the quantity of testing deliverables found in the quality surveillance.
| 02SL - Stations (LUL) | Cxxx-NCR-002138 | NCR | LULO - GSM - D1/059 Toothing In |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-10-31 | 2017-10-13 16:07 | -18 | 2017-09-04 12:14 | Architectural - Brickworks/Blockworks | 2000 |  | Planning | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Doorway D2/059 was created during Week 3 Possession. The amount of brickwork to be removed was originally asessed with the time constraints of the possession in mind, and deemed adequate. As a result of this we now have 3 materials which all move differently, causing cracks in the mortar joints
| 02SL - Stations (LUL) | Cxxx-NCR-002139 | NCR | LULO - Stair 27 Handrail Finishes |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2017-11-18 | 2017-10-23 09:48 | -26 | 2017-09-05 10:44 | Architectural - Handrail | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | As stated in CRL-OBS-18141 from 21/08/2017, the inspection of the handrail to stair 27 highlighted multiple defects: - Joint gaps above the 2mm tolerance - Sharp edges around the bolt holes - Sharp edges on tube ends - Tube ends cut at angles These defects were also brought up on the inspection of LO SME stair 3 (Cxxx-NCR-001576) and East Stair Shaft stair 23. No snagging list had been collated at the time of inspection and the sub-contractor had already demobilized from site.
| 02SL - Stations (LUL) | Cxxx-NCR-002140 | NCR | LULO- ETH- CMH04 Existing Manhole |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-12-14 | 2018-01-09 08:53 | 26 | 2017-09-05 11:59 | Civil - Drainage | 1500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The CMH04 existing manhole drainage design was approved through the by exception process. However, the design was unsuitable and resulted in the works being demolished. The CMH04 drainage chamber was then redesigned and has subsequently been approved- as detailed in the drawings attached and referenced. The new design incorporates; a hinged grating which covers the existing manhole, a double skin brickwork with concrete surround built in the upper chamber, steps fixed into the brickwork to provide access to the upper chamber and also a __ cover at FFL. The dimensions of the drainage cover at FFL have been increased to 1.250 x 1.140 to allow for adequate room for a person to stand on a ledge within the upper chamber.
| 02SL - Stations (LUL) | Cxxx-NCR-002141 | NCR | LULO - Northern Concourse - Damaged of intumescent paint during Secondary Steelwork installation |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-11-30 | 2017-11-01 12:52 | -29 | 2017-09-06 08:59 | Civil - Structural Engineering | 2500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the installation works of Secondary Steelwork underneath the West wing on the Northern Concourse the intumescent paint previously applied on the primary steelwork got damaged.
| 02SL - Stations (LUL) | Cxxx-NCR-002142 | NCR | Phase 10 - Stair 27 Temporary handrail - drilling through hollandia stair |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-11-30 | 2017-11-06 10:02 | -24 | 2017-09-07 14:00 | Architectural - Balustrade | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | This NCR has been raised to address __ deviating from the agreed design in place. As part of the Phase 10 SME works a __ handrail is to be installed onto stair cases 26, 27 & 28 as per CAT III document Cxxx-__M-C-CER-D061_WS106-53353 - Phase 10 Stair 26, 27 and 28 Temporary Handrails. This NCR specifically relates to the Western handrail of stair 27. Originally in the CAT design the handrail was to be fixed directly to the W616 wall. However, due to clashes and construction issues it was decided to use the same methodology for fixing the handrail as the Eastern side of stair 27 and utilise the __ stair treads to support the handrail. Subsequently MDC Cxxx-__M-C-CER-D061_WS106-53414 - Stair 27 temporary handrail has been raised to address the new installation methodology. The MDC has been raised after confirmation from __ that fixing directly to the stair tread was acceptable. (Please see attached). __ have drilled an additional 6 holes in the half landing of stair 27 (as per attached picture) to allow the installation of the temporary handrail. These will be the only holes required as __ will utilise the existing counter sunk stair tread connection holes for the remainder of the handrail.
| 02SL - Stations (LUL) | Cxxx-NCR-002143 | NCR | 6mm Plate out of tolerance on South Accommodation Block southern face |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-03-22 | 2019-03-13 19:43 | -9 | 2018-05-15 08:10 | Architectural - Walls | 1200 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Due to the increased deflection caused by the build up of intumescent paint on the top hats, secondary steel and primary steel on 1DS South Face (Over tracks), the 6mm plates have been pushed out of alignment marginally beyond the ITP tolerance. Our as built survey estimates this as approximately 7mm
| 02SL - Stations (LUL) | Cxxx-NCR-002144 | NCR | Cracks in __ base layer on 1DN Roof |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-12-21 | 2019-01-21 10:33 | 31 | 2017-10-02 10:47 | Architectural - Roofing & Exterior Treatment | 3000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | __ boards are not shown in F1 design of the accommodation block roofs (e.g. Cxxx-__M-A-DDD-D061_WS106_Z-11060). Boards have been added into the F2 design by __ who recommended its installation for the purpose of providing a flat surface on which __ roof insulation can be laid over the profiled deck. Drawing Cxxx-A-DWG-D061_WS106-54505 refers. Due to foot traffic on the profiled deck, the boards at the underside of the roof system have sustained hairline cracks (particularly along the line of the deck troughs and fixing locations). See attached sketch indicating the layer in question and pictures indicating extent of the damage. While the ITP (Cxxx-__M-A-ITP-D061_WS106-50155) states boards are not to have cracks, the hairline cracks (see attached images) present have not had a negative impact on the intended purpose which is simply to provide a flat surface. It is suggested that the bottom layer of __ boards are used-as-is which has been verbally agreed between CRL (__) and __ (__).
| 02SL - Stations (LUL) | Cxxx-NCR-002145 | NCR | CRL-P Westbound platform WHI/DSS/CRL-P/B/WB2 Damaged DB |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-11-30 | 2017-12-01 15:05 | 1 | 2017-09-11 07:43 | Electrical - Power Distribution | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Damage to assets caused when installing. DB WHI/DSS/CRL-P/B/WB2 paint has been scratched off on the top right corner of the panel door as in attached pictures.
| 02SL - Stations (LUL) | Cxxx-NCR-002146 | NCR | CHS - Permanent doors catching slab floor |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-01-26 | 2018-03-21 16:37 | 54 | 2017-09-26 10:09 | Civil - Civil Engineering General | 2000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During installation of permanent doors, the rubber fire seal at the bottom of the door is catching the floor slab. This is due to the uneven concrete surface at certain level in Cambridge Heath Shaft. All possible openings have been surveyed and attached mark up as shown.
| 02SL - Stations (LUL) | Cxxx-NCR-002147 | NCR | DSS - Level 6 - AHU 1 Room - Damage to Distribution Door |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-01-31 | 2018-01-31 16:05 | 0 | 2017-09-11 12:08 | Electrical - LV Equipment | 700 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | DB Board door has been damaged
| 02SL - Stations (LUL) | Cxxx-NCR-002148 | NCR | DSS - Level 7 - SR3 Room - Rust in 110 DB |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-02-09 | 2018-01-11 13:00 | -29 | 2017-09-11 12:12 | Electrical - LV Equipment | 2700 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper storage of material | Completed |  | Dampness in a 110V DB causing rust.
| 02SL - Stations (LUL) | Cxxx-NCR-002150 | NCR | Crossrail Platforms - GRC - CP1/WB PT4 tusk plinth plate |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-03-30 | 2017-10-31 09:43 | -150 | 2017-09-11 15:32 | Architectural - General | 1500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | This NCR occurs at the PT4 tusk arch junction WB-CP1. 1) During installation of the PT4 tusk splice plates (plinth to arch), it was observed that one of the holes in the front splice plate does not line up with that of the rear plate. The contractor was therefore unable to install the required M16x140mm bolt. 2) During installation of a M16x140mm bolt it sheared inside the captive nut on the rear splice plate. The contractor was using a calibrated torque wrench, set to the correct torque value. Please see attached extract of "1753-SCN-0244". This is an answer to Cxxx-GRC-RFI-013 from the designer, __, detailing the accepted remedial work. Also uploaded is the attachment to the RFI that went to __, containing pictures of this NCR. Remedial work in summary: 1) Drill through rear splice plate where required. Install loose nut and washer in place of existing captive nut. 2) Remove existing captive nut and sheared thread and install loose nut and washer.
| 02SL - Stations (LUL) | Cxxx-NCR-002152 | NCR | CRL Platforms - GRC Architectural Cladding - ES1 - Ladder frames - Additional fixing required |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-02-10 | 2018-01-30 13:08 | -11 | 2017-09-12 13:13 | Architectural - General | 1500 |  | Design | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | The ES1 frames are restrained at the crown and at the side SCL brackets. This means there is no restraint / adjustment at the bottom of the ladder frame. Due to this it has been found that the ribs cannot be installed to the correct tolerance. Due to the interface between the GRC stainless steel and the escalator there is a risk that the ladder frames may clash with the escalator install. To overcome the issue the Contractor proposes that an additional restraint is installed at the bottom of the ribs. The Contractor proposes to install an L bracket fixed into the SCL, which has slotted holes as illustrated to allow for the required adjustment. Two number holes will be drilled in the rib to secure the rib in place. The Contractor is currently is currently resolving the issue with the Supplier of the GRC Cladding – GRC-UK
| 02SL - Stations (LUL) | Cxxx-NCR-002153 | NCR | PES Plenum Testing Westbound West 125m |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-04-03 | 2018-07-16 08:35 | 104 | 2018-01-22 14:08 | Civil - Civil Engineering General | 6000 |  | Damaged | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The most recent air test on the Westbound West Plenum was on 27/11/17 and achieved 580l/s which is 16% above the maximum leakage allowed by the specification. Only 5% tolerance on failure is permitted. Previous informal air tests were resulting in higher leakage and the following remedial works have been carried out: - __ sealant applied to leaks identified in the durasteel plenum lining joints. - __ applied to PES head brackets as per FCD - Cxxx-FCD-001958. - Parex grout topped up where it had not provided an air tight seal to the tunnel wall due to the granular nature of the SCL. Following this most recent air test of the plenum WB West and a subsequent smoke test, it was been identified that the leakage is now coming from the joints between the pre-cast planks. The grout joints show some minor cracks which could allow air to leak through and will need repairing. Also the movements joints show the luff providing the air seal has lifted away from the corofil.
| 02SL - Stations (LUL) | Cxxx-NCR-002154 | NCR | PES Shotcrete Result |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-12-11 | 2017-12-06 13:43 | -5 | 2017-09-12 14:17 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The non-shrink grout used in the top and side brackets of the PES between the bracket and the SCL is Shotcrete 513 (MCR Reference: Cxxx-__M-A-LRC-D061_WS106-50373 - Grout for tunnel brackets) See attached core results for test panel sprayed on 10/08/16. The result at 28 days is 38.7N/mm2. This result is only a nominal amount below the required 40N/mm2 so the Contractor proposes to use as is. This NCR was not raised at time of works and is being retrospectively raised. For reference on site record extract from certification package attached. These works were carried out under ITP Cxxx-__M-A-ITP-D061_WS106-50110.
| 02SL - Stations (LUL) | Cxxx-NCR-002155 | NCR | R12 concourse - Damage of PCC plank R12 east PL020 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-04-20 | 2019-05-18 11:39 | 393 | 2017-09-12 17:15 | Architectural - Flooring | 3500 |  | Damaged | Reject | 3 (3-6k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Damage of PPC plank on R12 East side PL020 (attached)
| 02SL - Stations (LUL) | Cxxx-NCR-002156 | NCR | LO Concourse - remove intumescent paint under gutter post |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-01-11 | 2018-11-16 09:27 | 309 | 2017-09-13 06:51 | Fire - Compartmentation | 59000 |  | Design | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The gutter post is a steelwork element, which is fixed back to the main steel with a standard bolded connection with Nord-lock serrated washers. The post will transfer a localized point load back to the main steel, which overtime can crush or crack the intumescent layer, causing the bolded connection to lose its torque. In order to install gutter brackets on concourse roof steelwork, areas of intumescent paint is to be removed to allow for connections to be fixed/drilled. Pleas find attached photo as example.
| 02SL - Stations (LUL) | Cxxx-NCR-002157 | NCR | LULO - GSM Level 2 - Incorrect Installation of Bi-Metallic Corrosion Protection Nylon Shoulder Washers in Soffiting __ |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-01-12 | 2017-12-20 17:41 | -23 | 2017-09-13 16:47 | Architectural - Ceilings & Soffits | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | On 31 August 2017, IRF 1351 was undertaken of thermal soffit installation on GSM Level 2. As the soffit areas under inspection were only available for inspection from the floor and a platform was erected in the Mist Suppression Room, where soffits were being installed, unistrut installation was inspected in close proximity in that area. It was observed that in several areas, the bi-metallic corrosion protection between the stainless steel drop rods, nuts and washers and the galvanised unistrut was not installed properly. Typical defects included: 1) Shoulder of Nyloc isolator washer appearing to be too short, crushed or even trimmed / cut off and thus not isolating the two metals correctly (attachment 1); and 2) Nyloc shoulder isolator washer and stainless steel washers installed in the incorrect order, so that the nylon shoulder isolator washers were not isolating the washers and drop rods from the unistrut (attachment 2).
| 02SL - Stations (LUL) | Cxxx-NCR-002158 | NCR | DSS - WA-02NS Structual opening Design change |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-11-12 | 2017-10-18 08:16 | -25 | 2017-09-14 16:30 | Shafts - Shafts General | 5500 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Structural opening on WA-02NS has had a design change post construction
| 02SL - Stations (LUL) | Cxxx-NCR-002159 | NCR | LULO - FX6000 yellow colour top coat benchmark not protected |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-02-28 | 2018-01-12 17:26 | -47 | 2017-09-14 15:07 | Architectural - General | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Contractor has failed to protect the completed works. Remedial works are now required to ensure compliance with Works Information.
| 02SL - Stations (LUL) | Cxxx-NCR-002160 | NCR | Crossrail Platforms - GRC - Lower ladder missing bracket |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-12-22 | 2017-12-14 11:49 | -8 | 2017-09-13 16:22 | Architectural - General | 1500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | On a standard __ lower ladder frame A-01-S01-Z-L01-50519-082, there is an infill strut bracket missing from the frame. This ladder frame has been installed in EB bay No. 85.
| 02SL - Stations (LUL) | Cxxx-NCR-002161 | NCR | LULO - GSM Building Level 2 - Suspended __ Installation Inspection |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-12-01 | 2017-11-22 18:36 | -9 | 2017-09-18 10:52 | Architectural - Ceilings & Soffits | 1000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | On 31 August 2017, an inspection of the __ firestopping installation was undertaken in GSM Level 2. On 30 August, __ site staff instructed subcontractor __ to ensure that the __ C144 firestopping was not covered up by the firestopping in the rooms under inspection (Mist Suppression Room and DNO / Switch Room). No snagging lists were provided to the contractor by the subcontractor upon the completion of their works or created by the contractor after their pre-inspection walkthrough. Upon arriving at the site on 31 August, __ staff realised that __ operatives had continued to install soffit insulation, covering up the __ areas under inspection for that day. Due to the inspection being held at 08:30 am, at that point, the inspection was suspended.
| 02SL - Stations (LUL) | Cxxx-NCR-002162 | NCR | Crossrail Platforms - GRC - Single Leg stiffener weld |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-12-15 | 2017-12-09 09:45 | -6 | 2017-09-25 11:39 | Architectural - General | 1000 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Please see attached 1753-SCN-0266 and Cxxx-GRC-019. This is a response from __, the designer, about the installation of the "L50" single ribs. These occur in 4 No. locations in the CRL platform tunnels. A stiffener plate at the junction with the levelling brace on the single rib has been delivered by the manufacturer loose. The fabrication drawings and model shows that this plate should have been welded to the single rib. Please see confirmation from the designer that the plate must be welded. This plate will be welded to the rib onsite by the manufacturer, an onsite weld procedure and ITP will be produced to cover these works.
| 02SL - Stations (LUL) | Cxxx-NCR-002163 | NCR | GSM Building - Installing insulation before ITP approval |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-12-01 | 2017-12-05 16:17 | 4 | 2017-09-19 08:27 | Architectural - Roofing & Exterior Treatment | 1500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - No evidence of program review from Contractor's Quality Manager or Management | Completed |  | GSM Cladding activities proceeded past the ITP approval point. Insulation was installed w/c 04/09 as part of the cladding benchmark installation, after which installation carried on with approx 10no additional insulation panels installed. At that point, ITP inspection covering insulation installation had not been approved. In detail: - ITP Cxxx-__M-A-ITP-D061_WS106-50139 Revision 4.0 received a code 3 on 29/08 - Revision 3.0 had received a code 2 for activities 1.0 to 5.6, and 6.0 to 6.4 to proceed. - Revision 2.0 had received a code 2 for activities 1.0 to 5.6 to proceed. - Insulation installation is activity 5.8
| 02SL - Stations (LUL) | Cxxx-NCR-002165 | NCR | CHS - Stair 42 and 43 PCC Stair Incorrect Mix Design |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-02-09 | 2018-02-22 10:59 | 13 | 2017-09-19 11:21 | Civil - Structural Engineering | 1200 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | The PCC Stairs, Stairs 42 and 43, have been cast using 32/40N Concrete when the specification calls for a 40/50N mix.
| 02SL - Stations (LUL) | Cxxx-NCR-002166 | NCR | LULO_ESS_EVANS panel clash with concrete up stand wall |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-03-20 | 2017-11-08 16:20 | -132 | 2017-09-21 09:41 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The end of concrete up stand wall that is located in northern side of East Stair Shaft, next to eastbound track, shown in the drawing Cxxx-HYD-S-DDD-D061_WS106_Z-79062, has been cast straight instead in an angle. Hence architectural __ cladding panel that shall be installed in that location clashes with the current up stand wall as shown in the attached Sketch.
| 02SL - Stations (LUL) | Cxxx-NCR-002167 | NCR | CHS - Permanent Doors Clashing With Pre Cast Stair Landing |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-04-23 | 2019-05-29 08:20 | 36 | 2018-05-15 08:12 | Architectural - Doors | 1000 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Cambridge Heath Shaft pre cast stairs landing is slightly clash with door DB/001 due to the tolerance of the insitu concrete and the PCC stair units. Currently the door has lose its rubber seal on the bottom and is not rubbing with the landing but once the seal is reinstalled and the 6mm external __ is installed on Stair 42 then this might make the door harder to open from the build up.
| 02SL - Stations (LUL) | Cxxx-NCR-002168 | NCR | Crossrail Platforms - Missing __ DSS EB |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-12-22 | 2017-12-14 12:07 | -8 | 2017-09-21 09:54 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 1 No. 250mm x 50mm builders works hole was not constructed in the EB platform slab. This __ is required for the beam emitter conduit. There is not a redundant __ in the location. The contractor proposes to core drill 2 No. 32mm dia holes for the conduits. Please see attached __ approval. A reinforcement scan will be conducted by the contractor to ensure that the two cores do not clash with any reinforcement steel. After installation of the 25mm DIA conduits the contractor proposes to fill the 32mm DIA cores with __ HF. Please see attached sketch of the __ location. The reinforcement drawing of the platform slab in this location is provided in the reference documents.
| 02SL - Stations (LUL) | Cxxx-NCR-002169 | NCR | LULO - Stair 24 Pile 112 grout cubes compressive strength not reached |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-03-14 | 2017-10-25 06:08 | -140 | 2017-10-05 07:26 | Civil - Geotechnical Engineering | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Stair 24 Foundation Pile 112 (Pile group 20) has not reached the required 28 Day strength of 40N/mm2 Sample CW1593 results: Average 28 days strength: 32.9 N/mm2 56 days strength: 35.4 N/mm2 Please see cubes results and location drawing attached Please confirm disposition: Use-as-is
| 02SL - Stations (LUL) | Cxxx-NCR-002170 | NCR | DSS - Stair 11 Poured out of Tolerance |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-02-19 | 2018-01-05 12:27 | -45 | 2017-09-22 17:33 | Shafts - Shafts General | 927.6 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In Stair 11 there are some risers out of tolerance
| 02SL - Stations (LUL) | Cxxx-NCR-002171 | NCR | DSS - Stair 12 Poured out of Tolerance |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-02-19 | 2017-12-10 11:10 | -71 | 2017-09-22 17:45 | Shafts - Shafts General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Electrical or instrument noise | Completed |  | In Stair 12 Flight 1There are some risers out of tolerance.
| 02SL - Stations (LUL) | Cxxx-NCR-002172 | NCR | Crossrail Platforms - GRC - Standard EB platform incorrectly welded frames |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-12-23 | 2017-12-14 12:13 | -9 | 2017-09-27 13:39 | Architectural - General | 1500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Further to Cxxx-NCR-002160 which details a lower ladder frame in the EB platform with a missing infill strut bracket. There exist two other locations in the EB platform where brackets have been incorrectly welded. Please find attached photos detailing each defect. 1) Basebracket [A-01-S01-A-B01-50519-089] Defect noticed after installation in in Bay 123. The passenger panel infill strut brackets (on both sides of the base bracket) have not been welded to the frame. Due to the lack of weld scorch it is evident that the brackets were never installed. They were not dislodged by __ during installation. 2) Lower Ladder Frame [A-01-S01-Z-L01-50519-090] Defect noticed after installation in Bay 93. An infill strut bracket has been welded on upside down. This means it is not possible to install the infill strut. The bracket will be re-welded on in the correct orientation. The manufacturer will attend site to conduct these works. An onsite weld procedure and ITP will be produced to cover these works. This ITP will include inspections from suitably trained operatives to ensure the quality of the welds. This NCR is to track the process.
| 02SL - Stations (LUL) | Cxxx-NCR-002173 | NCR | Crossrail Platforms - GRC - ES1 ladder frame defective weld |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-12-31 | 2017-12-14 12:26 | -17 | 2017-09-27 13:20 | Architectural - General | 1000 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | A ladder frame in ES1 has been manufactured with a defective weld. Post installation it was noticed that the frame contained a split weld. A photograph of this defect is attached. The manufacturer will attend site and repair the joint. An onsite weld procedure and ITP will be produced to cover these works. This ITP will include inspections from suitably trained operatives to ensure the quality of the remedial works. This NCR is to track the process.
| 02SL - Stations (LUL) | Cxxx-NCR-002174 | NCR | LULO - GSM soffit acoustic insulation incorrect support |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-01-22 | 2017-12-13 15:23 | -40 | 2017-09-25 15:03 | Architectural - Ceilings & Soffits | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A row of INS-301 __ RW5 rigid slab faced acoustic insulation has been observed over Platform 1 as being supported by only a single row of unistrut. This is not installed in accordance with the requirements of ITP Cxxx-__M-A-ITP-D061_WS106-50137 rev 2, item 4.5.
| 02SL - Stations (LUL) | Cxxx-NCR-002175 | NCR | DSS - Level 6 - OHLE Door - Signs of Oxidation |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-12-14 | 2017-12-14 10:04 | 0 | 2017-09-25 15:45 | Architectural - Doors | 1000 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | As noted in CRL Observation CRL-OBS-18689, the stainless steel strike plate on the OHLE Room Door DS/D6/011, DSS, Level 6, is showing signs of oxidation. This is potentially due to a manufacturing defect or as a result of damage after install. Cost of rework per strike plate (including replacement parts and labour) - £500
| 02SL - Stations (LUL) | Cxxx-NCR-002176 | NCR | North Accommodation Block: __ Boards |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-06-15 | 2018-06-22 12:38 | 7 | 2017-09-26 13:14 | Architectural - Roofing & Exterior Treatment | 5500 |  | Damaged | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __ __ board details are missing from the approved MCR list (Cxxx-__M-A-LRC-D061_WS106-50443). Boards installed for the North Accommodation block have been exposed to the elements, and have visible damage.
| 02SL - Stations (LUL) | Cxxx-NCR-002177 | NCR | CHS-Level 4 Switchroom A & B CMS |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-12-21 | 2018-02-01 15:30 | 42 | 2017-09-27 07:36 | Electrical - Cable Management | 500 |  | Planning | Repair | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | swa cables have been installed in the chs level 4 switchroom A & B. due to the installation of the busbar all the cms install was on hold which affected programme requirements.
| 02SL - Stations (LUL) | Cxxx-NCR-002178 | NCR | LU HCDL Canopy Structural Steelwork top coat paint |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-03-31 | 2018-02-15 07:19 | -44 | 2017-09-27 08:35 | Structural Engineering - Finishes | 3000 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The structural steelwork specification requires that all HCDL canopy and platform primary steelwork be painted with a primer, an intermediate and a finish coat, which comprises the __ Specification ‘N4’ classification for protective treatment. The HCDL steelwork currently only has primer and intermediate coats; the top coat (50micron acrylic/urethane paint) has been omitted. There currently is no approved MCR in place for any eligible top coat products. It is noted that the HCDL primary steelwork, including that which is contained within the roof void, has been assigned NSSS classification E-1 (Annex E). However the enveloping of this steelwork by roofing, ceiling and fascia elements suggests it may be reasonably re-classified as I-4 (Annex E), whose criteria do not include a top coat. The Structural steelwork specification Appendix D (Section KM10) assigns all HCDL steelwork as E-1 as NSSS annex E. NSSS Annex E derives its classifications from CIRIA publication 174, which in turn provides definitions for each of 6 exposure categories. Exposure category E-1 requires 3 coats – primer, intermediate and finish. Definition: Urban / Industrial External Exposed Steel Exposure category I-4 requires primer only. Definition: Semi controlled environments: plant rooms, dry warehouses, roof voids (where occasional condensation may occur) In addition, it should be noted that i) The platform (lower) canopies have now been decked out with __ D100 structural roof deck, covering and preventing access to the top surfaces of these beams. ii) Galvanised secondary steel brackets and beams are ready to be installed across the length of the upper canopy; completion of which will allow the roof installation to start.
| 02SL - Stations (LUL) | Cxxx-NCR-002179 | NCR | LULO - GSM - CMS Nuts slipping and failing to tighten. |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-01-27 | 2018-05-24 11:45 | 117 | 2017-09-29 10:37 | Electrical - Cable Management | 500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | CMS Nuts (Size M10) slip and fail to tighten before reaching the recommended tightening torque. These nuts are used to support the CMS on studwork suspended from the Primary Grid within the GSM.
| 02SL - Stations (LUL) | Cxxx-NCR-002180 | NCR | Crossrail Platforms - GRC - Faulty ladder frame cross braces |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-12-16 | 2017-12-12 10:00 | -4 | 2017-09-27 16:33 | Architectural - General | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | There are 5 No. frames in the Eastbound platform tunnels and 2 No. in the escalator shaft that have faulty ladder frame cross braces. Please see attached table which details the unique frame id, type of item and installation location. Each ladder frame contains a thin cross brace member. In the course of transit from factory to the contractors storage facility, and then on to site, some of these members have become damaged. Each frame is damaged in one of two different ways. The cross brace has either become contorted, or the weld has failed. These cross braces bolt onto the ladder frames. In all 7 No. cases referenced here, the manufacturer will supply a replacement cross brace. The contractor will replace these damaged cross braces onsite. This NCR does not constitute a design change, it's purpose is to track the replacement of the faulty cross braces.
| 02SL - Stations (LUL) | Cxxx-NCR-002182 | NCR | DSS - As-Built for WA-18NS - Wall not cast within tolerance to install submarine door. |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-01-08 | 2017-12-18 16:35 | -21 | 2017-10-02 16:49 | Shafts - Shafts General | 2150 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | DSS - As-Built for WA-18NS, Wall was originally not cast within tolerance (see attached As-Built for WA-18NS). Due to it not being in tolerance this has a direct effect on the installation of the submarine door.
| 02SL - Stations (LUL) | Cxxx-NCR-002183 | NCR | GRFC Installation Drawing Control |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2017-10-31 | 2017-10-31 11:02 | 0 | 2017-10-03 09:15 | Architectural - General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Not Defined | Completed |  | A planned Crossrail surveillance was undertaken on 28th September 2017 to look at __`s GRFC Cladding Installation, Offsite Manufacture of GRFC Panels and Substructure Steelwork. Activities in progress were inspected during the site visit and the drawings and documentation were checked for currency and acceptance. Whilst on site during the inspection of the works, a review was undertaken of the site drawings, in relation to the GRFC Cladding works going on, on site. The __ engineer also attended the site visit where drawings were presented from the __ site folder. On checking the following drawings were recorded; Cxxx-__M-A-DWG-D061_WS106-50089 – (Standard Platform Base Bracket) was at C02 revision on site. Cxxx-__M-A-DWG-D061_WS106-50098 – (__ Anchor Bolt Details) was at P04 revision on site. Following subsequent review on eB, it was identified that the ‘current’ and ‘approved’ revision of *50089 was P06 (Dated 04/07/2017). Revision C02 was showing as ’not approved’ and ‘draft’ (dated 26/04/2017). Based on this the drawing on site had not been accepted showing a break down in drawing control. Moreover, it was also identified that the ‘current’ and ‘approved’ revision of *50098 was C01 (dated 09/11/2016). Revision P04 was showing as ‘not approved’ and ‘draft’ (dated 15/03/2017); based on this an outdated drawing was being used on site. Control of Drawings procedure Cxxx-__M-O4-GPS-D061-50002 section 6.7 ‘Control of Drawings on Site’ states “Only the latest accepted drawings are allowed on site. The engineer responsible for an area of work is responsible for ensuring that works are constructed to the correct revision. Regular reviews of site files against the latest RIR will be undertaken to ensure compliance.” In both instances, the process for controlling drawings had failed; including those processes for ensuring new revisions of drawings are disseminated to site engineers and specialist sub contractors.
| 02SL - Stations (LUL) | Cxxx-NCR-002185 | NCR | Sealant on ductwork |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-01-16 | 2018-01-31 14:06 | 15 | 2017-10-05 08:59 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | On ductwork system in DSS there has been areas where excess mastic has been applied to joints or shoes on the ductwork installation in areas such as DSS level 3 Fan room high level above fans
| 02SL - Stations (LUL) | Cxxx-NCR-002186 | NCR | DSS - Missing off-site records for risers |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2017-12-08 | 2017-11-23 10:29 | -15 | 2017-10-09 14:15 | Architectural - General | 1000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | The Quality Surveillance on Cxxx-__M-A-CER-D061-53038 outlined in CRL-OBS-18559 revealed missing off-site data: There was a lack of 90% of the off site records for risers. This includes, but is not limited to, weld testing (__ etc.), galvanization or paint records, fabrication check sheets.
| 02SL - Stations (LUL) | Cxxx-NCR-002188 | NCR | CHS/DSS Discrepancy between F1 and F2 designs for roofing build up in paved areas |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-12-21 | 2018-02-26 14:52 | 67 | 2017-10-09 13:41 | Architectural - Roofing & Exterior Treatment | 1500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | There is currently a discrepancy between the F1 and F2 designs for the roofing build up in the paved areas of CHS and DSS. The build up is currently 122mm where as per the F1 intent it should be 162mm.
| 02SL - Stations (LUL) | Cxxx-NCR-002189 | NCR | R12 PCC Planks- 2No of planks too big |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-04-29 08:42 | -62 | 2017-10-10 11:34 | Architectural - Flooring | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | 2no planks on R12 walkways are too big. 1st plank on South - West walkway PL040 and 1st plank on south - east walkway PL024. Planks are too big approx. 30mm and 50mm. __ is waiting for subcontractor action. Option A - cut planks only if supplier can confirm that cut will have no impact on the structural performance, integrity and design life of the unit Option B - recast
| 02SL - Stations (LUL) | Cxxx-NCR-002190 | NCR | Crossrail Platforms - GRC - Captive sub-frame studs on panels |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-12-15 | 2017-10-30 12:24 | -46 | 2017-10-12 08:49 | Architectural - General | 1500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | During installation of the standard main platform hook on panels there has been 3 No. instances of captive sub-frame studs shearing off. Please see attach 1 - panel installation as per design and attach 2 - an example of sheared studs. This has occurred on the following panels: D-01-S01-S-SFP-1594506 D-01-S01-S-ACP-1581641 D-01-S01-S-SFP-1594017 These panels have not been installed and are quarantined onsite. New lower sub-frames will be delivered to replace faulty ones, this replacement will be done onsite. Sub-frames are held in via cast in anchors which are to be torqued to 14Nm. These repaired panels will then be removed from quarantine and installed. Please see attach 3, an email chain, which includes a response from the Supplier/Manufacturer. __, as per the Suppliers advice, will introduce a hammer test on all panel sub-frame studs. The hammer test will be added to the visual check already conducted on panels onsite prior to install. If any movement is found in the stud the panel will be quarantined. If all four studs pass the hammer test then the panel will be installed. Please see attach 4, a briefing sheet on this new procedure, and on this NCR, to the __ installation team.
| 02SL - Stations (LUL) | Cxxx-NCR-002192 | NCR | ESS Below ground drainage pipe - Backfall |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-06-24 | 2019-05-17 08:16 | -38 | 2017-10-12 09:43 | Civil - Drainage | 8500 |  | Incorrect Installation | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The ESS below ground drainage at the HCDL track level has a back fall for about 1.3m as Identified in the CCTV survey. See attached sketch for location of the back fall. The back fall is along the westbound track between the Rodding eye and the outfall to Platform 6 drainage.
| 02SL - Stations (LUL) | Cxxx-NCR-002194 | NCR | DSS - __ Flex Cote - Render out of tolerance on lvl B walls and parapets |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-08-31 | 2018-08-15 09:54 | -16 | 2018-04-30 15:50 | Architectural - General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Previous Construction - Improper As Built | Completed |  | The specified tolerances for application of __ render on Lvl B service courtyard walls was reduced to +-5mm per 3m as per FCD 002150: ‘Tolerances to be less than +/-5mm with 3m straight edge in any direction as confirmed by __ to suit the installed substrate.’ Despite the relaxation of tolerances achieving these with the substrate walls was not achievable. The rendered walls are up to 20mm out of plumb and up to 30mm out of alignment. This does not affect the durability of the render as the minimal requirements for installation have been met.
| 02SL - Stations (LUL) | Cxxx-NCR-002195 | NCR | LULO MEP Submain Cable W111 Split Outer Sheath |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-08-31 | 2018-11-30 09:32 | 91 | 2017-10-16 14:43 | Electrical - Power Distribution | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | During the Week 29 Cable pulling possession (15 October 2017) submain Cable W111(__ 25mm 4 core FTP-120) had it's outer sheathing split when being zip tied into place over platform 5 and 6. This cable was installed to supply Lift 3 from DSS level 5 LVMSB/B
| 02SL - Stations (LUL) | Cxxx-NCR-002196 | NCR | LULO MEP Submain Cable D22 Outer sheathing Damage |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-07-31 | 2019-10-01 13:00 | 427 | 2017-10-16 15:44 | Electrical - Power Distribution | 15000 |  | Damaged | Rework | 2 (6-60k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | During the Week 29 Cable pulling possession (15 October 2017) submain Cable D22 (Exane 50mm 4 core XPLE SWA) had minor damage to the outer sheathing that was only noticed when the plastic cover used to wrap the cable was removed. The cable has been fully tested including 1000v Insulation resistance between all conductors and between all conductors and the SWA. The results were all >1000. Also all continuity test between phases where completed and correct This cable was installed to supply The LO CER from GSM E58 DNO panel.
| 02SL - Stations (LUL) | Cxxx-NCR-002197 | NCR | LULO HCDL below ground drainage defects |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-09-22 16:40 | 84 | 2018-05-15 08:17 | Civil - Drainage | 5900 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following defects have been identified in HCDL drainage during CCTV survey: Defect 1 (Section 2- page 4 of the report): Fracture, circumferential, from 8 to 4 o'clock and Fracture, longitudinal, at 12 o'clock Defect 2 ( Section 5- page 9 of the report): Fracture, circumferential, from 12 to 6 o'clock Defect 3 (section 29, page 46 of the report): Crack, circumferential, from 9 to 1 o'clock Defect 4 (section 29, page 46 of the report): Crack, longitudinal, at 1 o'clock Defect 5 (section 30, page 48 of the report): Object in invert, from 6 to 10 o'clock,20% cross-sectional area loss Remarks: UNKNOWN OBSTRUCTION (Piece of plastic) Please see attached report (extract from Cxxx-__M-C-RGN-D061-50150 )
| 02SL - Stations (LUL) | Cxxx-NCR-002199 | NCR | R12 roof - Small hole in decking sheet |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-08-09 | 2019-03-13 13:29 | 216 | 2017-10-24 07:25 | Architectural - Roofing & Exterior Treatment | 3000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During gutter weld small hole in metal decking sheet has been made. Welding touch turned on whilst laid down on the decking sheets leaving a small hole in the deck. New piece of metal decking fixed on the exterior, internal face filled, sanded and painted. See photos enclosed.
| 02SL - Stations (LUL) | Cxxx-NCR-002200 | NCR | LULO - ESS Valley Gutter |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-05-31 | 2018-03-28 08:48 | -64 | 2017-10-24 09:42 | Architectural - Roofing & Exterior Treatment | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On The ESS roof the operatives have installed the Valley gutter incorrectly resulting in a damaged roof that does not drain correctly (see attached).
| 02SL - Stations (LUL) | Cxxx-NCR-002201 | NCR | R10N west wing -Top hats re-fixed leave fixings close to prior holes |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-08-08 | 2019-02-02 10:59 | 178 | 2017-10-24 10:06 | Architectural - Roofing & Exterior Treatment | 6500 |  | Damaged | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On __ roof installed on the R10N West wing between GL 14 an 15, 4No. top hats were fixed with the VCL membrane installed above the top hats. This was found to be wrong, as the VCL should go underneath the top hat. Therefore top hats had to be removed and the VCL membrane to be installed underneath. Metal deck was already drilled which causes causes a problem fixing again the screws.
| 02SL - Stations (LUL) | Cxxx-NCR-002202 | NCR | CHS-Level A Damaged tray |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-12-23 | 2017-12-14 23:27 | -9 | 2017-10-24 12:41 | Electrical - Cable Management | 1400 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | LV ’B’ 150mm Cable Tray has been damaged when installing the swa also itp procedure has not been followed as the tray in question has not been signed off.
| 02SL - Stations (LUL) | Cxxx-NCR-002203 | NCR | HCDL LULO Stair 24 blockwork low compressive strength and wrong size of mortar cubes taken |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-01-25 | 2017-11-08 14:29 | -78 | 2017-10-27 06:21 | Architectural - Brickworks/Blockworks | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | For blockwork in riser 2/764 (under stair 24) 70 mm sample cubes (Reference CW1950) were taken instead of 40 mm cubes (As per BS EN 1015-11) and they did not achieve required 28-day compressive strength. (Compressive strength of samples 2.2 N/mm2 @28 days) __ suggest that this is might be potential reason of low compressive strength mortar results. Clause JZ21.4301 h) of architectural specification states: Half of the samples shall be tested at 7 days, the remainder at 28 days. The 28-day crushing strength of the cubes shall not be less than 3.6N/ mm² for the preliminary test and 2.5N/mm² for the work test. As the cubes results are slightly lower than required __ propose to use as work test results of sample CW1954. CW1954 samples were taken in the same week. Same gang of bricklayers were mixing the mortar and mortar used was from the same delivery (same pallet). Please also find few more cubes results from relevant period as well as excel spreadsheet with all mortar cubes results to date
| 02SL - Stations (LUL) | Cxxx-NCR-002204 | NCR | CRL Platforms - CS1 - Void between cast and sprayed fireproofing layer |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-12-06 | 2018-05-29 13:29 | 174 | 2017-10-27 12:21 | Civil - Civil Engineering General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following the striking of the shutter for the CS1 cast fireproofing, a void between the cast and sprayed fireproofing has been discovered, please see attached photos. Approximate size of void 300x80x180mm. __ propose to fill the void with __ S5400 (MCR Cxxx-__M-C-LRC-D061_WS106-50222). It is a High-strength, shrinkage compensated, fibre reinforced, structural repair mortar. See attached sketches.
| 02SL - Stations (LUL) | Cxxx-NCR-002206 | NCR | Crossrail Platforms - GRC - Boroscope hole incorrectly positioned on acoustic panel |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-03-31 | 2017-12-18 16:44 | -103 | 2017-11-01 17:39 | Architectural - General | 1600 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There is 1no. acoustic panel in WB platform tunnel installed at bay 20A has the boroscope hole incorrectly positioned. The actual position of the hole is lower than the design position - please see the attached documents. This results in the panel appearing to be upside down. This is not an installation defect as the panels cannot only be installed one way round, it is believed to be a manufacturing defect.
| 02SL - Stations (LUL) | Cxxx-NCR-002207 | NCR | Crossrail Platforms - GRC - P-CP3 Missing Infill Bracket |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-01-25 | 2018-01-25 15:27 | 0 | 2017-11-02 12:29 | Architectural - General | 2950 |  | Design | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | SOP drawings [Cxxx-__M-A-DWG-D061_WS106-53096] and [Cxxx-__M-A-DWG-D061_WS106-53105] show infill strut bays in the bays adjacent to P-CP3. Drawing [Cxxx-__M-A-DWG-D061_WS106-53115] shows an infill strut L tab, which are required to install the infill strut bay. However, the model [D-80-JCT_WTC P-CP3 Junction -__.nwd] does not show infill strut L Tabs. The P-CP3 upper single legs have been fabricated reflecting the model. Therefore it is not possible to fully install the infill bays as shown on the SOP drawings. __ has raised RFI [Cxxx-GRC-RFI-035] with the supplier, and it has been agreed with __, the designer, that the manufacturer will complete onsite welding of the infill L Tabs. This will enable infill bay installation. The manufacturer will attend site to conduct these works. An onsite weld procedure and ITP will be produced to cover these works. This ITP will include inspections from suitably trained operatives to ensure the quality of the welds. This NCR is to track the process.
| 02SL - Stations (LUL) | Cxxx-NCR-002208 | NCR | PES Plenum Testing Westbound East 125m |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-11-22 | 2017-11-07 09:39 | -15 | 2017-11-02 16:39 | Mechanical - Mechanical Engineering General | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Following the remedial works (design and workmanship) to the east 125m of the Westbound Plenum an informal air test was carried out on 18/07/2017. It showed that the remedial works had improved the leakage rate as at the test pressure of 500pa, a leakage rate of 564l/s was achieved. This is 5.64% of the design volume of 10m³/s. The test was repeated at the working pressure of the PES plenum (200pa) plus a safety margin (100pa) which is a total of 300pa. The test result was 417l/s which is 4.17% of design volume which is within the acceptance criteria. On the basis that all possible has been done to achieve the 5% acceptance at 500pa and the result was very close, __ request that the alternative acceptance criteria is considered as an ALARP. The positive and negative test will be repeated 3 no times at both pressures for 15 minutes with Crossrail attendance before a formal test report is issued. The less onerous test using the leakage rate at the operating pressure will not be considered the norm. This will be incorporated into a revised ITP - Cxxx-__M-M-ITP-D061-50029 - Plenum Air Leakage Testing 3.0
| 02SL - Stations (LUL) | Cxxx-NCR-002209 | NCR | Lift 8 lift panels damaged on site prior to installation |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-09-03 | 2018-09-20 13:51 | 17 | 2017-11-03 11:15 | Mechanical - Lifts | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Whilst in Storage on site and prior to installation, some of the finshed lift panels have been damaged, by trades other than the lift installer, moving the panels arround within the Designnated lift installers barriered off storage area. it is also believed that the damage occured during a niht shift whilst the lift installers engineers were not on site.
| 02SL - Stations (LUL) | Cxxx-NCR-002210 | NCR | LULO HCDL Floor finish level in riser 2/764 (under stair 24) |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-12-01 | 2017-11-10 14:54 | -21 | 2017-11-03 15:41 | Architectural - Flooring | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Top of drawpit DP8 wall should be 110.240=FFL in riser 2/764 During inspection of finished floor in riser 2/764 (under stair 24) it was discovered that the small section of the drawpit wall is not flush with elefant gratings installed (approximately 6 mm lip). See photos attached Non conformance present on very small area and pose no trip hazard to LU staff due to its location
| 02SL - Stations (LUL) | Cxxx-NCR-002211 | NCR | __ not fire compliant for internal use, only compliant for exterior use. |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2017-12-13 | 2017-11-28 08:08 | -15 | 2017-11-03 15:39 | Architectural - Finishes | 1500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | A planned Crossrail surveillance was completed at Whitechapel Station on 18th October 2017 to review Fire Compliance of Cladding Systems and associated materials. During the Surveillance it was noted that __ Breather Membrane had been used as part of the __ LU cladding Installation on the new Station Operations Room in side the New Station. Further investigations found that the system installation was installed inside the Temporary Ticket Hall (TTH) and the Secondary Means of Escape. __ also forms part of the __ Façade System Installation that has been installed on the exterior of the TTH and installation is in progress on the exterior of the GSM Building. On reviewing the Rainscreen Cladding Breather Membrane (__ )’ Cxxx-__M-A-LRC-D061_WS106-50123 (Rev 5) Code 1 and Comment Sheet Cxxx-__M-A-XCS-D061-50092 (Rev 5), it was found that the material has been assessed by CEG Fire Engineers for exterior use only. On discussions with the CEG Fire Team and CEG Materials Engineer it was confirmed that __ is not compliant for internal Station locations and therefor the installation in the internal areas of the Station is not compliant with LU 1-085. MCR ‘__’ Cxxx-__M-A-LRC-D061_WS106-50161 (Rev 2) Code 3 (28/11/2015) existed, This MCR had also been reviewed by CEG Fire Engineers and in the ‘Comment Sheet’ Cxxx-__M-A-XCS-D061_WS106-50259 (Rev 2), a request for clarification; that the material will only be used when covered with a further layer of a fully compliant material (as used on the TTH). It was also stated that; the material is class O but does not meet all of the requirements of LU standard 1-085. Non-Conformance raised to record either (a) justification for its continued use or (b) agreement that the product is to be removed and replaced with a compliant product.
| 02SL - Stations (LUL) | Cxxx-NCR-002212 | NCR | Crossrail Platforms - GRC - ES1 SCL Bracket grout cube results |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-12-19 | 2017-11-16 09:15 | -33 | 2017-11-09 16:38 | Architectural - General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The SCL bracket installed in 'ES1 - Bay 5' did not reach the required 40 N/mm2 strength after 28 day test (32.6 N/mm2) but reached 55.9 N/mm2 after 56 days test. Despite not reaching design strength after 28 days the design strength has been met. Grout cubes results and sketch of location are attached.
| 02SL - Stations (LUL) | Cxxx-NCR-002213 | NCR | LULO - Station Concourse. Corroded CMS |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2021-04-25 20:20 | 299 | 2017-11-07 16:02 | Electrical - Cable Management | 10000 |  | Damaged | Rework | 2 (6-60k) | Complete | External Phenomenon - Weather or ambient condition | Completed |  | Primary CMS installed on the LULO station Lower Concourse has become corroded, due to rainwater ingress and is now non-compliant.
| 02SL - Stations (LUL) | Cxxx-NCR-002214 | NCR | LULO HCDL Movement joint in blockwork- stair 24 riser |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-12-17 | 2017-11-14 10:45 | -33 | 2017-11-07 12:51 | Architectural - Brickworks/Blockworks | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | n PTR-3525 raised by __ __ introduced __-303 in blockwork under stair 24. (Sketches 10240596-XKA-1399, 10240596-XKA-1400, 10240596-XKA-1401, and 10240596-XKA-1418). This information did not reach the construction team prior to constructing the blockwork, and in result walls were built without vertical movement joints and with block head restraints at full extents of the walls. Also sprayed concrete fire protection to adjacent steel columns has been completed. __ propose as follow (This is endorsed by __ under PTR-4330): 1) 2No. of head restraints (One north and one south) which are already fixed to the stairs at the higher end beyond the mid landing to be removed. Head restraints to be removed as marked in attached photos) 2) Vertical movement joints to be constructed. Position to follow the lines of the blockwork joints (as marked on the attached photos). MAC-111 wall ties to the columns are not required. Saw cut existing joints and post install MAC-110 wall ties with debonding sleeve to one side at every course. 3) Vertical movement joint will be carried out to the top DPC level. DPC course to be left intact. Care to be taken during cutting to ensure DPC course in not damaged.
| 02SL - Stations (LUL) | Cxxx-NCR-002217 | NCR | LULO HCDL Stair 24 screed failure |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-02-17 | 2017-12-06 08:43 | -73 | 2017-11-29 09:02 | Architectural - Flooring | 2300 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | Screed and nosings were installed to stair 24. Installation took place from 30/10/17 to 03/11/2017. This was done during warm and dry weather. Over the weekend it was raining and during the nights temperature dropped below 0 degrees. On Monday morning (06/11/2017) It was discovered that: - screed installed to stair 24 cracked -nosings installed to the stairs raised (approx. 3-5 mm) -screed debonded from concrete stairs
| 02SL - Stations (LUL) | Cxxx-NCR-002218 | NCR | Sitewide - Process NCR - QA Inspections being signed off by correct levels of signatories |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-03-16 | 2018-06-07 11:14 | 83 | 2017-11-16 13:07 | Architectural - General | 1000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Following a review of the correct/sufficient levels of signatories on ITP records in 6 QA packages across the project, compliance was found to be only at 50%. The results of the review are attached to this NCR.
| 02SL - Stations (LUL) | Cxxx-NCR-002219 | NCR | GSM Building - __ Works - PSK101 Thickness Measurements |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-01-22 | 2018-01-11 16:07 | -11 | 2017-11-23 16:57 | Fire - Compartmentation | 1000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Scope of works: GSM __ Works Issue: - QCR05 checksheet has not been progressively filled as works have progressed. - No records are available for works carried out prior to June 2017 (this represents most of the GSM __ works)
| 02SL - Stations (LUL) | Cxxx-NCR-002220 | NCR | CRL Platforms - Westbound - Screed cracking around man hole |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-03-17 | 2018-09-10 14:32 | 177 | 2017-11-17 18:45 | Architectural - General | 1500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On the Westbound Crossrail Platform, 2 No cracks in the screed around the manhole have been identified when the ply and Cordek protection was lifted to install the manhole cover. Please see attached marked up drawing and photos. The screed surrounding all other manholes has been inspected and no signs of cracking have been identified at any other location. __ the screed supplier have been onsite to investigate the possible causes, See NCR Root Cause below.
| 02SL - Stations (LUL) | Cxxx-NCR-002221 | NCR | LULO GSM - Installing __ curtain wall beyond approved point in ITP |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-03-21 | 2018-03-19 09:13 | -2 | 2017-11-21 12:01 | Architectural - Roofing & Exterior Treatment | 1250 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Subcontractor for GSM Cladding installed the __ Curtain Wall system to the north elevation beyond the approved level within revision 5.0 of the ITP. Revision 5.0 of ITP Cxxx-__M-A-ITP-D061_WS106-50139 is Code 1 approved up to item 8.4 for installation of brackets and testing of anchors.
| 02SL - Stations (LUL) | Cxxx-NCR-002222 | NCR | Concrete 28-day cube strength not reached for drainage channel for Eastbound single legs bays 74, 86, 119 and Eastbound CP1 & CP2 junctions |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-05-22 | 2018-05-30 07:15 | 8 | 2017-12-13 14:59 | Architectural - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __ poured the drainage channel in short 1m long sections on the Eastbound platform around the single leg ladder frames and 2m long sections below the tusks at CP1 & CP2. The concrete was mixed on-site using Heidelberg C32/40 bag mix to Cxxx-__M-A-ITP-D061_WS106-50148 and achieved a slump of 80mm which is within the target range. Four concrete test cubes were made in accordance with Cxxx-__M-A-ITP-D061_WS106-50148 and sent to the UKAS laboratory for testing. The 28 day strength for the CP1 section was 25.0N/mm^2 and 56 day was 27.5N/mm^2. The 28 day strength for single legs bays 74, 86, 119 & CP2 was 26.1N/mm^2 and 56 day was 28.6N/mm^2. These are below the design strength of 40N/mm^2. Lab sheets showing this are attached. __ have poured over 500m of drainage channel which have reached strength. The drainage channel itself in none structural and none load bearing along its entire length.
| 02SL - Stations (LUL) | Cxxx-NCR-002223 | NCR | PES Plank Defects |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-09-20 | 2018-11-20 12:18 | 61 | 2018-03-27 10:09 | Civil - Civil Engineering General | 40000 |  | Damaged | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the installation of the Plenum lining panels in the Eastbound PES, tapcon screws are used to connect the __ panels to the PES PCC soffit planks. While carrying out these works pilot holes were drilled and in 130 locations the pilot hole has been drilled too deep and caused spalling to the underside of the planks. See attached photos for examples of these defects. These defects sit above the track. The spalling is around 50mm diameter and 10mm deep.
| 02SL - Stations (LUL) | Cxxx-NCR-002224 | NCR | LULO - GSM Level 1 - Change in Firestopping Compound Material in CER5 from FPS-114 to FPS-113 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-02-28 | 2018-01-10 14:33 | -49 | 2017-11-27 12:00 | Fire - Compartmentation | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | After constructing the benchmark using FPS-114 (__ __ Fire Compound), FPS-113 (PFC __ Firestop Compound) was used in the rest of the blockwork openings in CER5. This is due to manufacturer's supplier issues; the subcontractor was only able to obtain FPS-113. The subcontractor took it upon themselves to change the product without consulting __; __ did not notice the change until installation was almost complete.
| 02SL - Stations (LUL) | Cxxx-NCR-002225 | NCR | Accommodation Block Glazing: Proceeding before Code 1 MCR |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-07-06 | 2019-10-16 18:15 | 467 | 2017-11-27 17:31 | Architectural - Glazing | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | The accommodation block glazing has been installed without an accepted MCR. Works had been planned for a later date (January '18) due to procurement, but the subcontractor managed to acquire them early and saw the opportunity to install them, ahead of programme. The MCR (Cxxx-__M-A-LRC-D061_WS106-50529) is currently code 3, where a code 1 MCR is required for the hold point in the ITP (Cxxx-__M-A-ITP-D061-50021 R2)
| 02SL - Stations (LUL) | Cxxx-NCR-002226 | NCR | CHS - Louvres 20-23 and 41 Failed Embedment Depths |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-01-30 | 2018-01-05 12:30 | -25 | 2017-11-28 10:47 | Architectural - General | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | When drilling the fixings for the support steelwork for Louvres CHS-20 - 23 and CHS-41 the required embedment depth of 120mm was not achieved due to clashes with installed reinforcing steel in a number of locations. Designer confirmation of 70mm embedment being acceptable has been received by the subcontractor. Individual as-built depths were not recorded during installation. Fixings were identified to not be of uniform length therefore a post-install survey of embedment depth was not feasible. As a result a full intrusive as-built survey has been undertaken to fully understand the extent of the clashes and to facilitate mitigation measures either through design, relocation of fixings or drilling of reinforcement. The extent of the clashes is as shown below. Total Fixings = 404 Less than 70mm embedment = 39 Between 70mm and 120mm embedment = 307 Greater than or equal to 120mm (original design) = 58
| 02SL - Stations (LUL) | Cxxx-NCR-002227 | NCR | DSS - PCC Cladding - Oversized corbel on panel P65D - South elevation |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2017-12-28 | 2017-12-18 15:29 | -10 | 2017-11-28 13:42 | Architectural - General | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The line of the corbel was detailed to follow the line of the edge of the panel, but it was cast incorrectly causing a clash with panel P15, on the west elevation. NCR 1004 by __ has been raised & the proposed remedial action was to cut the corbel on site to the correct profile.
| 02SL - Stations (LUL) | Cxxx-NCR-002228 | NCR | LULO - Level 3 Plant Room Screeding |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-06-01 | 2018-06-26 12:36 | 25 | 2018-01-05 07:33 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Two screed types have been applied within the Level 3 plant room. Drawing Cxxx-__M-A-DDA-D061_WS106_3-12506 details screed type SCR-206 throughout the Level 3 Plant Room. Throughout the majority of the plant room, SCR-206 Option A has been installed. Within the architectural specification, this option utilises SCR-205 Option A or Option B. All rooms and corridors used SCR-205 Option B (heavy duty __ screed) in accordance with the design drawing and specification, other than room ERSI 3/667 which used SCR-207 Option A (__ A38 with K80 wearing surface). SCR-207 Option A is a an improved floor finish to the similar SCR-205 Option A as a wearing course has been applied to the screed. The checksheets submitted within Cxxx-__M-A-CER-D061_WS106-50073 reflect the use of screed type SCR-207.
| 02SL - Stations (LUL) | Cxxx-NCR-002229 | NCR | LULO GSM - Damaged Blockwork Plant Room 1-769 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-03-02 | 2018-01-18 14:16 | -43 | 2017-11-29 17:01 | Architectural - Brickworks/Blockworks | 1500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | The top course of blockwork to the Plant Room (1-769), in level 1 of the GSM, has been damaged by operatives using the louvre openings as an access to the south canopy scaffold.
| 02SL - Stations (LUL) | Cxxx-NCR-002230 | NCR | LO brickwork wall above lower concourse - Western Run Off Beam concrete core strength |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-03-30 | 2018-02-02 13:11 | -56 | 2017-11-30 13:07 | Architectural - Brickworks/Blockworks | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Concrete cores were installed where the western run off beam was removed and the parapet wall (W616 wall above platform 5) was reinstated - as per drawing Cxxx-HYD-S-DDH-D061_WS106_Z-10021 (see attached). 40N concrete mix bag was used to pour the 3 no. concrete cores, but an average 56 day cube strength of 28.9N was achieved (see attached concrete & grout cube testing form - CW 1988). Is the strength that was achieved acceptable? Also, what is the concrete mix and minimum strength required for said concrete cores (see other drawings as per Cxxx-RFI-004472 that require concrete cores to be installed when reinstating brickwork) since it is not stated on the drawings?
| 02SL - Stations (LUL) | Cxxx-NCR-002231 | NCR | LULO - Station Concourse. CER5 ATS Steel Plinth |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-03-30 | 2018-03-07 08:48 | -23 | 2017-11-30 17:52 | Electrical - Power Distribution | 1000 |  | Design | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | The wall-mounted ATS in CER5 in the GSM is specified as being mounted on a steel plinth as an integral part of the ATS assembly. Owing to a potential non-conformance with a mechanical services pipe (yet to be fitted) (required to be 75mm clearance from any CMS), the plinth was removed to allow the pipe to be fitted. The wall-mounting of the ATS was considered sufficient. Crossrail were invited out to inspect the whole ATS installation. This non-conformance was raised as a result of the inspection. However the plinth is a mandatory part of the design and has now been installed as per design.
| 02SL - Stations (LUL) | Cxxx-NCR-002232 | NCR | CHS - Dislodged blockwork on level 7 CIR-S Section E-E |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-01-17 | 2018-01-19 15:44 | 2 | 2017-12-01 12:53 | Architectural - Brickworks/Blockworks | 600 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On level 7 in the CIRS area, some blocks have become dislodged and cracked the bed joint. The top courses of block are damaged and needs relaying. This needs to be repaired and re pointed back to its original state.
| 02SL - Stations (LUL) | Cxxx-NCR-002233 | NCR | GSM Building - __ Mullions |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-09-30 | 2018-12-14 14:53 | 75 | 2017-12-11 12:30 | Architectural - Roofing & Exterior Treatment | 1250 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Subject __ mullions have been observed to have some coating removed. See CRL-OBS-19688 which reads: "The Curtain walling system mullions are damaged at the base with paint work abraded away". This NCR is raised to confirm the cause and determine whether any remedial action is required. Details 1. Mullions have been delivered from the __ workshop in their current condition. 2. These mullions have been purposely modified in the __ workshop 3. The lower part of the mullions noses have been cut in the workshop 4. The reason is that no Aluminium or glass panels will be installed in these locations. Also, these sections of mullions are located under the future stair 52. 5. As such the noses of the mullions are a)not required and b)in the way of the new stairs 6. Cutting the noses of the mullions involves exposing metal. I.e. the exposed aluminium is inherent to the design. 7. Exposed aluminium has not been recoated by the manufacturer on the basis that only visible aluminium parts need to be coated. 8. It can be argued that there is more exposed aluminium than strictly required. But again, the exposed aluminium is not visible and so the performance of the product is not impaired. Conclusion These mullions have been modified in the workshop as per design which results in minor areas of non-visible exposed metal. Manufacturer has provided a statement to confirm that the performance of the system is not impaired. There are no architectural or structural concerns. No further action.
| 02SL - Stations (LUL) | Cxxx-NCR-002234 | NCR | West stair shaft - Void in RC liner walls |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-03-31 | 2018-04-23 09:18 | 23 | 2017-12-07 12:00 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the construction of the West stair shaft an air pocket has caused a void to form between the upper and lower liner wall as per picture attached. The void is approximately 300mm long, 220mm at its deepest point and tapers from 10mm to 100mm.
| 02SL - Stations (LUL) | Cxxx-NCR-002235 | NCR | CHS- Drainage Works - Non conforming landing area |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-03-18 | 2018-03-16 11:42 | -2 | 2017-12-08 17:19 | Civil - Drainage | 3500 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | NCR relating to the landing areas of the benching on affected Manholes at CHS not being compliant with regulations in regards to the distance needed on the benching needed for a secure foot access.
| 02SL - Stations (LUL) | Cxxx-NCR-002236 | NCR | LULO - Cracked pipe within ETH drainage |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2021-03-28 21:32 | 271 | 2018-02-28 18:08 | Civil - Drainage | 15000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Similarly to Cxxx-NCR-002197 and Cxxx-NCR-002298, a crack has been discovered within the ETH drainage following a CCTV survey of the works. 5.93m from CMH01 to BR2, there is a circumferential crack from 6 to 11 o'clock. See page 38 and 39 of the attached report.
| 02SL - Stations (LUL) | Cxxx-NCR-002237 | NCR | LULO - ESS __ damage & incomplete works |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-06-30 | 2019-02-02 11:26 | 217 | 2017-12-12 17:10 | Civil - Civil Engineering General | 12000 |  | Incomplete Works | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There are some outstanding __ works that are covered in document Cxxx-__M-O4-LRC-D061_WS106-50189. Part of these outstanding works shows a partially completed beam above Stair 23. Following an inspection with __ it has been confirmed that the __ on this beam needs to be removed and re-applied. In addition to this there are a number of __ repairs that are required where temporary works were installed, see attached. Finally there was no Certificate of Conformity issued by __ to Ardent when the works were complete in 2015. Since this date Ardent has ceased trading. Assurance is required that the __ is installed correctly
| 02SL - Stations (LUL) | Cxxx-NCR-002238 | NCR | LULO Secondary Steelwork - ETH - Concourse Roof Geometry Installation |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-02-28 | 2018-01-23 10:04 | -36 | 2017-12-13 18:02 | Civil - Structural Engineering | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the installation of the Secondary Steelwork - Concourse Roof Geometry, 2no bracings were modified to fit them in. 1. In member 1003, the holes in the end connection tab plates were slotted by 5mm outwards towards the end of the tab plates. 2. In member 1011, the holes in the end connection tab plates were slotted by 15mm inwards towards the brace member. The tab plates were also trimmed back by 5mm. 3. The existing grade 8.8 bolts were replaced with M24 Tension Control Bolts. All these changes have been captured and detailed in the attached email "RE Concourse Roof Geometry - NCR required.msg ".
| 02SL - Stations (LUL) | Cxxx-NCR-002239 | NCR | PES Shotcrete Result |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-03-16 | 2018-03-21 13:53 | 5 | 2017-12-18 09:06 | Civil - Civil Engineering General | 1500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The non-shrink grout used in the top and side brackets of the PES between the bracket and the SCL is Shotcrete 513 (MCR Reference: Cxxx-__M-A-LRC-D061_WS106-50373 - Grout for tunnel brackets) See attached core results for test panel sprayed on 13/03/2017, 15/03/2017, 12/04/2017, 13/04/2017, 21/04/2017, 25/04/2017. The results obtained at 28 days did not achieve the minimum strength required (40Nmm2). The results obtained are only a nominal amount below the required 40N/mm2 so the Contractor proposes to use as is. This NCR was not raised at time of works and is being retrospectively raised. For reference on site record extract from certification package attached
| 02SL - Stations (LUL) | Cxxx-NCR-002240 | NCR | Crossrail Platforms - GRC - Damage to CP1/WB PT4 PNZ panel |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-07-06 | 2018-04-19 15:16 | -78 | 2017-12-18 11:06 | Architectural - General | 1500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | During installation of the PT4 tusk arch passenger panel at CP1/WB, a small piece of panel was damaged. The chip is approx. 60mm x 200mm. Please see the attached photos.
| 02SL - Stations (LUL) | Cxxx-NCR-002243 | NCR | CHS - Louvres CHS-22 and CHS-23 Incorrect Fabrication |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-06-08 | 2018-07-27 13:02 | 49 | 2017-12-15 16:43 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient surveillance of subcontractors | Completed |  | Louvres CHS-22 and CHS-23 have been installed as __ WG-AL with a 50mm flange on all 4 sides. This is not as per the approved F2 design which denotes a 20mm flange on the internal joint.
| 02SL - Stations (LUL) | Cxxx-NCR-002244 | NCR | 5 star grout installation as per Cxxx-RFI-004586 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-10-22 | 2018-07-12 15:54 | -102 | 2018-05-15 08:20 | Architectural - Flooring | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | No evidence/assurance of 5 star grout installation as per Cxxx-RFI-004586
| 02SL - Stations (LUL) | Cxxx-NCR-002245 | NCR | LULO - No MCR for Access Steps into CMH04 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-05-29 | 2018-04-03 09:51 | -56 | 2018-02-28 17:29 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | The stepped access to the CMH04 manhole chamber was changed from the steps specified in the Architectural Spec (details in Cxxx-FCD-002077 attached). The FCD detailed information on fire compliance for the product and also provided the technical data sheet for the product. The Engineer incorrectly assumed that the approved FCD meant that the steps were an accepted product and so did not submit a MCR. Therefore, works were undertaken without an approved MCR in place.
| 02SL - Stations (LUL) | Cxxx-NCR-002246 | NCR | CP - Westbound platform cracking |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-05-30 | 2018-07-12 14:47 | 43 | 2017-12-20 14:00 | Civil - Civil Engineering General | 14410.27 |  | Material | Repair | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Cracks have been discovered at regular intervals along the length of the westbound platform (please see attached marked up drawings). The cracks appear to be fully through the slab including the platform nosing. These were not previously picked up during the sign off and handover process.
| 02SL - Stations (LUL) | Cxxx-NCR-002247 | NCR | LULO - North Accommodation Block - Glazed Windows Installed Incorrectly |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-07-02 | 2018-07-23 08:21 | 21 | 2017-12-20 14:28 | Architectural - Glazing | 4000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | __, a subcontractor of __, has not installed the glazing in accordance with design; the fire-resistant layer being visibily on the external face and the ballistic face on the internal.
| 02SL - Stations (LUL) | Cxxx-NCR-002248 | NCR | CHS - __ louvres fabricated not in accordance with the approved F2 Design |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-05-31 | 2018-06-26 13:51 | 26 | 2018-02-20 17:54 | Architectural - General | 120000 |  | Manufacturing Defect | Reject | 1 (>60k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | The __ louvres for installation to the CHS draught reliefs have arrived on site but are all the incorrect dimensions. The dimensions delivered on site bear no correlation to the F2 or F1 design. The order was rejected.
| 02SL - Stations (LUL) | Cxxx-NCR-002249 | NCR | LULO Accommodation Block Wind Post Installation to Unapproved Drawings |  | Contr | VIN | WHI - Whitechapel Station (Central) |  | 2018-12-01 | 2018-12-11 11:58 | 10 | 2018-05-15 08:20 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | The below drawings have been used to install the wind posts in the accommodation blocks. The drawings have been reviewed by __ but only 4No have been updated to address comments. The wind posts have therefore been installed with the majority of the drawings formally at code C status. Cxxx-__M-A-DWG-D061_WS106-54518 C03 (C01 Code C) Cxxx-__M-A-DWG-D061_WS106-54519 P03 (P02 Code C) Cxxx-__M-A-DWG-D061_WS106-54521 P02 (Current revision Code C) Cxxx-__M-A-DWG-D061_WS106-54522 P02 (P01 Code C) Cxxx-__M-A-DWG-D061_WS106-54572 P02 (P01 Code C) Please note that the comments provided by __ relate to minor setting out discrepancies and do not relate to structural elements or coordination.
| 02SL - Stations (LUL) | Cxxx-NCR-002250 | NCR | DSS - Riser A out of tolerance gaps between riser floor panels |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-03-10 | 2018-03-28 14:31 | 18 | 2018-01-02 14:02 | Architectural - General | 3737.5 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | This NCR captures the following issues throughout all levels of Risers at DSS: - Gaps between finished concrete and PCP floor panels >10mm - Gaps between PCP panel and PCP Panel >5mm - Gaps between PCP panel and kickflat >10mm - Level difference between PCP panel and RC slab >3mm
| 02SL - Stations (LUL) | Cxxx-NCR-002251 | NCR | DSS - Riser B1 & B4 out of tolerance gaps between riser floor panels |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-03-10 | 2018-03-28 14:32 | 18 | 2018-01-02 14:18 | Architectural - General | 1887.5 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | This NCR captures the following issues throughout all levels of Risers at DSS: - Gaps between finished concrete and PCP floor panels >10mm - Gaps between PCP panel and PCP Panel >5mm - Gaps between PCP panel and kickflat >10mm - Level difference between PCP panel and RC slab >3mm
| 02SL - Stations (LUL) | Cxxx-NCR-002252 | NCR | DSS - Riser B2 out of tolerance gaps between riser floor panels |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-03-10 | 2018-03-28 14:34 | 18 | 2018-01-02 14:25 | Architectural - General | 1332.5 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | This NCR captures the following issues throughout all levels of Risers at DSS: - Gaps between finished concrete and PCP floor panels >10mm - Gaps between PCP panel and PCP Panel >5mm - Gaps between PCP panel and kickflat >10mm - Level difference between PCP panel and RC slab >3mm
| 02SL - Stations (LUL) | Cxxx-NCR-002253 | NCR | DSS - Riser B3 out of tolerance gaps between riser floor panels |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-03-10 | 2018-03-28 14:36 | 18 | 2018-01-02 14:30 | Architectural - General | 1610 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | This NCR captures the following issues throughout all levels of Risers at DSS: - Gaps between finished concrete and PCP floor panels >10mm - Gaps between PCP panel and PCP Panel >5mm - Gaps between PCP panel and kickflat >10mm - Level difference between PCP panel and RC slab >3mm
| 02SL - Stations (LUL) | Cxxx-NCR-002254 | NCR | CP - Back of house room structural openings |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-04-01 | 2018-03-19 09:38 | -13 | 2017-12-22 12:14 | Architectural - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The back of house rooms on the crossrail platforms have been constructed, the structural openings have been surveyed and found to be out of tollerance. Some openings are greater and some are smaller.
| 02SL - Stations (LUL) | Cxxx-NCR-002255 | NCR | Crossrail Platforms - GRC - CP1-WB PT4 big head damage |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-07-21 | 2018-04-10 08:04 | -102 | 2018-01-02 12:16 | Architectural - General | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During installation of a tusk arch panel at CP1-WB a cast in fixing was damaged. Please see attachment with photos of the damaged arch, location and dimensions.
| 02SL - Stations (LUL) | Cxxx-NCR-002256 | NCR | CRL Platforms – Under platform services area – SSL on Eastbound |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-05-31 | 2018-02-20 10:59 | -100 | 2018-01-03 13:19 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In the services area, under the eastbound platform, the benching that meets at gridline Y has been cast with a 20 to 30mm height difference. Furthermore, metal work grating is located in this section and interfaces with this height transition. We propose to use __ , an approved product, to level out the difference in height as per attached pdf “EB under platform combined”. This has been sent to __ as per attached "Cxxx-PTR-4874"
| 02SL - Stations (LUL) | Cxxx-NCR-002257 | NCR | Cxxx Whitechapel Projectwide - Non fulfilment of Works Information - UKAS Test House Pull Testing Verification - PES Installation |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2021-03-01 17:15 | 244 | 2018-01-02 14:19 | Architectural - General | 2000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | The Eastbound PES works included the requirement for pull testing. This was undertaken by __ and witnessed by __ but there has been no independent verification by a UKAS accredited test house. All testing was carried out by suitably competent individuals (see Cxxx-__M-A-LRC-D061-50179 Section 4) . Records of pull testing are found in Construction Records Cxxx-__M-A-LRC-D061-50179 Section 2. Update 26/10/2020: it’s been agreed with CRL to apply this NCR across the project (C&A and MEP disciplines).
| 02SL - Stations (LUL) | Cxxx-NCR-002258 | NCR | R12 SME walkway Pre & Post Pour Records and Concrete Cube Results Missing |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-10-30 14:16 | 122 | 2018-04-19 15:06 | Civil - Concrete Pavement | 3000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Cube results are not avaliable at the point of certification, for all the planks
| 02SL - Stations (LUL) | Cxxx-NCR-002259 | NCR | LULO - Level 3 Plant Room - Concrete Cube Result Failure at 56 Day Test |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-03-09 | 2018-01-17 15:05 | -51 | 2018-01-08 13:36 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | The concrete plinth for LV SR II (Room 3/666) was extended in length by approximately 250mm. The concrete used for this was 40N strength bag mix concrete. Test cubes were made for this pour and submitted to the laboratory. On the 56 day test, the cube reached a strength 37.7N/mm2 (required design strength is 40N/mm2). A remaining cube was tested at a later date (125 days after the pour) and reached a strength of 45.9N/mm2. Please see attached laboratory report.
| 02SL - Stations (LUL) | Cxxx-NCR-002260 | NCR | DSS - Level 1 - A Reinforce Concrete items pour out of tolerance |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-04-19 | 2018-03-20 09:40 | -30 | 2018-01-09 12:38 | Shafts - Shafts General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | RC Items in Level 1-A Slab walls and columns have been poured out of Tolerance.
| 02SL - Stations (LUL) | Cxxx-NCR-002261 | NCR | LULO - Lift Control Room 7 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-07-31 | 2019-02-12 08:54 | 196 | 2018-01-16 15:48 | Electrical - General | 4000 |  | Design | Use As-Is | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | 150 wide Cable Tray had been installed in accordance with drawing revision C02. This tray was then required to be relocated by 300mm to allow for additional equipment to be fitted. This resulted in redundant fixings in blockwork, which will require making good No FCD was raised for this. The drawings have since been revised to P06 ( covered "By Exception") to show the new cable tray position
| 02SL - Stations (LUL) | Cxxx-NCR-002262 | NCR | CP - Dry Shrinkage result for CS1 fireproofing concrete. |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-04-30 | 2018-01-30 13:15 | -90 | 2018-01-16 17:29 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Cxxx Specification Cxxx-OVE-Z4-RSP-CR001-00002 (Table KF10-01) requires a cast insitu concrete mix to have a dry shrinkage value of 0.03%. Our line 40 concrete was tested by __ and found to have a dry shrinkage value of 0.035%. The concrete is out of spec by 0.005%.
| 02SL - Stations (LUL) | Cxxx-NCR-002263 | NCR | PCC Cladding - South Elevation Missing 40mm penetrations in the design of panels P65E and P69 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-06-09 | 2018-05-31 07:30 | -9 | 2018-02-09 18:16 | Architectural - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Two 40mm penetrations for cables have been missed in the design of panels P65E and P69 on South elevation. The are requiree as per drawing Cxxx-__M-A-DDC-D061_WS105_Z-10476. The panels were cast and installed without the penetrations like shown in drawing Cxxx-__M-A-DWG-D061_WS105-50035.
| 02SL - Stations (LUL) | Cxxx-NCR-002264 | NCR | DSS CHS __ Door - Special Acoustic Door Offsite Fabrication - Outstanding documentation |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-02-26 | 2018-02-23 07:25 | -3 | 2018-01-17 11:49 | Architectural - Doors | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Difficulty to obtain offsite fabrication records for the special acoustic doors from __ Doors. This is for the 2 doors at Durward Street Shaft and Cambridge Heath Shaft, as per ITP Cxxx-__M-A-ITP-D061-50033
| 02SL - Stations (LUL) | Cxxx-NCR-002265 | NCR | CP - Eastbound Platform Cracking |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-08-31 | 2018-09-13 14:20 | 13 | 2018-01-18 11:16 | Civil - Civil Engineering General | 5000 |  | Material | Repair | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Cracks have been discovered at regular intervals along the length of the eastbound platform (please see attached marked up drawings). The cracks appear to be fully through the slab including the platform nosing. These were not previously picked up during the sign off and handover process.
| 02SL - Stations (LUL) | Cxxx-NCR-002266 | NCR | LULO - SOR Mess Room. Works commenced without approved FCD |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-07-31 | 2018-09-10 13:11 | 41 | 2018-01-18 13:05 | Electrical - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | LULO Concourse SOR Mess Room. The designers, has made revisions made to the power socket layout, after a meeting with LU. These revised socket locations had been shown by __ on a preliminary, un-issued drawing, and the changes have been made on site, without an FCD in place.
| 02SL - Stations (LUL) | Cxxx-NCR-002267 | NCR | PES Universal Blanking Plate Paint Repairs |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-03-02 | 2018-03-27 10:35 | 25 | 2018-01-18 14:42 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Following the installation of the eastbound Universal Blanking Plates a paint defect was noted. The defect occurred due to the way in which they were stored after production and during transportation. The damage noted after installing the plates is that the paint has discoloured and flaked away.
| 02SL - Stations (LUL) | Cxxx-NCR-002268 | NCR | DSS - Level A Wall WA-01S Structural Opening |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-02-28 | 2018-02-20 15:00 | -8 | 2018-01-19 12:40 | Shafts - Shafts General | 2000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Wall WA-01S is requires a structural opening of 1000mm x 2100mm. This has not been installed as the wall was installed to drawings 'Cxxx-__M-C-DWG-D061_WS105-51388' and 'Cxxx-__M-C-DWG-D061_WS105-50848' where this wall is not included
| 02SL - Stations (LUL) | Cxxx-NCR-002269 | NCR | West Stair Shaft - AS built survey to Lift shaft 3 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-03-06 | 2018-03-01 09:59 | -5 | 2018-01-25 14:18 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | An As built has been completed for Lift shaft 3 within stair 25. The reults are shown in attached as built files. The tolerance given in relevant ITP - Cxxx-__M-C-ITP-D061_WS105-50043 - Liner walls, Base Slab and Insitu Concrete Works is +/- 5mm. In the worst location the tolerance has been exceeded by 11mm.
| 02SL - Stations (LUL) | Cxxx-NCR-002270 | NCR | No Benchmark for Brickwork Type EWS-605 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-03-26 | 2018-09-17 20:01 | 175 | 2018-01-25 12:34 | Civil - Civil Engineering General | 1000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | No Benchmark for Brickwork Type EWS-605
| 02SL - Stations (LUL) | Cxxx-NCR-002271 | NCR | CRL Platforms - Bench bracket arms |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-03-26 | 2018-04-18 08:54 | 23 | 2018-01-25 16:15 | Architectural - Finishes | 1500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | There are 9 no. incorrect bench brackets which have been installed in the Westbound Platform. GRC pedestrian zone panels have been installed in front. Due to programme requirements these bench brackets will be remediated insitu. This negates the need to remove GRC panels and skirting. Agreed method in SNC Cxxx-__M-A-CCN-D061_WS106-50030.
| 02SL - Stations (LUL) | Cxxx-NCR-002272 | NCR | LULO - West Lift Lobby - Cover up of works without formal close out of DOWL list |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-04-23 | 2018-05-10 07:55 | 17 | 2018-03-16 10:34 | Civil - Civil Engineering General | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | Cladding works began on lift 5 without the formal closure of all snags on the DOWL list. Photographs have since been provided, and all snags are now closed out. Proper process was, however, not followed.
| 02SL - Stations (LUL) | Cxxx-NCR-002273 | NCR | IRF from subcontractor RDS to __ /CRL |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-03-22 | 2018-03-21 13:27 | -1 | 2018-01-31 14:05 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | RDS offered IRF as completed works, on inspection a rivet hole was found in the fire rated ductwork where a shoe had been relocated due to original installation not level. Section of duct should have been replaced. RDS will now replace
| 02SL - Stations (LUL) | Cxxx-NCR-002274 | NCR | Failed Inspection CHS Level A |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-03-26 | 2018-03-26 07:58 | 0 | 2018-01-31 14:13 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Inspection prevented from being carried out due to blanking plates covering openings to ductwork which were there for test purposes. Therefore the internal inspection of the duct couldn't be carried out.
| 02SL - Stations (LUL) | Cxxx-NCR-002275 | NCR | Failed Test CHS Level A |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-05-16 | 2018-04-25 09:37 | -21 | 2018-01-31 14:30 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | As a result of incorrect carrying out of testing procedure, a test failed resulting in wasted time. As a result of this retest and IRF will have to be completed.
| 02SL - Stations (LUL) | Cxxx-NCR-002276 | NCR | GSM - E57 DNO / Intake Power Supply Energised without accepted IRN |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2018-03-13 | 2018-05-15 09:32 | 63 | 2018-02-01 16:08 | Electrical - Power Distribution | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | __ have energized the DNO / E57 intake head via EDF Energy without an accepted IRN. As a result, __ will require isolation of said supply to adhere to the ITP intervention points for the inspection of the associated Cable Chamber, Fuse Switch, Earth Bar etc. No permanent works assets should be energised without an accepted IRN.
| 02SL - Stations (LUL) | Cxxx-NCR-002277 | NCR | LULO GSM - Coding error on __ curtain wall MCR, leading to works proceeding without approval |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-09-28 | 2019-09-25 09:59 | 362 | 2018-02-02 14:32 | Architectural - Walls | 4000 |  | Documentation and Records | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | The __ curtain wall system to GSM level 1 was procured and commenced 06/11/17 on the basis the MCR had been granted Code 1 approval 14/03/17. An internal audit by CRL later revealed that the MCR had 3no. residual review comments made against it, one of them being an 'A' comment. Therefore the auditor recommended the MCR be recoded to Code 3. CRL notified __ of the coding error via email on 06/11/17. The __ curtain wall MCR is Cxxx-__M-A-LRC-D061_WS106-50281.
| 02SL - Stations (LUL) | Cxxx-NCR-002278 | NCR | LULO - Intumescent Paint Delamination |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-05-31 | 2018-11-26 16:17 | 179 | 2018-03-12 17:47 | Fire - Compartmentation | 26005 |  | Damaged | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Due to water ingress, the intumescent paint has begun delaminating from the steelwork.
| 02SL - Stations (LUL) | Cxxx-NCR-002279 | NCR | CHS - Level 1 - Section J-J |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-03-14 | 2018-03-19 09:23 | 5 | 2018-02-02 17:18 | Architectural - Brickworks/Blockworks | 700 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Lintel between two windposts installed to the incorrect height and not making allowance for screed in that area running through the doorway. Also missing builders work hole (BW1/013) for pressure relief damper.
| 02SL - Stations (LUL) | Cxxx-NCR-002280 | NCR | GSM Building - __ anchors |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-05-15 | 2018-08-21 06:24 | 98 | 2018-02-02 17:32 | Civil - Structural Engineering | 3000 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Activity: Installation of threaded resin anchors, as part of the GSM North elevation __ curtain wall 1. The Contractor confirms that no pull-tests have yet been carried out by a UKAS accredited body, on these anchors. 5% of tests are required to be carried out by a UKAS accredited body, as per Cxxx-PMC-15846; this has not happened in this instance, which constitutes an NCR. However the Contractor confirms that pull-tests have been carried out by a non-UKAS accredited competent person. 10% of the anchors have been tested, and no failures have been recorded. 2. Additionally, it has been observed that threaded resin anchors, part of the GSM North elevation __ curtain wall "have been cut (...), with varying lengths of bar protruding".
| 02SL - Stations (LUL) | Cxxx-NCR-002281 | NCR | CP - Trimming of EPW1 end wall to suit escalator install |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-04-20 | 2018-02-15 12:27 | -64 | 2018-02-03 08:28 | Civil - Civil Engineering General | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The tolerance required for the installation of the escalators was not taken into account when constructing the EPW1 RC end wall and platform slab. Thus the wall and slab need to be trimmed by 0mm in the north to 16mm in the south (see attached sketch). The wall / slab need to be trimmed from top of slab to 1.4m below FFL (85.700m). This is required to allow the installation of the escalator trusses.
| 02SL - Stations (LUL) | Cxxx-NCR-002282 | NCR | DSS - Level 3 Slab Interface with Escalator |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-03-17 | 2018-02-22 08:43 | -23 | 2018-02-05 13:27 | Shafts - Shafts General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Level 3 Slab has been poured out of tolerance and encroaches into the escalator
| 02SL - Stations (LUL) | Cxxx-NCR-002283 | NCR | LULO - Incorrect Position of M__-202 Control Joint at Gridline 1.1 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2021-03-08 02:55 | 251 | 2018-04-16 06:46 | Architectural - Flooring | 2500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | The movement joint located at Gridline 1.1 of the LO Concourse has been installed in the incorrect location. Rather than being offset 1.49m from Gridline 1.1, it has been installed to the Gridline with no offset.
| 02SL - Stations (LUL) | Cxxx-NCR-002284 | NCR | LULO - ESS concrete upstand bag mix no cubes taken |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-05-07 | 2018-02-12 13:34 | -84 | 2018-02-06 09:42 | Civil - Civil Engineering General | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | Following Cxxx-RFI-003158 this NCR has been raised as no concrete cubes were taken to pour the up stand around Stair 23. bag mix was used.
| 02SL - Stations (LUL) | Cxxx-NCR-002285 | NCR | LULO Lift 7 __ Board Installation- works commencing without an approved ITP |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2018-06-01 | 2018-07-06 14:21 | 35 | 2018-02-07 08:29 | Architectural - Walls | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | Works commenced without an approved ITP, as identified during __ surveillance dated 02.02.17
| 02SL - Stations (LUL) | Cxxx-NCR-002286 | NCR | LULO - Lack of Evidence of ITP Temperature Parameters |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-05-11 | 2018-07-10 13:18 | 60 | 2018-02-07 16:34 | Fire - Compartmentation | 1200 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On Thursday 01/02/2018 Nightshift during engineering hours, __ applied top coat to intumescent paint on the south side truss by east bound HCDL track. when asked for evidence of the substrate and air temperatures, the supervisor on site had no evidence to prove that the temperature was winthin the ITP parameters. These works were a continuation of a weeks worth of engineering hours activities, but on Thursday there was a substantial air temperature drop, under 5degrees. Works were carried on in this shift, with the best intentions, to profit from the presence of the HV assessor and scaffold platform built on the tracks. The amount of works carried out were significantly less than previous nights. Temperature controls had been made during the shift but in a different area of the site, these checks complied with the ITP. Evidence is attached.
| 02SL - Stations (LUL) | Cxxx-NCR-002287 | NCR | Stair 25 - Upstand steelwork missed from Base slab pour |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-03-24 | 2018-03-14 15:46 | -10 | 2018-02-12 12:19 | Civil - Civil Engineering General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the construction of the Southern Base slab through retaining wall W616 (DWG - Cxxx-__M-C-DWG-D061_WS105-50744) the Reinforcement for the upstands was not cast into the slab.
| 02SL - Stations (LUL) | Cxxx-NCR-002288 | NCR | Unapproved Benchmark - Windows Installation GSM |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-07-01 | 2019-06-25 14:32 | 359 | 2018-04-25 08:18 | Architectural - Glazing | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Approved Code 1 or Code 2 Benchmark in place for the installation of the GSM Aluminium Windows. Windows have been installed without approved Benchmark in place. Benchmark eb number Cxxx-__M-A-LRC-D061_WS106-50872 is currently a placeholder.
| 02SL - Stations (LUL) | Cxxx-NCR-002289 | NCR | GSM Windows - Unapproved MCR's 2 No |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-06-16 15:17 | -14 | 2018-04-25 08:19 | Architectural - Glazing | 5000 |  | Documentation and Records | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | __ windows, installed in the GSM building, do not have a code 1 or 2 MCR: Cxxx-__M-A-LRC-D061_WS106-50529 (Code 3).
| 02SL - Stations (LUL) | Cxxx-NCR-002290 | NCR | DSS - PCC Cladding - North East elevation - W1-11S and column C1-20 scabbled back to allow for bracket installation |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-07-05 | 2018-04-12 16:23 | -84 | 2018-02-16 14:09 | Architectural - General | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The support bracket type 7a supporting panel P103 on the NE elevation of DSS located on the junction of column C1-20 and wall W1-14S required a small section of the wall to be chased back approx 10mm to allow for the bracket to be installed in the correct place. Due to an mistake on site the wall W1-14S and column C1-20 that the bracket was fixed to got overscabbled by approx 30mm. Due to reduction of cover by 30mm the scabbled section of the wall was protected with Intercrete similarily to Cxxx-NCR-001891 by the engineer supervising the works. The bracket was installed as per the design and packed out 5mm to bring it back to an alignment allowing installation of panel within tolerance.
| 02SL - Stations (LUL) | Cxxx-NCR-002291 | NCR | Platform Tunnels Damaged Grilles |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-08-20 | 2019-11-18 11:44 | 455 | 2018-02-21 10:01 | Architectural - General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Within the Westbound and Eastbound tunnels forming part of the PES structure we have 167 number lower grilles on each platform. A number of lower grilles within the Eastbound and Westbound Platforms have been damaged after being struck by moving plant. Some of the grille fins are scratched and some are bent as shown in the attached photos.
| 02SL - Stations (LUL) | Cxxx-NCR-002292 | NCR | DSS - PCC Cladding - Upper NE Elevation - Missing chamfer on the inner edge of panels P92R and 2 No. P91A |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-07-29 | 2018-06-06 15:54 | -53 | 2018-02-19 12:40 | Architectural - General | 500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Due to manufacturing error 2 No. P91A panels and panel P92R were cast without the chamfer on the back edge where the panels are joining the underslung panels P91B and P91C.
| 02SL - Stations (LUL) | Cxxx-NCR-002293 | NCR | DSS/CHS Wall Hatch Fixings No MCR |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-05-31 | 2018-04-09 11:09 | -52 | 2018-02-20 14:01 | Architectural - Walls | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Permanent works were installed & secured with fixings that were not covered by an MCR
| 02SL - Stations (LUL) | Cxxx-NCR-002294 | NCR | Stair 25 - Support for Fabreeka bearing |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-04-08 19:05 | -83 | 2018-02-21 11:43 | Civil - Civil Engineering General | 2000 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __ have cast stair 25 through the W616 retaining wall as per DWG Cxxx-__M-C-DWG-D061_WS105-51312 however the position of the stair does not leave sufficient space to support the Fabreeka bearing that connects the Lower concourse crossover steelwork. Currently fixing holes on the steel I beams that span from the lower concourse to Stair 25 are only 20mm within the bearing area as shown on attached Pic (IMG_1432). The Fabreeka bearings require a minimum of 152.4mm and a fixing position of half this shown on attachment (Bearing Type 4). __ propose to install a steel angle to the face of stair 25 to extend the bearing surface for the Fabreeka bearing as shown on Mark-up sketch attached.
| 02SL - Stations (LUL) | Cxxx-NCR-002296 | NCR | CRL Platforms - L tabs welded 10 mm high |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-05-14 | 2018-05-11 12:31 | -3 | 2018-04-04 10:05 | Architectural - General | 1000 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On Ladder Bay 68 one side of L tabs have been welded approx. 10mm too high. These are the tabs that hold the lower face fix brackets and the PNZ strut. Please see attached sketch 'Cxxx-NCR-00296 - Attach 1'.
| 02SL - Stations (LUL) | Cxxx-NCR-002297 | NCR | CHS - Primary Anchor Fixings Inspections |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-05-31 | 2018-06-25 12:36 | 25 | 2018-02-21 13:26 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The CHS external cladding steel support structure is fixed back to the RC structure by HIT-V-8.8F M24 anchor rods with __ HIT-HY 200-A injection grout - as per drawing numbers Cxxx-__M-C-DWG-D061_WS107-508*18-31*. These anchors are to be installed as per the parameters set out in section 4.4 of the matrix in ITP no. Cxxx-__M-A-ITP-D061_WS107-50007 (attached). The inspection of drill hole diameter was not carried out by __ for the East, South & West elevations prior to setting the anchors.
| 02SL - Stations (LUL) | Cxxx-NCR-002299 | NCR | Paving sett Levels and General Workmanship |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-07-18 | 2018-11-30 17:34 | -230 | 2018-02-22 13:58 | Architectural - Flooring | 5750 |  | Workmanship | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Paving setts laid so far in Court st eastern footpath has sunk in due to lack of curing time for the screed and and the General workmanship for laying the setts has been poor, Including: -Grout spills on the setts and covers. -skewed paving setts - Joint widths not maintained. -Grout washed out due to excess cleaning.
| 02SL - Stations (LUL) | Cxxx-NCR-002300 | NCR | DSS - Level 6 - Riser A - Parallel Conduits |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-04-23 | 2018-04-16 14:01 | -7 | 2018-02-22 16:38 | Consents - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Parallel conduits were installed in riser A DSS for multiple services running into the Cxxx vent room area
| 02SL - Stations (LUL) | Cxxx-NCR-002301 | NCR | CRL Platforms - GRC Architectural Cladding - Big head issue |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-07-05 | 2018-05-04 13:18 | -62 | 2018-02-22 16:20 | Architectural - General | 9404 |  | Workmanship | Reject | 2 (6-60k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Whilst GRC cladding operatives were removing GRC face fix panels from the storage crate, 3no sub frames popped from the panel. The operatives followed the inspection procedure in the GRC cladding installation ITP - Cxxx-__M-A-ITP-D061_WS106-50153.
| 02SL - Stations (LUL) | Cxxx-NCR-002302 | NCR | CHS - __ Louvre Insect Mesh Corrosion |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-07-05 | 2018-04-25 09:33 | -71 | 2018-03-07 15:24 | Architectural - General | 5750 |  | Material | Rework | 3 (3-6k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | A number of the __ WG-AL Louvres that have been installed at CHS are experiencing rust/corrosion to the insect mesh that is fixed to their back. The CHS-41 Louvre on Level C has experienced wide-spread rust/corrosion to the insect mesh - shown in the photos attached. Upon closer inspection, it has been noticed that a number of the other installed Louvres are starting to rust in patches and a number of those that are not currently installed are also beginning to rust - see photos attached. The __ Louvre's installed have not been signed off by __ or Crossrail.
| 02SL - Stations (LUL) | Cxxx-NCR-002303 | NCR | LULO - Site Installation changes to a By Exception Drawing |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-08-08 | 2018-08-06 09:40 | -2 | 2018-04-10 09:18 | Electrical - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Site Installation changes to a By Exception Drawing. CMS re routed to avoid clash with mechanical services. This took place under a P Rev drawing covered under the By Exception Process.
| 02SL - Stations (LUL) | Cxxx-NCR-002304 | NCR | Insufficient fabrication control for Kacier Roof gutter posts and top hats |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2018-06-30 | 2018-06-11 14:51 | -19 | 2018-03-01 10:37 | Architectural - Roofing & Exterior Treatment | 5000 |  | Documentation and Records | Rework | 3 (3-6k) | Complete | Management Problem - Inadequate administrative control | Completed |  | It was witnessed during a CRAF site visit that the lower top hats had been fabricated (galvanised) as an addition to the __ Roof System as an intermediate between the supporting steel and lower deck panels, whilst the guttering posts had been fabricated (welded and galvanised) to support the roof gutter. The ITP was requested for the offsite fabrication of these bespoke components; it was noted that no ITP existed, only an MCR. Works Information Vol 2B Part 20.8 states “The Contractor and his subcontractors and suppliers of any tier engaged in supplying, manufacturing, construction, installation, commissioning and testing or any other service connected with the works, shall maintain ITPs appropriate for the services they provide that are accepted by the Supervisor.” Without the ITP and associated records, the following is unknown; a) competence of welders b) availability of weld procedure c) what checks and testing has been carried out on welds d) what galvanised thickness(es) have been applied e) how applied thickness aligns with design life and corrosivity environmental category to assure this will be met f) what records will be used as part of the certification of these fabricated components.
| 02SL - Stations (LUL) | Cxxx-NCR-002305 | NCR | Quality checksheets for __ Roof work not complete, traceable and fail to capture CRL Hold Points |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2021-06-18 21:06 | 353 | 2018-03-01 10:39 | Architectural - Roofing & Exterior Treatment | 3500 |  | Documentation and Records | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Quality checksheets were requested for installation at GL 9-11 which was checked during a CRAF site visit. On review of checksheets QF47 ‘__ Roof inc. Wings’ as detailed in the ITP, the following was found; a) a number of CRL Hold Points had not been completed as required in the ITP b) checksheets contained blank entries and/or had been partially completed c) checksheets referred to other records for full completion however these could not be found or traced. Based on this acceptable installation for the GLs sampled could not be confirmed due to the state of the current deliverable records. This was the same for guttering checksheets. Works Information Vol 2B Part 13.2 states “The Contractor shall provide progressive assurance that the Contractor’s design (where appropriate) and the constructed works comply with the requirements set out in the contract … __ assurance means that there will be continual confirmation of compliance by the generation of contemporaneous records.” ITP (Cxxx-__M-A-ITP-D061_WS106-50120) notes the following definition for a Hold Point; “Hold point - A hold point is an inspection stage of a process, beyond which no work shall proceed until the relevant inspection is undertaken and accepted.”
| 02SL - Stations (LUL) | Cxxx-NCR-002306 | NCR | LULO GSM - Non-compliant Adhesive Use in Curtain Wall Installation |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-08-10 | 2018-07-30 15:35 | -11 | 2018-03-02 10:11 | Architectural - Roofing & Exterior Treatment | 1000 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | Unapproved use of adhesive in __ curtain wall system to bond the __ duoslab insulation to the rear of the aluminium composite panel. The product used is 'Indasol Foam Bonder' and is not S1-085 compliant for fire. Use of adhesive was not specified in the F2 design nor MCR.
| 02SL - Stations (LUL) | Cxxx-NCR-002307 | NCR | DSS Cross passages A and B switch boards |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-04-14 | 2018-04-27 12:43 | 13 | 2018-03-05 15:42 | Electrical - Switchgear | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | __ Maintenance, Access and Replacement Strategy specifies - The panel will be front entry with adequate space (>750 mm) in front of the panel for access and for the removal of MCCBs. The cables are top entry (note that said sub-switchboards are bottom entry therefore this is an error in the strategy). BS 7671 specifies - Minimum Passing Width in case of evacuation = 700mm Gangway width between barriers or enclosures or other barriers or enclosures and the wall = 700mm The rough measurement for Panel A was 650mm between front panel handle and steel frame. Panel B was 630mm – this has potential to further reduce due to room finishes.
| 02SL - Stations (LUL) | Cxxx-NCR-002308 | NCR | Escalator Guarding |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-06-27 | 2018-05-31 14:15 | -27 | 2018-03-07 12:09 | Mechanical - Escalators | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The Escalator Sub-contractor __ has omitted the design and installation of machine guarding in the Pan TfL design for te Escalators line wide, including the Escalators for Whitechapel Station.
| 02SL - Stations (LUL) | Cxxx-NCR-002309 | NCR | DSS level 6 AHU 2 room 6/763 CMS |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-06-06 | 2018-05-18 12:33 | -19 | 2018-03-08 11:02 | Electrical - Cable Management | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Installation of CMS in AHU 2 room 6/763 in DSS
| 02SL - Stations (LUL) | Cxxx-NCR-002310 | NCR | CRL Platforms - CS1 fireproofing east side - 28 & 56 day concrete strength not achieved |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-04-18 | 2018-03-26 07:30 | -23 | 2018-03-09 14:58 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __ poured the in-situ CS1 Fireproofing (East side) with a C40/50 Line 40 concrete mix. Slumps tests were taken and were in specification. 4no test cubes were made in accordance with Cxxx-__M-C-ITP-D061_WS106-50125. The 2no cubes crushed at 28 days had results of 41.5N/mm^2 and 39.0N/mm^2; and the 2no cubes crushed at 56 days had results of 47.7N/mm^2 and 48.6N/mm^2. This is below the design compressive strength of 50N/mm^2. See attached report CW2033.
| 02SL - Stations (LUL) | Cxxx-NCR-002311 | NCR | LULO - West Lift Lobby Steelwork - Application of Interfine 691 Top Coat |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-09-21 | 2018-09-30 19:07 | 9 | 2018-03-13 14:48 | Civil - Structural Engineering | 2000 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The West Lift Lobby beam was delivered and installed following the approved N4 paint system for LU/LO structural steelwork [Cxxx-__M-C-LRC-D061-50184]. This MCR states the application of 2no coats, primer and intermediate, but it does not mention the application of the top coat. The top coat was omitted from the MCR as it was supposed that all structural steelwork was going to be fire protected. The steelwork beam was not fire protected and the top coat was never applied. The beam is now located underground.
| 02SL - Stations (LUL) | Cxxx-NCR-002312 | NCR | CHS - Louvres Missing Samples |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-05-02 | 2018-04-30 15:32 | -2 | 2018-03-13 14:03 | Architectural - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The following louvres have been installed at CHS without a sample approved for them as required by the architectural specification document no. Cxxx-__M-A-RSP-D061-50079: 1. Gilbert WH-75 Louvre - EWS-751 2. Gilbert PHH Louvre - EWS-758 3. __ L70D Louvre - EWS-771 4. __ L120D Louvre - EWS-772 5. GKD PC Futura Mesh Screen - EWS-715 (Internal at DSS FV Shaft) The louvres installed at CHS are all located behind the external cladding and the mesh screen installed at DSS is internal and not 'customer facing'.
| 02SL - Stations (LUL) | Cxxx-NCR-002313 | NCR | DSS Riser A level 4 Earth tray |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-06-18 | 2018-03-28 10:55 | -82 | 2018-03-20 14:34 | Electrical - Cable Management | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A 300mm earth tray which had already been signed off by Crossrail was found to have been altered without the electrical team knowing and had been cut along a line of tray perforations
| 02SL - Stations (LUL) | Cxxx-NCR-002314 | NCR | Crossrail Platforms - GRC - P-CP3 cornice panels cast incorrectly |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-04-30 | 2018-04-11 10:34 | -19 | 2018-03-21 11:09 | Architectural - General | 660 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | The P-CP3 right hand cornice panels were cast incorrectly. They were cast with an integral infill strip which is not required. The P-CP3 right hand cornice panel is not a mirror image of the left hand side. This cast in infill strip clashed with the cast in infill strip of the adjacent correct panel. Please see attached document which details the defect. This defect occurs on both the EB and WB panel.
| 02SL - Stations (LUL) | Cxxx-NCR-002315 | NCR | LULO - ETH Manhole not constructed to Cxxx-FCD-001725 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-06-09 | 2018-06-25 12:40 | 16 | 2018-03-21 17:40 | Civil - Drainage | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | Cxxx-FCD-001725 was approved for the construction for manhole CMH03. However, upon site surveys and communication with __, the manhole has been constructed to differing levels due to differing asbuilt dimensions. This change has since been captured within a revision of Cxxx-__M-P-DDL-D061_WS105_1-00001 (P02).
| 02SL - Stations (LUL) | Cxxx-NCR-002316 | NCR | Crossrail Platforms - GRC - CP3b Rib Alignment |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-07-05 | 2018-04-17 09:45 | -79 | 2018-03-27 12:18 | Architectural - General | 750 |  | Design | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Please see attachments and response to MCC 405 (GRC-RFI-054). It details 2 No. issues __ experienced to 2 adjacent ribs, both created alignment issues.
| 02SL - Stations (LUL) | Cxxx-NCR-002317 | NCR | CHS - Ground Water Drainage - Incorrect surface water drainage warning tape |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-06-10 | 2018-07-06 14:24 | 26 | 2018-03-22 14:43 | Civil - Drainage | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Specification of the CHS Below ground drainage was not followed, and a material used that is not on the Specification nor a approved MCR was used
| 02SL - Stations (LUL) | Cxxx-NCR-002318 | NCR | ESS - Stair 23 - Glazed Rooflight Non-compliant |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-07-02 | 2018-12-11 10:11 | 162 | 2018-04-04 17:10 | Architectural - Glazing | 20500 |  | Documentation and Records | Repair | 2 (6-60k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The ESS rooflight is in accordance with the BH architectural specification, however specification is not LU compliant, in accordance with LU G-085 Code of practice – Fire Safety of Materials and Fire Safety of Specific Items and Materials used in the Underground. The lowest layer of glass should be 8mm toughened, however our glass in accordance with the spec is 8mm heat strengthened. All the rest of the layers should remain the same.
| 02SL - Stations (LUL) | Cxxx-NCR-002319 | NCR | DSS - Stair 3 - Out of tolerance |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-07-04 | 2018-07-03 15:51 | -1 | 2018-03-26 08:01 | Civil - Civil Engineering General | 1200 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Some steps have been poured outside of the concrete tolerance +/- 5mm
| 02SL - Stations (LUL) | Cxxx-NCR-002321 | NCR | DSS level 1 TR 2 room 1/782 damage to conduit |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-05-25 | 2018-05-16 07:46 | -9 | 2018-03-27 11:32 | Electrical - Cable Management | 3000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | In DSS level transformer room 2 there has been damage done to an installed conduit for the MEP team
| 02SL - Stations (LUL) | Cxxx-NCR-002322 | NCR | Court Street - Water Ponding |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-07-25 | 2018-10-01 15:29 | 68 | 2018-03-27 18:15 | Architectural - Flooring | 4500 |  | System Defect | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please see attached photograph of Water ponding during heavy rain fall at the bottom of Court St South Stairs. Please also see attached Asbuilt survey of the area. The survey shows the Asbuilt levels are within tolerance- Design Level (112.283). The reason for the ponding as it appears the Corduroy Paving’s are laid very tight against each other – reducing the chance for water to run off easily. There is also a Down pipe from the adjacent property discharging directly onto the Corduroy area, which is compounding the problem. It was not in the design scope to account for adjacent properties to discharging onto the pavement directly.
| 02SL - Stations (LUL) | Cxxx-NCR-002323 | NCR | DSS level 4 stair 10 area 600mm tray |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-07-26 | 2018-05-24 07:38 | -63 | 2018-03-28 11:38 | Electrical - Cable Management | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | An end portion of some 600mm tray in the stair 10 area of DSS was damaged
| 02SL - Stations (LUL) | Cxxx-NCR-002324 | NCR | The GFRC Manufacturing ITP reflect the correct frequency of dimensional check being carried out. |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2018-05-29 | 2018-04-26 07:54 | -33 | 2018-03-28 14:27 | Materials - General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | A surveillance was carried out at GRC Uk in __ and the following was found; Mould dimensional checking is being completed as follows: External GRP (Patterns and Moulds, Cordek) > 100% dimensional check (FaroArm or equivalent) Internal Timber > 100% dimensional check (Manual) Internal CNC FreeFab (Model Board Blocks) > 20% dimensional check (FaroArm). Of that 20%, for re-useable moulds no further dimensional check is completed after first casting. It was stated by __ that the 100% checking of CNC (FreeFab) moulds was reduced to 20% around October 2017 based on confidence in end product performance. However, this change was not relayed to Cxxx, Cxxx and Cxxx to ensure agreement and update of the ITP Cxxx-__M-O4-ITP-D061_WS106-50001 (Rev 5.0) . The ITP currently states for Activity - ‘Mould Set Up’ that ‘Each Casting’ should be checked for ‘Visual and Dimensional’ in accordance with design drawings and tolerances. This is not being met. A Mould Checking Form is only being completed where the checks as noted above are being completed. Furthermore, the GRC Unit Checking Form includes a section for Mould Pre-Production – Key Dimensions Check which is always noted as ‘Yes’ irrespective of whether the 20% FaroArm check has been completed. This is miss-leading information as in cases Mould Dimensional Checking has NOT been completed, i.e. outside of the 20%. Post Demould dimensional checking is NOT being completed for panels manufactured by CNC (curved panels) through the use of the FaroArm. The ITP states for Activity – ‘Post Demould QA Check’ that ‘Each Casting’ should be checked for ‘Complete Final Dimensional Check and Finishes’. This is not being met. The GRC Unit Checking Form is again miss-leading as it includes a section for De-Moulding – Key Dimensions Correct (see below) which is again noted as ‘Yes’ irrespective of whether such check has been completed. It was stated that this check is not being completed as confidence is gained through Mould checking. Dimensional checks are only completed for cast in items.
| 02SL - Stations (LUL) | Cxxx-NCR-002325 | NCR | CHS - Level 1 - Damage to sub Distribution A WHI/CHS/LVADB by zink enriched paint |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-07-12 | 2018-06-29 12:36 | -13 | 2018-04-03 09:52 | Electrical - LV Equipment | 700 |  | Damaged | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Theft, tampering, sabotage, or vandalism | Completed |  | Malicious damage to sub Distribution A WHI/CHS/LVADB by zink enriched paint (Picture 1 attached). The damage was identified on 02/04/2018 over the weekend during a time when operative numbers were low on site. It was noted that the mechanical protection for the sub distribution had been removed to intentional with tools. The extent of the Zink rich paint damage from picture 1 can be seen on the front face paintwork / various labels / isolation switched / monitoring/metering equipment / door handles and door locking devices. Picture 2/3/4 attached after cleaning by water with damp cloth
| 02SL - Stations (LUL) | Cxxx-NCR-002326 | NCR | LULO - LO Concourse Rooflights - Incorrect Torque to Bolt Connection |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-05-15 | 2018-05-30 15:55 | 15 | 2018-04-05 14:44 | Architectural - General | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate man -machine interface | Completed |  | Concerns were raised during an inspection carried out by __ (Alicia Harfield) and Crossrail (James Oliver) for the first of the bolted connections between rooflight and brackets on 04/04/18. Upon questioning, there were discrepancies between the ITP and the operative’s understanding of the torque value. The ITP states that the bolted connection between the rooflight and the bracket should be 464 Nm however the Operative believed it to be much less at 367 Nm. Upon further investigation, there was a discrepancy in the ITP for the torque values required at other connections related to the rooflights. To summarise: - Brackets to structural steel should have a torque value of 97 Nm. The ITP is correct to this and successful site inspections have been completed -Rooflights to brackets should have a torque value of 464 Nm. The ITP is correct to this however the site inspection proved that a much less torque value was being applied. These torqued bolts shall be removed and reinstalled to the correct value. - Balustrade spigot bracket to rooflight should have a torque value of 80 Nm. The ITP is incorrect to this and states 97 Nm, however all site inspections have been successful and witnessed 80 Nm. The ITP shall be updated to reflect this.
| 02SL - Stations (LUL) | Cxxx-NCR-002327 | NCR | Use of Visqueen in along GLA1, 1DS, LULO |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-08-17 | 2018-07-26 08:50 | -22 | 2018-04-12 13:19 | Architectural - Walls | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | __ High performance vapour barrier sheet membrane was installed. It transpires that the MCR for this product is Code 3
| 02SL - Stations (LUL) | Cxxx-NCR-002328 | NCR | DSS level 4 stair 10 area - water ingress |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-02-28 | 2019-02-02 12:28 | -26 | 2018-04-06 13:32 | Electrical - Cable Management | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In DSS level 4 stair 10 area water ingress happened which fell over some CMS and DB,s
| 02SL - Stations (LUL) | Cxxx-NCR-002329 | NCR | DSS - PCC Cladding - Scabbling of SW elevation (service road) wall to correct the alignment of brackets |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-08-10 | 2018-06-22 12:46 | -49 | 2018-04-12 13:16 | Architectural - General | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In two locations on the SW elevation of DSS the RC is cast up to 30mm out of alignment does not allow us to install the cladding brackets for panel installation to our design position: - downstand beam CDB-C-01 above the submarine door - downstand beam CDB-A-04 above louvre DSS-17A/B
| 02SL - Stations (LUL) | Cxxx-NCR-002330 | NCR | DSS level 5 switch room Battery panel installed in the wrong place |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-10-06 | 2018-06-29 12:44 | -99 | 2018-04-09 08:56 | Electrical - LV Equipment | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | A battery panel which was installed on level 5 DSS switch room was installed to close to the main switch panel
| 02SL - Stations (LUL) | Cxxx-NCR-002331 | NCR | LULO - Damage to SB1 Distribution Panel Door |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-08-11 | 2018-10-04 08:22 | 54 | 2018-04-13 15:34 | Electrical - Power Distribution | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | The Door of Panel SB1 has been damaged due to plant movement in the room.
| 02SL - Stations (LUL) | Cxxx-NCR-002332 | NCR | LULO/ AP Power Asset ( LUL S1915 - 810mm ) for maintenance purpose of Inverter/batteries panel. |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-08-08 | 2018-09-03 10:18 | 26 | 2018-04-10 13:19 | Electrical - Switchgear | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | OLBI/E54 GSM building level 2 LV equipment measurement and setting out was installed to __ designed and on completion of room installation we did not achieved the LUL AP Power Asset (LUL S1915) 810mm clearance requirement. In order to achieve this spec requirement we had to move the 100amps __ isolator,Bypass panel, OLBI inverter/batteries panel. Please see attached redline drawing with this NCR.
| 02SL - Stations (LUL) | Cxxx-NCR-002333 | NCR | Not following the snagR system implemented on the project for recording/closing Snags |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-05-09 | 2018-05-31 19:02 | 22 | 2018-04-11 09:20 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Supervision - Supervisor does not have sufficient experience | Completed |  | Snags have been raised and closed for the Inspections relating to the installation of windows on the GSM Building without recording them on the Project SnagR System implemented on this project Cxxx-__M-N1-STP-D061-50014 Rev 7.0
| 02SL - Stations (LUL) | Cxxx-NCR-002334 | NCR | Armour cables termination. Where copper strands isn't presence at __ lug inspection hole. |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-05-20 | 2018-05-15 13:25 | -5 | 2018-04-10 14:55 | Electrical - General | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 2 x 150mm XLPE/SWA/XLPE/LSOH been terminated into a 400amps fuse switch disconnector in E57 DNO Intake switch room where cable copper strands are 5mm short of __ lug inspection hole. This is incorrect installation of the lug to manufacturer's guideline.
| 02SL - Stations (LUL) | Cxxx-NCR-002335 | NCR | CRL PLT - Cross passage 3 - loose connection SWA Gland on DB __DB2 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-07-20 | 2018-08-23 20:54 | 34 | 2018-04-11 15:43 | Electrical - LV Equipment | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | During inspection with CRL PFE it was identified that the incoming SWA gland to __DB2 was loose that held the earth ring in position.
| 02SL - Stations (LUL) | Cxxx-NCR-002336 | NCR | CT4 Big head |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-05-27 | 2018-05-30 15:23 | 3 | 2018-04-17 11:42 | Architectural - General | 1000 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 2 No. big heads have pulled out of the CT4 tusk during installation. This is similar to Cxxx-NCR-00225, where a big head pulled out of the PT4 tusk. Also, 1 No. cast in socket is not modelled in the same location as the panel fixing. The contractor is subsequently unable to install this fixing. This occurs on all 4 No. CT4 tusk arches.
| 02SL - Stations (LUL) | Cxxx-NCR-002337 | NCR | GSM MCC1 Spreader Box Installation |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2018-05-27 | 2018-06-22 08:12 | 26 | 2018-04-17 11:09 | Electrical - Switchgear | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Cxxx-FCD-002630 (addition of spreader box to facilitate cable termination) stated FDC accepted on the basis of MCR approval - do not commence works without MCR approval. __ operatives were aware as part of a site visit and conversation on 12/04/18 that Spreader Box was not to be installed without an approved FCD + MCR Site visit 16/04/18 - Spreader Box has been witnessed as installed without an MCR submitted / accepted.
| 02SL - Stations (LUL) | Cxxx-NCR-002338 | NCR | WSS - liner wall void remedial grout cube strength |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-05-28 | 2018-04-24 14:53 | -34 | 2018-04-18 10:08 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The following NCR (Cxxx-NCR-002234) was raised in regards to a void that had formed within the liner walls in the WSS (see NCR for more information). __ proposed to clean and fill said void with repair concrete.
| 02SL - Stations (LUL) | Cxxx-NCR-002339 | NCR | LULO Upper concourse cracks in paving |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-08-12 | 2019-07-10 10:04 | 332 | 2018-05-14 16:27 | Architectural - Flooring | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Background: On the area on upper concourse between gridlines DE-DI paving was installed between 05/03/2018 and 23/03/2018. During this period temperature was low (with sub-zero temperatures especially during the nights). The area was protected from adverse weather (Monarflex tent was set up with space heaters to maintain required temperature) Paving was installed and progressively inspected in 3 stages: 09/03/18- IRF 1601 (marked green) 16/03/18- IRF 1613 (marked pink) 23/03/18- IRF 1622 (marked yellow) After the 3rd inspection cracks in the grout were found (Yellow area). Area was left uncovered for the weekend to assess if the cracks getting worse. They got worse, so __ (paving subcontractor) was notified about the issue. __ invited __ Technician (supplier) who on 11/04/2018 carried out on-site assessment (including taking samples of grout and screed to laboratory). __ produced the report showing 4 potential root causes of the cracks (__ comment in brackets): 1.It is recommended that as part of any remediation that the suspended concrete deck be inspected. For any signs of cracking or change in levels that could indicate deflection under load and be either the root cause or contributed to the screed issues seen on site (Slab was checked by __ and __ prior applications of waterproofing membrane and no cracks were noticed) 2. Screed was placed in temperatures below the recommended 5°C minimum (Area was heated and no placing of the screed took place in temperatures below 5 degrees) 3. “Immature” screed has cracked under load during the follow-on works and loads applied by fitting of the overlying tiles and other traffic (Area wasn't subject of traffic/loading) 4. It is important to consider that in a period of sustained low temperatures and overnight sub-zero, that even when the air temperature is 5°C, the materials themselves and, often, the substrate they are placed on, can still be several degrees below the air temperature. (__ believes this was the root cause of cracks. Area was heated above with air temperatures reaching 20 degrees, but it wasn't heated from below (HCDL level) which could lead to the low substrate temperatures)
| 02SL - Stations (LUL) | Cxxx-NCR-002340 | NCR | Crossrail Platforms - GRC - CP2 Baseplates grout cube results |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-05-29 | 2018-05-17 14:26 | -12 | 2018-04-19 16:26 | Architectural - General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The grout for the base plates installed in 'CP2 - Bays 407-411' did not reach the required 40 N/mm2 strength after 28 day test (36 N/mm2) Unfortunately the 56 days cube has been struck in error at 28 days. The reasons for the low strength is unknown. However, possible reasons include: Poor cube making Poor cube storage Incorrect labelling Insufficient care during transit Not making grout to manufacturers instructions The GRC baseplates have been poured over 66 No. different batches of grout representing over 260 No. compliance cubes. This is the second to fail to gain 28 day strength and therefore deemed to be an anomaly. Over the 66 batches poured the grout has gained some strength between the 28 day and the 56 day. It is therefore surmised that the cubes would have reached design strength at the 56 day had the cube not been struck in error.
| 02SL - Stations (LUL) | Cxxx-NCR-002341 | NCR | LULO - Cable installation proceeded before CMS and Switchboard sign-off |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-06-02 | 2018-09-10 13:15 | 100 | 2018-04-23 07:49 | Electrical - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | SWA (identified as C17) cable was installed in CMS traywork, and glanded into the Switchpanel LUSB04 in Switchroom E55, ahead of the CMS and switchpanel being signed off by Crossrail.
| 02SL - Stations (LUL) | Cxxx-NCR-002342 | NCR | LULO - Works proceeding without an ITP - Inclined Glazing Brackets |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2018-06-30 | 2018-07-05 12:43 | 5 | 2018-04-23 07:58 | Architectural - Glazing | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | As stated in CRL-OBS-22087, multiple lower and upper steel brackets have been installed to the R12 primary steelwork for the inclined glazing support. The current ITP (Cxxx-__M-A-ITP-D061_WS106-50123 (1.0)) has only been approved for the setting out, drilling and zinga application of the bolt holes for the brackets.
| 02SL - Stations (LUL) | Cxxx-NCR-002343 | NCR | LULO - Concourse Roof - Failed Inspection on VCL membrane R10S wing |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-08-28 | 2018-10-29 08:51 | 62 | 2018-06-29 13:02 | Architectural - Roofing & Exterior Treatment | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | LULO - Concourse Roof - Failed Inspection on VCL membrane R10S wing due to water presence
| 02SL - Stations (LUL) | Cxxx-NCR-002344 | NCR | HCDL platform canopies gutter sealant |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-08-01 | 2019-07-09 10:11 | 342 | 2018-04-23 18:21 | Architectural - Roofing & Exterior Treatment | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The box gutter sections which are installed end-to-end along the western edge of the HCDL upper canopy have been sealed together using a sealant product not captured within MCR Cxxx-__M-A-LRC-D061_WS106-50467 Rev 3.0.
| 02SL - Stations (LUL) | Cxxx-NCR-002345 | NCR | LULO - Level 3 Plant Room - No Benchmark for Floor Finishes |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-07-24 | 2019-02-13 15:49 | 204 | 2018-04-25 08:58 | Architectural - Flooring | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | A benchmark was not agreed and approved prior to completion of floor paint finishes within the Level 3 Plant Room.
| 02SL - Stations (LUL) | Cxxx-NCR-002347 | NCR | CHS - Lack of Samples |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-06-24 | 2018-09-12 13:12 | 80 | 2018-04-25 15:01 | Architectural - Finishes | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Cxxx-NCR-002312 was raised to resolve the lack of samples for louvres at CHS. To allow the closure of Cxxx-NCR-002312, I have raised this NCR to cover the benchmarks that we haven't yet completed which are: 1. __ at DSS 2. __ PHH 3-sided Louvre at CHS In order to close this NCR, the two benchmarks noted above are to be at code 1 on eB.
| 02SL - Stations (LUL) | Cxxx-NCR-002348 | NCR | Crossrail Platforms - GRC Cladding - Rectilinear acoustic soffit panels |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-06-04 | 2018-09-11 08:36 | 99 | 2018-04-25 15:22 | Architectural - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Please see the report attached which details a discrepancy with the number of holes in the rectilinear acoustic soffit panels.
| 02SL - Stations (LUL) | Cxxx-NCR-002349 | NCR | Sitewide- __ treads non-compliance |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-09-09 | 2018-07-25 12:32 | -46 | 2018-05-11 15:31 | Architectural - Flooring | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | During inspection of __ on stairs 40 in Cambridge Heath Shaft (10/04/2018) it was noticed that yellow contrasting strip on the __ goings is non-compliant with MCR and building regulations. Following on-site meeting between __ (__), __ (CRL), __(LU),__ (__-subcontractor) and __ (__-supplier) it was agreed: 1. All installed treads will be repainted on-site to the required standard 2. __ (supplier) states that painting will not affect warranty of the product (see email attached) 3. First flight of painted nosings (CHS, Stair 40, Flight 7) will be inspected by CRL and acceptance will be required to proceed with remaing treads.
| 02SL - Stations (LUL) | Cxxx-NCR-002350 | NCR | GSM Windows Installation Checksheets |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-06-22 | 2018-09-21 13:33 | 91 | 2018-04-26 14:14 | Civil - Civil Engineering General | 2500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | The Current GSM Window Installation Checksheet does not demonstrate progressive assurance as detailed in the ITP activities. There is only 1 line item in the checksheet and 5 steps in the ITP
| 02SL - Stations (LUL) | Cxxx-NCR-002351 | NCR | LULO - GSM Levels 1 & 2 - |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-06-25 | 2018-05-29 07:29 | -27 | 2018-04-26 15:51 | Mechanical - Piping | 5000 |  | Planning | Repair | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | __have installed pipework without a C01 drawing or a by exception in place
| 02SL - Stations (LUL) | Cxxx-NCR-002352 | NCR | WSS - intermediate slab __ position |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-07-31 | 2018-08-14 12:29 | 14 | 2018-04-27 11:12 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As part of package Cxxx-__M-C-CER-D061-53011, __ constructed the Western Stair Shaft (Stair 25 and Lift 3). Part of the construction was the intermediate slab (level 3 landing for lift 3 which links to the lower concourse). Said slab has an 800x300 hole through slab as detailed in the RC drawing Cxxx-__M-C-DWG-D061_WS105-50784. The centre line of the 800x300 hole through slab is shown as being 5348mm off of the WSS gridline W1, however the centre line is actually 5680mm from gridline W1. Due to the builders work hole being in the wrong position the halfen channels (to support MEP assets - trunking/cabling etc.)do not align with the __.
| 02SL - Stations (LUL) | Cxxx-NCR-002354 | NCR | LULO - Lift 7 Wings Torque Testing |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-06-09 | 2018-05-11 15:47 | -29 | 2018-04-30 16:44 | Architectural - Roofing & Exterior Treatment | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The wings installed to lift 7 to support the gutters were installed on the weekend of 31/03/18. The records and photos were collated for CRL inspection. It was found that a value of 208Nm was used for the bolts with Nordlock washers instead of the 237Nm value stipulated in the ITP and Nordlock Torque Table.
| 02SL - Stations (LUL) | Cxxx-NCR-002355 | NCR | CMS installed without drawings |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-08-30 | 2019-02-20 13:05 | 174 | 2018-05-02 07:58 | Electrical - General | 5000 |  | Documentation and Records | Repair | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | CMS in lobby area outside switchrooms E55 and E56 have been installed without any I.F.C drawings.
| 02SL - Stations (LUL) | Cxxx-NCR-002356 | NCR | LULO Concourse concrete slab repairs |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-08-31 | 2018-07-05 12:37 | -57 | 2018-05-11 06:04 | Civil - Civil Engineering General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Small area of upper concourse concrete slab (approximately 6 square meters) was identified poured 25 mm higher than designed SSL. In this area due to falls in paving it was impossible to achieve minimum 50 mm screed thickness. Concrete level in this area was poorly reduced (without relevant control measures in place) by approx. 30 mm which led to exposing the reinforcement mesh. Waterproofing coat (WPS-305) was applied in this area
| 02SL - Stations (LUL) | Cxxx-NCR-002357 | NCR | North Accommodation Block shot peened window surround |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-08-23 | 2018-09-05 11:44 | 13 | 2018-05-15 13:27 | Architectural - Finishes | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __ have installed a shot peened stainless steel sill and surround to the 3no windows in the North Accommodation Block (3no in SOR and 1no in SSO). Cxxx-FCD-002512 (based on PTR5163) states that the plates will overhang the wall by 5-10mm. A small section of the curved window surround does not overhang the wall; in fact the wall protudes past the steel by 2mm for 200mm (top centre plate).
| 02SL - Stations (LUL) | Cxxx-NCR-002358 | NCR | LO heritage brickwork mortar strength |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-09-30 | 2019-02-20 09:48 | 143 | 2018-05-16 13:55 | Architectural - Brickworks/Blockworks | 1000 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | As part of the LO platform 5&6 brickwork remedial package Cxxx-__M-A-CER-D061-53066 __ are reinstating the heritage brickwork across the LO platform 5&6 domain. The mortar used in these works is __ Hydraulic Lime mortar (MCR = Cxxx-__M-A-LRC-D061_WS106-50651), which gains strength much slower compared to Portland cement based mortars, hence is tested for compressive strength at 28 days and then 91 days (see data sheet within MCR - page 7, bullet point '9.Mortar Mix Proportions' and see attached __ statement in regards to lime mortar testing).
| 02SL - Stations (LUL) | Cxxx-NCR-002359 | NCR | Live LV Battery Chargers - Inadequate Protection (Swarf ingress) |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2018-06-11 | 2018-07-06 10:03 | 25 | 2018-05-02 14:56 | Electrical - General | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | CRL were invited to attend the inspection of 4x LV Battery Chargers at CHS and DSS LV Switchrooms. IRF_MEP PERM_CHS_0275 lacked the sufficient detail of what was to be inspected / what stage of the ITP the installation had been completed to. Minor drawing reference errors were also present on the IRF On attendance in CHS LV Switchroom, __ presented the ITP and drawings. __ had no evidence of self assurance as the ITP had not been followed as no check sheets were completed (all were blank), however these were presented post IRF. In addition, on request to look inside one of the Battery Chargers, a substantial amount of swarf / dust was present. The purpose of the IRF / inspection was to facilitate the Discharge Test of the Batteries on 03/04/18. The assets are live (temporary supply) and have not been adequately protected and will require thorough cleaning ASAP and prior to said discharge test. A new invite / IRF to be issued to re-inspect Battery Chargers with the above addressed.
| 02SL - Stations (LUL) | Cxxx-NCR-002360 | NCR | Glazing Frame Installed prior to approved documentation |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-06-12 | 2018-07-06 14:29 | 24 | 2018-05-03 08:22 | Architectural - Glazing | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | Inclined Glazing frame on GL 3.3 and 4 on west side was installed prior to all documentation approved.
| 02SL - Stations (LUL) | Cxxx-NCR-002361 | NCR | Accomodation Block roofing - Lack of MCRs |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-02-28 | 2019-09-30 09:22 | -151 | 2018-05-03 08:19 | Architectural - General | 3500 |  | Documentation and Records | Use As-Is | 3 (3-6k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Cxxx-__M-A-LRC-D061_WS106-50443 raised, and found to be lacking in details. 2 new MCRs are required for the below - Stone Ballast for Roofing Bauder thermoplan standard outlet
| 02SL - Stations (LUL) | Cxxx-NCR-002362 | NCR | Accommodation Block, CHS and DSS Roofing - Non UKAS Accredited Testing |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-09-28 | 2018-09-30 19:29 | 2 | 2018-05-03 12:32 | Architectural - General | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | CHS Roofing, Electronic Testing as per Cxxx-__M-A-CER-D061-50316 & DSS Roofing, Electronic Testing Cxxx-__M-A-CER-D061-50182 and Accommodation Block roofing, Electronic Testing testing as per Cxxx-__M-A-CER-D061_WS106-50054 no 4.07 has not been carried out by a UKAS Accredited company. See reports attached.
| 02SL - Stations (LUL) | Cxxx-NCR-002363 | NCR | CRLP DBs Standard of Completion for IRF |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2018-06-27 | 2018-06-27 09:34 | 0 | 2018-05-04 13:08 | Electrical - General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | CRL were invited to inspect WHI/CHS/CRLP/B/WB4, WHI/DSS/CRL-P/B/WB3, WHI/DSS/CRL-P/B/WB2, WHI/DSS/CRLP/A/WB1 - Distribution Board & Associated Cables and Final Fittings as part of IRF_MEP PERM_CRL_P_0059 On attendance, the ITP (Cxxx-__M-E-ITP-D061_WS106-50099) was presented which was returned Code 2 on 19/02/18 to enable __ to continue working on the basis that the comments would be addressed and the ITP accepted / Code 1 within 14 days. None of the Witness Points in the ITP (or the previous ITPs which were superseded by the above) had been adhered to. 90% of the outgoing circuits had been completed (wired) and terminated at Z end and a majority had no previous IRFs / invites for associated CMS, bracketry etc. In addition, as part of the ongoing site finishes, a lot of structural and station finishing elements have been progressed or completed (such as ceiling tiles) which limits the ability to now inspect said CMS / wiring. As the IRN / commlot for the DBs includes associated cabling (all outgoing circuits including installation of lighting and small power) these unfinished works make it complicated and will result in a large punchworks list. One of the DBs a circuit was missing / incomplete due to ongoing PTRs between __ and BH. At the time of inspection, __ were carrying out dead tests on the cabling from said DBs which limited the inspection of a finished asset as cabling and circuit breakers were disconnected / removed and parties had to work around one another. After completion of dead testing, CRL noticed that the __ and cable had been installed in the wrong circuit designation / way but hadn't been picked up by either the installation team or the tester. As the witness points have not been adhered to, for installations such as this, a considerable amount of time would have to be allocated for the IRF
| 02SL - Stations (LUL) | Cxxx-NCR-002364 | NCR | Access / Maintenance Restrictions due to CRLP DB __ Enclosures |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-10-30 12:31 | 122 | 2018-05-04 13:21 | Civil - Civil Engineering General | 10000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Design Problem - Other | Completed |  | WHI/CHS/CRLP/B/WB4, WHI/DSS/CRL-P/B/WB3, WHI/DSS/CRL-P/B/WB2, WHI/DSS/CRLP/A/WB1 Distribution Boards have been installed previous to a "__" enclosure being built / fitted. The __ enclosures now present a restriction on access and maintenance due to the opening of the DB door clashing with the __ enclosure in addition to the DB door damage present and in the future.
| 02SL - Stations (LUL) | Cxxx-NCR-002365 | NCR | CHS - Stairs and Ladders - Welders not listed under approved weld procedure |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-06-17 | 2018-06-13 08:15 | -4 | 2018-05-08 12:35 | Architectural - Handrail | 1000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Welders used to weld the CHS Stairs and Ladders are not listed under approved weld procedure on eB, Cxxx-__M-A-GPD-D061-50001 Rev 3.0.
| 02SL - Stations (LUL) | Cxxx-NCR-002366 | NCR | CHS - Stairs and Ladders - MCR for Stair Tread nosings not in place. |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-06-17 | 2018-05-29 15:17 | -19 | 2018-05-08 12:47 | Archaeology - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - No evidence of program review from Contractor's Quality Manager or Management | Completed |  | CHS - Stairs and Ladders - MCR for Stair Tread nosings not in place.
| 02SL - Stations (LUL) | Cxxx-NCR-002367 | NCR | LULO - ESS/Stair23 - VE Cladding panels installed without approved ITP or MCR |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-08-31 | 2018-09-19 17:25 | 19 | 2018-05-08 16:17 | Architectural - Walls | 1290 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | During the Week 6 possession Link Signs installed 3 VE cladding panels without an approved ITP or approved MCR. They had approval for sub-frame only.
| 02SL - Stations (LUL) | Cxxx-NCR-002368 | NCR | LULO- LO Concourse- INS-403 fixing strap |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-07-18 | 2018-05-16 12:02 | -63 | 2018-05-09 12:43 | Architectural - Ceilings & Soffits | 15080 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Cxxx-__M-A-DWG-D061_WS106-53704 P03 was approved on a by-exception (Cxxx-__M-A-RGN-D061_WS106-50111) to allow __ to install the insulation metal straps. Installation of the straps was undertaken on site with approximately 50% of straps installed. __ were subsequently notified by their subcontractor that the straps detailed would deflect with the load of the 2no layers of __ and therefore were not suitable for use as detailed.
| 02SL - Stations (LUL) | Cxxx-NCR-002369 | NCR | LULO - GSM - IPS Installation - Lack of self-assurance |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2018-10-08 | 2019-03-29 10:42 | 172 | 2018-05-10 06:22 | Architectural - Sanitary Fittings | 500 |  | Documentation and Records | Reject | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | CRL invited by __ management to inspect installation of IPS system (within WCs) on Level 1 of GSM. The following issues were identified by CRL at point of inspection; 1. ITP yet to be submitted to CRL for acceptance. 2. F2 Design not submitted to CRL for acceptance. 3. CAT document yet to be submitted to CRL for acceptance. 4. Quality checksheets not presented at inspection. 5. Installed works do not align with the F2 drawings which were present on site. The __ framework is currently secured back to the three adjacent plasterboard walls. The rear secondary support / reinforcement are yet to be constructed as are the head support framework back to the beams above. This is not the first instance in recent weeks of works being undertaken without all pre-start assurance deliverables in place.
| 02SL - Stations (LUL) | Cxxx-NCR-002370 | NCR | LULO - GSM - Fire Alarm Panel Energised prior to IRN acceptance |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2018-10-31 | 2018-09-16 09:10 | -45 | 2018-05-10 13:57 | Fire - Detection | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | Fire Alarm panel energised in Level 1 of the GSM prior to submission and acceptance of associated Installation Release Notice (IRN). This is in contravention of the CRL Testing & Commissioning Process Overview for Stations, Portals & Shafts (CRL1-XRL-O7-GPS-CR001-50007 Rev 1.0) issued under Cxxx-PMI-00449 and the Contractor's own Testing & Commissioning Plan (Cxxx-__M-O3-GPS-D061-50001 Rev 5.0). Cxxx-NCR-002276 (GSM - E57 DNO / Intake Power Supply Energised without accepted IRN) previously raised on this topic.
| 02SL - Stations (LUL) | Cxxx-NCR-002371 | NCR | Sitewide-In situ paving slip resistance test failed |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-10-17 | 2018-10-03 13:55 | -14 | 2018-05-10 16:22 | Architectural - Flooring | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | In situ paving slip resistance test were carried out by paving subcontractor __: HCDL platforms 28/11/2017 (9 locations)- FL-621 Paving (Marshalls) In 3 locations: (D,G,I) slip resistance results for wet paving on sloping floor doesn't meet specification requirements CRL platforms-19/12/2017 (10 locations)- FL-211 Paving (Granazzo) In all 10 locations slip resistance results for wet paving on sloping floor doesn't meet specification requirements
| 02SL - Stations (LUL) | Cxxx-NCR-002372 | NCR | DSS - Level 8 outstanding offsite fabrication records SCP-8-6-01 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-08-31 | 2019-01-05 12:13 | 127 | 2018-05-11 09:39 | Civil - Civil Engineering General | 1500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - No evidence of program review from Contractor's Quality Manager or Management | Completed |  | Steel Beam SCP-8-6-01 has been fabricated and installed. At the point of certification, the Declaration of Performance was not available.
| 02SL - Stations (LUL) | Cxxx-NCR-002373 | NCR | LULO - Concourse Inclined Glazing Bracket Manufacture (__) |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-07-25 | 2018-09-13 14:24 | 50 | 2018-05-16 07:45 | Architectural - Glazing | 11000 |  | Documentation and Records | Rework | 2 (6-60k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | __ have procured a subcontractor to fabricate brackets that form part of the inclined glazing system. The subcontractor in question (__) have sub-sub contracted this work to A. Barraclough. When asked for the company's certification (in relation to W/I Clause 20.7) and relevant factory production controls (Weld Procedures and associated documents), it was stated that these were not in place.
| 02SL - Stations (LUL) | Cxxx-NCR-002374 | NCR | LULO - Commencing wall tiling without station-wide ITP |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-06-26 | 2018-07-09 14:19 | 13 | 2018-05-17 12:49 | Architectural - Finishes | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | The Contractor commenced tiling works to GSM WCs / Wet Rooms without a station-wide ITP in place, and were reliant on an existing ITP for the TTH (ref Cxxx-__M-A-ITP-D061_WS106-50009 rev 2). The Contractor has since submitted a revised ITP (ref Cxxx-__M-A-ITP-D061_WS106-50178) to cover station-wide works. Please note: MCRs and Sample Acceptances were in place prior to commencing works and there is no discrepancy between tile type applied in TTH and GSM.
| 02SL - Stations (LUL) | Cxxx-NCR-002375 | NCR | LULO GSM - Cracked lintel to Plant Room 1/769 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-08-31 | 2018-08-10 08:58 | -21 | 2018-05-23 17:42 | Architectural - Brickworks/Blockworks | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Multiple cracks have been discovered in the Kingstone Type 16 concrete lintel above Plant Room 1/769 door D1/063, due to the duct installers notching the top of the lintel to fit their installation. There are 3no. hairline cracks in total which have been observed - refer attached document. The structural opening of this lintel is 1900mm, with 150mm bearing either end.
| 02SL - Stations (LUL) | Cxxx-NCR-002376 | NCR | CRL Platforms - CS1 - Void between cast and sprayed fireproofing layer |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-07-05 | 2018-05-30 15:13 | -36 | 2018-05-24 11:12 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As per Cxxx-NCR-002204, a void between the cast and sprayed fireproofing was discovered after striking the shutter for the CS1 cast fireproofing. __ filled the void with __ S5400 (MCR Cxxx-__M-C-LRC-D061_WS106-50222) and carried out contact grouting using __ MP650 (Cxxx-__M-C-LRC-D061_WS106-50053). Checksheets and cube results were provided for the MasterRoc contact grout works but could not be provided for the __ void works.
| 02SL - Stations (LUL) | Cxxx-NCR-002377 | NCR | LULO - Non-Compliant Fabrictation of Bracketry for R12 Inclined Glazing and Roof Lights |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2018-08-17 | 2019-10-14 10:26 | 423 | 2018-05-29 13:07 | Architectural - Glazing | 500 |  | Documentation and Records | Reject | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | The bracketry fabricated and delivered to site for the installation of roof lights and __ inclined glazing was found to be non compliant on multiple occurrences. The Contractor has not been able to provide off site documentation (DOP, FPC, Galvanising records, Welding records etc.) for the first batch of roof light and inclined glazing brackets procured. It was found that the supplier for the brackets did not have the relevant certification or fabrication controls. The roof light brackets were delivered w.c. 19/03/2018 and the inclined glazing brackets w.c. 16/04/2018. The second batch of brackets for the inclined glazing delivered on 26/05/2018 had the following issues: - Lower brackets were fabricated as a two piece system which contradicts the loading calculations in Cxxx-__M-A-CER-D061_WS106-50197 - Lower brackets were fabricated with 315mm base plates which is 15mm wider than the design. Therefore they cannot be installed using the predrilled holes in the primary steelwork. - Top brackets had been replaced with stainless steel brackets. This change in material has not been captured in an eB PTR. - The stainless steel top brackets had a signed final release document from the supplier. As stated in CRL-OBS-22654, they had noticeable defects including: - Visual decolouration due to overheating - Deformation to the fin/flange element. - Voids in welds. - The fin plate of the top brackets had been fabricated 15mm too wider than the design. It was found that the root cause of the dimensional issues with the second batch was an uncontrolled drawing being sent to the fabricator. This new revision of the lower inclined glazing brackets had the following issues: - The drawing had not been approved by the stage F designer or Crossrail. - The drawing number had been changed from the previous revision included in Cxxx-__M-A-CER-D061_WS106-50197. - There was no annotation or cloud to highlight the modifications. - No CAT check had taken place for Rev B. Unclear if an ICE had reviewed.
| 02SL - Stations (LUL) | Cxxx-NCR-002378 | NCR | Sanitary installation missed off ITP |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-07-08 | 2018-06-26 13:52 | -12 | 2018-05-29 14:36 | Mechanical - Public Health Engineering | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | It was noticed that the sanitary install was missing off the ITP once the install had started
| 02SL - Stations (LUL) | Cxxx-NCR-002379 | NCR | Lack of Records/Assurance Court Street Bridge Refurbishment Works |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-11-09 | 2019-06-13 07:51 | 216 | 2018-05-30 13:51 | Civil - Civil Engineering General | 1500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Assurance documentation related to the Works on Court Street is currently outstanding. This includes works which are adjacent to the operational railway (HCDL) as well as areas open to the public. Works were completed on the aforementioned in late 2015, with the TTH BIU in January 2016.
| 02SL - Stations (LUL) | Cxxx-NCR-002380 | NCR | Non adherence to Change Control Process for CMS Install DSS FV for Cxxx |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2018-07-09 | 2018-06-29 14:07 | -10 | 2018-05-30 14:11 | Electrical - Cable Management | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | IRF_MEP PERM_0317 submitted to CRL was very poor due to missing +/ incorrect drawings referenced on the IRF. On attendance in DSS Level A CHW Room - there were installation changes to the accepted drawing for CMS not adhering to the change control process. This was further highlighted and much worse on entrance to the Force Vent (FV) for Cxxx where considerable changes to the installation of CMS against the accepted design (again not adhering to the change control process). On further investigation, __ have failed to raise a PTR to BH and the considerable changes to the FV will also need to be agreed formally with Cxxx as the installation now utilises the FV equipment for fixing / supports for the CMS. Additional concern that Cxxx contractors were on site ready to pull / install cables on said CMS
| 02SL - Stations (LUL) | Cxxx-NCR-002381 | NCR | CHS & DSS - Louvre Anchor Fixings - No UKAS Pull Tests |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-07-27 | 2018-10-02 10:03 | 67 | 2018-05-31 14:09 | Civil - Civil Engineering General | 1000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | All the __ louvres at CHS and 3 no. of the __ louvres at DSS have been installed and pull testing was carried out by a test house that was independent to the contractor installing the louvres. On review of the pull test reports from this test house, it has been found that the independent test house is not UKAS accredited. The test house used is a company called __ who are a member of the LEEA - an example of their certificate of membership is attached. An example of the load test report for the louvre anchors is attached. Also attached is a certificate from __ (who are UKAS accredited) confirming that the quality management system of __ in respect to the testing of lifting equipment has been assessed and registered against the provisions of ISO 9001:2015.
| 02SL - Stations (LUL) | Cxxx-NCR-002382 | NCR | LULO - Northern Concourse - Secondary Steelwork - Incorrect drilling at Grid Line 1 for Concourse End Wall Support |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-08-31 | 2018-06-27 12:57 | -65 | 2018-06-26 07:25 | Civil - Structural Engineering | 1200 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Due to a site surveying error, the holes drilled for the secondary steelwork members (UB and PFCs) at the concourse main inclined columns are offset from the correct location. The deviation is 5-7mm low at the East column and 10-12mm low at the West column. The proposal is to ream/widen the holes vertically (upwards) creating slotted holes so that the secondary steelwork frame can be installed. Pre-load bolts to be used in the slotted holes.
| 02SL - Stations (LUL) | Cxxx-NCR-002383 | NCR | Proceeding without an approved MCR - GSM Mist supression Control Panels |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2018-07-16 | 2018-08-24 08:20 | 39 | 2018-06-06 07:49 | Fire - Suppression | 500 |  | Material | Reject | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | This NCR has been raise for proceeding without the approved MCR 'in place' and 'in use' in accordance with the requirements of CRL1-XRL-N2-GPD-CR001-50007 'Demonstration of Materials Compliance Procedure'. The MCR for these control panels (CRL-MCR-006074) is currently under review by CRL but is not approved for use on Cxxx.
| 02SL - Stations (LUL) | Cxxx-NCR-002385 | NCR | GSM - Relocation / Rework to CMS previously inspected / signed off |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2018-07-16 | 2018-07-03 10:45 | -13 | 2018-06-06 08:50 | Electrical - Cable Management | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | CMS previously inspected / signed off (including various cabling installed on said CMS) has been relocated. No evidence has been provided of change control or self assurance capturing relocation in addition to notification of said re-works.
| 02SL - Stations (LUL) | Cxxx-NCR-002386 | NCR | CHS - Walkway Anchors Fixed Outside Original Design Positions |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-09-28 | 2019-01-03 12:53 | 97 | 2018-06-06 11:32 | Civil - Civil Engineering General | 7500 |  | Design | Use As-Is | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The M16 anchors for the RC walkway connections at CHS have been drilled and fixed on all four elevations at CHS as per the 'Walkways.pdf' drawings attached - in total there are 55 anchor clusters with a total of 220 anchors that are to be embedded to a minimum of 150mm. Due to clashes with reinforcement bars in the concrete, a number of anchors have been fixed outside of the original design slotted positions and patterns that were defined in the structural calculations for the connections. In order to capture this change, the sub-contractor has raised three design queries to __ who are the structural designers of the walkways and connections. These queries are Cxxx-__-PTR-5795, Cxxx-__-PTR-5803 & Cxxx-__-PTR-5819 - I will attach these to the NCR once __ have formally responded to them. __ are currently running additional design checks on these anchor locations in order to certify the design. The design check they are carrying out is considering the positions of the anchors and the as-built embedment of each anchor - a survey of which is attached in this NCR (anchors marked with a cross are due to be cored following Cxxx RFI response). The output from this design check will be the three PTR's responded to and a CAT II check cert. to confirm the position of the anchors is acceptable. In lieu of the change in position of the anchors, the maximum tensile load on any one anchor is likely to change. Therefore, a further output from the __ check will be the pull test regime that is to be adopted. This pull test regime will likely increase from the original ITP requirement of 5% UKAS & 5% non-UKAS testing - I will confirm this once __ have formally responded to the PTR's.
| 02SL - Stations (LUL) | Cxxx-NCR-002387 | NCR | LULO - ESS - Westbound Access Stair Slab - Concrete Cube Strength Failure |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-09-30 | 2018-10-19 14:55 | 19 | 2018-07-05 07:50 | Civil - Civil Engineering General | 972.67 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | We have poured a concrete slab on the southern side of the East Stair Shaft (Stair 23) for the Westbound access stair (see drawings: Cxxx-__M-C-DWG-D061_WS106-53768). The concrete strength reached only 30N/mm2 at 28 days, and 33N/mm2 at 56 days (see attached cube results). However, as per PTR-5931 (attached), this reduced strength has been accepted by __ to use as-is for the purpose.
| 02SL - Stations (LUL) | Cxxx-NCR-002388 | NCR | LULO GSM - Non-compliant room size for disabled WCs |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-07-16 | 2018-07-01 16:00 | -15 | 2018-06-06 13:15 | Architectural - Partitions | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Further to Cxxx-FCD-002597, __ raise this NCR to record the following rooms where there minimum required length to meet Part M disabled has not been achieved: Female WC 1/420 (2030mm) Male WC 1/423 (2040mm)
| 02SL - Stations (LUL) | Cxxx-NCR-002389 | NCR | Installation and Testing of GSM Lightning Protection System without Accepted Design |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2018-07-13 | 2018-08-14 10:06 | 32 | 2018-06-07 13:34 | Electrical - Earthing & Bonding | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | GSM Lightning Protection System has been installed and tested without an accepted design. In addition, the (installed and tested) system has been modified as part of an interim proposition without adhering to the change control process.
| 02SL - Stations (LUL) | Cxxx-NCR-002390 | NCR | LULO - GSM - Lack of Samples and Benchmarks for External Cladding works |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-09-15 | 2019-02-12 10:39 | 150 | 2018-06-07 13:40 | Architectural - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Lack of progressive assuruance with no samples, and no benchmark document on eB. __ please provide definitive list of samples and benchmarks that are required Benchmarks - __ curtain wall __ cladding systems Proteus cladding systems Samples -
| 02SL - Stations (LUL) | Cxxx-NCR-002391 | NCR | GSM Building - Damages to Curtain wall panels |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2021-06-22 08:35 | 357 | 2018-06-12 16:09 | Architectural - Roofing & Exterior Treatment | 3500 |  | Damaged | Repair | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | Following remedials to the __ cladding on the North Elevation of the GSM building to remove non-compliant adhesive to the back of the panels, it is noted that the external face of the panels have become scratched from transporting the panels back and forth off-site to carry out the remedial.
| 02SL - Stations (LUL) | Cxxx-NCR-002392 | NCR | DSS PCC Panels Western Elevation Exposed Reinforcing |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-09-27 | 2018-10-03 12:41 | 6 | 2018-06-12 16:19 | Architectural - Finishes | 500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | The photos attached show exposed rebar to panels P50C PTN-33 and P50C PTN-34 on the DSS Western Elevation where the penetrations were cast for the lighting conduits.
| 02SL - Stations (LUL) | Cxxx-NCR-002393 | NCR | Control of Drawing Process Not being followed |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-08-21 | 2019-01-04 09:45 | 136 | 2018-06-22 13:36 | Civil - Civil Engineering General | 2000 |  | System Defect | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Following a recent Surveillance carried out on __ Roofing Works on the 4th/5th June 2018 a number of problems have been discovered. • eB Numbers are duplicated on the __/__ Drawing Register, sometimes with the same information, sometimes with different information • Incorrect eB numbers on the __/__ Drawing Register • Formatting issues on the __/__ Drawing Register - so not showing submission dates • Other subcontractor drawing numbers included in the __/__ Drawing Register • Status of drawings from BC to the __/__ Drawing Register don’t always match • Revisions of drawings from BC to the __/__ Drawing Register don’t always match • Drawings missing CC number on __/__ Drawing Register, so cannot find them on BC • Drawing numbers incorrectly labelled in current server folder • Drawing numbers not written with status or revision in current server folder • Drawings listed on the __/__ Drawing Register but missing from the current server folder • Missing status information from drawing numbers in current server folder • Placeholders on eB where drawings are on BC and code A
| 02SL - Stations (LUL) | Cxxx-NCR-002394 | NCR | Control of Drawings used on Site By __ |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-10-04 | 2019-02-27 14:19 | 146 | 2018-06-22 13:35 | Civil - Civil Engineering General | 1000 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | __ has been found to be using the drawings listed below on site at C rev that have not been sent to __ hence not discoverable on eB/BC on Wednesday 06/06/2018 . There is no Communication on BC from __ to __ with C rev Drawing Number __ Rev on Site eB Rev/Status BC Rev/Status DC Drawing register Rev/Status Cxxx-__M-A-DWG-D061_WS106-53942 C01 P03 - Code 1 P03 - Code A P03 - Code A Cxxx-__M-A-DWG-D061_WS106-53948 C01 P03 - Code 1 P03 - Code A P03 - Code A Cxxx-__M-A-DWG-D061_WS106-53949 C01 P03 - Code 1 P03 - Code A P03 - Code A Cxxx-__M-A-DWG-D061_WS106-54817 C01 P03 - Code 1 P03 - Code A P03 - Code A
| 02SL - Stations (LUL) | Cxxx-NCR-002395 | NCR | Installation of Incorrect Earthing and Bonding Cables DSS |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2018-07-23 | 2018-06-26 09:58 | -27 | 2018-06-13 09:36 | Electrical - Earthing & Bonding | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Not Defined | Completed |  | Cxxx-__M-E-XSK-D061_WS105-50060 – Sketch - Fan Room Level 3 , EB-D/3/776/1 and Cxxx-__M-E-XSK-D061_WS105-50069 – Sketch - TV MCC Level 5 , EB-D/5/761/1 have incorporated changes to the accepted design, which have been installed without following the change control process. Subsequently, __ have rejected the PTR and __ have had to re-install the correct size Earthing and Bonding Cables
| 02SL - Stations (LUL) | Cxxx-NCR-002396 | NCR | CHS - Stair Flight 3 Starter Bars in the Incorrect Location |  | Crossrail | PDP | WHI - Whitechapel Station (Central) |  | 2018-12-09 | 2018-07-09 07:49 | -153 | 2018-07-02 07:17 | Shafts - Shafts General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On flight 3 of CHS stairs the starter bars that project from the level 7 slab into the stairwaist have been installed incorrectly. They are approximately 300mm too far west. In order to install the stair reinforcement these bars have been cranked into a new position (see attached photos and sketches). There is reinforcement from the 125mm upstand to the half landing. This however leaves the bottom two steps (east of the up-stand) with no reinforcement. This NCR is replacement for Cxxx-NCR-001118, which was cancelled by mistake.
| 02SL - Stations (LUL) | Cxxx-NCR-002400 | NCR | Site Wide - Platform Tunnels BoH Doors QA - Not progressivly assured |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-08-31 | 2019-02-02 12:51 | 155 | 2018-06-21 08:12 | Architectural - Doors | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Lack of progressive assurance regarding Back of House doors in the Crossrail Platform Tunnels. Works were finished in March 2018 and yet to receive any redlines or QA records. Back of House Tunnel Areas, Plan, West Bound Platform Cxxx-__M-A-DDD-D061_WS106_Z-19368 Back of House Tunnel Areas, Plan, West Bound Platform Cxxx-__M-A-DDD-D061_WS106_Z-19369 Back of House Tunnel Areas, Plan, East Bound PlatformCxxx-__M-A-DDD-D061_WS106_Z-19370 Back of House Tunnel Areas, Plan, East Bound Platform Cxxx-__M-A-DDD-D061_WS106_Z-19371 Back of House Tunnel Areas, Elevations, West Bound Platform Cxxx-__M-A-DDD-D061_WS106_Z-19372 Back of House Tunnel areas., Elevations, West Bound Platform Cxxx-__M-A-DDD-D061_WS106_Z-19373 Back of House Tunnel Areas, Elevations, East Bound Platform Cxxx-__M-A-DDD-D061_WS106_Z-19374 Back of House Tunnel Area ., Elevation, East Bound Platform, Cxxx-__M-A-DDD-D061_WS106_Z-19375 The above drawings are yet to be redlined from works finished in March 2018 Yet to receive onsite QA for the same works. Only received UPE door installation. See attached. The above needs to be addressed and on eB, to allow progression of this package.
| 02SL - Stations (LUL) | Cxxx-NCR-002401 | NCR | Cxxx - DSS - Stainless Steel Panels |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-10-31 | 2018-11-08 12:04 | 8 | 2018-06-20 15:53 | Architectural - Walls | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | DSS Level 7`s stainless steel panels were stored poorly in a single pile. The edged corner panels were bearing the load of panels piled on top of the pack. It was also noted that the inner face of the top panel had been walked over with boot marks all over it.
| 02SL - Stations (LUL) | Cxxx-NCR-002402 | NCR | LULO Upper Concourse slab scabbling |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-09-30 | 2018-10-29 08:50 | 29 | 2018-06-21 06:21 | Structural Engineering - Concrete Member | 3000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __ have scabbled a section of the upper concourse RC slab to reduce the level for M&E CMS. This work was carried out without the approval of the stage F designer (Cxxx) or the CRL Field engineer team. There is no evidence that the ITP for reducing the slab level (Cxxx-__M-C-ITP-D061_WS106-53072 Rev 3.0) was adhered to.
| 02SL - Stations (LUL) | Cxxx-NCR-002404 | NCR | Energisation of Sub Main Cable C15, GSM DB6 and Hold off Circuits for OLBI Switchboard without an Accepted IRN |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2018-10-31 | 2018-09-16 09:15 | -45 | 2018-06-21 10:06 | Electrical - General | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Sub Main Cable C15, LUL/C/DB6 and Circuits 13L1, 13L2, 13L3 and 14L1, 14L2 and 14L3 energised in the GSM prior to submission and acceptance of associated Installation Release Notices (IRN). This is in contravention of the CRL Testing & Commissioning Process Overview for Stations, Portals & Shafts (CRL1-XRL-O7-GPS-CR001-50007 Rev 1.0) issued under Cxxx-PMI-00449 and the Contractor's own Testing & Commissioning Plan (Cxxx-__M-O3-GPS-D061-50001 Rev 5.0). Cxxx-NCR-002276 (GSM - E57 DNO / Intake Power Supply Energised without accepted IRN) Cxxx-NCR-002370 (LULO - GSM - Fire Alarm Panel Energised prior to IRN acceptance ) previously raised on this topic.
| 02SL - Stations (LUL) | Cxxx-NCR-002405 | NCR | LULO - Accomodation Block Cladding - Lack of samples |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-08-17 17:53 | 48 | 2018-06-22 14:49 | Architectural - General | 2000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | Lack of samples for the Accommodation Block Cladding - Proteus Cladding Shot Peened Rimex C1A, Spec reference EWS-305/306/307/309/313/314. See attachment for full details, highlighted 8116-006 Obtain CRL acceptance on the sample, and to submit the documentation to eB under Cxxx-__M-A-LRC-D061-50195
| 02SL - Stations (LUL) | Cxxx-NCR-002406 | NCR | Lift 9 Isolator Moved after IRN Sign off. |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-12-25 | 2018-07-19 10:30 | -159 | 2018-06-28 10:16 | Electrical - LV Equipment | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Installed Isolator for Lift control room 9 has been moved from original location, due to the current room layout and location of equipment installed, It is not practical and is conflicting with other equipment in the room.
| 02SL - Stations (LUL) | Cxxx-NCR-002407 | NCR | Installation of outgoing circuits for LPDB/2A & 2B |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-09-25 | 2018-06-29 13:55 | -88 | 2018-06-27 13:33 | Electrical - Power Distribution | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | During the installation of LPDB/2A & 2B P REV drawings were used that were not code one
| 02SL - Stations (LUL) | Cxxx-NCR-002408 | NCR | LULO - Accomodation Block - Cladding - Drawings not covered in a By Exception submission |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-03-15 | 2019-04-04 08:09 | 20 | 2018-06-28 13:13 | Architectural - General | 1000 |  | System Defect | Rework | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | The following F2 drawings have been used at P rev, and are not covered under a By Exception Cxxx-__M-A-DWG-D061_WS106-53684 Cxxx-__M-A-DWG-D061_WS106-53724 Cxxx-__M-A-DWG-D061_WS106-54557 The below drawings are covered under By Exceptions, but have since been uprevved and not covered Cxxx-__M-A-DWG-D061_WS106-53237 Cxxx-__M-A-DWG-D061_WS106-53540 Cxxx-__M-A-DWG-D061_WS106-53360 Cxxx-__M-A-DWG-D061_WS106-53361 Cxxx-__M-A-DWG-D061_WS106-53362 Cxxx-__M-A-DWG-D061_WS106-53364 Cxxx-__M-A-DWG-D061_WS106-53580 Cxxx-__M-A-DWG-D061_WS106-53581 Cxxx-__M-A-DWG-D061_WS106-53582 Cxxx-__M-A-DWG-D061_WS106-53583 Cxxx-__M-A-DWG-D061_WS106-53584 Cxxx-__M-A-DWG-D061_WS106-53685 Cxxx-__M-A-DWG-D061_WS106-53693 Cxxx-__M-A-DWG-D061_WS106-53694 Further to this some of the uprev to these drawings have come back at code 3. Please see attached table for full details
| 02SL - Stations (LUL) | Cxxx-NCR-002409 | NCR | CHS - Fire Detection Loops 2, 3, 4 - Installation to non approved drawings (Protec) |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-12-06 | 2018-09-06 10:56 | -91 | 2018-06-29 10:29 | Fire - Detection | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | Works were installed to P02 (Code 2) drawings what a By Exception in place. CRL Comments have been received and the drawings require updating and resubmitting at P03 for acceptance, allowing them to achieve IFC status. There have been subsequent changes on site that have not been agreed through the formal change control process. The issue was identified at IRN page turn stage when it was identified by __ that the test sheet records did not align themselves with the content of the P Rev drawing. The drawings in question are listed in the 3 IRNs linked to this NCR
| 02SL - Stations (LUL) | Cxxx-NCR-002411 | NCR | Electrical spreader box for Escalater equipment in room 4/171 level 4 DSS |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-10-01 | 2018-11-23 12:45 | 53 | 2018-07-03 09:07 | Electrical - Power Distribution | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | The Escalator supply for __ equipment is a duel fed A & B supply with the A supply coming from switch room 1 level 5 DSS 5/661 and the B supply coming from switch room 2 level 5 DSS and each supply is 2 x120mm SWA cables to the ATS ( automatic transfer switch ) located in the escalator equipment room. From this ATS is then 2 x 120 SWA cables which feed the __ escalator equipment
| 02SL - Stations (LUL) | Cxxx-NCR-002412 | NCR | CHS - Ships Ladder Plinth Step Level |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-11-08 | 2018-12-10 12:56 | 32 | 2018-07-03 10:37 | Architectural - General | 1800 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The lowering of paving slabs on the roof of CHS by 30/40mm has created an increase of 30/40mm in the first step up on to the first ships ladder step. All other ships ladder steps are equidistant from each other. This roof paving slab level was raised as an NCR to Crossrail and closed out via. Cxxx-NCR-002188. The ships ladders that this issue applies to are the two from level B to level C1 at Cambridge Heath Shaft. They are not in main walkways and maintenance access to level C1 will only be required on very rare occasions. The change will be captured via. this NCR and the NCR noted above within the ships ladder package redline drawings and as a residual risk in the A&M strategy. In reality, any operatives coming to the base of one of the ships ladders will hold onto the handrail on both sides prior to stepping up on to the ladder. The residual risk of the paving slab change in level to the plinth itself is deemed to be low and as such, Cxxx-NCR-002188 was closed out following a number of Crossrail queries being responded to by __.
| 02SL - Stations (LUL) | Cxxx-NCR-002413 | NCR | LULO - Concourse __ Bracket Manufacture - failure to implement BS EN 1090 (__) |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-12-10 | 2019-07-07 09:49 | 209 | 2018-07-03 14:54 | Structural Engineering - Steel Member | 5500 |  | Documentation and Records | Use As-Is | 3 (3-6k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | __ Brackets have been manufactured by __. When asked for the company's certification (in relation to W/I Clause 20.7) and relevant factory production controls (Weld Procedures and associated documents), it was stated that these were not in place.
| 02SL - Stations (LUL) | Cxxx-NCR-002414 | NCR | Cxxx - DSS - Level 7 PCC Panels |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-09-10 | 2018-10-16 08:02 | 36 | 2018-07-06 15:00 | Architectural - Walls | 30000 |  | Manufacturing Defect | Reject | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __ PCC panels delivered & installed have the following defects and their repair method: - Chamfer Lip: Increase the size of chamfer by 3mm (13mm) to eliminate the lip. - Chalk patches: Wash the affected areas with __. - Diamonds not aligned: Re-cast the panels to make all the diamond aligned - Bug holes: fill the bug holes
| 02SL - Stations (LUL) | Cxxx-NCR-002415 | NCR | Mist Suppression |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-08-28 | 2018-08-23 11:14 | -5 | 2018-07-05 12:58 | Mechanical - Piping | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | pipework tested before design is signed off
| 02SL - Stations (LUL) | Cxxx-NCR-002416 | NCR | Energisation of escalator equipment |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-10-31 | 2018-11-23 13:49 | 23 | 2018-07-06 12:56 | Electrical - Power Distribution | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | The escalator equipment has been powered up without an approved Code 1 IRN in place. A temporary spreader box has been fitted to progress commissioning ahead of the permanent solution ( bespoke IP55 spreader box )
| 02SL - Stations (LUL) | Cxxx-NCR-002417 | NCR | fabricating structural steelwork with weld documentation at a Code 3 Decal (__) |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2018-09-30 | 2018-09-20 12:18 | -10 | 2018-07-06 13:03 | Civil - Structural Engineering | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | A planned Crossrail Quality Surveillance was completed on 4th July 18 to look at offsite fabrication assurance associated with __ sub contract works. The following documentation was requested for WEC; ITP, WPS, WPQR, WPQC, FPC and RWC Certificate. On checking, it was found that the Weld Documentation submitted under Cxxx-__M-C-GPD-D061-50019 (Rev 1) for WEC was at a Code 3 Decal. A Code 3 Decal means ‘Not Accepted. Revise and resubmit. Work may not proceed’. Further to this, ITP Cxxx-__M-A-ITP-D061_WS106-50120 Rev 6 Code 1 Inspection Numbers 1.5 and 1.6 (Weld Documentation) are defined as a Hold Point for both __ and CRL as a Pre Construction Activity; this intervention had not been met. No CRL Acceptance of Weld Documentation existed.
| 02SL - Stations (LUL) | Cxxx-NCR-002418 | NCR | fabricating structural steelwork with weld documentation as Placeholder, and no ITP to capture assurance documentation (__) |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2018-12-07 | 2019-04-04 13:26 | 118 | 2018-07-06 13:05 | Civil - Structural Engineering | 1000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | A planned Crossrail Quality Surveillance was completed on 4th July 18 to look at offsite fabrication assurance associated with __ sub contract works. The following documentation was requested for __; ITP, WPS, WPQR, WPQC, FPC and RWC Certificate. __ provided eB number Cxxx-__M-C-GPD-D061-50020 as the submission for Weld Documentation; however on review it was found that Rev 1 was a ‘Placeholder’. In addition, no ITP is in place covering offsite fabrication and associate pre requisites, which the Weld Documentation would fall under. Works Information Part 20.8 requires the production of ITPs and demonstration of competence. No CRL Acceptance of Weld Documentation existed.
| 02SL - Stations (LUL) | Cxxx-NCR-002419 | NCR | fabricating structural steelwork with weld documentation not accepted by CRL, and the ITP to capture assurance documentation at a Code 3 Decal (__) |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2018-10-31 | 2019-04-04 13:37 | 155 | 2018-07-06 13:08 | Civil - Structural Engineering | 1000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | A planned Crossrail Quality Surveillance was completed on 4th July 18 to look at offsite fabrication assurance associated with __ sub contract works. The following documentation was requested for Safety Fabrications Ltd; ITP, WPS, WPQR, WPQC, FPC and RWC Certificate. __ provided eB number Cxxx-__M-A-LRC-D061_WS106-51007 for Offsite Fabrication Records for R12 Brackets; the Weld Documentation formed part of the submission. On checking it was found that this submission was at Rev 1 ‘Draft’ and ‘Not Approved’. No CRL Acceptance of Weld Documentation existed. Furthermore, the ITP for offsite fabrication Cxxx-__M-A-ITP-D061_WS106-50194 was at Rev 1 Code 3 Decal. A Code 3 Decal means ‘Not Accepted. Revise and resubmit. Work may not proceed’. Moreover, Inspection Numbers 3.2 and 3.3 (Weld Documentation) are defined as a Hold Point for both __ and CRL as a Pre Construction Activity; this intervention had not been met.
| 02SL - Stations (LUL) | Cxxx-NCR-002420 | NCR | LO - Additional holes drilled in the councourse Primary steel work |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-10-26 | 2018-10-18 09:55 | -8 | 2018-07-18 07:33 | Civil - Civil Engineering General | 1047 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | Please see attached marked up sketch. In a three locations on the concourse primary steel, holes were drilled in the incorrect location for the roof light brackets. On GL 11 east and west holes were drilled to close to the edge of the flange. On GL 12 east two holes were drilled to close together.
| 02SL - Stations (LUL) | Cxxx-NCR-002421 | NCR | fabricating structural steelwork with weld documentation as a Placeholder, and the ITP to capture assurance documentation at a Code 3 Decal (__) |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2018-10-31 | 2018-09-21 13:35 | -40 | 2018-07-06 13:11 | Civil - Structural Engineering | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | A planned Crossrail Quality Surveillance was completed on 4th July 18 to look at offsite fabrication assurance associated with __ sub contract works. The following documentation was requested for __; ITP, WPS, WPQR, WPQC, FPC and RWC Certificate. __ provided eB number Cxxx-__M-A-LRC-D061_WS106-51009 for Offsite Fabrication Records for Second Fix Packers and Posts; the Weld Documentation formed part of the submission. On checking it was found that this submission was a ‘Placeholder’ on eB. No CRL Acceptance of Weld Documentation existed. Furthermore, the ITP for offsite fabrication Cxxx-__M-A-ITP-D061_WS106-50195 was at Rev 1 Code 3 Decal. A Code 3 Decal means ‘Not Accepted. Revise and resubmit. Work may not proceed’. Moreover, Inspection Numbers 3.2 and 3.3 (Weld Documentation) are defined as a Hold Point for both __ and CRL as a Pre Construction Activity; this intervention had not been met.
| 02SL - Stations (LUL) | Cxxx-NCR-002422 | NCR | fabricating structural steelwork with weld documentation not submitted to CRL for acceptance, and no ITP to capture assurance documentation (__) |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2018-10-31 | 2018-09-21 13:37 | -40 | 2018-07-06 13:14 | Civil - Structural Engineering | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | A planned Crossrail Quality Surveillance was completed on 4th July 18 to look at offsite fabrication assurance associated with __ sub contract works. The following documentation was requested for __; ITP, WPS, WPQR, WPQC, FPC and RWC Certificate. No Weld Documentation had been received, as such could not be provided, and CRL acceptance could be demonstrated. In addition, no ITP is in place covering offsite fabrication and associate pre requisites, which the Weld Documentation would fall under. Works Information Part 20.8 requires the production of ITPs and demonstration of competence. No CRL Acceptance of Weld Documentation existed. WI Part 20.8 - The Contractor and his subcontractors and suppliers of any tier engaged in supplying, manufacturing, construction, installation, commissioning and testing or any other service connected with the works, shall maintain ITPs appropriate for the services they provide that are accepted by the Supervisor.
| 02SL - Stations (LUL) | Cxxx-NCR-002424 | NCR | fabricated structural steelwork with weld documentation not submitted to CRL for acceptance, and no ITP to capture assurance documentation (__) |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2018-12-07 | 2019-04-04 13:49 | 118 | 2018-07-06 13:26 | Civil - Structural Engineering | 1000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | A planned Crossrail Quality Surveillance was completed on 4th July 18 to look at offsite fabrication assurance associated with __ sub contract works. The following documentation was requested for __; ITP, WPS, WPQR, WPQC, FPC and RWC Certificate. No Weld Documentation had been received, as such could not be provided, and CRL acceptance could be demonstrated. In addition, no ITP is in place covering offsite fabrication and associate pre requisites, which the Weld Documentation would fall under. Works Information Part 20.8 requires the production of ITPs and demonstration of competence. No CRL Acceptance of Weld Documentation existed.
| 02SL - Stations (LUL) | Cxxx-NCR-002425 | NCR | Calculations and loadings (CAT check) not produced and submitted for the V Mesh Screen with fabrication complete (brackets) and progressing (posts) |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2018-10-12 | 2019-02-27 14:26 | 138 | 2018-07-06 13:31 | Civil - Structural Engineering | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | A planned Crossrail Quality Surveillance was completed on 4th July 18 to look at offsite fabrication assurance associated with __ sub contract works. The CAT design check was requested for the V Mesh Screen to confirm the weld outputs as part of the structural calculations against the Weld Documentation. On discussion, it was noted by __ that the CAT check was still in progress. At the time of the visit, the top and bottom brackets had been manufactured, whilst fabrication was underway for the posts. This puts the fabrication at risk should changes occur as part of the design check.
| 02SL - Stations (LUL) | Cxxx-NCR-002426 | NCR | DSS FDDB1 & FDDB2 Distribution boards |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-10-08 | 2018-07-11 13:02 | -89 | 2018-07-10 13:42 | Electrical - LV Equipment | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | During the installation of FDDB 1 & FDDB 2 P REV drawings were used that were not code one
| 02SL - Stations (LUL) | Cxxx-NCR-002427 | NCR | LULO - __ - HCDL EB, HCDL WB and Area 7 no thickness checksheets |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-09-07 | 2018-11-30 08:33 | 84 | 2018-07-09 16:07 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Following a review of the checksheets for the __ it has been identified that there are no thickness check sheets QCR04 for the HCDL EB, HCDL WB or Area 7. See attached marked up drawing showing locations.
| 02SL - Stations (LUL) | Cxxx-NCR-002428 | NCR | DSS Drainage-Non compliance with Control of Drawings Process Cxxx-__M-O4-GPS-D061-50002 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-10-26 | 2018-10-24 10:16 | -2 | 2018-07-11 13:54 | Information Management - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | The DSS ground drainage drawings captured in RIR Cxxx-__M-C-LRG-D061-50007 (2288) are currently at revision C01. The RIR for P02 Cxxx-__M-C-LRG-D061-50007 (227) was cancelled and the RIR for P01 RIR Cxxx-__M-C-LRG-D061-50007 (78) was code 3. This is applicable to the below drawings; Cxxx-__M-P-DDA-D061_WS105_2-10279 Cxxx-__M-P-DDA-D061_WS105_2-10280 Cxxx-__M-P-DDA-D061_WS105_2-10281 Cxxx-__M-P-DDB-D061_WS105_2-10300 Cxxx-__M-P-DDD-D061_WS105_2-12501 Cxxx-__M-P-DDD-D061_WS105_2-12502 Cxxx-__M-P-DDD-D061_WS105_2-12503 Cxxx-__M-P-DDD-D061_WS105_2-12504 Cxxx-__M-P-DDD-D061_WS105_2-12505 Cxxx-__M-P-DDD-D061_WS105_2-12506 Cxxx-__M-P-DDJ-D061_WS105_2-10200
| 02SL - Stations (LUL) | Cxxx-NCR-002429 | NCR | LULO- DC8 and 9 concrete plinths |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-09-13 | 2019-01-21 12:31 | 130 | 2018-07-12 09:51 | Architectural - General | 2200 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Onsite it was discovered that the baseplates of the fabricated steel columns for DC8 and 9 did not fully sit on the constructed concrete plinth. The baseplates at the corner of each of the comms rooms and at the doorways were a width of 180mm, whereas the top of the plinth was only 125mm. Therefore due to the make up of the baseplate, the fixing points for the anchor bolts overhung the plinth.
| 02SL - Stations (LUL) | Cxxx-NCR-002430 | NCR | LULO GSM - FF&E Installation |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-08-25 | 2018-11-14 09:30 | 81 | 2018-07-16 16:24 | Architectural - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Cxxx-__M-A-TSC-D061_WS106-50001 FF&E Schedule revision 3.0, was last submitted to eB on 01/06/2017 and has been superseded through various revisions and workshops, email exchanges etc. between BH / __ / LU Premises / CRL / SWIP. Revision 3.0 is now very much outdated, and a revised schedule has still not been issued as products, equipment and who is supplying (__ or SWIP) is still very fluid and subject to change. The schedule has been keep as a live document with __ and updated regularly by __. As there have been a lot of late changes, this has not allowed __ to finalise the schedule and submit revision 4.0, or provide all MCRs for __ supplied items in advance of the works being installed. Due to time pressures with handover, __ have proceeded with procurement and installation of the following items for which MCRs have not been raised: - Clocks - Fire Extinguishers - Kitchen worktop and sinks units - Cooker hoods - Kitchen wall cupboards In addition to the above, there are items which are yet to be agreed who is supplying; for instance eye wash and first aid stations.
| 02SL - Stations (LUL) | Cxxx-NCR-002431 | NCR | CHS DB'S Installation to P rev drawings. |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-09-15 | 2018-07-18 12:17 | -59 | 2018-07-17 15:49 | Electrical - Power Distribution | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | __ Have installed electrical circuits in the cambridge heath shaft to P Rev Drawings due to time scale on approval for updated drawings.
| 02SL - Stations (LUL) | Cxxx-NCR-002432 | NCR | CRL platforms- Botom of escalator paving out of position |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-10-23 | 2018-09-04 08:02 | -49 | 2018-07-25 10:59 | Architectural - Flooring | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Due to error in setting out/installation paving at the bottom of the Escalator shitfed/rotated by approximately 180mm towards north
| 02SL - Stations (LUL) | Cxxx-NCR-002433 | NCR | LULO - Stair 25 - Missing Concrete Cube Paperwork |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-09-21 | 2018-10-19 15:15 | 28 | 2018-07-18 07:57 | Civil - Civil Engineering General | 1200 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Missing concrete cube paperwork for the Stair 25 civils works. Stair 25 3rd Lift, upstand Walls on S25 1st and 2nd Lift & intermediate level slab. UKAS record number CW2056
| 02SL - Stations (LUL) | Cxxx-NCR-002434 | NCR | __DB1/5L1,1L1,2L1 CHS |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-10-08 | 2018-08-14 10:18 | -55 | 2018-07-20 10:46 | Electrical - LV Equipment | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Due to __DB1 being energised for commissioning of Cxxx comms equipment in cer2 we have missed the inspection request process for the newly installed circuits 5L1,1L1,2L1 which was installed and dead tested over a bank holiday weekend __ supervision have self assured the installation but due to the short duration of the shutdown did not issue a request to CRL. we would like to energise the circuits in order to commission the DOO cameras and lu connect systems.
| 02SL - Stations (LUL) | Cxxx-NCR-002435 | NCR | Ristricted Access to ATS LPDB23B SOR Plant Room |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-10-23 | 2018-10-05 10:43 | -18 | 2018-09-13 15:26 | Electrical - LV Equipment | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Electrical install has been completed in SOR plant room with CMS feeding Distribution boards and ATS panels signed off. Mechanical at a later date have installed pump sets and tanks much larger than expected, the frame work for these now restrict access for maintenance to the ATS for LPDB23B.
| 02SL - Stations (LUL) | Cxxx-NCR-002436 | NCR | Installation of CMS - Upper concourse Floor trunking. |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-11-20 | 2018-08-06 11:04 | -106 | 2018-07-23 07:57 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Installation of CMS - Floor trunking on the Upper concourse under a P revision drawing not covered under the By Exception process.
| 02SL - Stations (LUL) | Cxxx-NCR-002437 | NCR | LULO - __ - Hold & Witness Points |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2021-01-30 10:20 | 214 | 2018-07-19 15:35 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | During the application of __ to the LULO Steelwork the Hold Points and Witness Points were not adhered to with Crossrail. See summary below detailing the % of areas/checks that do not have Crossrail signatures or a record of IRF's being formally sent. Following discussions with __ Engineers it has been confirmed that Crossrail did attend informal inspections on both day shifts and night shifts however these were not recorded. Area 1 : D3-224 (handover check sheets) – 50% QRC-03 (mesh)– 100% QRC-04(__ thickness) – 100% QRC-05 (primer thickness) - 100% Area 2: D3-224(handover check sheets) – 30% QRC-03 (mesh)– 100% QRC-04(__ thickness) – 100% QRC-05(primer thickness) - 100% Area 4&5: D3-224 (handover check sheets) – 100% QRC-03 (mesh)– 100% QRC-04(__ thickness) – 100% QRC-05(primer thickness) - 100% Area 6: D3-224(handover check sheets) – 100% QRC-03 (mesh)– 100% QRC-04(__ thickness) – 100% QRC-05(primer thickness) -100% Area ESS: D3-224 (handover check sheets) – 100% QRC-03 (mesh)– 100% QRC-04 (__ thickness) – 100% QRC-05(primer thickness) -100% Area 8: D3-224 (handover check sheets) – 50% QRC-03 (mesh)– 100% QRC-04(__ thickness) – 100% QRC-05 (primer thickness) - 100% HCDL EB & WB D3-224 (handover check sheets) – 100% QRC-03 (mesh)– 100% QRC-04(__ thickness) – 100% QRC-05(primer thickness) - 100%
| 02SL - Stations (LUL) | Cxxx-NCR-002438 | NCR | R12 BAL 123 Incorrectly Fabricated |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-10-28 | 2018-11-16 20:29 | 19 | 2018-07-20 09:34 | Architectural - Balustrade | 4500 |  | Manufacturing Defect | Repair | 3 (3-6k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | The R12 BAL 123 has been discovered to be fabricated incorrectly. The fabrication drawings call for 50mm fillet welds in all locations. After an inspection it was discovered that these welds varied from 37mm to 50mm.
| 02SL - Stations (LUL) | Cxxx-NCR-002439 | NCR | Accidental drilling through concourse primary steel work fin plate welds |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-12-17 | 2018-09-21 14:01 | -87 | 2018-07-20 10:52 | Civil - Civil Engineering General | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please refer to attached sketches In order to fit the roof light brackets, holes need to be drilled in the top flange of the transverse beam to attach the roof light brackets. In 10 locations in R10, the weld for the fin plate that attaches the longitudinal beam to the transverse arch beam has been drilled through. A 14mm hole has been drilled either fully through the weld or partially damaging it. The contractor will not be able to install a bolt in the design location and an additional hole will need to be drilled to take the roof light bracket.
| 02SL - Stations (LUL) | Cxxx-NCR-002440 | NCR | Insufficient Cable Tray Spare Capacity |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-08-08 | 2018-08-10 14:23 | 2 | 2018-07-25 11:11 | Electrical - Cable Management | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | A Cable Tray passing through the floor from the invert level to level 7 has been found to have less than 25% spare capacity. The builderswork hole through the slab was too small to allow a larger Cable Tray to be installed
| 02SL - Stations (LUL) | Cxxx-NCR-002441 | NCR | mist suppression |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-09-02 | 2018-08-24 08:24 | -9 | 2018-07-24 13:58 | Mechanical - Piping | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | a hold point on an ITP was passed
| 02SL - Stations (LUL) | Cxxx-NCR-002442 | NCR | LULO GSM - level 2 Mech Room louvre wind post head restraints and fire roller shutter spec |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-11-02 | 2019-07-25 09:35 | 265 | 2018-07-25 09:28 | Structural Engineering - Load Bearing Walls | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The below relates to GSM Building level 2 Mech Room louvre wind posts: - The F2 designer for the GSM Cladding Package has not met the F1 design intent for the louvre wind posts, which should have included 3no. wind posts extending full height with heading restraint connections. Both the outer posts and the corner post should have head restraint connections. - The above head restraint connections provide rigidity to the blockwork wall constructed above the louvre lintel, and the future installation of the wall mounted fire roller shutter. The F2 designer did not account for the above loadings in their initial F2 calculations, and only for the weight of the louvres themselves. - The Architectural Specification for fire roller shutter type DRS-452 specifies a product (Guardian Industrial Doors, FR-INS 240) which does not meet the performance requirements of the specification; 60 mins integrity and insulation. Instead, the specified product only provides 7 mins insulation.
| 02SL - Stations (LUL) | Cxxx-NCR-002443 | NCR | GSM - CER4 isolator cables installed without a design |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-11-12 | 2018-09-18 11:28 | -55 | 2018-09-13 15:35 | Electrical - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | A new isolate was required to be installed in GSM CER 4. Works proceeded without a confirmed design or PTR response from __ in place.
| 02SL - Stations (LUL) | Cxxx-NCR-002444 | NCR | LPDB3/A & B incorrect cables installed |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-09-24 | 2018-08-14 10:31 | -41 | 2018-07-26 16:40 | Electrical - Power Distribution | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | __ have installed the wrong cable type for 2 circuits - LPDB3/A/8L123 & 9L123 they are to be removed from breakers and put in connector blocks till we have access to c650 areas to install a new cable ( 10mm singles class2) cable calculation by baker hicks NCR RAISED
| 02SL - Stations (LUL) | Cxxx-NCR-002445 | NCR | GSM - Installation of cables without approved design |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-11-28 | 2018-08-09 14:04 | -111 | 2018-07-31 15:53 | Electrical - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Cables installed from DNO/DB6 19L1 feeding Dado circuit in room 1/291
| 02SL - Stations (LUL) | Cxxx-NCR-002446 | NCR | DSS DB,s Installation to P rev drawings |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-10-30 | 2018-08-14 10:27 | -77 | 2018-08-01 11:04 | Electrical - Power Distribution | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | __ have installed electrical circuits in the Durwood Street shaft to P rev drawings due to the time scale on approval foe updated drawings
| 02SL - Stations (LUL) | Cxxx-NCR-002447 | NCR | Fan removal is obstructed in Level A DSS by electrical isolators |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2018-09-10 | 2018-09-06 10:46 | -4 | 2018-08-01 08:05 | Electrical - Electrical Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The current A&M strategy for removing ventilation fans on DSS level A is through the structural fan supports and egressed via the external Louvre. Electrical isolators a have been installed on the fan support frame impeding the route of the fans for replacement.
| 02SL - Stations (LUL) | Cxxx-NCR-002448 | NCR | CHS & DSS - Louvre Steelwork Galvanised Thickness |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-10-31 | 2018-10-24 11:22 | -7 | 2018-08-07 11:16 | Civil - Civil Engineering General | 2000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | The architectural specification (Cxxx-__M-A-RSP-D061-50079) states that in any event, the galvanised 'average coating thickness shall be a minimum of 140 microns' (JZ30.4403 - part j - iv). The value of 140 microns is also a parameter in the __ off-site fabrication ITP for steelwork - see attached. The louvre steelwork has been installed and off-site galvanised thickness records show that some of the steelwork has a galvanised thickness less than 140 microns. In summary, of 45 average coating thickness tests for the CHS & DSS louvre support steelwork; 19 no. are above 140 microns, 22 no. are between 85-140 microns and 4 no. are below 85 microns. The lowest average galvanised thickness coating value is 73.6 microns. The galvanised thickness reports for CHS & DSS louvres are attached.
| 02SL - Stations (LUL) | Cxxx-NCR-002449 | NCR | Installation of Mist Suppression CMS with out design drawings F2 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-09-18 | 2018-08-20 10:23 | -29 | 2018-08-09 12:52 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | F2 CMS Installation under taken with design drawings from baker hicks.
| 02SL - Stations (LUL) | Cxxx-NCR-002451 | NCR | Stair 25 - missing concrete cubes for Southern slab through retaining wall |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-09-24 | 2018-09-20 17:20 | -4 | 2018-08-15 11:37 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | 4 No. concrete testing cubes for the Southern roof slab pour have been misplaced.
| 02SL - Stations (LUL) | Cxxx-NCR-002452 | NCR | Damaged Distribution Board - E51 |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2018-09-25 | 2020-01-11 15:56 | 473 | 2018-08-16 10:58 | Electrical - LV Equipment | 4000 |  | Damaged | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | A damaged distribution board found previously (~ 4 months ago) has been stored in E51 in preparation to be installed and commissioned as a new asset. E51 should not be used as a storage facility. The DB should be removed / replaced / refurbished as per below JA.5600 CORROSION PROTECTION JA.5601 General a) Ensure that protective measures are taken to avoid any corrosion or any deleterious effects caused by manufacturing, finishing, transportation, storage and installation of materials. JA.6305 Protective Measures a) Provide full details of the protective measures proposed for implementation at each of the following stages: i) Manufacture and packaging of goods and materials at off-site locations. ii) Shipment to site and unloading. iii) Storage on site and movement to point of installation or construction. iv) Installation/ construction. v) Completion to handover. JA.6502 Materials & Equipment b) Ensure all plant, equipment and materials are protected against damage or adverse weather conditions until practical completion. Any plant equipment or materials that have been subjected to damage, incorrect storage or incorrect installation shall be replaced.
| 02SL - Stations (LUL) | Cxxx-NCR-002453 | NCR | LULO - Accommodation Block Mortar Cube Results |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-11-30 | 2019-10-13 11:53 | 317 | 2018-08-16 10:44 | Architectural - Brickworks/Blockworks | 1200 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Mortar Cube results CW2044 for the Accommodation Block taken on 28/11/2017 have failed to reach the required 28 Day Strength
| 02SL - Stations (LUL) | Cxxx-NCR-002454 | NCR | DSS level 7 SR3 7-663 room - extra tray to keep 25% spare capacity |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-11-15 | 2018-09-14 08:59 | -62 | 2018-08-17 08:50 | Electrical - Cable Management | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | A 100mm cable tray was installed in the SR3 7/633 room on level 7 DSS to carry supply cable to Distribution Board LPDB3/A and also to carry earth cables, the size of the cable tray was as per design
| 02SL - Stations (LUL) | Cxxx-NCR-002455 | NCR | Alterations to Signed off CMS - High Level trunking on the Lower Concourse. |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-10-21 | 2019-01-23 09:16 | 94 | 2018-09-11 09:32 | Electrical - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Signed off Installation has to be altered. Lack of coordination between __ and 3rd parties has resulted in the F1 intent for the high level CMS being altered to compensate for any clashes with the architectural cladding.
| 02SL - Stations (LUL) | Cxxx-NCR-002456 | NCR | Sitewide- Installed __ non-compliant |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-01-31 | 2018-12-12 09:41 | -50 | 2018-08-23 11:46 | Architectural - Flooring | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | All __ finishes (Architectural specification tags FL-501, FL-502, FL-504) installed to date in following locations: DSS: Stair 1, Stair 2, Stair 4, Stair 5, Stair 9, Stair 11, Stair 12, Stair 55 CHS: Stair 40, Stair 41, LULO: Stair 27 (TBC), Stair 52 Are non-conformant with specification. Supplied and Installed VulcaGRIP external range product is Class 3 fire rated (As per BS 476 part 7)
| 02SL - Stations (LUL) | Cxxx-NCR-002457 | NCR | Energizing OLB1-2 Interface unit without CMS and approved 13A power supply design. |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-12-02 | 2018-11-16 10:27 | -16 | 2018-09-13 15:40 | Electrical - Switchgear | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | We had energized OLB1-2 interface unit without an approved design supporting the CMS and 13A power supply to the Scada interface unit.
| 02SL - Stations (LUL) | Cxxx-NCR-002458 | NCR | GSM Building - Damages to cladding |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2021-06-30 20:44 | 365 | 2018-09-06 16:00 | Architectural - Roofing & Exterior Treatment | 8000 |  | Damaged | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The __ cladding panels installed across the East, South and West elevations of the GSM show signs of damage and misalignment. Photos have been gathered to record each incidence of damage and misalignment requiring repair/re-work by __.
| 02SL - Stations (LUL) | Cxxx-NCR-002459 | NCR | __ V-MESH Panels - workmanship |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-10-31 | 2019-03-29 11:32 | 149 | 2018-08-29 11:35 | Architectural - General | 58000 |  | Workmanship | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __ Fabricated V-MESH Panels rejected by __ under NCR Number: NCR23 raised 29.08.2018. V-MESH Panels for poor workmanship issues... 1. Continuity and Stop/start porosity of welds to the frames 2. Spot weld cracked 3. Sharp points left on raking cut panels 4. Mesh not clamped tight to frames 5. Side of panel not welded NOTES: __ visited __ Logistic Hub at Barking (28.08.2018) and requested that the panels be returned to their works for a complete review/evaluation of each panel (this will be fully documented and provided). Any discrepancy's will be recorded and repaired inconjuction with the requirements of the PO and CRL Standards. This will include (but not limited to) a Visual Inspection of welds by __ UKAS Accredited Inspection provided SIG c/w a formal report. __/__ to be given the opportunity to visit the fabrication yard Huntingdon to inspect prior to despatch.
| 02SL - Stations (LUL) | Cxxx-NCR-002460 | NCR | Scratches to HCDL upper canopy fascia panels |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2021-02-26 17:16 | 241 | 2018-09-06 08:59 | Architectural - Roofing & Exterior Treatment | 4500 |  | Damaged | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | During an inspection with CRL held on 30.08.2018, various cosmetic defects (scratches and minor dents) were identified on the HCDL upper canopy fascia panels. These panels are powder coated. To fully eliminate these defects would require removal of the panels for off-site re-coating by the manufacturer. On-site rectification is possible using the methodology detailed in the Interpon D Approved Applicators Manual for Aluminium panels.
| 02SL - Stations (LUL) | Cxxx-NCR-002461 | NCR | LULO - Accomodation Block - Unapproved Sketches - Fire Stopping |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-02-28 | 2019-09-19 10:06 | 203 | 2018-09-07 10:47 | Architectural - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Following on from a surveillance on the Accomodation Block Fire Stopping it became apparent 13 sketches from __ have not been communicated to CRL via eB for approval. The drawings also include details from the partition works carried out by __. Full list of sketches attached.
| 02SL - Stations (LUL) | Cxxx-NCR-002462 | NCR | MIST SUPPRESSION |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-10-15 | 2018-09-11 12:51 | -34 | 2018-09-05 14:56 | Mechanical - Mechanical Engineering General | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | NO APPROVED DESIGN BEFORE INSTALLATION STARTED
| 02SL - Stations (LUL) | Cxxx-NCR-002463 | NCR | mist suppression |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-10-15 | 2018-09-11 09:19 | -34 | 2018-09-05 15:14 | Mechanical - Mechanical Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | drawings not approved before install commenced
| 02SL - Stations (LUL) | Cxxx-NCR-002464 | NCR | mist suppression |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-10-15 | 2018-09-11 09:23 | -34 | 2018-09-05 15:19 | Mechanical - Mechanical Engineering General | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | mechanical pipework pressure tested with out an approved ITP in place
| 02SL - Stations (LUL) | Cxxx-NCR-002465 | NCR | mist suppression |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-10-15 | 2018-09-11 09:26 | -34 | 2018-09-05 15:29 | Mechanical - Mechanical Engineering General | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | pre commissioning has taken place before IRN was approved
| 02SL - Stations (LUL) | Cxxx-NCR-002466 | NCR | DSS escalator equipment room CMS changes |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-12-05 | 2018-09-24 10:46 | -72 | 2018-09-06 14:16 | Electrical - Cable Management | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | A lot of extra CMS has had to be installed for supplies to escalator and associated equipment which meant other items such as lights have had to be relocated slightly
| 02SL - Stations (LUL) | Cxxx-NCR-002467 | NCR | HCDL upper canopy gutter outflows installed contrary to F1 intent |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-10-17 | 2019-02-11 11:25 | 117 | 2018-09-07 15:10 | Architectural - Roofing & Exterior Treatment | 9500 |  | Design | Rework | 2 (6-60k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The HCDL upper canopy gutter outflow positions installed by __ do not match the positions specified on the F1 intent drawing(s) ending A-10253 and 1-10253. __'s F2 drawings ending 54126 and 54124 faintly show gutter outflow positions which were likely missed by __ in their review of these drawings. The gutter downpipe arrangement requires the outflows to be positioned in line with the primary steel columns (as achieved by the F1 design).
| 02SL - Stations (LUL) | Cxxx-NCR-002468 | NCR | HCDL upper canopy fascia levels - East edge |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-11-30 | 2018-11-02 15:14 | -28 | 2018-09-10 14:54 | Architectural - Roofing & Exterior Treatment | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | The upper canopy fascia levels across its eastern edge (above the Accommodation Blocks) were agreed and confirmed to __ in Cxxx-__-00225-MCC-285. However, the fascia panels have not been installed to these levels. The result of this is that the ceilings installer (__), whose works can be adjusted more easily than the fascia panels (which would require re-fabrication) has had to undertake rework in order to make good the interface between the fascia and ceiling.
| 02SL - Stations (LUL) | Cxxx-NCR-002469 | NCR | Stair 24 BAL 112 Incorrect Drilling |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-12-05 | 2018-12-17 17:34 | 12 | 2018-09-20 06:39 | Architectural - Balustrade | 1200 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | It has been identified that 4 no. 16mm holes have been drilled in the incorrect place on the North stringer of Stair 24. The holes are circa 8mm out of position.
| 02SL - Stations (LUL) | Cxxx-NCR-002471 | NCR | THC - Mains Schematic Diagram of LVAC Switchboard LVSB/A not C status |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-12-06 | 2018-10-04 09:11 | -63 | 2018-09-17 15:11 | Electrical - LV Equipment | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | Subcontractor / specialist manufacture has delivered and installed LVSB/A switchboard without code A drawings from designer and C rev drawing from Client; Cxxx-__M-E-DWG-D061_WS106-50309 - Drawing Pack - Ticket Hall & Concourse Mains Schematic Diagram of LVAC Switchboard LVSB/A . The subcontractors P01 drawing was issued to designer and stamped with C comments to address, this drawing was issued to CRL on RIR 2353 31/08/2018 and is currently un-answered. Note: C Stamp from design is to add 'Ref doc'. The subcontractor incorrectly produced a C01 drawing that was not issued on eB, this drawing was then used to SAT the LVSB/A switch board
| 02SL - Stations (LUL) | Cxxx-NCR-002472 | NCR | THC earthing Installation to P rev drawing |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-12-02 | 2019-02-14 12:38 | 74 | 2018-09-13 15:05 | Electrical - Earthing & Bonding | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | __ have installed earth cables to Cxxx-__M-E-DDE-D061_WS106_Z-300941 P10 Rev Drawings due to time scale on approval for updated C-rev. P10 is on eB and labelled as "Issued for Construction" but has not been issued on RIR register. P09 has been issued on RIR 2166 and is Code 1. C02 in place and the changes on P09 / P10 are due to C6xx requirements.
| 02SL - Stations (LUL) | Cxxx-NCR-002473 | NCR | GSM - Cabling installed without approved design to VRF and BMS |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-01-25 | 2018-10-04 09:18 | -113 | 2018-09-27 08:44 | Electrical - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | An additional circuit has been requested to the __ VRF controller in the GSM. Also an additional circuit to the BMS Black Pear Controller. Neither of these circuits have a signed off approved design. FCD's have been raised for each of these circuits, but not closed.
| 02SL - Stations (LUL) | Cxxx-NCR-002474 | NCR | CHS - Sealing Level 1 Riser 2 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-06-03 | 2019-07-01 08:43 | 28 | 2018-09-17 09:27 | Civil - Civil Engineering General | 5500 |  | Design | Rework | 3 (3-6k) | Complete | Management Problem - Other | Completed |  | At Cambridge Heath Shaft, there is a void in riser 2 level 1 meaning that the room isn’t completely sealed. This is the interface between the blockwork wall and the insitu stairs up to level A. The model shows that the stairs are to be casted around the column which isn’t what’s been built on site.
| 02SL - Stations (LUL) | Cxxx-NCR-002475 | NCR | CHS - Cantilever Beam Concrete Break |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-11-16 | 2019-04-08 16:22 | 143 | 2018-09-17 16:13 | Civil - Civil Engineering General | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following the tightening of a beam to beam connection on the North-East corner of Cambridge Heath Shaft, the concrete corbel adjacent to the connection has cracked and concrete pieces have broken away from it. The design for the steel to corbel connection at this location is for two no. __ bar anchors. At the time of the tightening activity, only one of these fixings was installed at this RC corbel connection. The tightening of the beam to beam connection applied a lateral load to the single fixing which has bent the __ bar anchor and caused cracking of the concrete and in turn concrete breaking off from the corbel RC structure - a detailed view of this can be seen in the 'corbel concrete damage' attachment. The __ bar anchor has now been damaged along with the concrete surround around it and the concrete damage is also present at the location of the second __ bar anchor in this location. This cantilever beam (no. 5) was cast smaller than the other cantilever beams around Cambridge Heath Shaft as per Cxxx-NCR-001620 (attached with supporting documentation). The reinforcement detail approved by TGP is contained within the email attachment to this NCR - with links at 150mm centres. The concrete cover to this link on site has been measured to be 55mm. In addition to cantilever beam no. 5, cantilever beam no. 1 is showing signs of cracking at one of the corbel fixing locations - see additional photos. The location of corbel numbers 1 & 5 is on the North elevation as per drawing number *50519* attached. All photos are attached.
| 02SL - Stations (LUL) | Cxxx-NCR-002477 | NCR | LULO Lower Concourse R10N - Incline Glazing Lower Brackets Drilled Holes Clash |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-11-04 | 2018-10-24 17:10 | -11 | 2018-09-25 08:42 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | It has come to the Contractors attention that the pre-drilled and tapped holes at GL 11-12 East & GL 12-13 East for the R10N Incline __ glass facade base brackets have been drilled in the incorrect position. See attached "LULO Lower Concourse R10N - Incline Glazing Lower Brackets Drilled Holes Clash Report.pdf" which details the clash for both areas
| 02SL - Stations (LUL) | Cxxx-NCR-002478 | NCR | LULO Lower Concourse R10N - Vertical Glazing Design Clashes |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-11-20 | 2019-06-13 07:53 | 205 | 2018-09-27 10:14 | Civil - Civil Engineering General | 2000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | __'s Sub-Contractor __ has procured and manufactured __ frames in R10N for the vertical glazed facade, prior to design acceptance. This includes the brackets, frames, glass, and ancillary materials. Subsequently, due to design processes not followed, there are a number of clashes with the as-built structure which had not been coordinated in the design, as detailed below: In a number of locations, the design for the vertical glazing clashes with the primary structure connecting plates and bolts. As a result, only 3 of 10 bays are deemed suitable for installation. In the 7 remaining bays, a number of adaptions will be needed to be made to the frames and brackets so that they clear the bolts. These will be designed such that the glazed facade remains it's structural, blast, and fire integrity.
| 02SL - Stations (LUL) | Cxxx-NCR-002479 | NCR | LULO Lower Concourse R12 - Gutter clashes |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-11-17 | 2019-10-08 10:43 | 325 | 2018-10-08 13:51 | Architectural - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | It has been identified that the gutters installed on the R12 roof are larger than those on the design for the wrightstyle/cladding. It has also been identified that these have not been installed at the design height, nor the incline required (16 degrees), this is due to the lack of co-ordination between __’s design and the as-built steel structure. See attached the clash report PDF, which shows the worst case location of the gutter.
| 02SL - Stations (LUL) | Cxxx-NCR-002480 | NCR | THC - Panel Install - Switchboard-LVSBA Damaged Multimeter Compartment F26. |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-12-03 | 2018-10-29 14:30 | -35 | 2018-10-24 08:19 | Electrical - LV Equipment | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | failure to protect switch gear in LV A & B Switch rooms has resulted in damage to Signed off Switch gear.
| 02SL - Stations (LUL) | Cxxx-NCR-002481 | NCR | DSS - Escalator iNCLINE Advertising CMS routes |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-01-18 | 2019-02-13 14:48 | 26 | 2018-09-20 12:45 | Electrical - Cable Management | 40000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Other | Completed |  | CMS for the Advertising installed in the Escalator area supported from the truss
| 02SL - Stations (LUL) | Cxxx-NCR-002482 | NCR | DSS roof SME the use of Prev drawings |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-10-31 | 2018-10-29 14:36 | -2 | 2018-09-21 13:32 | Electrical - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | We are installing lighting and power on the roof SME to P rev drawings which are not code 1
| 02SL - Stations (LUL) | Cxxx-NCR-002483 | NCR | LULO GSM and Accommodation Blocks - __ Firestopping Detail |  | Contr | VIN | WHI - Whitechapel Station (Central) |  | 2019-02-08 | 2019-02-27 14:31 | 19 | 2018-09-21 16:02 | Fire - Compartmentation | 36500 |  | Design | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Fire stopping has been installed through the GSM and Accommodation blocks in accordance with the details submitted via FCD-2544. When collating the information for passive fire assurance to be issued to CRL & CEG in August 2018, the manufacturer’s confirmation of the __ fire stopping ‘overboarding’ detail was requested. However, the detail has no specific manufacturers guidance, only the product assurance. The original argument that the Duraline board (an approved material) was being used in the same manner as it is in a partition (an approved arrangement), was not accepted due to the joints between abutting boards (ie along the penetrating service line) not being backed by metal stud. CEG therefore rejected the detail.
| 02SL - Stations (LUL) | Cxxx-NCR-002484 | NCR | LULO - Concourse Link Bridge - DSS Crossover - Fabrication Error |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-11-03 | 2018-11-25 18:25 | 22 | 2018-09-24 15:58 | Structural Engineering - Steel Member | 1000 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | __ have fabricated and installed the Concourse Link Bridge - E-G/5-5.2 - DSS Crossover. However the north eastern column has been fabricated with existing holes in the wrong location (wrong side of the bottom plate).
| 02SL - Stations (LUL) | Cxxx-NCR-002486 | NCR | Emergency Lighting Levels GSM |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-05-26 14:30 | -35 | 2018-09-27 07:44 | Electrical - Lighting | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | LUX Levels in Room 1/333 Male Locker room failed to meet the minimum requirement of 15lux when tested.
| 02SL - Stations (LUL) | Cxxx-NCR-002487 | NCR | LULO - THC EL UPS 5 - P Rev Drawings |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-02-12 16:07 | -139 | 2018-10-15 14:16 | Electrical - Power Generation | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | NCR raised due to installation to unapproved drawings. __ to issue drawings to CRL for approval. due to programme requirements installation had to proceed.
| 02SL - Stations (LUL) | Cxxx-NCR-002488 | NCR | Pilkington Plyglass No: Glazing Units (# 42, 43, 51 & 52) |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-12-27 | 2019-02-02 13:41 | 37 | 2018-09-28 10:01 | Architectural - Glazing | 6000 |  | Manufacturing Defect | Reject | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Roof light glazing units have been manufactured incorrectly for 4 no roof lights (42,43,51 and 52) The 12no number glazing units (3 per rooflight) have been installed in-situ on site, but it has been discovered after installation that the pane on the upper most of the units is 8mm toughened and heat strengthened and the bottom pane is 10mm toughened and heat strengthened. This should be the other way around. The units are shaped therefore cannot be installed the wrong way round __ MCR - Cxxx-__M-A-LRC-D061-50004 & Cxxx-__M-A-LRC-D061_WS106-50491 Applies. Locational drawing included: Cxxx-__M-A-DWG-D061_WS106-54439
| 02SL - Stations (LUL) | Cxxx-NCR-002489 | NCR | CHS - West Elevation Cladding Support Steel - Misaligned Fixing Holes |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-01-27 | 2019-05-10 06:12 | 103 | 2018-10-01 12:17 | Civil - Civil Engineering General | 4000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | At backing plate location D2 (shown on drawing no. Cxxx-__M-A-DWG-D061_WS107-50438), due to discrepancies in the as-built survey of anchor locations by the sub-contractor, two of the four anchors at this location did not line up with the holes in the backing plate. See photos and mark up attached showing the difference. As a result of this, two new 30mm dia. holes were broached into the D2 backing plate in order to accommodate the anchors. This solution was chosen instead of sending the entire column section back to the fabrication yard in order to get it changed. The solution was approved by the designer of the RC-steelwork connections - TGP - via email and is awaiting formal minor design change sign off by them.
| 02SL - Stations (LUL) | Cxxx-NCR-002490 | NCR | Primary CMS for outgoing sub main cables are too small from ATS to Castell isolator and Distribution board. |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-11-12 | 2019-03-07 11:23 | 115 | 2018-10-03 09:07 | Electrical - Cable Management | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | 100mm² heavy duty cable tray Primary CMS for outgoing sub main cables from ATS to Castell isolators and Distribution boards in Lift Control Room: LCR 3, LCR 4, LCR 5, LCR 7 and LCR 10.
| 02SL - Stations (LUL) | Cxxx-NCR-002491 | NCR | KALZIP Roof - Damage |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-11-14 | 2019-02-27 14:43 | 105 | 2018-10-05 13:11 | Architectural - Roofing & Exterior Treatment | 4200 |  | Damaged | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Site walk conducted by __ (TN) and __ (GC/NG) to view the roof prior to KALZIP attending to undertake a Inspection. At 2 separate locations puncture marks of the KALZIP roof where noted (see pictures), also an area of 'ferrous material' contamination was noted (see pic), the roof still has a reasonable amount of materials stored on wooden pallets along with many scaffold clamps!
| 02SL - Stations (LUL) | Cxxx-NCR-002492 | NCR | Installation and Testing of Fire Alarm System with drawings not submitted / accepted (GSM) |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2019-01-19 | 2019-05-21 12:08 | 122 | 2018-10-04 10:10 | Fire - Fire Systems & General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | GSM Fire Alarm & Detection installation was completed and IRN's subsequently Code 1 Accepted. During the review of the Fire Alarm & Detection IPAC X0 drawings, it was noted that there were 4 drawings not submitted for Crossrail Review / Acceptance. These drawings are as follows - Cxxx-__M-E-DWG-D061_WS106-50476 Cxxx-__M-E-DWG-D061_WS106-50477 Cxxx-__M-E-DWG-D061_WS106-50478 Cxxx-__M-E-DWG-D061_WS106-50479
| 02SL - Stations (LUL) | Cxxx-NCR-002493 | NCR | __ Doors - Vision Panels non-compliance site wide |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-07-30 | 2021-04-24 13:37 | 268 | 2020-05-11 16:55 | Architectural - Doors | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | There are 39No. door drawings which have be approved for manufacture that do not meet part K of the building regulationsin relation to the size and location of vision panels. Some of these doors were part way through manufacture when the error was discovered.
| 02SL - Stations (LUL) | Cxxx-NCR-002494 | NCR | Trunking firestopping- use of incorrect material |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2018-12-20 | 2020-01-11 11:21 | 387 | 2018-10-07 12:38 | Fire - Compartmentation | 10000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | Following discussions with the MEP site team, it appears that the incorrect firestopping material is being used in cable trunking. The material (as per attached photographs) is a hard firestopping material. This was being broken out by the MEP team (with cables in-situ, see indentation in compound) to enable further cable installation. This was discovered in DSS level 6. __ to confirm if this is 1) the correct material 2) how the cables will be assessed where the material has been removed (visual inspection, dead test etc) 3) methodology for removing the non-compliant material (if applicable) 4) full list of areas where this has been installed __ to issue a project wide quality alert immediately to ensure that a) breaking out of compound is fully controlled around installed cables b) correct material is used.
| 02SL - Stations (LUL) | Cxxx-NCR-002495 | NCR | LULO Lower Concourse R10N - Incline Glazing Upper Brackets Drilled Holes Error |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-11-17 | 2018-10-24 09:41 | -24 | 2018-10-08 13:43 | Civil - Civil Engineering General | 1500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The holes drilled into the primary steel for the top brackets for 3 bays of __ GL 12-15 West in R10N have been drilled incorrectly, and as a result need to be moved 22mm to the south. Although the current holes which have been drilled are correct to the co-ordinates provided by __ design, this leaves the bay in a trapezoidal shape meaning the glass cannot be installed.
| 02SL - Stations (LUL) | Cxxx-NCR-002496 | NCR | Early Energisation of Bin Store Fan Isolator - GSM |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-02-08 13:28 | -143 | 2018-10-08 16:23 | Mechanical - Mechanical Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The fan isolator panels in the GSM were relocated following a PTR response from BH. An FCD was raised for this new location and evidence to show that the panels would be protected by a balustrade was requested by CRL before the FCD was accepted and closed. Subsequently there has been some difficulty in agreeing a balustrade design, during which time the fan isolators were energised. Please see the attached PTRs which show this, and FCD-2793 once complete will show the final balustrade design for this area.
| 02SL - Stations (LUL) | Cxxx-NCR-002497 | NCR | Upper Concourse Roof fascia Brackets |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-11-21 | 2019-03-08 13:02 | 107 | 2018-10-12 09:19 | Architectural - General | 500 |  | Material | Reject | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | According to the drawings (Cxxx-__M-A-CER-D061_WS106-50228), the top hats supporting the Anodised Fascia Panels were to be 3mm galvanised brackets. These top hats were procured by the subcontractor in 3mm 20 microns galvanised sheet coated with Interpon D1036 Polyester Powder Coating. A PTR was raised to __ requesting the change. This was rejected as the PPC requires regular (maximum of 12 months interval) cleaning and maintenance to ensure protective properties of coating is retained for the intended design life. Additionally, during transportation, where the brackets rubbed together the PPC coating was damaged. This does not give confidence of a durable coating which could take further damage by installation e.g. torquing bolts.
| 02SL - Stations (LUL) | Cxxx-NCR-002498 | NCR | Installation to P revision not under by exception. |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-11-18 | 2018-10-12 08:20 | -37 | 2018-10-09 08:48 | Electrical - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Installation of Cables to MCC 13 from P revision Schematic Drawing
| 02SL - Stations (LUL) | Cxxx-NCR-002499 | NCR | Inspection Request Form |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-11-19 | 2019-01-22 09:12 | 64 | 2018-10-10 08:14 | Electrical - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Inspection Request form for the PSD ATS units and Sub Main Cables did not identify individual drawing revisions and whereas it included an ITP for the sub main cable works, it failed to include the ITP for the ATS which meant that none of the witness points detailed were not adhered to.
| 02SL - Stations (LUL) | Cxxx-NCR-002500 | NCR | LULO - 1DN Column Concrete Encasement |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-12-29 | 2019-10-09 10:00 | 284 | 2018-10-10 09:18 | Structural Engineering - Structural Engineering - General | 2100 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | The columns of the north accommodation block founded within Winthrop Street have been concrete encased as per drawing Cxxx-HYD-S-DDD-D061_WS106_Z-76001. However it was noticed during the pre-pour inspection that the paint system applied to the steel had not been removed as per the response to Cxxx-RFI-004900.
| 02SL - Stations (LUL) | Cxxx-NCR-002502 | NCR | LULO - HCDL - Pull testing failures on the WB Glazed Screen Fixings |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-02-07 | 2018-12-03 22:05 | -66 | 2018-10-10 12:16 | Architectural - Glazing | 8500 |  | Incorrect Installation | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following UKAS pull tests on the Westbound Glazed Screen, some fixings did not reach the required pull out value (23kN) stated in the ITP. See attached UKAS report for further details.
| 02SL - Stations (LUL) | Cxxx-NCR-002503 | NCR | CHS - South Elevation Walkway Cantilever Arms - Out of Position Tolerance |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-11-20 | 2019-01-02 17:43 | 43 | 2018-10-11 15:11 | Civil - Civil Engineering General | 2200 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Walkway cantilever arms on the South elevation of CHS have been positioned up to 15mm out of design line. A full survey of all 10 cantilever arms on the South elevation is currently being undertaken - this will be attached to the NCR once complete.
| 02SL - Stations (LUL) | Cxxx-NCR-002504 | NCR | Works commenced without an approved ITP |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2018-11-21 | 2019-01-05 12:42 | 45 | 2018-10-12 11:29 | Structural Engineering - Structural Engineering - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Cxxx-__M-A-ITP-D061_WS106-50192 rev 1.0 was signed off code 1 14/06/2018. The submission was to approve activities 10.1 - 10.4 (which was denoted on the decal at time of acceptance). The Project Manager has since revised the coding of the document to code 3. Works to install the totem continued without approval. Furthermore, there was no off-site ITP in place for the items fabricated off-site.
| 02SL - Stations (LUL) | Cxxx-NCR-002505 | NCR | LULO Lower Concourse R10N - GL 13-14 West Bottom Splice Plate |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-11-21 | 2019-04-03 19:51 | 133 | 2018-10-12 13:09 | Architectural - Glazing | 3500 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The __ lower bracket to the R10N Incline GL 13-14 West bay has been manufactured incorrectly. When erecting the frame, it has been made apparent that the bracket does not clear the primary steel splice plate bolts, and as a result means the __ bay cannot be installed - See attached photo and marked up drawing showing exact location. We believe this clash is due to the __ model not adequately reflecting the as-built condition of the primary structure. __ are awaiting confirmation from __ design, however it is envisaged that the bracket will either be modified on site (through notching the base plate underneath - see pictures) thus allowing the bolts to slot through, or the bracket will be re-manufactured off-site to suit. In either scenario, the alterations or changes will be captured on a CAT III check and submitted to CRL in this NCR. Any on site adaptions to the galvanized bracket will be repaired with galvanizing spray.
| 02SL - Stations (LUL) | Cxxx-NCR-002506 | NCR | LULO - Accommodation Blocks - Lack of F2 CAT design & check certificates submission |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-11-21 | 2019-03-13 13:39 | 112 | 2018-10-12 13:54 | Civil - Structural Engineering | 1200 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | As part of the progressive assurance works, there is lack of F2 CAT design & check certificate submissions. __ to provide design assurance documentation to the client. Design team to request S/C to provide design assurance documentation against their F2 design.
| 02SL - Stations (LUL) | Cxxx-NCR-002507 | NCR | LULO - Accommodation Blocks - Lack of progressive construction records submission |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-02-15 | 2019-03-29 09:33 | 42 | 2018-10-12 14:07 | Architectural - General | 1200 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | As part of the progressive assurance works, there is lack of both offsite and onsite construction records submissions. __ to provide offsite and onsite assurance documentation to the client. Delivery team to request S/C to provide construction records against the works completed on site.
| 02SL - Stations (LUL) | Cxxx-NCR-002508 | NCR | Stair 32 BAL 144 Incorrectly Fabricated |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-11-02 | 2018-11-28 18:21 | 26 | 2018-10-13 09:07 | Architectural - Balustrade | 2500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 8 no. BAL 144 posts on Stair 32 have been discovered to be fabricated incorrectly. The posts are 33mm too high in comparison with the fabrication drawings.
| 02SL - Stations (LUL) | Cxxx-NCR-002509 | NCR | __DB2 & 5 platform DC Cabinet Isolator energise |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-11-23 | 2019-02-12 10:03 | 81 | 2018-10-14 08:19 | Electrical - LV Equipment | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | NCR for energising platform dc cabinets. due to requirements for __ commissioning on the platforms we have temporary fed 4 of the 8 Isolators installed. this was due to no housing location for the Distribution board.
| 02SL - Stations (LUL) | Cxxx-NCR-002510 | NCR | Installation of Floor CMS tap off boxes without MCR registration. |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-12-04 | 2018-12-13 15:21 | 9 | 2018-10-25 12:28 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | __ have installed approximately 200 metres of IP65 trunking at floor level, on the Lower and Upper concourse in line with BH F1 intent. At each gridline line on the lower concourse 3 Trunking Tap of box to secondary CMS (conduit) has been installed to feed multiple systems in the high level trunking from DSS. The CMS trunking that has been installed does have an MCR, but the Tap off boxes do not. Armour duct (CMS Manufacturer) have now supplied al relevant and associated material and MCR to be submitted for design approval.
| 02SL - Stations (LUL) | Cxxx-NCR-002513 | NCR | LULO Concourse - Bailey Panels Designed/Manufactured Incorrectly With Code 3 MCR |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-03-14 | 2019-09-26 13:56 | 196 | 2018-10-18 16:30 | Architectural - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | It has been identified that an estimated 550 of Bailey cladding panels have been incorrectly designed/manufactured. It is also noted that the Bailey panels have been manufactured and installed on site with a Code 3 MCR. It is envisaged that Bailey will make modifications/amendments to the affected panels where possible to salvage materials. Those which cannot be modified or altered will be disposed of, and the panels will be re-manufactured to the correct size.
| 02SL - Stations (LUL) | Cxxx-NCR-002514 | NCR | Wind posts- lack of off-site assurance |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-10-23 08:18 | 115 | 2018-10-26 10:32 | Architectural - Brickworks/Blockworks | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | There is currently no off-site ITP in place for the wind posts installed in the shafts & tunnels. As a result, off-site records have not been progressively compiled. This includes, but not limited to: - mill certs - galvanising records - WPS - WPQR - weld tests (i.e. N__) - RWC review The Contractor is to confirm which documentation is to be provided along with a forecast date
| 02SL - Stations (LUL) | Cxxx-NCR-002515 | NCR | Stair non-consistent widths from flight to flight to each stair |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-12-09 | 2018-10-24 16:31 | -46 | 2018-10-17 14:15 | Architectural - General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please refer to attached FCD-002791 - Stair handrail tolerances. In DSS and CHS shafts stair handrails could not be installed as per workmanship tolerances - JL32.3213 due to concrete walls being out of tolerance. For instance, if the concrete wall is out of tolerance by 15 mm, handrail cannot be installed within 2mm tolerance as stated in JL32.3213. This issue has been captured in attached FCD-002791 which allows width reduction for fire escape staircases (DSS Stair 1, 2, 3, 4 and CHS Stair 40 and 41) up to 100mm per staircase and for maintenance staircases (DSS Stair 5,9,10,11,12 and CHS 40A,42,42A,42B,43) up to 50mm per staircase. This change has been reviewed and approved by __ fire engineer and BH (see FCD-002791 attachments). This NCR covers stair non-consistent widths from flight to flight to each stair. Please find attached as-builts of handrail widths (in FCD-002791 attachments) showing the design dimensions and proposed dimensions where handrail is not installed. All measurements have been taken from the same location on each stair flight. Please confirm that as per the approved FCD a relaxation of the handrail tolerances is acceptable.
| 02SL - Stations (LUL) | Cxxx-NCR-002517 | NCR | LV Switchboard Indicator Lamps |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-02-16 | 2019-06-19 10:23 | 123 | 2018-10-18 08:06 | Electrical - LV Equipment | 1000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | It was noted during recent testing / witnessing with CEG that the indicator lamps on the main LV Switchboards were incorrectly coloured. It was noted that the colours of the Indicator lamps was in contradiction to the BS standard 60204. This information is in contradiction to the answer that Crossrail provided to a __ PTR.
| 02SL - Stations (LUL) | Cxxx-NCR-002518 | NCR | IRF Inspection Procedure for __DB5 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-11-28 | 2018-11-12 15:00 | -16 | 2018-10-19 10:18 | Electrical - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Not Defined | Completed |  | Multiple Inspections offered where there should have been separate inspections meaning that the ITP had not been followed correctly Heatshrink fitted to Gapped Gland prior to IRN.
| 02SL - Stations (LUL) | Cxxx-NCR-002519 | NCR | Working to P Rev Drawing without a By Exception |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-05-04 | 2019-01-24 13:35 | -100 | 2018-10-19 09:43 | Electrical - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Installation Works have been carried out to a P Rev Drawing due to C Rev drawings being unavailable
| 02SL - Stations (LUL) | Cxxx-NCR-002521 | NCR | TTH / Concource Electrical Switchgear SATs |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-02-17 10:55 | -134 | 2018-10-23 09:59 | Electrical - General | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | __ have carried out numerous SATs for Electrical Assets in the TTH without an IRF - failing to adhere to ITP Witness Points. In addition, there is lack of evidence of __ Commissioning Team Attendance / Witnessing and or Acceptance. __ to confirm number and Assets where SATs have been carried out without an IRF and that those that have witnessed and accepted the SATs are authorised to do so.
| 02SL - Stations (LUL) | Cxxx-NCR-002525 | NCR | SOR Plant Room Earth Bars (IRF 50341) |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2019-02-10 | 2019-01-11 12:55 | -30 | 2018-10-25 08:14 | Electrical - Earthing & Bonding | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | On inspection of the SOR Plant Room Earth Bars (IRF 50341) we found the following issues: - Snags not accurately captured - No snags recorded on SnagR - Multiple PTRs missing for changes - Assets not ready for inspection (DB Front panels require removing to inspect bonding) - Temporary Labels incorrect - ITP not available during inspection - No IPad available / on site during inspection - P Rev Drawing(s)
| 02SL - Stations (LUL) | Cxxx-NCR-002526 | NCR | Poor standard of installation and lack of quality control |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-12-04 | 2019-03-16 14:52 | 102 | 2018-10-25 09:53 | Fire - Fire Systems & General | 5000 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Cables not terminated or incorrectly terminated. Installation not QA checked and inspected prior to requesting power on.
| 02SL - Stations (LUL) | Cxxx-NCR-002527 | NCR | NCR for IRN -Cxxx-__M-E-NOX-D061_WS106-50223 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-12-04 | 2018-10-29 15:38 | -36 | 2018-10-25 13:06 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | P revision drawings used to build and to sign off the above IRN due to outstanding C Rev drawings.
| 02SL - Stations (LUL) | Cxxx-NCR-002528 | NCR | R12 Stairs Redundant Hole Repair |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-12-04 | 2018-11-14 17:59 | -20 | 2018-10-25 16:24 | Civil - Civil Engineering General | 1800 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Following BAL 123 design changes, to suit as-built tolerances of the finished floor level, there are redundant holes in the RHS steel stringers of the R12 stairs (S29,30 and 31). A procedure to repair these is attached.
| 02SL - Stations (LUL) | Cxxx-NCR-002529 | NCR | LULO Lower Concourse R12 - Skirting defect |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-12-10 | 2019-05-10 05:55 | 151 | 2018-10-31 09:55 | Architectural - General | 1500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __'s sub-contractor __ have manufactured the R12 floor skirtings not in accordance with the accepted sequence pack drawings. A result of the above has resulted in skirtings which are defective for use due to welds warping the thin 2.5mm folded stainless steel at regular intervals. See attached pictures indicating this (please note it is more noticeable in person).
| 02SL - Stations (LUL) | Cxxx-NCR-002530 | NCR | Energising refrigeration (VRF) systems in DSS without IRN in place |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2018-12-08 | 2019-01-30 10:04 | 53 | 2018-10-29 10:07 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | The north (2no systems) and south (4no systems) VRF systems in DSS were energised without an IRN in place.
| 02SL - Stations (LUL) | Cxxx-NCR-002531 | NCR | GSM Replacement WC Extract Fan GSM/01/EF/03 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-01-28 | 2020-01-14 08:11 | -14 | 2019-12-19 10:00 | Mechanical - Heating Ventilation & Air Conditioning | 8000 |  | Design | Reject | 2 (6-60k) | Complete | Design Problem - Other | Completed |  | Due to lack of performance it was necessary to install a fan capable of a greater duty. The fan was installed in close co-operation with __ but without any formal Design Change documentation in place with either our Designers or our Client, therefore, it has been necessary to raise retrospective documentation and an appropriate NCR.
| 02SL - Stations (LUL) | Cxxx-NCR-002533 | NCR | NCR for IRN Cxxx-__M-E-NOX-D061_WS106-50010 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-12-09 | 2019-02-25 09:25 | 78 | 2018-10-30 10:02 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | P revision drawings used to build and to sign off the above IRN due to outstanding C Rev drawings. Drawing Cxxx-__M-E-DDB-D061_WS106_1-30338 P05 (Ventilation Plant Room Sections A-D) Relevant changes from C02- • MCC20 position • Secondary CMS to MCC20 Drawing Cxxx-__M-E-DDA-D061_WS106_1-30364 P08 (Cable Management System Ticket Hall) Relevant changes from C02- • Additional BMS/SCADA trunking • MCC20 position Drawing Cxxx-__M-E-DDE-D061_WS106_Z-30950 P07 (MCC Schematic) Relevant changes from C02- • Additional Isolator control box for 4No AHU/TEF. • Additional 2 No AE200 VRF Cabinets Drawing Cxxx-__M-E-DDA-D061_WS106_1-31950 P08 (Small Power Ticket Hall) Relevant changes from C02- • MCC20 position
| 02SL - Stations (LUL) | Cxxx-NCR-002534 | NCR | CHS transformer room integrity tests- works without an approved ITP |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2018-12-09 | 2019-09-06 17:50 | 271 | 2018-10-30 10:08 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Room integrity tests were carried out without any notification to CRL for attendance via IRF, No ITP was in place to indicated acceptance criteria for room integrity (as per CRL-OBS-25215).
| 02SL - Stations (LUL) | Cxxx-NCR-002536 | NCR | DSS Louvre installation |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2019-01-17 | 2019-01-06 17:34 | -11 | 2018-10-30 12:47 | Architectural - Walls | 950 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | Incorrect bolts have been installed for the DSS-10 louvre in the Level A PFR 1 room. It is noted that the M10 fixings (M12 required) still passed the pull test, which was conducted by a UKAS accredited tester, but are not in accordance with the ITP. NCR to be raised regarding bolts and __ to confirm that there is a by-exception in place to use P04 drawing on site.
| 02SL - Stations (LUL) | Cxxx-NCR-002537 | NCR | Lack of provision of progressive Assurance-CAT Design and check certificates |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-04-30 | 2019-07-04 07:33 | 430 | 2018-10-30 13:22 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Following a recent Surveillance carried out on the 30/10/2018 by the __ Quality Team to determine compliance of the CAT Design and Check Certificates project wise, a number of problems have been discovered: 1.CAT Design & Check Certificates not listed/referenced in package listing 2.CAT Design & Check Certificates found as a placeholders on eB despite the fact that the Installation works are completed 3.The drawings revision number used on site does not match with the revision referred in the CAT Design & Check Certificates Surveillance report reference: Surveillance Report – Control of CAT Design and Check Certificates-Cxxx-__M-O4-RGN-D061_WS106-53044
| 02SL - Stations (LUL) | Cxxx-NCR-002539 | NCR | Control of Sketch Submissions (MEP) |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-01-18 | 2019-02-12 10:12 | 25 | 2018-10-30 16:47 | Electrical - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Following a recent Surveillance carried out on the 30/10/2018 by the __ Quality Team, it has been found that a number of sketches have been updated after the related PTR acceptance date. Surveillance report reference: Surveillance Report – Control of Sketches Submission – Cxxx-__M-O4-RGN-D061_WS106-53045.
| 02SL - Stations (LUL) | Cxxx-NCR-002540 | NCR | CHS Steelwork Corbel & Anchor Fixing Loading |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-02-22 | 2019-04-15 16:27 | 52 | 2018-10-30 17:55 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The CHS cladding steelwork is loaded incorrectly on the corbel and anchor connections fixing it back to the RC structure. The Cxxx F1 load design and TGP anchor connection design utilised the RC cantilever beam (corbel) to take the full vertical load from the cladding system. In order for this to work, a vertical slotted hole was utilised at the end of transverse beams. At some point during the steelwork design, this slotted connection was changed to a fixed welded connection. This, along with the installation sequence of loading the steel structure on the anchor connections only has meant that the vertical load from the self-weight of the steel structure is currently acting on the anchors alone and not the RC cantilever beam (corbels) as intended. A summary of the above can be found in the attachment: 'Summary of Steelwork Loading Issue'.
| 02SL - Stations (LUL) | Cxxx-NCR-002541 | NCR | Inclined Galzing Stair 26/28 Platform 5/5 Unprotected Installed Asset |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-11-17 | 2019-03-10 16:36 | 113 | 2018-11-01 15:53 | Architectural - Glazing | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Please see attached a couple of pictures of the inclined glazing on Stair 26/28 Platform 5/6. The lack of hard protection is not acceptable. Currently they have only used a layer of Cordex half way up. Protection of installed assets is critical and failing to do so could be extremely costly to the programme and cost.
| 02SL - Stations (LUL) | Cxxx-NCR-002542 | NCR | GSM WC Extract Fan MCR |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-12-10 | 2019-06-05 12:06 | 177 | 2018-10-31 14:40 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | GSM WC Extract Fan GSM/01/EF/03 was replaced by a different __ model without a relevant MCR in place, however, this has now been rectified.
| 02SL - Stations (LUL) | Cxxx-NCR-002543 | NCR | LU - HCDL - Lack of Provision of __ Assurance |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-02-15 | 2019-03-05 13:54 | 18 | 2018-10-31 16:20 | Architectural - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Installation works for circular column cladding at Area 1 (HCDL platform level) have started without the design documentation being approved. Neither the drawing nor the CAT Design & Check Certificate were approved when the works commenced.
| 02SL - Stations (LUL) | Cxxx-NCR-002544 | NCR | Sitewide- alternative screed angle fixings used without approval |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-12-31 | 2018-12-03 21:02 | -28 | 2018-11-01 12:24 | Architectural - Flooring | 1000 |  | Material | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient surveillance of subcontractors | Completed |  | __ noticed that __ (paving subcontractor) is using R-XPTII-A4 Stainless Steel anchors to fix screed angles to substrate. Specified fixings are __ HUS3-H6 (As per PTR-1599 attached) RAWL plugs don't have approved MCR in place.
| 02SL - Stations (LUL) | Cxxx-NCR-002545 | NCR | P Rev drawings wrongly referenced (Cxxx-__M-E-NOX-D061_WS106-50011) |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-12-11 | 2019-04-08 14:58 | 118 | 2018-11-01 13:44 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | P Rev drawing referenced on IRF decal and check sheets for IRN Cxxx-__M-E-NOX-D061_WS106-50011. There has been no change to the relevant services and equipment installed from the last C Rev drawing therefore the C Revision drawing should have been referenced on the IRF decal and reference sheets. Cxxx-__M-E-DDA-D061_WS106_1-30364 P08 used - no change from C01 Cxxx-__M-E-DDA-D061_WS106_1-31950 P08 used - no change from C02 Cxxx-__M-E-DDB-D061_WS106_1-30330 P06 used - no change from C02 In addiction to the above, MCC Schematic diagram Cxxx-__M-E-DDE-D061_WS106_Z-30950 has been installed to Rev P07 due to the upgrade of 4 isolators to ICB units.
| 02SL - Stations (LUL) | Cxxx-NCR-002546 | NCR | PSD ATS |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-12-11 | 2018-11-06 14:13 | -35 | 2018-11-01 15:50 | Electrical - General | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | __ failed to invite Crossrail field engineer to SAT for PSD ATS EB & WB as per witness point in ITP. Commissioning team also did not attend
| 02SL - Stations (LUL) | Cxxx-NCR-002547 | NCR | Emergency Exit Signs - Energisation |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2019-05-31 | 2020-01-05 10:01 | 219 | 2018-11-02 11:50 | Electrical - General | 10000 |  | Testing and Commissioning | Use As-Is | 2 (6-60k) | Complete | Material/Preservation Problems - Other | Completed |  | CRL attended an inspection on 04/09/18 to witness Emergency Exit Sign installations. There were various defects identified, including issues surrounding the suitability of the exit sign covers which can be removed without a tool. These defects were not recorded per the __ Quality Plan, nor the IRF process followed. On submission of the IRNs for various Distribution Board(s) that supply the emergency exit signs, the check sheet was not included, neither the snags / defects recorded as part of the inspection. These emergency exit signs have been energised as part of the IRN acceptance. Due to the accessibility on various staircases to these exit signs, CRL have requested that in the meantime - these be disconnected until a resolution (such as manufacturer confirming self tapping / security screws being installed without voiding the warranty) is confirmed.
| 02SL - Stations (LUL) | Cxxx-NCR-002548 | NCR | LU - GSM - Benchmark documentation not submitted |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-02-10 | 2019-09-16 13:14 | 218 | 2018-11-03 14:44 | Architectural - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | A total of 3no Benchmark Inspections in the GSM building we offered to CRL during the Week 32 possession: * IRF 1998 - GSM Benchmark inspection for __ Cladding. * IRF 1999 - GSM Benchmark inspection for __ Curtain Wall. * IRF 2000 - GSM Benchmark inspection for Proteus Cladding System. All these inspections have already been carried out, however some of the documentation has not been submitted to CRL: * __ Cladding: this benchmark inspection was offered in IRF 1317. Documentation for the benchmark has not been produced and the sample acceptance document [Cxxx-__M-A-LRC-D061-50193 Rev 1.0] is a placeholder. * __ Curtain Wall: this benchmark inspection was offered in IRF 1525. Documentation was produced and comments were raised, however not all of them have been closed out. Both benchmark [Cxxx-__M-A-LRC-D061_WS106-50871 Rev 1.0] and sample acceptance [Cxxx-__M-A-LRC-D061-50191 Rev 1.0] documents are placeholders. * Proteus Cladding System: benchmark is Code 1 [Cxxx-__M-A-LRC-D061_WS106-50828 Rev 1.0], however a sample acceptance document has not been submitted to CRL.
| 02SL - Stations (LUL) | Cxxx-NCR-002550 | NCR | Upper Concourse Roof Fascia Design |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-01-23 | 2019-04-04 14:54 | 71 | 2018-12-14 14:01 | Architectural - General | 1200 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | Upon changing the top hat material for the Fascia (Cxxx-FCD-003005), checks were done to ensure that the change did not affect the structural support of the panels. It was found that some checks were missed in the original CAT check. The result of these checks now being completed was to add additional washers. This and checks on the rest of the design is covered under a new CAT check.
| 02SL - Stations (LUL) | Cxxx-NCR-002551 | NCR | NCR For Comlot Cxxx-__M-E-NOX-D061_WS106-50023 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-12-16 | 2019-04-08 15:12 | 113 | 2018-11-06 15:31 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | P revision drawings used to build, inspect and sign off, when C rev drawings would suffice.
| 02SL - Stations (LUL) | Cxxx-NCR-002552 | NCR | __DB1 capacity change |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-12-16 | 2018-11-12 10:09 | -34 | 2018-11-06 18:38 | Electrical - Power Distribution | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | At CHS Distribution board __DB1 is down as an 8 way on the Distribution board schedule but a 12 way has been installed with a surge suppressor installed on 12L1,2,3. NCR raised as this should have been captured in the IRN that was previously Code 1.
| 02SL - Stations (LUL) | Cxxx-NCR-002553 | NCR | INSTALLATION OF CIRCUIT FOR __ SUPPLY ON DB - LUL/C/DB7 POST IRN |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-12-17 | 2018-11-15 11:19 | -32 | 2018-11-07 10:50 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Additional circuit added to Distribution Board LUL/C/DB7-5L3 at request of Baker hicks to capture the Power supply to the __ system post IRN of the distribution board.
| 02SL - Stations (LUL) | Cxxx-NCR-002554 | NCR | Escalator ATS |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-03-02 | 2019-01-24 16:28 | -37 | 2019-01-21 09:10 | Electrical - General | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | __ failed to invite Crossrail field engineer to SAT for Escalator ATS as per witness point in ITP. Commissioning team also failed to attend.
| 02SL - Stations (LUL) | Cxxx-NCR-002555 | NCR | Lift 2 ATS |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-11-22 | 2018-11-08 14:01 | -14 | 2018-11-08 08:49 | Electrical - General | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | __ failed to invite Crossrail Field Engineer to SAT for Lift 2 ATS as per witness point in the ITP, the commissioning team also did not attend
| 02SL - Stations (LUL) | Cxxx-NCR-002556 | NCR | LULO GSM - Firestopping materials - lack of sample documentation |  | Contr | VIN | WHI - Whitechapel Station (Central) |  | 2019-01-11 | 2019-02-02 14:13 | 22 | 2018-11-07 17:51 | Materials - Approval | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | The attached spreadsheet (GSM Firestopping Materials - samples) contains the list of applicable materials for GSM firestopping that require sample and/or benchmark documentation. Sample documentation for a number of materials have not been provided for acceptance. Items highlighted in red indicate materials that require but do not have approved sample documentation.
| 02SL - Stations (LUL) | Cxxx-NCR-002557 | NCR | Lighting Layout Redline Drawings |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-03-07 09:47 | -115 | 2018-11-08 12:01 | Electrical - General | 5000 |  | Documentation and Records | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | __ have presented numerous Distribution Board IRNs that contain lighting circuits / assets as part of the comm lot structure that have been Code 1 Accepted. CRL are yet to see any changes to the lighting installation (height, orientation etc) on the submitted / accepted Redline Drawings that are included and referenced in the Code 1 Accepted IRNs CRL were invited to inspect ELDB5 (IRF_MEP PERM_0483) - during inspection CRL LFAE confirmed that various height and orientation changes to the light fittings had not been captured. As a result, confirmation that __ have captured and submitted accurate redline drawings for the previous Code 1 Accepted IRNs and the future IRN submissions is required Please refer to Works Information Volume 2B – Part 13 – Assurance Records and Certification 13.3.6 Redlines, As Built and Operational Records
| 02SL - Stations (LUL) | Cxxx-NCR-002558 | NCR | DSS Level 4 ESR Relief trunking |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-07-22 | 2019-08-14 14:13 | 388 | 2018-11-08 12:37 | Electrical - Cable Management | 2000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | It is required to install a relief trunking to ensure that on completion of there is a minimum of 25% spare capacity within the trunking
| 02SL - Stations (LUL) | Cxxx-NCR-002559 | NCR | DSS ELDB2 - 6L2 Incorrect Cable Size |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2018-12-18 | 2018-11-30 11:25 | -18 | 2018-11-08 15:01 | Electrical - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | IRN Page Turn of DSS ELDB2 uncovered a discrepancy / incorrect cable size for 6L2. The installation and dead test of 6L2 specified a 4mm cable. __ have installed a 2.5mm without PTR and acceptance from BH. __ to confirm via PTR to BH attached to this NCR whether reworks / use as is outcome.
| 02SL - Stations (LUL) | Cxxx-NCR-002560 | NCR | Test Sheet results Change for DB after IRN. |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-12-19 | 2018-11-15 11:06 | -34 | 2018-11-09 10:19 | Electrical - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Not Defined | Completed |  | Construction Records / Test results submitted for IRN of DB - LUL/C/DB7 Show cable installed as 1.5mm CSA on circuits 1L1-4L3. __ report shows 1.5 to be installed and referenced for IRN. __ installed 2.5mm CSA and the updated test results are being submitted at IPAC for Page turn of DB.
| 02SL - Stations (LUL) | Cxxx-NCR-002561 | NCR | Working to P rev Drawing without a By Exception |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-03-04 | 2019-01-24 13:59 | -39 | 2018-11-09 15:37 | Electrical - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Installation Works have been carried out to a P Rev Drawing due to C revision being unavailable
| 02SL - Stations (LUL) | Cxxx-NCR-002562 | NCR | LULO - HCDL - ESS - Eastbound Access Ramp - Top slab out of tolerance |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-01-12 | 2019-01-14 09:17 | 2 | 2018-12-03 15:27 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The top slab of the Eastbound Access Ramp is approximately 15-20mm too wide. This is outside the acceptable tolerance. Please see attached as-built survey for the top slab widths at 2.0m intervals, showing the location and extent of the issue.
| 02SL - Stations (LUL) | Cxxx-NCR-002563 | NCR | LULO- DC8 and 9 Comms rooms steel and __ |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-01-25 | 2019-04-03 20:20 | 68 | 2018-11-12 14:01 | Architectural - General | 2540 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | The Contractor was invited on an inspection of the DC 8 and 9 comms rooms. During the inspection the following defects were observed (please see attached document for pictures): P5- DC9 1- 80mm packing of a ceiling steel frame member 2- Ceiling steel frame member not fixed to the wall 3- 2no steel frame members not fixed to the wall as members are 150mm too short P6-DC8 1- 80mm packing of a ceiling steel frame member 2- 1no ceiling steel frame member is not fixed to the wall as 100-150mm too short 3- 1no ceiling steel frame member not installed 4- Poor quality of builders work hole and damaged __
| 02SL - Stations (LUL) | Cxxx-NCR-002564 | NCR | BAL 145 (Incline Glazing) Balustrade Posts - to Archtectural Spec |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-03-12 | 2019-05-18 10:48 | 67 | 2018-11-12 16:40 | Architectural - Balustrade | 8000 |  | Design | Rework | 2 (6-60k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Installed Balustrade Posts (BAL 145 Inclined Glazing) do not meet the requirements of the CRL Works Information Architectural Specification Cxxx-__M-A-RSP-D061-50079 R75 Clause JL32.1219 (c, i) states that all edges are to have a 3mm chamfer. 3 x pictures attached
| 02SL - Stations (LUL) | Cxxx-NCR-002567 | NCR | Not working to ITP procedure / Cables installed into Panel before IRF was issued |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-06-10 | 2019-06-01 12:33 | -9 | 2019-03-01 09:03 | Electrical - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Work has been carried out (Cables Installed into the Panel) to Power Factor Correction Panels prior to an IRF being issued for an Inspection of the PFC Panels
| 02SL - Stations (LUL) | Cxxx-NCR-002568 | NCR | Escalator sump pump pit |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2018-12-24 | 2019-10-17 08:46 | 297 | 2018-11-14 09:09 | Civil - Civil Engineering General | 1300 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | The sump pit at the base of the escalators has been constructed with a sloping bottom, as attached photo. The sump pit is also very shallow to install level sensors with adequate spacing. The sump pumps cannot be installed on a sloping base.
| 02SL - Stations (LUL) | Cxxx-NCR-002569 | NCR | LU - HCDL - Loose bolts on primary steelwork connections |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-02-28 11:52 | -123 | 2018-11-14 14:02 | Civil - Structural Engineering | 5500 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | During the on-going construction works within the LU section, a number of bolts have been found loose on the column to canopy connections of the primary steelwork members at the HCDL area. Subcontractor (__) has been contacted to carry out remedial works on the loose bolts and to provide a clarification. __ night shift team has tighten the bolts again while waiting for an answer.
| 02SL - Stations (LUL) | Cxxx-NCR-002570 | NCR | GSM General Supply Men's Locker Room |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-12-25 | 2019-06-05 12:08 | 162 | 2018-11-15 15:07 | Mechanical - Heating Ventilation & Air Conditioning | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | Late changes to Mechanical Services design in GSM Level 1 meant that the supply ventilation duct install to the Male locker room was not completed as per F1 drawing and this has resulted in commissioning results being far less than acceptable. Ductwork modifications are set to be undertaken to correct the low flow issues.
| 02SL - Stations (LUL) | Cxxx-NCR-002571 | NCR | Fan Coil units in SOR |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-09-16 16:05 | 78 | 2018-11-16 15:00 | Mechanical - Heating Ventilation & Air Conditioning | 6000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | The fan coil units in the SOR on the concourse are chassis version designed to go above a false ceiling and therefore has no casing/finish. These units are used in a different application for which they are design. A cased version with easy clean surfaces should be used in office applications
| 02SL - Stations (LUL) | Cxxx-NCR-002572 | NCR | DSS Level 4 stair 10 area water ingress on CMS |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-02-18 | 2019-02-04 16:06 | -14 | 2018-11-20 10:39 | Electrical - Cable Management | 15000 |  | Damaged | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | In DSS on level 4 stair 10 area the design shows us installing 3 DB,s plus all associated CMS, The CMS takes cables to the DB,s but also acts as a through route taking cables to the station lower concourse and lighting boom at the top of the escalators. The CMS and one of the DB,s is damaged as we had a lot of water ingress coming from the concourse and because the Atrium at the top of the escalator was not installed
| 02SL - Stations (LUL) | Cxxx-NCR-002573 | NCR | Platform PES Structure - B9 Bracket |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-04-14 | 2019-03-15 07:53 | -30 | 2019-03-05 11:43 | Architectural - General | 750 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Incorporated within the PES structure on both the Eastbound and Westbound platforms is a B9 bracket which is used to to fix signs too. The dimension of the holes used for the signage is currently a 10mm hole. As per Code 4 drawing Cxxx-__M-C-DWG-D061_WS106-53747 the size of the hole needs to be 12mm. Due to a manufacturing error the hole is only 10mm. The B9 bracket will be amended on site to suit
| 02SL - Stations (LUL) | Cxxx-NCR-002574 | NCR | Works commencing without an accepted WEC WPS being inplace. |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-12-21 | 2019-02-02 14:16 | 43 | 2018-11-20 12:46 | Architectural - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | WEC commenced works on the following __ PO with WPS WEC500 being accepted by the client. __ order number:8526/202845 R10N-Rooflight Steel sub frame assembly. __ order number:8526/202846 R10N-Rooflight 45 Steel sub frame assembly. __ order number:8526/202847 R12-Rooflight Steel sub frame assembly.
| 02SL - Stations (LUL) | Cxxx-NCR-002575 | NCR | ELDB1 - Punchworks after IRN |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-02-18 | 2019-10-23 12:13 | 247 | 2018-11-20 14:13 | Electrical - Power Distribution | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | ELDB1 was IRN,d but not all the circuits could be put away in the DB at the time of inspection because certain parts of the building were not ready so they were put on Snag R and were going to be cleared on the punchworks
| 02SL - Stations (LUL) | Cxxx-NCR-002576 | NCR | Platforms - PES - Control of Drawings Submission |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-12-30 | 2019-01-04 09:48 | 5 | 2018-11-20 15:40 | Architectural - General | 1000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | During the red line drawings submission for the Platform End Screen - Secondary Steelwork packages [A-53053 and A-53054] it was identified that a different drawing revision was used on site compare with the CRL approved revision. The revision used on site was never issued to CRL for acceptance.
| 02SL - Stations (LUL) | Cxxx-NCR-002577 | NCR | Sump pumps and sump pits |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2018-12-31 | 2019-11-26 10:46 | 330 | 2018-11-21 08:11 | Mechanical - Public Health Engineering | 2000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The sump pump sets for under platform drainage (3No) and escalator pit (1) do not fit into the available space in the sump pits that have been cast into the structural slabs. The pits have been available for survey for sometime however no detailed drawings have been produced for review to support the selection/installation of these pumps. The sump pumps are currently on site and a solution is required to over come this issue
| 02SL - Stations (LUL) | Cxxx-NCR-002578 | NCR | Platform - Cross Passages - No Benchmark for Smoke Screen Installation |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2018-12-31 | 2019-04-25 12:35 | 115 | 2018-11-21 08:42 | Architectural - Glazing | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | A benchmark was not agreed and approved prior to completion of smoke screens in the Platform cross passages.
| 02SL - Stations (LUL) | Cxxx-NCR-002579 | NCR | __ thickness testing to R10 S |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-01-01 | 2018-12-19 13:47 | -13 | 2018-11-22 11:41 | Fire - Fire Systems & General | 1600 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | Item 4.9 of ITP Cxxx-__M-C-ITP-D061_WS106-53040 - LULO Steelwork Fire Protection requires thickness measurements for __ to be completed on each face of a beam at 3m intervals. The site team assured the thickness requirments as per the ITP however recorded the data on checksheet ACL-WHICHKS-017 and not QCR04 as sepcified in the ITP.
| 02SL - Stations (LUL) | Cxxx-NCR-002580 | NCR | R10S Application of PSK to Eastern perimeter beams |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-01-01 | 2018-12-21 14:23 | -11 | 2018-11-22 12:59 | Fire - Fire Systems & General | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | __ to the East and West perimeter beams of R10S (see marked up DWG) was removed to allow the installation of __ facia brackets. Upon reinstatement of the __ the site team cleaned the substrate and re applied PSK 101 where necessary. It has come apparent that the substrate must be abraded back to the interseal coating as the PSK 101 is pealing due to poor adhesion with the areas of the beam previously coated in __.
| 02SL - Stations (LUL) | Cxxx-NCR-002581 | NCR | Door Clash with MCC20 (Vent Plant Room) |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-02-28 12:20 | -123 | 2018-11-22 16:04 | Electrical - LV Equipment | 6000 |  | Design | Use As-Is | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | The door which opens inwards to the Vent Plant Room (South Accommodation) clashes with the side of MCC20 Panel.
| 02SL - Stations (LUL) | Cxxx-NCR-002582 | NCR | LULO - GSM - Works Commencing Without Approved Drawings |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-02-15 | 2019-03-29 16:26 | 42 | 2018-12-05 09:23 | Architectural - Doors | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | 12no GSM Door drawings, did not have 'C' status at the point of installation. these are listed below and attached in the reference documents Cxxx-__M-A-DWG-D061_WS106-53777 - P03 Cxxx-__M-A-DWG-D061_WS106-53811 - P02 Cxxx-__M-A-DWG-D061_WS106-53812 - P02 Cxxx-__M-A-DWG-D061_WS106-53816 - P06 Cxxx-__M-A-DWG-D061_WS106-53820 - P02 Cxxx-__M-A-DWG-D061_WS106-53822 - P02 Cxxx-__M-A-DWG-D061_WS106-53823 - P02 Cxxx-__M-A-DWG-D061_WS106-53826 - P02 Cxxx-__M-A-DWG-D061_WS106-53829 - P02 Cxxx-__M-A-DWG-D061_WS106-53830 - P02 Cxxx-__M-A-DWG-D061_WS106-53831 - P02 Cxxx-__M-A-DWG-D061_WS106-53832 - P02
| 02SL - Stations (LUL) | Cxxx-NCR-002583 | NCR | Working to P Rev Drawing |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-01-25 | 2019-01-29 15:44 | 4 | 2018-11-28 15:02 | Electrical - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | C Revision drawings were reissued as P Revision with additional information and subsequently sat on EB for a considerable amount of time. Due to programme requirements work had to be carried out whilst the drawings were still at P Revision.
| 02SL - Stations (LUL) | Cxxx-NCR-002584 | NCR | LULO GSM - Non Compliance With Control of Drawings Process |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-03-20 | 2019-03-29 11:11 | 9 | 2018-11-29 16:10 | Architectural - Doors | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The below GSM door drawings have not followed the correct process of approval, according to the Control of Drawings Quality Process Cxxx-__M-O4-GPS-D061-50002 Section 6.6 in that the last P revision of the drawings had not been approved by CRL prior to the submission of 'C' revisions. Cxxx-__M-A-DWG-D061_WS106-53772 Cxxx-__M-A-DWG-D061_WS106-53773 Cxxx-__M-A-DWG-D061_WS106-53774 Cxxx-__M-A-DWG-D061_WS106-53775 Cxxx-__M-A-DWG-D061_WS106-53780 Cxxx-__M-A-DWG-D061_WS106-53785 Cxxx-__M-A-DWG-D061_WS106-53789 Cxxx-__M-A-DWG-D061_WS106-53791 Cxxx-__M-A-DWG-D061_WS106-53796 Cxxx-__M-A-DWG-D061_WS106-53800 Cxxx-__M-A-DWG-D061_WS106-53802 Cxxx-__M-A-DWG-D061_WS106-53803 Cxxx-__M-A-DWG-D061_WS106-53805 Cxxx-__M-A-DWG-D061_WS106-53807 Cxxx-__M-A-DWG-D061_WS106-53808 Cxxx-__M-A-DWG-D061_WS106-53814 Cxxx-__M-A-DWG-D061_WS106-54367 Cxxx-__M-A-DWG-D061_WS106-53815 Cxxx-__M-A-DWG-D061_WS106-53819 Cxxx-__M-A-DWG-D061_WS106-53824 Cxxx-__M-A-DWG-D061_WS106-53825 Cxxx-__M-A-DWG-D061_WS106-53827 See attached break down with further information as to the different 'P' revisions reviewed.
| 02SL - Stations (LUL) | Cxxx-NCR-002591 | NCR | LULO Damaged fire boarding |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2021-08-10 13:39 | 406 | 2018-12-01 10:48 | Fire - Compartmentation | 6000 |  | Damaged | Reject | 3 (3-6k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Fireboarding at the top of Stair 22 has been damaged due to water ingress. The Contractor is to confirm water ingress has stopped and replace any damaged boards. This is as per CRL-OBS-25764 raised 06/11/18.
| 02SL - Stations (LUL) | Cxxx-NCR-002592 | NCR | DSS Lifting beam washers |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2019-01-10 | 2019-01-15 11:31 | 5 | 2018-12-01 11:02 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As witnessed during IRF-Shafts-1377, temporary washers and bolts have been used. This was identified during the inspection after a query was raised regarding dissimilar metals. The Contractor is to provide further information regarding the failed inspection and proposal/evidence to close out. This is as per CRL-OBS-25744 raised 09/11/18.
| 02SL - Stations (LUL) | Cxxx-NCR-002593 | NCR | DSS Ductwork- failed inspection |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2019-01-10 | 2019-01-08 09:22 | -2 | 2018-12-01 11:11 | Mechanical - Mechanical Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | An inspection of the staircase pressurisation ductwork system found gaps in the manufacture/installation of the duct work on mezz flange joints and branch shoes that have been cut into the main duct. There is no confidence that this ductwork leakage is acceptable and therefore should be fully leak tested to prove that leakage is acceptable. Consequently the inspection failed. This is as per CRL-OBS-25640 raised 01/11/18
| 02SL - Stations (LUL) | Cxxx-NCR-002594 | NCR | ITP checksheets- uncontrolled changes |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2019-04-25 | 2019-11-01 17:31 | 190 | 2018-12-01 11:21 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - No evidence of program review from Contractor's Quality Manager or Management | Completed |  | There are instances where changes have been made to ITP checksheets (approved documents). __ to fully investigate the issue and confirm how they manage this from an assurance perspective. This is as per CRL-OBS-25676, raised 07/11/18
| 02SL - Stations (LUL) | Cxxx-NCR-002596 | NCR | LULO 1DN Plant Room- damage |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2019-01-31 | 2019-02-27 14:54 | 27 | 2018-12-01 11:52 | Mechanical - Mechanical Engineering General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | 1 no. duct has damage to the silver tape layer, which has left the insulation exposed. This is as per CRL-OBS-25418 raised 16/10/18. No evidence found on snagR.
| 02SL - Stations (LUL) | Cxxx-NCR-002597 | NCR | LCR ATS Outgoing cable upgrades |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-03-03 | 2019-02-20 13:27 | -11 | 2019-01-22 14:30 | Electrical - General | 5000 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | Outgoing cables upgraded due to design mistake on outgoing cables from all LCR ATS's. The original design showed a 2 core cable from the ATS to the Castell, when the Castell Isolators installed on site are three phase, meaning the cables need to be upgraded to 4 core. After approval from __, 25mm 4 core cable was agreed to be used for both outgoing from all LCR ATS's.
| 02SL - Stations (LUL) | Cxxx-NCR-002598 | NCR | R10S Roof works undertaken - ITP to be amended to reflect new condition |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-01-13 | 2019-01-30 18:32 | 17 | 2018-12-04 11:51 | Architectural - Roofing & Exterior Treatment | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | The current ITP: Cxxx-__M-A-ITP-D061_WS106-50120 R7.0 (Decal Code 1 06.08.2018), did not reflect the installation/size/torqueing of the Hollo Bolts tbc by __.
| 02SL - Stations (LUL) | Cxxx-NCR-002600 | NCR | Rooflight brackets installed without code 1 CATII check |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-01-30 | 2019-03-10 16:57 | 39 | 2018-12-07 17:05 | Architectural - Roofing & Exterior Treatment | 3600 |  | Supervision/Management | Rework | 3 (3-6k) | Complete | Management Problem - Inadequate administrative control | Completed |  | 5no rooflight brackets were installed without a code 1 CATII check. 2no in R12 (for rooflight 1), 1no in R10N (for rooflight 36), and 2no in R10S for rooflights 77, and 86.
| 02SL - Stations (LUL) | Cxxx-NCR-002602 | NCR | LULO __ Steelwork Protection - Area 1 Link Tunnel Circular Columns and Beams Missing Checksheets |  | Contr | LAO | WHI - Whitechapel Station (Central) |  | 2019-10-16 | 2019-09-19 11:32 | -27 | 2019-07-18 12:06 | Civil - Civil Engineering General | 1500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | There was no Sharp Fibre Quality Checksheets in place for Area 1 Upper Link Tunnel Circular Columns and Beams. Most of the works had been carried out during night shift and the application of the __ had been recorded on time sheets/commercial sheets.
| 02SL - Stations (LUL) | Cxxx-NCR-002603 | NCR | DSS screeding lack of progressive assurance |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-02-15 | 2019-02-27 14:58 | 12 | 2018-12-07 15:21 | Architectural - Flooring | 1000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | There are no checksheets or IRFs showing progressive assurance of screed installation in Durward Street Shaft from 2016 until February 2018. There is sufficient evidence of works being carried out in line with specification requirements (photographs, independent drop hammer tests) which will allow __ and __ to prepare required documentation for Crossrail approval and acceptance.
| 02SL - Stations (LUL) | Cxxx-NCR-002604 | NCR | CHS Level 5 BMS Secondary CMS - Assured Design Sketch |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-03-17 | 2019-03-27 15:13 | 10 | 2018-12-07 15:42 | Electrical - Cable Management | 2000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Trunking installed as secondary CMS by __ without assured design.
| 02SL - Stations (LUL) | Cxxx-NCR-002605 | NCR | Crossrail Platforms __ Access Covers |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-09-02 | 2019-08-08 08:45 | -25 | 2018-12-07 16:49 | Architectural - Flooring | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | During inspection of __ access covers __ identified that 5no AHP-125 access covers (MH9, MH15, MH20, MH30 & SH4) have not had the fixings for the beam support bracket drilled deep enough (minimum embedment should be 85mm) or/and the wrong fixings have been used. (RAWL plugs which ave no MCR. __ fixings should be used)
| 02SL - Stations (LUL) | Cxxx-NCR-002607 | NCR | LO - Waterproofing detail to West stair shaft |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-03-06 | 2019-08-14 08:02 | 161 | 2018-12-10 14:26 | Civil - Civil Engineering General | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | __ are required to install a waterproofing membrane to the surface of the West stair shaft as shown in DWG Cxxx-HYD-C-DDB-D061_WS105_Z-23042. It has previously been confirmed through Cxxx-RFI-004903 that Flexiphalte Pommar 5077 waterproofing system is suitable. Upon inspection of the existing __ that was previously installed between the Capping beam and liner wall of the West stair shaft it has been identified that its condition is not suitable to provide a 150mm overlap required between the two waterproofing systems. A specialist waterproofing contractor and ‘GCP’ applied technologies have been consulted and they advise that the attached detail (FCD 2607 mark-up) will provide a waterproofing system incorporating the existing __. It is proposed to coat the slab either side of the existing __ with a 150mm wide strip of Aquatek Super XA which is a cementitious coating which draws into the concrete at least 50mm deep and will provide a waterproofing link to the __ then continue with the detailed deck treatment with Integritank liquid waterproofing to the edge of the Aquatek.
| 02SL - Stations (LUL) | Cxxx-NCR-002608 | NCR | BAL 123 Lamp Post Connection Adaption |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-01-27 | 2019-04-03 19:32 | 66 | 2018-12-11 11:46 | Architectural - Balustrade | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | Due to a setting out error onsite, two no. holes for one of the balusters have been drilled in the wrong place.
| 02SL - Stations (LUL) | Cxxx-NCR-002609 | NCR | LO - WSS and CW126 40N bag mix cube failure |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-01-28 | 2019-02-12 16:30 | 15 | 2018-12-12 12:13 | Civil - Civil Engineering General | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | 28 day compressive strength results for concrete cubes taken as part of construction of the West Stair Shaft and Covered way 126 concrete piers have not reached the required 40N strength. 28 day results are as follows and shown in attached Cube reports West stair shaft – 28.9N/mm^2 Covered way 126 – 35.3N/mm^2
| 02SL - Stations (LUL) | Cxxx-NCR-002610 | NCR | LULO - HCDL Platforms - Circular Column Cladding - Multiple Incorrect Fixings due to Unconstructable Design |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-04-16 | 2019-02-22 10:21 | -53 | 2019-01-16 12:18 | Architectural - General | 5750 |  | Workmanship | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The circular column cladding Z brackets have been re-drilled several times with unacceptable spacings. Please see attached photographs, highlighting the issue.
| 02SL - Stations (LUL) | Cxxx-NCR-002616 | NCR | CHS Level A BMS Secondary CMS - Assured Design Sketch |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-09-20 | 2019-10-19 15:20 | 29 | 2019-03-06 15:52 | Electrical - Cable Management | 2000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | CMS installed without a prior assured design
| 02SL - Stations (LUL) | Cxxx-NCR-002617 | NCR | CHS Level B BMS Secondary CMS - Assured Design Sketch |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-04-16 | 2019-10-18 11:10 | 185 | 2019-03-07 08:42 | Electrical - Cable Management | 2000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | CMS installed for the BMS without an approved design
| 02SL - Stations (LUL) | Cxxx-NCR-002618 | NCR | CHS MCC VRF Change |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-01-28 | 2019-04-05 12:31 | 67 | 2018-12-19 08:33 | Electrical - Switchgear | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Modifications carried out to Section B4 on both VRF MCC panels CHS/VRF/A & CHS/VRF/B before a FCD was raised & approved.
| 02SL - Stations (LUL) | Cxxx-NCR-002619 | NCR | DSS Level 7 PCC panel finish |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2021-02-08 08:55 | 223 | 2018-12-20 10:34 | Architectural - Finishes | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | PCC panels in DSS Level 7 have been installed / cleaned and signed off by __ and CRL (please see attached picture before anti-graffiti coating). After anti-graffiti coating applied, panels became patchy and are not uniform. Please see attached pictures (after anti-graffiti coating applied). Panels finish does not comply with acceptable standard. Cost impact for remedial works - £1500 No programme impact depending on approval of remedial works
| 02SL - Stations (LUL) | Cxxx-NCR-002620 | NCR | R12 Roof Spandrel Panel Clash |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-03-06 | 2019-05-10 06:15 | 65 | 2019-01-25 12:43 | Architectural - Roofing & Exterior Treatment | 5600 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | __'s sub-contractor __, have procured spandrel panels for the R12 roof. Whilst installing the panels it was found that there are four locations where the panels clash with rooflight frames. As a result, four bespoke spandrel panels are required to be manufactured.
| 02SL - Stations (LUL) | Cxxx-NCR-002621 | NCR | CHS External CMS |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-01-29 | 2019-04-20 11:51 | 81 | 2018-12-20 10:56 | Electrical - Cable Management | 5000 |  | Documentation and Records | Use As-Is | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | External CMS on CHS is installed to unapproved red line drawings.
| 02SL - Stations (LUL) | Cxxx-NCR-002622 | NCR | __ Door Design GS/D1/065 Missing Vision Panel |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-03-28 | 2019-05-18 10:53 | 51 | 2018-12-20 16:02 | Architectural - Doors | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Door GS/D1/065 in the GSM building has not been designed and manufactured with a vision panel making it non-compliant with the Building Regulations 2010. This door is currently installed and within a fire escape route in a back of house area.
| 02SL - Stations (LUL) | Cxxx-NCR-002623 | NCR | Door Installation Benchmarks and Samples have not been submitted |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-04-20 | 2021-01-27 21:13 | -83 | 2018-12-31 14:53 | Architectural - Doors | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Door quality benchmarks as per Cxxx-__M-A-RSP-D061-50079 Section JL20.2105 and door samples as per Cxxx-__M-A-RSP-D061-50079 JL20.2102 have not been provided in a timely manner for QA package submissions. Benchmarks of the first completed installation of each type of manually operated doorset should have been completed. All samples have not been received from the supplier.
| 02SL - Stations (LUL) | Cxxx-NCR-002626 | NCR | LU - Stair 23 - VE cladding Handrail supports and penetrations |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-10-07 18:02 | 99 | 2019-01-14 16:17 | Archaeology - General | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | __ have designed, fabricated and installed vitreous enamel panels, with the handrail penetrations not in line with co-ordinated F2 discussions (instructed) - regarding an incorporation of penetrations for handrails. Due to this, several issues have arisen, requiring redesign and refabrication of both several panels and subframe steelwork. These works are currently installed on site and will require removal works. Issues of note: 1. There is no PFC or steelwork behind the penetrations in some locations (approx 3) - see photo 1 in attached guide for reference. 2. In 4no locations, there are top hats (of which the VE panel is mounted to) behind the penetrations. We have no confirmation that this top hat can provide the structural integrity required - see photo 2 in attached guide for reference. 3. In 4no locations, there is a return on the VE panel clashing with the penetration. We have been advised that on-site drilling or and work to the panels is not acceptable - see photo 3 in attached guide for reference
| 02SL - Stations (LUL) | Cxxx-NCR-002627 | NCR | missing RWP's |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-02-19 | 2019-03-28 09:02 | 37 | 2019-01-10 11:19 | Mechanical - Public Health Engineering | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | there is no public health drawing available that shows 4no RWP's that connect the upper and lower concourse roofs to the underground drainage. we installed the pipework so that there is no water ingress into the area below
| 02SL - Stations (LUL) | Cxxx-NCR-002628 | NCR | CHS - Internal Screed - Minor FFL tolerance exceedances |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-02-24 | 2019-01-25 11:48 | -30 | 2019-01-15 13:20 | Architectural - Flooring | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In accordance with the Architectural Specification Cxxx-__M-A-RSP-D061-50079_75 Cl JM10.3223, the permissible deviation of a screeded floor finish level is limited to +-3mm. The attached asbuilt survey report for the CHS internal screed contains a number of marginal exceedances of these tolerances. These are as follows: Level 1: +4mm Level 3: -7mm (D3/009) and -6mm (D3/013) - both poured to match adjacent concrete level Level 4: +5mm (against the FFL revisions of Cxxx-FCD-001860) Level 8: +6mm (D8/005), -4mm (D8/003 landing), -5mm (D8/012) and -4mm (8/771)
| 02SL - Stations (LUL) | Cxxx-NCR-002629 | NCR | working out of sequence |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-02-20 | 2019-03-04 11:08 | 12 | 2019-01-11 12:09 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inadequate work environment | Completed |  | Due to the tight restraints and safety issues it was agreed that when we were installing the ductwork to riser B2 it would be safer to lag the ductwork as the duct was installed. keeping it a safe place to work. however this meant that we would be going past a hold point on the ITP
| 02SL - Stations (LUL) | Cxxx-NCR-002630 | NCR | __DB2/10L1 cable damadged |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-02-23 | 2019-08-14 15:02 | 172 | 2019-01-14 11:24 | Electrical - LV Equipment | 1500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Prior to Crossrail inspection __DB2/10L1 circuit was inspected to find the cable was damaged and insulation had been damaged which impacted the cables integrity and not providing sufficient protection.
| 02SL - Stations (LUL) | Cxxx-NCR-002631 | NCR | CHS - Internal Screed - Drop Hammer Calibration Certificate |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-02-24 | 2019-01-22 11:58 | -33 | 2019-01-15 14:47 | Architectural - Flooring | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | In accordance with Item 6.1 of Cxxx-__M-A-ITP-D061-50031_03, calibration certificates for all screed soundness and hygrometer test equipment shall be provided. The test house 4-Rail are unable to provide the calibration certificate for the drop hammer equipment utilised in the following reports; 4RS-MC-160650-R563751, 4RS-MC-160604-R561776 and 4RS-MC-160669-R567601. *Update 16/01/2019* The above calibration certificate is the same missing from DSS screed soundness Report 4RS-MC-160650-R563752.
| 02SL - Stations (LUL) | Cxxx-NCR-002632 | NCR | ETH __ & __ Ceiling Installation - Works Commencing Without An Approved ITP |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-03-04 | 2019-03-10 17:25 | 6 | 2019-01-16 13:27 | Architectural - Ceilings & Soffits | 700 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | The ETH __ & __ Ceiling Installation works Commenced Without An Approved ITP that contained all elements of work. - The __ ITP [Cxxx-__M-A-ITP-D061_WS106-50181 Rev 04] did not include Installation of __ RW5 and wire mesh. - The __ ITP [Cxxx-__M-A-ITP-D061_WS106-50199 Rev 01] did not include Installation of __ channels.
| 02SL - Stations (LUL) | Cxxx-NCR-002633 | NCR | DSS - Internal Screed - Minor FFL Tolerance Exceedances |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-02-26 | 2019-01-25 12:34 | -32 | 2019-01-17 14:25 | Architectural - Flooring | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In accordance with the Architectural Specification Cxxx-__M-A-RSP-D061-50079_75 Cl JM10.3223, the permissible deviation of a screeded floor finish level is limited to +-3mm. The attached asbuilt survey report for the DSS internal screed contains a number of marginal exceedances of these tolerances. These are as follows: Level 4: +17mm (ESR 4/666) Level 5: -5mm and +5mm (SRLV 5/661), -8mm (SRLV 5/662), +16mm (CER 1 5/731) Level 7: +13mm (D7/018) Level 8: -4mm (UPE 8/908), -5mm (8/925), -5mm (8/923), +5mm (8/919), +6mm (8/903), -5mm (8/EST1)
| 02SL - Stations (LUL) | Cxxx-NCR-002634 | NCR | LULO - HCDL - ESS - Precast Concrete Cladding - Large chips present in finished works |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-05-17 | 2019-05-17 11:18 | 0 | 2019-01-18 11:53 | Architectural - General | 3500 |  | Workmanship | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | Large chips are present on the final installed products (Segmented Cladding Panels) and small chips present on the copings. This is not acceptable, as per the specification. See attached photographs for reference.
| 02SL - Stations (LUL) | Cxxx-NCR-002636 | NCR | DSS Node 2 Loop 1 Energisation without an Accepted IRN |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2019-03-02 | 2019-09-08 08:34 | 190 | 2019-01-21 14:41 | Fire - Detection | 2000 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | DSS Node 2 Loop 1 energised prior to submission and acceptance of associated Installation Release Notice (IRN). This is in contravention of the CRL Testing & Commissioning Process Overview for Stations, Portals & Shafts (CRL1-XRL-O7-GPS-CR001-50007) issued under Cxxx-PMI-00449 and the Contractor's own Testing & Commissioning Plan (Cxxx-__M-O3-GPS-D061-50001 ). Cxxx-NCR-002370 (LULO - GSM - Fire Alarm Panel Energised prior to IRN acceptance) previously raised on this topic.
| 02SL - Stations (LUL) | Cxxx-NCR-002637 | NCR | Stair 25 Baluster Position Adjustment |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-03-02 | 2019-04-11 10:34 | 40 | 2019-01-21 16:27 | Architectural - Balustrade | 7800 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | As per attached sketch, the balustrade design in Stair 25 leaves the top flight handrail low in the centre.
| 02SL - Stations (LUL) | Cxxx-NCR-002638 | NCR | Stair 21 East Stringer Notching |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-03-04 | 2019-09-25 07:44 | 205 | 2019-01-23 13:42 | Architectural - Balustrade | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In order to install the BAL 112 balustrade on the East stringer of Stair 21, Eurosafe set-out the line of the balusters showing a significant clash with the stringer and stair paving. The paving and stringer were notched out to accommodate the baluster install, however during this process the brackets were packed out to beyond the original edge of the stringer, making the enabling works unnecessary.
| 02SL - Stations (LUL) | Cxxx-NCR-002639 | NCR | Access Gantry 3A Incorrect Drilling |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-03-04 | 2019-03-25 09:20 | 21 | 2019-01-23 16:17 | Architectural - Balustrade | 1200 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | The first fix element for Gantry 3A has not been drilled central to the structural steel beam (as per design).
| 02SL - Stations (LUL) | Cxxx-NCR-002640 | NCR | CHS/VRF/A & CHS/VRF/B Modifications |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2019-06-05 | 2019-09-02 11:51 | 89 | 2019-01-24 10:38 | Electrical - General | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Personnel Error - Inattention to detail | Completed |  | CHS/VRF/A MCC & CHS/VRF/B MCC have been modified due to condenser upgrades. Cxxx-FCD-003160 was raised confirming - Modification to CHS/VRF/A section B4 cable E411. Upgrade the CDP to 80A and the cable size increased to 25mm Modification to CHS/VRF/B section B4 cable E432. Upgrade the CDP to 80A and the cable size increased to 25mm Subsequently Cxxx-NCR-002618 has been raised due to Modifications carried out to Section B4 on both VRF MCC panels CHS/VRF/A & CHS/VRF/B before a FCD was raised & approved. Reviewing in line with Cxxx-__M-E-NOX-D061_WS107-50182 Installation Release Notice - CHS VRF/A MCC Outgoing Cables (E411,E412,E413 & E414) and Cxxx-__M-E-NOX-D061_WS107-50187 Installation Release Notice - CHS VRF/B MCC Outgoing Cables (E432,E433,E434 & E435), it would seem that E411 cable increase has been captured within the IRN and the live test records (attached). E432 cable size has not been increased as per the IRN or the live test records (attached). After various discussions it seems that the PTR and Cxxx-FCD-003160 referenced E432 in error instead of E433. E433 cable size has been increased, without modifications to the breaker but additionally CHS/VRF/B section B4 (E432) breaker size has been increased to 80A where the cable hasn’t (datasheet for Current Carrying Capacity showing 78A). In addition, the live test results reference the wrong BS – but specifies the protection device set at 50A rather than 80A - this raises concerns over the assurance documentation being provided and the checks undertaken on site and not just referenced against what the design states.
| 02SL - Stations (LUL) | Cxxx-NCR-002641 | NCR | LPDB2/B Changes Post IRN |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-03-03 09:18 | -119 | 2019-01-24 10:55 | Electrical - General | 1500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | On review of DSS LPDB2/B PCC I have discovered an additional 3 phase circuit (3L1 – 3L3) that was not captured in the IRN / Construction Record Dead Test, or the current accepted DB Schedule. I understand that there has been no PTR raised to BH – although they have updated their records and provided a response via email. Therefore after conducting an eB report have found no CRL PTR proposing this additional circuit which I believe is for a Fan Coil Unit. In addition and in line with the above, see no evidence or authorisation to install and energise this circuit. The live test records attached show that this circuit has been energised and therefore I will be raising an NCR. We need to ensure that changes post IRN, including completion of outstanding works and additional works, are better managed and follow the various processes and procedures. Please also note that circuit 1L2 that was installed / dead tested has no live test results (in the attacehed). This in addition to the errors on E432 Live Test sheet sent this morning raises issues and concerns over the assurance records being submitted.
| 02SL - Stations (LUL) | Cxxx-NCR-002644 | NCR | __ Construction installed incorrect fixings to fix __ to PFC in the ETH ceiling |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-03-06 | 2019-02-20 10:41 | -14 | 2019-01-25 13:08 | Architectural - Ceilings & Soffits | 2700 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __ Construction installed incorrect fixings to fix __ to PFC in the ETH ceiling
| 02SL - Stations (LUL) | Cxxx-NCR-002645 | NCR | WHI TTH CER ATS - Lack of SAT / Commissioning documentation |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2019-03-09 | 2019-03-07 10:40 | -2 | 2019-01-28 16:08 | Electrical - General | 10000 |  | Testing and Commissioning | Use As-Is | 2 (6-60k) | Complete | Verification Problems - Other | Completed |  | The ATS had not been set up correctly as both the Main Failure Time (MfT) and Main Return Time (MrT) were set at 0 seconds and 0 minutes respectively. This was not consistent with LU Specs nor manufacturers default settings and therefore the documentation within the MAID was interrogated, but there were no SAT or commissioning results within the documents to help understand the settings.
| 02SL - Stations (LUL) | Cxxx-NCR-002647 | NCR | CHS Level 6 Field Device Locations |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-07-18 | 2019-04-11 12:39 | -98 | 2019-04-09 14:20 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | BMS Field device locations assured by __ and reviewed by __ as shown on __-SKETCH-0109, 0110, 0111 and 0112 IRF number - IRF_MEP PERM_CHS_0366 IRN number - Cxxx-__M-M-NOX-D061_WS107-50010
| 02SL - Stations (LUL) | Cxxx-NCR-002648 | NCR | CHS Level 5 Field Device Locations |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-03-30 | 2019-04-02 09:44 | 3 | 2019-02-18 15:46 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | BMS Field device locations assured by __ and reviewed by __ as shown on __-SKETCH-0015, 0017, 0051 and 0052 IRF number - IRF_MEP PERM_CHS_0355 IRN number - Cxxx-__M-M-NOX-D061_WS107-50009 MCC Field device locations assured by __ and reviewed by __ as shown on __-SKETCH-0016, 0018, 0019, 0020, 0035 and 0068. IRF number - IRF_MEP PERM_CHS_0357 IRN number - Cxxx-__M-M-NOX-D061_WS107-50048
| 02SL - Stations (LUL) | Cxxx-NCR-002649 | NCR | Installation has commenced and is progressing using unaccepted ‘P’ revision drawings. |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2019-03-13 | 2019-08-22 11:24 | 162 | 2019-02-01 10:49 | Architectural - Roofing & Exterior Treatment | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Management Problem - No evidence of program review from Contractor's Quality Manager or Management | Completed |  | During a planned surveillance the Contractor submitted ‘Sequence Pack 7 (R12 Lower Concourse) By Exception’ Cxxx-__M-C-RGN-D061_WS106-53075 (Rev 3), dated June 2018 and ‘Installation of __ panels and associated bracketry By Exception’ Cxxx-__M-C-RGN-D061_WS106-50119 (Rev 1), dated June 2018. On checking eB it was found that both documents including the listed drawings were found to be place holders on were found to be place holders. It was confirmed that the installation is continuing using unaccepted ‘P’ status drawings
| 02SL - Stations (LUL) | Cxxx-NCR-002650 | NCR | By Exception Procedure has not been followed correctly. |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2019-03-13 | 2019-08-23 13:21 | 163 | 2019-02-01 11:16 | Architectural - Roofing & Exterior Treatment | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | During a planned surveillance the Contractor submitted ‘Sequence Pack 5 (R12 Lower Concourse) By Exception’ Cxxx-__M-A-RGN-D061_WS106-50110 (Rev 2), dated June 2018. On checking eB the document has not been approved, on checking the drawings listed within the ‘By Exception’ all were found to be at C01 for construction. Further checks found that no NCR has been raised in line with ‘By Exception Construction Prior to Gate Acceptance for Station, Shafts and Portals’ Procedure CRL1-XRL-O7-GPD-CR001-50023 (Rev 2)
| 02SL - Stations (LUL) | Cxxx-NCR-002651 | NCR | DSS Level 1 Field Device Locations |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-06-30 | 2019-03-27 14:36 | -95 | 2019-03-22 16:10 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | BMS Field device locations assured by __ and reviewed by __ as shown on __-SKETCH-0096, 0097 and 0098.
| 02SL - Stations (LUL) | Cxxx-NCR-002652 | NCR | No evidence provided for sample acceptances |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2019-03-13 | 2019-09-25 09:02 | 196 | 2019-02-01 11:29 | Architectural - Roofing & Exterior Treatment | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | During a Planned surveillance the Contractor was requested to provide evidence of sample acceptance in line with Architectural Specification Cxxx-__M-A-RSP-D061-50079 JH13.2102; Samples of the following shall be provided, in accordance with Section JA.4000 of the Specification. a) Examples of proposed types of finish and colours. b) Minimum 300mm lengths of all proposed materials and components forming the secondary support. c) All visible fixings and fittings. d) Proposed ironmongery and hardware. _e) Operating mechanisms, switches and controls, including mounting. f) 300mm length of each type of framing/ channel, with finishes and colours, and including the interface (method of attachment) with the glazing and solid infill panel and joints. g) All accepted gasket types, extrusions, caps, trims and flashings, including at least one joint and one corner joint and including finishes and colours where applicable
| 02SL - Stations (LUL) | Cxxx-NCR-002653 | NCR | LO - Set out of Fascia Top Hats |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-04-05 | 2019-04-23 07:42 | 18 | 2019-02-04 14:40 | Architectural - General | 3500 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the set out of the 3rd fix of the fascia it was discovered that in the sloped sections of the concourse roof the 1st fix had been set out incorrectly. This error means that the fascia panel joint would not fix into the 3rd fix top hat correctly.
| 02SL - Stations (LUL) | Cxxx-NCR-002654 | NCR | DSS Level 6 Field Device Locations |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-05-01 | 2019-04-03 13:30 | -28 | 2019-03-22 16:51 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | BMS Field device locations assured by __ and reviewed by __ as shown on __-SKETCH-0029, 0027, 0025 and 0023 IRF number - IRF_MEP PERM_DSS_0460 IRN number - Cxxx-__M-M-NOX-D061_WS105-50011 MCC Field device locations assured by __ and reviewed by __ as shown on __-SKETCH-0028, 0024, 0026 and 0030. IRF number - IRF_MEP PERM_DSS_0510 IRN number - DSS MCC-06 (AHU) Panel Outgoing Cables (Control) - Currently No Placeholder - To be included at implementation
| 02SL - Stations (LUL) | Cxxx-NCR-002655 | NCR | DSS Level 5 Field Device Locations |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-05-12 | 2019-04-04 14:12 | -38 | 2019-04-02 13:42 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | BMS Field device locations assured by __ and reviewed by __ as shown on __-SKETCH-0116, 0117, 0118, 0119, 0120, 0121 and 0122 IRF number - IRF_MEP PERM_DSS_0447 IRN number - Cxxx-__M-M-NOX-D061_WS105-50010
| 02SL - Stations (LUL) | Cxxx-NCR-002656 | NCR | Fire Alarm and Detection Concourse / Ticket Hall, Upper Concourse Level |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-02-08 13:26 | -143 | 2019-02-05 16:12 | Fire - Fire Systems & General | 5000 |  | Supervision/Management | Use As-Is | 3 (3-6k) | Complete | Management Problem - Other | Completed |  | The below Fire Alarm and Detection Drawings for Concourse / Ticket Hall, Upper Concourse Level are the latest drawings on eB and are Code 3 - Cxxx-__M-E-DWG-D061_WS106-50211 P02 Cxxx-__M-E-DWG-D061_WS106-50213 P02 Cxxx-__M-E-DWG-D061_WS106-50214 P03 Cxxx-__M-E-DWG-D061_WS106-50215 P03 It has been noted that installation works have commenced and or are at various stages (Secondary Containment, Wiring, 2nd Fix, 3rd Fix) in line and or deviating from the above drawings – with no accepted design. As per Cxxx-__M-E3-ITP-D061-50001 CRL have requested that __ provide evidence that the witness points have been adhered to as detailed in said ITP. No verifying documents specified in the ITP have been provided. In addition, finishes such as ceiling tiles are now being fitted on site which will require removal to adhere to the various ITP witness points such as Secondary CMS installation. Works currently being undertaken to Cxxx-__M-E3-ITP-D061-50001 which is not accepted.
| 02SL - Stations (LUL) | Cxxx-NCR-002657 | NCR | LULO - 1DN - Door D1/034 - Secondary steel installed with incorrect orientation |  | Contr | VIN | WHI - Whitechapel Station (Central) |  | 2019-11-29 | 2019-07-04 09:58 | -148 | 2019-02-06 17:20 | Archaeology - General | 5500 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Management Problem - Inadequate administrative control | Completed |  | __ F2 drawing (Cxxx-__M-A-DWG-D061_WS106-53579) shows the secondary steel support cladding and door openings. Detail 5 of this drawing shows a steel PFC section on either side of the door opening. The steel is oriented such that that back (flat face) of the PFC faces the door opening and therefore provides a suitable surface to fix fire boards and door. The PFCs on either side of the door have been installed in the incorrect orientation (recess of the PFC towards door opening).
| 02SL - Stations (LUL) | Cxxx-NCR-002658 | NCR | Lower Concourse Under Floor CMS Replacement - Mechanical Protection for Cabling |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-03-23 10:34 | -99 | 2019-02-07 15:29 | Electrical - General | 2000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Lower Concourse under floor CMS being replaced as part of Cxxx-NCR-002213 During inspection / visual survey, cables (which have not been inspected / signed off) have been installed. __ to confirm ITP witness points adhered to. In addition, these cables have no mechanical protection during the replacement of CMS
| 02SL - Stations (LUL) | Cxxx-NCR-002659 | NCR | LU - WSME - External Cladding - Lack of Assurance Documentation |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2021-09-29 09:25 | 456 | 2019-02-12 11:07 | Architectural - General | 1500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | The installation works for the external cladding at the WSME have already been completed. However neither the design certificate nor the off-site and on-site construction records have been submitted yet. Please refer to Cxxx-CCM-17894 regarding warranties provided by __ for the supply chain. No warranty is available for __ works (WSME external cladding in this case) and is instead covered by the JV collateral warranty.
| 02SL - Stations (LUL) | Cxxx-NCR-002660 | NCR | FCD/ change of design was not presented at inspection of IRF 50375. P0.1 referenced drawings were issued on inspection |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-04-06 | 2019-02-26 09:13 | -39 | 2019-02-25 15:14 | Electrical - Earthing & Bonding | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | NCR raised due to referenced P0.1 drawings on IRF invitation 50375. These are internal drawings between __ and BH and are not CRL accepted drawings.
| 02SL - Stations (LUL) | Cxxx-NCR-002662 | NCR | WHI/DSS/CRLP/B Door Opening Direction |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-08-25 13:37 | 56 | 2019-02-15 11:13 | Electrical - LV Equipment | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | Cxxx-NCR-002307 was raised due to not meeting BS 7671 - Minimum Passing Width in case of evacuation = 700mm On further review of room finishes, WHI/DSS/CRLP/B Door Opening Direction does not conform with the requirements of BS7671 - "Doors and hinged panels of equipment are to be installed to close in the direction of the exit route"
| 02SL - Stations (LUL) | Cxxx-NCR-002663 | NCR | Escalator __ / Aspirator Installation to Non Accepted Drawings |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2019-03-28 | 2019-08-14 10:39 | 139 | 2019-02-16 10:27 | Fire - Detection | 1500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | On review of IRN - __ / __have completed the installation of Escalator __ to non accepted drawings. In addition, the installation has deviated from said drawings without adhering to the change control process
| 02SL - Stations (LUL) | Cxxx-NCR-002664 | NCR | Fascia Bracket Drilled Incorrectly |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-03-28 | 2019-06-12 11:56 | 76 | 2019-02-16 13:13 | Architectural - Roofing & Exterior Treatment | 600 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __'s subcontractor, __, is currently installing the Fascia on the Upper Concourse roof. During the installation of a second fix 'box section' bracket, a human error was made whilst drilling, as a result, the 'box section' bracket was not installed in the correct location. In order to adjust the bracket to its correct position, two additional holes were drilled into the first fix bracket. The additional holes are too close to the original holes to ensure the structural integrity of the bracket.
| 02SL - Stations (LUL) | Cxxx-NCR-002665 | NCR | Installation without approved drawings |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-04-30 | 2020-06-17 11:26 | 414 | 2019-02-18 14:39 | Electrical - Cable Management | 3000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Relief trunking installed in the HCDL for SWIP without approved drawings.
| 02SL - Stations (LUL) | Cxxx-NCR-002666 | NCR | MEP - CHS Level 3 Field Device Locations |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-10-27 | 2019-08-13 10:34 | -75 | 2019-07-19 12:28 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | BMS Field device locations assured by __ and reviewed by __ as shown on __-SKETCH-0127, 0128, 0129, 0130 and 0131. IRF number - IRF_MEP PERM_CHS_0371 IRN number - Cxxx-__M-M-NOX-D061_WS107-50007
| 02SL - Stations (LUL) | Cxxx-NCR-002667 | NCR | HCDL - __ not working in accordance with ITP |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-04-14 09:23 | -77 | 2019-02-20 13:50 | Civil - Civil Engineering General | 1500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | HCDL- it has been noted during an inspection by __ that __ have installed a safety critical item not in accordance with the ITP: (Cxxx-__M-A-ITP-D061_WS106-50139)Section 6.14 - Lanyard anchors (ASE-103) Type : Mansafe Constant Force Post For Standing Seam Roofing. The ITP also refers to the MCR (Cxxx-__M-A-LRC-D061_WS106-50481) Type: MSW __s Constant Force Posts. The product actually installed is the SFS Fall Protection System. In addition __ had been provided certification from the Sub-contractor retaining that the fall arrest system was safe for use; however on cursory inspection by __, it was found that bolts fixing the cable to the anchor posts are loose, lack a minimum of 3no protruding threads beyond the nut face, and comprise a mixture of Nylock and non-locking nuts. The system has been de-tagged by __, and access onto the roof prohibited.
| 02SL - Stations (LUL) | Cxxx-NCR-002668 | NCR | LULO Accommodation Block Roofs - Incomplete Balustrade Cowl Detail |  | Contr | VIN | WHI - Whitechapel Station (Central) |  | 2019-12-07 | 2019-10-14 10:27 | -54 | 2019-02-20 12:17 | Architectural - Roofing & Exterior Treatment | 1500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Intergrated cowls have been provided by __ to the North & South accommodation block and the GSM. This is in accordance with the accepted F2 designs (ref. drawings Cxxx-__M-A-DWG-D061_WS106-54112, 54113 and 54366). The cowl provided is not continuous around the circumference of the balustrade and so there is a portion of this detail that is unprotected by a cowl. A portion of the balustrade/ roof membrane interface is therefore subject to direct rainfall which will not provide longevity.
| 02SL - Stations (LUL) | Cxxx-NCR-002669 | NCR | LULO South Accommodation Block - Parapet capping width |  | Contr | VIN | WHI - Whitechapel Station (Central) |  | 2020-02-28 | 2021-02-26 16:06 | 364 | 2019-02-20 17:18 | Architectural - Finishes | 2500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Capings to the parapet on the South accommodation block have been fabricated (and part installed). There are a number of locations where the capping is shorter than the underlying parapet and therefore a portion of the parapet is not covered and the underlying waterproofing membranes are exposed and unprotected. - Installed cappings along the North elevation - Whilst the width of the capping is in accordance with the F1 drawing (ref Cxxx-__M-A-DDD-D061_WS106_Z-19216), the drawing indicates cappings overhanging the parapet which is not what has been installed. - Installed cappings along the East elevation - Capping has been installed in accordance with the approved F2 drawing (ref. Cxxx-__M-A-DWG-D061_WS106-53361). The drawing incorrectly shows the capping being shorter than the parapet. Attached pictures indicate examples of capping width relative to parapet width.
| 02SL - Stations (LUL) | Cxxx-NCR-002670 | NCR | LULO Accommodation Blocks - High level column cladding incorrect colour |  | Contr | VIN | WHI - Whitechapel Station (Central) |  | 2019-06-28 | 2019-03-05 09:38 | -115 | 2019-02-21 10:24 | Architectural - General | 750 |  | Supervision/Management | Reject | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The HCDL canopy is supported by 8No short sections of column above the accommodation blocks. The F1 design does not include an intended cladding system for these column sections but they are (in part) visible to the public. The Contractor therefore raised PTRs to clarify and the sketch "PTR-4121 mark-ups" was provided by __ and subsequently issued to __ to produce and assure an F2 design. The sketch and PTR indicate 1No being Rimex Black, 5No being shot peened stainless steel, 2No being cementitious board. The F2 design produced shows 5No columns being Rimex Black (ref. drawings Cxxx-__M-A-DWG-D061_WS106-53688, 53689 and 53691). Whilst this is consistent with the remainder of the HCDL columns, this is not in accordance with the F1 infomation provided. Some of the column casings have currently been installed on site.
| 02SL - Stations (LUL) | Cxxx-NCR-002672 | NCR | R10N Rooflight Flashings Not Designed to As-Built Rooflight Frames |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-04-02 | 2019-07-01 07:03 | 90 | 2019-02-21 18:09 | Architectural - Roofing & Exterior Treatment | 5500 |  | Design | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | __'s subcontractor __, have designed and procured rooflight flashings for the R10N rooflights. Whilst installing the flashings it was found that they do not fit over the aluminium support structure between the rooflight handrail spigots and the central roof gutter. We believe this is due to __ designing the rooflight flashings based off a 3D model that does not reflect the as-built locations of the rooflight frames and the central roof. As a result tolerences between the rooflight frames and the central roof were not considered in the design process.
| 02SL - Stations (LUL) | Cxxx-NCR-002673 | NCR | HCDL - Internal Fascia Panels (Lower Canopies) |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2021-07-01 20:54 | 366 | 2019-02-22 12:34 | Architectural - General | 5400 |  | Design | Rework | 3 (3-6k) | Complete | Previous Construction - Improper As Built | Completed |  | HCDL - Internal Fascia Panels (Located on the Lower Canopies) During attempted installation of the internal Fascia Panels, it was discovered that the Fascia and the Roof verge seam Design is not in accordance with as-built conditions on site.
| 02SL - Stations (LUL) | Cxxx-NCR-002674 | NCR | CHS - Northern Elevation - Corbel Fracture |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-03-29 | 2019-04-15 16:25 | 17 | 2019-02-25 16:56 | Architectural - Roofing & Exterior Treatment | 7589 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The North-eastern corbel at CHS was repaired in line with NCR-02475. On the 20th February, approximately 3 days after the column was installed and approximately 1 day after the column was torqued, it was observed that the corbel had fractured in the location of approximately where the repair was completed. The fracture is shown in the image attached titled "Damaged Corbel".
| 02SL - Stations (LUL) | Cxxx-NCR-002675 | NCR | Cxxx - Level 4 Riser B1 - Angle Plate. |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-06-10 | 2019-05-10 07:25 | -31 | 2019-02-27 10:03 | Architectural - Brickworks/Blockworks | 5000 |  | Documentation and Records | Rework | 3 (3-6k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | As witnessed during an inspection (IRF-1419) the angel beam to support the block was installed prior acceptance of the FCD-002686.
| 02SL - Stations (LUL) | Cxxx-NCR-002676 | NCR | Failure to following QA procedures prior to equipment change on site |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-03-07 | 2019-08-14 08:42 | 160 | 2019-02-28 10:56 | Fire - Detection | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | FA smoke detector has been removed and relocated within riser B2 without raising the appropriate documentation. The detector has been relocated to a potential location for future ductwork as no PTR had been raised or approved for its new position.
| 02SL - Stations (LUL) | Cxxx-NCR-002677 | NCR | LO-Baileys Panel Top Hat Misalignment |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-08-10 | 2019-08-13 21:50 | 3 | 2019-05-02 15:10 | Architectural - General | 3500 |  | Manufacturing Defect | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Counterfeit Items | Completed |  | It has been found that the slotted holes around the perimeter of the stainless steel cladding do not align (horizontally and vertically) with the slotted top hats fastened to the honeycomb backing of the panels. Due to this misalignment, the panels cannot be installed on the fabricated hook rails as intended.
| 02SL - Stations (LUL) | Cxxx-NCR-002679 | NCR | Spandrel Panel Interface with Roof Access Gantries |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-06-01 | 2019-06-12 12:23 | 11 | 2019-03-05 10:18 | Architectural - Roofing & Exterior Treatment | 5500 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | During the installation of spandrel panels on the R12 Roof, it was found that __'s subcontractor __ had designed and procured spandrel panels that were to be installed in areas that clashed with existing roof access gantry posts. Upon investigation it was found that __ had not designed any spandrel panels that have an interface with access gantries for the concourse roof.
| 02SL - Stations (LUL) | Cxxx-NCR-002680 | NCR | Concourse roof drainage hoppers procured without approved design |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-06-01 | 2019-09-12 09:08 | 103 | 2019-03-05 10:38 | Architectural - Roofing & Exterior Treatment | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | __'s sub-contractor, __ has designed and procured 6no hoppers for the concourse roof drainage system. All 6no hoppers have been delivered to site without the hold down detail being approved. As a result none of the hoppers can be used permanently.
| 02SL - Stations (LUL) | Cxxx-NCR-002681 | NCR | Fire Suppression System Installed Without an accepted Design |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2019-04-10 | 2019-07-25 09:55 | 106 | 2019-03-01 11:34 | Fire - Suppression | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | During a planned surveillance, it was found that the installation of the Gas Suppression System and associated Cable Management System (CMS) had been carried out with no accepted design in place. No evidence of Inspection Request Forms (IRF) for CRL Intervention points as shown on Inspection and Test Plan (ITP) ‘Gas Suppression System Installation’ Cxxx-__M-M-ITP-D061-50027 (Rev 1) could not be provided.
| 02SL - Stations (LUL) | Cxxx-NCR-002682 | NCR | Fire Detection System and associated Cable Management System (CMS) had been carried out with no accepted drawings in place |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2019-04-10 | 2019-07-25 10:32 | 106 | 2019-03-01 11:39 | Fire - Detection | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | During a planned surveillance, it was found that the Fire Detection System and associated Cable Management System (CMS) had been carried out with no accepted drawings in place. No evidence of Inspection Request Forms (IRF) for CRL Intervention points as shown on Inspection and Test Plan (ITP) ‘Fire Detection and Alarm System’ Cxxx-__M-E3-ITP-D061-50001 (Rev 4) could not be provided.
| 02SL - Stations (LUL) | Cxxx-NCR-002683 | NCR | Station Fire Main Installed Without Accepted Drawings. |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2019-04-10 | 2019-07-25 11:12 | 106 | 2019-03-01 11:49 | Fire - Fire Systems & General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | During a planned surveillance, it was found that the Fire Main Installation had been carried out with no accepted drawings in place. No evidence of Inspection Request Forms (IRF) for CRL Intervention points as shown on Inspection and Test Plan (ITP) ‘Installation of New Fire Main System’ Cxxx-__M-E1-ITP-D061-50004 (Rev 2) could not be provided.
| 02SL - Stations (LUL) | Cxxx-NCR-002684 | NCR | LO - Incorrectly installed __ roof preventing Fascia installation |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-05-31 | 2019-05-10 07:10 | -21 | 2019-03-02 07:52 | Architectural - Roofing & Exterior Treatment | 4700 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the installation of the the LO concourse roof fascia panels it was discovered that the __ outer standing seam and EClip had been incorrectly set and welded in three localised areas. GL 12.5 - 16 West, GL 10-13 and 19-19.1 East. This has intern impeaded the installation of the fascia top C-channel and capping of the fascia panel.
| 02SL - Stations (LUL) | Cxxx-NCR-002685 | NCR | R10S Rooflight flashings not designed to as-built rooflight frames |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-08-01 | 2019-07-01 08:32 | -31 | 2019-03-05 11:32 | Architectural - Roofing & Exterior Treatment | 4600 |  | Design | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | __'s subcontractor __, have designed and procured rooflight flashings for the R10S rooflights. The R10S rooflight flashings are a continuation from the R10N rooflight flashings, which were found to not have been designed to as-built conditions (detailed in Cxxx-NCR-002672). A desktop survey has been carried out by __, and has confirmed that the R10S rooflight flashings will not fit as they have not been designed as per the rooflight as-built conditions.
| 02SL - Stations (LUL) | Cxxx-NCR-002687 | NCR | Damaged BMS Cable CHS Level 5 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-06-14 | 2019-04-20 11:46 | -55 | 2019-03-06 13:31 | Electrical - General | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | BMS Cable Damaged on CHS Level 5
| 02SL - Stations (LUL) | Cxxx-NCR-002688 | NCR | CHS - Northern Elevation - Incorrectly Installed Steel Column |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-04-15 | 2019-04-23 09:03 | 8 | 2019-03-06 14:51 | Architectural - Roofing & Exterior Treatment | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The installation of CHS structural steel has previously been undertaken where horizontal members were incorrectly installed, resulting in tensile forces being applied to the concrete corbel and thus resulting in a fracture. The non-conformances for these works is captured in NCR-02475 & NCR-02540. With the remedial works completed for NCRs 002475 & 002540, Column No. 5 for the CHS Northern Elevation was re-installed with a newly welded stub to bear on the concrete landing. Approximately 3 days after Column No. 5 was re-installed, the repaired corbel (completed in accordance with NCR-002475) was identified by __ Supervision as fractured. An investigation into the fractured corbel was carried out and with the advice of __ design engineers, it was determined the corbel fracture was a result of a weld on the column connection. The details of the concrete corbel non-conformance are captured in NCR-002674. An investigation of the fractured corbel identified the following, with respect to the steelwork only: 1. The Column No. 5 stub was not bearing on the concrete landing as intended. Refer the attachment titled "NCR-02688 - Incorrect Bearing Photograph"; 2. With Column No. 5 having oversized holes, it was confirmed that the column was not bearing on the corbel bolts. Refer the attachment titled "NCR-02688 - Column Corbel - No Loading"; and 3. Based on Points 1 & 2 above, it was concluded the column was currently bearing it's self-weight back against the concrete structure of CHS.
| 02SL - Stations (LUL) | Cxxx-NCR-002690 | NCR | LFTDB Distribution Board Energise without uploaded IRN |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-04-15 | 2019-04-03 12:22 | -12 | 2019-03-06 17:39 | Electrical - LV Equipment | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | LFTDB Distribution Board at CHS has previously been inspected and energised but no records or IRN uploaded onto EB to provide proof.
| 02SL - Stations (LUL) | Cxxx-NCR-002692 | NCR | DSS & CHS - Pull testing for screw anchors - Balustrades & Handrails |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-04-16 | 2019-03-12 16:08 | -35 | 2019-03-07 14:58 | Architectural - Handrail | 1200 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient surveillance of subcontractors | Completed |  | Pull out test on DSS & CHS balustrades and handrails were not carried out at the point of certification. When pull testing is not relevant due to the nature of the fixings installed, __ shall raise the correspondent RFI to formally capture this agreement between CRL and __ as per Cxxx-PMC-16454. Confirmation from designer was obtained once the works were completed.
| 02SL - Stations (LUL) | Cxxx-NCR-002693 | NCR | Energisation of Cable D07 - Supply Cable to OLBI 1 By pass Panel |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-04-17 | 2019-03-16 14:44 | -32 | 2019-03-08 10:29 | Electrical - LV Equipment | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The cable D07 has been energised prior to IRN signoff by CRL to allow for the Equipment to charge the OLBI 1 batteries.
| 02SL - Stations (LUL) | Cxxx-NCR-002694 | NCR | Sitewide: __ working to P rev drawings without exception |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-08-06 | 2019-09-06 18:01 | 31 | 2019-03-08 11:24 | Architectural - Doors | 3000 |  | Design | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Following a recent surveillance carried out by the __ quality team, the sitewide door packages were found to have proceeded with the manufacture and installation of doors against P revision drawings. __ Procedure Cxxx-__M-O4-GPS-D061-50002 has therefore not been adhered to by Design or Delivery.
| 02SL - Stations (LUL) | Cxxx-NCR-002695 | NCR | DSS - Glazed Roof above Escalators - Cosntruction started with no approved sample |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-06-17 | 2019-05-17 11:50 | -31 | 2019-03-08 11:49 | Architectural - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | During the surveillance carried out on 22/02/2019 it was found out that a sample hasn't been approved by Crossrail and installation on site had already started. As a result of Clause 20.9 this NCR has been raised in order to record the non-conformance.
| 02SL - Stations (LUL) | Cxxx-NCR-002696 | NCR | BMS Connections on ATS's - Not following change procedure. |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-04-21 | 2019-04-04 13:20 | -17 | 2019-03-12 15:52 | Electrical - LV Equipment | 8000 |  | Documentation and Records | Use As-Is | 2 (6-60k) | Complete | Design Problem - Other | Completed |  | Initial drawings were issued of ATS Units showing the BMS Terminals inside Section 3 which is the ATS compartment. However during a FAT it was noted that it was difficult to terminate the cables into the BMS Klippon Terminals due to Insulated Busbars directly above. It was then decided to move the BMS Terminals down into Section 4 directly below, (drawings attached). Unfortunately this change was not picked up on GA drawings which continued to show the Terminals in section 3, whereas an FCD should have been produced to identify the change. however this did not happen and we failed to adhere to the change process. DSS - FDDB1, FDDB2, LIFT 1, LIFT 2 & ESCALATOR CHS - FDDB1, FDDB2, LIFT 8 & MCC 8
| 02SL - Stations (LUL) | Cxxx-NCR-002697 | NCR | Early energisation of lift equipment |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-04-24 | 2019-04-01 10:11 | -23 | 2019-03-15 15:21 | Electrical - General | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | A temporary supply was installed to LCR 3, 4, 5, 6, 7 and 10's Castell isolators and DB's. This was due to __ needing power to this equipment to proceed with installation inside the lift shaft and progress commissioning.
| 02SL - Stations (LUL) | Cxxx-NCR-002698 | NCR | EB-C/8/Riser1/1 Earth pit Earth bar not MCR approved |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-04-29 | 2019-03-25 16:28 | -35 | 2019-03-20 07:29 | Electrical - Earthing & Bonding | 3000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Cambridge Heath Shaft EB-C/8/Riser1/1 Earth pit Earth bar was IRF'ed without an MCR approved earthbar installed
| 02SL - Stations (LUL) | Cxxx-NCR-002699 | NCR | PLC panels procured and built without an assured design |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-04-30 | 2019-11-18 14:53 | 202 | 2019-03-21 14:33 | Mechanical - Heating Ventilation & Air Conditioning | 5000 |  | Design | Use As-Is | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | The PLC panels have been procured and built without an assured design.
| 02SL - Stations (LUL) | Cxxx-NCR-002700 | NCR | IRF_MEP PERM_CHS_0422 24 hour notice |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-04-30 | 2019-03-25 16:41 | -36 | 2019-03-21 17:24 | Electrical - General | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | IRF_MEP PERM_CHS_0422 IRF not submitted to Crossrail giving 24 hour notice period required
| 02SL - Stations (LUL) | Cxxx-NCR-002701 | NCR | Cxxx - CRL Platform Equipment Enclosure |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-04-10 | 2019-03-31 21:29 | -10 | 2019-03-21 18:25 | Architectural - Walls | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Cxxx-__M-A-ITP-D061_WS106-50150 Rev 2.0 was not accepted in advance of the installation of Equipment Enclosures (in CRL Platforms). This ITP was the controlling docuemnt. Rev 1.0 was at Code 1 but did not cover the installation the procedure of Equipment Enclosures.
| 02SL - Stations (LUL) | Cxxx-NCR-002702 | NCR | DSS Level A BMS Field Devices - Assured Design Sketch |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-05-09 | 2019-06-05 12:12 | 27 | 2019-03-22 13:47 | Mechanical - Mechanical Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | DSS Level A Field Devices installed without assured design.
| 02SL - Stations (LUL) | Cxxx-NCR-002704 | NCR | DSS Level 1 BMS Panel Location |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-05-07 | 2019-03-29 02:01 | -39 | 2019-03-28 07:26 | Mechanical - Heating Ventilation & Air Conditioning | 1500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The BMS Panel in DSS level 1 was moved due to potential access egress issues.
| 02SL - Stations (LUL) | Cxxx-NCR-002706 | NCR | CHS - MCC07 Control Wiring |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2019-05-05 | 2019-06-19 09:41 | 45 | 2019-03-26 15:48 | Electrical - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | During the BMS cable IRF for CHS Level 5 it was noted that the Cable Schedule for BMS (and potentially PLC) does not correspond with the MCC Schematic (terminal numbers where cable cores terminated were incorrect). This MCC Schematic drawing was not part of the IRF and from a lessons learnt / correction needs to be moving forward. Subsequently __ have discovered a new P05 revision of said schematic (Cxxx-__M-E-DWG-D061_WS107-50134) on BC that rectifies the errors / changes above. Unfortunately, without having said drawing to review, cannot confirm the extent of the changes – but the concern is that panel wiring modifications / uncontrolled changes have been undertaken post FAT and IRN. IRF to be carried out on review of the above and in line with new drawing revision acceptance
| 02SL - Stations (LUL) | Cxxx-NCR-002707 | NCR | DSS Level 5 Secondary CMS |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-09-29 | 2019-08-13 13:55 | -47 | 2019-05-20 08:01 | Electrical - Cable Management | 2000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Trunking installed as secondary CMS by __ without assured design.
| 02SL - Stations (LUL) | Cxxx-NCR-002709 | NCR | CMS Alterations after sign off - Upper Concourse CMS PCC walkway. |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-09-13 14:17 | 75 | 2019-07-09 10:23 | Electrical - General | 5000 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | The CMS installed and Signed off by __ need to be altered / raised to ensure that the trunking falls inside the __ Hinged CMS architectural cladding panel.
| 02SL - Stations (LUL) | Cxxx-NCR-002711 | NCR | Lift ATS' - BMS control terminals |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2021-01-17 08:38 | 201 | 2019-04-02 09:56 | Electrical - LV Equipment | 10000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Initial drawings were issued of ATS Units showing the BMS Terminals inside Section 3 which is the ATS compartment. However during a FAT it was noted that it was difficult to terminate the cables into the BMS Klippon Terminals due to Insulated Busbars directly above. It was then decided to move the BMS Terminals down into Section 4 directly below, Unfortunately this change was not picked up on GA drawings which continued to show the Terminals in section 3, whereas an FCD should have been produced to identify the change. However this now does not conform to Form 4 Type 2. DSS - LIFT 1, LIFT 2 CHS - LIFT 8
| 02SL - Stations (LUL) | Cxxx-NCR-002712 | NCR | GSM South Canopy - Discrepancy between Ceiling and Fascia levels |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-05-15 | 2019-09-25 15:42 | 133 | 2019-04-05 11:00 | Architectural - Ceilings & Soffits | 5300 |  | Design | Rework | 3 (3-6k) | Complete | Management Problem - Inadequate administrative control | Completed |  | GSM South Canopy - During Installation of __ ceiling it was noted that the fascia panels where low (30 to 50mm in areas) this has lead to there being a more exposed fascia panel edge. It is yet to be fully established what has caused the differentiation in heights. An investigation is being carried out
| 02SL - Stations (LUL) | Cxxx-NCR-002717 | NCR | CHS - Northern Elevation - Non-Compliant Bolt |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-05-18 | 2019-05-10 06:47 | -8 | 2019-04-08 17:13 | Architectural - Roofing & Exterior Treatment | 3000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | When completing snagging works to the Northern Elevation of CHS Walkways and Structural Steel, an inexperienced operator cut the threads of three threads too short. The area affected is limited to the snagging works on C1 Level of the CHS Northern Elevation Structural Steel and Walkways scope. The two types of issues identified are: 1. Shortened threads, whereby the threads exposed are less than (x3) full threads; and 2. A non-compliant nut connection, where the nut and thread have been damaged by an angle-grinder. The following attachments detail the damage to the threads listed: "CHS - Northern Elevation - Damaged Nut.JPG"; "CHS - Northern Elevation - Short Thread Photo 1.JPG"; and "CHS - Northern Elevation - Short Thread Photo 2.JPG".
| 02SL - Stations (LUL) | Cxxx-NCR-002718 | NCR | Installation of Sump Pump Panels without FAT or Design Acceptance |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-01-30 15:13 | -152 | 2019-04-06 15:18 | Electrical - General | 2000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | __ have delivered and installed various Sump Pump Panels without FAT or Design Acceptance. __ to confirm which panels have been installed in contravention of the Works Information and __ Quality Plan.
| 02SL - Stations (LUL) | Cxxx-NCR-002720 | NCR | CHS - Western Elevation - Panel Clash with Structural Steel Plate |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-05-18 | 2019-05-17 15:07 | -1 | 2019-04-08 16:23 | Architectural - Roofing & Exterior Treatment | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The CHS Western elevation return at GL3 has a clash between the cladding panel and the steel bracket plates. The clash is due to the steel plate being packed out further than shown within the 3d model for the steelwork. The attached MDC, Cxxx-__M-A-CER-D061_WS107-50015 provides the details of this NCR.
| 02SL - Stations (LUL) | Cxxx-NCR-002721 | NCR | Existing Ticket Hall & Concourse - Fail to invite Crossrail to inspect Lightning Protection IRFs |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-05-19 | 2019-04-20 11:50 | -29 | 2019-04-09 08:11 | Electrical - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Crossrail not being invited to inspection & witness at the time of installation & testing of ETH pile cap bonding & Exothermic Welding.
| 02SL - Stations (LUL) | Cxxx-NCR-002722 | NCR | DALI Reworks LULO |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-10-16 13:12 | 108 | 2019-04-11 15:04 | Electrical - General | 45000 |  | Incorrect Installation | Use As-Is | 2 (6-60k) | Complete | Design Problem - Other | Completed |  | CRL have been made aware of various reworks to DALI installation in LULO areas (specifically Platforms 1, 2, 5 and 6). This is primarily due to high test readings (over the acceptable value). (Maximum DALI length should be 300m with no more than 48 Fittings) DALI installation has commenced with - - No ITP - No Accepted Drawings This in contradiction of Contract Quality Plan - 8.7 Construction Control 10.3 Control of Non conforming Product __ to confirm extent of reworks
| 02SL - Stations (LUL) | Cxxx-NCR-002723 | NCR | __ Steel/Macspec Ltd Stair 33/34 N__ |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-07-09 | 2019-09-07 09:11 | 60 | 2019-04-16 08:16 | Architectural - General | 1500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | PTS Surveillance Report No: 35388 (ATTACHED) references N__ Report 21637-001 (ATTACHED) – which only covers 2 off samples which are not part of the actual fabrication supplied, there are 13 columns to baseplate welds on both stair 33 & 34 giving a total of 26 items available for N__ Testing. The requirement if for 10% of items to ne N__’d which has not been carried out. The report also fails to identify the welder identification and material thickness. To meet the N__ Inspection criteria these items to undergo N__ on site by a UKAS Accredited entity.
| 02SL - Stations (LUL) | Cxxx-NCR-002724 | NCR | LULO - Interim Station - External Cladding - Lack of Red Line Drawings |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-11-15 | 2019-09-30 13:53 | -46 | 2019-04-18 11:27 | Architectural - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Red line drawings have not been produced for Sub-Construction Certificate - Interim Station - Cladding External Cxxx-__M-A-CER-D061-50020. Interim Station is form of Temporary Ticket Hall (TTH) and Western Secondary Means of Escape (WSME) elements.
| 02SL - Stations (LUL) | Cxxx-NCR-002725 | NCR | DSS Level 4 BMS Field Device Locations Assurance |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-08-02 | 2019-08-12 13:23 | 10 | 2019-04-24 16:58 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Field device locations for DSS level 4 BMS Outstation assured by __ and reviewed by __ as shown on __-SKETCH-0190, 0191, 0192, 0193, 0194 and 0195. NCR has been raised to capture these locations and provide the necessary assurance to the client. IRF number - IRF_MEP PERM_DSS_0573 IRN number - Cxxx-__M-M-NOX-D061_WS105-50009
| 02SL - Stations (LUL) | Cxxx-NCR-002726 | NCR | FDDB2 8L1 incorrect cable size stated in construction records |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-06-04 | 2019-05-06 12:44 | -29 | 2019-04-25 15:13 | Electrical - Power Distribution | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | FDDB2 IRN states 8L1 is 2.5 on the test sheets in the construction records and is incorrect as the cable size is a 4mm as per DB schedule
| 02SL - Stations (LUL) | Cxxx-NCR-002727 | NCR | LULO GSM - Level 2 Corridor - Insufficient width of firestopping in __ |  | Contr | VIN | WHI - Whitechapel Station (Central) |  | 2019-11-12 | 2019-05-29 15:28 | -167 | 2019-04-26 14:02 | Fire - Compartmentation | 2750 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | During the week 4 possession (19th - 22nd April), __ installed relief trunking between the DNO switchroom (room 2/613) and corridor (room 2/230) in level 2 of the GSM. The additional relief trunking was installed within an existing __ but was installed too close to the side of the __ and therefore did not allow for the required 50mm of firestopping between the CMS and the side of the __. See attached pictures for clarity. There was insufficient time on the possession for the __ to be extended to allow 50mm of firestopping compound to be installed. To faciliate handback, the CMS was firestopped in the existing __ with circa 12mm of firestopping compound on one side. Note: firestopping within the relief trunking was installed sufficiently.
| 02SL - Stations (LUL) | Cxxx-NCR-002728 | NCR | Electrical services impedeing air flow in the concourse ESR room to fan coil unit |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-09-16 16:07 | 78 | 2019-04-29 10:05 | Mechanical - Heating Ventilation & Air Conditioning | 1000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | electrical services have been installed directly in from of the discharge from a fan coil unit providing critical cooling to the room. The electrical services will reduce the cooling performance of the unit and therefore possibility of overheating.
| 02SL - Stations (LUL) | Cxxx-NCR-002730 | NCR | A-53128 Smokescreens & A-50325 Endscreens– grout cube crush outstanding |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-08-16 | 2019-07-01 09:03 | -46 | 2019-06-06 16:09 | Archaeology - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Smokescreens (smoke downstands) located at Platform Cross Passages ‘CP1’ & ‘CP2’ have outstanding grout cube testing (crush) reports. The grout samples were taken at date of grout installation, however these have not been taken for laboratory testing (scheduled for lab testing @ May-2018. Smokes screens affected are: CP1 – Eastbound & Westbound CP2 – Eastbound & Westbound Total = 4 no.
| 02SL - Stations (LUL) | Cxxx-NCR-002731 | NCR | Platform 1 - Selux Trunking Installation GD to GL |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2019-06-09 | 2019-11-06 13:11 | 150 | 2019-04-30 13:07 | Electrical - Cable Management | 10000 |  | Incorrect Installation | Use As-Is | 2 (6-60k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | Platform 1 (see drawing 31972 - GD to GL) the platform edge CMS design shows 4c 250w in grey and an adjacent 4c 250w trunking in orange. The installation does not reflect this design; the platform edge trunking / boom is now a single compartment “trunking” which is to be wired via conduit from 4c 250w trunking (orange on drawing). We have not seen a PTR to support cable calcs, and the adaptable box with conduit fixed to 4c 250w trunking (orange on drawing) now impacts rewiring and or new installation as no adequate fixed lid either side of adaptable box.
| 02SL - Stations (LUL) | Cxxx-NCR-002732 | NCR | Failure to adhere to hold & Witness points. |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-03-23 10:54 | -99 | 2019-05-07 07:15 | Electrical - Cable Management | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Secondary CMS (conduit not signed off by CRL) and approx. 35 Open SNAGR items at IRF. __ continued to install cables in the conduits and terminate the cables and install the Speakers, System has need been released for commissioning.
| 02SL - Stations (LUL) | Cxxx-NCR-002734 | NCR | HCDL - Installation of Copex between Multicompartment CMS |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-04-09 15:36 | -82 | 2019-04-30 14:25 | Electrical - Cable Management | 4000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | HCDL F1 CMS accepted design shows multicompartment trunking to multicompartment trunking (overlap / interchange). __ have carried out installation of 25mm conduit or 32mm Copex between multicompartment CMS' without adhering to the change control process. __ to provide PTR acceptance from Principal designer including all relevant CMS/Cable Calcs. In addition, advise on current status of installation (wiring etc) and highlight via drawings / sketches instances where this has been undertaken
| 02SL - Stations (LUL) | Cxxx-NCR-002736 | NCR | AHU1 and ductwork installed to P rev drawing |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-06-10 | 2019-05-02 10:59 | -39 | 2019-05-01 10:56 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | AHU1 and associated ductwork has been installed to a P rev drawing. (Cxxx-__M-M-DWG-D061_WS106-50132) This relates to: Cxxx-__M-H-NOX-D061_WS106-50004 Cxxx-__M-H-NOX-D061_WS106-50003
| 02SL - Stations (LUL) | Cxxx-NCR-002737 | NCR | LO - Fascia clash with the northern accomodation block |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-10-18 | 2019-08-31 07:01 | -48 | 2019-05-01 12:45 | Architectural - General | 1500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Please refer to the attached sketches: During the installation of the main concourse roof fascia it was discovered that a fascia panel clahes with the capping panel of the northern accomodation block. Apon discovering the clash the area was as-built and checked and both the fascia and northern accomodation block have been installed correctly. The P33 architectural model was reviewed and shows the clash. One or both of the clashing panels need to be re-fabricated.
| 02SL - Stations (LUL) | Cxxx-NCR-002739 | NCR | Incorrect Installation of DB5/110 E51 Electrical Works |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2019-12-06 | 2020-01-13 09:43 | 38 | 2019-05-02 07:37 | Electrical - General | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | Cxxx-FCD-003324 was accepted for the modifications to be undertaken as part of the permanent installation works for DB5/110 in E51. During Week 3 possession, these works were completed without adherence to the ITP Witness Points. In addition and upon inspection of the room, it was found that the installation had not been undertaken in accordance with Cxxx-FCD-003324. Cable Tray had not been installed correctly and SWA / Supply cable had been pulled through the incorrect duct and fixed to the wrong tray, meaning incorrect segregation between supplies.
| 02SL - Stations (LUL) | Cxxx-NCR-002740 | NCR | Gap between the damper on the PES and back of louver |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2019-09-27 | 2019-08-13 10:41 | -45 | 2019-05-02 09:54 | Architectural - Finishes | 10000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Management Problem - Inadequate supervision | Completed |  | Architects drawing number Cxxx-__M-A-DDD-D061_WS106_Z-19380 indicates a gap of 15mm max between the damper outlet and the rear of the PES Louvre. This dimension has not been provided and is CIRCA 120mm.
| 02SL - Stations (LUL) | Cxxx-NCR-002741 | NCR | LU - GSM - Stair 52 Balustrade - Works Commencing Without An Approved ITP |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-08-31 | 2019-07-02 13:47 | -60 | 2019-05-03 08:48 | Architectural - Balustrade | 1000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Works on Stair 52 balustrade at GSM have commenced without the ITP [Cxxx-__M-A-ITP-D061_WS106-50198 Rev 4.0] being approved.
| 02SL - Stations (LUL) | Cxxx-NCR-002742 | NCR | DALI Reworks required GSM |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2019-09-13 | 2019-10-20 12:28 | 37 | 2019-05-06 10:51 | Electrical - General | 3500 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | CRL have been made aware of various reworks required to DALI installation in GSM. This is primarily due to high test readings (over the acceptable value). (Maximum DALI length should be 300m with no more than 48 Fittings) DALI installation has commenced with - - No ITP - No Accepted Drawings This in contradiction of Contract Quality Plan - 8.7 Construction Control 10.3 Control of Non conforming Product __ to confirm extent of reworks Note: Cxxx-NCR-002722 has been raised previously for the same issue in LULO
| 02SL - Stations (LUL) | Cxxx-NCR-002743 | NCR | LU - 1DS - POMS room/cupboard partition |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-12-20 | 2019-07-02 08:04 | -171 | 2019-05-10 15:46 | Architectural - Partitions | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Drawing Cxxx-__M-A-DDA-D061_WS106_1-10260 shows partitions throughout 1DS. Between Rev C01 and P18, the POMS store has become the POMS cupboard due to FF&E changes. The partition between the POMS room and the POMS cupboard has moved and the doors have been changed. Rev C01 states that the partition is to be IWS-215 (double skin) however Rev 18 drawing no longer states what partition spec ref is required for the section of wall above the new double doors. Onsite a single skin partition has been construction which corresponds to IWS-213.
| 02SL - Stations (LUL) | Cxxx-NCR-002744 | NCR | Pull testing - Level B- DSS External Roof access hatch [DSS-AH-17] |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-06-17 | 2019-05-17 08:14 | -31 | 2019-05-08 14:10 | Architectural - General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | Location: Level B- DSS External Roof access hatch [DSS-AH-17] Issue: Pull out testing was not carried out at the point of certification. When pull testing is not relevant due to the nature of the fixings installed, __ shall raise the correspondent RFI to formally capture this agreement between CRL and __ as per Cxxx-PMC-16454. Confirmation from designer was obtained once the works were completed. Final Disposition: Use As-Is
| 02SL - Stations (LUL) | Cxxx-NCR-002746 | NCR | Level 5 Fan Room Comm's Containment 25% capacity not achieved |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-02-12 16:37 | -139 | 2019-05-14 06:42 | Electrical - Cable Management | 3000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In Level 5 fan room the current designed and installed CMS on inspection/review with Crossrail does not currently provided the required 25% spare capacity. This is due to a BMS panel and PLC panel being situated in the same location and the CMS Cross sectional area being reduced to the the panels.
| 02SL - Stations (LUL) | Cxxx-NCR-002747 | NCR | LU - GSM - Stair 52 balustrade colour not achieving 30 points difference |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-03-05 13:56 | -117 | 2019-05-16 16:33 | Architectural - Handrail | 5990 |  | Design | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Counterfeit Items | Completed |  | The F2 designer for the Stair 52 balustrade including posts, installed on 06.05.19, has given it colour RAL 7015 (stated on his drawing Cxxx-__M-A-DWG-D061_WS106-54934) which closely matches the GSM __ wall finish behind. The subcontractor is required to design and install his works in accordance with LU standard S1-133 and BS 5395-1:2010 - specifically chapter 4.1 part j) - and BS 8300 which requires a minimum of 30 points difference between balustrade and background finishes. The installed works do not deliver this requirement.
| 02SL - Stations (LUL) | Cxxx-NCR-002748 | NCR | LU - GSM - Balcony slab extension metalwork dimensions unsuitable |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-11-27 | 2019-09-19 15:32 | -69 | 2019-05-20 09:01 | Architectural - Flooring | 3500 |  | Design | Reject | 3 (3-6k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The GSM slab extension F2 design specifies a 3-sided galvanised steel angle to be installed around the extension perimeter, flush with the top of concrete to create a seamless finish linking the Bin store slab to the existing west balcony slab. However, following installation it appears that the steel angle height dimension is approximately 50mm too high where it runs alongside the existing (west balcony) slab, on its southern edge.
| 02SL - Stations (LUL) | Cxxx-NCR-002749 | NCR | LULO - HCDL - Circular Column Cladding - Final Installation not Acceptable |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-01-29 | 2021-04-22 12:51 | 83 | 2019-05-20 16:55 | Architectural - General | 3500 |  | Workmanship | Rework | 3 (3-6k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | This NCR encompasses 4 issues. 1. Alignment in plan, as per the specification The specification states both that the circular column cladding should be designed to match the gridlines, and also that it must be within 5mm of it's intended location in plan. The cladding appears to fix to the steelwork, and does not follow any gridlines. As such, several cladding lines are out of tolerance. 2. Damage to the Panels The installed panels have chips, dents and bends that have occurred during the installation process, and will need to be replaced. 3. Joint Displacements The intersection joints highlight that the panels are not in alignment, as the gaps vary vertically and horizontally. Please see attached photographs for clarity. Further to this, there are noticeable tapers along the joints around the perimeter of the panel. 4. Overhang of the Plinth In relation to point 1, the alignment of the circular column cladding causes the cladding overhang of the plinth to vary between columns and differ on both sides. On some columns, the cladding lies inside the plinth boundary on one side, and overhangs by up to 30mm on the other. For all items, please see attached photo survey for clarity.
| 02SL - Stations (LUL) | Cxxx-NCR-002750 | NCR | Platform 1 and 2 Edge Lighting Trunking |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-04-09 14:05 | -82 | 2019-05-20 11:59 | Electrical - General | 10000 |  | Incorrect Installation | Use As-Is | 2 (6-60k) | Complete | Design Problem - Other | Completed |  | • Platform 1 Run 1 – FCD and MCR still outstanding for deviations from accepted design. This is currently installed and part of the ‘Operational Railway’ with neither in place • Platform 1 Run 1 – Where there are gaps to the single compartment lighting housing / trunking, please can you confirm the finish in relation to the clashes. Will the pipework or structural supports be visible? • Platform 1 Eastbound – Adaptable Box / __ positions in relation to the dummy panels. Is the requirement (due to depth) for the adaptable box / niphan to sit in the middle of the dummy panel? • Platform 1 Eastbound – Adaptable Box / __s require fixed lid either side for A&M purposes. • Platform 2 – Currently alignment issues between runs, this is not per accepted design. • Platform 2 - Adaptable Box / __ positions in relation to the dummy panel. Is the requirement (due to depth) for the adaptable box / niphan to sit in the middle of the dummy panel? • General – We believe that some diffusers currently open towards the track and not the station. A&M issue. • General – Spacing of fittings and or dummy panels seem to still be work in progress or an issue. This is likely to affect the adaptable box / niphans that are already installed. • General – Flex Cable MCR outstanding (at initiate after rework)
| 02SL - Stations (LUL) | Cxxx-NCR-002751 | NCR | GSM MEP - Lack of Checksheet - GSM Roof Solar Panel |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-02-07 13:40 | -144 | 2019-05-20 13:40 | Mechanical - Public Health Engineering | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The Solar Panel system installed in GSM Roof Level, Roof Access 1/253 was installed using Cxxx-__M-P-ITP-D061_WS106-50005 . There was no solar panel checksheet in existence at the time of installation or inspection. The installation team based their install checks on the manufacturers installation instructions detailed in Cxxx-__M-M-XDS-D061_WS106_1-51067 (see CRL-MCR-000844).
| 02SL - Stations (LUL) | Cxxx-NCR-002752 | NCR | Design error-Cxxx Cab DC16 no UPS backed |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-02-17 12:16 | -134 | 2019-05-22 14:19 | Electrical - General | 2500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | D.C 16 in riser 1 is fed from LPDB21A/1L2, this is not a UPS backed D.B. The Cab has no internal battery back up and needs to be fed from a UPS backed supply.
| 02SL - Stations (LUL) | Cxxx-NCR-002753 | NCR | CRL Platforms - CS1 Closure Works - Foamed Concrete Backfill - Deviation from the ITP checks |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-11-03 | 2019-08-13 22:02 | -82 | 2019-06-06 10:11 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | During the Foamed Concrete backfill pour for CS1 closure works __ and the subcontractor __ Engineering deviated from the approved ITP for the following controls: 1) 15.4 (...) Take 3 No. cubes / Target 28 day strength of 0.5-0.1N/mm2. Three cubes were taken but only two were tested at 28 days. The subcontractor retained the third cube to be tested at 90 days. 2) 15.5 Max temeperature: 65oC at any point in layer The subcontractor has not performed any of the temperature checks during the pour. No temperature has been recorded. 3) 15.5 Maximum 800mm per lift as per SNC. 800mm in lift equates to 95m3 of concrete. 95m3 is the limit of a single pour. The subcontractor has increased the pour volume to 104m3 which resulted in the exceeding of each pour height by >50mm per layer.
| 02SL - Stations (LUL) | Cxxx-NCR-002754 | NCR | LU - Stair 24 - As-built Survey Dimension Discrepancies |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-07-03 | 2019-07-11 08:50 | 8 | 2019-05-24 13:57 | Architectural - Balustrade | 0 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As-built installation of Stair 24 balustrade has minor discrepancies against design dimensions.
| 02SL - Stations (LUL) | Cxxx-NCR-002755 | NCR | LULO V Mesh Base bracket anchors |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-07-02 | 2019-07-08 09:24 | 6 | 2019-05-23 17:28 | Architectural - General | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __ have noticed 6no V mesh base brackets do not have the required amount of anchors installed. This is due to anchors becoming damaged and cut flush with the concrete during installation meaning those locations could not be used.
| 02SL - Stations (LUL) | Cxxx-NCR-002756 | NCR | DSS Level 6 Secondary CMS |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-08-23 | 2019-08-13 14:33 | -10 | 2019-05-23 09:13 | Electrical - Cable Management | 2000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Trunking installed as secondary CMS by __ without assured design.
| 02SL - Stations (LUL) | Cxxx-NCR-002757 | NCR | Incorrect size CMS installed between platform 6 and the lower concourse |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-02-17 11:19 | -134 | 2019-10-04 11:10 | Electrical - Cable Management | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | DC8 and DC9 primary CMS installed between platform 6 and the lower concourse is the incorrect size. 6 compartment trunking 300mm x 50mm installed, should be 300mm x 100mm.
| 02SL - Stations (LUL) | Cxxx-NCR-002759 | NCR | DSS Level A Secondary CMS - Sheet 1 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-07-31 | 2019-08-14 09:59 | 14 | 2019-05-23 10:59 | Electrical - Cable Management | 2000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Trunking installed as secondary CMS by __ without assured design.
| 02SL - Stations (LUL) | Cxxx-NCR-002760 | NCR | DSS Level A Secondary CMS - Sheet 2 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-10-30 | 2019-08-14 14:53 | -77 | 2019-05-23 11:06 | Electrical - Cable Management | 1500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Trunking installed as secondary CMS by __ without assured design.
| 02SL - Stations (LUL) | Cxxx-NCR-002761 | NCR | Crossrail Platforms PES Lighting - Additional DALI Provisions |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-10-02 02:29 | 94 | 2019-05-28 15:55 | Electrical - Lighting | 10000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Not Defined | Completed |  | Each PES light has 3 drivers and therefore requires 3 DALI addresses. Currently __ have only allowed for one DALI address per PES light.
| 02SL - Stations (LUL) | Cxxx-NCR-002762 | NCR | Stair 24 __ Installation |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-06-12 14:48 | -18 | 2019-06-05 08:30 | Electrical - Lighting | 10000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Supervision - Insufficient supervision | Completed |  | Stair 24 - Adaptable Box / __s require fixed lid either side for A&M purposes. The current installation does not meet the A&M requirements for future cable installation or rewiring. The __s / adaptable boxes are not uniform, in terms of distance between light fittings. These lights / circuits have been installed, IRNd and energised. __ to confirm corrective action and extent of reworks
| 02SL - Stations (LUL) | Cxxx-NCR-002763 | NCR | Selux Lighting Trunking Dummy Panels |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2021-05-07 12:11 | 311 | 2019-06-05 08:44 | Electrical - General | 10000 |  | Material | Use As-Is | 2 (6-60k) | Complete | Material/Preservation Problems - Other | Completed |  | Selux Lighting Trunking Dummy Panels have been designed / procured not fit for the environment that they are to be installed. The Dummy Panels incorporate a back plate which clashes with the __s (which are required for local isolation JV21.1301 Lighting Design). __ to confirm proposal and relationships with existing MCR, A&M requirements etc. Extent of areas and reworks to be confirmed by __. CRL are aware of issues on LU HCDL P1/P2 and Stair 24.
| 02SL - Stations (LUL) | Cxxx-NCR-002764 | NCR | CRL Platforms - CS1 Closure Works - Waterproofing installation, non-calibrated testing equipment |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-07-18 | 2019-07-01 10:01 | -17 | 2019-06-06 09:08 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Info: Close out works of Construction Shaft 1 [CS1] was handed to Cxxx. Cxxx was tasked to complete the following aspects of work to close out CS1: > Construction of Capping slab > Continuation of Waterproofing membrane [this NCR] > Foam Concrete backfill This NCR is related to the waterproofing works. Water proofing works was carried out by sub-contractor 'Ck-teck ltd' whom have worked within the tunnel sections for the water proofing membrane. Issue: Non-conformance to section 9.1, Testing of ITP - Cxxx-__M-C-ITP-D061_WS106-53079 [Rev 2] From reviewing the construction records. it is noted that the calibration certificates for the below testing equipment are outstanding : Durometer - To test curing of Masterseal 345 Humidity tester - To test humidity Depth Gauge - For dry film thickness testing
| 02SL - Stations (LUL) | Cxxx-NCR-002765 | NCR | Court Street Staircase Handrails: Retrospective Inspection |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-08-17 | 2019-08-20 07:55 | 3 | 2019-06-07 13:25 | Architectural - Handrail | 1200 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Cxxx-NCR-002379 captures the lack of assurance records/documentation for the Court St Urban Realm works. This included the staircase handrail fabrication and installation, for which the works were completed in the absence of an approved ITP. Following review of Cxxx-NCR-002379, a retrospective inspection was arranged with CRL and completed and checked against an adapted version of Cxxx-__M-A-ITP-D061_WS106-50124: ITP for Balustrade, Handrail and Walkways. The following non-conformances were identified: - Top posts at bridge level were fabricated 891mm instead of 870mm as shown on drawing Cxxx-__M-C-DWG-D061_WS106-53677. - In some instances, dome nuts are installed atop regular nuts. - Lack of evidence to support correct installation of anchor rods. Pull-out test certificate is provided, however this was completed by a non-UKAS accredited body. - Lack of evidence to support correct resin, and correct installation. Pull-out test certificate is provided, however this was completed by a non-UKAS accredited body. - Lack of evidence to confirm correct torquing applied to nuts / elbow fixings. No calibration certificate is provided for the torque wrench used. - Incomplete grouting. - Granite tile steps slightly out of tolerance.
| 02SL - Stations (LUL) | Cxxx-NCR-002766 | NCR | LO - Stair 25 - As-built Survey Dimension Discrepancies |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-08-21 | 2019-07-01 10:08 | -51 | 2019-06-07 09:04 | Architectural - Balustrade | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As-built installation of Stair 25 balustrade has minor discrepancies against design dimensions.
| 02SL - Stations (LUL) | Cxxx-NCR-002767 | NCR | DSS LV7 Mist Suppression Drainage - Installation Of Pipework Without Assured Design |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-08-12 | 2019-08-09 09:32 | -3 | 2019-06-13 15:07 | Mechanical - Mechanical Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | Mist suppression drainage pipework installed prior to having an assured design
| 02SL - Stations (LUL) | Cxxx-NCR-002768 | NCR | DSS LVA Stair Case Pressurisation Louvre Connection - Failure To Comply With Specification |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-07-24 | 2019-12-13 15:34 | 142 | 2019-06-14 10:05 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | __ have failed to comply with specification Cxxx-__M-M-RSP-D061_WS106-50002 and BESA DW 143: Guide to Good Practice - Ductwork Air Leakage Testing as the final leg of the stair case pressurisation ductwork leading to the louvre cannot be tested as it is not practicable. 100% of the ductwork must be tested on life-safety systems, meaning that in this instance, __ are in breach of the above specification and guides.
| 02SL - Stations (LUL) | Cxxx-NCR-002769 | NCR | DSS LVB Platform Smoke Extract Louvre Connection - Failure To Comply With Specification |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-07-24 | 2019-12-13 15:37 | 142 | 2019-06-14 10:27 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | __ have failed to comply with specification Cxxx-__M-M-RSP-D061_WS106-50002 and BESA DW 143: Guide to Good Practice - Ductwork Air Leakage Testing as the final leg of the platform smoke extract ductwork leading to the louvre cannot be tested as it is not practicable. 100% of the ductwork must be tested on life-safety systems, meaning that in this instance, __ are in breach of the above specification and guides.
| 02SL - Stations (LUL) | Cxxx-NCR-002770 | NCR | PRD design pressure |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2019-10-31 | 2019-12-18 17:54 | 48 | 2019-06-18 06:42 | Mechanical - Heating Ventilation & Air Conditioning | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | The design value for the PRD's to open in the staircase pressurisation system is 30pa. The dampers open to early to maintain staircase pressure and should be 50pa
| 02SL - Stations (LUL) | Cxxx-NCR-002771 | NCR | THC LV1 Ductwork Installation - Working To Unapproved Drawings |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-07-31 | 2019-08-09 07:51 | 9 | 2019-06-18 09:12 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | __ completed the installation of ductwork in Ticket Hall & Concourse Level 1 Area working to drawings that had not been given a Code 1 status by Crossrail
| 02SL - Stations (LUL) | Cxxx-NCR-002772 | NCR | CHS Level A MCC02 Field Device Locations |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-09-26 | 2019-06-20 11:15 | -98 | 2019-06-18 09:47 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | MCC Field device locations assured by __ and reviewed by __ as shown on __-SKETCH-0016, 0018, 0019, 0020, 0035 and 0068. IRF number - IRF_MEP PERM_CHS_0392 IRN number - Cxxx-__M-E-NOX-D061_WS107-50221
| 02SL - Stations (LUL) | Cxxx-NCR-002773 | NCR | CHS Level A MCC04 Field Device Locations |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-09-26 | 2019-06-20 11:10 | -98 | 2019-06-18 09:53 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | MCC Field device locations assured by __ and reviewed by __ as shown on __-SKETCH-0049 and 0050. IRF number - IRF_MEP PERM_CHS_0393 IRN number - Cxxx-__M-E-NOX-D061_WS107-50220
| 02SL - Stations (LUL) | Cxxx-NCR-002774 | NCR | CHS Level A MCC02 PLC and MCC04 PLC Header Trunking CMS Undersized |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-03-02 12:58 | -120 | 2019-06-18 10:43 | Electrical - Cable Management | 4000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Following a __ review of the CMS on CHS Level A, it appears that the header trunking for the MCC02 PLC panel may be under sized. Current CMS calculations and assumptions mean that the CMS cannot be validated by __. The current CMS is 100mm x 100mm IP4X Trunking. The CMS for all of level A is captured under a single CMS IRF under the Outstation IRN, so both are linked to this NCR.
| 02SL - Stations (LUL) | Cxxx-NCR-002775 | NCR | THC LV1 Ductwork Insulation - Working To Unapproved Drawings |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-08-18 | 2019-08-09 09:37 | -9 | 2019-06-19 08:02 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | __ proceeding to install lagging on ductwork prior to having drawings approved
| 02SL - Stations (LUL) | Cxxx-NCR-002776 | NCR | CHS and DSS cold water booster sets |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2019-07-29 | 2019-12-09 13:34 | 133 | 2019-06-19 08:55 | Mechanical - Mechanical Engineering General | 2000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | During the commissioning stage it has become apparent that the booster sets provided in the both DSS and CHS are supplied with a 1 phase electrical supply when they should have been provided with 3 phase. equipment schedule references CHS Cxxx-__M-M-TSC-D061_WS107-50004 DSS Cxxx-__M-M-TSC-D061_WS105-50041
| 02SL - Stations (LUL) | Cxxx-NCR-002778 | NCR | THe Contractor was unable to provide checksheets for Asset Labelling in line with Cxxx-__M-E-ITP-D061_WS106-*50097 Rev 2.0 |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2019-09-30 | 2019-11-30 14:38 | 61 | 2019-06-20 09:53 | Information Management - Asset Information | 10000 |  | Documentation and Records | Repair | 2 (6-60k) | Complete | Management Problem - No evidence of program review from Contractor's Quality Manager or Management | Completed |  | During a Crossrail led Surveillance the Contractor was unable to provide deliverable records/checksheets for the installed asset labels in line with ITP *50097
| 02SL - Stations (LUL) | Cxxx-NCR-002779 | NCR | Re-location of CHS OPE-TVS Interface Panel |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-09-29 | 2019-07-13 14:18 | -78 | 2019-06-21 11:36 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The OPE-TVS Interface panel in CHS Level 6 has been installed in a different location to the original design.
| 02SL - Stations (LUL) | Cxxx-NCR-002781 | NCR | CMS modifications to DC8 / DC9 |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-02-11 16:14 | -140 | 2019-06-22 08:52 | Electrical - Cable Management | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Modifications undertaken to previously installed CMS in DC8 / DC9 due to clashes with the Fire Main. These changes have been undertaken without adhering to the change control process. This CMS was originally altered and increased due to being undersized - __ to confirm coordination was undertaken for original change via change control process reference / evidence. __ to provide details of reworks including validation to proposed modifications including CMS calcs etc.
| 02SL - Stations (LUL) | Cxxx-NCR-002782 | NCR | Rewiring P5 / P6 Lighting Boom Circuits |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-02-11 16:22 | -140 | 2019-06-22 09:52 | Electrical - General | 10000 |  | Incorrect Installation | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | __ have had to undertaken rewiring of various lighting circuits on Platform 5 and Platform 6 due to relocation of the __s for Access and Maintenance within the Lighting Booms __ to confirm extent of reworks and confirm that previous witness points as per ITP have been adhered to prior to cabling installation.
| 02SL - Stations (LUL) | Cxxx-NCR-002783 | NCR | Reinstallation of Cable D22 |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2019-08-01 | 2020-01-27 12:14 | 179 | 2019-06-22 10:11 | Electrical - General | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | Cable D22 has been installed as a Non Fire Rated cable for a secure / operational critical supply to LO ATS with inadequate segregation between alternative supply (L03). As a result, per LU S1120, the supplies are to be FTP 120 (Fire Rated) These works were undertaken prior to design acceptance and without adhering to the ITP witness points.
| 02SL - Stations (LUL) | Cxxx-NCR-002784 | NCR | Poor Inspection / IRF of SAT test of LO CER ATS |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-03-24 09:09 | -98 | 2019-06-24 09:34 | Electrical - Power Distribution | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | IRF scheduled by __, On the 3rd attempt the correct drawings were listed along with the ITP. At the time of the inspection __ did not have any of the drawings listed and when speaking to the Engineering/Supervision leading the inspection they did not have Access to EB or know how to use it. __RT who are responsible for the SAT testing turned up to site with the wrong schematic, Witnessing of SAT test was successful as the correct documentation was supplied by the CRL FAE.
| 02SL - Stations (LUL) | Cxxx-NCR-002785 | NCR | Damage to multimeter on MCC 08 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-09-25 | 2019-10-14 09:00 | 19 | 2019-06-25 14:27 | Electrical - Switchgear | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | MCC 08 - panel section B6 - E445 - CHS/8/UPSP/03 & CHS/8/UPSP/04 WEST BOUND 1.2kW. Multimeter broken MCC 08 - panel section B5 - E444 - CHS/8/UPSP/01 & CHS/8/UPSP/02 EAST BOUND 1.2kW. Multimeter broken
| 02SL - Stations (LUL) | Cxxx-NCR-002787 | NCR | DSS Level B Secondary CMS |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-02-28 15:44 | -123 | 2019-07-01 14:48 | Electrical - Cable Management | 2000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Trunking installed as secondary CMS without assured design.
| 02SL - Stations (LUL) | Cxxx-NCR-002788 | NCR | CRL Platforms - GFRC Asbuilt tolerance |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-08-13 | 2019-07-11 08:17 | -33 | 2019-07-04 15:12 | Architectural - General | 0 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The asbuilt survey has been carried out on CRL platforms (including cross passages). It shows some of the areas to be out of the required tolerance. Asbuilt surveys highlighting the sections of GFRC that are out of tolerance are attached.
| 02SL - Stations (LUL) | Cxxx-NCR-002789 | NCR | Missing CMS for 300mm Earth Ring Cables between E3 and E9 |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-08-25 14:47 | 56 | 2019-07-08 12:29 | Electrical - Cable Management | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | As part of the requirements for EMP Rev 10, various 300mm Earth Cables were required to form part of the Earth Ring to existing operational switchrooms E3 and E9. __ have installed and terminated 300mm Earth Ring cables with insufficient CMS which does not adhere to the ITP prerequisites and witness points prior to installing and terminating cables
| 02SL - Stations (LUL) | Cxxx-NCR-002790 | NCR | MEP - CHS Level 6 BMS Secondary CMS |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-11-07 | 2019-11-30 15:50 | 23 | 2019-07-08 16:35 | Electrical - Cable Management | 1500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Trunking installed as secondary CMS by __ without assured design.
| 02SL - Stations (LUL) | Cxxx-NCR-002791 | NCR | DSS LV1 North Stair Case Pressurisation Louvre Connection - Failure To Comply With Specification |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-08-18 | 2019-12-13 15:26 | 117 | 2019-07-09 16:03 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | __ have failed to comply with specification Cxxx-__M-M-RSP-D061_WS106-50002 and BESA DW 143: Guide to Good Practice - Ductwork Air Leakage Testing as the final leg of the stair case pressurisation ductwork leading to the louvre cannot be tested as it is not practicable. 100% of the ductwork must be tested on life-safety systems, meaning that in this instance, __ are in breach of the above specification and guides.
| 02SL - Stations (LUL) | Cxxx-NCR-002792 | NCR | Corrosion to UPS back of house UPS trunking |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-08-19 | 2019-09-04 13:13 | 16 | 2019-07-10 18:10 | Electrical - Cable Management | 2500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Installation of 50X50mm UPS single compartment trunking at the back of house area, East platform of the Westend (trace). Cxxx has installed trunking as per design but due to water seepage from the walls of the tunnels falling onto the trunking has caused corrosion to the trunking and questions the location and IP Rating of the of the trunking.
| 02SL - Stations (LUL) | Cxxx-NCR-002793 | NCR | Pull Testing LO Platform 5 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-11-09 | 2019-08-14 09:29 | -87 | 2019-07-12 10:57 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Fixings to earth bars EB-E/3/663/1A in Switch room E3 and EB-E/3/662/1A in switch room E9 were not pull tested in accordance with specification which requires a percentage of the live fixings to be pull tested. Instead sacrificial anchors in the same location were pull tested.
| 02SL - Stations (LUL) | Cxxx-NCR-002794 | NCR | Failed Witness of CHS/8/SREF/01&02 Air Volume Test |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-08-24 | 2019-08-13 10:39 | -11 | 2019-07-15 08:30 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | IRF Doc Number : IRF_MEP PERM_CHS_0461 was issued to witness CHS/8/SREF/01&02 Air Volume Flow Rates, however, whilst attempting to witness these flow rates it was realised that the first flow rate was significantly higher than the test sheet recorded figures.
| 02SL - Stations (LUL) | Cxxx-NCR-002795 | NCR | Staricase pressuristation connection to external louvre |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-02-07 11:02 | -144 | 2019-07-16 06:34 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The ductwork connection to from the staircase pressurisation duct work to the external Louvre in the southern head house in DSS is a self adhesive foam joint. This is unacceptable and does not conform to HVAC DW144 specification listed in the WI. This has been outstanding for some considerable time and is with holding the IRN progress and risk to SC1
| 02SL - Stations (LUL) | Cxxx-NCR-002796 | NCR | CMS in Dist Room B2 Insufficient Cable capacity |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-08-25 | 2019-10-01 15:12 | 37 | 2019-07-16 17:50 | Electrical - Power Distribution | 1500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | On drawing Cxxx-__M-E-DDA-D061_WS106_7-32284 C01 - the drawing shows a 50x50mm secondary CMS trunking for the dali cabling route to the LCM's & smart router in Dist Room B2. This 50x50mm trunking was installed mid last year. On the newly issued drawing coded C02 it now shows the dali trunking in 100x100mm trunking. This is due to Increase in install of additional lighting control cables to accomodate the PES lights. On cable calculation report the C01 install provides Inssufficient Cable capacity. Due to the rooms size and other services it cannot be installed as per C02 design.
| 02SL - Stations (LUL) | Cxxx-NCR-002797 | NCR | DSS PRSF Fans |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-02-08 11:20 | -143 | 2019-07-18 14:37 | Mechanical - Heating Ventilation & Air Conditioning | 2000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Not Defined | Completed |  | MCC 10 Outgoing cables going to DSS/A/PRSF/03&04 have been run to the incorrect fans. The Mechanical drawing Cxxx-__M-M-DDA-D061_WS105_A-10270 shows PRSF/04 on the Left and PRSF/03 on the right. The fans have been installed as per the drawing. The electrical cables and controls are wired as PRSF/03 on the left and PRSF/04 on the right. Electrical Drawing Cxxx-__M-E-DDE-D061_WS105_A-30904 X03 used at the IRN shows the isolators located on the wall next to MCC10. This is not as installed, the isolators are now located in front of the fans with PRSF/03 on the left and PRSF/04 on the right.
| 02SL - Stations (LUL) | Cxxx-NCR-002799 | NCR | Faulty MCCB Trips |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-09-01 | 2019-08-14 13:22 | -18 | 2019-07-23 15:57 | Electrical - LV Equipment | 2000 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | During Function testing some __ MCCB trip devices failed to operate correctly.
| 02SL - Stations (LUL) | Cxxx-NCR-002800 | NCR | Removal of permanent asset post IRN |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-09-02 | 2019-08-28 09:57 | -5 | 2019-07-24 07:33 | Mechanical - Public Health Engineering | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Removal of permanent asset post IRN - Cable W449 from MCC9 to Booster bump panel via Isolator, was disconnected from the isolator to make way for a temporary supply.
| 02SL - Stations (LUL) | Cxxx-NCR-002801 | NCR | Energising equipment that has not been IRN'd |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-09-02 | 2019-11-30 15:57 | 89 | 2019-07-24 15:44 | Mechanical - Public Health Engineering | 2000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Energisation of the DSS/3/BP/01 & 02 Booster Pump Set Control Panel before the panel was IRN'd.
| 02SL - Stations (LUL) | Cxxx-NCR-002802 | NCR | LU Platforms 1 & 2 S33/34 glazed screen and balustrade design |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-09-24 20:00 | 86 | 2019-07-26 09:47 | Architectural - Balustrade | 3000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The glass screen and stanchion balustrade around the perimeter of S33 and S34 on patforms 1 and 2 has an approved F2 design and an approved CAT check. The Subcontractor for these works, __, internally reviewed the CAT while designing a separate element of works and noticed errors in the design calculations. These errors should have been picked up either by the internal check of the designer (Somerset Structural) or by the CAT II checker (Howard and McNamara), indicating inadequate checking.
| 02SL - Stations (LUL) | Cxxx-NCR-002803 | NCR | MEP - CHS Level 3 BMS Secondary CMS |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-11-06 | 2019-10-23 12:16 | -14 | 2019-07-29 15:15 | Electrical - Cable Management | 1500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Trunking installed as secondary CMS by __ without assured design.
| 02SL - Stations (LUL) | Cxxx-NCR-002805 | NCR | MEP - DSS Level A DSS/A/CE/02 Field Device Assurance |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-11-07 | 2019-08-13 10:13 | -86 | 2019-07-30 12:55 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | BMS Field device locations assured by __ and reviewed by __ as shown on __-SKETCH-0286, 0287, 0288 and 0289 IRF number - IRF_MEP PERM_CHS_0629 IRN number - Cxxx-__M-M-NOX-D061_WS107-50005
| 02SL - Stations (LUL) | Cxxx-NCR-002806 | NCR | MEP - DSS Level A DSS/A/CE/03 Field Device Assurance |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-11-08 | 2019-08-13 10:16 | -87 | 2019-07-31 09:26 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | BMS Field device locations assured by __ and reviewed by __ as shown on __-SKETCH-0290, 0291, 0292 and 0293 IRF number - IRF_MEP PERM_DSS_0642 IRN number - Cxxx-__M-M-NOX-D061_WS105-50006
| 02SL - Stations (LUL) | Cxxx-NCR-002807 | NCR | MEP - DSS Level A MCC10 Field Device Assurance |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-11-08 | 2019-08-13 10:21 | -87 | 2019-07-31 10:12 | Mechanical - Mechanical Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | BMS Field device locations assured by __ and reviewed by __ as shown on __-SKETCH-0301 and 0302 IRF_MEP PERM_DSS_0643 Cxxx-__M-M-NOX-D061_WS105-50052
| 02SL - Stations (LUL) | Cxxx-NCR-002808 | NCR | MEP - DSS Level A MCC11 Field Device Assurance |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-11-08 | 2019-08-13 10:25 | -87 | 2019-07-31 10:22 | Mechanical - Mechanical Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | BMS Field device locations assured by __ and reviewed by __ as shown on __-SKETCH-0303, 0304 and 0305 IRF_MEP PERM_DSS_0644 Cxxx-__M-M-NOX-D061_WS105-50053
| 02SL - Stations (LUL) | Cxxx-NCR-002809 | NCR | Isolators in Mechanical Plant Room 2 Re-works, GSM Level 2 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-03-27 09:00 | -95 | 2019-08-02 08:30 | Electrical - General | 5000 |  | Design | Use As-Is | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | Design issue.
| 02SL - Stations (LUL) | Cxxx-NCR-002810 | NCR | sump pump isolators GSM level 2 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-09-11 | 2019-11-30 16:01 | 80 | 2019-08-02 15:00 | Electrical - General | 4000 |  | Design | Use As-Is | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | We are now using one of the redundant circuits fed from DNO DB6 10L 1, 2, 3 originally installed for one of the isolators feeding sump pumps in the cleaners lobby GSM building Level 2. 2 isolators installed by __ are no longer required as Pump Server have installed their own isolators for the sump pumps which are fed directly from the main sump pump control panel GSM/02/SP/01-02. DB schedule shows that main sump pump control panel DNO DB6 12L, 1, 2, 3 requires a 4mm supply. Rather than pull in a new 3 phase supply from DNO DB6, we will be using one of the redundant circuits DNO DB6 10L,1 2, 3 - N + E [6mm] if there is enough length on the cable to move and use for the sump pump control panel. This would mean the CSA of the cable would increase from a 4mm to a 6mm.
| 02SL - Stations (LUL) | Cxxx-NCR-002811 | NCR | Failure of Commissioning Witness for DSS/3/BP/01&02 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-09-15 | 2019-09-16 07:40 | 1 | 2019-08-06 14:37 | Mechanical - Hot & Cold Water Supplies | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | During the commissioning witness of the above pumps, it was noted that the pressure switch on the inlet of the pump was not able to protect the pump from running dry. The minimum pressure for the switch was 1.5 Bar however as the tank is located just above the pump the head was less than 1 Bar. The pressure switch had been linked out so that the pump could operate however this removed the pump protection.
| 02SL - Stations (LUL) | Cxxx-NCR-002812 | NCR | LULO - HCDL Glazed Screen Out of tollerence |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-09-16 | 2019-09-16 15:44 | 0 | 2019-08-07 08:49 | Architectural - Glazing | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following an as-built survey of the HCDL glazed screen (IWS-813) it has been identified that the position is outside the allowable tolerance specified in the architectural specification Cxxx-__M-A-RSP-D061-50079 Revision 75. See attached As-Built Survey with further details.
| 02SL - Stations (LUL) | Cxxx-NCR-002813 | NCR | MEP - DSS Level 4 BMS Secondary CMS |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-11-16 | 2019-10-22 10:07 | -25 | 2019-08-08 13:32 | Electrical - Electrical Engineering General | 3000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Trunking installed as secondary CMS by __ without assured design.
| 02SL - Stations (LUL) | Cxxx-NCR-002814 | NCR | MEP - CHS Level A BMS Field Device Assurance |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-11-16 | 2019-08-13 10:29 | -95 | 2019-08-08 13:23 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - NCR excessive closure due to design issue | Completed |  | BMS Field device locations assured by __ and reviewed by __ as shown on __-SKETCH-0324, 0325, 0326, 0327, 0328, 0329 and 0330. IRF number - IRF_MEP PERM_CHS_0435 IRN number - Cxxx-__M-M-NOX-D061_WS107-50005
| 02SL - Stations (LUL) | Cxxx-NCR-002815 | NCR | MEP - DSS Level A ICB fan isolator relocation (DSS/A/CE/03) |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-11-17 | 2019-11-30 16:02 | 13 | 2019-08-09 10:16 | Electrical - LV Equipment | 1500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The ICB fan isolator was moved on DSS level A without an accepted FCD. The PTR had been raised and accepted by __ and an FCD created but not accepted at the time of the relocation.
| 02SL - Stations (LUL) | Cxxx-NCR-002817 | NCR | MEP - DSS Level B BMS Outstation Panel Move |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-11-21 | 2019-11-01 11:52 | -20 | 2019-08-13 14:50 | Electrical - Electrical Engineering General | 3000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Please see the attached PTR for the move of the BMS outstation panel on DSS level B. The panel had to move due to the increased size of the MCC. The outstation would have been above the heater so it was relocated to the wall that the PLC is on. Please see attached mark ups showing panel locations and small power items such as isolators. This has been transferred from Cxxx-FCD-002995, which was originally created to capture this design change.
| 02SL - Stations (LUL) | Cxxx-NCR-002818 | NCR | MEP - DSS Level B DSS/B/CE/01 Field Device Locations |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-11-21 | 2019-08-23 09:51 | -90 | 2019-08-13 15:51 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | This NCR is being raised to capture the locations of the BMS field devices on DSS level B. BMS field device locations were only detailed on the F1 Ventilation design schematic Cxxx-__M-M-DDE-D061_WS105_Z-40805. BMS Field device locations were assured by __ and reviewed by __ as shown on __-SKETCH-0145, 0187, 0188, 0296, 0297 and 0298. IRF number - IRF_MEP PERM_DSS_0578 IRN number - Cxxx-__M-M-NOX-D061_WS105-50003
| 02SL - Stations (LUL) | Cxxx-NCR-002820 | NCR | MEP - DSS Level 3 Secondary CMS |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-03-07 09:42 | -115 | 2019-08-22 12:21 | Electrical - Cable Management | 3000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Trunking installed as secondary CMS by __ without assured design.
| 02SL - Stations (LUL) | Cxxx-NCR-002821 | NCR | MEP - DSS Level 3 BMS/PLC Field Device Locations |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-11-30 | 2019-08-23 09:57 | -99 | 2019-08-22 13:25 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | This NCR is being raised to capture the locations of the BMS and PLC field devices on DSS level 3. Field device locations were only detailed on the F1 Ventilation design schematic Cxxx-__M-M-DDE-D061_WS105_Z-40805. Field device locations were assured by __ and reviewed by __ as shown on __-SKETCH-0333, 0337, 0338, 0339, and 0347. IRF number - IRF_MEP PERM_DSS_0454 IRF number - IRF_MEP PERM_DSS_0572 IRN number - Cxxx-__M-E-NOX-D061_WS105-50762 IRN number - Cxxx-__M-M-NOX-D061_WS105-50008
| 02SL - Stations (LUL) | Cxxx-NCR-002823 | NCR | LULO - ESS - Weep Holes installed incorrectly |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-11-29 | 2019-11-06 08:20 | -23 | 2019-08-15 15:29 | Architectural - General | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The weep holes on the East Stair Shaft have been installed incorrectly, with mastic visibly blocking the route behind it. This stops the weep hole acting as designed, as condensation/water cannot transfer between the two sides of the PCC Cladding.
| 02SL - Stations (LUL) | Cxxx-NCR-002825 | NCR | LULO - Lower Canopy Inside Fascia Height Discrepancy |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2021-01-18 10:21 | 202 | 2019-08-20 15:34 | Architectural - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __ has installed the fascia panels along the inside of the lower canopy on the HCDL platforms. However, the levels of the fascia are approximately 30mm higher than the heights as per Cxxx-__M-A-DDF-D061_WS106_2-12253. This has caused their to be a step between the fascia and ceiling interface (See attached photo).
| 02SL - Stations (LUL) | Cxxx-NCR-002826 | NCR | MEP - CHS Level 1 Secondary CMS |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-11-29 | 2019-10-22 10:05 | -38 | 2019-08-21 13:47 | Electrical - Cable Management | 3000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Trunking installed as secondary CMS by __ without assured design.
| 02SL - Stations (LUL) | Cxxx-NCR-002827 | NCR | MEP - CHS Level 5 ARDC PLC Secondary CMS |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-11-29 | 2019-10-19 15:25 | -41 | 2019-08-21 10:50 | Electrical - Cable Management | 2000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Trunking installed as secondary CMS by __ without assured design.
| 02SL - Stations (LUL) | Cxxx-NCR-002828 | NCR | Tunnel Platforms - CRL Platforms & DSS Level 7 - Paving - Screed Hammer Test not carried out |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-10-27 | 2019-10-10 10:34 | -17 | 2019-08-21 12:52 | Architectural - Flooring | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | During installation of the paving in CRL Platforms and Crosspassages & DSS Level 7 Public Areas the “Impact and Strength Test” (Hammer Test) to the base screed was not carried out, as per the Specification JM10.2202. The material used for the base screed and the screed underneath the tiles is a Ultra Rapid Drying Cement __ A38, as per spec JM41.1210 The installation methodology used "wet fix method" is described below: 1. Lay polythene (unbounded screed) 2. Lay bed of screed 75mm (pre-screed) 3. After 4 hours (when walkable) Apply coat of slurry (__ A38+E100) on top of Prescreed and install fresh bed of screed 4. Apply coat of slurry (__ A38+E100) on top of screed 5. Place Grannazzo tiles on top of wet slurry 6. Hammer the tiles down to required level with mallet With this sequence pre screed will be walkable and will allow for second layer of screed and pavers to be installed (after 3-4 hours), but base screed still will not be ready for drop hammer test (it will be ready after 6 hours from installation).
| 02SL - Stations (LUL) | Cxxx-NCR-002829 | NCR | MEP - DSS Level 6 ARDC01 & 02 Secondary CMS |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-11-30 | 2019-10-18 09:44 | -43 | 2019-08-22 15:11 | Electrical - Cable Management | 2000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Trunking installed as secondary CMS by __ without assured design.
| 02SL - Stations (LUL) | Cxxx-NCR-002830 | NCR | MEP - DSS Level 3 - Booster Pump Cavitation & Vessel Pressure |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-10-30 | 2019-10-26 09:44 | -4 | 2019-08-23 11:53 | Mechanical - Pumps | 3500 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | Cold booster pump set is currently installed incorrectly due to the feed from the tank to the pump set being an incorrect size. The feed from the tank to the pump set is currently 32mm, in which goes in to a 54mm header. In addition to this, the pressure vessel is currently set at 0.7 bar above the set point (2.5 bar), but this needs to be changed to 0.7 times the set point pressure, meaning that the vessel should be set at 1.75 bar.
| 02SL - Stations (LUL) | Cxxx-NCR-002831 | NCR | Installation of ARDC Panels - CHS & DSS |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2020-01-21 | 2020-01-11 16:06 | -10 | 2019-12-12 11:56 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | __ have installed ARDC Panels in CHS and DSS without an accepted MCR. Due to the location of some of these panels (areas greater than 200m3) __ to confirm via MCR submittal Fire Compliance Code and whether concession is required. Panel positions have been captured via Cxxx-FCD-002911. Said FCD has queries / suggestions, __ to confirm panel positions via PTR and sketches, including heights of panels as during inspection it was noted that some have restricted access due to height - have these been agreed in addition to where they are to be captured (O&M / Risk Register) etc.
| 02SL - Stations (LUL) | Cxxx-NCR-002832 | NCR | LULO - Column Manifestation LRV Results & Incorrect RAL Colour |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-12-29 | 2019-10-22 10:02 | -68 | 2019-08-27 18:09 | Architectural - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The Architectural Specification clause JH75.1241 specifies that the HCDL column manifestations are RAL 7045. On the __ F2 design drawing Cxxx-__M-A-DWG-D061_WS106-53688 __ incorrectly labelled the manifestation as RAL 7015 and subsequently fabricated the manifestations as RAL 7015. The criteria of the manifestation is that it needs to provide a 30 point LRV contrast with the column lining. __ sent Rimex Black Granex M1A 316 & RAL 7015 for LRV testing with a UKAS accredited test house to establish the LRV difference between the two materials that had been manufactured. See attached test report from Lucideon. The test report confirmed that the Black Rimex that was assumed by the F1 designer to have an LRV of 2 in fact has an LRV of 17.1. RAL 7015 gave an LRV of 11.1. Therefore only a 6 points difference between the two manufactured products exists instead of 30 points. This NCR has been raised specifically for the manifestations on the HCDL columns. A separate NCR will be raised for other interfaces with Black Rimex.
| 02SL - Stations (LUL) | Cxxx-NCR-002833 | NCR | MEP - Stationwide BMS/PLC Design Assurance |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-03-23 12:29 | -99 | 2019-11-08 16:27 | Mechanical - Mechanical Engineering General | 25000 |  | Design | Use As-Is | 2 (6-60k) | Complete | Design Problem - Other | Completed |  | There have been ongoing issues throughout the project relating to the assurance of the BMS/PLC systems; in order to provide an F2 design from the BMS and PLC points lists, the network schematic and F1 design drawings and schematics the design must be assured by all relevant parties.
| 02SL - Stations (LUL) | Cxxx-NCR-002834 | NCR | MEP - DSS - LVA to LV7 - Staircase Pressurisation Ductwork Lagging |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-10-28 | 2019-12-13 16:18 | 46 | 2019-08-29 09:58 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | __ proceeding to install lagging on staircase pressurisation ductwork prior to the ductwork being signed off by CRL.
| 02SL - Stations (LUL) | Cxxx-NCR-002835 | NCR | MEP - DSS ARDC Panels and DPx Sensor Locations Changed |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-12-08 | 2019-12-17 14:34 | 9 | 2019-08-30 09:34 | Electrical - Electrical Engineering General | 2000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The ARDC panels and DPx units on DSS levels 5 and 6 have been moved without a prior assured design.
| 02SL - Stations (LUL) | Cxxx-NCR-002836 | NCR | MEP - LULO - Lv4 - DC8/DC9 CMS Installation pre-FCD |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-02-11 16:17 | -140 | 2019-08-30 08:39 | Electrical - Cable Management | 2000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | We have installed Trunking rather than Basket at __ request in DC8 & DC9
| 02SL - Stations (LUL) | Cxxx-NCR-002837 | NCR | MEP - No MCR Currently Exists for SOR OPE Override Switch |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-12-08 | 2020-01-27 12:19 | 50 | 2019-08-30 13:59 | Electrical - Electrical Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | No MCR currently exists for the SOR OPE Override switch in the SOR room, ticket hall and concourse area.
| 02SL - Stations (LUL) | Cxxx-NCR-002838 | NCR | Concourse Cladding - Dead fixing detail |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-02-13 08:44 | -138 | 2019-09-05 12:28 | Architectural - General | 2500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | This is NCR is being raised further to SIER report for RIVO number 11056205. The design philosphy is to dead fix the last installed panel in a row of panels. However, it has been found that where headroom is limited and the hooks to support the stainless steel cladding are orientated horizontally, once the dead fix panel is removed, the remaining panels are not secure in the temporary condition. This has the potential to cause issues in the future station O&M activities. To mitigate this risk all panels on the concourse will be dead fixed. Horizontally hooked panels - 2no Vertically hooked panels - 1no The Contractor attaches CAT II report Cxxx-__M-A-CER-D061_WS106-57010 which provides the general method of dead fixing panels. Where required, further details will be provided for other areas. The fixings will be captive as per discussions.
| 02SL - Stations (LUL) | Cxxx-NCR-002839 | NCR | LULO - ESS Roof Handrail As-Built out of tolerance |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-12-14 | 2019-10-11 09:52 | -64 | 2019-09-05 10:56 | Architectural - Balustrade | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On completion of an as-built of the east stair shaft handrail it has been identified that the handrail is not within the allowable 2mm tolerance. See attached survey in PDF format that will be formally issued to Crossrail on Cxxx-__M-A-RGN-D061_WS106-50201.
| 02SL - Stations (LUL) | Cxxx-NCR-002840 | NCR | MEP - DSS LV7 - Staircase Pressurisation Ductwork - Failure to follow ITP |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-10-16 | 2019-12-13 15:54 | 58 | 2019-09-06 14:05 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | __ failure to test the whole of the staircase pressurisation ductwork due to the volume being too small
| 02SL - Stations (LUL) | Cxxx-NCR-002841 | NCR | MEP - LULO - Lightning Protection Stair 24 Roof Canopy - Deviation to Design Drawings |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-11-05 | 2020-01-14 08:22 | 70 | 2019-09-06 14:33 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | __ have installed lightning protection air tape without an F2 design drawing
| 02SL - Stations (LUL) | Cxxx-NCR-002842 | NCR | DSS Trace Heating - Works Constructed without a F1 or F2 design |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-10-16 | 2019-11-26 10:33 | 41 | 2019-09-06 14:54 | Electrical - General | 4500 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | DSS Level 1 Trace installation has proceeded without IFC (F1 or F2) drawings in place. Further investigation revealed that key supporting documentation had not been fully approved. CRL1-XRL-M-RSP-CR001-50062 JY23 Trace Heating- j) Each heat-tracing circuit shall be protected electrically by a __ to BS EN 60898 type C or D or equivalent. Additionally a residual current device of 30 mA sensitivity that trips within 100ms should be used. These will form an integral part of the motor control panel or local distribution board.
| 02SL - Stations (LUL) | Cxxx-NCR-002843 | NCR | DSS - Weep Holes installed incorrectly |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2019-12-20 | 2019-11-17 11:30 | -33 | 2019-09-08 16:21 | Architectural - Walls | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The weep holes on the DSS have been installed incorrectly, with mastic and backing rod visibly blocking the route behind it (see attached photos). This stops the weep hole acting as designed, as condensation and or water cannot transfer between the two sides of the PCC Cladding. 1) Reason for change – Works not installed incorrectly. 2) The proposed action: a) Create a hole the full width of the joint and height of the weep hole cage. b) Validate the integrity of the DPC (Cavity tray), ensuring it aligns with the current design. 3. Cost & Programme Impact – None 4. Impact to follow-on/interfacing works – None 4. Evidence of acceptance – Approval from the Designer BH (e.g. PTR) and completed Check sheets as per the ITP.
| 02SL - Stations (LUL) | Cxxx-NCR-002844 | NCR | Stair 26 Lighting Boom wired without IRF |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-02-12 10:29 | -139 | 2019-09-10 12:24 | Electrical - Lighting | 3000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The Selux Lighting Boom was installed above Stair 26 and subsequently wired internally without having the Boom IRF'd in the first instance.
| 02SL - Stations (LUL) | Cxxx-NCR-002845 | NCR | LU - Colour Contrast Requirements Across the HCDL Platforms and Concourse |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-09-27 | 2019-11-21 11:13 | 55 | 2019-09-13 10:28 | Architectural - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Details: In order to meet requirements for visually impaired persons, a colour contrast is required for a number of assets across the HCDL platform and concourse areas. A contrast of 30 points (LRV) difference is required between a number of items and their associated background material. The affected assets have been identified by __ via PTR-8070 and are: HCDL platform handrails – Substrate: Black Rimex column cladding HCDL platform handrails – Substrate: Black Rimex cladding HCDL platform handrails – Substrate: Platform flooring (paved) HCDL column skirting – Substrate: Platform flooring (paved) HCDL Doors – Substrate: Black Rimex cladding As noted in NCR-2832, the Black Rimex cladding has an LVR of 17.1 as opposed to 2 as noted in the F1 design. For this reason the colour contrast for some of the items notes above are different than envisaged in the design. Proposed Answer: Following a workshop with __ (__) and CRL (__), it was verbally agreed that the colour contrast currently provided for the above items was acceptable. It is therefore proposed that the above items are “used-as-is”.
| 02SL - Stations (LUL) | Cxxx-NCR-002846 | NCR | LO - Stair 28 - Incorrect landing slab extension |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-07-16 11:59 | 16 | 2019-09-19 15:13 | Civil - Civil Engineering General | 6000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | 1. Reason for NCR - It has been determined that the Stair 28 extension steel work has been constructed too short and does not satisfy the F1 requirements outlined within DWG Cxxx-__M-A-DDA-D061_WS106_3-12510 and Cxxx RFI 4750. 2. Clear outline of proposal – Rework - __ propose to re-design the landing extension to meet F1 requirements. This will involve replacing the current support members with newly designed members as per attached drawing mark up. 3. Cost & Programme Impact - Cost £3000, Programme delay of 4 weeks however, item is not on the critical path. 4. Impact to follow-on/interfacing works – Completion of architectural paving on the LO concourse
| 02SL - Stations (LUL) | Cxxx-NCR-002847 | NCR | CHS Trace Heating - Works Constructed without a F1 or F2 design |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-12-18 | 2019-11-06 12:24 | -42 | 2019-09-19 15:16 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - NCR excessive closure due to design issue | Completed |  | CHS Level 1/Level A/Level B Trace installation has proceeded without IFC (F1 or F2) drawings in place. Further investigation revealed that key supporting documentation had not been fully approved. CRL1-XRL-M-RSP-CR001-50062 JY23 Trace Heating- j) Each heat-tracing circuit shall be protected electrically by a __ to BS EN 60898 type C or D or equivalent. Additionally a residual current device of 30 mA sensitivity that trips within 100ms should be used. These will form an integral part of the motor control panel or local distribution board.
| 02SL - Stations (LUL) | Cxxx-NCR-002848 | NCR | MCC 07 - supplies to fans - cable size and type incorrect on dead test results. |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-02-08 12:42 | -143 | 2019-09-20 11:25 | Mechanical - Heating Ventilation & Air Conditioning | 1500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Cables E420&E421 on MCC 07 CHS and Cables W405&W408 MCC 06 DSS are run in SWA cable as per the __ schedule from the VSD to the local isolator to the Fan. the cable fitted between the isolator and the motor is a manufacturer supplied CY cable which is 1.5mm. This is incorrect on the dead test sheets.
| 02SL - Stations (LUL) | Cxxx-NCR-002849 | NCR | CHS - Glazed Brickwork - Level A Support Angle |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-10-31 | 2019-10-15 12:03 | -16 | 2019-10-01 12:08 | Architectural - Brickworks/Blockworks | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | A section of stainless steel angle has been installed to the Northern Elevation of CHS on Level A, in order to support the capping bricks. The approval of this method to install the angle is captured in FCD-3427. However, __ failed to include a design for this section of angle and installed and proceeded with the architectural approval only. The attached response to PTR-8276 details a CAT check on the angle installed and confirms it is sufficient as support for the capping brickwork. Additionally, the PTR response confirms there is no testing required for the anchors installed.
| 02SL - Stations (LUL) | Cxxx-NCR-002850 | NCR | CHS - External Glazed Brickwork - Reduced Mortar Testing |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-10-31 | 2019-10-15 12:10 | -16 | 2019-10-01 12:45 | Architectural - Brickworks/Blockworks | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The mortar testing undertaken when constructing the CHS External Glazed Brickwork does not meet the testing frequency outlined in the Architectural Specification Clause JZ21.4300. __ have undertaken grout strength testing but the quantity of test results ascertained is insufficient. However, the actual strength results do reach the minimum strength requirement as demonstrated in the attached PTR response PTR-8277.
| 02SL - Stations (LUL) | Cxxx-NCR-002851 | NCR | MEP - DSS/CHS - Installation of sump pump panels without an ITP |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-11-10 | 2020-01-13 23:34 | 64 | 2019-10-01 13:46 | Electrical - LV Equipment | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | PumpServ have installed the surface water sump pump panels in both DSS & CHS without an approved ITP
| 02SL - Stations (LUL) | Cxxx-NCR-002852 | NCR | Damper actuator fitted is incorrect type |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-11-11 | 2019-12-23 11:25 | 42 | 2019-10-02 07:54 | Systems - Ventilation and Pressure Relief | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Personnel Error - Not Defined | Completed |  | Damper actuators fitted on the inlet to the PRSF (Stair 41 Pressurisation system) are "__ SF24A" type. These are Drive open spring return type dampers. These should be drive open drive closed dampers. Damper type fitted is __ SF24A to be replaced with __ SM24A. MCR for both damper actuators not associated with the IRN.
| 02SL - Stations (LUL) | Cxxx-NCR-002853 | NCR | CHS __ Ceiling As-Built Position |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-06-15 08:54 | -15 | 2019-10-04 15:59 | Fire - Compartmentation | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As per the approved F2 drawings the soffit level of the __ ceilings at CHS are to be 2.420m AFFL Levels 3-7 and 2.632 AFFL at Level 1. The as-builts show variation from these levels outside of the permitted tolerances.
| 02SL - Stations (LUL) | Cxxx-NCR-002854 | NCR | CHS - Glazed Brickwork - Survey As-Built Out of Tolerance |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-11-13 | 2019-10-23 11:07 | -21 | 2019-10-04 15:15 | Architectural - Brickworks/Blockworks | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The external glazed brickwork at CHS has been installed outside of the allowable verticality and straightness tolerances in various locations. The as-built survey details the various levels where checks were undertaken and raw data. This has been analysed by __ whom have confirmed via PTR-8266 that the as-built brick wall is acceptable.
| 02SL - Stations (LUL) | Cxxx-NCR-002855 | NCR | DSS/CHS Sump Pump Panels - Outstanding MCR's |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-11-17 | 2019-11-20 09:30 | 3 | 2019-10-08 13:43 | Mechanical - Pumps | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Lack or improper material identification and traceability | Completed |  | Pressure Transducer CRL-MCR-007852 Flygt Level Probes CRL-MCR-008101 Flygt - N-Pump Series - NP 3202 - CRL-MCR-004283 1.5mm LSZH cable - CRL-MCR-008313 PVC Sheet - Sump Control Panel - CRL-MCR-008341 Not approved on Whitechapel
| 02SL - Stations (LUL) | Cxxx-NCR-002856 | NCR | Cxxx - CHS and DSS - Block work - Mortart test |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-10-23 | 2019-11-07 09:25 | 15 | 2019-10-11 10:51 | Architectural - Brickworks/Blockworks | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | The mortar testing for block work in CHS & DSS does not meet the testing requirement specified in Arch Specification & ITP. All the testing done by __- (UKAS accredited - Some of them are not tested to BS4551) & The mortar supplier: __ (not UKAS accredited - Tested to BS EN 1015) have achieved the minimum strength required. BH`s approval is attached.
| 02SL - Stations (LUL) | Cxxx-NCR-002857 | NCR | LO - R12 Roof Walkway and Access Gantries - As-built Survey Dimension Discrepancies |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-11-20 | 2019-10-28 11:42 | -23 | 2019-10-11 10:22 | Archaeology - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As-built installation of the R12 Roof Walkway and Access Gantries have minor discrepancies against design dimensions.
| 02SL - Stations (LUL) | Cxxx-NCR-002858 | NCR | Emergency Sump Pumps protective devices |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-11-22 | 2019-12-23 15:24 | 31 | 2019-10-13 11:26 | Electrical - Power Distribution | 3000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The design states that RCBO's are to be installed on the circuits, EB4/4L1,2,3, WB1/5L1,2,3, WB4/4L1,2,3. feeding the emergency sump pumps in the back of house areas. currently __ are fitted and due to the design of the DB the only option would be to install Vigi RCBO breakers which would take up in total 6 ways on the distribution boards compromising its 25% spare capacity.
| 02SL - Stations (LUL) | Cxxx-NCR-002859 | NCR | LO - R10 Roof Walkway and Access Gantries - As-built Survey Dimension Discrepancies |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-08-15 12:01 | 46 | 2019-10-16 12:47 | Architectural - Balustrade | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As-built installation of the R10 Roof Walkway and Access Gantries have minor discrepancies against design dimensions.
| 02SL - Stations (LUL) | Cxxx-NCR-002860 | NCR | LULO - ETH Drainage Mat Well Gully Relocation |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-07-01 07:08 | 1 | 2019-10-21 16:54 | Civil - Drainage | 2500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | 1. Reason for Change Through F2 design development of the mat system within the ETH (FL-102), it is necessary to relocate the gully to ensure drainage of the mat occurs. 2. Proposal Cxxx-__-PTR-8327 details the proposal and confirms __ acceptance of the proposed change. 3. Cost & Programme Impact Cost - £1000 Programme - none. The work is to be completed prior to __ returning to site to install the mat system. 4. Impact to follow-on works This change will allow for the mat well to be installed successfully. 5. Evidence of Acceptance Cxxx-__-PTR-8327
| 02SL - Stations (LUL) | Cxxx-NCR-002861 | NCR | Emergency Sump Pumps protective devices CHS |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-12-01 | 2019-12-23 15:25 | 22 | 2019-10-22 06:55 | Electrical - Power Distribution | 2000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The design states that RCBO's are to be installed on the circuit, LPDB3/A/6L1,2,3. feeding the emergency sump pumps in the sump pump room Level 8 at CHS. currently __ is fitted and due to the design of the DB the only option would be to install Vigi RCBO breakers which would take up in total 6 ways on the distribution boards compromising its 25% spare capacity and interferring with other circuits.
| 02SL - Stations (LUL) | Cxxx-NCR-002862 | NCR | CAT III required for GFRC Cladding CRL Platforms |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2021-02-09 12:12 | 224 | 2019-10-24 08:54 | Structural Engineering - Pre-cast | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | At the point of certification, the document Cxxx-__M-C-CER-D061_WS106-53390 CAT III Design and Check Certificate for Trumpet Blast Load PLACEHOLDER was not available. __ are stating “It has been noted that there is reference to CAT III documentation for the GRC Cladding within Structural Report Cxxx-__M-A-RGN-D061_WS106-50017 Rev 1.0. This was carried out separately to the Cxxx contract. The Contractor would like to clarify that they are not providing a CAT III and have instead submitted a CAT II Design and Check Certificate for the GRC Cladding in the tunnels, Escalator and Trumpet (Cxxx-__M-C-CER-D061_WS106-53243 Rev 3.0), which is Code 1. Separate Blast Assessments have been done on specific areas e.g. Cxxx-__M-C-CER-D061_WS105-53138 Rev 1.0. This is considered compliant with LU Standard 1-538, considering the GRC as similar to those examples shown on Page 12 of Cxxx-__M-Z-STP-D061-50071 Rev 1.0”. GFRC and Ladder Frame Structural Report Cxxx-__M-A-RGN-D061_WS106-50017 quotes a CAT III and states “The final blast tests were successfully completed in January 2016 prior to issue of revision T05 and T06 of this report. The report in revision T07 includes clarifications to Crossrail comments received on revision T05. Furthermore, records of Category 2 Checking are included directly in this report. Category 3 Checks carried out by Robert Bird and __ (commissioned by __) are issued separately”.
| 02SL - Stations (LUL) | Cxxx-NCR-002863 | NCR | Different Pump Protection devices |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-02-09 11:22 | -142 | 2019-10-24 16:04 | Mechanical - Pumps | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Pump 1 and pump 2 of the CHS surface water pump set have different protective devises. One being a thermistor which is incorrect and the other being a Klixon over load motor protection which is to design.
| 02SL - Stations (LUL) | Cxxx-NCR-002864 | NCR | Gas Suppression Equipment damage |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-02-14 11:17 | -137 | 2019-10-29 14:02 | Fire - Suppression | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | gas suppression system equipment has been damaged within the CHS(1/410) Gas Bottle Store. The gas suppression system protects the transformer rooms on level 3, TX A 3/810 & TX B 3/811. Control cabling links to the gas bottle gauges have been removed.
| 02SL - Stations (LUL) | Cxxx-NCR-002865 | NCR | Level 3 ESR CHS 25% capacity on earth bar |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-12-09 | 2019-12-23 15:27 | 14 | 2019-10-30 14:11 | Electrical - Earthing & Bonding | 2500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Level 3 ESR at CHS has a 14 way earth bar installed with 12 way are in use. 25% spare capacity not achieved
| 02SL - Stations (LUL) | Cxxx-NCR-002866 | NCR | Emergency Exit Signage has not been installed as per design |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2021-05-14 20:36 | 318 | 2019-10-31 15:12 | Electrical - Lighting | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | Emergency Exit Signs have not been installed as per design. Furthermore, __ have not adhered to the change control process and currently have not validated the Exit Signage positioning / heights against requirements or specification (including LU S1371)
| 02SL - Stations (LUL) | Cxxx-NCR-002867 | NCR | LU-MEP - Lack of FCD - THC Level 1 FCU Condensate Pumps (ref Cxxx-NCR-002745) |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-03-09 14:20 | -113 | 2019-11-01 13:20 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | The FCU Condensate pumps (SB/1/CR/01 & 02) in SOR Room 1/753 and condensate pump (SB/01/CR/03) in SSO Room 1/283 were converted as they were no longer required due to the fact that the FCUs are at high level. Condensate from FCU 01 & 02 discharge into floor gully in SOR Mess Room and condensate from FCU 03 discharge into trapped tundish on RWP. The attached PTR-4878 is raised for the conversion of the FCU's. However, no further FCD was raised to CRL.
| 02SL - Stations (LUL) | Cxxx-NCR-002868 | NCR | ETH - OLOD - Lvl 3 plantroom - Cracks to GL A2 block work wall |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2021-08-25 08:14 | 421 | 2019-11-12 17:22 | Civil - Civil Engineering General | 6000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 1. Reason for NCR – Two cracks have appeared on the blockwork wall that runs along gridline A2 forming switch rooms LV 1 & LVII within the level 3 plant room. It appears the blockwork wall has been constructed using 7.3N blocks rather than 10.4N blocks as specified within drawing Cxxx-HYD-S-DDL-D061_WS106_2-74053. It also appears that one of the cracks has previously been repaired due to the patination of the mortar either side of the crack. 2. Clear outline of proposal – __ propose to repair the crack in the same manner as the first crack with helibond ties or similar. __ request Cxxx to confirm the feasibility of the proposal and provide a design. 3. Cost & Programme Impact – Increase cost and programme due to re-work. 4. Attachments o Cxxx-HYD-S-DDL-D061_WS106_2-74053 o Cxxx-__M-A-DDA-D061_WS106_3-10260 o PTR 3052 mark up sketch o IMG’s
| 02SL - Stations (LUL) | Cxxx-NCR-002869 | NCR | GSM MCC01 AHU Electric Heater Battery Isolator |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-02-20 13:21 | -131 | 2019-11-12 16:52 | Electrical - LV Equipment | 3000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Drawing Cxxx-__M-E-DWG-D061_WS106-50338 shows the isolator for GSM MCC01 AHU Electric Heater Battery as having auxiliary contacts, however the isolator that has been installed does not have these auxiliary contacts.
| 02SL - Stations (LUL) | Cxxx-NCR-002870 | NCR | Faulty VSD on DSS Staircase Pressurisation Duty Fan |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2019-12-23 | 2019-12-12 11:13 | -11 | 2019-11-13 14:26 | Electrical - General | 5000 |  | System Defect | Use As-Is | 3 (3-6k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | DSS Staircase Pressurisation Duty Fan has a faulty VSD. This was raised in CRL-OBS-29704 __ to confirm whether VSD is to be repaired or replaced. __ to raise a DRACAS.
| 02SL - Stations (LUL) | Cxxx-NCR-002871 | NCR | DSS Level 7 PCC no UKAS Pull Testing |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-12-24 | 2020-01-24 12:04 | 31 | 2019-11-14 18:25 | Architectural - Walls | 2500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | There has been no UKAS pull testing completed on the fixings back to concrete for the DSS Level 7 UKAS Pull Testing. The locations of the affected areas are as per the location plan attached.
| 02SL - Stations (LUL) | Cxxx-NCR-002872 | NCR | Installation of an unapproved material |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-02-10 10:44 | -141 | 2019-11-15 11:40 | Mechanical - Heating Ventilation & Air Conditioning | 1500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | __ have proceeded to install __ VICUCLAD without an approved Material Conformance Report.
| 02SL - Stations (LUL) | Cxxx-NCR-002873 | NCR | DSS level 7 TFL POD room Traction earth bar and associated cables |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-02-18 | 2019-12-07 14:19 | -73 | 2019-11-20 11:07 | Electrical - Earthing & Bonding | 2500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In DSS level 7 north the TFL POD room the earth bar is fed by traction earth cables coming from trackside, the subsequent earth required for this room then come off this earth bar. The room is earthed gapped from normal supply earths with power supplies feeding equipment in this room from station side distribution boards. Looking at the earth schematic the earth cables from the earth bar seems excessive in size compared to what else had been installed on other parts of DSS shaft so a talk was had with the designers as we stated that some of these would be difficult for us to install which was agreed and stated that we have to try and install the largest cable possible. We installed what we could and raised a PTR to the designers which was rejected as they wanted conformation from Crossrail CEG asking what was acceptable under the circumstances
| 02SL - Stations (LUL) | Cxxx-NCR-002875 | NCR | Incorrect and amended Trace Heating Test Sheet dated 01/05/2019 incorporated into Construction record pack ref Cxxx-__M-E-LRC-D061_WS105-50215 for DSS External Water Tap Trace Heating & Lagging |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-01-13 | 2019-12-11 11:46 | -33 | 2019-12-04 15:31 | Mechanical - Hot & Cold Water Supplies | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | The IRN, along with the Construction Records, for DSS External Water Tap Trace Heating and Lagging) was presented for page turn with CRL and on the afternoon of Weds 20th November it was identified that there were two copies of the same Trace Heating Test sheet in the Construction Record Pack, one of which had been altered by hand. eB ref numbers: IRN - Cxxx-__M-E-NOX-D061_WS105-50773, Construction Records - Cxxx-__M-E-LRC-D061_WS105-50215.
| 02SL - Stations (LUL) | Cxxx-NCR-002876 | NCR | Smoke Ventilation Fan and Associated Inverters - Failure To Comply With BS EN 12101-3:2015 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-03-18 16:10 | -104 | 2019-12-02 15:52 | Mechanical - Heating Ventilation & Air Conditioning | 2000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Smoke ventilation fan and associated inverters do not comply with BS EN 12101-3:2015 (smoke and heat control systems)
| 02SL - Stations (LUL) | Cxxx-NCR-002877 | NCR | GSM Solar Hot Water System Pipework Insulation |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-09-13 | 2020-08-13 15:54 | -31 | 2020-08-04 07:40 | Mechanical - Hot & Cold Water Supplies | 2950 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | Lack of MCR for insulation and additional works required
| 02SL - Stations (LUL) | Cxxx-NCR-002879 | NCR | Air Release fans DSS/3/ARF/01&02 Low Performance due to Hige Ductwork Resistance |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-02-28 15:58 | -123 | 2019-11-29 13:42 | Mechanical - Heating Ventilation & Air Conditioning | 4000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | During the Commissioning of the ARF fans in DSS, it was noted that the discharge pressure of the fan was high (1100Pa) and the pressure drop across the discharge grill on the roof was approx 600Pa. This is in contradiction of normal design codes and does not align with the Ductwork pressure loss calculation document Cxxx-__M-M-XCL-D061_WS107-50016. The Fan is unable to achieve 100% of it's design duty due to this issue.
| 02SL - Stations (LUL) | Cxxx-NCR-002880 | NCR | Trace heating supply CHS Level B Incorrect Fuse spur installed |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-01-11 | 2019-12-06 12:24 | -36 | 2019-12-02 17:19 | Electrical - Power Distribution | 2500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Not Defined | Completed |  | In CHS Level B there is a circuit to feed the trace heating, LPDB2A/1L3. This was shown on the drawing fitted external area of the chiller room, Although the trace heating has been fitted internally. (see attached sketch). The supply for the trace heating was installed internally as per FCD-003734 but on change a fuse spur was installed instead of an isolator as per design.
| 02SL - Stations (LUL) | Cxxx-NCR-002881 | NCR | DSS Domestic Electric Hot Water Heater DSS/7/EWH/02 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-02-18 11:35 | -133 | 2019-12-03 16:23 | Mechanical - Hot & Cold Water Supplies | 2000 |  | System Defect | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | During Commissioning and Testing of the Domestic Hot Water Heater, Model Ref Heatrae FLO15, in Room 7/764, it was discovered that the max. hot water temperature achievable was 55 degrees C which is below the minimum requirement set out in MEP Specification Cxxx-__M-M-RSP-D061_WS106-50002 Rev. 9.0 page 182 which states that "the water heater shall be set to output water at 60 Degrees C".
| 02SL - Stations (LUL) | Cxxx-NCR-002882 | NCR | Proceeded with installation without approved RAMS |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-03-09 14:40 | -113 | 2019-12-04 13:17 | Mechanical - Public Health Engineering | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Work proceeded without the SCN eb ref Cxxx-__M-M-CCN-D061_WS107-50008 being approved(code 3). The SCN relates to CHS and DSS trace heating works.
| 02SL - Stations (LUL) | Cxxx-NCR-002883 | NCR | Replacement of RL73 glass |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-10-08 08:44 | 100 | 2019-12-04 14:53 | Architectural - Glazing | 3000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the installation of the BAL 403 handrail on the R10S roof, an Allen Key was dropped hitting on panel of glass on rooflight 73. This caused the external leaf to shatter. The other 2 remain intact and the area is safe. This panel of glass needs to be replaced.
| 02SL - Stations (LUL) | Cxxx-NCR-002885 | NCR | Lift 6 ATS MCCB Overload Unit Incorrect |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-12-20 | 2019-12-06 11:57 | -14 | 2019-12-06 08:16 | Electrical - Power Distribution | 3000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | During the commissioning of Lift 6 ATS it was noted that the protection device fitted was not as per the __ Report. The type fitted on the outgoing circuit to LPDB30 (Cable W076B) is a "__ 2.2 M" and the __ states a "__ 5.2". Photos and extract from __ attached. The previous revisions of the __ have been checked and the specification for this unit has never changed therefore this is an NCR for incorrect installation.
| 02SL - Stations (LUL) | Cxxx-NCR-002886 | NCR | CHS Level 7 BMS Panel Relocation |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-01-15 | 2020-01-28 08:36 | 13 | 2019-12-06 11:52 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The BMS panel on CHS level 7 has been installed in a different location to what is shown on the mechanical drawings. The panel has been installed in the location shown on the __ Banner drawings which are not approved by CRL.
| 02SL - Stations (LUL) | Cxxx-NCR-002887 | NCR | LULO GSM – South Canopy __ Flashing |  | Contr | VIN | WHI - Whitechapel Station (Central) |  | 2020-11-27 | 2020-11-21 13:41 | -6 | 2019-12-09 09:18 | Architectural - Finishes | 4500 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The flashing between the GSM __ (HD) cladding and the South canopy is indicated on drawing Cxxx-__M-A-DWG-D061_WS106-53489 (Detail G). The detail shows the flashing being fixed behind the HD cladding. However, onsite the HD cladding has been installed down the side of the canopy and the flashing has simply been installed on top of the cladding and therefore does not direct water away from the cladding or GSM structure. See attached picture for clarity.
| 02SL - Stations (LUL) | Cxxx-NCR-002888 | NCR | AHU01 TH-CC Duct work installed without approved design |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-03-23 10:21 | -99 | 2019-12-11 07:57 | Mechanical - Heating Ventilation & Air Conditioning | 4000 |  | Design | Rework | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | Duct install commenced without an approved design and FCD.
| 02SL - Stations (LUL) | Cxxx-NCR-002889 | NCR | Ticket Hall Switchboard 'B' (LVSB/B) MCCB and Overload Unit Incorrect for outgoing cable W152 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2019-12-25 | 2019-12-12 10:41 | -13 | 2019-12-11 10:24 | Electrical - Power Distribution | 4000 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Personnel Error - Not Defined | Completed |  | During the commissioning of Switchboard 'B' (LVSB/B) in the Ticket Hall area, it was noted that the MCCB and protection device fitted for cable W152 was not as per the __ Report. The MCCB and overload micrologic type fitted on the outgoing circuit to Cable W152 is a 'NSX160N __ 2.2' whereas the __ report states a 'NSX250N __ 5.2'. Extract from __ report attached. The previous revisions of the __ report have been checked and the specification for this MCCB and overload micrologic unit was always a 'NSX250 __ 5.2' therefore, this is an NCR for incorrect installation.
| 02SL - Stations (LUL) | Cxxx-NCR-002891 | NCR | IP rating of panel is affected by fan and filter |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-06-11 09:47 | -19 | 2019-12-12 15:10 | Mechanical - Pumps | 8000 |  | Manufacturing Defect | Rework | 2 (6-60k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | The IP rating of the surface water sump pump panels have been decreased to IP 21 by the Fan and filter in the following locations DSS/8/S__/01 and 02 Surface Water Sump Pumps Control Panel & Associated Cabling and CHS/8/SPU/01 & 02 Surface Water Sump Pumps Control Panel & Associated Cabling. Four solutions have been suggested to resolve the issue: 1.Find a Fan and filter with the correct IP rating(IP54) for a straight swap. 2.Find a filter and fan that would require the panel to redrilled and altered. 3.A new door and new filter could be fitted.(lead time might affect visit 4.A cowl could be fitted over the fan and filter to restore the IP rating of the panel
| 02SL - Stations (LUL) | Cxxx-NCR-002892 | NCR | Door pressures for stair presuriation do not all meet 100N |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-02-14 | 2021-08-13 14:59 | 546 | 2019-12-12 18:37 | Systems - Ventilation and Pressure Relief | 5000 |  | Testing and Commissioning | Rework | 3 (3-6k) | Complete | Design Problem - Not Defined | Completed |  | See email attachment detailing the Status of Staircase Pressurisation as of 12/12/2019 about which __ believe that the systems are now in a rudimental state of balance and that there is nothing that cause the system to operate in a way that may impede the free exit of persons from Level 7 or accommodation areas. The proving of velocities through open doors to prevent smoke ingress into the stair has not been confirmed at this stage. Not all of the door forces recorded during the presurisation test acheived the 110N force requirement
| 02SL - Stations (LUL) | Cxxx-NCR-002893 | NCR | DSS Staircase pressurisation fans - required pressure not met on standby fan. |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-02-28 16:15 | -123 | 2019-12-12 17:33 | Mechanical - Mechanical Engineering General | 6000 |  | Testing and Commissioning | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | DSS Staircase pressurisation fans Level A - During commissioning it has been identified that we have met the required pressures generated by the duty fan but not buy the standby fan.
| 02SL - Stations (LUL) | Cxxx-NCR-002894 | NCR | Access doors on ductwork has not been fitted with tethers |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2021-07-09 15:34 | 374 | 2019-12-19 08:56 | Mechanical - Heating Ventilation & Air Conditioning | 6000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Access hatches on ductwork have been installed without tethers, which are a requirement of clause JY30.1414 found within both WI Crossrail M&W Specification CRL1-XRL-M-RSP-CR001-50064 & Mechanical Specification Cxxx-__M-M-RSP-D061_WS106-50002 Version 9.0
| 02SL - Stations (LUL) | Cxxx-NCR-002895 | NCR | HCDL lower concourse - re design of multi compartment trunking and additional fire alarm trunking |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-02-17 11:33 | -134 | 2020-01-07 18:06 | Electrical - Cable Management | 3000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Due to a change in design on CMS drawing regarding the compartment layout, we have had to install an extra 100x100mm trunking for the fire alarm cables. LB foster had pulled their PAVA cable in the correct compartment in the trunking as stated on Drawing Cxxx-__M-E-DDA-D061_WS106_2-31975 C02 17/01/2017. These cables have been signed off and IRN'd. However on 18/10/2017 P08 was issued with a change to the design of the compartments, now including a Fire compartment where the PAVA was on the C02 drawing and moving the PAVA in to the comms compartment (cables already installed in both compartments to C02). The 100x100mm Fire Alarm Trunking was accepted by __ by PTR-8114 & 8136 (attached) so we proceeded to install. An FCD was raised Cxxx-FCD-003607 however this NCR now supersedes the FCD. in addition to the install, __ did not adhere to the witness points on the ITP and __wired their fire cables without __ signing off the trunking via an IRF. on a __ inspection it was noticed that the install team had fabricated a set in the trunking on site due to the obscure angle.
| 02SL - Stations (LUL) | Cxxx-NCR-002896 | NCR | VRF Systems in CHS not installed as per drawings |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-02-17 | 2020-01-20 16:28 | -28 | 2020-01-08 15:16 | Mechanical - Heating Ventilation & Air Conditioning | 2000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | When commissioning the BMS interface with the VRF controllers it was noted that some of the FCU's are piped / wired differently from the drawings / schematics.
| 02SL - Stations (LUL) | Cxxx-NCR-002897 | NCR | VRF Systems in DSS not installed as per drawings |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-02-17 | 2020-01-20 16:33 | -28 | 2020-01-08 15:17 | Mechanical - Heating Ventilation & Air Conditioning | 2000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other management problem | Completed |  | When commissioning the BMS interface with the VRF controllers it was noted that some of the FCU's are piped / wired differently from the drawings / schematics.
| 02SL - Stations (LUL) | Cxxx-NCR-002898 | NCR | SB/01/AHU/01 Ductwork Incorrect |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-03-09 14:29 | -113 | 2020-01-09 07:49 | Mechanical - Heating Ventilation & Air Conditioning | 2000 |  | Design | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The ductwork connections for SB/01/AHU/01 are installed as per the drawings, however it would appear that the connections onto the unit are in conflict with the drawings. The F1 drawings do not reflect the configuration of the unit that has been purchased.
| 02SL - Stations (LUL) | Cxxx-NCR-002899 | NCR | LO - Platform 5 & 6 end barriers – Misalignment of anchors |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-09-07 07:24 | 69 | 2020-01-09 09:19 | Architectural - Balustrade | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The bosses of the fixing detail which connect the fixing anchor to the base plate of the balustrade were grouted prematurely before the system was fully ‘set’. This resulted in a misalignment of the end barriers which are outside the tolerances of the ITP.
| 02SL - Stations (LUL) | Cxxx-NCR-002900 | NCR | LU/LO – Front of House – Support steel exceeding its deflection limit. |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-04-30 10:00 | -61 | 2020-01-09 11:26 | Civil - Structural Engineering | 5500 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Upon installation of the main entrance folding gates it was discovered that the additional loading introduced 10mm deflection into the gate support beam. This exceeded the 4.2mm allowable within the CAT check Cxxx-__M-A-CER-D061_WS106-50297 Rev 1.0.
| 02SL - Stations (LUL) | Cxxx-NCR-002901 | NCR | Ticket Hall Switchboard 'A' (LVSB/A) MCCB and Overload Unit Incorrect for outgoing cable W062 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-01-24 | 2020-01-11 11:14 | -13 | 2020-01-10 07:35 | Electrical - Power Distribution | 2500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the commissioning of Switchboard 'A' (LVSB/A) in the Ticket Hall area, it was noted that the MCCB and protection device fitted for cable W062 was not as per the __ Report. The MCCB and overload micrologic type fitted on the outgoing circuit to Cable W062 is a 'NSX160N __ 2.2' whereas the __ report states a 'NSX250N __ 5.2'. Extract from __ report attached. The previous revisions of the __ report have been checked and the specification for this MCCB and overload micrologic unit was always a 'NSX250 __ 5.2' therefore, this is an NCR for incorrect installation.
| 02SL - Stations (LUL) | Cxxx-NCR-002902 | NCR | Switchboard 2 & 3 switch room E51 Outgoing Cables - Test Sheets did not match what was installed regarding Fuse rating |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-02-17 11:46 | -134 | 2020-01-11 11:49 | Electrical - Power Distribution | 1500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Switchboard 2 & 3 switch room E51 Outgoing Cables - Test Sheets did not match what was installed regarding Fuse rating. the Test results for C14, C17, N05, N07 & N10 were incorrect due to having the incorrect fuse installed. the test sheets were correct to the __, however did not match what was installed. C14 - Fuse now changed to match __ and Test sheet - was 100A now 160A N05 - Fuse now changed to match __ and Test sheet - was 63A now 100A N10 - Fuse now changed to match __ and Test sheet - was 125A now 63A C17 - Re calculated __, fuse size acceptable - 100A installed test sheet amended. N07 - Fuse changed – 160A installed
| 02SL - Stations (LUL) | Cxxx-NCR-002903 | NCR | inaccessible fire damper in SSOR |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-02-28 16:13 | -123 | 2020-01-13 08:49 | Mechanical - Heating Ventilation & Air Conditioning | 8000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Other | Completed |  | due to congested services in the ceiling the fire damper serving the room is obstructed by CMS making servicing and removal of the damper impossible without dismantling other services.
| 02SL - Stations (LUL) | Cxxx-NCR-002904 | NCR | Faulty light Installed at Stair 24. Light not present / Installed at time of IRN and now energised without CRL Acceptance. |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-10-02 02:35 | 94 | 2020-01-13 12:00 | Electrical - Lighting | 2500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | A light fitting has been installed which looks to be faulty. The light fitting was not present at the time of the IRN of the associated distribution board. __ have not invited CRL to witness or accept the lighting or CMS to the lights. The below observation was raised by CRL with NCR required, __ have failed to raise the NCR to cover the associated works.
| 02SL - Stations (LUL) | Cxxx-NCR-002905 | NCR | Solar Panel Controller |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2020-02-12 16:09 | -139 | 2020-01-15 10:31 | Electrical - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | __ have installed a solar control panel in the Roof Access Room of the GSM, Level 1. This piece of equipment was installed with no ITP, MCR's or approved design in place. This NCR has been raised to cover re-works for this equipment with the above procedures in place.
| 02SL - Stations (LUL) | Cxxx-NCR-002906 | NCR | LULO - HCDL Square Column Cladding Defects |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2021-07-01 21:26 | 366 | 2020-01-15 13:18 | Architectural - General | 54111 |  | Damaged | Rework | 2 (6-60k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | __ have installed the Proteus cladding to the HCDL square columns. However during inspections (IRF-3529 & 3543) defects have been identified in the installed panels. Please see attached 2no defect reports indentifying the defects found. Detailed in the report is __'s proposals for whether each defect is 'leave as is', 'repair' or 'replace'. Please note that Proteus Rimex Granex Black panels cannot be repaired and therefore options are only noted as either 'leave as is' or 'replace'. Whereas the manifestation strips can be repaired as it is a powder coated finish.
| 02SL - Stations (LUL) | Cxxx-NCR-002907 | NCR | LULO - ESS __ Concrete Cladding Out of Tollerence |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-30 | 2021-01-18 16:36 | 202 | 2020-01-22 16:08 | Architectural - General | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Due to alignment issues on the pre-cast concrete segmented panels, a tapering gap has become visible during the installation of the adjacent lift shaft cladding panels (see attached photo). The gap tapers from touching at the bottom, to a 25mm gap at the top. As per the approved __ drawing (Cxxx-__MA-DWG-D061_WS106-56524), the gap should remain 10mm throughout the interface between both.
| 02SL - Stations (LUL) | Cxxx-NCR-002909 | NCR | Incorrect use of HY200-A resin within brickwork |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-03-07 | 2020-02-19 16:30 | -17 | 2020-01-27 15:41 | Mechanical - Heating Ventilation & Air Conditioning | 3000 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | A section of spiral ductwork (from SB/03/AHU/01) has been installed on level 3 ticket hall and concourse with a vertical section supported by a wall mounted bracket. The bracket is fixed into the concrete brickwork using threaded bar and chemical resin. The chemical resin used, __ HIT HY-200A, is designed for use in cracked and un-cracked concrete only, it does not have a suitable ETA for fixing into concrete brickwork/masonry. Although the fixings have passed the 3.5kN pull testing specified in the ITP, it is not possible to guarantee their long term performance.
| 02SL - Stations (LUL) | Cxxx-NCR-002910 | NCR | No accepted MCR for Nordlock anti vibration washers |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2020-03-09 | 2020-02-21 16:42 | -17 | 2020-01-29 14:13 | Architectural - General | 501 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | During a surveillance carried out on the Stainless Steel Cladding installed in the Existing Ticket Hall and Upper Concourse, on request the Contractor was unable to provide an accepted MCR for Nordlock anti vibration washers that form part of the installation of Stainless steel Cladding.
| 02SL - Stations (LUL) | Cxxx-NCR-002911 | NCR | Pull test points/results not witnessed by CRL on Selux Boom (ELL). ITP procedures not followed and hold points not adheared to. |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-03-15 | 2020-02-17 11:27 | -27 | 2020-02-04 09:18 | Electrical - General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The supporting fixings for ELL Selux Boom Lighting were pull tested, the results recorded and captured by means of photographs, but were not witnessed by CRL. __ failed to follow the ITP procedures and hold points were not adheared to.
| 02SL - Stations (LUL) | Cxxx-NCR-002913 | NCR | CHS external lighting DALI PD -installation without Design or MCR approved product |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-04-30 | 2020-10-02 01:56 | 155 | 2020-01-31 15:24 | Electrical - Lighting | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | no Design or MCR approved for the external presence detector. therefore they have not been installed resulting in circuits being incomplete
| 02SL - Stations (LUL) | Cxxx-NCR-002914 | NCR | Public Facing Fire Hydrant Label Positions |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-04-24 | 2020-04-24 20:37 | 0 | 2020-02-03 16:10 | Information Management - Asset Information | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Label positioning of Fire Hydrants on the CRL Platforms do not conform to the labelling requirements for assets within the public areas set in the Public Facing Labelling Guidance. Label is currently installed on the back wall at the level of the valve, whereas the requirement is to be "Placed inside the cabinet on the lateral inner wall of the door’s leading edge, close to the bottom edge."
| 02SL - Stations (LUL) | Cxxx-NCR-002915 | NCR | Asset Labels for Wiring Cables and Infra Red Radiation Detectors |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-05-22 | 2021-06-15 18:51 | 389 | 2020-02-03 16:39 | Information Management - Asset Information | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A number of labels installed on site do not conform to the requirements set in the Asset Naming and Labelling Convention Document (ANLCD) - non-conformance observed for Infra Red Radiation Detectors (4 lines or text on the label as opposed to 3, where the name is on Label Text Lines 2 and 3 ) and Wiring Cables (5 or 6 lines of text on the label as opposed to 4, where the source OR/AND the destination is/are on two different Label Text Lines).
| 02SL - Stations (LUL) | Cxxx-NCR-002916 | NCR | Loop 14 installation proceeding without CEG Approved Design |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-04-23 | 2020-04-22 10:15 | -1 | 2020-02-09 11:39 | Fire - Detection | 1000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The approved design for 1-066 did not have void detection shown. Void detection was subsequently identified during an IRN as the ceiling void was greater than 800mm. This detection was subsequently confirmed as necessary by __ in PTR Cxxx-__-PTR-8696. __proceeded to install the solution on the basis of the PTR, prior to drawings being submitted and approved by CEG.
| 02SL - Stations (LUL) | Cxxx-NCR-002917 | NCR | Cable Duct Routes LULO - Cables installed in incorrect ducts |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2020-08-31 | 2021-04-05 06:33 | 217 | 2020-02-06 12:46 | Electrical - General | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | As per CRL-OBS-30303 raised on 27/01/2020 - During the past few possessions, it has been noted that various cabling has been installed in the incorrect duct(s) in LULO platforms/inverts. __ to raise an NCR and provide a report / summary of status and corrective action(s) where required.
| 02SL - Stations (LUL) | Cxxx-NCR-002918 | NCR | Ticket Hall and Concourse Dali Addresses not installed |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2020-03-17 | 2020-03-23 11:44 | 6 | 2020-02-06 12:51 | Electrical - General | 60000 |  | Design | Use As-Is | 2 (6-60k) | Complete | Design Problem - Other | Completed |  | The ACDC Integrex 'LED Strip Lights' in the Ticket Hall and Concourse have 3 DALI Addresses. __ have installed Lighting Control assets / cabling based on 1 address per light. __ to confirm requirement for additional LCMs, CMS calcs etc.
| 02SL - Stations (LUL) | Cxxx-NCR-002919 | NCR | Trace heating Spurs changed to rotary isolators at the GSM with no CRL design approval. |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2020-07-15 | 2020-07-14 09:25 | -1 | 2020-02-08 11:20 | Electrical - General | 5000 |  | Design | Use As-Is | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | CRL FAE observed __ swapping out fused connection units for Rotary isolators in the roof access room. A PTR / FCD has been raised indicating that an additional FCU be installed which has been agreed by BH. Since then __ have now installed 2 x rotary isolators to cover the trace heating and will also need to install RCBO's as the protective device. No FCD has been presented to CRL for acceptance and the circuits have been signed off and accepted under the GSM Small power IPAC
| 02SL - Stations (LUL) | Cxxx-NCR-002921 | NCR | CHS CER2 BMS Panel - Install (With Pull Tests) |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-03-23 | 2020-02-28 12:22 | -24 | 2020-02-12 14:59 | Electrical - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | IRF not carried out with CRL at time of IRN (Cxxx-__M-M-NOX-D061_WS105-50001) for CHS CER2 BMS Panel - Level 6.
| 02SL - Stations (LUL) | Cxxx-NCR-002922 | NCR | CHS/DSS/GSM Sump Pump - Non Compliant Cable installed - No MCR |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-03-27 | 2020-03-07 09:30 | -20 | 2020-02-16 14:00 | Electrical - LV Equipment | 5000 |  | Manufacturing Defect | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | On review of the installation of the sump pumps installed sitewide it was discovered that the incorrect type of cable was installed and not fit for purpose
| 02SL - Stations (LUL) | Cxxx-NCR-002923 | NCR | DSS level 6 air release duct modifications |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-03-24 | 2020-09-02 22:34 | 162 | 2020-02-13 11:45 | Mechanical - Mechanical Engineering General | 10000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Design Problem - Other | Completed |  | This NCR has been raised as requested by __ to capture the change requested in Cxxx-FCD-003937.
| 02SL - Stations (LUL) | Cxxx-NCR-002924 | NCR | FA Loop 13 cable Damage |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-04-22 | 2020-04-03 15:27 | -19 | 2020-02-18 13:39 | Fire - Detection | 1500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Replacement cable of Loop 13 between FAP.04 & DCP.64
| 02SL - Stations (LUL) | Cxxx-NCR-002925 | NCR | Lift 4 ATS Panel Overload Unit Incorrect for outgoing cable to LPDB28 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-03-16 | 2020-02-24 15:19 | -21 | 2020-02-24 09:58 | Electrical - LV Equipment | 2000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | During the commissioning of Lift 4 ATS panel in the Ticket Hall area, it was noted that the overload protection device fitted for outgoing supply to LPDB28 (cable W040B) was not as per the latest Main Ticket Hall & Concourse - __ Report (Cxxx-__M-E-RGN-D061_WS106-50035 revision 6.0). The overload micrologic type fitted on the outgoing circuit to LPDB28 is a '__ 2.2M' whereas the __ report states a '__ 5.2'. Extract from __ report attached. The previous revisions of the __ report have been checked and the specification for this overload micrologic unit was always a '__ 5.2' therefore, this is an NCR for incorrect installation. Please note that on the live test sheet cable W040B is referenced as W140B to align with Cxxx-__-PTR-7270 which states that ATS outgoing cables should be referenced using the primary supply cable id and in the case of lift 4 ATS the primary supply cable is W140; Cxxx-PWK-02781 has been raised for this.
| 02SL - Stations (LUL) | Cxxx-NCR-002926 | NCR | Faulty ATS Digital Controller within Lift 4 ATS Panel |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-03-16 | 2020-02-28 12:25 | -17 | 2020-02-24 13:21 | Electrical - LV Equipment | 3000 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | During the commissioning of Lift 4 ATS panel in the Ticket Hall area, it was noted that the ATS Digital Controller was not functioning properly as it was not switching over between primary and standby supply. There was also a fault indicated on the controller LED display that was not possible to clear (see attached photo). __ to confirm whether ATS digital controller is to be repaired or replaced. DRACAS incident CRL-DRA-000510 has been raised for this.
| 02SL - Stations (LUL) | Cxxx-NCR-002927 | NCR | Cxxx-CHS Making good on wall concrete at Level C1 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-07-30 | 2020-11-03 10:18 | 96 | 2020-02-24 15:10 | Civil - Civil Engineering General | 4500 |  | Workmanship | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After a postpour inspection is been found that the making good done at the top of the wall at Level C1 have several superficial crack all along the wall, the area of making good will need to be broken out and reaply the repair material in correct manner.
| 02SL - Stations (LUL) | Cxxx-NCR-002928 | NCR | GSM BMS Panel - Component Failure |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-07-15 | 2020-08-13 09:04 | 29 | 2020-02-25 08:52 | Communications and Control Systems | 10000 |  | Equipment Breakdown | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | At approx. 16:21 Cxxx construction site fire alarm was triggered due to Whitechapel LU station fire alarm being activated (and proximity of live station to site). Station fire alarm had been activated by aspirating smoke sensor detecting smoke in St. Mary's House (known as GSM building on project). Station was evacuated of passengers / staff and LFB attended. At approx. 17:45, cause of detector activation was found to be BMS panel in lower floor of St. Mary's House.
| 02SL - Stations (LUL) | Cxxx-NCR-002929 | NCR | Fan Coil Units in POMS & SCR – Number Change |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-04-06 | 2020-04-28 07:37 | 22 | 2020-02-26 15:16 | Mechanical - Heating Ventilation & Air Conditioning | 1000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | We have noticed there is a discrepancy between the Electrical small power/MCC Schematic and the mechanical VRV Refrigerant Schematic on the numbering of the FCU’s in the POMs & SCR rooms. Causing confusion we commissioning.
| 02SL - Stations (LUL) | Cxxx-NCR-002931 | NCR | mororised damper inaccessable in ceiling void to SOR room |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-04-07 | 2020-04-02 08:42 | -5 | 2020-02-27 08:43 | Mechanical - Mechanical Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | motorised damper now obstructed by other services impeding the maintenance or removal of this item
| 02SL - Stations (LUL) | Cxxx-NCR-002932 | NCR | DSS & CHS INDUSTRIAL HEATERS |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-05-16 | 2020-04-02 10:52 | -44 | 2020-03-17 13:54 | Electrical - LV Equipment | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | For DSS & CHS we have to install heaters in certain rooms as per the small power drawings, as per some other parts of the project Dimplex heaters were installed so these were installed in CHS which are not the type of heaters that we need to install in our rooms in the shaft, the heaters were installed by the electrical team.
| 02SL - Stations (LUL) | Cxxx-NCR-002933 | NCR | SOR Relief DADO Trunking. |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2020-03-31 | 2020-03-23 12:49 | -8 | 2020-02-28 08:54 | Electrical - Cable Management | 5000 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | After the installation of 2 x oversized FCU in the SOR room it completely restricted access to the F1 multi compartment CMS in the room. CRL pointed this out and suggested a relief trunking be installed for future cabling. With an accepted design from BH and CRL __K installed the wrong trunking. A second PTR was then raised to verify what was installed as acceptable which was by BH, unfortunately the CMS has been installed in a fashion where you cannot access. The CMS needs to be reworked again to allow access for future cabling to the SOR room.
| 02SL - Stations (LUL) | Cxxx-NCR-002934 | NCR | LU approval of Statutory Labels |  | Contr | VIN | WHI - Whitechapel Station (Central) |  | 2021-11-15 | 2021-09-02 12:52 | -74 | 2020-02-28 12:31 | Information Management - General | 10000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Management Problem - Other | Completed |  | Statutory labels installed on Switchboards, __ Sockets and Isolators not approved by LU.
| 02SL - Stations (LUL) | Cxxx-NCR-002935 | NCR | DSS service yard condenser re-locating due to locatation impeeding fire escape route |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-08-30 | 2020-11-19 00:09 | 81 | 2020-02-28 13:51 | Mechanical - Heating Ventilation & Air Conditioning | 20000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Design Problem - Other | Completed |  | The 2 no. condensers DSS/1/EC/5 and DSS/1/EC/06 impede the fire escape doors on grid line DSY/DS2 shown on drawing Cxxx-__M-M-DDA-D061_WS105_1-10271.
| 02SL - Stations (LUL) | Cxxx-NCR-002936 | NCR | Cxxx-DSS-__ ceiling tolerances exceeded |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-04-08 | 2020-04-04 13:48 | -4 | 2020-02-28 14:09 | Fire - Compartmentation | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The DSS durasteel ceilings asbuilt survey revealed the ceiling levels and hatch positions being outside the +/- 2mm Specification tolerances.
| 02SL - Stations (LUL) | Cxxx-NCR-002937 | NCR | Extra lights to install in DSS to meet LUX levels |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-04-11 | 2020-03-31 11:13 | -11 | 2020-03-02 14:02 | Electrical - Lighting | 10000 |  | Design | Use As-Is | 2 (6-60k) | Complete | Design Problem - Other | Completed |  | Designers __ have stated that certain areas of DSS need extra lighting as some areas are darker than others which are deemed not to meet LUX levels
| 02SL - Stations (LUL) | Cxxx-NCR-002939 | NCR | Equipment installed in a different room as opposed to design |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-04-11 | 2020-04-02 11:45 | -9 | 2020-03-02 11:07 | Mechanical - Public Health Engineering | 3000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Equipment installed in a different room as opposed to design. Foul sump pump and waste water pipework has been installed in adjacent cubicle in 8/927 (as the fire strategy plan Rev P02.1) to the original design
| 02SL - Stations (LUL) | Cxxx-NCR-002940 | NCR | Alterations to signed off device post IRN (fire beacon) |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2020-04-11 | 2020-04-22 12:34 | 11 | 2020-03-02 11:49 | Fire - Detection | 1000 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During SC1/2 cause and effect testing device 039 was disconnected post IRN acceptance
| 02SL - Stations (LUL) | Cxxx-NCR-002941 | NCR | LV SwitchBoards - Non Conformance to CRL Cyber Security Requirments |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-07-15 | 2021-05-07 15:28 | 296 | 2020-03-02 15:30 | Electrical - Switchgear | 5000 |  | Testing and Commissioning | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | During the commissioning and integration of the LV switchboards with the BMS network it became apparent that the IP network devices and Layer 2 switches within the LV Switchboards do not comply with the CRL requirements outlined in the document CRL1-XRL-O7-__-CRG03-50001.
| 02SL - Stations (LUL) | Cxxx-NCR-002942 | NCR | Water Ingress To PAVA Assets |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-04-12 | 2020-10-28 22:24 | 199 | 2020-03-03 10:10 | Communications and Control Systems - Public Address Systems | 3000 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | It has been identified that a significant number of PAVA assets have been discovered to have been subject to water ingress. This water ingress has resulted in already commissioned PAVA zones to produce faults. The subsequent water ingress has rendered speakers damaged/inoperable.
| 02SL - Stations (LUL) | Cxxx-NCR-002943 | NCR | DSS/A/EF/02 Fan Faulty |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-07-15 | 2020-07-23 09:04 | 8 | 2020-03-03 10:16 | Mechanical - Heating Ventilation & Air Conditioning | 2500 |  | Equipment Breakdown | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | Fan in PFR2 Plant room, Level A DSS is reporting a fault at the fan controller.
| 02SL - Stations (LUL) | Cxxx-NCR-002944 | NCR | ticket hall and concourse plantroom 1/776 condenser moves |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-07-29 | 2021-09-22 10:00 | 420 | 2020-03-03 15:10 | Mechanical - Heating Ventilation & Air Conditioning | 10000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | condensers SB/01/OU/01 and SB/01/OU/02 cannot be maintained as no safe access is available. These condensers could be re-located directly above on the roof,.
| 02SL - Stations (LUL) | Cxxx-NCR-002945 | NCR | Extract Fan Differential Pressure Switch Range Too High |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-07-15 | 2020-08-07 16:02 | 23 | 2020-03-06 14:10 | Mechanical - Heating Ventilation & Air Conditioning | 2000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | During commissioning it was picked up that the differential pressure switch for extract fan EF-01 does not make. This switch has a range of 50-500Pa and would there need to be replaced with a switch with a range of 30-300Pa.
| 02SL - Stations (LUL) | Cxxx-NCR-002946 | NCR | Damaged PAVA Asset |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-11-30 | 2021-07-21 07:10 | -132 | 2020-03-11 11:34 | Communications and Control Systems - Public Address Systems | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Within CHS DR2 Level A (SID 1m/882) Horn Speaker Z15/A23, was noted to have been damaged beyond repair. CRL-OBS-30907 refers. The asset had already been IRN'd. A new speaker is to be issued by Cxxx. Cxxx are to replace and re-test the speaker.
| 02SL - Stations (LUL) | Cxxx-NCR-002947 | NCR | CHS PRSF Intake actuators incorrect type |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-07-15 | 2020-09-25 16:30 | 72 | 2020-03-11 09:31 | Systems - Ventilation and Pressure Relief | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Actuators fitted to the PRSF system intake in CHS stair 41 are of spring return / fail closed type. This type of actuator is not suitable for this application and does not align with the design of the PLC system which requires an actuator that can be driven open and closed. The damper type originally fitted was type __ SF24A. These were replaced with __ SM24A however whilst these were the correct operation the drive time was found to be too slow for the application.
| 02SL - Stations (LUL) | Cxxx-NCR-002950 | NCR | FDDB1 ATS Faulty DSS & CHS |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-07-15 | 2021-03-12 10:42 | 240 | 2020-04-06 10:40 | Electrical - Switchgear | 3000 |  | Equipment Breakdown | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | ATS was found to be faulty. On inspection from __RT who supply the unit it was found to be working correctly.
| 02SL - Stations (LUL) | Cxxx-NCR-002951 | NCR | FDDB1 ATS Faulty CHS |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-07-15 | 2020-05-18 14:37 | -58 | 2020-04-06 11:18 | Electrical - Switchgear | 2500 |  | Equipment Breakdown | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | ATS showing intermittent fault. F9 fault (motor fault). Video of fault sent to __ for analysis.
| 02SL - Stations (LUL) | Cxxx-NCR-002952 | NCR | Cxxx Whitechapel Projectwide - Supply Chain __ Inconsistencies with the use of steel grades in fabrication and records |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-09-21 | 2020-11-26 09:57 | 66 | 2020-07-10 10:20 | Structural Engineering - Steel Member | 2500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Insufficient quantity of material to do the job | Completed |  | __ supplier __ have completed detailed designed and installed secondary steelwork at various locations across the project, including louvre frames in DSS. __ have identified some discrepancies between the recently submitted fabrication records and the materials mill certificates supplied. Some steel appeared to have been replaced with both higher and lower grades to those stated on the fabrication drawings.
| 02SL - Stations (LUL) | Cxxx-NCR-002953 | NCR | motorised damper un-accessable in POMS room lobby T>H>C> 1/903 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-04-23 | 2020-11-19 00:14 | 210 | 2020-03-14 08:22 | Mechanical - Heating Ventilation & Air Conditioning | 4000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | other services hinder the maintenance access and testing of motorised damper SB/01/MFD/21
| 02SL - Stations (LUL) | Cxxx-NCR-002954 | NCR | Cxxx - DSS Kickflat installation L5 FV walkway |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-07-29 | 2020-06-27 11:58 | -32 | 2020-03-19 13:12 | Architectural - Flooring | 2890 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | One of the walkways has been raised as requiring a kickflat installed at the end of the walkway, this is because there is a clash between the metal mesh floor and MEP, so the walkway could not go all the way up the wall as per design.
| 02SL - Stations (LUL) | Cxxx-NCR-002955 | NCR | Flakt Woods fan alignment and flexible coupling unsupported lengths |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-08-30 | 2021-03-05 16:47 | 187 | 2020-03-19 17:01 | Mechanical - Heating Ventilation & Air Conditioning | 8000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Requirements of DW144 (Fig 200) require unsupported flexible couplings to be a minimum of 50mm in length and a maximum of 250mm in length. It has been observed on site that the distance between fan spigot and ductwork is less than 50mm in some cases. This represent a non-conformance with WI standard DW144. Concern has also been raised regarding misalignment between fan spigot and connecting ductpiece.
| 02SL - Stations (LUL) | Cxxx-NCR-002957 | NCR | Disconnection of a Cxxx commissioned asset WHI-1-01-005-MD11 without approval |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-05-01 | 2020-10-20 11:59 | 172 | 2020-03-22 15:35 | Electrical - General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | At CHS Door contact WHI-1-01-005-MD11 situated on level 1 was not disconnected in the correct manor or abiding by the project controls and the cables appear to of been cut at the door and the door/frame replaced. No instruction was in place with the comms contractor to disconnect nor an approved isolation from the systemwide contractor to disconnect the door contacts. Cables have been disconnected/damaged which is monitored back to the RCC which caused dirstruption to a commissioned asset.
| 02SL - Stations (LUL) | Cxxx-NCR-002958 | NCR | Fire Alarm FCU Shutdown Interface |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-07-15 | 2021-03-04 11:11 | 232 | 2020-03-26 11:23 | Fire - Fire Systems & General | 10000 |  | Incomplete Works | Use As-Is | 2 (6-60k) | Complete | Design Problem - Other | Completed |  | At present there is no direct interface between the FCU's located outside of their associated rooms and the Fire alarms to shut them down when required. The fire alarm design accounts for an interface for each instance of this however the mechanical design did not include this detail.
| 02SL - Stations (LUL) | Cxxx-NCR-002959 | NCR | UPS 5 THC - Additional Batteries added to UPS 5 due to extra load. Battery Rack CMS & Bracketry Install, Additional Light Fitting and PIR Repositioning. Capturing Changes done on Site by __ |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-05-05 | 2020-05-14 14:35 | 9 | 2020-03-26 15:52 | Electrical - General | 20000 |  | Design | Use As-Is | 2 (6-60k) | Complete | Design Problem - Other | Completed |  | Due to a Load increase from UPS 5 MSB, __ had been instructed to install additional Batteries, MCCBs, Cabling and Recommision/Testing of UPS 5. This NCR will capture the additional assurance for Installation of new primary CMS and bracketry to support the battery __'s and associated framework over and adjacent to the additional batteries and rack in UPS room 5. __ have also reduced the existing Battery MCCB to incorporate the load change. As a result of the new installation an existing luminaire and PIR control will be repositioned accordingly and an additional luminaire will be introduced to suit the new room layout. addition to this it was noticed that on install of the new cables, there was a damaged terminal bolt that needed to be replaced. This NCR will supersede Cxxx-FCD-003936 because this did not give all the infomation needed for the work carried out.
| 02SL - Stations (LUL) | Cxxx-NCR-002960 | NCR | Access and Maintenance to HDCL Trunking |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-07-15 | 2021-03-16 09:23 | 244 | 2020-03-27 09:53 | Electrical - General | 5000 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | In the HDCL Y conflict area the trunking that has been installed was noticed on IRF inspection it was not accessible to remove the trunking lid due to the clearance between Steelwork & Lid and other facilities and CMS in close proximity preventing access from above
| 02SL - Stations (LUL) | Cxxx-NCR-002961 | NCR | GSM Building minor defects |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-24 | 2021-03-16 14:57 | 265 | 2020-05-15 13:56 | Architectural - General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The GSM building has minor defects to finished works of the building envelope such as: - scratches - installation defects such as mastic not being perfectly straight - gaps to flashings not within tolerance as shown in construction drawings These minor defects cannot be seen by the public. Attached is a report on these defects which details the type and location and proposed solutions. Please note that for photo clarity this report should be read in its digital format.
| 02SL - Stations (LUL) | Cxxx-NCR-002962 | NCR | non compliant rainwater bracketry to DSS |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-08-28 | 2020-09-15 09:32 | 18 | 2020-07-04 09:07 | Mechanical - Public Health Engineering | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | there are discrepancies regarding the DSS rainwater pipework and the designers report. 1. The revised solution on site differs from the proposal shown in Figure 11 sketch. On site no square washer + M16 stud + lock nut arrangement has been used to support beneath the pipe – instead the pipework is suspended from unistrut + drop rods in tension. Please confirm has this installed arrangement been accepted by the designer? 2. The P2665T Cantilever seen in the sketch is shown as a bolted connection drilled through the existing Cxxx beam. Please confirm is this the design intent to drill through the existing steelwork? The site team have left in place the clamp style cantilever fixings to the Cxxx beam as seen in the photo on page 51, in order to avoid drilling into the existing Cxxx steelwork. Please confirm if this is accepted by the designer?
| 02SL - Stations (LUL) | Cxxx-NCR-002963 | NCR | LULO - Stair 23 Portal Frame Special Finish |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-11-08 | 2021-11-09 10:54 | 1 | 2020-04-16 13:41 | Architectural - General | 500 |  | Workmanship | Reject | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | At the bottom of Stair 23 and in the Lift 6 lobby on level 4 there is an exposed concrete structure. In the architectural spec there is a clause (JE20.1203) for exposed architectural finishes. BH have confirmed that the finish on the concrete does not meet the requirements of the specification as it presents a surface not uniform in colour and appearance, and is not free from discolouration.
| 02SL - Stations (LUL) | Cxxx-NCR-002965 | NCR | Cxxx - DSS - BRASS Panel oxidation |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-05-29 | 2021-05-28 15:32 | -1 | 2021-05-28 13:37 | Architectural - Finishes | 0 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | The brass panels facing the DSS service yard & R-12 walk are showing signs of oxidation & patina. See picture attached.
| 02SL - Stations (LUL) | Cxxx-NCR-002967 | NCR | LULO - E55/6 SRV Results |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-02 | 2020-04-24 10:36 | -39 | 2020-04-23 07:15 | Architectural - Flooring | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The SRV tests for E55/6 switch rooms in the East Stair Shaft do not meet the required value as per the architectural specification. See attached results.
| 02SL - Stations (LUL) | Cxxx-NCR-002968 | NCR | LULO - Platform 1 End barrier alterations |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-08-27 | 2020-12-03 15:00 | 98 | 2020-04-29 09:46 | Architectural - General | 3500 |  | Design | Use As-Is | 3 (3-6k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The as-built position of the platform edge on drawing Cxxx-__M-A-DWG-D061_WS106-56507 CO1 (Platform 1 end barrier at GL DH edge on __) is incorrect. As such the end barrier cannot be installed on site in accordance with LU standards and alterations are required.
| 02SL - Stations (LUL) | Cxxx-NCR-002969 | NCR | CHS Platform Smoke Extract Fans - Excessive Noise |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-06-21 | 2020-09-25 16:41 | 96 | 2020-05-12 12:56 | Mechanical - Heating Ventilation & Air Conditioning | 4000 |  | Testing and Commissioning | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | It was noted when running the Platform Smoke Extract fans in CHS that the noise emitted from the Fans external to the shafts was excessive. The fans were commissioned to their final speed and duty however they regularly caused noise alerts from our acoustic specialists.
| 02SL - Stations (LUL) | Cxxx-NCR-002970 | NCR | LULO - East Stair Shaft Roof __ damage (CRL-OBS-27666) |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-11-11 | 2021-10-06 10:03 | 329 | 2020-07-31 07:17 | Architectural - General | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The __ roof between the lift shaft and the walkway on the ESS roof has become worn and dropped due to foot traffic.
| 02SL - Stations (LUL) | Cxxx-NCR-002971 | NCR | Cxxx - DSS - West Elevation - Damaged Cavity barrier |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-09-16 | 2021-04-07 09:05 | 203 | 2020-05-18 11:18 | Fire - Compartmentation | 2500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | DSS West elevation (South End) fire cavity has been damaged due to water ingress. The Contractor is to confirm water ingress has stopped and replace any damaged firestopping. This is as per CRL-OBS-27687.
| 02SL - Stations (LUL) | Cxxx-NCR-002972 | NCR | lack of metal cladding to insulated services |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-07-31 | 2021-02-25 16:38 | 209 | 2020-05-20 11:20 | Mechanical - Heating Ventilation & Air Conditioning | 20000 |  | Incomplete Works | Rework | 2 (6-60k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | WI JY50 requires thermal insulation to be ali-clad in plantrooms upto a height of 2.5m above finished floor level in plant rooms. There are numerous examples at WHI where this has not happened for both pipework and ductwork services. This NCR is to capture all occurrences.
| 02SL - Stations (LUL) | Cxxx-NCR-002973 | NCR | Ticket hall and concourse level 1 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-07-27 | 2020-08-26 08:45 | 30 | 2020-06-17 08:36 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Fire damper at CHS LV1 in the corridor is obstructed by other services making maintenance and replacement of the damper impossible without dismantling other services
| 02SL - Stations (LUL) | Cxxx-NCR-002974 | NCR | Naming Conventions for Power Supplies |  | Contr | VIN | WHI - Whitechapel Station (Central) |  | 2021-09-17 | 2020-12-07 14:46 | -284 | 2020-05-20 18:42 | Information Management - General | 15000 |  | Incorrect Installation | Use As-Is | 2 (6-60k) | Complete | Verification Problems - Other | Completed |  | As the Contractor raised in Cxxx-EWN-03066, although not yet instructed to Cxxx, CRL1-CEC-00430 refers to the Naming Conventions for Power Supplies (A and B). The CEC provides clarification on the labelling arrangements and documentation. It is stated that “If the Contractor has adopted "1 or 2" then this is to be amended to "A or B" and this refers to “Labelling Of Electrical Cables, Electrical Equipment and Electrical Rooms.” If the CEC were to be instructed to Cxxx, the non-conformance of the asset labelling with the CEC relates to the naming of the Switch Rooms (LV Supplies are already A and B). However, the design Drawings are also referring to these spaces as to SR LV I & II (as shown in Cxxx-__M-E-DDA-D061_WS105_5-30911 X08 - DSS SRLV I & II, Cxxx-__M-E-DDA-D061_WS107_1-30901 X11 - SRLV 4 & 5 and Cxxx-__M-E-DDA-D061_WS107_4-30900 X08 CHS SRLV I & II).
| 02SL - Stations (LUL) | Cxxx-NCR-002975 | NCR | Luminaires Showing Signs of Rusting |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2020-07-06 | 2020-11-11 09:12 | 128 | 2020-05-27 13:44 | Electrical - Lighting | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | During VAP on DALI lighting system for Cambridge Heath Shaft at Whitechapel station it was noticed that the external light fitting in the staircase leading to switch room (B/610) was showing signs of rusting, similar condition was noticed on other light fittings located in the same area. For further details refer to attached photographs. This was raised under Observation CRL-OBS-30166. It was agreed that an NCR was to be raised by the Contractor to close the Observation. The Contractor has failed to do this.
| 02SL - Stations (LUL) | Cxxx-NCR-002976 | NCR | No evidence of formal acceptance for Label samples could be provided |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2020-07-06 | 2020-10-15 13:27 | 101 | 2020-05-27 13:53 | Architectural - General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | On request the Contractor supplied evidence of Samples for all types of labels to be installed in line with Cxxx-__M-E-RSP-D061-50008 (Rev 7) JY82.2101 Post Contract Samples; “A sample shall be provided of each label type for acceptance by the Project Manager”. At the time of the surveillance no formal acceptance could be provided. This was raised under Observation CRL-OBS-28177. To this date the Contractor has failed to provide the evidence to close this Observation. The Observation has now been escalated to an NCR.
| 02SL - Stations (LUL) | Cxxx-NCR-002977 | NCR | Additional Lighting Required for Sump Pump Panels (located beyond PES) |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2020-07-11 | 2020-06-16 10:40 | -25 | 2020-06-01 09:05 | Electrical - Lighting | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | During VAP on BMS system on 17/03/2020, CRL observed poor illumination in the east and west bound cupboards of the platform, which contain sump-pump control panels (UPSPs) The required lighting levels (1-066 Issue A2) - rooms greater than 2m in depth from the door to have a min of two lights derived from different DB locations and one being an emergency fitting.
| 02SL - Stations (LUL) | Cxxx-NCR-002978 | NCR | EMG Supply Cable installed in the Wrong Trunking compartment. |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2020-08-26 | 2020-08-25 10:11 | -1 | 2020-07-17 17:03 | Electrical - General | 2500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | Cables were pulled in to the wrong compartment in LCR 4
| 02SL - Stations (LUL) | Cxxx-NCR-002979 | NCR | Solar system calorifier in GSM roof access room defective |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-08-31 | 2020-08-24 10:35 | -7 | 2020-07-03 08:59 | Mechanical - Public Health Engineering | 1000 |  | Equipment Breakdown | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | GSM calorifier installed in the roof access room in the GSM is leaking.
| 02SL - Stations (LUL) | Cxxx-NCR-002980 | NCR | HCDL fire main - 9 Feb 2020 site inspection by CRL __ |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-08-16 | 2021-07-23 11:21 | 341 | 2020-07-07 10:18 | Fire - Suppression | 10000 |  | Incomplete Works | Use As-Is | 2 (6-60k) | Complete | Management Problem - Inadequate supervision | Completed |  | Following the site inspection by CRL 9/02/20 a number of concerns were raised as listed below in the NCR Route Cause Description
| 02SL - Stations (LUL) | Cxxx-NCR-002981 | NCR | DSS/CHS Submarine Doors non-compliance |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-10-26 | 2021-03-12 08:26 | 137 | 2020-07-20 15:40 | Architectural - Doors | 3000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Door installation is not in compliant with design requirements Non-compliance identifed include the following items 1 -Design submissions do not include all fixing details 2 -Fixings - do not meet corrosion requirements as per Arch Spec 3 -Fixings to concrete frame using chemical fixings not mechanical 4 Different size fixings used, small more frequent fixings to RHS of door 5 Drilling through rebar without prior acceptance for fixings 6 -Quality Records provided for installation do not capture the modifications above 7 Fire certification records not supplied - subcontractor __ to provide Fire certification records, including fire competence training records of the installers (added 27/07/20) 8 Loading beam has not been fire protected in line with the IFC Engineering Assessment Report, clause 4.7 (added 31/07/20)
| 02SL - Stations (LUL) | Cxxx-NCR-002982 | NCR | CHS/1/EF/01 Replacement Fan |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-08-23 | 2020-12-07 11:32 | 106 | 2020-07-14 15:52 | Mechanical - Heating Ventilation & Air Conditioning | 2000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Original fan installed were axial type __ these were replaced post IRN with the __ fan as the __ were not compatable
| 02SL - Stations (LUL) | Cxxx-NCR-002983 | NCR | Damaged C690 & Cxxx Cables - GLAP D061-TEL-00249 - Upper Concourse |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-08-25 | 2020-09-23 18:14 | 29 | 2020-07-16 07:30 | Communications and Control Systems - General | 5000 |  | Damaged | Use As-Is | 3 (3-6k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | C690 & Cxxx cables associated with the GLAP D061-TEL-00249 have been reported as damaged. Evidence of the damage has been captured in the attachment and the cable details are listed below. C690 cable damage: - See attached pics showing some of the damage on 2x C690 cables. - No other information known as this is a CRL contractor (__). Cxxx cable damage, this still belongs to __/__ (has not been IRN’d to Cxxx yet): - See attached pics showing some of the damage on 1x Cxxx Tel cable. - Attached drawing Cxxx-SMN-R3-DDA-D061_WS106_1-60002 X01 TEL THC – signed – Shows location of GLAP and Cxxx cable reference (WHI-00-LUA-3018). - The Comlot for this cable is (TEL-WHI-TEL00-08000). - The asset ID is (D061-TEL-00249).
| 02SL - Stations (LUL) | Cxxx-NCR-002984 | NCR | Cxxx - CRL Platform - Endwall: __ boxing detail |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-08-25 | 2020-09-30 14:08 | 36 | 2020-07-16 15:57 | Architectural - Walls | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | During Dynamic testing (10/07/2020) __ was notified by the Dynamic testing team that the __ boards fixed to CRL Eastbound Eastend`s end wall was loose and not fixed adequately. The __ detailed was specified in the F1 & F2 design to provide protection from touch potential and not fire rating. Upon inspection by __ (during construction), it was confirmed that supluax was not installed as per the approved detail shown in Cxxx-__M-A-DWG-D061_WS106-55265 C01. Site installation as-built sketche is attached. After further investigation (by speaking to the supervisor responsible for the works), it was confirmed that __ detail was extended to close the gap between the Platform screen doors & End wall (as a temporary measure) , as the flashing detail was not developed at the time. Extended __ detailed was agreed on-site only and was not formally confirmed with __ or CRL.
| 02SL - Stations (LUL) | Cxxx-NCR-002985 | NCR | LO - LO Platforms - DC8 & DC9 Rooms - Concrete Plinth Cube Test Strength |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-09-21 | 2020-08-16 10:31 | -36 | 2020-08-12 11:43 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Counterfeit Items | Completed |  | The cube results from the concrete plinths in DC8 & DC9 came back as reaching 38.9N/mm2 after 56 days. This is understrength by specification.
| 02SL - Stations (LUL) | Cxxx-NCR-002986 | NCR | S&T - CHS - External Handrails - Stairs 42 & 43 - Non-compliant design |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-09-21 | 2020-10-13 07:37 | 22 | 2020-07-23 11:46 | Architectural - Balustrade | 1500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | While updating the CAT II design and check certificate (Cxxx-__M-C-CER-D061-53082 Rev 2.0 - __ Steel) to include the mesh panels and kick flats along stairs 42 and 43, it was found out that the design used a section size of angle which was not picked up at the fabrication drawing stage and therefore a different size has been used in the fabrication of the frames.
| 02SL - Stations (LUL) | Cxxx-NCR-002987 | NCR | Cxxx - CHS and DSS Surespan Delivery Shaft Floor Access Hatch Yellow Safety Grids |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-11-30 | 2021-11-10 10:25 | 345 | 2020-07-28 16:34 | Architectural - General | 6000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The following queries were raised in regards to the safe functionality and usage of the plant delivery shaft floor access hatches and the yellow safety grids within the hatches during the permanent usage: - (a) Opening of the hatches and then the yellow safety grids once temporary measures (e.g. scaffold handrail/edge protection) is removed. - (b) Weight/size of specific hatch yellow safety grids in the CHS shaft (hatches CHS-AH-02 on level 1 to CHS-AH-06 on level 6). - (c) Yellow safety grids having 0 (zero) load capacity in the up right position. - (d) Height of some of the yellow safety gates in the upright position being as little as 400mm from FFL. - (e) Hatches CHS-AH-03 on level 3 to CHS-AH-06 on level 6 in CHS having a single door from the escape staircase leading onto the hatch - when the hatch is in an open position this poses a fall risk through the hatch if the door is opened (doors in question are: CHS/D3/004; CHS/D4/004; CHS/D5/004; CHS/D6/004).
| 02SL - Stations (LUL) | Cxxx-NCR-002988 | NCR | Cxxx - DSS & CHS - Floor hatches FIRES report |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-09-12 | 2021-04-23 20:09 | 223 | 2020-08-03 16:53 | Architectural - Flooring | 1500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Counterfeit Items | Completed |  | Some of the surespan floor hatches installed in DSS & CHS are not covered by the FIRES report. As some the floor hatches does not satisfy the FIRES report requirement set in Section 2.3.
| 02SL - Stations (LUL) | Cxxx-NCR-002989 | NCR | DSS LPWM |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-09-11 | 2020-08-20 21:16 | -22 | 2020-08-02 15:21 | Fire - Suppression | 1000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | 68 Degree centigrade Nozzles installed on the LPWM system are not tested above 5 Metre height coverage.
| 02SL - Stations (LUL) | Cxxx-NCR-002990 | NCR | DSS LPWM Drawings |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-09-11 | 2020-10-13 12:20 | 32 | 2020-08-02 15:31 | Fire - Suppression | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | LPWM Pipework and plantroom installation not as per revision of drawings on eB
| 02SL - Stations (LUL) | Cxxx-NCR-002991 | NCR | GSM non-self cleaning sump pump |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-10-23 | 2020-12-02 11:30 | 40 | 2020-08-05 06:15 | Mechanical - Pumps | 10000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | The the GSM pumps duty point should be 1.3l/s @ 51KPa (5.1m). However, the head of the installation between the bottom of the sump and the point where the pipe discharges is 7.08m. This 2m additional head has caused the pumps to pump at lower flow rate (0.9l/s) and therefore the velocity is below the minimum required value of 0.7m/s.
| 02SL - Stations (LUL) | Cxxx-NCR-002992 | NCR | LULO - Scomac Kitchen Sink MCR |  | Contr | VIN | WHI - Whitechapel Station (Central) |  | 2021-02-02 | 2021-05-03 16:03 | 90 | 2020-08-06 17:03 | Architectural - Sanitary Fittings | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Kitchen units (inclusive of counter tops, sinks, wall mounted cupboards, cooker hood) have been produced by Scomac and installed in the mess rooms of the GSM and Accommodation Blocks. The stainless steel units installed so not have MCR approval.
| 02SL - Stations (LUL) | Cxxx-NCR-002993 | NCR | Electrical supply to Media Converters |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-09-21 | 2020-10-12 20:16 | 21 | 2020-08-12 12:43 | Electrical - General | 1500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | There are 2 fibre cables installed for the BMS which monitor the status of the CRLP switchboards. The media converters that these fibres terminate into are fed from distribution board CRLP/A/WB1 which is in turn fed from CRLP A. When the MCCB for this distribution board trips, it takes out the very comms that is supposed to be monitoring the MCCB.
| 02SL - Stations (LUL) | Cxxx-NCR-002994 | NCR | LO - FOH collapsible gate - CAT check does not capture jamb post fixing detail accurately |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-09-24 | 2021-03-03 21:02 | 160 | 2020-08-15 18:28 | Architectural - General | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | The fixing detail for the collapsible gate jamb post captured in CAT check Cxxx-__M-A-CER-D061_WS106-50316 and calculations Cxxx-__M-A-XCL-D061_WS106-50154 is not accurate as alternative mechanical anchors were used to fix the central jamb post.
| 02SL - Stations (LUL) | Cxxx-NCR-002995 | NCR | LO - FOH cladding not installed as per F2 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-09-24 | 2020-08-19 10:27 | -36 | 2020-08-15 17:53 | Architectural - Finishes | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The cladding and glazing installed above the solicitors office has not been installed as per the approved F2 design
| 02SL - Stations (LUL) | Cxxx-NCR-002996 | NCR | CHS VRF System |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-09-22 | 2020-12-02 11:40 | 71 | 2020-08-13 21:37 | Mechanical - Heating Ventilation & Air Conditioning | 10000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | It has been noted during the commissioning of the VRF system and the integration with other systems that the design of the system is not in allignment with the LV System. There are 4 systems comprising of two duty and two standby. These systems need to have redundancy and for this to be the case in the event of a power failure all components within each system need to be fed from the same supply, either "A" or "B". This means that in the event of either a loss of the "A" or "B" supply there is still a complete VRF system that can contiue to run. At present this is not the case.
| 02SL - Stations (LUL) | Cxxx-NCR-002997 | NCR | Door TP/D7/003 and CP1 switchroom compartmentation |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-03-31 | 2021-04-11 10:32 | 11 | 2020-08-14 12:46 | Fire - Compartmentation | 1500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Interfacing detail between door TP/D7/003 and structural opening to be confirmed to complete the room compartmentation. F1 design to be reviewed by BH.
| 02SL - Stations (LUL) | Cxxx-NCR-002998 | NCR | UPS Battery Non-Compliant Material and Battery Rooms (more than 200m3) |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-11-27 | 2021-03-11 11:12 | 104 | 2020-08-19 09:00 | Electrical - General | 10000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | It has been identified that at four stations, there are six UPS battery rooms which exceed 200m3 in volume and therefore fall outside of the Crossrail concessions and are non-compliant against LU 1-085. The rooms are: • Paddington (Battery Rooms I and II) • Woolwich (East Box Battery Room II - Room 783) • Whitechapel (Durward Street Shaft Room 4/901) • Bond Street (ETH 4/663 and WTH 5/665) Testing of UPS battery material was undertaken (through the Cxxx contract) to provide supporting evidence for potential further concessions for these specific larger rooms. The testing was undertaken in June 2020 and the report issued by __ in July 2020 (CRL1-BUR-E1-RGN-CR001-50001). The test report has now been reviewed by Crossrail CEG and the level of failure against the test standards related to combustibility and smoke emissions mean that the CEG heads of discipline cannot support further concessions unless additional mitigation measures are implemented. As a result of this non-compliance, the ATU cannot currently be accepted for these stations and urgent action is required to resolve and prevent delay to the fire assurance of the stations.
| 02SL - Stations (LUL) | Cxxx-NCR-002999 | NCR | blockage in refrigerent pipework between plantroom 1/766 and SSO room 1/283 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-09-28 | 2021-01-28 10:41 | 122 | 2020-08-19 13:13 | Mechanical - Heating Ventilation & Air Conditioning | 4000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Personnel Error - Inattention to detail | Completed |  | blockage in single liquid pipe stopped full test of pipework above platform on district line, between SB/01/OU/03 condenser and FCU SB/01/FCU/03
| 02SL - Stations (LUL) | Cxxx-NCR-003000 | NCR | LULO - Accommodation Block - Roofing & Guttering - Benchmark of Bauder roof system rejected by CRL |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-11-30 | 2021-11-22 10:25 | 357 | 2020-08-22 14:43 | Architectural - Roofing & Exterior Treatment | 1500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | CRL rejects to sign off the benchmark for the Bauder thermoplan roofing system at the accommodation blocks as they have not been offered to witness the build up of the internal layers. There is not a section of the roof that can be offered to CRL where all the layers of the roofing system are visible.
| 02SL - Stations (LUL) | Cxxx-NCR-003001 | NCR | DSS-CHS Risers. Voids to be protected and kick-plates to be added |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-01-19 | 2021-05-26 10:38 | 127 | 2020-09-08 10:14 | Architectural - Handrail | 33000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | It is been notice some design issues on the metal flooring on DSS & CHS risers, Below the list of risers. DSS Level B - Riser A, Riser B2 Level A - Riser A, Riser B2 Level 1 - Riser A, Riser B2, Riser B3 Level 3 - Riser A, Riser B1, Riser B2 Level 4 - Riser A, Riser B2 Level 5 - Riser A, Riser B2 Level 6 - Riser A, Riser B1, Riser B2 CHS Level 1 - Riser 1, Riser 2 Level 3 - Riser 1, Riser 2, Riser 3 Level 4 - Riser 1, Riser 2, Riser 3 Level 5 - Riser 1, Riser 2, Riser 3, Riser 4 Level 6 - Riser 1, Riser 2, Riser 3 Level 7 - Riser 3 See attached "DSS Riser Voids in floor to be protected 2" & "CHS Riser Voids in floor to be protected" for support documentation, mark up and pictures. There are 2 problem. 1- Missing kick-plate in various levels, that can cause that tools or material can drop down the riser and cause and accident in levels below. 2- Future use builder work holes needs to be protected by handrail or cover plate. Kickplates, safety guard rails and the infilling of redundant void will be required in order to comply with Building Regulation and LUL/CRL standards. F2 design will be produce by BH for each individual area This NCR will also cover the work of Cxxx-PWK-03578 - Design & installation of handrail. The installation of the permanent handrail now will block the access to Escalator equipment room 4/171 that is frequently use for maintenance (as per Cxxx-__M-S-DWG-D061_WS105-53009_C01).
| 02SL - Stations (LUL) | Cxxx-NCR-003002 | NCR | LULO - ESS - S23 Balustrade Clashes |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-10-05 | 2021-03-10 12:24 | 156 | 2020-08-26 08:54 | Architectural - Balustrade | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Three clashes have been identified during the installation of the __ S23 balustrade and handrail works: 1) The Lift 6 Level 2 Lobby landing area ('Lot 1') baseplate clashes with the paving. This is in localised areas where the balustrade post baseplates extend beyond the tiling line, causing the stiffeners to sit close to the FFL. 2) The handrail to the South side of 'Lot 1' clashes with the __ circular column preventing installation of the final bay of handrail. 3) The baseplate of the handrail post on the S23 mid-landing clashes with the tiling because the stiffeners sit too close to the FFL.
| 02SL - Stations (LUL) | Cxxx-NCR-003003 | NCR | unaccessable motorised dampers to CHS level 3 ductwork |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-11-06 | 2021-08-07 10:48 | 274 | 2020-08-26 09:04 | Mechanical - Heating Ventilation & Air Conditioning | 3000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | CHS/3/TAD/02 – May be able to prove accessibility by demonstration using MEWP/tower. May require movement of services and/or damper. CHS/3/MFD/03 – Not accessible due to ductwork running beneath damper. Damper needs to be extended away from the wall. CHS/3/MFD/07 – Not accessible due to services running beneath damper. Services and/or damper need to be moved.
| 02SL - Stations (LUL) | Cxxx-NCR-003004 | NCR | CHS - __ - Door CH/D1/017 - Minimum Clear Opening W (m) |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-10-13 | 2021-05-20 21:53 | 219 | 2020-09-03 13:01 | Architectural - Doors | 1500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Door CH/D1/017 does not comply with the "Minimum Width Clear Opening" stated on the Door Schedule Rev 39.0. Minimum Width Clear Opening on Door Schedule - 850mm Minimum Width Clear Opening on F2 Drawing + Installed - 835mm This door is located on the Room 1/237 - Escape Route For People With Restricted Mobility.
| 02SL - Stations (LUL) | Cxxx-NCR-003005 | NCR | Sitewide - Flooring - Lower Concourse - R12 SME Walkway - __ incorrect installation |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-08-15 | 2021-08-10 13:11 | -5 | 2020-09-03 14:15 | Architectural - Flooring | 40000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | __ Sheets are debonding after installation completed
| 02SL - Stations (LUL) | Cxxx-NCR-003006 | NCR | LULO - GSM Building - Roofing and Guttering - Lack of Samples & Benchmarks |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-11-11 | 2021-03-31 16:29 | 140 | 2020-09-12 15:38 | Architectural - Roofing & Exterior Treatment | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | No samples or benchmarks have been produced/offered to CRL during the construction of GSM Roof.
| 02SL - Stations (LUL) | Cxxx-NCR-003007 | NCR | SIL Faulty Lamppost Flood Lighting HCDL circulation |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-10-17 | 2021-03-29 20:21 | 163 | 2020-09-07 15:17 | Electrical - Lighting | 10000 |  | Manufacturing Defect | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Other | Completed |  | __ Procured flood light fittings from SIL. The lights provided were faulty and required returning to the supplier for investigation and rectification.
| 02SL - Stations (LUL) | Cxxx-NCR-003008 | NCR | LULO - West Lift Lobby & Subways Failed Cube Results |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-10-18 | 2020-09-24 12:36 | -24 | 2020-09-08 09:07 | Architectural - General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | For the West Lift Lobby & Subways package there has been 2 cube failures. - cube failure for the blockwork plinth - cube failure for the HCDL slab edge around the Stair 34 stairwell See attached results
| 02SL - Stations (LUL) | Cxxx-NCR-003009 | NCR | train pressure pulse / piston effect loading |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-10-18 | 2020-11-03 17:14 | 16 | 2020-09-08 09:11 | Mechanical - Heating Ventilation & Air Conditioning | 12000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Design Problem - Not Defined | Completed |  | An early warning notice 03008 is raised to highlight the risk tor that the brackets installed are not suitable for the train pressure pulse / piston effect loadings as CAT II check has identified remedial works are required.
| 02SL - Stations (LUL) | Cxxx-NCR-003011 | NCR | Smoke Recirculation - Platform Smoke Extract |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-10-19 | 2021-07-29 13:55 | 283 | 2020-09-09 08:13 | Systems - Ventilation and Pressure Relief | 30000 |  | Testing and Commissioning | Rework | 2 (6-60k) | Complete | Design Problem - Other | Completed |  | During the testing of the Platfrom Smoke Extract with smoke generation on the CRL platforms it was noted that Smoke from the discharge louvre of DSS/B/PSEF01&02 was being drawn into the intake of fans DSS/A/PSEF/01&02 that serve the pressurisation system for Stair 3 DSS.
| 02SL - Stations (LUL) | Cxxx-NCR-003012 | NCR | Sitewide – __ Doors – Installation of Door Frame Fixings not captured within a Cat II check |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-01-25 | 2021-05-26 10:53 | 121 | 2020-09-15 15:23 | Architectural - Doors | 1600 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Installation of fixings without a CAT Design Check Certificate. CAT Design Check Certificate does not capture all different fixings used by __ to fix the door frames into substrate.
| 02SL - Stations (LUL) | Cxxx-NCR-003013 | NCR | CHS Level 4, THC Level 3, DSS Level 3 and DSS Level 5 Damper access |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-10-21 | 2021-08-04 14:04 | 287 | 2020-09-11 12:16 | Mechanical - Heating Ventilation & Air Conditioning | 10000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Design Problem - Other | Completed |  | CHS Level 4 Battery room Damper is installed above a battery rack and in THC Level 3 CER3 and UPS5 smoke dampers are inaccessible due to other services impeding maintenance. In DSS Level 3 fan room and Level 5 CER maintenance access to dampers is awkward.
| 02SL - Stations (LUL) | Cxxx-NCR-003014 | NCR | CHS 3/611 Additional protection against condensate required from possible dripping from FCU tray above UPS. . |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-05-18 | 2021-04-27 10:40 | -21 | 2020-09-11 12:27 | Mechanical - Heating Ventilation & Air Conditioning | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | in CHS room 3/611 a FCU sits partially over UPS. leak/condensation could drip from tray on to UPS
| 02SL - Stations (LUL) | Cxxx-NCR-003015 | NCR | DSS roof condenser repairs to insulation |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-01-21 | 2021-02-25 16:18 | 35 | 2020-09-11 13:00 | Mechanical - Heating Ventilation & Air Conditioning | 1500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Insulation is not UV rated and has been left uncovered to both refrigerant pipe and blue insulation
| 02SL - Stations (LUL) | Cxxx-NCR-003016 | NCR | Stair 25 Selux trunking installed in a non-maintainable fashion |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-10-27 | 2020-10-01 10:09 | -26 | 2020-09-17 07:42 | Electrical - General | 2000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The Selux trunking on stair 25 has been installed in a non-maintainable fashion where the light fitting could not be unplugged and removed completely. The wire-way and light fitting mounts within the Selux trunking housing are preventing the plug from being able to freely travel the length of the wire-way when the light fitting had been unplugged stopping the light fitting from being removed. __ are to move their __ sockets to a position where the light fitting plugs can be unplugged and removed with no hindrance.
| 02SL - Stations (LUL) | Cxxx-NCR-003017 | NCR | GSM Bin Store lift - Removal of signed off Isolator without an approved design |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2020-10-29 | 2020-10-12 13:48 | -17 | 2020-09-19 14:00 | Electrical - General | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | CRL-OBS-34388 was raised on 29/08/2020 00:00:00 - the OBS stated an NCR was to be raised by the T1, which hasn't been actioned. The Previously installed and operational Rotary isolator for the Bin store hoist was removed and swapped for a castell isolator without an approved design and after this had been discussed with CRL who advised this was not to be swapped until contact with CEG for confirmation. The rotary Isolator was removed over a possession and a castell installed only for CEG to confirm the following week it was not required. The Isolator was then changed again on the following possession to revert back to the original F1 design.
| 02SL - Stations (LUL) | Cxxx-NCR-003018 | NCR | LO - Platform 5 & 6 End Barriers - Splice Joints out of Tolerance |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-12-20 | 2020-12-15 11:06 | -5 | 2020-09-21 10:25 | Architectural - Balustrade | 1200 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following the installation of the Platform 5 & 6 end barriers, there are noticeable issues with the splice joints. A variety of joints are either misaligned or have gaps that are too large.
| 02SL - Stations (LUL) | Cxxx-NCR-003020 | NCR | Installation of VRF pipework to DSS services yard |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-11-02 | 2021-01-22 13:32 | 81 | 2020-09-23 12:42 | Mechanical - Heating Ventilation & Air Conditioning | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Last week the condenser moves in the DSS services yard neared completion. When the refrigerant pipework wtests took place to the VRF systemsnine leaks were discovered. Three bottles of nitrogen was used in the testing activities. Where the leaks were discovered the installed pipework was pulled apart with the insulation taken off to allow access to these leaks. the decision was made to stop all works and requested the VRF operative to stop all works and leave site. You will see from the photographs that the installation is not satisfactory now and the offending pipework being ripped out and replaced. ripping out and re-fitting.
| 02SL - Stations (LUL) | Cxxx-NCR-003021 | NCR | MEP S&T Acceptance Status ITP's Code 2 some have not been resubmitted |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-01-07 | 2021-05-16 08:36 | 129 | 2020-09-24 09:40 | Mechanical - Mechanical Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | A number of ITP's have been at Code 2 status for over the CRL speciifed time scale. These include the following ITPs. Cxxx-__M-E-ITP-D061-50092 Commissioning & Test Plan Electrical Systems – LV Systems - Code 2 since 05/04/19 Cxxx-__M-M-ITP-D061-50044 Inspection and Test Plan for CHS and DSS Trace Heating Works - Code 2 since 02/10/19 Cxxx-__M-P-ITP-D061_WS106-50006 Inspection and Test Plan LU/LO Variable Refrigerant Flow [VRF] System Installation - Code 2 since 16/01/19 Cxxx-__M-R3-ITP-D061_WS106-53009 Commissioning & Test Plan - Smoke Control System (SCS) - Code 2 since 09/09/19
| 02SL - Stations (LUL) | Cxxx-NCR-003022 | NCR | LO - Code 2 ITP Cxxx-__M-C-ITP-D061_WS106-53072 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-12-23 | 2020-10-16 14:07 | -68 | 2020-09-24 10:41 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | ITP Cxxx-__M-C-ITP-D061_WS106-53072 was Code 2 on 29/06/2017 and has not been updated within specified timescales.
| 02SL - Stations (LUL) | Cxxx-NCR-003023 | NCR | __ installation clash with lift overrun |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-11-09 | 2020-10-19 09:53 | -21 | 2020-09-30 06:32 | Fire - Detection | 5000 |  | Design | Use As-Is | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | __ pipework installations within Lifts 2, 3, 7 and 10 have been installed within the lift over run areas at the top of the shafts.
| 02SL - Stations (LUL) | Cxxx-NCR-003024 | NCR | Missing Fibre for Smart Router 08 Media Converter Post IRN |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-11-24 | 2020-10-16 13:20 | -39 | 2020-10-15 13:03 | Electrical - General | 2500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | NCR raised to capture the missing fibre for media converter 08
| 02SL - Stations (LUL) | Cxxx-NCR-003025 | NCR | LO Concourse - Baileys Stainless Steel Panels - CMS Drop wires |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-01-19 | 2021-03-30 10:12 | 70 | 2020-09-30 08:03 | Architectural - General | 2000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | As communicated to the Project Maanager, the Contractor has found an issue with the drop wires used to hang the Baileys CMS access panels. The current CMS panel support arrangement has been tested, opening and closing the panel 50no times. This was done in an controlled manner and the panel was not allowed to suddenly fall open. Due to the nature of the work, it has occurred on site where a panel has fallen open and it caused one of the drop wire crimps to break. The panel did not drop, as it is held in place securely by the hinge. There is no risk to the panels fixity as they are supported by the hinge and lock plates, the risk is when opening. The Deltaland installation team have been briefed to ensure that no access panels are left to fall open when opening, or left hanging without additional support. With this in mind we have realised that in the real world there is a risk that the maintainer will allow the panel to drop and would like to alter the CMS drop wires to mitigate this risk. The Contractor has found some suitable drops wires, which are being used on the project as an alternative.
| 02SL - Stations (LUL) | Cxxx-NCR-003026 | NCR | DSS L1 - Stair 3 handrail - Handrail high |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-11-19 | 2020-10-24 15:45 | -26 | 2020-09-30 11:50 | Architectural - Balustrade | 3000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | There is a discrepancy between the F2 drawing and the asbuilt of the slab. After breaking the tarmac for the post installation it is been found that the SSL level is 25mm lower. The posts have been fabricated, __ propose to use this post to avoid any over cost on the fabrication of new handrail. The new high on the handrail will be min. of 970mm all the way, instead of 1000mm.
| 02SL - Stations (LUL) | Cxxx-NCR-003027 | NCR | THC Earthing & Bonding References |  | Contr | VIN | WHI - Whitechapel Station (Central) |  | 2021-04-03 | 2021-03-29 20:26 | -5 | 2020-10-01 12:01 | Systems - Earthing and Bonding | 2000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Labelling to Supplementary Earthing for the Ticket Hall & Concourse use the 'CTH' reference, rather than the 'THC' reference shown on the approved Schematic (Cxxx-__M-E-DDE-D061_WS106_Z-30941).
| 02SL - Stations (LUL) | Cxxx-NCR-003028 | NCR | [A-53178] ETH - FOH Door support & Cladding - Missing grout packer records |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-11-10 | 2021-01-28 13:51 | 79 | 2020-10-01 17:35 | Architectural - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Construction Records - ETH FOH Steel for __ Door Onsite Installation Records At the point of certification and package submission it was identified that the grout records as part of the packing of the connection plate to brick face of the main support beam were outstanding.
| 02SL - Stations (LUL) | Cxxx-NCR-003029 | NCR | LULO - LO Concourse - Fire Protection (__) - Working To Unapproved Drawings |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-12-01 | 2021-01-15 09:47 | 45 | 2020-10-02 14:52 | Architectural - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Fire protection works have been carried out on site on Stairs 26 & 28 with the drawings being at Code 3 and on Stair 3 Cross Passage without the drawings being submitted to CRL. List of affected drawings have been referenced in 'Reference Documents' section.
| 02SL - Stations (LUL) | Cxxx-NCR-003030 | NCR | Installation of material that is not MCR'd |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-11-14 | 2020-10-21 14:32 | -24 | 2020-10-05 16:11 | Electrical - Lighting | 10000 |  | Incorrect Installation | Use As-Is | 2 (6-60k) | Complete | Material/Preservation Problems - Other | Completed |  | installation of __s ALSECURE BS6724 on the HCDL Platform 1 & 2 for the Lamppost supplies and Dali without an MCR. MCR-007657 is approved for this cable but it states it is not to be used in an area where LU standard 1-085 is applicable.
| 02SL - Stations (LUL) | Cxxx-NCR-003031 | NCR | LU GSM - External Cladding Outstanding Construction Records |  | Contr | VIN | WHI - Whitechapel Station (Central) |  | 2021-02-26 | 2021-09-29 10:00 | 215 | 2020-10-06 15:15 | Architectural - General | 1000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | At the point of certification, a number of onsite records are not available for the GSM External cladding cert pack (Cxxx-__M-A-CER-D061-53014) including fire rated elements. See attached excel file summarising the elements of work and the available certification.
| 02SL - Stations (LUL) | Cxxx-NCR-003032 | NCR | LU - Accommodation Block - External Cladding Construction Records |  | Contr | VIN | WHI - Whitechapel Station (Central) |  | 2020-11-27 | 2021-07-08 13:27 | 223 | 2020-10-06 15:20 | Architectural - General | 1000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Verification Problems - Inspection points not adequate | Completed |  | At the point of certification, construction records for fire rated elements of the Accommodation Block cladding works are not available for submission (ref. cert pack Cxxx-__M-A-CER-D061_WS106-50055).
| 02SL - Stations (LUL) | Cxxx-NCR-003033 | NCR | GSM __ VRF Condenser Units installed without MCR & without an approved design |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-04-16 | 2021-04-07 19:49 | -9 | 2020-10-07 07:07 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | It was noted during a recent survey of the GSM that the condenser units on Level 2 differ from those specified within the approved schedule and do not have an approved MCR. As a consequence of this the electrical design and supplies to these units are not appropriate for the current installation. This applies to units GSM/02/EC/01 & 02. Attached is PTR-2779 that was previously rasied against this issue.
| 02SL - Stations (LUL) | Cxxx-NCR-003034 | NCR | LU - Accommodation Block - __ drawings not listed in CAT checks |  | Contr | VIN | WHI - Whitechapel Station (Central) |  | 2021-06-25 | 2021-07-04 18:32 | 9 | 2020-10-07 17:01 | Architectural - General | 6000 |  | Documentation and Records | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | __ drawings and design checks for the LU Accommodation Block cladding are listed in package listing Cxxx-__M-A-CER-D061_WS106-50055. Each CAT check document contain a list of the F2 drawings that are covered by that check and certificate. A number of drawings used for the construction of the Accommodation block cladding are not listed in the existing CAT checks.
| 02SL - Stations (LUL) | Cxxx-NCR-003035 | NCR | LULO - LO Concourse - Fire Stopping (__ & __) - Fire Registers No __ly Updated |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-11-30 | 2021-07-22 07:11 | 234 | 2020-10-07 15:26 | Architectural - General | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Fire registers for __ and __ have not been updated as the works progress along the LO Concourse. This issue has been captured under this NCR in order to progress with the certification of sub-construction certificate Cxxx-__M-A-CER-D061-53186 Rev 1.0.
| 02SL - Stations (LUL) | Cxxx-NCR-003037 | NCR | additional doors for access for ductwork cleaning |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-11-16 | 2021-08-06 13:16 | 263 | 2020-10-07 15:41 | Mechanical - Heating Ventilation & Air Conditioning | 51800 |  | Incomplete Works | Repair | 2 (6-60k) | Complete | Procedure Problem - Not Defined | Completed |  | Full clean of the ductwork system is to be carried out. It has been identified by the cleaning subcontractor that additional/larger hatches are required to enable cleaning of the ductwork.
| 02SL - Stations (LUL) | Cxxx-NCR-003038 | NCR | LULO - LO Concourse - Firefly to Concourse Glazing - Loss of Firefly Assurance Records |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-11-30 | 2020-10-28 16:48 | -33 | 2020-10-08 09:58 | Architectural - General | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | R12 Firefly assurance records were lost and needed to be replicated by the current production team. Note that __ Fire Engineer and CRL Assurance team have both witnessed the installation.
| 02SL - Stations (LUL) | Cxxx-NCR-003039 | NCR | CDFM Failed pressure test |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-11-21 | 2020-11-10 13:38 | -11 | 2020-10-12 11:21 | Fire - Suppression | 2000 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the pressure testing of the CDFM pipework for the LULO platforms a leak was discovered at gridline 4 on Platform 6 South bound. This section of CDFM pipework is at high level supported by the architectural stainless steel brackets.
| 02SL - Stations (LUL) | Cxxx-NCR-003040 | NCR | LPWM - comissioing without and accepted CATII design check or IRN |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2020-10-23 | 2021-01-29 15:38 | 98 | 2020-10-13 11:15 | Fire - Suppression | 2000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | This NCR has been reluctantly raised by CRL, the contractor was requested to do so 2 weeks ago. The DSS LPWM system has been energised and commissioning has started without an accepted IRN or CART II design check certificate. This represents out of sequence working and carries associated risk of rework. Cxxx-PWK-03379 has been raised to capture the outstanding CATII cert, although PWK's are not the correct vehicle to document and track out of sequence works and risk of reworks.
| 02SL - Stations (LUL) | Cxxx-NCR-003041 | NCR | LULO - Signage - Design Check Outstanding for Signs already installed on site |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-11-25 | 2021-04-23 19:42 | 149 | 2020-10-16 09:56 | Architectural - Signage | 1000 |  | Design | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | CAT Design Checks below are not submitted for __ & CRL for approval, and the signs have already been installed on site. LULO Projected Sign Brackets - Cxxx-__M-A-CER-D061_WS106-50023 S/1-009, 018, 022, S/2-031 and 034 Lift Sign Brackets - Cxxx-__M-A-CER-D061_WS106-50025 S/1-010, 012, 023, 055 and S/2-014 Ticket Sign Bracket - Cxxx-__M-A-CER-D061_WS106-50117 S/1-019 S/1-026 Fixings - Cxxx-__M-A-CER-D061_WS106-50119 Level 1 Wide Free Standing Signs - Cxxx-__M-A-CER-D061_WS106-50123 S/1-043, 044 and 045
| 02SL - Stations (LUL) | Cxxx-NCR-003042 | NCR | Asset Labelling - Use of Circuit References |  | Contr | VIN | WHI - Whitechapel Station (Central) |  | 2021-08-29 | 2021-01-20 16:38 | -221 | 2020-10-16 16:24 | Information Management - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Asset Labels on some electrical assets (such as spur outlets, isolators and maintenance sockets) state the Circuit reference on Line 3.
| 02SL - Stations (LUL) | Cxxx-NCR-003044 | NCR | Cxxx A1 Schematic's |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-11-29 | 2020-10-20 16:11 | -40 | 2020-10-20 10:53 | Electrical - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | As per specification Cxxx-__M-E-RSP-D061-50008, JY82.1310. A diagram showing clearly a schematic arrangement of the local electrical distribution shall be provided within all switchrooms in accordance with BS 7671. Such diagrams shall be controlled and updated whenever a material alteration takes place. Size A1 encapsulated and securely fixed to the wall with cup and screws within each switch-room. __ are not able to install an A1 schematic for both the LV & Earthing in Switchrooms due to the lack of wall space in the room's
| 02SL - Stations (LUL) | Cxxx-NCR-003045 | NCR | DSS Level 6 Mist room duty and standby pump electrical supplies |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-01-19 | 2020-10-30 08:59 | -81 | 2020-10-21 08:17 | Electrical - LV Equipment | 3000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | In the mist room we have 2 mist control panels which give power the the large pumps that run the mist control, one panel feeds the duty and jockey pump and the 2nd panel feeds the standby pump, the electronic motor starter contactors in the panels require cabling for the duty and standby pump motors to be star delta startup to evenually obtain full speed, the motor start running on the star motor connection to get through the high torgue startup then chane to the delta connection to run up to the required speed thus meaning from the mist control panels we require 2 x 3phase supplies to both the duty and standby pumps but only one 3 phase cable was run to each of the pumps meaning full speed would not be obtained
| 02SL - Stations (LUL) | Cxxx-NCR-003046 | NCR | LULO - Primary Steel Loose Bolts 2020 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-08-23 | 2021-07-07 13:42 | -47 | 2020-11-02 17:51 | Civil - Structural Engineering | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | Further to NCR 2569, during the on-going construction works within the LU section, a number of bolts have been found loose on the column to canopy connections of the primary steelwork members on the platform 2 lower canopy HCDL area. __ are currently carrying out a survey to determine the extent of the number of bolts effected, and the primary steelwork Subcontractor (__) has been contacted for review and input.
| 02SL - Stations (LUL) | Cxxx-NCR-003048 | NCR | Removal Methodology CHS/05/ARF/02 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-02-23 | 2021-02-23 10:00 | 0 | 2020-11-03 12:25 | Mechanical - Heating Ventilation & Air Conditioning | 4000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | Following CEG VAP inspection it was identified that the removal of CHS/05/ARF/02 appears to be obstructed by the surrounding steel framework. CRL-OBS-34045 was raised to request a description detailing the removal strategy for this fan.
| 02SL - Stations (LUL) | Cxxx-NCR-003049 | NCR | Stair 3 handrail colour |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-09-10 | 2021-09-13 14:07 | 3 | 2021-09-09 09:02 | Architectural - Handrail | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The handrails on Stair 3 from level 1 to level 3 have different colour, one side is grey and the other is yellow. There was a miscommunication between __ and __ when installing the new handrail. __ want to leave the handrail as is.
| 02SL - Stations (LUL) | Cxxx-NCR-003050 | NCR | Gapping glands used on the Q2 switch cables |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2020-12-18 | 2021-04-05 08:57 | 108 | 2020-11-08 12:08 | Electrical - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | During the CEG Completion VAP the following item was raised - Gapping glands used on the Q2 switch cables at both ends, so SWA appears to be not earthed. Investigation required and solution proposed This was found on all UPS / Neutral Switches.
| 02SL - Stations (LUL) | Cxxx-NCR-003051 | NCR | 16A 230 V sockets not fitted in electrical equipment rooms, so non-compliant with JV22 |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2020-12-18 | 2020-12-15 08:59 | -3 | 2020-11-08 12:37 | Electrical - General | 2500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | 16A 230 V sockets not fitted in electrical equipment rooms, so non-compliant with JV22
| 02SL - Stations (LUL) | Cxxx-NCR-003052 | NCR | CHS and DSS Roof Damage |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2021-04-02 | 2021-05-26 07:02 | 54 | 2020-11-08 12:36 | Architectural - Roofing & Exterior Treatment | 1600 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | During CEG Completion VAP, the following was raised at DSS and CHS - Green roof edging is damaged and the growing medium is entering the gutters Mitigation - Repair the roof
| 02SL - Stations (LUL) | Cxxx-NCR-003053 | NCR | Inaccessible Riser adjacent to door 7/041 (DSS) |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2021-06-01 | 2021-06-23 06:41 | 22 | 2020-11-08 14:13 | Architectural - General | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | During the CEG Completion VAP, the following was raised - Pipe riser behind wall next to door 7/041 is unacceptable, please confirm / provide access for inspection and maintenance
| 02SL - Stations (LUL) | Cxxx-NCR-003054 | NCR | DSS/B/PRSF/02 Isolation Damper Failure |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-12-18 | 2021-07-23 13:21 | 217 | 2020-11-27 08:04 | Systems - Ventilation and Pressure Relief | 6000 |  | Workmanship | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | During fan testing in the DSS on the night of 28th October a component, holding a manual damper open, failed whilst the Smoke extractor fans were running. This caused a build-up of negative pressure, which in turn pulled a flexible connection into the air stream and associated strangle band. The damper is held open via a cast clamp and associated flat end grub screws. It is not clear how the casting failed as no signs of damage could be determined. We also examined the remaining three clamps to find no signs of wear or loose grub screws.. We can only assume either a weakness in the casting or stresses over time cause the failure.
| 02SL - Stations (LUL) | Cxxx-NCR-003055 | NCR | GSM AHU damper damaged to level 2 plantroom |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-12-20 | 2021-04-23 10:19 | 124 | 2020-11-10 13:27 | Mechanical - Heating Ventilation & Air Conditioning | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | when the motor was installed to control the damper on the spindle it was fitted the wrong way. This caused irreparable damage
| 02SL - Stations (LUL) | Cxxx-NCR-003056 | NCR | DSS - Riser B2 - Level 6- Fire Compartmentation design not complete |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-06-01 | 2021-08-10 19:34 | 70 | 2020-11-13 10:20 | Fire - Compartmentation | 2700 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The floor of Riser B2 level 6 is a metal hatch floor installed by __ as per Cxxx-__M-C-DWG-D061_WS105-51663. This does not provide a separate fire compartment between the level 6 riser and level 7 cross passage below.
| 02SL - Stations (LUL) | Cxxx-NCR-003057 | NCR | Fire Strategy Plan – CHS Level 1 – LEER room to provide 2 hours of Fire Compartmentation |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-04-25 | 2020-12-15 12:17 | -131 | 2020-11-16 15:37 | Fire - Compartmentation | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Design - Fire Strategy Plan Level 1 to show DSS THC Lift 8 - 2 hours of Fire Compartmentation. See drawing Cxxx-__M-A-DDA-D061_WS107_1-15610 - CHS Fire Strategy Plan Level 1
| 02SL - Stations (LUL) | Cxxx-NCR-003058 | NCR | Boroscope coring size |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-12-15 | 2021-03-02 13:15 | -288 | 2020-12-03 09:46 | Civil - Civil Engineering General | 1200 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The DSS PCC Cladding Panel Inspection Strategy contained within the Maintenance, Access & Replacement Strategy Report (Cxxx-__M-C-RGN-D061_WS106-50045) required where possible boroscope inspections are to be completed through the parapet. Boroscope detail was formally agreed on Cxxx-FCD-003853 & Cxxx-RFI-004845. The agreed detail was 20mm core hole. However, Due to material availability __ only could install boroscope access point that are 52mm diameter. __ carry out the installation works without opening a new PTR.
| 02SL - Stations (LUL) | Cxxx-NCR-003059 | NCR | FCU access to filters in DSS Corridor serving Please raise an NCR to capture this, to be clear these are the 4no. FCUs in the ground floor corridor of DSS serving the transformer rooms. |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-02-15 | 2021-02-24 17:33 | 9 | 2020-11-18 11:06 | Mechanical - Heating Ventilation & Air Conditioning | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Electrical cable tray impedes access to back of fan coil units serving ground floor transformer rooms from DSS corridor
| 02SL - Stations (LUL) | Cxxx-NCR-003060 | NCR | Fan coil units in GSM no access to clean or replace filters GSM/01/FCU/17, GSM/00/FCU/12 & GSM/00/FCU/13 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2020-04-19 | 2021-07-07 12:10 | 444 | 2020-11-18 15:09 | Mechanical - Heating Ventilation & Air Conditioning | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Where GSM/01/FCU/17, GSM/00/FCU/12 & GSM/00/FCU/13 are located the filters cannot be cleaned or replaced.
| 02SL - Stations (LUL) | Cxxx-NCR-003062 | NCR | Incorrect ATS Timings |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-01-11 | 2021-01-18 19:06 | 7 | 2020-12-02 14:45 | Electrical - LV Equipment | 3000 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | ATS Timings are currently set as per referenced test packs. Primary failure switches to secondary after 15sec. On reinstatment of primary supply ATS reverts after 15sec. This is contrary to attached PMI-01109.
| 02SL - Stations (LUL) | Cxxx-NCR-003063 | NCR | WHI __ Fibre Cable Damage (WB-P invert under DC15) |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-01-11 | 2021-04-07 09:04 | 86 | 2020-12-02 17:10 | Communications and Control Systems - Fibre Optic Network | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | While on inspection it was noticed some __ fibre cables have been damaged: - CER2 731U2 to FHWU3 DC15 (D061-DAT-00200) - CER2 731U2 to PSDWU4 (D061-DAT-00220) - FHWU2 DC14 to FHWU3 DC15 (D061-DAT-00207) These cables will need to be replaced or repaired if possible. Since the damage was found a test has been done which passed, confirming no internal core damage to the cables. Due to no internal damage Cxxx have said it will be accepted to use a sheath repair kit on these cables. See attached pictures and email.
| 02SL - Stations (LUL) | Cxxx-NCR-003064 | NCR | LO - Stair 21 - As-built Survey Discrepancies |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-01-12 | 2021-01-07 12:54 | -5 | 2020-12-03 10:12 | Architectural - Balustrade | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Previous Construction - Problems based on previous construction errors | Completed |  | As-built installation of Stair 21 handrails and balustrade has minor discrepancies against design dimensions.
| 02SL - Stations (LUL) | Cxxx-NCR-003065 | NCR | UPSP coupling clasps when used on pressurised ensign pipework |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-01-17 | 2021-01-28 12:25 | 11 | 2020-12-08 16:49 | Mechanical - Pumps | 4000 |  | Incomplete Works | Repair | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | On the discharge pipework from the under platform sump pumps the ensign couplings need a purpose made clasp that fits over the ensign coupling. This ensures that this pipework can endure pressures up to 5 bar.
| 02SL - Stations (LUL) | Cxxx-NCR-003066 | NCR | DSS Trace Heating Fault Signals |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-01-19 | 2021-04-13 16:14 | 84 | 2020-12-10 09:54 | Fire - Suppression | 4000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | Configuration of the Trace Heating systems in DSS Level 1 (PFR1) do not allow he correct fault signals to be related to the protected system. The Trace heating circuit that protects the ELL Breaching inlet is shared with the header tank feed. Faults on these two systems needs to be monitored by separate systems and the current installation does not allow for this.
| 02SL - Stations (LUL) | Cxxx-NCR-003067 | NCR | Traceheating controller installed without MCR |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-01-23 | 2021-04-20 09:51 | 87 | 2020-12-14 22:13 | Electrical - General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Raystat trace heating controller installed without MCR approval
| 02SL - Stations (LUL) | Cxxx-NCR-003068 | NCR | Sitewide - __ Doors - Evidence required for changes from the assured design - [CRL-OBS-33500] |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-06-14 | 2021-09-30 15:19 | 108 | 2020-12-15 11:30 | Architectural - Doors | 7500 |  | Design | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As per CRL-OBS-33500: While carrying out door inspections between 16/06/2020 and 09/07/2020, the following observation were made and require evidence to capture the change: 1. Aluminium frame vision panel in FR doors are not captured in the fire test results (e.g. CH/D7/005), 2. Door hinges with one spacer per leaf, which means only one hinge is carrying all the load. (most of the GSM doors), 3. Opening sizes smaller than the requirements set out on the door schedule (e.g. TP/D7/061, DS/D5/005, CH/D5/014 & CD/D8/009), 4. Doors open in a different direction as stated in the design (i.e. from opening into the room to out into the corridor) 5. There is a small percentage of closed SnagR item that are still open and need attention. List held by CR. 6. Door DS/D3/029 needs the floor to be leveled for the drop seal to function. 7. Approved detail for the deflection head detail above the doors (e.g. CH/D7/003). 8. Rib nuts and screws required to fill holes in the door (e.g. CH/D3/006). 9. Threshold required for door DS/D4.5/003. 10. Panic lock required for door DS/D6/022 as per the doors hardware schedule. Door drawing is incorrect. 11. Installation of all grub screws (i.e. Security Rated).
| 02SL - Stations (LUL) | Cxxx-NCR-003069 | NCR | Station Entrance Signs - Use of Acylic for Face of Sign |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-04-28 | 2021-07-26 08:19 | 89 | 2021-01-18 17:17 | Architectural - Signage | 1500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | The Whitechapel Station Entrance signs (reference S/1-004 on Whitechapel Road and S/1-038 on Durward Street Bridge), have been manufactured using an acrylic sheet material for the front of the signs. The MCR for these signs, reference Cxxx-__M-A-LRC-D061_WS106-51381 has received a Code 3 with the comment that the acrylic sheet material used for the front of the signs is not suitable for Section 12 stations, even though the signs are located outside.
| 02SL - Stations (LUL) | Cxxx-NCR-003070 | NCR | FCU clash with SCADA cables |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2021-03-31 | 2021-03-29 20:38 | -2 | 2020-12-22 11:13 | Mechanical - Mechanical Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | As per Cxxx-PWK-01571 there is a clash in ESR room 4/666 between DSS/4/FCU/03 and the nearby SCADA cables/conduits. The location of the conduits prevents the FCU filter casing from being installed. As discussed with Cxxx and A Wyer Cxxx The Scada cables in the conduits will need to be retested by Cxxx once removed. Confirmation is also required that there has been no damage or impact to the performance of the FCU due to the lack of filter.
| 02SL - Stations (LUL) | Cxxx-NCR-003071 | NCR | Site Wide - Metal Doors - DSS - Security rating of DSS service yard doors (__ 00109) |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-02-14 | 2021-10-04 15:57 | 232 | 2021-01-05 16:30 | Architectural - Doors | 0 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Following site inspections with Crossrail the security rating of several doors in DSS have been questioned on site; these are as follows: 1. DS/D1/046 2. DS/D1/049 3. DS/D1/117 4. DS/D1/118 5. DS/D1/119 6. DS/D1/120 For a historic timeline of events of the security rating of these doors please refer to Cxxx-RFI-005235. Page 1 of the attached marked up GA shows the security rating status of each door which have been installed. As shown on page 2 there is an additional gate located perpendicular to the service yard which provides an additional level of protection and ensures this area is not public facing. Part of the response to RFI-4748 advised that additional IR detection was required in the service yard but this has not yet been implemented by Cxxx. With the additional gate and given how separated the area is from the public we request further clarification on whether the security rating of the doors needs to change and/or if additional IR detection is required.
| 02SL - Stations (LUL) | Cxxx-NCR-003072 | NCR | Riser 1 - Landing extension - Failed concrete cube |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-02-15 | 2021-01-13 09:07 | -33 | 2021-01-06 11:56 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | The riser 1 landing extension was poured with 40N concrete. The cube results show that at 28 days the cube strength has failed to reach the specified strength of 40N and instead has achieved an average of 31.15 N/mm^2
| 02SL - Stations (LUL) | Cxxx-NCR-003073 | NCR | Sitewide – __ Door – LULO – Upper Concourse – SB.D1.037 – Vision Panel Location |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-02-16 | 2021-01-15 16:42 | -32 | 2021-01-07 15:25 | Architectural - Doors | 1000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Counterfeit Items | Completed |  | Door SB.D1.037 installed on site has both of the vision panels manufactured at 1333mm from FFL to top of vision panel (middle of the leaf vertically). The approved door design shows the vision panels 1500mm from FFL to top of vision panel. The manufactured vision panel height is therefore 167mm lower than design. The single small vision panel is not required for DDA requirements. The location of the vision panel was decided with CRL and __. See attachments.
| 02SL - Stations (LUL) | Cxxx-NCR-003074 | NCR | GSM Mist duty and standby pump electrical supplies |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-02-17 | 2021-01-17 15:21 | -31 | 2021-01-08 11:32 | Fire - Suppression | 5000 |  | Design | Use As-Is | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | In the mist room we have 2 mist control panels which give power the the large pumps that run the mist control, one panel feeds the duty and jockey pump and the 2nd panel feeds the standby pump, the electronic motor starter contactors in the panels require cabling for the duty and standby pump motors to be star delta startup to evenually obtain full speed, the motor start running on the star motor connection to get through the high torgue startup then chane to the delta connection to run up to the required speed thus meaning from the mist control panels we require 2 x 3phase supplies to both the duty and standby pumps but only one 3 phase cable was run to each of the pumps meaning full speed would not be obtained
| 02SL - Stations (LUL) | Cxxx-NCR-003075 | NCR | Failure to meet the required 200 LUX Level in LEER LCR 5,6,8 and 10. |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-02-26 | 2021-05-14 14:36 | 77 | 2021-02-10 10:03 | Electrical - General | 3000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | LCR rooms have insufficient LUX level reports. __ have suggested upgrading the 40w fittings installed in each room to 60w fittings. If the LUX levels are then reported as sufficient no further design changes are required.
| 02SL - Stations (LUL) | Cxxx-NCR-003076 | NCR | WHI CCTV Cable Damage (CAM-0221 & 0227) |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-02-20 | 2021-02-10 21:23 | -10 | 2021-01-11 16:04 | Communications and Control Systems - CCTV | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | •Camera 0221: structure cable has been damaged. •Camera 0227 also has Structure Cable issue.
| 02SL - Stations (LUL) | Cxxx-NCR-003077 | NCR | LULO - HCDL Canopies - Incorrect installation of primary steelwork bolts in the splice plate connections at the HCDL columns |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-06-03 | 2021-03-27 14:02 | -68 | 2021-01-12 10:09 | Civil - Structural Engineering | 3500 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the erection of the primary steelwork structure at the HCDL canopies, M20 8.8 bolts were installed in the splice plate connections at the HCDL columns between grid lines DA-DC and along grid lines D3 (platform 1) and D4 (platform 2). However the approved design shows that M20 10.9 HSFG bolts were meant to be installed in those locations. A total of 192 bolts are affected ditributed in 24 splice plates and 8 columns. This issue was found as part of the investigation works on Cxxx-NCR-003046.
| 02SL - Stations (LUL) | Cxxx-NCR-003078 | NCR | LU_Stair 34_Shroud Trip Hazard |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-01-29 | 2021-03-30 08:30 | 60 | 2021-01-15 14:15 | Architectural - Balustrade | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | On HCDL platform 1 subway 34, shrouds were installed as per the approved (ADEY) F2 design. Following inspection with CRL&LU, these were identified as trip hazards (site photo attached) and remedial works are required.
| 02SL - Stations (LUL) | Cxxx-NCR-003079 | NCR | better access required to motorised damper in SCR room THC 1/770 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-02-23 | 2021-05-01 09:27 | 67 | 2021-01-14 11:33 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | the motorised damper in SCR room cannot be maintained due to other services below.
| 02SL - Stations (LUL) | Cxxx-NCR-003080 | NCR | THC plantroom 2 no ventilation to room |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-02-27 | 2021-06-18 13:49 | 111 | 2021-01-18 14:14 | Mechanical - Heating Ventilation & Air Conditioning | 2000 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During inspection it was noted that Ticket Hall Concourse Plant Room 2 (1/785) does not have any ventilation provided to the room. This plant room requires ventilation.
| 02SL - Stations (LUL) | Cxxx-NCR-003082 | NCR | Installation works carried out without Design approval and post IPAC sign off. |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2021-03-06 | 2021-02-02 10:46 | -32 | 2021-01-25 09:18 | Electrical - Lighting | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | NCR raised for the below: Installation works were undertaken without a PTR submitted to BH or CRL approval in place. The works were undertaken post acceptance of the Small power IPAC. Design change due to __ failing to submit a WAD to carry out accepted design in place. CRL asked that an ncr be raised to capture and not the FCD submitted post all works have taken place.
| 02SL - Stations (LUL) | Cxxx-NCR-003083 | NCR | CHS __R room level 7. discharge air requires angle to stop discharge over installed CMS tray |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-03-08 | 2021-05-30 09:46 | 83 | 2021-01-27 10:19 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Discharge air is installed over electrical tray in CHS __R room level 7. This inhibits the flow of cool air to where it is required.
| 02SL - Stations (LUL) | Cxxx-NCR-003084 | NCR | THC Level 2 Plant Room - Fire Damper Replacement |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-03-09 | 2021-03-03 13:24 | -6 | 2021-01-28 21:52 | Fire - Compartmentation | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | During the commissioning of the Fire Dampers it was noted that SB/MFD/03/17 located within Plant Room 2/780 was defective. The damper was stiff to operate and could not be opened via the motorised actuator. Actions were taken to remedy the issue however the fault could not be rectified without further remedial action.
| 02SL - Stations (LUL) | Cxxx-NCR-003085 | NCR | LULO - Repair Procedure for water damaged intumescent paint |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-05-04 | 2021-03-10 09:18 | -55 | 2021-02-03 17:02 | Structural Engineering - Structural Engineering - General | 2675 |  | Damaged | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Weather or ambient condition | Completed |  | This NCR has been raised to record the works that are related to the repair of intumescent paint that has been damaged due to prolonged periods of exposure to rain. Identified areas of damaged intumescent paint have been repaired using the procedure outlined in Cxxx-__M-A-CCN-D061_WS106-50031.
| 02SL - Stations (LUL) | Cxxx-NCR-003086 | NCR | Cxxx - DSS and CHS - Level C Grating`s fixings |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-03-15 | 2021-06-23 12:24 | 100 | 2021-02-03 14:38 | Architectural - Flooring | 1500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __`s support structure in CHS (Cxxx-__M-S-DDD-D061_WS107_C-00002) & DSS (Cxxx-__M-S-DDD-D061_WS105_C-00001) is fixed to the substrate with HUS-N (8.8) M16 anchors as per the F1 intend. However, the fixing has a lifetime of 50years specified for internal environment and there is no data to prove its life in external environment. __`s have carried out calculation check to establish the estimated design life of HIS-N fixings in C3 external environment (see `CAL-350 design life estimation pf HIS-N`).
| 02SL - Stations (LUL) | Cxxx-NCR-003087 | NCR | Hydrant Cabinets on LO Platforms - Panel Remakes |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2021-06-08 | 2021-05-26 08:16 | -13 | 2021-02-08 10:04 | Architectural - General | 5500 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | In the time since the F2 designs were issued to BH for review, the final design for the position of the fire hydrants has changed. Both internal and external panels will need to be remade to accommodate the new hydrant location. The intent of Cxxx-FCD-004409 was to outline and seek consent for the architectural design changes required for the hydrant cabinets on the LO platforms 5 & 6, however this NCR is to capture both the consent and implementation stages.
| 02SL - Stations (LUL) | Cxxx-NCR-003089 | NCR | c512 - DSS - Brass Cladding clash |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-03-24 | 2021-10-15 13:20 | 205 | 2021-02-12 15:24 | Architectural - Walls | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | There is a scope clash between __ brass cladding and LULO SS panels. Due to the clash the Hydrant cabinet in Brass cladding can not be oepened.
| 02SL - Stations (LUL) | Cxxx-NCR-003090 | NCR | THC SB/D1/121 - push bar hazard |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2021-10-15 | 2021-10-15 08:44 | 0 | 2021-02-15 08:57 | Architectural - Doors | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | The hold open doors at the end of the public walkway pose a hazard whilst open, this is due to the push bars protruding into the corridor. See attached photographs for further details. Contractor to ensure both push bars are checked in both directions (i.e. entering & exiting the upper concourse) and are satisfactory.
| 02SL - Stations (LUL) | Cxxx-NCR-003091 | NCR | Platform 6 lights/bracketry |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2021-04-16 | 2021-06-03 15:42 | 48 | 2021-02-15 12:01 | Architectural - Finishes | 5000 |  | Design | Use As-Is | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | Following a review of a sample/mock-up, it became apparent that the P6 light assembly was unsatisfactory for the FOH location it is intended for. Upon further check, it appears that the F2 drawing did not receive a code A stamp from BH (see attached emails). Lights to be procured to ensure sufficient for FOH use (as agreed by Lead Designer and confirmed by CRL).
| 02SL - Stations (LUL) | Cxxx-NCR-003094 | NCR | Sitewide- __ Doors - Redundant Holes |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-07-08 | 2021-07-07 08:16 | -1 | 2021-02-16 21:36 | Architectural - Doors | 1200 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Please note this NCR is for BoH Doors only. Due to changes in closer location, removal of selectors and other face mounted door components a number of doors have been left with redundant holes across site. The redundant holes comprise: -Holes from closer removed on leaf -Holes from selector bracket removal on leaf -Holes from selector arm removed from frame header and also junction box removed from frame See below for a list of the known affected doors: CH/D1/012 CH/D3/005 CH/D3/006 CH/D3/015 CH/D5/002 CH/D6/009 CH/D8/003 DS/D3/036 DS/D3/036 DS/D7/023 SB/D1/019 SB/D1/025 - In order to be able to sign off this NCR the repair scope from this door has been transferred to Cxxx-PWK-03327. The door will be repaired in accordance with the process agreed in this NCR and the records attached to Cxxx-PWK-03327
| 02SL - Stations (LUL) | Cxxx-NCR-003095 | NCR | LULO - confirmation of the permenant lighting meets the 1-066 A2 standard. Interim CMS of the operational station is hampering LUX levels to be taken and validated. |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2021-03-30 | 2021-08-20 10:35 | 143 | 2021-02-18 12:44 | Electrical - Lighting | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Interim CMS installed and interim lighting serving operational assets on the LULO are hampering Lux measurements being taken to validate the new permanent installed fittings meet the 1-066 A2 requirements. Over the course of the project we have brought into use many of these areas with the understanding that the values will be met once the interim CMS and interim lights have been removed. __ have assessed the areas in question by removing hoardings & isolating the interim lighting to conduct what measurements that can be taken and it appears some locations will need to potentially have additional lighting to be installed as the Interims are not having the impact on the Lux values as assumed. In addition to the above the permanent signage has been designed and installed in the stair 23 area which also caused a failure to meet the requirement which is captured in the VAP 697 linked. The sign has now been relocated for the time being to allow the levels to meet the standard and CRL to ensure the new location proposal is satisfactory and meets all requirements.
| 02SL - Stations (LUL) | Cxxx-NCR-003097 | NCR | Sitewide - __ Doors - SR3 Rated Doors Dog Bolt and Hinge Plate Issues |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-04-05 | 2021-09-14 16:43 | 162 | 2021-02-24 17:27 | Architectural - Doors | 5500 |  | Manufacturing Defect | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Counterfeit Items | Completed |  | This NCR covers the following no. 3 SR3 rated door issues. Issue 1. The below no. 10 doors have been manufactured with the intended Issue 7 design and are missing all of their hinge guard plates. CH / D1/001 DS / D1/041 DS / D1/042 SB / D1/016 SB / D1/036 SB / D1/037 SB / D1/038 SB / D1/141 TP / D7/048 TP / D7/049 Issue 2. The below no. 2 doors have been manufactured with the intended Issue 7 design but have had some of their hinge guard plates damaged or removed. GS / D2/014 TP / D7/060 Issue 3. Hinge guards on the below no. 2 doors have been installed correctly to these doors but they do not match the two adjacent doors which are missing hinge guards. All four of these doors will be clad with brass cladding and should be identical. DS / D1/039 DS / D1/040
| 02SL - Stations (LUL) | Cxxx-NCR-003098 | NCR | Sitewide – __ Door – SB.D1.035 SR3 Certification Requirement |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-04-10 | 2021-03-10 15:26 | -31 | 2021-03-01 14:41 | Architectural - Doors | 1200 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | 1. Reason for Change CRL has raised concerns about SB.D1.035 not having SR3 certification due to the requirement for a 25mm undercut (to avoid the door swing clashing with the 1:55 ramped floor) as shown in the approved door drawing Cxxx-__M-A-DWG-D061_WS106-54894 and the door schedule extract attached. 2. Clear Outline of Proposal Find attached PTR-9739 response with the reasoning and acceptance of SB.D1.035 as is (not having SR3 certification) from Bakerhicks. CRL to confirm acceptance of SB.D1.035 not having SR3 certification? 3. Cost & Programme Impact (both delivery and design) There is no cost or programme impact. 4. Impact to Follow-on/Interfacing Works SB.D1.035 does not have SR3 certification due to the requirement for a 25mm undercut. 5. Proposed Answer CRL accepts SB.D1.0.35 not having SR3 certification due to the requirement for a 25mm undercut.
| 02SL - Stations (LUL) | Cxxx-NCR-003099 | NCR | Non-Conformity Durward Street Roof Walkway/Staircases |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-04-17 | 2021-03-30 13:14 | -18 | 2021-03-08 17:34 | Electrical - Cable Management | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Following on an IRF inspection with CRL new C rev drawings for the following areas are required, • Cxxx-__M-E-DDB-D061_WS106_C-30370 • Cxxx-__M-E-DDB-D061_WS106_C-30376 • Cxxx-__M-E-DDB-D061_WS106_C-30378 • Cxxx-__M-E-DDA-D061_WS106_C-30368 • Cxxx-__M-E-DDA-D061_WS106_C-30369 • Cxxx-__M-E-DDA-D061_WS106_C-30139 • Cxxx-__M-E-DDA-D061_WS106_C-30140 Reason being is they do not comply to Crossrail Main Works – Electrical Specification Cxxx-__M-E-RSP-D061-50008-7.0 JY61.3104 Single core cables and non-armoured multi-core cables k) Cables from more than one distribution board shall not be drawn into a common conduit, but they can be run within a common trunking. The current drawings do meet the specification, albeit the drawings are approved on EB CRL do not Cross reference all service drawings. It is expected the Designer has taken the specification into consideration and reviewed before issuing
| 02SL - Stations (LUL) | Cxxx-NCR-003100 | NCR | BMS Monitoring of FCU isolation / faults |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-04-24 | 2021-05-13 10:58 | 19 | 2021-03-15 07:43 | Communications and Control Systems - General | 2000 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Following on from CRL/__ meetings on 03/03/21 & 10/03/21 (minutes attached) The requirements set out in JW60.1200 xviii) are not being met with regards to Mitsubish VRF FCU’s, namely if an FCU is electrically isolated it does not show as in fault on the BMS software.
| 02SL - Stations (LUL) | Cxxx-NCR-003101 | NCR | CHS VRF Condenser Maintenance Access |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-05-02 | 2022-01-06 08:23 | 249 | 2021-03-23 16:31 | Mechanical - Heating Ventilation & Air Conditioning | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Design Problem - Not Defined | Completed |  | CRL deem the access to the VRF Condenser to be unsatisfactory for regular maintenance to be progressed on units CHS/B/EC/01-04. Currently to access the Condensers the Engineer must lean across 300mm tray surrounded by Bigfoot support system which takes the 'leaning' distance to approx. 500mm. The Units and associated CMS can be repositioned to provide improved access.
| 02SL - Stations (LUL) | Cxxx-NCR-003102 | NCR | LULO R10 Eastern Walkway – Cracked Plank |  | Contr | VIN | WHI - Whitechapel Station (Central) |  | 2021-08-20 | 2021-09-07 10:55 | 18 | 2021-03-23 17:01 | Architectural - General | 3000 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | A number of minor cracks have been identified in 1No plank on the R10 Eastern walkway (unpaid walkway). Cracks have been identified a considerable time after installation and likely causes could include site traffic over the planks. See pictures and details in the attached report (titled: L11533 Crack Width Monitoring Rev00).
| 02SL - Stations (LUL) | Cxxx-NCR-003103 | NCR | GL 3.3 -3.4 high level CMS |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-06-16 | 2021-12-01 09:24 | 168 | 2021-05-07 11:48 | Architectural - Finishes | 2500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | There is a small section of CMS running between the Stair 25 link bridge and the CMS along the boundary wall which is currently exposed and in view from both the platform and the Lower Concourse
| 02SL - Stations (LUL) | Cxxx-NCR-003105 | NCR | Durward Street - Breeching Inlet Heights |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-06-21 | 2021-05-19 10:14 | -33 | 2021-05-12 11:35 | Fire - Fire Systems & General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Following the revision of the external paving levels to suit the Cxxx structural bridge heights it has created a higher than originally designed pavement level in front of the breeching inlet valves. This has reduced the height to the centre of the inlet by 50mm. In agreement with LFB and the fire inspectors it has been agreed that this reduction in height is acceptable and can be used as is.
| 02SL - Stations (LUL) | Cxxx-NCR-003106 | NCR | DSS & CHS Pulling Points |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-06-30 | 2021-07-21 20:41 | 21 | 2021-03-26 09:10 | Civil - Civil Engineering General | 2500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The pulling points which are specified in the F1 drawings for both DSS and CHS to aid the installation and removal of key equipment have not been installed
| 02SL - Stations (LUL) | Cxxx-NCR-003107 | NCR | L3 Lower Concourse Suspended PHP Sign Artwork (S/3-004,007,024,048) |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-07-08 | 2021-07-29 10:00 | 21 | 2021-04-09 10:43 | Architectural - Signage | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Suspended PHP Signs on the Lower Concourse (Level 3) have been installed with the incorrect artwork. Affected signs S/3-004, 007, 024 and 048. All other levels have been checked and have the correct PHP artwork.
| 02SL - Stations (LUL) | Cxxx-NCR-003108 | NCR | Lack of Monitoring relating to DSS CDFM Cold Water Supply |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-05-22 | 2021-06-24 10:04 | 33 | 2021-04-12 13:16 | Utilities Engineering - Water | 2500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Within the current design there is no way to differentiate between water usage in the station and water usage for the CDFM (Charged Dry Falling Main).
| 02SL - Stations (LUL) | Cxxx-NCR-003109 | NCR | Missing Surge Protection Devices from F1 design for Lightning Protection |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-05-23 | 2021-07-21 10:35 | 59 | 2021-04-13 15:43 | Electrical - LV Equipment | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | On review of the installation as part of the Lightning Protection Risk Assessment Management Calculation Report by Omega Red it was identified that additonal surge suppressors devices were required on the project that currently not fitted.
| 02SL - Stations (LUL) | Cxxx-NCR-003110 | NCR | DSS - Damaged down conductor |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-06-25 | 2021-06-29 18:00 | 4 | 2021-04-17 10:14 | Civil - Civil Engineering General | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Previous Construction - Interfacing issues | Completed |  | During the installation of the boroscope holes which are required to inspect the pre-cast concrete panel fixings on the Eastern elevation of DSS the earthing strap to down conductor 16 (DC16) was cored through and therefore the link has been broken and can now not be utilised.
| 02SL - Stations (LUL) | Cxxx-NCR-003111 | NCR | THC Condensers SB/1/OU/01 & 02 pipe and cable repairs |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-05-28 | 2021-05-11 16:00 | -17 | 2021-04-18 09:59 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the relocation of Condensers SB/1/OU/01 & 02 from THC level 1 MCC21 plantroom to the roof above Crossed pipes were identified between the two fan coil units in the SCR room. Some comms cable jointing was also found which was sub standard.
| 02SL - Stations (LUL) | Cxxx-NCR-003112 | NCR | insufficient pressure test to cover level 5 CDFM modifications. |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2021-06-07 | 2021-04-30 13:44 | -38 | 2021-04-28 11:05 | Fire - Suppression | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Pipework modifications have been carried out on the CDFM at level 5. The pipework was pressure tested to only 12 Bar for 15 minutes where WI requires a much more onerous test. See PMI-1127 / PMC-16412 for more details. No agreement was sought prior to the pressure test to agree a relaxation is WI requirements. The FAE requested the contractor to raise this NCR in February when the issue first became apparent, but has been raised by the FAE in April as no NCR had been raised. Please see emails in the attachments.
| 02SL - Stations (LUL) | Cxxx-NCR-003113 | NCR | LULO – PCC Walkway – Outstanding QA Documents |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-10-01 | 2021-10-21 12:47 | 20 | 2021-05-12 12:23 | Structural Engineering - Pre-cast | 800 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | This NCR-3113 relates to the Precast Concrete Plank Ramp R10 and R12 construction records as detailed in PWK-3128. The status of the items detailed in the punchwork and proposed solutions are as follows: 1. Drawings are at Code 2 as per the above RIR Cxxx-__M-C-LRG-D061-50007 Rev 984 Cxxx-__M-C-DWG-D061_WS106-53453 [P02] Cxxx-__M-C-DWG-D061_WS106-53454 [P02] Solution: CRL to Code 1. Action complete. Complete RLDs for drawings 53453 & 53454 as part of Construction Records. __ action. 2. Outstanding Onsite construction records for fire sealant installation Construction Records - Fire Sealant [Cxxx-__M-A-LRC-D061_WS106-50850] Solution: Not required since no fire-stopping installed. No further action required. 3. R10N & R12 Incomplete Onsite construction records for Precast concrete plank placement & installation, including calibration certificates & concrete cubes for Dry Packed shear Key Construction Records - Secondary Means of Escape R12 - Cxxx-__M-A-LRC-D061_WS106-50847 Construction Records - Secondary Means of Escape R10N - Cxxx-__M-A-LRC-D061_WS106-50849 Solution: Raise NCR for missing information. Submit what we have in PWK-03128. __ action. 4. Outstanding benchmark submission for the PCC Walkway Solution: Raise NCR - benchmark cannot be provided as works have been covered up with finishes. Propose to accept this as-is. CRL to confirm this is acceptable. 5. As-built surveys outstanding AsBuilt Survey - R10N PCC WALKWAY [Cxxx-__M-A-RGN-D061_WS106-50255] AsBuilt Survey - R12 SME PCC WALKWAY [Cxxx-__M-A-RGN-D061_WS106-50136] Solution: Accept as-is and instead provide an as-built for the finished walkways. CRL to confirm this is acceptable. 6. F1 & F2 Redline drawings Solution: Complete RLDs for Work Pack. __ action. 7. Warranty documentation outstanding. Solution: Warranty can likely be provided by __ for R10 ramps. Documentation to be sought and form part of the Construction Records. __ action. Warranty cannot be provided by the Sub-contractor for the __ R12 installed ramps as the company no longer exists. Propose to accept as-is and confirm whether __ warranty is acceptable to provide appropriate warranty coverage. CRL to advise. Outstanding works: 8. Cxxx-FCD-004161 - R10N PCC Walkways - Lateral Restraint details The proposed lateral restraint is accepted, the installation work and installation records for these lateral restraints are to be submitted upon completion. Solution: Installed by __/__ thus records to be provided in Construction Records. __ action. Outstanding works: 9. Cxxx-FCD-004162 – R10N PCC Planks - Dry packing of planks The proposal to dry pack the planks is accepted, the installation work and installation records for these lateral restraints are to be submitted upon completion. Solution: Installed by __/__ thus records to be provided in Construction Records. __ action.
| 02SL - Stations (LUL) | Cxxx-NCR-003114 | NCR | CHS PRSF North Intake Smoke Detector not fitted as per manufactures specification |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-06-10 | 2021-05-20 15:24 | -21 | 2021-05-01 13:15 | Fire - Detection | 4000 |  | Design | Use As-Is | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Due to the configuration of the ductwork between the North intake of the Stair pressurisation and the Fans there is not a suitable location to site the in duct smoke detector.
| 02SL - Stations (LUL) | Cxxx-NCR-003115 | NCR | debris found in horizontalpublic health pipework |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-11-01 | 2021-09-29 16:27 | -33 | 2021-05-05 13:49 | Mechanical - Public Health Engineering | 12000 |  | Testing and Commissioning | Repair | 2 (6-60k) | Complete | Management Problem - Other | Completed |  | The CCTV survey undertook to all the horizontal public health pipework has discovered debris that will hinder the flow of effluent. This will result in impeding the flow creating blockages and causing major disruption to the station. This NCR supersedes Cxxx- PWK-03515 (P-CER-D061_WS107-50003) at present there are 3 no. places where 2 metre lengths in GSM that have not be surveyed. These will be carried out under this NCR
| 02SL - Stations (LUL) | Cxxx-NCR-003116 | NCR | DSS LPWM system star/delta starter tripping |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-07-04 | 2021-07-07 13:13 | 3 | 2021-05-25 12:31 | Fire - Suppression | 4000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | During the star/delta start up sequence of the DSS LPWM duty, and standby pumps, there has been nuisance tripping of the mains supply breakers at the distribution board. This tripping occurs at inconsistent times and sometimes the pumps have operated without issue. This has meant that due to the inconsistent starting 100% confidence in the system has not been achieved. __ have supplied a detailed design and information backing up the selection of the protective device with breaker characteristic curves. __have supplied the control panels and have had an independent review of the system by a specialist, with a report issued showing their findings
| 02SL - Stations (LUL) | Cxxx-NCR-003117 | NCR | LULO - Mild steel Nylon coated handrails |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-07-27 | 2021-11-25 17:39 | 121 | 2021-06-17 13:09 | Architectural - Handrail | 6000 |  | Design | Use As-Is | 3 (3-6k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The architectural specification (Cxxx-__M-A-RSP-D061-50079) states handrails in various locations are to be finished with nylon coating type PT-302 as per Section JM60.1223. This section states the substrate is to be Galvanised mild steel and Nylon coated by Omnikote Ltd. The contractor has become aware that the handrail subcontractor has misinterpreted the architectural specification and provided nylon coated handrails with mild steel rails rather than galvanized rails. The contractor has held workshops with the designer (__) and Crossrail to review locations and corrosivity categories for the 12no handrail locations that are nylon coated. See attached "Handrail location mark up and proposals" which show proposals to rework 6no locations that are external and exposed to rainfall and also 6no locations that are internal and proposed to use as is. Baker hicks have advised that the works information states corrosivity categories are generic and based on above or below ground location to be C4(high) and C5(very high) respectively. By using previous assessments of corrosion classification for elements in similar areas and examples given in BS EN 12944-2:1217, Bakerhicks have provided proposed corrosivity categories at C2/C3 for the 6no internal handrail locations noting stairs 21,24 and 32 have the potential to be revised to C2 as the handrails are protected from direct rainfall. see attached report issued for corrosion classifications to service support elements in the tunnels Cxxx-__M-S-RGN-D061_WS106-50002. __ has obtained a technical report in which mild steel handrails coated by Omnikote Ltd have been tested to London Underground Specification E6241-A2 (see attached). Test 4 is a salt spray test to BS 3900:F4 for a period of 1000 hours, the nylon coated handrails receive a cross cut in the centre of each panel with a sharp knife prior to exposure. London underground requirement for the test is "No blistering or corrosion of un-scribed areas. Less than 2mm undercutting from scribe", the test results showed no blistering or loss of adhesion around the scribe. Only one panel was partially stripped as the nylon coating was very resistant to removal and there was no sign of corrosion of the metal. Based on the proposed corrosivity categories and technical report for handrails used on London Underground trains. __ propose to rework 6no external handrail location to be galvanised and leave 6no internal handrail locations and use as is.
| 02SL - Stations (LUL) | Cxxx-NCR-003118 | NCR | DSS - LU/LFB access |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-08-05 | 2021-10-21 11:57 | 77 | 2021-06-26 11:23 | Archaeology - General | 3500 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Non-compliance of Door DS/D1/042 for access by LU and LFB in accordance with BS 9999.
| 02SL - Stations (LUL) | Cxxx-NCR-003119 | NCR | Door monitoring on insecure side |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2021-09-30 | 2021-10-01 08:26 | 1 | 2021-07-19 10:15 | Architectural - Doors | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | An observation was raised within Security Statement CRL1-XRL-O5-XST-CR001-50054 Rev 1.0, which highlighted concerns about door monitoring being on the insecure side of doors. This was raised again with current Security Consultant Peter Sinden, who has confirmed the need for corrective action. This issue has been identified on DSS Staircase 1 + 2, with doors affected including DS/D3/028, DS/D4/016, DS/D3/030, DS/D4/017, DS/D4/016, DS/D4/019, DS/D5/006. The issue is not confined to those doors listed, and further investigation from the contractor is required.
| 02SL - Stations (LUL) | Cxxx-NCR-003120 | NCR | S/1-044 Upper Concourse LO Line Diagram |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-12-05 | 2021-11-12 13:47 | -23 | 2021-10-06 13:05 | Architectural - Signage | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | S/1-044 Upper Concourse LO Line Diagram Wayfinding sign states: - Northbound platform 6 - Southbound platform 5 when it should state: - Northbound platform 5 - Southbound platform 6 Temporary solution for ISA-14 is to cover the platform numbers with vinyl patches while the sign is re-made.
| 02SL - Stations (LUL) | Cxxx-NCR-003121 | NCR | Fall Protection Asset Naming |  | Contr | VIN | WHI - Whitechapel Station (Central) |  | 2021-09-07 | 2021-08-16 13:34 | -22 | 2021-07-29 17:41 | Information Management - Asset Information | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | The naming used for the assets within “L4424 – Fall Protection System” at Whitechapel Station do not conform to the Naming Convention – “FALL PROTECTION [nnn]”. The word “SYSTEM” has been included in addition to the set naming convention. The labels maintain legibility and appropriate text size (see examples attached). Updating the Asset Name would require re-labelling, which is not considered feasible (given the access requirements to some of these assets) or necessary (as the Asset Names and labels are clear and understandable).
| 02SL - Stations (LUL) | Cxxx-NCR-003122 | NCR | GSM __ FCU Fan Bearing Failures |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-09-15 | 2021-11-11 11:41 | 57 | 2021-08-06 08:40 | Mechanical - Heating Ventilation & Air Conditioning | 2000 |  | Equipment Breakdown | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | All __ fan coil units located in the GSM are showing signs of bearing failure. Severity ranges from noisy to seizure of fan motors.
| 02SL - Stations (LUL) | Cxxx-NCR-003123 | NCR | DSS/4/FCU/03 & 04 to be altered for access and maintenance to filters |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2021-09-16 | 2021-10-22 15:10 | 36 | 2021-08-07 09:34 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Cxxx-NCR-003070 was previously raised due to clash in ESR room 4/666 between DSS/4/FCU/03 and the nearby SCADA cables/conduits. The location of the conduits prevents the FCU filter casing from being installed. The CMS relocation works have been complete and accepted, but DSS/4/FCU/03 & 04 require alteration for access and maintenance to filters
| 02SL - Stations (LUL) | Cxxx-NCR-003124 | NCR | Non Return Valves not installed to LPWM water main supplies |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-11-16 | 2021-11-22 16:13 | 6 | 2021-10-07 07:42 | Mechanical - Public Health Engineering | 4000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Design Problem - Not Defined | Completed |  | There are no Non Return Valves(NRV) installed on the water main pipework that supply the LPWM systems at DSS & GSM building.
| 02SL - Stations (LUL) | Cxxx-NCR-003125 | NCR | Interim Lighting Arrangement Court Street Bridge |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-12-24 | 2022-02-22 11:10 | 60 | 2021-11-09 11:59 | Electrical - Lighting | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | Lux Level Values utilising only the permanent lighting were not sufficient at ISA 14
| 02SL - Stations (LUL) | Cxxx-NCR-003126 | NCR | SR3 Glass / Panic Bar combo |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-09-29 | 2021-08-25 08:19 | -35 | 2021-08-20 08:30 | Architectural - Doors | 1500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | __ have installed doors with a combination of SR3 vision panels and push bars to the following 12 locations. - DS / D1/044 - CH / D1/004 - GS / D1/112 - SB / D1/008 - SB / D1/035 - SB / D1/036 - SB / D1/037 - SB / D1/038 - TP / D7/057 - TP / D7/058 - TP / D7/059 - TP / D7/060 While the separate components are both rated SR3, this combination is unable to be certified since it is possible to drill a pilot hole through the glass and ‘fish’ a cable to gain access via the pushbar.
| 02SL - Stations (LUL) | Cxxx-NCR-003128 | NCR | LULO - Platform 1 Lower Canopy / GSM CMS Below FCL |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-09-13 | 2021-11-23 17:26 | 71 | 2021-09-03 12:42 | Architectural - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | This NCR has been raised as requested in Cxxx-FCD-004337. On Platform 1 there is CMS that runs from the lower canopy in to the GSM. The CMS has been installed, and wired, below the FCL. The CMS cannot be raised as requested in the answer to Cxxx-FCD-004337 as the penetrations in the primary steelwork do not allow for this.
| 02SL - Stations (LUL) | Cxxx-NCR-003129 | NCR | LULO - LO Concourse Roof - Lack of offsite fabrication records for rooflights |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-10-24 | 2021-09-14 16:55 | -40 | 2021-09-14 12:10 | Architectural - Glazing | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | The rooflights were all pre-fabricated off-site as a series of units (85 No in total) comprising of a structural steel subframe, rooflight frame and glazing. __ Ltd procured all the components which were supplied to__ Ltd as follows: ·__ fabricated and supplied the steelwork sub-frame. · __ supplied the rooflight system frame and system components. · __ supplied the glass units. · __Ltd fabricated and installed the rooflight system into pre-fabricated units ready for delivery to site. There are no offsite fabrication records for the suppliers __ and __ Ltd.
| 02SL - Stations (LUL) | Cxxx-NCR-003130 | NCR | LULO - Mesh Screens M&D - Lack of offsite fabrication records |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-11-02 | 2021-09-29 08:14 | -34 | 2021-09-23 09:41 | Architectural - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Mesh screens M&D are located at both sides of Durward Street Bridge; screen M along the North side and screen D along the South side. These elements have been manufactured by supply chains __ and __ (__). __ undertook the fabrication of the majority of this scope while __ fabricated the elements around the doors at screen M location. __ ceased trading in 2019; their offsite assurance records available for this scope are Certificates of Conformity for the shot peening finish, N__ test for some of the steelwork frame and fabrication drawings. __ CE marking and Welding Certificate are available and in date at the time of fabrication of these elements. However, other relevant offsite assurance elements are missing; in example: Declaration of Performance, Job Cards and welding records, mill certificates, etc. Full sweep of offsite assurance records are available for the elements fabricated by __.
| 02SL - Stations (LUL) | Cxxx-NCR-003131 | NCR | CHS - Stair 42 drainage outlet |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-11-15 | 2021-11-26 16:21 | 11 | 2021-10-06 13:06 | Civil - Drainage | 3000 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 1. Reason for change = CHS level 1 Stair 42 slab slope doesn't take the water to the gully below the stair, water ponding has occurred onsite at the base of the stairs. A site survey was conducted and found that the ponding is due to high spots preventing water flowing towards to drainage outlet. 2. Clear outline of proposal = __ propose to locally break out high spots in the flooring and relay the flooring with __ A46 forming a V type channel towards to the drainage outlet. Localised build up with __ A46 will also be required in areas. __ propose for a V channel to be installed as per the mark up attached ‘V channel mark-up’ Areas to be unaffected and to remain as is include: • The doorway • The base of stairs • The perimeter of the room with exception to the northeast corner of the room. PT-123 coloured floor sealer Option B is to be applied to the floor finish surface at this location, in line with other areas in CHS with F7 floor type. Attachments: • Email: __ and BH email correspondence ‘FW: CHS – Stair 42 drainage outlet’ • Photo 1 • Photo 2 • Photo 3 • V channel mark-up 3. Cost & Programme impact = Additional cost for breaking and installing channel 4. Impact to follow-on / interfacing works = No impact 5. Evidence of acceptance of change from relevant party = Please see attached Cxxx-__PTR-9918 from BH
| 02SL - Stations (LUL) | Cxxx-NCR-003132 | NCR | DSS UPS Room - FCU Performance |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-11-16 | 2021-11-12 17:35 | -4 | 2021-10-07 12:04 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Equipment Breakdown | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | It has been noted that FCU4 located in DSS UPS room 4/614 has poor performance under certain scenarios. This has caused periods of high temperature within the room and alarms to be generated to SCADA related to high temperatures.
| 02SL - Stations (LUL) | Cxxx-NCR-003133 | NCR | LULO - HCDL ESS - Suspended Ceiling Drop 60mm Due to Clash with Services |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-12-01 | 2021-11-24 21:51 | -7 | 2021-10-22 13:56 | Architectural - Ceilings & Soffits | 2000 |  | Design | Rework | 4 (0.5-3k) | Complete | Previous Construction - Interfacing issues | Completed |  | It has been identified that there is a clash between the ceiling and electrical services outside the Stair 23 riser (See attached photo). This is preventing the ceiling from being installed in accordance with the design.
| 02SL - Stations (LUL) | Cxxx-NCR-003134 | NCR | DSS - Door DS/D1/048 - Raised Threshold |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2021-12-18 | 2022-01-05 08:45 | 18 | 2021-11-08 12:30 | Architectural - Doors | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | It has been noted that the raised threshold for door DS/D1/048 - located at the top of Stair 1 leading into the DSS service yard - presents a trip hazard. The door threshold design and levels are fixed and have been optioneered at earlier design stages to achieve security specifications, floor falls and weather protection. However, the raised threshold hasn't been clearly demarcated and/or signed for the end user(s).
| 02SL - Stations (LUL) | Cxxx-NCR-003135 | NCR | Fire Resistant Cable Equipment Allocation |  | Contr | VIN | WHI - Whitechapel Station (Central) |  | 2021-12-19 | 2021-11-16 13:40 | -33 | 2021-11-09 12:15 | Information Management - Asset Information | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | __ FTP120 and __ FP600S fire resistant cabling has been used on the project in various cores and sizes. Equipment IDs have been allocated to these assets (L746211 - Wiring cables), however in some cases, although the cable type/specification of the EQ ID is correct, an EQ ID for __ FTP120 cabling has been allocated to a __ FP600S cable.
| 02SL - Stations (LUL) | Cxxx-NCR-003136 | NCR | DSS South elevation doors closer not installed as per product literature |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-11-30 | 2022-02-08 18:05 | 70 | 2021-11-10 13:00 | Architectural - Doors | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | The __ closer system is not been installed as per product literature as a solution to resolve a clash with the slimline lock, because of this the __ closer is having issue and getting mal adjusted. Currently the door Co-ordinator has been installed differently to the product literature, the rail and the closer should be at same level, instead the rail is mounted on the frame and the closer box on the door leaving a 60mm gap between them, as a result the lever roller (actuator) does not make contact with the in-active door to realise the active door leaf. A solution need to be agree to resolve the issue.
| 02SL - Stations (LUL) | Cxxx-NCR-003137 | NCR | Platform 5 Drainage (LCR 3 and Lift 3 Lobby) |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-03-25 | 2022-01-23 20:53 | 304 | 2021-11-15 15:15 | Civil - Drainage | 6000 |  | Damaged | Rework | 3 (3-6k) | Complete | Personnel Error - Other human error | Completed |  | Drainage runs from Lift 3 Lobby and LCR 3 Manholes were investigated. - 4 out of the 5no. drainage runs from Lift 3 Lobby MH are blocked with solid material. - 3 out of the 5no. drainage runs from LCR 3 MH are blocked with solid material.
| 02SL - Stations (LUL) | Cxxx-NCR-003138 | NCR | LO: R12 Raised Walkway leak above XP2 (GL3-4 east) |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2022-01-18 | 2022-02-23 09:31 | 36 | 2021-12-09 15:26 | Architectural - General | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | It has been identified that there is water ingress through the R12 raised walkways above cross passage 2 (GL3-4). Cracks have been observed in the Contar resin at the joint of the precast planks.
| 02SL - Stations (LUL) | Cxxx-NCR-003140 | NCR | Cxxx Drainage outstanding CCTV surveys and Defects |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2022-06-10 | 2022-06-14 08:20 | 4 | 2021-12-19 20:00 | Civil - Drainage | 60000 |  | System Defect | Repair | 2 (6-60k) | Complete | External Phenomenon - Other | Completed |  | Within the attached Drainage CCTV status file, there remains a number of areas which require CCTV surveys to be carried out/clarified. In addition, there are a number of runs which require "repair". For the purpose of this NCR - Stair 25 can be ignored as it is already captured in Cxxx-NCR-003137 As per the Public Health Specification - JR12.3300 SYSTEM DESCRIPTIONS System Description, Functional Requirements and Interfaces j) Upon satisfactory completion of each phase of the installation, the Contractor shall provide the Client's representative with 2 complete sets of 'As Installed' drawings in Bentley Microstation format, O&M documentation including all test certificates) on CD, together with 2 copies of a CCTV survey of the completed installation. Any defects identified by the CCTV survey in the Clients representatives' opinion shall be rectified and the entire CCTV survey shall be repeated again, all at the Sub-Contractor's expense. JR12.1203 Cleaning Prior to final testing or CCTV inspection, remove all silt and debris by flushing entire installation with water. Repeat immediately before handover. Refer to Health and Safety Plan with respect of safe disposal of washings and detritus. Do not discharge into sewers or watercourses. JR12.1209 CCTV INSPECTION OF PIPES a) Application: Foul and surface water systems including drainage outfall to sewer b) Use CCTV equipment to undertake an internal inspection of pipes: record results. Provide all necessary equipment: provide experienced personnel to operate equipment and interpret results. Ensure adequate illumination within pipe(s). i) Record position and distance travelled continuously. ii) Take still photographs as instructed. iii) Provide copies of recordings: number of copies 5 iv) Provide covered area for viewing monitor. v) Obtain instructions as required to remedy defects recorded vi) Remedy defects. JR12.1214 CLOSED CIRCUIT TELEVISION SEWER SURVEY Scope of Work a) Before the below ground drainage is handed over, a CCTV survey shall be undertaken by the drainage contractor. Three copies of the survey DVD and report shall be presented to the Contractor for submission to the Project Manager. The scope of work shall include inspection of the drains/ sewers and associated manholes shown on the drawings so as to discover evidence of their structural and serviceable condition and locate all branches. The survey of the drains/ sewers shall be by colour closed circuit television.
| 02SL - Stations (LUL) | Cxxx-NCR-003141 | NCR | Lift 6 Level 2 Cosmetic Door Damage (CRL-OBS-35763) |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2021-12-29 | 2022-03-02 09:06 | 63 | 2021-12-22 10:27 | Civil - Civil Engineering General | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As per the attached photo and further to CRL-OBS-35763 it has been identified on the F54 Lift inspection that there is cosmetic damage to Lift 6 Level -2 (HCDL) doors. It is noted that the damage does not affect the safety of functionality of the lift or lift doors.
| 02SL - Stations (LUL) | Cxxx-NCR-003142 | NCR | LULO - Stair 24 Damaged Cladding |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2022-01-27 | 2022-01-27 17:34 | 0 | 2022-01-26 11:21 | Archaeology - General | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Prior to station opening it was identified that there were two damaged panels on Stair 24 that require replacing.
| 02SL - Stations (LUL) | Cxxx-NCR-003143 | NCR | Urban Realm - CHS Albion Yard - Curved Wall - Concrete Results Below Strength |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2022-03-15 | 2022-02-27 13:30 | -16 | 2022-02-03 14:36 | Civil - Structural Engineering | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The concrete test results obtained for the for the curved wall footing at CHS Albion yard at 56-days have been found below the design strength. The test results show a compressive strength of 30.2 N/mm² whereas de CAT II Design and Check Certificate document states a characteristic strength of the concrete of 40 N/mm².
| 02SL - Stations (LUL) | Cxxx-NCR-003144 | NCR | Pull Testing Calibration Certificate |  | Contr | VIN | WHI - Whitechapel Station (Central) |  | 2022-03-23 | 2022-02-11 20:20 | -40 | 2022-02-11 10:12 | Mechanical - Mechanical Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Calibration Certificate for pull testing equipment, and Competency Record for pull tester not provided with the Fire Main Construction Records: - Construction Records: GSM-HCDL platforms 1 & 2 CDFM fire main, Cxxx-__M-M-LRC-D061_WS106-50054
| 02SL - Stations (LUL) | Cxxx-NCR-003145 | NCR | Water leak above stair 23 |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2022-04-04 | 2022-03-31 08:57 | -4 | 2022-02-23 14:05 | Architectural - Roofing & Exterior Treatment | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | CRL-OBS-36002 was previously raised for a water leak from ceiling above stair 23 on route way leading to from HCDL platforms to platform 6 __ were requested to raise an NCR to propose how they would rectify the defect. Photographs are provided in the referenced OBS
| 02SL - Stations (LUL) | Cxxx-NCR-003146 | NCR | LULO - CLG-706/7 Panels not fully engaged in to C profiles |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2022-04-23 | 2022-03-24 13:51 | -30 | 2022-03-14 16:50 | Architectural - Ceilings & Soffits | 3000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 5no ceiling tiles on the HCDL canopy had become dislodged from the support frame during Storm Eunice. As a result the ceiling tiles were suspended from the safety lanyards and were moving around in the wind above the public. Station staff closed off the platform areas below the ceiling tiles while __ had them removed. __ mobilised to inspect all areas of HCDL canopy and investigate cause. A vertical pressure was applied to ceiling tile to check that the clip system is engaged. Approximately 4% of the ceiling tiles were identified as not engaged on the HCDL upper canopy.
| 02SL - Stations (LUL) | Cxxx-NCR-003147 | NCR | LULO - R12 walkway water ingress GL 3 - 4 |  | Contr | __M | WHI - Whitechapel Station (Central) |  | 2023-02-10 |  | -4 | 2022-05-13 10:07 | Architectural - Flooring | 500 |  | Design | Rework | 4 (0.5-3k) | Open |  | IMPLEMENTATION |  | On the 11/5/2022 there was water ingress between GL 3-4 on the lower concourse from the R12 walkway. An investigation is required for the cause of the leak.
| 02SL - Stations (LUL) | Cxxx-NCR-003148 | NCR | WHI - Defect Notice - Gas Suppression System |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2022-11-11 | 2022-10-31 09:25 | -11 | 2022-08-10 21:46 | Fire - Suppression | 6000 |  | System Defect | Rework | 3 (3-6k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | The Supervisor’s Representative issues this communication to formally notify the Contractor of the following Defects relating to the gas suppression system at Whitechapel Station: 1. A faulty gauge on one (1) gas bottle serving 3/811 was identified, preventing the end user from taking pressure readings. 2. The low pressure warning system for the gas suppression system serving 3/811 did not alert the main fire panel. 3. The gas suppression system serving 3/811 has activated in error on two (2) occasions on 31 May 22 and 04 July 22. In both instances, a station evacuation was initiated. 4. The gas suppression system serving 3/810 has activated in error on one (1) occasion on 23 July 22. This activation did not result in a station evacuation. 5. Various discrepancies with the type and quality of O-rings fitted to gauges. The Supervisor’s Representative notes the ongoing collaboration between the Project Manager, Contractor, Infrastructure Manager and supply chain to rectify the Defects.
| 02SL - Stations (LUL) | Cxxx-NCR-003150 | NCR | LULO - GSM - Hazard Marking for the Level 2 Plant Room Roller Shutter |  | Crossrail | XRL | WHI - Whitechapel Station (Central) |  | 2022-12-10 | 2022-10-31 11:46 | -40 | 2022-10-31 11:16 | Architectural - Signage | 2500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | The GSM Roller Shutter (SID: 2/783) can be operated automatically on operation of the fire alarm system. The operation roller shutter is an essential part of the station fire precautions. A Risk Assessment on the roller shutter was undertaken in March 2021 prior to the bringing into use (BIU) of the platform surrounding the GSM building. The risk assessment identified that a yellow hazard marking should be painted to the floor around the roller shutter as a visual aid and reminder to prevent materials from being stored in the area (thus preventing proper function of the roller shutter), or operatives from entering the hazard area without proper isolations in place. A temporary measure was implemented to enable the BIU of the platform area, however the permanent solution was not implemented.
| 03SR - Stations (RfL) | Cxxx-NCR-000044 | NCR | Pile Mat Material 6F2 |  | Contr | LAO | CUH - Custom House Station (East) |  | 2013-05-21 | 2013-05-21 16:32 | 0 | 2013-05-07 14:53 | Civil - Fill | 500 |  | Material | Reject |  | Complete |  | Completed |  | During a surveillance on 6F2 on 27/04/13 it was noted that from a random sample of the material there were a number of particles greater than 125mm. This means that the 6F2 is outside the limits set in the Department for Transport Specification for Highways Works Volume 1, Series 600
| 03SR - Stations (RfL) | Cxxx-NCR-000045 | NCR | Method Statement Briefing record |  | Contr | LAO | CUH - Custom House Station (East) |  | 2013-08-09 | 2013-08-23 15:13 | 14 | 2013-07-26 08:49 | Civil - Construction Health & Safety | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete |  | Completed |  | During a Method Statement Surveillance examination, a method statement briefing record was found not to be available. The method statement was Site Clearance and hoarding of eastbound DLR track Cxxx-LAO-C-GMS-CR145_WS157_1-50003.
| 03SR - Stations (RfL) | Cxxx-NCR-000046 | NCR | Piling Rig Breakdown |  | Contr | LAO | CUH - Custom House Station (East) |  | 2013-08-02 | 2013-08-23 15:15 | 21 | 2013-07-03 09:38 | Civil - Civil Engineering General | 500 |  | Equipment Breakdown | Rework | 4 (0.5-3k) | Complete |  | Completed |  | Whilst piling location P620 the flexible hose became detached from the swan neck component part of the rig. There is no defect remaining on site. The partly formed pile was bored away and a new pile installed 1 meter deeper at the same position. the non conformance was purely related to the piling rig and the way it was set up.
| 03SR - Stations (RfL) | Cxxx-NCR-000048 | NCR | Pile P66 Cage Reinforcement Installed Too Low |  | Contr | LOS | CUH - Custom House Station (East) |  | 2013-09-16 | 2013-09-04 09:57 | -12 | 2013-08-08 11:33 | Civil - Geotechnical Engineering | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The top of the pile cage reinforcement for P66, a 450mm diameter pile, was to be installed to piling platform level of 102.2m to achieve the levels as per the __ pile schedule and tolerances as per the KP10 pile specification. The cage was placed in the bore which was filled with concrete by pushing it in to the wet concrete. Once the level was checked by the setting out engineer at the design level it was concluded that the cage was sinking under its one self weight. The engineer instructed one of the piling operatives to lock the level of the pile cage off using a length of bar. The locking off bar was not tied securely enough. The pile was not rechecked a short duration after it was locked off and the cage continued to sink under its one self weight. An as built was taken of the pile the following day and it was concluded that the pile had sunk to -60mm below its design position and therefore was 10mm lower that the permitted tolerance of +150mm / -50mm. The engineer had set the pile in the bore to the design level. The defect resulted because of the reinforcement sinking under its own self weight. The design tolerances were not used to full effect to ensure the cage levels remained within tolerance.
| 03SR - Stations (RfL) | Cxxx-NCR-000049 | NCR | NCR Pile P140 PIle Bore Too Short |  | Contr | LOS | CUH - Custom House Station (East) |  | 2013-10-14 | 2013-10-24 16:09 | 10 | 2013-08-08 12:24 | Civil - Geotechnical Engineering | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Pile P140 was to be constructed to a design bore length of 24.2m. The pile was constructed to a bore of 22.7m, 1.5m too short.
| 03SR - Stations (RfL) | Cxxx-NCR-000050 | NCR | Incorrect Pile Diameters Installed for Piles P98, P106, P109 & P114 |  | Contr | LOS | CUH - Custom House Station (East) |  | 2013-08-30 | 2013-09-09 09:44 | 10 | 2013-08-16 11:53 | Civil - Geotechnical Engineering | 2000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Four piles were constructed to an appproved __ design that increased the diameter of the pile from 600mmQ as detailed on the __ schedules to 750mmQ. NCR arises due to a lack of timely communication of the desgin change. __ were not informed of this change prior to construction of these piles. __ have design responsibility for the pile desgin.
| 03SR - Stations (RfL) | Cxxx-NCR-000051 | NCR | Pile P85 Slumped 3.7M |  | Contr | LOS | CUH - Custom House Station (East) |  | 2013-12-01 | 2013-09-23 15:50 | -69 | 2013-08-20 10:39 | Civil - Geotechnical Engineering | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Pile P85 slumped 3.7m while constructing pile P87. The top section of this pile was back filled with earth and not concrete.
| 03SR - Stations (RfL) | Cxxx-NCR-000052 | NCR | Use of unapproved concrete mix for piling works |  | Crossrail | XRL | CUH - Custom House Station (East) |  | 2013-10-14 | 2013-10-10 15:38 | -4 | 2013-10-03 13:23 | Civil - Geotechnical Engineering | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | It has been identified that concrete mix with 10mm aggregate used by the contractor for piling works has not been formally submitted under an MCR and accepted by CRL.
| 03SR - Stations (RfL) | Cxxx-NCR-000053 | NCR | Works on site proceeding without accepted pile reinforcement cage drawings |  | Crossrail | XRL | CUH - Custom House Station (East) |  | 2013-10-10 | 2013-10-09 16:05 | -1 | 2013-10-04 11:56 | Civil - Geotechnical Engineering | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | First issue of pile reinforcement cage drawings for cages A,B,C,D,G have been coded 3. The updated drawings have not been formally issued by contractor on eB for formal acceptance for CRL despite the works proceeding on site. Drawings which require submnission are : Cxxx-LAO-C-DWG-CR145_WS157_1-500104 Cxxx-LAO-C-DWG-CR145_WS157_1-500105 Cxxx-LAO-C-DWG-CR145_WS157_1-500106 Cxxx-LAO-C-DWG-CR145_WS157_1-500107 Cxxx-LAO-C-DWG-CR145_WS157_1-500110
| 03SR - Stations (RfL) | Cxxx-NCR-000054 | NCR | TW design for piling cages (lifting details) not submitted for CRL acceptance |  | Crossrail | XRL | CUH - Custom House Station (East) |  | 2013-10-18 | 2013-10-14 14:49 | -4 | 2013-10-11 09:37 | Civil - Geotechnical Engineering | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | The contractor did not follow the approved ITP for piling works (ITP ref. Cxxx-LAO-C-ITP-CR145_WS157_1-50006 rev. 04). Item 6 of the ITP requires the TW design for piling cages (lifting details) to be submitted to CRL (hold point). The design and design checks were carried out by the contractor prior to the works starting on site but the document has not been issued to CRL.
| 03SR - Stations (RfL) | Cxxx-NCR-000055 | NCR | Pile cage bars cut off at southern foundation for temporary bridge |  | Crossrail | XRL | CUH - Custom House Station (East) |  | 2014-01-15 | 2014-01-10 15:08 | -5 | 2013-10-23 14:45 | Civil - Civil Engineering General | 2000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | During installation of the reinforcement for temporary bridge (southern foundation) the contractor identified that there was a clash between reinforcement cage and holding down anchor plates. The contractor contacted the designer to obtain confirmation if reinforcement bars clashing with the holding down anchor plates could be cut off. Email confirmation was obtained that this was acceptable. Refer to email from __ to __ dated 24/09/13 @ 13:40 (attached). During the pre-pour inspection carried out by Cross Rail (__) it was identified that 4no. bars were cut off instead of 3no. (eastern pile). Verbal confirmation from contractors engineer was obtained that this was checked by the designer and would be formally confirmed by him the following day. On this basis the pre-pour inspection was signed off by Cross Rail on 02/10/13. 'IRF_051' pre-pour inspection records attached for reference. As of 23/10/13 no confirmation has been presented to Cross Rail that the design change introduced on site has been approved by the designer. Note: The design for temporary bridge foundation and piling has been carried out by the contractor’s designer.
| 03SR - Stations (RfL) | Cxxx-NCR-000056 | NCR | Exposed blinding rebar pins protruding into pile cap concrete |  | Crossrail | XRL | CUH - Custom House Station (East) |  | 2014-01-31 | 2014-02-14 08:27 | 14 | 2013-10-25 15:18 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During site inspection carried out on 25/10/13 Crossrail have identified a few exposed blinding rebar pins protruding into pile cap concrete (PC-7 and PC-8). Please see attached photo. This suggests that the carpenters were using pins inside the formwork for fixing purposes. As there is no concrete cover on these exposed pins this could decrease the concrete durability in the pile caps.
| 03SR - Stations (RfL) | Cxxx-NCR-000057 | NCR | Lack of notifications for witness points at __ |  | Crossrail | XRL | CUH - Custom House Station (East) |  | 2014-01-07 | 2013-12-18 09:40 | -20 | 2013-10-25 15:56 | Civil - Civil Engineering General | 1000 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Crossrail note that as of 18/10/13 series of precast concrete elements were fabricated but no Inspection Request Form was raised to Crossrail for witnessing pre-pour inspections as required by the accepted ITPs. Notification status as of 18/10/13 was as follows: Ground beams (1 out of 16 notified) 1427A-1APL70-005 – not notified 1427A-1APL70-006 – notified 1427A-1APL70-007 – not notified 1427A-1APL70-008 – not notified 1427A-1APL70-009 – not notified 1427A-1APL70-010 – not notified 1427A-1APL70-011 – not notified 1427A-1APL70-012 – not notified 1427A-1APL70-013 – not notified 1427A-1APL70-014 – not notified 1427A-1APL70-015 – not notified 1427A-1APL70-016 – not notified 1427A-1APL70-017 – not notified 1427A-1APL70-018 – not notified 1427A-1APL70-019 – not notified 1427A-1APL70-020 – not notified Platform slabs (1 out of 16 notified) 1427A-1APL62-006 – not notified 1427A-1APL62-007 – not notified 1427A-1APL62-008 – not notified 1427A-1APL62-009 – not notified 1427A-1APL62-010 – not notified 1427A-1APL62-011 – not notified 1427A-1APL62-012 – not notified 1427A-1APL62-013 – not notified 1427A-1APL62-014 – not notified 1427A-1APL62-015 – not notified 1427A-1APL62-016 – not notified 1427A-1APL62-017 – not notified 1427A-1APL62-019 – not notified 1427A-1APL62-020 – notified 1427A-1APL62-022 – not notified 1427A-1APL62-023 – not notified Single height column (1 out of 6 notified) 1427A-1APL69-001 – not notified 1427A-1APL69-002 – not notified 1427A-1APL69-003 – not notified 1427A-1APL69-004 – not notified 1427A-1APL69-005 – notified 1427A-1APL69-006 – not notified Mezzanine beams (3 out of 4 notified): 1427A-1AML74-401 –notified 1427A-1AML68-302 –notified 1427A-1AML68-303 – not notified 1427A-1ACL68-503 – notified
| 03SR - Stations (RfL) | Cxxx-NCR-000058 | NCR | Column 1427A-1APL69-009 not offered for CRL pre-pour inspection |  | Crossrail | XRL | CUH - Custom House Station (East) |  | 2014-01-07 | 2013-12-18 09:42 | -20 | 2013-11-01 14:20 | Civil - Civil Engineering General | 1000 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | On 21/10/13 __ raised an inspection request form ref. Cxxx-LAO-C-IRF-CR145_EIP02 offering column ref. 1427A-1APL69-009 for pre-pour inspection on 31/10/13. Crossrail (Piotr Swieboda) confirmed that they will carry out the inspection as scheduled. On 30/10/13 __ informed Crossrail that the column no. 09 was already cast without giving Crossrail the opportunity to witness the works as stated in current ITP. Instead of column no. 09 column no. 010 was offered for innspection by __.
| 03SR - Stations (RfL) | Cxxx-NCR-000059 | NCR | Honeycombing and cracks on precast beam 1427A-1APL70-018 |  | Crossrail | XRL | CUH - Custom House Station (East) |  | 2014-02-28 | 2014-02-28 20:06 | 0 | 2013-11-19 11:32 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During inspection at __ pre-cast fabrication shop on 05/11/13, Crossrail have identified that one of the beam elements cast has honeycombing and visible cracks on top of the beam. They do not look like shrinkage cracks as suggested by the site team. Photos attached.
| 03SR - Stations (RfL) | Cxxx-NCR-000060 | NCR | Rust on underside of baseplates for precast column 1427A-1APL69-006 |  | Crossrail | XRL | CUH - Custom House Station (East) |  | 2014-02-28 | 2014-02-28 20:03 | 0 | 2013-11-19 11:57 | Civil - Civil Engineering General | 2500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Rust has been noted on underside of galvanised baseplates for precast column 1427A-1APL69-006. Contractor to investigate further and introduce a physical check at __ yard to ensure there is no rusting on other baseplates.
| 03SR - Stations (RfL) | Cxxx-NCR-000061 | NCR | North VDR Wall Strip Foundation - Incorrect size of U-bars |  | Crossrail | XRL | CUH - Custom House Station (East) |  | 2013-12-25 | 2014-01-08 13:09 | 14 | 2013-11-25 10:47 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the notified pre-pour inspection on 22/11/2013 for North VDR Wall Strip Foundation at GL 2a-4a Crossrail identified that the cover at the upstand was ~40mm instead of 50mm specified. It had been discovered that the size of U-bars, although as per the contractor’s design, was incorrect in order to achieve the required cover i.e. U-bars width 110mm + 50mm cover + 50mm cover = 210mm, whereas the specified thickness of upstand wall was 200mm. Refer to contractor’s reinforcement drawing ref. Cxxx-LAO-S-DWG-CR145_Ws157_1-50045 rev. C03, section 2, BM 90(a-n).
| 03SR - Stations (RfL) | Cxxx-NCR-000062 | NCR | VDR upstand concrete cast short |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-02-28 | 2014-02-26 15:24 | -2 | 2013-11-29 17:19 | Structural Engineering - Reinforcement | 1200 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Concrete fininshes along the upstand area of the VDR show exposed rebar in some areas. This have been caused by difference in levels from the way VDR strip foundation and track slab design to form.See attached sketch showing affected area
| 03SR - Stations (RfL) | Cxxx-NCR-000063 | NCR | Welded steelwork fabrications for pre-cast concrete components |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-02-01 | 2014-01-28 08:42 | -4 | 2013-12-09 10:55 | Structural Engineering - Welding | 3000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | There are a significant number of fabricated steelwork components cast within the precast concrete elements being produced by __ Manufacturing. The entries in the Inspection and Test Plans for the individual elements (columns, beams etc.) do not provide either a sufficient level of detail or identify the deliverable records. At present there is no separate Inspection and Test Pan for the steel fabrication and welding works being carried out. Despite the above not being in place __ Manufacturing are procuring and installing fabricated steel components within pre-cast concrete units.
| 03SR - Stations (RfL) | Cxxx-NCR-000064 | NCR | South Track slab upstand concrete finish |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-03-18 | 2014-03-20 09:59 | 2 | 2013-12-09 15:43 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following striking of Formwork, grout loss and rust were observed on surface of South Track slab upstand at the following locations: Grid line 1A+1- 2 1/2/AF- Photos attached Grid line 3A+1/AF- Photos attached Drawing attached-Showing extent of grout loss
| 03SR - Stations (RfL) | Cxxx-NCR-000065 | NCR | Lack of Notification of witness points |  | Crossrail | XRL | CUH - Custom House Station (East) |  | 2014-01-09 | 2014-01-13 14:47 | 4 | 2013-12-10 11:27 | Electrical - LV Equipment | 700 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Failure to issue IRF's for 4 line items (3.1,3.2,3.3,3.4) on ITP Cxxx-LAO-E-ITP-CR145_WS157-50010 Rev 1
| 03SR - Stations (RfL) | Cxxx-NCR-000067 | NCR | VDR strip Foundation-Incorrect Torsion link |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-01-10 | 2014-01-10 10:31 | 0 | 2013-12-18 15:42 | Structural Engineering - Reinforcement | 1000 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Drawing Reference 50001 & 50045 At grid line 1A-4A VDR strip foundation, outer torsion links installed were not shape code 63, As agreed with the designer additional links were added and fixed to the non- conforming links in order to have equivalent torsion links design load. See attached designer response-RFI No 271.As built drawing and photos attached Root Cause: New revision of Reinforcement Design Intent issued which requires torsional links in VDR strip foundation instead of normal links
| 03SR - Stations (RfL) | Cxxx-NCR-000069 | NCR | Materials Compliance Record |  | Crossrail | XRL | CUH - Custom House Station (East) |  | 2014-03-10 | 2014-03-03 14:28 | -7 | 2014-01-27 16:06 | Materials - Approval | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | The MCR for concrete design mix C, Cxxx-LAO-C-LRC-CR145_WS157_1-50026 Rev 1 was found to be Decal 2 reviewed 23/07/13 “Not accepted. Revise and resubmit. Work may proceed subject to incorporation of changes indicated”.. The Contractor has had a reasonable time to comply with comments on the MCR reviewed by the PFE.
| 03SR - Stations (RfL) | Cxxx-NCR-000070 | NCR | Drainage and Ducts drawings |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-02-13 | 2014-02-13 14:14 | 0 | 2014-01-30 15:27 | Civil - Drainage | 3000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Following updated drainage and duct drawings are not available for Crossrail to check and approve design and installation prior to the commencement of the work at grid line 1A-4A. Cxxx-LAO-D-DDA-CR145_2-72010- Below Ground Drainage Cxxx-LAO-D-DDA-CR145_2-72011- Below Ground Drainage Cxxx-LAO-D-DDA-CR145_2-72012- Below Ground Drainage Cxxx-LAO-D-DDA-CR145_2-72013- Below Ground Drainage Cxxx-LAO-E-DDA-CR145-62601-Combined Electrical Services Cxxx-LAO-E-DDA-CR145-62602-Combined Electrical Services Cxxx-LAO-E-DDA-CR145-62603-Combined Electrical Services Cxxx-LAO-E-DDA-CR145-62604-Combined Electrical Services NCR- Cores for LV ducts in LV pit- Grid line 3A In Cxxx/610 LV duct interface meeting with Neville Leary, Rakesh OZA & David Bigg, alternative LV cable rouble was agreed due to the size of the cable and the 180 degree turn back required out of the pit. As LV pit already constructed in VDR foundation, core holes are required for LV cable ducts through concrete pit wall,the ducts are going into the pit from the South and then taking a straight route to the pit in the undercroft. Please find attached sketch detailing cored holes for the LV cables through the LV pit in the VDR foundation Could you please confirm if it is acceptable to core the pit as per attached sketch. Core holes for LV cables through the LV pit in the VDR foundation completed and duct installed- See attached photos
| 03SR - Stations (RfL) | Cxxx-NCR-000071 | NCR | self certification was not fully place |  | Crossrail | PDP | CUH - Custom House Station (East) |  | 2014-05-22 | 2014-05-16 15:07 | -6 | 2014-02-11 11:50 | Structural Engineering - Pre-cast | 3000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | The Contactor could not fully meet the requirements of Work Information volume 2 B clause 13.2 for progressive assurance as the following could not be demonstrated: 1) That weld test frequency was in line with production quantities 2) That the welding equipment was calibrated 3) That the reinforcement mill certification was traceable to the steel used , a requirement of BS4449 4) That the steel base plate certification was traceable
| 03SR - Stations (RfL) | Cxxx-NCR-000072 | NCR | Concrete batching plant calibration |  | Crossrail | PDP | CUH - Custom House Station (East) |  | 2014-07-25 | 2014-07-15 08:48 | -10 | 2014-02-11 12:11 | Structural Engineering - Pre-cast | 1500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The Works Information volume 2B part 20.8 states “The Contractor shall maintain a schedule of all inspection, measuring and test equipment used for the works that includes records of the calibration of such Equipment to nationally recognised standards”. QSRMC Quality and Product Conformity Regulations (who are a nationally recognised certification body for concrete production) 2003 Issue 1 Rev 4 clause 2.3.1 states that “all weighing and measuring equipment shall be tested and calibrated, over its full working range by a relevant specialist, every three months and immediately following any modification or repair that could have effected its accuracy". The calibration records for the on-site batching plant which were provided by the Contractor for post surveillance review were dated 9th August 2013, more than 5 months old and as such do not meet the above requirements.
| 03SR - Stations (RfL) | Cxxx-NCR-000073 | NCR | Acceptance status of records and documentation |  | Crossrail | PDP | CUH - Custom House Station (East) |  | 2014-02-25 | 2014-02-21 09:54 | -4 | 2014-02-11 12:18 | Structural Engineering - Pre-cast | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Document Control Procedure CRL1-XRL-Z3-GPD-CR001-50001 Rev.2.0 clause 7.3 could not be verified by the contractor with respect to the acceptance of the following documents: 1. Cxxx-LAO-C-ITP-CR145_WS157_1-50056 ITP (Columns) 2. MCR’s for concrete mix designs 1530 and 1235V 3. Mock ups The __ team do not have access to eB or the current CMDL and the ability to check the acceptance status of documents they are producing; this is always confirmed via email/ telephone. Works Information volume 2B clause 14.7.2 requires that “The decal label shall be applied by the Contractor on the front cover of all deliverables. The following Project Manager’s acceptance status of all deliverables shall be recorded by the Contractor on the CMDL.” Without access to eB or the CMDL the Contactor could not demonstrate that documentation was current as required by clause 13.2 of the Works Information volume 2B
| 03SR - Stations (RfL) | Cxxx-NCR-000074 | NCR | Undertaking repairs to concrete and galvanising without an accepted repair procedure/ technical details |  | Crossrail | PDP | CUH - Custom House Station (East) |  | 2014-03-25 | 2014-03-24 11:40 | -1 | 2014-02-11 12:23 | Structural Engineering - Pre-cast | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Structural Specification KF10 – Concrete Cxxx-LAO-C-RSP-CR145_WS157_1-5002 Rev 5 clause 2107 states “Method Statements shall be prepared and submitted to the Project Manager for acceptance prior to commencing any work” and “shall contain full details of matters detailed in this specification and of the following where appropriate, ix) proposals for making good”. The Contractor had already commenced producing pre-cast elements for Cxxx works. It was confirmed that some of these elements had undergone repair to the Contractors internal repair procedure. This procedure has not been accepted by Crossrail and it was confirmed that there were on-going trials between the Contractor and Crossrail to determine and agree acceptable repairs. In addition to this the repair information with respect to NCR Cxxx-NCR-000060 on the subject of corrosion of galvanised embedment failed to include the repair material technical data sheet and as such it remains unknown if the requirements EN ISO 12944 part 5:2007 for zinc rich paints were complied with.
| 03SR - Stations (RfL) | Cxxx-NCR-000075 | NCR | Commencement of Pre-cast works without accepted records |  | Crossrail | PDP | CUH - Custom House Station (East) |  | 2014-06-01 | 2014-05-16 16:34 | -16 | 2014-02-11 12:27 | Structural Engineering - Pre-cast | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Structural Specification KF10 – Concrete Cxxx-LAO-C-RSP-CR145_WS157_1-5002 Rev 5 clause 2106 trial sections states “the Contractor shall submit details of the trial sections for the acceptance of the Project Manager..” and Works Information Vol 2B part 20.7 states “The Contractor shall provide representative samples of proposed manufactured items, mock-ups/ prototypes/benchmarks of proposed fabricated or constructed items, and test panels of standard finishes, including concrete, to be achieved during construction as required by the drawings and materials and workmanship specifications in Part 2 of Volume 2C of the Works Information and applicable drawings or materials and workmanship specifications produced by the Contractor as part of his design obligations”. As detailed in finding 3, the Contractors team at __ had already commenced production of pre-cast elements for Cxxx works. On post visit review of the Mock up documentation acceptance status it was found that the following document Cxxx-LAO-C-LRC-CR145_WS157_1-50035 – double height column has been Code 2 since Aug 2012.
| 03SR - Stations (RfL) | Cxxx-NCR-000076 | NCR | OHLE bolts |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-06-01 | 2014-06-10 08:16 | 9 | 2014-02-18 12:02 | Structural Engineering - Bolted Connections | 5000 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Holding down bolts located at GL2A & 5A-6A for OHLE mast in the VDR foundation are worng size. The bolts cast are 36 dia instead of specified 42mm. (Highlighted drawing showing location of affected mast bolts)
| 03SR - Stations (RfL) | Cxxx-NCR-000077 | NCR | Pile Testing - Pile Integrity Testing |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-03-15 | 2014-03-11 16:52 | -4 | 2014-02-19 16:05 | Geotechnical Engineering - Geotechnical Engineering - General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | Regarding Integrity testing Of Piles. RFI’ 000134 & 000048 refer (attached) We have currently installed 478 No. Contract Piles. Current Integrity Test Numbers are: Formation Level Integrity Tests: 42 35 No. Tested outside 21 Day old window Cut Off Level Integrity Tests: 142. All are outside 21 day old window.
| 03SR - Stations (RfL) | Cxxx-NCR-000078 | NCR | Cracks on Pile Cap surface PC 10 & PC 2 GL5A |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-04-14 | 2014-03-18 16:49 | -27 | 2014-02-20 09:34 | Structural Engineering - Concrete Member | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Plastic shrinkage cracks (1-3mm) on surface of 2no Pile Caps along gridline 5A/AG/AF.
| 03SR - Stations (RfL) | Cxxx-NCR-000079 | NCR | Rust on underside of baseplates for precast columns - further to Cxxx-NCR-000060 |  | Crossrail | XRL | CUH - Custom House Station (East) |  | 2014-03-26 | 2014-03-31 08:56 | 5 | 2014-02-24 15:50 | Civil - Civil Engineering General | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Further to NCR ref. Cxxx-NCR-000060 rust has been identified on other column baseplates (despite the fact they were galvanised). The NCR 60 covers only element number 1427A-1APL69-006. The Contractor is to list all the other baseplates which have been identified as defective and propose remedial action.
| 03SR - Stations (RfL) | Cxxx-NCR-000080 | NCR | PCC Element 1APL62-007 - Displaced U-bars |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-04-12 | 2014-04-11 16:58 | -1 | 2014-02-26 16:10 | Structural Engineering - Concrete Member | 800 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During manufacture of platform slab 1APL62-007 stitch reinforcement the loose U-bars were not sufficently tied. Subsequently, when the concrete was placed, the U-bars rotated. Refer to attached NCR from __ Manufacturing 1427A-NCR-001 (7403)
| 03SR - Stations (RfL) | Cxxx-NCR-000081 | NCR | PCC Element 1AML74-401 - Well voids displaced |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-05-02 | 2014-04-28 14:40 | -4 | 2014-02-26 16:28 | Structural Engineering - Concrete Member | 2000 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During construction of the cross beam the top strops were not significantly bolted to the mould, subsequently some of the top well voids have moved by up to 20mm. One of the bottom well voids has moved out by 18mm. This has occured due to the movement at the top. See attached __ Manufacturing NCR 1427A-NCR-004 (7356). --------------------------------------------------------------------------------------------------- Reinforcement cut as per attachment '1427A-1AML74-401 - Reinforcement cut information'. Review of structural integrity required. --------------------------------------------------------------------------------------------------------------------- 14/04/14 - Refer to attached email from __ Manufacturing confirming the diamater of the bars cut and identifying the reason for these bar being present.
| 03SR - Stations (RfL) | Cxxx-NCR-000082 | NCR | PCC Element 1AML68-303 - Bottom corner of unit out of dimensional tolerance |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-05-12 | 2014-04-28 14:48 | -14 | 2014-02-26 17:10 | Structural Engineering - Concrete Member | 1000 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The bottom length of unit 1AML68-303 is long by 15mm. See attachment showing __ Manufacturing NCR 1427A-NCR-005 (7358) and associated as-built survey. The unit should measure 8671mm. The top of the element complies with a measurement of 8672mm; however the bottom length measurement is 8686mm. The element is 10mm out of tolerance accordign to the +/- 5mmspecification in the general notes sheet 1 of 3 for beams ranging 6-10m.
| 03SR - Stations (RfL) | Cxxx-NCR-000083 | NCR | PCC Element 1ALL68-503 - Dimensional tolerance and well voids |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-05-12 | 2014-04-14 11:01 | -28 | 2014-02-26 17:44 | Structural Engineering - Concrete Member | 1500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The length of unit is short by 14mm. Please see attached as built of element. The unit should measure 9524 but is 9510mm. Issue 1-Architectural: The element is out of tolerance by 10mm according to the +/-5mm specification in the general notes sheet 1 of 3 for beams ranging 6-10m. Issue 2 – Structural: The well voids have been set out correctly but in relation to the ends, but as the overall unit is short by 14mm the well voids on either end of the beam will be out of design location by 7mm. Refer to attached __ Manufacturign NCR 1427A-NCR-006 (7375) --------------------------------------------------------------------------------------------------- Reinforcement cut as per attachment '1427A-1ACL68-503 - Reinforcement cut information'. Review of structural integrity required.
| 03SR - Stations (RfL) | Cxxx-NCR-000085 | NCR | PCC Element 1ACL68-507 - Well voids filled with concrete |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-05-02 | 2014-04-14 11:00 | -18 | 2014-02-27 07:51 | Structural Engineering - Concrete Member | 1500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the construction of beam 1ACL68-507, the well voids have become blocked with concrete. The concrete has now been effectively removed however one of the top well voids is out of place (by up to 27mm). This has occurred due to well void sitting on a magnet which has moved out of place during the cast. Refer to attached __ Manufacturing NCR 1427A-NCR-012 (7500). --------------------------------------------------------------------- Reinforcement cut as per attachment '1427A-1ACL68-507 - Reinforcement cut information'. Review of structural integrity required.
| 03SR - Stations (RfL) | Cxxx-NCR-000086 | NCR | PCC Element 1ACL68-506 - Well void out of position |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-03-27 | 2014-04-15 11:14 | 19 | 2014-02-27 07:57 | Structural Engineering - Concrete Member | 1500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During construction of the concourse beam the top well voids have moved out of place by up to 19mm. (x=19,y=15) This has occurred due to the well void sitting on a magnet which has moved out of place during the cast. Refer to attached __ Manufacturign NCR 1427A-NCR-016 (7555) --------------------------------------------------------------------------------------------------- Reinforcement cut as per attachment '1427A-1ACL68-506 - Reinforcement cut information'. Review of structural integrity required.
| 03SR - Stations (RfL) | Cxxx-NCR-000087 | NCR | PCC Elements 1427A-1CPL69-019, 1427A-1CPL69-022 - Temporary works couplers missing |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-05-28 | 2014-05-15 15:41 | -13 | 2014-02-27 08:23 | Structural Engineering - Concrete Member | 9000 |  | Design | Use As-Is | 2 (6-60k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | There was an error during the design phase of the two double height columns (1427A-1CPL69-019, 1427A-1CPL69-022. They have both been designed without couplers at the mezzanine level. These would have been required to take the temporary lattice angle brackets. Refer to attached NCR 1427A-NCR-017
| 03SR - Stations (RfL) | Cxxx-NCR-000088 | NCR | Pile concrete damaged |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-03-13 | 2014-03-11 10:38 | -2 | 2014-02-27 12:40 | Civil - Excavation | 800 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 2 No Pile P565 & P566 pile head side concrete damaged during track slab excavation activity. No damage to rebar-see attached images.
| 03SR - Stations (RfL) | Cxxx-NCR-000089 | NCR | Damage to IP rated fittings |  | Crossrail | XRL | CUH - Custom House Station (East) |  | 2014-05-01 | 2014-05-01 16:13 | 0 | 2014-03-03 09:47 | Electrical - Lighting | 2000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Following the GROF that was raised on the 23rd January 2014 stating that there was water ingress to the IP rated light fittings installed on the temporary footbridge and stairs, it has now been discovered that the light fittings have been drilled to allow the water out, this contradicts the IP rating of the fittings and is against BS7671 IET Wiring regulations
| 03SR - Stations (RfL) | Cxxx-NCR-000090 | NCR | __ Concrete Mixes - Greater than 15% variance in 28 day cube results |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-04-25 | 2014-04-04 10:44 | -21 | 2014-03-11 09:54 | Structural Engineering - Concrete Member | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The initial set of concrete test cube results for the __ Manufacturing concrete mixes CM-2000, CM-1235, CM-1518 and CM1530 show some variances in the individual 28 day cube results of greater than the 15% allowance in BS EN 206.
| 03SR - Stations (RfL) | Cxxx-NCR-000091 | NCR | Insufficient thread protruding in holding down bolts columns 001 and 002 |  | Contr | LOS | CUH - Custom House Station (East) |  | 2014-03-31 | 2014-03-13 09:01 | -18 | 2014-03-10 17:27 | Civil - Structural Engineering | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 1no bolt in column 001 and 3no bolts in column 002 baseplates have insufficient thread protruding from the nut as per NSSS requirements. See attached marked up drawings and photos.
| 03SR - Stations (RfL) | Cxxx-NCR-000093 | NCR | Well voids out of positional tolerance in GL2A pile cap |  | Contr | LOS | CUH - Custom House Station (East) |  | 2014-05-26 | 2014-05-23 11:52 | -3 | 2014-03-12 16:53 | Civil - Structural Engineering | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The well voids in the pile caps at GL2A that tie in platform beams 005 and 008 are out of positional tolerance - Please see attached as built sketch. the positions of the well voids means we are unable to insert the correct dowel bars through the beam ends into the pile caps. Beam 008:- original design is for 4no 25mm dia bars. See attached email from __ confirming that at Beam 005, we can install 2no 40mm dia bars in 2no well voids and leave the other 2no well voids empty. Beam 005:- Original design is for 2no 40mm dia bars, the beam has been moved 20mm to the west to accomodate these bars. (10mm over the allowable positional tolerance of the precast) We would need to move it a similar amount to accomodate the alternative bar arrangment suggested by __. the beam's position in the north-south direction is within the 10mm tolerance. Beams 001 and 004 will also be affected by well voids being out of position however this will be covered by a separate NCR or FCD.
| 03SR - Stations (RfL) | Cxxx-NCR-000094 | NCR | PCC Element - 1427A-1APL69-002 - Column concrete finish |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-11-26 | 2014-11-05 12:47 | -21 | 2014-03-11 10:37 | Architectural - Finishes | 800 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The architectural concrete finish to column unit 1427A-1APL69-002 (column on grid 2A/AF) is not to the required standard as set by the agreed benchmarks. Items to address: - Chip to South face at top is not sufficiently well repaired and does not blend well with surrounding concrete - Small dots in vertical line to centreline of South face have not been well finished compared to other column units - Rectangular blanking plate on South face at approx. 2/3 height for conduits currently stands out and requires finishing to blend in Refer to attached markup highlighting areas for re-work.
| 03SR - Stations (RfL) | Cxxx-NCR-000095 | NCR | PCC Element - 1427A-1APL69-001 - Concrete finish |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-04-15 | 2014-03-13 09:04 | -33 | 2014-03-11 10:54 | Architectural - Finishes | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Precst concrete column 1427A-1APL69-001 (grid 2A/AG) has marbling in the concrete finish on the bottom half of the column - refer to attached photo.
| 03SR - Stations (RfL) | Cxxx-NCR-000096 | NCR | P335E - Unable to plunge reinforcement cage to correct level. |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-05-28 | 2014-05-02 10:48 | -26 | 2014-03-13 17:09 | Geotechnical Engineering - Concrete - Bored Pile | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the course of CFA piling on 11th March, Pile P335E was being constructed sixth in the sequence of eight piles for the day. The site team could not plunge the cage to the required level. Target TOS level is +102.3mAOD but the cage refused at TOS level of +103.2mAOD. This means that the threaded bar ends to accommodate the __ D14 occur 0.9m higher than they should for incorporating into the VDR Wall Ground Beam. The Central tension bar was able to be plunged to the required level. The time between batch time for that load and the completion of concreting was 1hr 01 mins which is not excessive. In an effort to maximize production, the piling rig and crew had proceeded onto the next piles and had left reinforcement placing to the crane team and setting out engineer. Due to other site activity there was a delay (circa 45mins) between finish of concreting P335E and the time that the crane team got to hang the cage and insert. The bottom of P335E would have been “going off” during this period and potentially this delay is the root of the problem. Please see attached sketch for information and an excerpt from the pile schedule for information for Pile group P335.
| 03SR - Stations (RfL) | Cxxx-NCR-000097 | NCR | PCC element 1427A-1APL70-013, platform beam |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-04-04 | 2014-04-04 17:10 | 0 | 2014-03-14 17:20 | Structural Engineering - Concrete Member | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A) Internal Surface of box out is not scabbled / no coarse finish. See fig 1. B) Main B25s are cast in at an angle. The gap between them at the bottom is too small to fit the __ in at the right level. See fig 2. For correct reinforcement positioning see fig 3. C) The B16s are spaced incorrectly and not as per Section C-C on the unit drawing, there is a clash between the top halfen and one of the B16 bars. For correct reinforcement positioning see fig 2 and how the Cret interfaces with the existing cret see figure 3. Please see attached __ manufacturing NCR.
| 03SR - Stations (RfL) | Cxxx-NCR-000098 | NCR | PCC element 1427A-1APL70-014, platform beam |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-04-04 | 2014-04-09 08:50 | 5 | 2014-03-14 17:12 | Structural Engineering - Concrete Member | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A) Hy-rib projecting past the finished face of the concrete face. See Fig 1. B) The construction of the recess has allowed for debris/expanding foam/laitance to build up within the base of the recess. There is not a sufficient construction joint between the base of the recess and the concrete that will be filled. See Fig 2. C) The B16’s are spaced incorrectly and not as per Section B-B on the unit drawing. This results in a clash between the Large Cret __ and the Reinforcement. D) The beam has been constructed 12mm short. On the exposed end face of the beam there is reduced cover. There is currently 12mm cover being provided to the reinforcement bars (B16mm closing UBars). Please see attached __ manufacturing NCR.
| 03SR - Stations (RfL) | Cxxx-NCR-000100 | NCR | PCC element 1427A-1BPL69-016, platform level column |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-06-13 | 2014-06-03 11:42 | -10 | 2014-03-21 14:05 | Structural Engineering - Concrete Member | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the construction of column number 016 the macalloy couplers were set out in the wrong location. This is due to the incorrect positioning of the macalloy within the mould. This will affect the connection between concourse edge beam 517 and the column. Please see as-built drawing Fig 1 in the attached __ NCR 14.
| 03SR - Stations (RfL) | Cxxx-NCR-000101 | NCR | PCC 1427A-1APL70-017, platform beam |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-05-18 | 2014-05-06 09:16 | -12 | 2014-03-21 14:32 | Structural Engineering - Concrete Member | 800 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the construction of platform beam 017 the side shutter moved whilst concreting causing there to be a bow of 15mm to one of the sides. The well voids on the platform beam have also moved due to the magnets moving out of place during the cast. Some of these well voids have moved out of their designed location by up to 20mm. Please see as-built in the attached __ manufacturing NCR.
| 03SR - Stations (RfL) | Cxxx-NCR-000102 | NCR | PCC 1427A-1ACL68-505, concourse level beam |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-05-21 | 2014-05-06 10:55 | -15 | 2014-03-21 15:24 | Structural Engineering - Concrete Member | 800 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The length of concourse level beam (505) is short by 13mm. The unit length should measure 9443 but is 9430mm (-13mm). Please see as-built drawing. Issue 1-Architectural: The element is out of tolerance by 8mm according to the +/-5mm specification in the general notes sheet 1 of 3 for beams ranging 6-10m. Issue 2 – Structural: Some of the well voids are also out of their specified designed location (up to 24mm). Please see attached __ manufacturing NCR.
| 03SR - Stations (RfL) | Cxxx-NCR-000103 | NCR | PCC 1427A-1__69-509, concourse level column |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-08-29 | 2014-08-28 11:10 | -1 | 2014-03-21 15:36 | Structural Engineering - Concrete Member | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During construction of column number 509 one of the macolloy couplers was set out in the wrong location by 13 mm. This will affect the connection between roof level beam 702 with the column. Please see as-built shown in the attached __ manufacturing NCR.
| 03SR - Stations (RfL) | Cxxx-NCR-000104 | NCR | PCC 1472A-1BML68-312, mezzanine edge beam |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-06-02 | 2014-05-06 15:32 | -27 | 2014-03-21 16:01 | Structural Engineering - Concrete Member | 2000 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A) During the construction of the beam, the bottom well voids have moved out of place (by up to 10mm). See Fig 1 in the attachment. B) The length of the unit is short by 6 mm. The length of the unit should measure 8671 but is 8665. ------------------------------------------------------------------------------------------------- Reinforcement cut as per attachment '1427A-1BML68-312 - Reinforcement cut information'. Review of structural integrity required.
| 03SR - Stations (RfL) | Cxxx-NCR-000105 | NCR | Concrete Sampling - Piling Ops - 28 Days Result <40N; 56 Days Result >40N |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-04-08 | 2014-04-08 15:31 | 0 | 2014-03-25 17:39 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Recently, 4 No. Samples showed mean 28 day cube results being slightly under the required 40N. [12.12.13 - 38.6N; 20.01.14 - 38.7N; 21.01.14 - 37.1N; 22.01.14 - 37.9N] Pile numbers in question are piles P464 (12.12.13), P602 (22.01.14), P603 (21.01.14) & P604 (20.01.14). Please see cube certificates attached. Only one of the piles in question (P604) has been integrity tested (Cut-Off Level Test - No Anomalies present) and the OHLE base constructed. Please see 56 day results on cube certificates attached Cxxx were confident from previous results that the 56 day results would make the required strength of 40N and incorrectly assumed that an NCR need not be raised until 56 day results confirmed.
| 03SR - Stations (RfL) | Cxxx-NCR-000106 | NCR | PCC element NCR 1427A-1__71-560, coffer unit |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-04-04 | 2014-04-07 08:55 | 3 | 2014-03-28 12:36 | Structural Engineering - Concrete Member | 1000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | -The Anchorage L-bars to mesh were scheduled on the design drawings to be 1000mm long (500x500mm) which is compliant with EC2. The production/steel fixers felt that this was too short so they amended the bars to 800mm long so that they can achieve the minimum anchorage into the mesh; The bars that steel fixers used were 500x850mm as this was available. -This is issue was highlighted during a routine inspection surveillance by Crossrail and __. The unit had been fixed to the mould at the time of the surveillance but had not undergone the scheduled inspection by the design and quality team at EIP as per the QAR process defined in the ITP. The unit would NOT have been cast unless approval from both teams was agreed and would have been corrected accordingly prior to casting.
| 03SR - Stations (RfL) | Cxxx-NCR-000107 | NCR | VDR precast panel - tie wire protruding from VDR face in number of locations |  | Crossrail | XRL | CUH - Custom House Station (East) |  | 2015-01-09 | 2015-01-09 15:30 | 0 | 2014-04-01 10:55 | Civil - Civil Engineering General | 1200 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | On 10/03/2014 Inspection Request Form (IRF) has been issued to Crossrail for inspection of VDR precast wall ref. 1427A-1APL64-002 at gridline 5a. During the inspection it has been identified that tie wire was protruding from VDR face in number of locations. Following discussions with __/__ it became apparent that the current methodology at __ requires tying reinforcement cage to the formwork with the wire in order to maintain required concrete cover. This methodology needs revising as tie wire protruding from the concrete face is not acceptable and may with time compromise concrete durability. Contractor to propose solution and remedials to the VDR panel 002.
| 03SR - Stations (RfL) | Cxxx-NCR-000108 | NCR | Culvert capping wall detail not available |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-05-18 | 2014-04-17 09:40 | -31 | 2014-04-04 09:43 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Culvert capping wall drawing Cxxx-LAO-S-DDD-CR145_Z_10208 was not available for Crossrail to check and approve design prior to the commencement of the culvert capping work at grid line 32A-33A. Root Cause:We had encountered an existing culvert obstruction when excavating South track slab at GL 33A-27A, as a result and due to extremely tight programme we removed the existing section crossing the site and construct culvert capping wall as per __ preliminary sketches. later drawing 10208 issued on EB to show culvert capping wall construction detail.
| 03SR - Stations (RfL) | Cxxx-NCR-000109 | NCR | Pile166 Out of position |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-05-21 | 2014-04-30 14:43 | -21 | 2014-04-07 09:34 | Structural Engineering - Structural Engineering - General | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Pile No 166 set out incorrectly according to drawing Cxxx-ATK-S-DDA-CR145-3-32080. The pile has set out 269mm west of theoretical position. See attached highlighted drawing
| 03SR - Stations (RfL) | Cxxx-NCR-000110 | NCR | PCC element 1427A-1APL62-010, platform slab - insufficient cover to reinforcement in two of the stitch pockets |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-05-07 | 2014-04-14 08:37 | -23 | 2014-04-07 15:49 | Structural Engineering - Concrete Member | 800 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | In the platform slab 010 between GL 02A-03A there is insufficient cover to reinforcement in two of the stitch pockets. There is approximately 10mm cover – see attached photos.
| 03SR - Stations (RfL) | Cxxx-NCR-000111 | NCR | PCC element 1427A-1BPL62-037, platform slab, loose u-bar |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-07-25 | 2014-07-23 17:18 | -2 | 2014-05-01 11:10 | Structural Engineering - Concrete Member | 700 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the construction of the slab stitch reinforcement u-bar was not sufficiently tied, subsequently when the concrete was placed, the u-bar moved Refer to attached picture and __ Manufacuting NCR 53.
| 03SR - Stations (RfL) | Cxxx-NCR-000112 | NCR | P336A - 11.03.14 - Low 28 Day Cube Results |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-06-27 | 2014-06-11 12:00 | -16 | 2014-04-14 16:14 | Geotechnical Engineering - Concrete - Bored Pile | 1000 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Due to the volume placed by piling operations on 11.03.14, two concrete spot samples were taken for concrete cubes. Please refer to Cube Certificates, __ Cube Request sheets, Expanded Piling Cube summary Excerpt, Expanded Piling Concrete Delivery Log, __ Batch Record Summary & Email for reference. Cubes were taken from the first (__ Ticket # 362597) load of the day and the penultimate (__ Ticket # 362626) load of the day. 28 day results for #362626 (penultimate load) were 30.0n/mm2 and 32.3 n/mm2 respectively 28 day results for #362597 (first load) were 48.3n/mm2 and 47.5 n/mm2 respectively. The cubes from the penultimate load (__ Ticket #362626) of the day did not reach the required 40n/mm2.
| 03SR - Stations (RfL) | Cxxx-NCR-000113 | NCR | PCC 1427A-1APL62-020, platform slab, reduced cover |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-05-15 | 2014-05-12 11:30 | -3 | 2014-04-15 13:10 | Structural Engineering - Concrete Member | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Reduced cover is seen on the movement joint face of the platform slab 020. Refer to picture in the attached __ manufacturing NCR 61, section: detail of non conformance.
| 03SR - Stations (RfL) | Cxxx-NCR-000114 | NCR | PCC element 1427A-BPL70-026, platform beam, well voids incorrectly positioned |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-06-30 | 2014-07-01 17:48 | 1 | 2014-04-16 12:10 | Structural Engineering - Concrete Member | 1500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | At GL 7A/AB the well voids were set out and cast into the pile cap, using setting out information from __ GA drawing Cxxx-LAO-C-DWG-CR145_WS157_1-50136 rev C01. The well void positioning in beam 026 does not match the GA. As a result, 1No well void is 58mm out of position. Attached GA and unit drawing have been marked up to show discrepancy.
| 03SR - Stations (RfL) | Cxxx-NCR-000115 | NCR | 1427 A-1 __71-561 Concourse Coffer 561 |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-05-07 | 2014-05-06 11:00 | -1 | 2014-04-23 12:00 | Structural Engineering - Pre-cast | 2000 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | IRF (Inspection request form) 027 was sent to Crossrail inviting them to inspect coffer 561 prior to casting. The inspection was carried out on 3.4.2014. On the day the inspection was carried out the element was not after undergoing all inspections by the __ Quality team. A number of comments were raised by the Crossrail representative Field Engineer; __. These comments can be seen below. Please note my comments in yellow. COMMENT 1: Link bars (BM 37) at the joint between the diagonal beam and the edge beams have been cut due to a perceived clash between the inside of the diagonal link and the inside of the beam link. Pic attached. "Cuts links in diagonal beam". REPLY: Correct. Links were cut due to clash. The links are replaced with 810 ubars in its place. We have stopped production, revised the drawings and re-issued for approval to overcome this issue. Please see old and aQproved revised drawings appended to NCR which covers the change of reinforcement assembly. COMMENT 2: 12 no. BM 37 are required at this same location over 1150mm at 100mm centres. 11 no. only were installed over approx. 1050mm. Pic attached. "Incorrect number of links at lOOmm centres in diagonal beam" REPLY: Correct; The 12th link is yet to be installed. COMMENT 3: Link bars (BM 38) at the joint between the edge beam shown in section C-C and the edge beam shown in section A-A have been cut due to a perceived clash. Pic attached. "Cut links in edge beam - top right corner" REPLY: Correct. Links were cut due to clash. The links are replaced with 810 u-bars in their place. We have stopped production, revised the drawings and re-isssued for approval to overcome this issue.(See attached) Please see old and approved revised drawings appended to NCR which covers the change of reinforcement assembl~. COMMENT 4: Link bars (BM 38) at the joint between the edge beam shown in section C-C and the edge beam shown in section A-A have been cut due to a perceived clash. Pic attached. "Cut links in edge beam - top left corner" REPLY: Correct. Links were cut due to clash. The links are replaced with 810 u-bars in their place. We have sto ped production, revised the drawings and re-isssued for approval to overcome this issue.(See attached Please see old and revised drawin sa ended to NCR which covers the chance of reinforcement assembly. COMMENT 5: Bottom slab mesh anchorage L-Bars have been cut to avoid clash between diagonal beam. Pic attached. "Cut to suit anchorage L -bars in bottom slab mesh" REPLY: Correct the anchorage 1-bars must be installed as pe~ the reinforcement drawing. Please see old and revised drawings appended to NCR which covers the change of reinforcement assembly. COMMENT 6: Bottom slab anchorage U-bars (BM04 and BMOS) have not been used at all as detailed. They do not fit due to the 190mm depth of the bar as designed. L-Bars have been used in their place. REPLY: Correct. The slab anchorage u-bars have been replaced with 1-bars. This is due to issues encountered during the assembly process. This was agreed with __ when the issue was first encountered. To address this issue- we have stopped production, revised the drawings to reflect exactly what is installed and re-issued for approval to overcome this issue. Please see old and revised drawings appended to NCR. COMMENT 7: Box out at bottom left and bottom right corner had not been installed, cast in bolts not installed, halfin inserts not installed, U-Bars BM07 not installed. REPLY: All are work in progress. As documented by Justin- Works are in progress. COMMENT 8: Cover to shear key shown in section A-A and D-D does not have the minimum 35mm cover. This has apparently been accepted by the designer, however this allowance has not been detailed on drawings. This has been accepted by the designer. REPLY: Note; The area where low cover is being highlighted is on the shear key face of the coffer. In the permanent works the shear key is grouted between coffered units. The area of reduced cover is one that is so in the temporary condition of the element. COMMENT 9: Cover to diagonal beam varies due to the sloping sides of the formwork (required to assist striking) up to approx. 80mm. This is not allowed through the drawing. REPLY: Corrrect;This is not allowed for in the drawing. __ have confirmed the detail is acceptable. Confirmation to be provided. COMMENT 10: Plastic wrapping on the void former had come loose and was in the concrete zone. Probably due to being caught by tying wire when installing beams. Needs to be tidied up REPLY: Once the element is ready for inspection there will be no plastic wrapping in the concrete zone. COMMENT 11: Cover was generally not correct. I was told that it was yet to be adjusted. REPLY: Once the element is ready for inspection cover to reinforcement can be reviewed. Please also refer to attached NCR from __ Manufacturing 'NCR 62- Custom House Coffer 561 Rev 1.pdf ' which provides additional information and photos for clarification on each of the above points.
| 03SR - Stations (RfL) | Cxxx-NCR-000116 | NCR | Grid line 8A- Pile 153 out of position |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-05-30 | 2014-05-23 14:11 | -7 | 2014-04-23 12:52 | Structural Engineering - Reinforcement | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Pile 153- Grid line 8A Pile 153 set out incorrectly according to drawing Cxxx-ATK-S-DDA-CR145-3-32080. The pile has set out 189 to North of theoretical position. See attached highlighted drawing In order to ensure structural integrity we propose that the alignment of the pile cap at GL 8A along the track slab upstand be altered in order to accommodate the out of position pile rebar. The proposed new alignment of ‘Skewed’ pilecap is shown on the attached marked up drawing. __ (Chris Croft) has confirmed the new alignment of pilecap is acceptable and design can accomodate this proposed change. See attached __ designer confirmation email that loading on the pilecap from beam is acceptable Please note: Ignore following attachements ( Showing old detail) unable to delete 1) DSCF3706.JG 2) DSCF3707.JPG 3) DSCF3708.JPG 4) SKM__ C28014042210050.pdf
| 03SR - Stations (RfL) | Cxxx-NCR-000117 | NCR | PCC Element 1427A-1AML68-302 - Core well void drilling damaged reinforcement |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-05-09 | 2014-05-06 11:03 | -3 | 2014-04-25 15:03 | Structural Engineering - Pre-cast | 1000 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | This NCR is the subject of Cxxx-FCD-000074 which was pre-agreed with the structural engineer to prevent a delay to delivery of units (refer to attached email). Following core drilling to increase the available connection tolerance reinforcement was damaged in the core hole. Refer to attached __ 1427A-NCR-054 providing details of the reinforcement damaged.
| 03SR - Stations (RfL) | Cxxx-NCR-000118 | NCR | PCC Unit 1427A-1APL62-026 - Incorrect recess at column cut out |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-05-19 | 2014-05-15 15:42 | -4 | 2014-04-25 15:25 | Structural Engineering - Pre-cast | 1500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Platform slab 1427A-1APL62-026 has been detailed and constructed at __ Manufacturing differently to how it was designed by __. The area of difference is around the opening where the platform slab interfaces with the column. Please refer to attached __ NCR 1427A-NCR-063 for additional information.
| 03SR - Stations (RfL) | Cxxx-NCR-000119 | NCR | Track slab pile broken down lower GL20A-21A |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-06-30 | 2014-05-27 09:04 | -34 | 2014-04-30 11:08 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 6 NoTrack slab piles from GL 20A-21A were broken down to lower level than cut off level not leaving the required 50mm protrusion into the track slab.See attached photos and plan drawing showing pile cut off level flush with the concrete blinding Rootcause: Engineer set out cut off piles at the incorrect level. To stop this happening in the future,tighter dimension control and better monitoring in setting out. All levels to be cross checked by another Engineer prior to cut off piles.
| 03SR - Stations (RfL) | Cxxx-NCR-000120 | NCR | PCC 1427A-1APL70-017, platform beam, missing well voids |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-05-31 | 2014-05-29 14:21 | -2 | 2014-05-01 17:18 | Structural Engineering - Concrete Member | 2000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Platform beam 017 is missing a set of well voids that form the stitch detail between the platform slab edge and the beam – this is shown on __ beam GA Cxxx-LAO-C-DWG-CR145_WS157_1-50067 rev C02. There is a void in the slab above for this detail, shown in slab GA Cxxx-LAO-C-DWG-CR145_WS157_1-50063 rev C02. See attached marked up drawings.
| 03SR - Stations (RfL) | Cxxx-NCR-000121 | NCR | Effect of __ cube tank temperature deviations |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-05-22 | 2014-05-16 14:25 | -6 | 2014-05-08 14:43 | Structural Engineering - Concrete Member | 1000 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Some __ Lab cube compressive strength reports being submitted have stating ‘cubes cured outside of specification requirements’. __ have advised that during the summer months the temperatures of curing tanks, on occasion, were above the specified maximum of 22 degrees for a few hours in a day.
| 03SR - Stations (RfL) | Cxxx-NCR-000122 | NCR | Grouted well voids, north platform beams at gridlines 3A and 4A |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-11-26 | 2014-10-02 13:01 | -55 | 2014-05-12 17:27 | Structural Engineering - Grouting | 1500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | __ drawings had not been updated to the latest __ reinforcement intent. Well voids that were meant to be removed remained on the drawings and the pile caps and platform beams were cast to these drawings. The well voids were grouted up with B25 dowels in them. This occurs on the north platform beams at gridlines 3A and 4A. Affected drawings: __ reinforcement drawing: Cxxx-LAO-S-DWG-CR145_ws157_1-58010 rev C01 __ GA: Cxxx-LAO-C-DWG-CR145_WS157_1-50066 REV C03
| 03SR - Stations (RfL) | Cxxx-NCR-000123 | NCR | Mezzanine steel brackets – work proceeding without accepted MCR and ITP |  | Crossrail | XRL | CUH - Custom House Station (East) |  | 2014-08-01 | 2014-07-14 13:20 | -18 | 2014-05-12 12:12 | Civil - Civil Engineering General | 2000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Application of the intumescent paint to the steel brackets at mezzanine level have been carried out without accepted MCR and ITP in place. The paint system proposed in Cxxx-LAO-C-LRC-CR145_WS157_1-50312 rev. 1.0 and 2.0 was rejected due to lack of enough details confirming compliance with KM10 specification. At the same time no formal copy of ITP has been issued for acceptance defining application and testing regime during the painting operation. Despite all of the above not being in place the contractor installed the brackets on site between GL 2a-6a.
| 03SR - Stations (RfL) | Cxxx-NCR-000124 | NCR | Pile P518, P516 rebar cages low |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-06-12 | 2014-06-02 15:07 | -10 | 2014-05-13 17:00 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Two piles (P518, P516) rebar cages were installed low due to site Gate access requirement at the east of the project. During installation of pile, it was necessary to plunge the cages so that the top of steel equates to the site access ramp grade level at the pile location.
| 03SR - Stations (RfL) | Cxxx-NCR-000125 | NCR | PCC element 1427A-1ACL68-502, concourse edge beam - well voids out of position |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-06-13 | 2014-06-12 09:03 | -1 | 2014-05-14 09:21 | Structural Engineering - Concrete Member | 800 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the construction of the concourse beam the top straps were not significantly bolted to the mould, subsequently some of the well voids have moved out by up to 23mm. This has occurred due to the top straps moving. Refer to attached __ Manufacturing NCR 81
| 03SR - Stations (RfL) | Cxxx-NCR-000126 | NCR | Cracks & staining to precast elements gridline 2A-6A |  | Contr | LOS | CUH - Custom House Station (East) |  | 2014-12-12 | 2014-11-28 16:24 | -14 | 2014-05-14 18:13 | Structural Engineering - Pre-cast | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | there are a number of cracks/ stains/ chips on the precast elements that have been installed to date:- - Stain on column 10 (GL AF/6A) - Platform beam 16 - mezzanine edge beam 305 - platform beam 024 - mezzanine edge beam 304 - south track slab upstand 5A-6A The locations and details of these can be seen in the attached photographs. element references are referred to on the __ drawings.
| 03SR - Stations (RfL) | Cxxx-NCR-000127 | NCR | Witness point for single height column ref. 1427A-1BPL69-012 not offered to Crossrail |  | Crossrail | XRL | CUH - Custom House Station (East) |  | 2014-06-06 | 2014-06-12 15:34 | 6 | 2014-05-16 12:49 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Notification of witness point was issued by __ to __ on 12/05/14 (IRF Cxxx-LAO-C-IRF-CR145_EIP45). Crossrail confirmed on the same day attendance of the witness point on 16/05/14. After arrival to __ on 16/05/14 Crossrail was informed that the column element in question (ref. 1427A-1BPL69-012) had been already cast.
| 03SR - Stations (RfL) | Cxxx-NCR-000128 | NCR | PCC element 1427A-1ACL68-504, concourse edge beam - well voids out of position |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-06-16 | 2014-05-22 09:40 | -25 | 2014-05-19 11:46 | Structural Engineering - Concrete Member | 1000 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the construction of the concourse beam the top straps were not significantly bolted to the mould, subsequently one of the well void has moved (see attached as-built sketch). Refer to attached __ Manufacturing NCR 88.
| 03SR - Stations (RfL) | Cxxx-NCR-000129 | NCR | Concrete Grout Loss - GL9 North Track Slab Upstand |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-07-11 | 2014-07-09 15:05 | -2 | 2014-05-28 13:27 | Civil - Civil Engineering General | 800 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following striking the formwork from the upstand at GL9 on the North track slab, the engineer identified an area of grout loss at the stopend shutter interface with side shutter during the post pour survey.
| 03SR - Stations (RfL) | Cxxx-NCR-000130 | NCR | PCC element 1427A-1CCL69-512 - well voids out of position, well void blocked, misaligned sockets |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-10-31 | 2014-10-21 09:25 | -10 | 2014-05-29 10:12 | Structural Engineering - Concrete Member | 1000 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the construction of the column the following non-conformities have arisen: 1. Wells voids out by 10mm as shown on the attached as-built drawing. 2. 01no. well void blocked with concrete. 3. Sockets misaligned by 20mm. (Refer to the attached __ Manufacturing NCR 82, Fig.1)
| 03SR - Stations (RfL) | Cxxx-NCR-000131 | NCR | PCC elements 1427A-1BPL70-028, 1427A-1BPL70-029 & 1427A-1BPL70-031 - clash between reinforcement and Cret __ |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-07-25 | 2014-07-10 13:52 | -15 | 2014-05-29 11:37 | Structural Engineering - Concrete Member | 2000 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 1. Platform beam 1427A-1BPL70-028 (__ Manufacturing NCR 83 attached): 1.1 Main B25’s are cast at an angle. The gap between them at the bottom is too small to fit the __ at the right level. Refer to the attached __ Manufacturing NCR 83 - fig 1. 1.2 The B16’s are spaced incorrectly and not as per section B-B on the unit drawing, there is a clash between the top __ and one of the B16 bars. Refer to the attached __ Manufacturing NCR 83 - fig 1. 1.3 Create a good scabbled/coarse finish to the bottom of the unit. 2. Platform beam 1427A-1BPL70-029 (__ Manufacturing NCR 84 attached): The B16’s are spaced incorrectly and not as per section B-B on the unit drawing, there is a clash between the top __ and one of the B16 bars. Refer to the attached __ Manufacturing NCR 84 - fig 1. 3. Platform beam 1427A-1BPL70-031 (__ Manufacturing NCR 85 attached): 3.1 Main B25’s are cast at an angle. The gap between them at the bottom is too small to fit the __ at the right level. Refer to the attached __ Manufacturing NCR 85 - fig 1. 3.2 The B16’s are spaced incorrectly and not as per Section B-B on the unit drawing, there is a clash between the top __ and one of the B16 bars. There is also a similar situation occurring at the bottom link. Refer to the attached __ Manufacturing NCR 85 - fig 1. 3.3 Create a good scabbled/coarse finish to the bottom of the unit.
| 03SR - Stations (RfL) | Cxxx-NCR-000132 | NCR | PCC element 1427A-1BPL62-060 - insufficient cover to reinforcement in the stitch pocket |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-08-22 | 2014-08-20 09:39 | -2 | 2014-06-02 13:30 | Structural Engineering - Concrete Member | 800 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the construction of the platform slab the top cover in the box out is out of tolerance (refer to photo in the attachment). Low cover is only present in one of the stitch pockets (refer to cover meter survey attached to NCR 74).
| 03SR - Stations (RfL) | Cxxx-NCR-000133 | NCR | PCC element - 1427A-1BPL69-014 single hight column, AG25 coupler out of position |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-09-19 | 2014-08-28 20:06 | -22 | 2014-06-02 14:14 | Structural Engineering - Concrete Member | 800 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the construction of the column 014, one AG25 bent coupler is out by 113mm. Please see as-built in the attached NCR 89.
| 03SR - Stations (RfL) | Cxxx-NCR-000134 | NCR | PCC element 1427A-1BML60-313 - 317 & 320 - 328, mezzanine lattice slabs - incorrect cover stated on the design drawings |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-07-30 | 2014-07-10 13:54 | -20 | 2014-06-03 10:06 | Structural Engineering - Concrete Member | 1500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The following mezzanine lattice planks have 25mm cover stated on their unit drawings. This should in fact of been 35mm. - 1427A-1BML60-313 - 1427A-1BML60-314 - 1427A-1BML60-315 - 1427A-1BML60-316 - 1427A-1BML60-317 - 1427A-1BML60-320 - 1427A-1BML60-321 - 1427A-1BML60-322 - 1427A-1BML60-323 - 1427A-1BML60-324 - 1427A-1BML60-325 - 1427A-1BML60-326 - 1427A-1BML60-327 - 1427A-1BML60-328
| 03SR - Stations (RfL) | Cxxx-NCR-000135 | NCR | Superstructure grout cubes – poor quality/ incorrectly stored |  | Crossrail | XRL | CUH - Custom House Station (East) |  | 2014-08-01 | 2014-07-11 16:25 | -21 | 2014-06-02 16:19 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | During site inspection on 31/05/2014 Crossrail have identified that Contractor stores superstructure grout cubes in the undercroft area. The quality of the cubes was very poor (unlevelled top surface, holes in the top surface) and storage conditions were far from good practice. See attached photo. The Contractor is reminded that all cubes are to be cured and tested in line with UKAS accreditation. Crossrail understood that all cubes testing was carried out for Contractor by __ who are UKAS accredited. In the instance that was not the case.
| 03SR - Stations (RfL) | Cxxx-NCR-000136 | NCR | Erection of gantry crane without fully accepted documentation in place |  | Crossrail | XRL | CUH - Custom House Station (East) |  | 2014-06-23 | 2014-06-16 14:28 | -7 | 2014-06-02 16:27 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Crossrail note that the erection of gantry crane over the possession weekend (31/05-01/06 2014) was carried out without fully accepted documentation in place i.e. a) The design for gantry crane superstructure was cade 3. b) Gantry Crane Substructure CAT III Design Check Certificate was not issued for acceptance (draft copy emailed by Cameron Corsby on the day of gantry crane erection, draft without final approval of design organisation). Hence no code. c) Design and CAT III check for Gantry Crane C-Leg Temporary Prop not issued for acceptance (copy emailed by Cameron Corsby on the day of gantry crane erection, draft without final approval of design organisation). Hence no code. d) The accepted ITP ref. Cxxx-LAO-C-ITP-CR145_WS157_1-50016 for installation of gantry crane stipulated hold point for Issuing Permit to Load – item 15. This hold points was not offered to Crossrail. e) MPI testing for welding on gantry crane rail clamps not carried out prior to the gantry crane installation. Refer to ITP ref. Cxxx-LAO-C-ITP-CR145_WS157_1-50081 item 15. Please note that Crossrail will not accept putting the gantry crane into operation until the items above are fully closed out.
| 03SR - Stations (RfL) | Cxxx-NCR-000138 | NCR | Track slab piles P373 and P374 cut off levels |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-07-18 | 2014-07-14 12:58 | -4 | 2014-06-09 14:01 | Geotechnical Engineering - Concrete - Bored Pile | 800 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During excavation for the North track slab it has been noted that 2 no. piles are damaged below cut off level. Refer to attached photos of piles P373 and P374 showing the damage.
| 03SR - Stations (RfL) | Cxxx-NCR-000139 | NCR | Piles with reduced projection into trackslab / ground beams |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-08-15 | 2014-07-29 08:29 | -17 | 2014-06-09 16:11 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During construction of the cantilever beams for the gantry crane foundations between grids 20A to 23A 7 no. piles have less than 50mm projection into the beams. The affected piles are: P671 to 674, P358, P362, P366. Please refer to attached document 'Markup NCR 138 - piles cut to low' showing photos of the affected piles.
| 03SR - Stations (RfL) | Cxxx-NCR-000140 | NCR | Mezz lattice 305 corner broken off |  | Contr | LOS | CUH - Custom House Station (East) |  | 2014-10-31 | 2014-10-08 14:23 | -23 | 2014-06-10 18:11 | Civil - Structural Engineering | 800 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Mezz lattice 305 is supported by beam 305 along gridline AF. At gridline 3A the last cast in coupler in the beam was located too low, and was blocked by the lattice. the corner of the lattice slab was scabbled down in order to install the bar and during this, a small section of the corner broke off. the required reinforcement has been installed and a deck has been erected underneath the broken corner. when the slab 2A-4A is poured the corner will be repaired in the process. please see attached photos
| 03SR - Stations (RfL) | Cxxx-NCR-000141 | NCR | PCC element - 1427A-1__67-518 coffer unit, 15mm bow on one of the sides |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-11-26 | 2014-10-06 11:50 | -51 | 2014-06-11 10:39 | Structural Engineering - Concrete Member | 1500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the construction of coffer unit 518 the side shutter moved causing a 15mm bow on one of the faces - as-built survey shown on the second page of the attachment (__ Manufacturing NCR 19). The element is out of tolerance by 12mm according to the +/-3mm specification in the general notes sheet 1 of 3 for straightness/bow.
| 03SR - Stations (RfL) | Cxxx-NCR-000142 | NCR | Tension bar in P354 installed low |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-08-15 | 2014-07-29 15:43 | -17 | 2014-06-11 14:51 | Geotechnical Engineering - Concrete - Bored Pile | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Pile P354 has a tension bar installed to carry gantry crane tension loads. This bar has been installed approximately 150mm below design postion. In order to access the __ P13 poistional coupler to connect the anchorage bar the pile will need to be broken down lower. Refer to attached photo's and marked up drawing 'Pile P354 tension bar level'.
| 03SR - Stations (RfL) | Cxxx-NCR-000143 | NCR | Substructure Concrete Finish (Gridline 31A-32A) |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-08-15 | 2014-08-11 15:42 | -4 | 2014-06-16 09:33 | Civil - Civil Engineering General | 800 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following a site inspection the following concrete surface Non-Conformities were noted: >1no nail found embedded in North Track Slab upstand chamfer (Photo 1) >3no areas of grout loss where a penetration inspection demonstrated >10mm loss of concrete cover (Photos 3,5,6)
| 03SR - Stations (RfL) | Cxxx-NCR-000144 | NCR | Substructure Concrete Finish (Gridlines 30A-31A) |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-08-15 | 2014-08-11 15:44 | -4 | 2014-06-16 10:20 | Civil - Civil Engineering General | 800 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During a site survey the following Non-Conformities were noted: >1no chip on central pile cap on GL 31A (photo 13) >1no length of slight grout loss on rear face horizontal joint of North track upstand (photo 36)
| 03SR - Stations (RfL) | Cxxx-NCR-000145 | NCR | Substructure Concrete Finish (Gridlines 29A - 30A) |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-08-29 | 2014-08-11 15:47 | -18 | 2014-06-16 11:16 | Civil - Civil Engineering General | 800 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During a site survey, the following concrete finish Non-Conformities were noted: >An extended length of slight grout loss along the rear face, horizontal joint of the North track upstand (photo 11) >Grout loss around 1no vertex on the Northern most pile cap on GL 30A (photo 12)
| 03SR - Stations (RfL) | Cxxx-NCR-000146 | NCR | Substructure Concrete Finish (Gridlines 28A-29A) |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-08-29 | 2014-08-29 17:27 | 0 | 2014-06-16 11:29 | Civil - Civil Engineering General | 800 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During a site survey, the following concrete finish Non-Conformities were noted: >An area of grout loss to the Northern face of the North track upstand (Photo 7) >An area of grout loss to the Southern face of the North track upstand (Photo 10) >An area of grout loss to the Northern face of the South track upstand (Photo 40) >1no movement joint on the North track upstand has been completed to a substandard quality incl. honeycombing and irregular edge (Photo 44)
| 03SR - Stations (RfL) | Cxxx-NCR-000147 | NCR | Substructure Concrete Finish (Gridlines 27A-28A) |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-08-29 | 2014-08-15 11:26 | -14 | 2014-06-16 11:34 | Civil - Civil Engineering General | 800 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During a site survey, the following concrete finish Non-Conformities were noted: >A small patch of grout loss on the Northern most pile cap along GL28A
| 03SR - Stations (RfL) | Cxxx-NCR-000148 | NCR | Substructure Concrete Finish (Gridlines 26A-27A) |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-08-29 | 2014-08-29 17:40 | 0 | 2014-06-16 11:43 | Civil - Civil Engineering General | 800 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During a site survey, the following concrete finish Non-Conformities were noted: >A bad chamfer on the North track upstand (photo 8) >A length of grout loss on the North track upstand, North face (photo 8) >A length of grout loss on the North track upstand, South face (photo 9) >An area of grout loss on the central pile cap on GL 27A (Photo 38) and a stepped formwork joint (Photo 47) >An area of grout loss on a PC-1 Pile cap adjacent to the North track slab (Photo 46)
| 03SR - Stations (RfL) | Cxxx-NCR-000149 | NCR | Substructure Concrete Finish (Gridlines 21A-23A) |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-08-29 | 2014-08-29 17:35 | 0 | 2014-06-16 12:47 | Civil - Civil Engineering General | 800 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During a site survey, the following concrete finish Non-Conformities were noted: >2no areas where the surface finish on top of the Southern track upstand is sub standard (Photo 17 & 18)
| 03SR - Stations (RfL) | Cxxx-NCR-000150 | NCR | Substructure Concrete Finish (Gridlines 9A-10A) |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-08-22 | 2014-08-22 15:01 | 0 | 2014-06-16 13:09 | Civil - Civil Engineering General | 800 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During a site survey, the following concrete finish Non-Conformities were noted: >An area of grout loss to the bottom corner of a PC-1 pile cap to the East of GL9A
| 03SR - Stations (RfL) | Cxxx-NCR-000151 | NCR | Substructure Concrete Finish (Gridline 8A-9A) |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-08-22 | 2014-08-22 14:56 | 0 | 2014-06-16 13:22 | Civil - Civil Engineering General | 800 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During a site survey, the following concrete finish Non-Conformities were noted: >An area of grout loss on the Southern most PC-1 pile cap equidistant between GL8A and 9A
| 03SR - Stations (RfL) | Cxxx-NCR-000152 | NCR | Substructure Concrete Finish (Gridline 7A - 8A) |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-08-22 | 2014-08-22 14:57 | 0 | 2014-06-16 13:31 | Civil - Civil Engineering General | 800 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During a site survey, the following concrete finish Non-Conformities were noted: >An area of grout loss at a vertical joint in the North track upstand in between grid lines 7A and 1B (Photo 31) >A length of substandard chamfer finishing on the North track upstand (Photo 30)
| 03SR - Stations (RfL) | Cxxx-NCR-000153 | NCR | Substructure Concrete Finish (Gridlines 6A-7A) |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-08-22 | 2014-08-22 14:59 | 0 | 2014-06-16 13:43 | Civil - Civil Engineering General | 800 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During a site survey, the following concrete finish Non-Conformities were noted: >A repair had already been attempted to the Southern face of the North track upstand. It is substandard and requires reworking (Photo 42) > An area of grout loss is evident on a PC-11 pile cap centred on GL6A (Photo 33) > The Northern face of the South track upstand has limited concrete cover in the corner adjacent to the PC-1 pile cap. This is to be investigated (Photo 32) > The chamfer on the South track upstand is badly finished (Photo 19)
| 03SR - Stations (RfL) | Cxxx-NCR-000154 | NCR | Substructure Concrete Finish (Gridline 5A-6A) |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-08-15 | 2014-08-15 11:24 | 0 | 2014-06-16 13:49 | Civil - Civil Engineering General | 800 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During a site survey, the following concrete finish Non-Conformities were noted: >An area of damage to the South track Southern upstand adjacent to GL6A (Photo 26) >An area of grout loss in the same element at the base of the Northern face (Photo 27)
| 03SR - Stations (RfL) | Cxxx-NCR-000155 | NCR | Substructure Concrete Finish (Gridlines 1A - 5A) |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-08-15 | 2014-08-15 11:24 | 0 | 2014-06-16 14:01 | Civil - Civil Engineering General | 800 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During a site survey, the following concrete finish Non-Conformities were noted: >An area of grout loss on the South track's Southern upstand between GL4A and 5A (photo 24) >A number of chips and grazes on the South track's Southern upstand between GL4A and 5A (photo 25) >An embedded nail in the South track's Northern upstand between GL 2A and 3A >A bad chamfer finish on the South track's Southern upstand on GL 2A (photo 23) >An embedded nail in the South track's Southern upstand chamfer at GL1A (photo 45)
| 03SR - Stations (RfL) | Cxxx-NCR-000156 | NCR | Substructure Chamfer Concrete Finish (Site Wide) |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-09-05 | 2014-09-05 11:33 | 0 | 2014-06-16 14:35 | Civil - Civil Engineering General | 3000 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During a site survey, it was noted that the concrete finish to the track upstand chamfers was poor. The concrete was spalling/crazing leaving a rough, unformed finish. Investigation revealed that the shutter release agent may not be being applied evenly on the chamfer timber. However, having closed this out, the problem continued. The site team now think that the timber was absorbing the concrete's water at the surface causing the top 1-2mm of surface concrete to crumble away.
| 03SR - Stations (RfL) | Cxxx-NCR-000157 | NCR | Incorrect Debonding Foam Level - 4no piles - GL25/26 |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-08-15 | 2014-07-11 15:50 | -35 | 2014-06-16 18:11 | Civil - Civil Engineering General | 800 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | At 6no pile locations (4no piles at GL25 and 2no piles GL26) the pile cage debonding foam has terminated below the cut off level by approximate 300mm. This is due to the change in design of the Secondary Communications Equipment Room which has raised the cut off level by 500mm, from 100.720mAOD to 101.220mAOD.
| 03SR - Stations (RfL) | Cxxx-NCR-000158 | NCR | Pile cropped to low |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-07-25 | 2014-07-15 08:21 | -10 | 2014-06-17 13:56 | Civil - Civil Engineering General | 800 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Pile 174 and 176 have been cropped lower than the designed cut off level. The correct level should be 101.400, but has been cropped down to the VDR foundation level of 100.600
| 03SR - Stations (RfL) | Cxxx-NCR-000159 | NCR | Incorrect size filler board used between track slab upstand and pile cap |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-11-14 | 2014-11-14 11:34 | 0 | 2014-06-18 17:03 | Civil - Civil Engineering General | 1200 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 50mm thick board has been used between a single pile cap and the north track slab/track upstand in a 20mm gap.
| 03SR - Stations (RfL) | Cxxx-NCR-000160 | NCR | PC-12 GL10A - Concrete Finish |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-09-05 | 2014-08-22 14:59 | -14 | 2014-06-23 13:10 | Civil - Civil Engineering General | 800 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following a post pour inspection of the above concrete element, the following was noted: >5no areas of grout loss at the base of the formwork >1no area of grout loss 2/3 the way up the concrete face >1no area of substandard F2 concrete finish
| 03SR - Stations (RfL) | Cxxx-NCR-000161 | NCR | PC1 GL10A North East - Concrete Finish |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-08-22 | 2014-08-22 15:01 | 0 | 2014-06-23 16:07 | Civil - Civil Engineering General | 800 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During a post pour check on the above concrete element, the following was noted: >3no areas of Grout Loss
| 03SR - Stations (RfL) | Cxxx-NCR-000162 | NCR | GL6a Track Upstand (South) - no flexcell included in movement joint |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-09-05 | 2014-08-29 17:29 | -7 | 2014-06-24 10:33 | Civil - Civil Engineering General | 600 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following a post-pour inspection of the South track upstand at GL6a, the following was noted: > No flexcell had been installed against the previous stopend prior to the concrete pour leading to the formation of a construction joint, not a movement joint.
| 03SR - Stations (RfL) | Cxxx-NCR-000163 | NCR | Damage to platform slab and track slab upstand at GL4A (south) |  | Contr | LOS | CUH - Custom House Station (East) |  | 2014-11-26 | 2014-10-22 08:35 | -35 | 2014-06-24 16:02 | Structural Engineering - Pre-cast | 600 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Excavation works were carried out during the possession weekend (31/05-01/06/2014) for cables pit at GL 4a (south). The excavator was placed on the track slab without any protection to the finished concrete works. As a result there are quite a few chips, scratches and stains on the finished concrete structure. See attached Photos 5,6 and 7.
| 03SR - Stations (RfL) | Cxxx-NCR-000164 | NCR | VDR base concrete cracking - GL21-24 |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-08-22 | 2014-08-20 08:07 | -2 | 2014-06-26 17:15 | Civil - Civil Engineering General | 1000 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During a post pour inspection, the following defect was noted: > Numerous cracks formed in the top of the VDR beam during curing
| 03SR - Stations (RfL) | Cxxx-NCR-000165 | NCR | PCC elements 1427A-1__60-525, 526, 528, 529, 532, 533 concourse lattice slabs, change in geometry. |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-08-29 | 2014-08-26 14:03 | -3 | 2014-06-27 15:02 | Structural Engineering - Concrete Member | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Due to change the geometry of beams 1427A-1__68-517, 521, 525, 529 and 533 (for details refer to attached __ Manufacturing NCR 93) the following concourse lattice slabs have been affected (decrease in size): - 1427A-1__60-525 - 1427A-1__60-526 - 1427A-1__60-528 - 1427A-1__60-529 - 1427A-1__60-532 - 1427A-1__60-533 Before the beam geometry was changed all concourse lattice planks in this area were casted.
| 03SR - Stations (RfL) | Cxxx-NCR-000166 | NCR | PCC element 1427A-1BML68-316 mezzanine level beam, missing movement plate |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-08-15 | 2014-08-01 12:10 | -14 | 2014-06-27 16:02 | Structural Engineering - Concrete Member | 750 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | During the design phase of the mezzanine beam 316 no movement plates were modelled on the beam unit drawings therefore the mezzanine beam were constructed without the movement plates being cast in.
| 03SR - Stations (RfL) | Cxxx-NCR-000167 | NCR | North track slab concrete finish |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-08-28 | 2014-08-28 20:10 | 0 | 2014-06-30 12:42 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A small step has formed between concrete upstand face and angle fillet at Gl 25a on the south upstand of the north trackslab
| 03SR - Stations (RfL) | Cxxx-NCR-000168 | NCR | Reduced cover and cracking on north gantry beam |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-11-21 | 2014-11-22 09:32 | 1 | 2014-06-30 13:06 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | reinforcement can be seen in one location on the north gantry beam at gl 21a and it is evident that there is not the required cover. there is also a few areas where cracks have formed, please see attached photos
| 03SR - Stations (RfL) | Cxxx-NCR-000169 | NCR | Holding down bolts for 013 & 014 out of position |  | Contr | LOS | CUH - Custom House Station (East) |  | 2014-07-25 | 2014-07-16 10:11 | -9 | 2014-07-01 18:46 | Structural Engineering - Pre-cast | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | the holding down bolts for columns 013 and 014 at GL 7A-8A were installed 75mm too far south. A new line of holes have been drilled in the pile cap to enable the columns to be installed into their correct locations, however due to rebar in the pile cap, the holes have been drilled 87mm to the north of the existing bolts rather than 75mm. this will put the columns 12mm out of design location.
| 03SR - Stations (RfL) | Cxxx-NCR-000171 | NCR | Concrete Finish - Insitu Upstand GL 7A / 8A |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-08-22 | 2014-08-22 10:20 | 0 | 2014-07-08 18:43 | Civil - Civil Engineering General | 750 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Concrete finish on upstand not acceptable (refer attached photos); • Grout loss at vertical Corner edge of upstand (exposed aggregate) • Grout loss around base of upstand ( exposed aggregate)
| 03SR - Stations (RfL) | Cxxx-NCR-000172 | NCR | Chips to intumescent paint on brackets |  | Contr | LOS | CUH - Custom House Station (East) |  | 2015-05-01 | 2015-04-29 16:28 | -2 | 2015-01-13 09:44 | Structural Engineering - Pre-cast | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | There are chips to the intumescent paint on the mezzanine brackets - see attached photos.
| 03SR - Stations (RfL) | Cxxx-NCR-000173 | NCR | Rust staining on mezzanine beams |  | Contr | LOS | CUH - Custom House Station (East) |  | 2014-11-28 | 2014-11-14 11:28 | -14 | 2014-07-09 09:22 | Structural Engineering - Pre-cast | 1000 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | Various mezzanine and concourse longitudinal beams have rust staining from couplers exposed to water ingress & water running down the beams. this affects the inside face only. see attached marked up drawings and photos
| 03SR - Stations (RfL) | Cxxx-NCR-000174 | NCR | Timber bearer marks to soffit of lattice slab |  | Contr | LOS | CUH - Custom House Station (East) |  | 2014-09-05 | 2014-08-20 08:14 | -16 | 2014-07-09 09:40 | Structural Engineering - Pre-cast | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The precast concrete lattice floor slabs for grids 2A-12 have been cast without a specific architectural finish requirement. the finish provided is only outside of requirements due to timber bearer marks from storage - see attached photo
| 03SR - Stations (RfL) | Cxxx-NCR-000175 | NCR | Insufficient thread projection from Macalloy bars (WBS 4) |  | Contr | LOS | CUH - Custom House Station (East) |  | 2014-08-09 | 2014-07-16 14:00 | -24 | 2014-07-10 09:11 | Structural Engineering - Pre-cast | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | FAO __ the Macalloy bars in the concourse level connections on grids 2A, 3A and 4A do not always project through the nut by the minimum 1 thread - some sit slightly below and some flush with the top of the nut - see attached photos.
| 03SR - Stations (RfL) | Cxxx-NCR-000176 | NCR | Cracks in soffit of lattice slabs (WBS 4) |  | Contr | LOS | CUH - Custom House Station (East) |  | 2014-11-26 | 2014-11-05 15:51 | -21 | 2014-07-09 11:18 | Structural Engineering - Pre-cast | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | FAO __ there are several cracks visible in the soffit of some of the lattice slabs at mezzanine and concourse level GL 2A-6A - see attached photos and marked up drawings showing locations of cracks and crack width.
| 03SR - Stations (RfL) | Cxxx-NCR-000177 | NCR | Concrete Finish - PC1 GL 11A |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-08-28 | 2014-08-28 20:12 | 0 | 2014-07-10 12:51 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Concrete finish around base of Pile Cap 1 and GL11A not acceptable (refer attached photos); • Grout loss eastern base of PC • Grout loss northern bottom of face of PC ( exposed aggregate)
| 03SR - Stations (RfL) | Cxxx-NCR-000178 | NCR | North Track Slab - North Face 80mm Narrow |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-05-01 | 2015-05-01 16:00 | 0 | 2014-07-10 17:51 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Northern edge of Northern Track Slab at Gridline 9A has 80mm step in slab, the track slab between GL7A to GL9A was found to be 80mm narrow (tapering in from GL 7A to 9A) the adjoining track slab between 9A and 12A alignment has been corrected hence creating a 80mm step (refer attached photos) Track slab was originally set out from coordinates given from design information as a result of Cxxx-RFI-000169 (set out clarification), and as the coordinates were only given for GL7A and GL12A a straight line connecting the 2 coordinates was set out. Refer attached As built dimensions of trackslab.
| 03SR - Stations (RfL) | Cxxx-NCR-000179 | NCR | Blocked well void in GL 10A pile cap (WBS 4) |  | Contr | LOS | CUH - Custom House Station (East) |  | 2014-08-29 | 2014-08-28 20:07 | -1 | 2014-07-11 07:58 | Structural Engineering - Pre-cast | 500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | FAO __ 1No. well void is blocked with grout on the gridline 10A pilecap - see attached marked up drawings. this affects the dowel connection between the pile cap and platform beam 036.
| 03SR - Stations (RfL) | Cxxx-NCR-000180 | NCR | Waterproof Detail - Return Wall (GL 2A - 4A) |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-10-31 | 2014-10-31 17:08 | 0 | 2014-07-11 13:20 | Civil - Civil Engineering General | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Waterproof barrier not installed flush with return wall at GL 2A-4A (refer attached photo)
| 03SR - Stations (RfL) | Cxxx-NCR-000181 | NCR | North Track Slab Upstand - Concrete Damage |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-08-20 | 2014-08-11 15:53 | -9 | 2014-07-11 17:11 | Civil - Civil Engineering General | 600 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Substantial concrete piece broken out of North Track Slab Upstand (north face) at GL31 (refer attached photos)
| 03SR - Stations (RfL) | Cxxx-NCR-000182 | NCR | Damage to column 012 (WBS 4) |  | Contr | LOS | CUH - Custom House Station (East) |  | 2014-10-31 | 2014-10-14 13:44 | -17 | 2014-07-11 17:34 | Structural Engineering - Pre-cast | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the installation of platform slabs at gridline 7A, one of the slabs made contact with column 012 and caused damage to the corner - see attached photo.
| 03SR - Stations (RfL) | Cxxx-NCR-000183 | NCR | PCC element 1427A-1BPL62-053, platform slab, insufficient cover to reinforcement in the stitch pocket and along slab edge |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-08-12 | 2014-08-12 10:14 | 0 | 2014-07-15 13:20 | Structural Engineering - Concrete Member | 700 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | During the construction of the platform slab the top cover in the box out is out of tolerance. Low cover is present in one of the stitch pockets and also along one of the slab edges (as shown on attached cover survey drawing). (__ Manufacuting NCR 76 attached).
| 03SR - Stations (RfL) | Cxxx-NCR-000184 | NCR | ExCel Bridge Pile EBP4 |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-10-10 | 2014-09-04 16:25 | -36 | 2014-07-17 14:38 | Geotechnical Engineering - Concrete - Bored Pile | 3000 |  | Equipment Breakdown | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During installation of the first pile for the ExCel bridge we have encountered some problems with the piling rig. The casing was sealed in the clay on the first pile (EBP4 - see attached plan) but the clay plug to design toe level could not initially be bored. The Klemm 709 piling rig was having difficulty “flighting” the wet sands and gravels over the clay. Action was taken by our subcontractor to improve the performance of the rig through a change of parts. Unfortunately this did not provide the necessary improvement so the rig was changed for a replacement (same make and model). The above has resulted in the pile bore being open for an extended period. At the end of drilling on the 16/07/14 checks showed that there was circa 1m of standing water in the base of the bore. Structural concreting of the pile was cancelled and the bore backfilled with a lean mix in order to prevent further ingress and allow re-drilling. --------------------------------------------------------------------------------------------------- Updated 22/07/14 Following the above EBP1 was drilled with the new rig. On reaching design depth and checking the bore, water was discovered in the base. The depth of water was less at approximately 400mm. The bore was again backfilled with lean mix concrete to allow re-drilling. Assessment of the situation by our subcontractor is that the current smaller rig is not sufficiently powerful to install the casing such that they gain a fully effective seal into the underlying clay. On this basis the rig is being exchanged for a Hutte HBR 204.
| 03SR - Stations (RfL) | Cxxx-NCR-000185 | NCR | Concrete Finish - Pile Cap 13 (GL11A) |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-08-28 | 2014-08-28 20:13 | 0 | 2014-07-18 14:14 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Concrete finish on pile cap not acceptable (refer attached photos); • Grout loss at base of East face of pile cap (exposed aggregate) • Step in concrete on the East face of the pile cap
| 03SR - Stations (RfL) | Cxxx-NCR-000186 | NCR | VDR wall panel 005 - repairs to north face |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-01-30 | 2015-01-16 16:08 | -14 | 2014-07-21 11:46 | Structural Engineering - Concrete Member | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the delivery inspection and subsequent inspections of VDR wall panel 005 it was found that repairs to the North face of the unit (Victoria Dock Road side) are unsatisfactory. Following repair of the unit where tying wire has been removed from the face the installed repairs are not well installed, some loose and appear substandard.
| 03SR - Stations (RfL) | Cxxx-NCR-000188 | NCR | Steel shims stuck between platform beams and slabs |  | Contr | LOS | CUH - Custom House Station (East) |  | 2014-11-15 | 2014-10-31 09:54 | -15 | 2014-07-21 12:37 | Structural Engineering - Pre-cast | 1000 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | FAO: __ There are a number of locations in GL 2A-6A where steel shims were inserted between platform beams and slabs during installation. these shims are not part of the permanent works but are stuck in and cannot be removed. the locations of the shims are marked up on the attached drawing.
| 03SR - Stations (RfL) | Cxxx-NCR-000189 | NCR | Missed well voids in pilecap gridline 10A |  | Contr | LOS | CUH - Custom House Station (East) |  | 2014-10-31 | 2014-10-21 09:31 | -10 | 2014-07-21 15:50 | Structural Engineering - Pre-cast | 1000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | FAO: __ 8No well voids are required in the gridline 10A pile cap, only 4No were cast in. See attached marked up drawings.
| 03SR - Stations (RfL) | Cxxx-NCR-000190 | NCR | Void too small in platform slab 212 |  | Contr | LOS | CUH - Custom House Station (East) |  | 2014-09-30 | 2014-09-30 11:40 | 0 | 2014-07-29 14:10 | Structural Engineering - Pre-cast | 700 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | FAO __ the void provided in platform slab 212 is too small - this was due to a detailing error. the __ unit drawing Cxxx-LAO-C-DWG-CR145_WS157_1-50966 rev C01 shows the void as 147mm long whereas the __ drawing Cxxx-LAO-S-DDD-CR145_Z-10433 rev C02 (unit PCS 30-5P) has detailed it as 225mm long. the void needs to be enlarged - see attached photo
| 03SR - Stations (RfL) | Cxxx-NCR-000191 | NCR | Concrete Finish North Track Slab Upstand (GL22-24A & WBS3D) |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-08-28 | 2014-08-28 20:14 | 0 | 2014-07-25 10:52 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Concrete finish on North track slab upstand is not acceptable (refer attached photos): - Large step between panels on south face of upstand - Concrete broken off from top face of upstand
| 03SR - Stations (RfL) | Cxxx-NCR-000192 | NCR | Concrete Finish - Pile Cap 14 (GL13A & WBS3B) |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-09-30 | 2014-09-30 15:49 | 0 | 2014-07-25 11:11 | Civil - Civil Engineering General | 750 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Concrete finish on pile cap not acceptable (refer to attached photos): - Grout loss at the base of East and South faces geater than 10mm in depth
| 03SR - Stations (RfL) | Cxxx-NCR-000193 | NCR | Missed Well Voids in Pilecap GL12A (WBS 3B) |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-09-30 | 2014-09-24 14:35 | -6 | 2014-07-25 12:31 | Structural Engineering - Pre-cast | 700 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 8No well voids were not cast into pile cap on GL12A as per drawings - See attached file for further details.
| 03SR - Stations (RfL) | Cxxx-NCR-000195 | NCR | PCC element 1427A-2APL62-200 platform slab, incorrect geometry |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-09-30 | 2014-09-25 16:53 | -5 | 2014-08-06 14:12 | Structural Engineering - Concrete Member | 800 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 1. Platform slab casted to the wrong geometry. 2. Cret casted 50mm out of position.
| 03SR - Stations (RfL) | Cxxx-NCR-000196 | NCR | PCC element 1427A-1BML68-318 beam, 3 couplers installed too low |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-09-30 | 2014-09-25 16:47 | -5 | 2014-07-29 13:47 | Structural Engineering - Concrete Member | 600 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 3Nr Couplers have been casted too low - 35mm, 30mm and 17mm (refer to the attached explore manufacturing NCR 115). The location of these 3 couplers is such that once the lattice is installed on site it will clash with the biscuit of the lattice.
| 03SR - Stations (RfL) | Cxxx-NCR-000197 | NCR | Concrete Finish - Lift base walls @ GL12A |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-12-03 | 2014-11-14 17:00 | -19 | 2014-07-31 13:34 | Civil - Civil Engineering General | 700 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Concrete finish on Lift base wall not acceptable (please refer to attached drawings): • Steps in concrete found on surrounding external faces of lift base walls.
| 03SR - Stations (RfL) | Cxxx-NCR-000198 | NCR | PCC element 1427A-1BML68-316 beam, 3 couplers installed too low |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-09-29 | 2014-09-25 15:31 | -4 | 2014-07-31 13:49 | Structural Engineering - Concrete Member | 500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 3Nr Couplers have been casted too low - 30mm, 30mm and 25mm (refer to the attached __ Manufacturing NCR). The location of these 3 couplers is such that once the lattice is installed on site it will clash with the biscuit of the lattice.
| 03SR - Stations (RfL) | Cxxx-NCR-000199 | NCR | Cracks to Precast Platform Beams GL8A-11A (WBS 4C) |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-12-19 | 2014-12-19 13:20 | 0 | 2014-07-31 17:52 | Structural Engineering - Pre-cast | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | FAO __. There re a number of cracks/chips to precast platform beams that have been installed to date:- -Chips to both corners of paltform beam 033 (GL9A-10A) -Chip to east corner of platform beam 032 (GL9A-10A) -Chip to west corner of platform beam 037 (GL10A-11A) -Chip to west corner of platform beam 036 (GL10A-11A) -Chip to both corners of platform beam 039 (GL10A-11A) See attached photos.
| 03SR - Stations (RfL) | Cxxx-NCR-000200 | NCR | Damage to PC1 GL24A (WBS 3D) |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-10-30 | 2014-09-08 10:50 | -52 | 2014-08-01 09:57 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Large piece of concrete broken off from corner of pile cap 1, to the south of gridline 24A. See photos for details of damage location and extent.
| 03SR - Stations (RfL) | Cxxx-NCR-000201 | NCR | 4No well voids instead of 6No available in platform stitch |  | Contr | LOS | CUH - Custom House Station (East) |  | 2014-12-05 | 2014-11-10 10:39 | -25 | 2014-08-06 07:49 | Structural Engineering - Pre-cast | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | FAO: __ at gridline 28A there are only 4no well voids visible through the slab stitch pocket instead of 6No – see attached drawings and photos. Please confirm that we can deviate from the reinforcement detailing and only install 4No L-bars instead of 6No. Please can you also check the remaining platform for similar instances where 6No well voids aren’t available.
| 03SR - Stations (RfL) | Cxxx-NCR-000202 | NCR | PCC elements 1427A-2aPL62-205 & 1427A-2aPL62-208 - Insufficient cover to platform stitches (WBS 4F) |  | Contr | LOS | CUH - Custom House Station (East) |  | 2015-02-27 | 2015-02-25 13:30 | -2 | 2014-08-06 08:05 | Structural Engineering - Pre-cast | 700 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | FAO: __ There is low cover in one stitch pocket in each of the slabs 205 and 208 as shown in the attached marked up drawing. the cover is sufficient for the existing reinforcement within the slabs but once the additional L-bars are added the cover to these would be only 29mm instead of 35mm. the nominal concrete cover of 35mm (+/- 5mm) to top layer of reinforcement was achieved by EIP operatives. Insufficient cover occurred after installation on site where additional 16mm L-bars on the T1 layer were placed. this issue was identified for platform slabs 010, 053, 060 (NCR 110, 132 and 183) which were manufactured by EIP in the first batch in 2013. Operatives were re-briefed (briefing attached) and this issue did not re-occur.
| 03SR - Stations (RfL) | Cxxx-NCR-000203 | NCR | PCC element 1427A-1BML68-320 mezzanine beam, well voids out of position |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-09-30 | 2014-09-25 16:48 | -5 | 2014-08-06 12:35 | Structural Engineering - Concrete Member | 500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the construction the beam the well voids have moved out of place by up to 20mm (refer to the attached __ Manufacturing NCR 127).
| 03SR - Stations (RfL) | Cxxx-NCR-000205 | NCR | Concrete Finish In-Situ Upstands GL12A (WBS 3B) |  | Contr | LOS | CUH - Custom House Station (East) |  | 2014-12-03 | 2014-11-14 17:01 | -19 | 2014-08-07 14:12 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Concrete finish on upstand not acceptable (refer to attached photos): - Large blowholes on both in-situ uptands (aggregate exposed) due to insufficient compaction
| 03SR - Stations (RfL) | Cxxx-NCR-000206 | NCR | Nth Track Slab - Piles P212, P214, P216 & P218 Concrete/Cage Cropped Lower @ GL17A |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-10-17 | 2014-09-05 12:32 | -42 | 2014-08-13 17:01 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | FOA - __ The above piles cage have had concrete cropped slightly lower than the standard to allow for a temporary site access gate. The concrete has now been cropped 900mm low to allow for additional L reinforcement bars to installed.
| 03SR - Stations (RfL) | Cxxx-NCR-000207 | NCR | Bore casings remaining in pile following concreting |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-09-30 | 2014-09-02 15:49 | -28 | 2014-08-15 14:42 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following the problems encountered by our Sub-Contractor doing the ExCeL Bridge pier piles in Seagull Lane, the auger casings for pile nos 1 and 4 remained in the ground for longer than would normally be the case. Following the placement of the steel and the tremmie-ing of the concrete, the piling crew were unable to free the casings from the bore due to casing-ground friction. Consequently there remains 11m of casing around pile 1 and 8m of casing around pile 4.
| 03SR - Stations (RfL) | Cxxx-NCR-000208 | NCR | VDR GL-16A - South Face of Foundation - Out of Shape (WBS 3C) |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-11-19 | 2014-08-29 13:00 | -82 | 2014-08-18 08:53 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | South face of VDR concrete foundation out of shape due to pecafill formwork deforming out of shape. (Refer to photo)
| 03SR - Stations (RfL) | Cxxx-NCR-000209 | NCR | PCC element 1427A-2APL69-027 - single height column, couplers out of position |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-11-26 | 2014-08-29 13:04 | -89 | 2014-08-26 15:35 | Structural Engineering - Concrete Member | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During construction column 1427A-2APL69-027 four couplers were casted up to 19mm out of design position. For as-built position of couplers refer to the attachment (__ Manufacturing NCR 134).
| 03SR - Stations (RfL) | Cxxx-NCR-000210 | NCR | PCC element 1427A-1BML60-325 mezzanine lattice slab - opening missing |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-10-02 | 2014-09-25 16:49 | -7 | 2014-08-18 12:36 | Structural Engineering - Concrete Member | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | 300 x 150mm opening is missing from the centre of mezzanine lattice slab.
| 03SR - Stations (RfL) | Cxxx-NCR-000211 | NCR | Sheared bolt in column on grid 11A |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-11-28 | 2014-12-02 08:59 | 4 | 2014-08-21 08:31 | Structural Engineering - Bolted Connections | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | FAO __ - __ During installation of the brackets for the mezzanine beam on gridline 11A/AA an M27 stainless steel bolt has sheared off. Please refer to attached sketch and photos.
| 03SR - Stations (RfL) | Cxxx-NCR-000212 | NCR | Wire loop lifters to precast concrete beams |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-02-13 | 2015-01-05 17:00 | -39 | 2014-08-26 14:40 | Structural Engineering - Pre-cast | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Mezzanine and concourse precast concrete beam elements have been detailed and installed with wire loop type lifters - see attachment A - Wire loop lifter. These lifters project through the concrete cover zone and do not meet the requirements for the design life of the structure.
| 03SR - Stations (RfL) | Cxxx-NCR-000213 | NCR | CONCRETE FINISH - Pile Cap 14 (I Shape) on GL16A (WBS-3C) |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-11-19 | 2014-11-14 16:58 | -5 | 2014-08-27 11:50 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Concrete finish around base of Pile Cap 14 and GL16A not acceptable (refer attached photos); • Grout loss north west face around base of PC ( exposed aggregate)
| 03SR - Stations (RfL) | Cxxx-NCR-000214 | NCR | Repairs to precast column on grid 12/AB |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-03-27 | 2015-03-26 17:06 | -1 | 2014-08-28 13:34 | Architectural - Finishes | 750 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Insepction of the precast column on grid 12/AB has identified a substandard quality of finishing / repairs. Refer to attached photo.
| 03SR - Stations (RfL) | Cxxx-NCR-000215 | NCR | PCC - Missing couplers at Mezzanine level on columns 1427A-1CPL69-019, 1427A-1CPL69-022 |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-11-14 | 2014-11-06 16:45 | -8 | 2014-08-29 12:36 | Civil - Civil Engineering General | 500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | For the attention of __ Please see attached documents showing the location of the missing couplers. 4No. 25mm couplers have not been cast and therefore bar marks 08(04) and 09(03) cannot be inserted to provide the necessary anchorage.
| 03SR - Stations (RfL) | Cxxx-NCR-000217 | NCR | Blocked Grout Tube on Precast column 512, GL12, Concourse level. |  | Contr | LOS | CUH - Custom House Station (East) |  | 2015-05-08 | 2015-05-07 17:53 | -1 | 2014-09-02 13:11 | Structural Engineering - Pre-cast | 500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 1no. well void blocked with concrete. Correction of this revealed that the Grout Tube was also blocked. - see attached __ NCR 82
| 03SR - Stations (RfL) | Cxxx-NCR-000218 | NCR | WBS 2B - Incomplete / Corrupted Electronic Pile Records for P279, P288, P293, P294, P301, P307, P308 & DLRP1 - DLRP8 Inclusive |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-10-31 | 2014-09-24 10:01 | -37 | 2014-09-11 10:51 | Civil - Geotechnical Engineering | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | SPERW B1.5 Table, KP10.3213, Cxxx-LOA-C-GMS-CR145_WS157_1-50011 & Cxxx-LOA-C-GMS-CR145_WS157_1-50012 call for an electronic log to be produced for each CFA pile on Custom HOuse. While collating the records for WBS-2B, it was discovered that the electronic records for piles P279, P288, P293, P294, P301, P307, P308 & DLRP1 - DLRP8 Inclusive were corrupted and no meaningful data could be interpreted from these logs.
| 03SR - Stations (RfL) | Cxxx-NCR-000219 | NCR | Eazistrip placed incorrectly in column 026 GL 11A |  | Contr | LOS | CUH - Custom House Station (East) |  | 2015-04-17 | 2015-04-09 14:12 | -8 | 2014-09-12 16:58 | Structural Engineering - Pre-cast | 800 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | FAO __ the Eazistrip placed in column 026 to provide starter bars for the south twinwall has been positioned incorrectly in the column - see attached marked up photo. the Eazistrip lies outside the envelope of the twinwall. we will need to drill and fix new starter bars into the column for the twinwall, remove the Eazistrip and repair the column face.
| 03SR - Stations (RfL) | Cxxx-NCR-000220 | NCR | P446 concrete damaged below designed cut off level |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-10-10 | 2014-10-09 15:40 | -1 | 2014-09-12 09:35 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Pile no. 446 had been damaged before excavation and concrete has broken lower than designed cut off level.
| 03SR - Stations (RfL) | Cxxx-NCR-000221 | NCR | Pile cap concrete finishes GL 17a and 18a |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-10-11 | 2014-10-11 08:32 | 0 | 2014-09-12 10:31 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 2 no. pile caps at gl 17a and 18a (south) have small shrinkage cracks formed on top of both pile caps.
| 03SR - Stations (RfL) | Cxxx-NCR-000222 | NCR | (WBS 5B) Concrete Finish Excel Bridge Pile Cap - Seagull Lane |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-11-16 | 2014-11-05 15:55 | -11 | 2014-09-17 15:29 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Concrete finish around base of Excel Bridge Pile Cap - Seagull Lane (refer attached photo); • Grout loss southern bottom of face of Pile cap (15mm depth max)
| 03SR - Stations (RfL) | Cxxx-NCR-000223 | NCR | Canopy connections to column on 14A/AA |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-05-01 | 2015-03-28 09:34 | -34 | 2014-11-10 16:57 | Structural Engineering - Pre-cast | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The connections for the platform canopy in double height column 035 on grid 14A/AA are not considered structurally sufficient.
| 03SR - Stations (RfL) | Cxxx-NCR-000224 | NCR | VDR wall GL AD - Level of grout not achieved during grouting process |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-10-30 | 2014-10-28 08:44 | -2 | 2014-09-23 14:04 | Civil - Civil Engineering General | 750 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | For the attention of __. Please see the attached images detailing the grouting procedure for the VDR walls at GL AD. During this process some areas were cast low due to air entrapment. This was caused by not allowing a void at the top of the timber shutter. As a result the level of cover required has not been ahieved. The method for securing the timber shutter to the VDR North face was done so by drilling and fixing using a number of nails. As a result the cover zone has been encroached on and requires remedials.
| 03SR - Stations (RfL) | Cxxx-NCR-000225 | NCR | East end connection on Platform Beam 065 - Dowel bars to be removed. |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-12-01 | 2014-11-07 15:11 | -24 | 2014-09-30 12:00 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | For the Attention of __. Please find the attached drawings and photographs that show the East End connection on Platform Beam 065. The pile cap PC101 cage reinforcement was too congested to install the well voids in the correct location, the decision was made to cast in 2No. H25 dowel bars instead. However, these dowel bars were cast in out of position and as a result the Precast platform beam could not be landed into position.
| 03SR - Stations (RfL) | Cxxx-NCR-000226 | NCR | Concrete Finish Escalator Pit GL17 (WBS 3C) |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-11-14 | 2014-11-14 17:04 | 0 | 2014-09-30 14:10 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Concrete finish on escalator pit base PC101 on GL17A not acceptable (refer to attached photos): - Air bubbling up to 5mm deep - bowed finish 10-20mm high
| 03SR - Stations (RfL) | Cxxx-NCR-000227 | NCR | Nuts cut down on concourse connections 2A-6A |  | Contr | LOS | CUH - Custom House Station (East) |  | 2015-01-23 | 2015-01-16 16:21 | -7 | 2014-10-01 17:04 | Structural Engineering - Pre-cast | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | when cutting excess thread down to the nut on the concourse connections, in 8No instances the top of the nut has been cut down as well as the bolt - see attached marked up GA drawing and photos. Please see attached survey where grout has been removed locally around the bolt – the photos show the highest and lowest point of the top of each nut with a measurement of the height of the nut in that location. The original height of the nut is 43mm, the maximum amount any nut has been cut down is 9mm. __ have previously confirmed that the thread itself is permitted to be up to 10mm below the top of the nut, due to the nuts being larger than the design - see attached email.
| 03SR - Stations (RfL) | Cxxx-NCR-000228 | NCR | Unapproved deviation from drawings when fabricating platform beams 85, 89, 90 |  | Contr | LOS | CUH - Custom House Station (East) |  | 2014-12-19 | 2014-12-19 13:23 | 0 | 2014-10-03 17:00 | Structural Engineering - Pre-cast | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | the position of B25 u-bars (BM7 and BM8) in Platform beams 85, 89 and 90 were adjusted by construction team due to clash with well voids (as shown on attached drawings). No deviation permit was issued. Detailers from EIP received approval (sent via e-mail) from __. Drawings have been updated to reflect this change (clouded areas on attached drawings).
| 03SR - Stations (RfL) | Cxxx-NCR-000229 | NCR | Macalloy bars missing in columns 018 and 021 |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-11-05 | 2014-10-16 15:41 | -20 | 2014-10-06 12:42 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | For the attention of __. Please find attached the following drawings: Column 018: RAM connection detail - Cxxx-LAO-S-DDD-CR145_A-10280 RAM connection schedule - Cxxx-LAO-S-DWG-CR145_WS147_1-58043 EIP Column elevation- Cxxx-LAO-S-DWG-CR145_WS147_1-50121 EIP column details - Cxxx-LAO-S-DWG-CR145_WS147_1-50130 Column 021 RAM connection detail – Cxxx-LAO-S-DDD-CR145_A-10280 RAM connection schedule – Cxxx-LAO-S-DWG-CR145_WS147_1-58043 EIP column elevations - Cxxx-LAO-S-DWG-CR145_WS147_1-50122 EIP column details - Cxxx-LAO-S-DWG-CR145_WS147_1-50130 The RAM and EIP drawings have conflicting information and as a result 4No. well voids have been cast into columns 018 and 021 instead of the 5No. specified by __.
| 03SR - Stations (RfL) | Cxxx-NCR-000230 | NCR | Rust staining on precast concrete |  | Crossrail | XRL | CUH - Custom House Station (East) |  | 2015-05-08 | 2015-07-17 09:52 | 70 | 2014-10-14 13:48 | Civil - Civil Engineering General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Number of areas has been identified as being stained with rust on the architectural concrete. This issue relates mostly to beams, columns and Excel Bridge supports between GL 8a - 12a (north side). The rust staining issue was already raised in the NCR-173 but there seems to be still not enough vigilance on site to prevent the staining e.g. reinforcement bars stored at the edge of beams (photo 5), no corrosion protection to plates installed at the edge of precast structure (photo 6 and 7), couplers at columns insufficiently protected against water ingress (photo 8).
| 03SR - Stations (RfL) | Cxxx-NCR-000231 | NCR | Waterproofing overspray |  | Crossrail | XRL | CUH - Custom House Station (East) |  | 2014-11-27 | 2014-11-27 10:18 | 0 | 2014-10-14 14:26 | Architectural - General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the waterproofing installation at mezzanine level the existing floor openings were not sufficiently protected by the waterproofing subcontractor and as a result parts of architectural concrete were over sprayed with waterproofing. At the same time the subcontractor was using compressed air to clean dirt from the flooring prior to installation of the waterproofing. As all the dirt was blown down the architectural façade the façade will require now additional cleaning prior to handover. There seems to be not sufficient control in place for the activities undertaken by the waterproofing sub-contractor. __ should consider review of the ITP and introduction of formal area handover between __ and sub-contractors.
| 03SR - Stations (RfL) | Cxxx-NCR-000232 | NCR | Drainage Manhole Covers Installed ahead of Documentation Approval |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-02-27 | 2015-02-27 08:57 | 0 | 2014-10-22 08:59 | Civil - Drainage | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Man Hole covers installed as per man hole openning sizes without; *Approved design change of size openning and type of cover *MCR for approval of cover type
| 03SR - Stations (RfL) | Cxxx-NCR-000233 | NCR | Chip to column 041 |  | Contr | LOS | CUH - Custom House Station (East) |  | 2015-04-15 | 2015-03-25 14:32 | -21 | 2014-10-17 11:50 | Structural Engineering - Pre-cast | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | There is a chip to the corner of double height column 041 at gridline 17A/AA. the chip is approximately 100-150mm long. see attached photos
| 03SR - Stations (RfL) | Cxxx-NCR-000234 | NCR | PCC element 1427A-1__67-519 - coffer unit, reduced cover to the float face (WBS 4B) |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-02-17 | 2015-02-03 09:21 | -14 | 2014-10-17 16:14 | Structural Engineering - Concrete Member | 500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the installation of the concrete into the mould – the void former began to float in the centre of the unit. At this point the pour was held and the former was restrained from moving further upwards in the pour. As the casting of the unit proceeded it was found that the reinforcement in the centre of the unit had lifted (above the void former) by 35mm fanning out to 5-10mm on the sides of the unit. In an effort to encase the reinforcement with concrete – the unit was cast with a bow in it on the float face to replicate the line of the reinforcement. At the highest point – the concrete measures 19mm above the designed height of the unit. Following the curing of the unit - the float face has been surveyed for cover and level (refer to the attached __ Manufacturing NCR). Please note that the cover readings have been taken from the finished float face of the unit. Refer to __ Manufacturing NCR: - Coffer Location GA. - Concourse Level Plan - Coffer cover survey of unit after casting on top of unit. - Coffer cover survey of unit after casting on soffit of unit. - Level survey of unit after casting - Flexcrete Cementitious_Coating_851 - Product info (Cxxx-LAO-C-LRC-CR145_WS157_1-50358)
| 03SR - Stations (RfL) | Cxxx-NCR-000235 | NCR | Poor finish to three full height VDR walls |  | Contr | LOS | CUH - Custom House Station (East) |  | 2015-06-23 | 2015-06-23 17:20 | 0 | 2014-10-21 11:24 | Structural Engineering - Pre-cast | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | The three full height VDR walls appear to have a different colour in comparison to other pre-cast elements erected. The difference is also distinctive between the individual walls and there is quilting visible. see attached photo
| 03SR - Stations (RfL) | Cxxx-NCR-000236 | NCR | Missing Void in Concourse lattice @ GL3A |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-11-26 | 2014-11-26 08:10 | 0 | 2014-10-27 10:54 | Civil - Civil Engineering General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | For the attention of __. Please see attached drawing highlighting the location where the void intended for an overflow pipe at concourse level was missing.
| 03SR - Stations (RfL) | Cxxx-NCR-000237 | NCR | Documents decal 2 for 6 months |  | Crossrail | XRL | CUH - Custom House Station (East) |  | 2014-12-01 | 2014-12-01 10:39 | 0 | 2014-11-03 13:35 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | During a review of documentation it was found that ITP; Precast Frame Installation – Mezzanine, Concourse and Roof level (WBS 4), Cxxx-LAO-C-ITP-CR145_WS157_1-50088 rev 1.0 , decal 2 reviewed 02/05/14 Method Statements; Pre-cast Frame Installation-Platform Level, Cxxx-LAO-C-GMS-CR145_WS157_1-50049 rev 2, decal 2 reviewed 28/02/14, Precast Installation -mezzanine, concourse and roof, Cxxx-LAO-C-GMS-CR145_WS157_1-50101 rev 1 decal 2 reviewed 02/05/2014.
| 03SR - Stations (RfL) | Cxxx-NCR-000238 | NCR | Plate thickness transition weld detail deviation |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-11-24 | 2014-11-26 18:11 | 2 | 2014-11-03 14:12 | Structural Engineering - Welding | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Upon inspecting the ExCeL Bridge in the fabricator's workshop __ discovered that the 4:1 plate thickness transition detail had not been followed. The 60mm/30mm plates had been butted together and full strength butt welded together with no transition.
| 03SR - Stations (RfL) | Cxxx-NCR-000239 | NCR | Chip to top corner of column 019 (9A/AA) |  | Contr | LOS | CUH - Custom House Station (East) |  | 2014-12-12 | 2014-12-09 16:41 | -3 | 2014-11-05 17:45 | Structural Engineering - Pre-cast | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A chip was sustained to the top corner of column 019 during lifting - see attached photo
| 03SR - Stations (RfL) | Cxxx-NCR-000240 | NCR | OHLE socket levels in precast |  | Contr | LOS | CUH - Custom House Station (East) |  | 2015-10-04 | 2015-09-01 16:12 | -33 | 2014-11-06 11:53 | Structural Engineering - Pre-cast | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | FAO Cxxx VDR wall number 020 at Gridline 7A-8A/AD has cast in sockets for the OHLE - these were cast into the unit incorrectly and as a result are 15-20mm lower than the design level -please see attached marked up drawings the OHLE levels in the lollipop walls at 11A and 15A are at the correct level (also attached) OHLE drawings also attached
| 03SR - Stations (RfL) | Cxxx-NCR-000241 | NCR | Lack of __ Witness Points in __ against ITP Requirements |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-09-30 | 2015-10-16 15:37 | 16 | 2014-12-02 08:58 | Structural Engineering - Pre-cast | 3000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | There is no evidence to show that the percentage requirement of __ witness points in __ in accordance with the __ ITPs has been met until 21/07/2014.
| 03SR - Stations (RfL) | Cxxx-NCR-000242 | NCR | GL2A Staircase Structural Opening Size Discrepency |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-01-30 | 2015-01-15 10:53 | -15 | 2014-11-10 09:28 | Civil - Structural Engineering | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | GL2A staircase Structural opening size/orientation discrepency (platform level) between structural and architectural drawings. 2 no. RC plinths must be cast (forming north and south opening extents) and precast platform slabs cut (forming east & west opening extents).
| 03SR - Stations (RfL) | Cxxx-NCR-000243 | NCR | PCC element 1427A-2ACL68-549 - Movement plate not modelled into the beam |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-12-12 | 2014-12-11 07:32 | -1 | 2014-11-12 14:03 | Structural Engineering - Concrete Member | 750 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The concourse beam element located – on GL 16A/AA 1427A-2ACL68-549 was detailed without the movement fabrication cast in. This was a detailing error that was not picked up at the time of drawing release. Similarly the error was not picked up by __ / LoR in the drawing approval stage. __ Manufacturing NCR attached.
| 03SR - Stations (RfL) | Cxxx-NCR-000244 | NCR | PCC element 1427A-2APL72-045 & 1427A-2APL72-048 - damage to top corner |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-06-19 | 2015-07-04 11:18 | 15 | 2014-11-12 13:36 | Structural Engineering - Concrete Member | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Damaged area of concrete grater than 100x100mm (__ Manufacturing NCR attached).
| 03SR - Stations (RfL) | Cxxx-NCR-000245 | NCR | Damage to underside of Coffer slab 557 @ GL11A. |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-02-22 | 2015-02-20 16:12 | -2 | 2014-11-12 15:20 | Civil - Civil Engineering General | 60 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | For the attention of __. Please see attached photographs to highlight the damage caused to coffer slab 557 during the installation procedure. This has resulted in a piece approximately 300mm x 100mm x 15mm breaking off leaving the aggregate exposed.
| 03SR - Stations (RfL) | Cxxx-NCR-000246 | NCR | Unsigned / undated quality assurance record form (GL 2A-4A) |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-04-16 | 2015-03-09 13:04 | -38 | 2014-11-14 12:04 | Structural Engineering - Pre-cast | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Some sections of the Quality Assurance Record form (QAR) have been left unsigned or undated for several units that have been supplied to the Custom House project.
| 03SR - Stations (RfL) | Cxxx-NCR-000247 | NCR | Asite RFI |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-12-19 | 2014-12-18 09:46 | -1 | 2014-11-17 11:03 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | In July 2014, __ failed to retrieve pile casings from 2no piles in Seagull Lane. They had been left in place too long and had ceased in the ground due to a build up of skin friction. A RFI was submitted to __ via Asite requesting permission to leave the casings in the ground. __'s answer confirmed that the pile casings could be left in the ground. The RFI read: Please confirm that the piling sub contractor can leave the pile casings in the ground from a level just below cut off level to a depth of 12m. The pile has been bored to a total depth of 20.5m. Due to piling difficulties, the casings have been left in the ground for a longer period than usual and have seized in the bore and cannot be removed.
| 03SR - Stations (RfL) | Cxxx-NCR-000248 | NCR | Concrete changes via Asite RFIs |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-12-19 | 2014-12-18 09:52 | -1 | 2014-11-17 14:09 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | Previously, __/__ have changed the concrete classes of the ExCeL Pier Piles and plinth via Asite RFI. This has been not been passed through the PTR system.
| 03SR - Stations (RfL) | Cxxx-NCR-000249 | NCR | Concourse / Roof level edge beams - core drilling of well voids at movement jont locations |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-02-06 | 2015-01-29 17:37 | -8 | 2014-11-20 11:05 | Structural Engineering - Concrete Member | 800 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The well void at the location of the movement joints (concourse edge beams 531, 532, 533, 547, 548, 549; roof edge beams 711, 712, 719, 720) have an internal diameter of 60mm and external diameter of 67mm. There is a 32mm threaded macolloy bar located in the well void. The external dimension of the macolloy bar is 36.2mm. Once in position the macolloy bar will have a movement tolerance of 12.4mm. 15mm clear tolerance is required for the macolloy to accommodate for the buildings movement. __ Manufacturing NCR attached.
| 03SR - Stations (RfL) | Cxxx-NCR-000250 | NCR | Understrength Concrete Cube Test Result - Seagull Lane Pile 3 (WBS 2E) |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-12-21 | 2014-12-16 14:33 | -5 | 2014-11-21 16:15 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the certification process for package 2E, the __ site team realised that the concrete cube test results had not been received from __ for Seagull Lane piles 2 & 3. When received, the pile 3 records indicated that the pile concrete was under strength at 28 days. The 2no cubes had reached 35.5N and 35.8N against a characteristic strength of 40N.
| 03SR - Stations (RfL) | Cxxx-NCR-000251 | NCR | PCC element 1427A-2APL69-049 double height column - missing AG25 coupler |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-04-24 | 2015-03-25 14:53 | -30 | 2014-11-21 11:13 | Structural Engineering - Concrete Member | 1000 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During casting, AG25 bent coupler moved. The original location where the coupler was fixed can be seen. There is no sign of reduced cover from the loose coupler. __ Manufacturing NCR attached.
| 03SR - Stations (RfL) | Cxxx-NCR-000252 | NCR | Well voids in coffer 558 out of alignment |  | Contr | LOS | CUH - Custom House Station (East) |  | 2015-04-17 | 2015-04-16 17:53 | -1 | 2014-11-21 16:11 | Structural Engineering - Pre-cast | 1000 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | FAO __ at gridline 11A/AC concourse level the well voids in coffer slab 558 are out of position and do not line up with the coupler locations in the column below - please see attached marked up drawing with as built location of well voids and also attached photos Refer to section F on drawing Cxxx-LAO-S-DDD-CR145_A-10269
| 03SR - Stations (RfL) | Cxxx-NCR-000253 | NCR | Shear key in column 019 GL9A/AA |  | Contr | LOS | CUH - Custom House Station (East) |  | 2015-05-29 | 2015-05-07 17:52 | -22 | 2014-11-21 16:41 | Structural Engineering - Pre-cast | 750 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | There is a shear key in the west face of column 019 at gridline 9A-AA - this should not be present. see attached photo.
| 03SR - Stations (RfL) | Cxxx-NCR-000254 | NCR | PCC element 1427A-2ACL68-560 concourse edge beam - excessive blow holes |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-03-27 | 2015-03-25 15:23 | -2 | 2014-11-21 17:15 | Structural Engineering - Concrete Member | 500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Poor finish on mould face and excessive blow holes over 1m length at one end of beam. __ Manufacturing NCR attached.
| 03SR - Stations (RfL) | Cxxx-NCR-000255 | NCR | Missing Pile Cube Test Results |  | Contr | LAO | CUH - Custom House Station (East) |  | 2014-12-21 | 2014-12-16 17:02 | -5 | 2014-11-21 18:40 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the certification process for package 2E, the __ site team realised that the concrete cube test results had not been received from __ for Seagull Lane piles 2 & 3. The cube results from pile 2 are not able to be retrieved.
| 03SR - Stations (RfL) | Cxxx-NCR-000256 | NCR | __ channels out of position in coffer slabs |  | Contr | LOS | CUH - Custom House Station (East) |  | 2015-06-24 | 2015-06-23 10:08 | -1 | 2015-01-15 12:39 | Structural Engineering - Pre-cast | 800 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | the halfen channels that are cast into the coffered slabs to pick up the canopy column baseplates are out of position at gridline 10A and 12A. see attached as built surevey of the locations. the green lines in the survey indicate the centre line and extend of each halfen channel. see drawing Cxxx-LAO-S-DDD-CR145_A-10271 for the canopy column connection detail to the slab.
| 03SR - Stations (RfL) | Cxxx-NCR-000257 | NCR | Internal Lift Wall (Nth) - Outside Tolerance (GL11A-12A) |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-02-03 | 2015-02-03 09:16 | 0 | 2014-11-25 11:29 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The internal lift walls North and South face were poured at a slight angle 20mm outside alignment. North wall tappering at worse 20mm inwards and is out of the -0 allowable tolerance so must be repaired. The sourthern wall tappers 20mm outwards in is still inside the allowable tolerance of +25 so can be left and used as is. Refer attached markup demonstrating the internal lift walls poured 20mm out of des The concrete finish tolerance allows for +25 and -0
| 03SR - Stations (RfL) | Cxxx-NCR-000258 | NCR | PCC element 1427A-1BRL68-709 roof edge beam - well void out of position |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-02-20 | 2015-02-04 09:20 | -16 | 2014-11-25 12:42 | Structural Engineering - Concrete Member | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the construction of the beam, a well void has moved out of place (by up to 20mm). Refer to attached __ Manufacturing NCR.
| 03SR - Stations (RfL) | Cxxx-NCR-000259 | NCR | well void out of position in column 511 (11A/AB) |  | Contr | LOS | CUH - Custom House Station (East) |  | 2014-12-28 | 2014-12-19 11:56 | -9 | 2014-11-28 16:12 | Structural Engineering - Pre-cast | 500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | FAO __ the well voids in column 511 are out of position by 48mm. as such it is not possible to install the column as is. see attached as built sketch of well void locations
| 03SR - Stations (RfL) | Cxxx-NCR-000260 | NCR | PCC Element 1427A-2ARL68-714 - damage to concrete |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-01-07 | 2015-01-07 10:18 | 0 | 2014-11-28 12:04 | Structural Engineering - Concrete Member | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Error by manufacturer in shipping or marking | Completed |  | Damage to concrete greater than 100 x 100 mm + reinforcement exposed (please refer to attached __ Manufacturing NCR and pictures).
| 03SR - Stations (RfL) | Cxxx-NCR-000261 | NCR | PCC element 1427A-2ACL72-057 VDR trident - AG25mm couplers cast into trident unit instead of AG16. |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-01-07 | 2014-12-12 13:03 | -26 | 2014-11-28 12:59 | Structural Engineering - Concrete Member | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | In the internal face of the trident 1427A-2ACL72-057 there is cast in OHLE connection couplers. These couplers are designed as Dextra AG 16mm stainless steel. The actual couplers that were cast in place of the Dextra AG16 were Dextra AG25mm stainless steel couplers. (Please refer to attached __ Manufacturing NCR).
| 03SR - Stations (RfL) | Cxxx-NCR-000262 | NCR | DLR Bridge Cast In Plate Plate Welded Stud Damage |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-04-15 | 2015-04-07 15:47 | -8 | 2014-11-28 17:29 | Civil - Structural Engineering | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Pre cast beam PCB - 15R (Unit number 1427A-2ACL-68-537) was delivered to site from explore with a damaged welded stud to the cast in plate. See attached photos. The explore NCR will be appended when available detailing the handling issue. Due to superstructure installation programme constraints the beam was installed with remedial actions proposed to be carried out in-situ. This NCR contains justification for omission of the damaged bolt from the connection, it also contains details for remedial works. On review of the connection in question and amount works/resource required in bending, retesting, and remedial working (excluding any planning, assuring and production of necessary documentation) it is proposed to discount the bolt altogether (as per email dated 05/02/15). The loads supplied by Cxxx (see connection loads email dated 03-02-15) have been checked working through only 5 bolts (see calculation extract ‘CR - DAM - 5 Bolt Calculation’) with a final utilisation of 63%. __ request Cxxx acceptance of the above calculation justifying the bolts removal. Works are to be completed by __ prior to the April 2015 possession. The bolt will cut off and ground flush with cast in plate. The fabricated end plate will have 5 no. holes to mirror the bolt arrangement and prevent any potential moisture ingress.
| 03SR - Stations (RfL) | Cxxx-NCR-000263 | NCR | Alterations to Stringer Shear Key Locations |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-02-17 | 2015-02-06 16:15 | -11 | 2014-12-02 16:47 | Civil - Civil Engineering General | 600 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | For the Attention of __. Please find attached __ sketches for new locations of stringer beam shear keys. The location of the nib recesses were cast in the wrong positions. 2No. 110mm deep recesses must be formed in existing slab for stair stringer nib at both GL 15A and GL21A (see attached drawings).
| 03SR - Stations (RfL) | Cxxx-NCR-000264 | NCR | ExCeL Bridge Pipe Work Fixings |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-01-03 | 2014-12-12 13:03 | -22 | 2014-12-04 10:47 | Systems - Drainage/Pumping Systems | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The angles to hold the ExCeL Bridge's drainage in place within beam 4 have been fabricated too short. Instead of the hole being at the service void's midspan, the hole is 25mm offset for the centreline.
| 03SR - Stations (RfL) | Cxxx-NCR-000265 | NCR | Lack of clearance around pipe passing through mez floor |  | Crossrail | XRL | CUH - Custom House Station (East) |  | 2015-05-01 | 2015-05-15 16:04 | 14 | 2014-12-04 12:17 | Mechanical - Piping | 700 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Surveillance on a section of drainage pipework passing from the mez level to the platform level (through the mez floor) was carried out by crossrail on 27/11/14. The pipe protruding through the hole in the pre-cast was found to clash with the side of the hole, see attached photo. The specification requires a clearance of 15 - 25mm around the installed pipe (JY45.1208) to allow for the installation of a fire protective collar and mineral wall filling. The findings of the surveillance were discussed with __ on the day of surveillance.
| 03SR - Stations (RfL) | Cxxx-NCR-000267 | NCR | Mis-application of Metagard Sealer on ExCeL Bridge Splice Connections |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-01-10 | 2014-12-17 16:27 | -24 | 2014-12-11 11:54 | Structural Engineering - Bolted Connections | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following discussion with the paint applicators and the manufacturers, the ExCeL Bridge splice connection detail was confirmed as allowing the Metagard sealer 38mm within the splice plate footprint i.e. 38mm into the faying surface. This was accepted by the designer, __. The paint applicators, in treating one half of a splice as the whole connection, painted Metagard sealer through the faying surface area (see photos).
| 03SR - Stations (RfL) | Cxxx-NCR-000268 | NCR | ExCeL Bridge - Bow in Beam 1 |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-01-16 | 2015-01-12 11:17 | -4 | 2014-12-11 12:01 | Structural Engineering - Steel Member | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following a visit to the ExCeL Bridge Paint Applicators workshop, __ discovered a bow in Beam 1. This is thought to be as a result of the high weld heats used to weld the beam together.
| 03SR - Stations (RfL) | Cxxx-NCR-000269 | NCR | Nuts Bolts and Studding Installed on site without MCR |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-02-12 | 2015-02-06 16:20 | -6 | 2014-12-11 14:20 | Mechanical - Piping | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Pipe work support system, Nuts, Bolts, Washers and threaded BZP studding installed on site without an accepted MCR.
| 03SR - Stations (RfL) | Cxxx-NCR-000270 | NCR | Coffer slabs - reduced concrete cover to reinforcement |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-03-26 | 2015-03-25 15:32 | -1 | 2014-12-16 13:13 | Structural Engineering - Concrete Member | 7000 |  | Manufacturing Defect | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | There is a number of locations in the float face of the coffered slab installed on site where the cover is below the allowable cover requirements of the specification. Coffers with low cover: 517, 518, 549, 550, 551, 553, 555, 556, 557, 559, 562, 563, 565, 566, 568, 569, 571 (for details please refer to page 1 of __ Manufacturing NCR 186 and to cover meter survey of coffers installed on site). Please note: separate NCR 234 for reduced concrete cover for coffer 519 was submitted.
| 03SR - Stations (RfL) | Cxxx-NCR-000271 | NCR | __ Pipe Work |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-01-23 | 2015-01-15 12:14 | -8 | 2014-12-17 15:08 | Mechanical - Public Health Engineering | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | __ pipe work installed on site without approved MCR.
| 03SR - Stations (RfL) | Cxxx-NCR-000272 | NCR | Excel Bridge Beam Steel Fabrication - Works proceeded without accepted ITP |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-02-27 | 2015-02-12 08:06 | -15 | 2014-12-19 16:37 | Structural Engineering - Concrete Member | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Excel Bridge Beam Steel Fabrication - Works proceeded without accepted ITP; Cxxx-LAO-C-ITP-CR145_WS157_1-50102 - code 3.
| 03SR - Stations (RfL) | Cxxx-NCR-000273 | NCR | Use of unapproved cladding subcontractor drawings (WBS6A) |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-02-28 | 2015-02-25 13:35 | -3 | 2015-01-09 10:48 | Architectural - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | In accordance with ITP Cxxx-LAO-S-ITP-CR145_WS157_1-50009 used by __ to installl their secondary steelwork, the fabrication GA drawings for the base angles have not been CRL approved prior to fabrication and installation as per the ITP requirements
| 03SR - Stations (RfL) | Cxxx-NCR-000274 | NCR | Roof cross beam 801 lack of fit |  | Contr | LOS | CUH - Custom House Station (East) |  | 2015-08-15 | 2015-08-11 13:12 | -4 | 2015-01-09 10:02 | Structural Engineering - Pre-cast | 750 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | FAO __ Roof cross beam 801 at 9A does not fit in position - alterations need to be made to the beam in order for it to fit - see corrective actions.
| 03SR - Stations (RfL) | Cxxx-NCR-000275 | NCR | Under strength 28 day grout cube result for platform stitches 16A-17A, 23A-25A |  | Contr | LOS | CUH - Custom House Station (East) |  | 2015-02-08 | 2015-02-06 17:00 | -2 | 2015-01-09 10:42 | Structural Engineering - Grouting | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | FAO: __ the 28 day grout cube strength is under the required strength of 60MPa in the following areas: 1. platform beam stitches 16A-17A 2. platform beam to pile cap 23A-25A 3. slab to platform stitches 24A-25A see attached marked up drawings showing affected grouted areas, 28 day cube results and 56 day cube results. 1. 16A-17A: 28 day cube results are 49.1 and 48.0MPa, 56 day result is 60.9MPa which meets the strength requirement 2. beams 23A-25A: 28 day cube results are 53.2 and 54.1MPa, 56 day result is 63.1MPa which meets the strength requirement 3. slab to beam 23A-24A: 28 day cube results are 53.9 and 54.8MPa, 56 day results is 62.2MPa which meets the strength requirement
| 03SR - Stations (RfL) | Cxxx-NCR-000276 | NCR | Under strength 28 day grout cube result for VDR wall base 8.5A-10.5A |  | Contr | LOS | CUH - Custom House Station (East) |  | 2015-02-20 | 2015-02-20 08:30 | 0 | 2015-01-09 16:34 | Structural Engineering - Grouting | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | FAO: __ the 28 day grout cube strength is under the required strength of 60MPa for the VDR wall base between 8.5A and 10.5A. see attached marked up drawings showing affected grouted areas, 28 day cube results and 56 day cube results. 28 day cube results are 50.1 and 51.1MPa, 56 day result is 57.8MPa There is no 90 day test cube available for this pour. the strength of the concrete in the pile cap below is as follows: 28 day = 68.5, 74.4MPa 56 day = 76.9MPa
| 03SR - Stations (RfL) | Cxxx-NCR-000277 | NCR | Cracks in columns and beams at movement joints on concourse level |  | Contr | LOS | CUH - Custom House Station (East) |  | 2016-04-15 | 2016-04-25 11:14 | 10 | 2015-03-09 10:39 | Structural Engineering - Pre-cast | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | FAO: __ Cracking and loss of material in the cover zone of the platform to concourse level columns on grids 8A/AC, 12A/AB and 16A/AB has been discovered. Refer to attached document ‘NCR 277 MJ Cracks’ for photos of the affected columns. Note that these images also show minor cracks to some of the longitudinal beams above. These are covered under Cxxx-NCR-000278 in order to expedite the repair to the movement joints and faces of the columns but also group repairs that require the same remedial action. This NCR has been discussed in an Extraordinary Early Warning meeting held on the 13th of March 2015. It was further discussed in detail with the relevant technical teams during a meeting on the 22nd of May 2015. Please refer to meeting minutes Cxxx-LAO-C-MRC-CR145_WS157_1-50095 for details of the discussion during the meeting and actions agreed. Additional information on the construction processes to be used to complete the remedial works are attached under cover of document ‘Cxxx-TS-147 - Movement joint remedial work’. ---------- 30/10/2015 NCR update: It has been observed that after completion of repair works as per method detailed in the attached document - Cxxx - Concourse MJ Remedial proposals_CC 260515.pdf, the crack on GL8 has re-occurred. 26/01/16 NCR update: Following further crack propagation, RUK have detailed another crack remedial action.
| 03SR - Stations (RfL) | Cxxx-NCR-000278 | NCR | Cracks in in-situ grout / beams |  | Contr | LOS | CUH - Custom House Station (East) |  | 2015-10-02 | 2015-11-27 16:10 | 56 | 2015-03-09 10:49 | Structural Engineering - Pre-cast | 2000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | FAO: __ Cracks have been discovered in the precast structure in the following locations: 1. The grouted connections at concourse level at 11A/AB and 11A/AC. 2. Beams at grids 8A/AC (concourse and mezzanine); 8A/AA (concourse); 12A/AB; 10A-11A (mezzanine); 9A south (mezzanine).
| 03SR - Stations (RfL) | Cxxx-NCR-000279 | NCR | VDR wall panels 006, 007, 008, 009, 015 - Repairs to North face |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-04-03 | 2015-03-25 15:24 | -9 | 2015-01-13 12:36 | Civil - Civil Engineering General | 2000 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | For the attention of __. The concrete surfaces for VDR wall panels 006, 007, 008, 009, 015 have a 10mm thick layer of laitance on the north face. This layer has become increasingly weathered after installation and as a result a 10mm layer shows signs of minimal strength.
| 03SR - Stations (RfL) | Cxxx-NCR-000280 | NCR | Failure of pull out test - GL 6A, platform beam 22 |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-07-24 | 2015-07-30 13:56 | 6 | 2015-01-13 09:48 | Structural Engineering - Pre-cast | 1500 |  | Testing and Commissioning | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | One of pull out tests (GL6A, platform beam 22) on the CMS support fixings (__ Screw Anchor HUS3-HF 10x60) has failed. The pull out test was carried out in accordance to requirements of ITP for CMS (Cxxx-LAO-E-ITP-CR145_WS157_1-50011).
| 03SR - Stations (RfL) | Cxxx-NCR-000281 | NCR | Cross beam 804 end plate clash with roof beam 705 @ GL 10A |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-02-27 | 2015-02-25 13:36 | -2 | 2015-01-13 16:09 | Civil - Civil Engineering General | 700 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | For the attention of __. Please see attached documentation highlighting a clash between roof level beam 705 and cross beam 804 at GL 10A. The cast in end plate currently prohibits the installation of beam 705 at Custom House.
| 03SR - Stations (RfL) | Cxxx-NCR-000282 | NCR | Discrepancy in macalloy & well void locations roof 12A/AB |  | Contr | LOS | CUH - Custom House Station (East) |  | 2015-03-20 | 2015-03-19 18:55 | -1 | 2015-01-14 12:11 | Structural Engineering - Pre-cast | 1000 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | FAO __ & Cxxx the macalloy locations in column 512 have been cast incorrectly. one of the 3no macalloys on the west side of the column is in the wrong location. see marked up sketch NCR-282-SK01. this affects the connection between roof beam 708 and the column, and the roof top plate connection. refer to the following drawings: Cxxx-LAO-S-DDD-CR145_A-10273 - __ main building details - "connection at 12A/AB movement joint - roof level" Cxxx-LAO-C-DWG-CR145_WS157_1-50329 (explore) roof beam details "Detail 1" Cxxx-LAO-C-DWG-CR145_WS157_1-50131 (explore) Phase 1B Columns 509-512 details "Section Wa-Wa" Cxxx-LAO-C-DWG-CR145_WS157_1-50624 (explore) column lineside details "section 9" Cxxx-LAO-S-DWG-CR145_WS157_1-50102 (__) "plan on top plate type 53" the column has been cast with the macalloys in the arrangement shown in drawings 50329 and 50624, this is incorrect and conflicts with the other drawings. the roof beam 708 and roof top plate have been cast correctly. in order to install the beam and plate they will both have to be drilled to match the column macalloy positioning. drilling the plate will affect the position of the lugs for the roof steelwork. the column has been grouted into position.
| 03SR - Stations (RfL) | Cxxx-NCR-000283 | NCR | Manufacturing Drawing Checklist SF105 unavailable as a deliverable record for WBS 4 |  | Contr | LOS | CUH - Custom House Station (East) |  | 2015-01-27 | 2015-01-23 15:05 | -4 | 2015-01-19 17:28 | Structural Engineering - Pre-cast | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | the 'manufacturing drawing checklist SF105' has been listed as a deliverable item in the following ITPs: column fabrication: Cxxx-LAO-C-ITP-CR145_WS157_1-50056 rev 5 (items 4.02 and 9.04) coffers: Cxxx-LAO-C-ITP-CR145_WS157_1-50064 rev 3 (item 4.02, 4.03, 9.04) platform slabs and beams: Cxxx-LAO-C-ITP-CR145_WS157_1-50066 rev 5 (items 4.02, 4.03, 9.04) VDR wall: Cxxx-LAO-C-ITP-CR145_WS157_1-50067 rev 3 (item 4.02, 4.03, 9.05) edge and longitudinal beams: Cxxx-LAO-C-ITP-CR145_WS157_1-50068 rev 4 (item 4.02, 4.03, 9.04) stairs and landings:Cxxx-LAO-C-ITP-CR145_WS157_1-50069 rev 2 (item 5.04) lattice planks: Cxxx-LAO-C-ITP-CR145_WS157_1-50072 rev 4 (item 4.02, 4.03, 9.03) twinwall: Cxxx-LAO-C-ITP-CR145_WS157_1-50082 rev 1 (item 4.02, 4.03) stringer beams: Cxxx-LAO-C-ITP-CR145_WS157_1-50108 rev 2 (item 4.02, 4.03, 9.04) this record is an __ internal drawing review sheet but is not available for handover. assurance that __ drawings are correct is provided by the contractor's declarations signed by __.
| 03SR - Stations (RfL) | Cxxx-NCR-000284 | NCR | DLR Bridge Roof Beam Connection Cast in Plate Omission |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-04-15 | 2015-04-10 22:38 | -5 | 2015-01-28 18:28 | Structural Engineering - Pre-cast | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Precast Beam 712 has been cast and installed without roof connection cast in plate as per detail 3 on Drawing Cxxx-LAO-S-DDD-CR145_Z-36500 and detail 3 on Cxxx-ATK-S-DDD-CR145_Z-36500. In addition the setting out of the roof structure has been based on the center line of the roof beam aligning with site gridlines 1D & 2D (as opposed to center line of supporting steel columns SC-1 & SC-6.) This means that the cast in studs will clash with the web of the roof beam. Modification is therefore required to the main roof beam setting out. This is addressed in a separate NCR (Cxxx-NCR-000287 - DLR Bridge - Roof Beam Web/Cast in Plate Clash) - please note that the solution proposed for this NCR takes account of the revised setting out. __ propose Cxxx verify the connection based on the attached in-situ repair solution which consists of 4 number M24 resin anchors (250mm embedment) drilled central to gridline 1D. Please note the anchors will be drilled as per the attached centres but may have to be altered owing to the presence of reinforcement. In this case the anchor locations will be as built and connection re checked. This could also result in the end plate of the roof beam increasing in size. See DAM structures GA 4 Cxxx-LAO-S-DWG-CR145_WS157_1-50186 ‘VIEW ON CAST IN PLTS’ detail for how this will be captured. Any subsequent changes/checks will be issued as part of closure of this NCR. The following Architectural impacts have been considered should the end plate increase in size: • North of the precast connecting beam – no impact as solution based on resin anchor solution not through bolt and end plate • The south side of the precast beam (and connection plate) will be hidden by the roof outline so a enlarged plate as shown in the attachment will be concealed Superseded attachments: • DLR Roof Beam Roof Connections 23/02/2015 Attachments: • Missing Cast in Plate jpeg • 23-02-15-61020436-S-SK-191 • 23-02-15-61020436-S-SK-192 • 23-02-15 - Cxxx-LAO-S-DDA-CR145_WS157_1-50186
| 03SR - Stations (RfL) | Cxxx-NCR-000285 | NCR | No 56 or 90 day cube results available for __ deliverable records |  | Contr | LOS | CUH - Custom House Station (East) |  | 2015-02-04 | 2015-01-29 18:09 | -6 | 2015-01-21 18:14 | Structural Engineering - Pre-cast | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Specification Cxxx-LAO-C-RSP-CR145_WS157_1-50002 clause KF10.2205 f) states that 56 and 90 day cubes should be taken for concrete above grade C20/25 containing PFA or GGBS. ITP Cxxx-LAO-C-ITP-CR145_WS157_1-50066 item 8.03 under parameters has 28 days, 56 and 90 day cube result certificates and batch sheets as deliverable items. 56 and 90 day results have not been taken for any __ items, only 2No 28 day tests results have been provided, however the 28 day strengths are well over the required strength of 60MPa. (see Cxxx-LAO-C-LRC-CR145_WS157_1-50446 rev 1.0)
| 03SR - Stations (RfL) | Cxxx-NCR-000286 | NCR | PCC element 1427A-2ACL74-646 cross beam, incorrect position of upstand |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-08-14 | 2015-08-07 09:16 | -7 | 2015-01-23 09:03 | Structural Engineering - Concrete Member | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The fabricarion that was cast into the unist is symmetrical in terms of geometry but assymetrical in terms of connection to the concourse edge beams and double height column. The fabrication was cast 180 degrees out of rotation. The issue was not detected as the unit passed through the quality inspections at EIP and was delivered to site. The architectural importance of this element is such that it will be constantly viewed by the public as it faces the main staircase alond GL 14-15AA/AB.
| 03SR - Stations (RfL) | Cxxx-NCR-000287 | NCR | DLR Bridge - Roof Beam Web/Cast in Plate Clash |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-05-01 | 2015-05-05 20:44 | 4 | 2015-01-29 10:01 | Structural Engineering - Bolted Connections | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | With reference to Cxxx-NCR-284 concerning the omitted cast in plate: On detailing of the DLR bridge roof steelwork a clash has been detected between the cast in connection plate within precast beam 714 and the SB-1 Roof beam (305 x 165 x 54 UB). The web of the beam falls on the line of the cast in studs meaning connection as per the original Cxxx design drawing (Cxxx-ATK-S-DDD-CR145_Z-36500) impossible. This clash is the result of misinterpretation of the connection detail with regard to its grid location which has incorrectly been taken as the centre of beam throughout design development (as is the case with main structural deck connections). The roof beams and support column centre lines are actually set to a grid offset of 53mm. __ require both roof beams to be relocated central to grid: • This will enable the cast in connection plate on precast beam 714 to be used • This will simplify fabrication and detailing for the steelwork fabricator and can be incorporated into beam 712 as the cast in plate was omitted Changes for the designer to consider: • The top connection plate on all support columns will have to be enlarged to accommodate the offset beam • The roof beams will be closer together which may require adjustment of the rafter steel radius and or height of connection into the web of the roof beam Cxxx attach proposal for thickened and enlarged top plates to account for realigned roof beams (with reference also to NCR 284 – Omitted end plate). Cxxx require Cxxx verification of beam realignment and incorporation of thickened and enlarged top plates 25-03-15: PLease see attached calculation as supplied by __.
| 03SR - Stations (RfL) | Cxxx-NCR-000288 | NCR | Escalator support steelwork manufactured to P revision drawings |  | Contr | LOS | CUH - Custom House Station (East) |  | 2015-04-10 | 2015-04-09 16:28 | -1 | 2015-02-04 14:59 | Structural Engineering - Steel Member | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | FAO __ The escalator support steelwork has been manufactured to the following drawings: Cxxx-LAO-S-DDD-CR145_B-10480 revision P01 and 10276 revision P02 these were P-revision drawings at the time of manufacture
| 03SR - Stations (RfL) | Cxxx-NCR-000289 | NCR | ExCeL Bridge RC deck - Laying of Out of Specification Concrete |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-03-21 | 2015-03-10 13:23 | -11 | 2015-02-05 10:22 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 0.3cu of out of specification concrete was laid on the ExCeL bridge deck at the beginning of the main pour. The concrete was C40/50 but was slumped at 250mm. As much concrete as possible was removed with shovels and then in specification concrete was used to complete the area. The surface temperature of the out of specification concrete remained at >5deg until overlaid.
| 03SR - Stations (RfL) | Cxxx-NCR-000290 | NCR | Blocked well voids in column 516 |  | Contr | LOS | CUH - Custom House Station (East) |  | 2015-04-24 | 2015-04-23 18:21 | -1 | 2015-02-11 18:43 | Structural Engineering - Pre-cast | 500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | FAO __ the 5No air tubes at the top of the grout tubes in column 516 are all blocked. grouting the well voids from the bottom will therefore not work as there is nowhere for air to escape at the top.
| 03SR - Stations (RfL) | Cxxx-NCR-000291 | NCR | 13A/AA roof bolt box out of alignment |  | Contr | LOS | CUH - Custom House Station (East) |  | 2015-03-14 | 2015-03-03 14:01 | -11 | 2015-02-12 10:53 | Structural Engineering - Bolted Connections | 650 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | FAO __ The cast in bolt boxes in beams 712 and 714 at 13A/AA have been cast in out of tolerance and as a result the 36mm dia Macalloy bar is not able to be installed. See attached marked up drawing with as built dimensions
| 03SR - Stations (RfL) | Cxxx-NCR-000292 | NCR | Roof beam 728 well voids out of positional tolerance (20A-21A) |  | Contr | LOS | CUH - Custom House Station (East) |  | 2015-03-27 | 2015-03-19 18:57 | -8 | 2015-02-12 13:54 | Structural Engineering - Pre-cast | 600 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | FAO __ during the construction of roof beam 728, 2no well voids moved out of position by up to 15mm. it is not possible to install the beam as is. please see attached marked up photo showing the well voids.
| 03SR - Stations (RfL) | Cxxx-NCR-000293 | NCR | 14A/AA roof bolt box out of alignment |  | Contr | LOS | CUH - Custom House Station (East) |  | 2015-03-14 | 2015-03-03 14:02 | -11 | 2015-02-12 11:39 | Structural Engineering - Bolted Connections | 500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | FAO __ The cast-in bolt boxes in the roof beams at 14A/AA are out of tolerance and therefore the Macalloy bar does not fit. See attached photo.
| 03SR - Stations (RfL) | Cxxx-NCR-000294 | NCR | 12A Roof cross beam connections out of tolerance |  | Contr | LOS | CUH - Custom House Station (East) |  | 2015-07-29 | 2015-08-11 13:13 | 13 | 2015-02-23 12:26 | Structural Engineering - Pre-cast | 800 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | FAO __ The cast in pipes conduits in column 512 at 12A/AB roof level are out of positional tolerance and do not align with the holes in the cross beam end plates. See attached marked up photo
| 03SR - Stations (RfL) | Cxxx-NCR-000295 | NCR | Entrance Building Liftshaft - Debonding of Proofex Engage from poured concrete |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-03-18 | 2015-03-09 13:58 | -9 | 2015-02-16 13:58 | Civil - Civil Engineering General | 600 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following the flooding of the prepared lift shaft base works area, the bitumenous waterproof membrane sealant (Proofex LM) cracked down the vertical joints. The manufacturer stated that __ could apply detail strip down the affected edges to strengthen the joint on the understanding that backing strip had already been applied to the back faces of the membrane and the joint should be waterproofed anyway. The manufacturer stated that the detail strip should be rolled into the membrane to achieve a good key with the membrane's raised detail. Upon pouring the base and then striking the shutters, the membrane has debonded from the concrete edges (4 corners) due to the detail strip not allowing the concrete to bind to it. The strip was rolled into the membrane with suitable pressure and the concrete was 19N at time of striking.
| 03SR - Stations (RfL) | Cxxx-NCR-000297 | NCR | VDR wall grouting - level not achieved |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-05-01 | 2015-06-08 12:50 | 38 | 2015-02-23 12:17 | Civil - Civil Engineering General | 800 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | For the Attention of __. Please see attached photographs indicating the incorrect grout level underneath the VDR wall on GL AD. During the process some areas were cast low due to air entrapment. This was caused by not allowing a sufficient gap between the sutter and wall at the top to allow air to escape as the grout level rose.
| 03SR - Stations (RfL) | Cxxx-NCR-000298 | NCR | Movement joint plate not level in beam 712 12A/AB roof |  | Contr | LOS | CUH - Custom House Station (East) |  | 2015-03-27 | 2015-03-19 18:59 | -8 | 2015-02-23 16:02 | Structural Engineering - Pre-cast | 500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | FAO: __ the movement joint plate was not cast level in the beam 712 - see attached photos and sketches.
| 03SR - Stations (RfL) | Cxxx-NCR-000299 | NCR | Stainless steel roof plate alterations |  | Contr | LOS | CUH - Custom House Station (East) |  | 2015-04-10 | 2015-04-09 14:19 | -1 | 2015-02-24 09:56 | Structural Engineering - Pre-cast | 1500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | FAO: __ there have been some discrepancies in the roof level macalloy positions, the roof stainless steel plates need to be altered to fit. see attached sketch showing alterations required to roof plates. this refers to attached __ roof plate drawings
| 03SR - Stations (RfL) | Cxxx-NCR-000300 | NCR | ExCeL Bridge Cover Plates - Incorrect fixing plate centres |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-04-20 | 2015-04-22 18:30 | 2 | 2015-02-24 08:34 | Structural Engineering - Structural Engineering - General | 800 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The fixing plates welded to the ExCeL Bridge to accommodate the coverplates have been welded to the bridge at the incorrect centres. This has resulted in the plates not aligning with their fixing plates through approximately 5m of the bridge's length on either side.
| 03SR - Stations (RfL) | Cxxx-NCR-000301 | NCR | ExCeL Bridge - Upstand links set into pour with excess cover |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-03-31 | 2015-03-26 19:14 | -5 | 2015-02-24 16:53 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The upstand links on the ExCeL Bridge (South End) have been set into the first pour with excess cover to the top of them. This has been measured at a maximum of 70mm.
| 03SR - Stations (RfL) | Cxxx-NCR-000302 | NCR | Platform Screed GL2A-3A - Infill Grout Around Stair Steelwork |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-05-01 | 2015-04-20 11:52 | -11 | 2015-03-02 11:08 | Architectural - General | 750 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 4 areas of concrete screed on the platform level between GL2A-3A had to be broken back to allow stair steelwork to be bolted into the structural slab. The largest area being 1300 x 800mm
| 03SR - Stations (RfL) | Cxxx-NCR-000303 | NCR | ExCeL Bridge Deck - Concrete Finish |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-04-15 | 2015-04-15 16:37 | 0 | 2015-03-03 16:09 | Civil - Civil Engineering General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Due to concrete supply issues, the concrete finish on the ExCeL Bridge deck has not met specification for grade of finish or minimum cover in some areas.
| 03SR - Stations (RfL) | Cxxx-NCR-000304 | NCR | Damage to the VDR Concrete Wall by drilling and hitting rebar |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-04-30 | 2015-05-01 07:26 | 1 | 2015-03-06 13:57 | Fire - Fire Systems & General | 750 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | See attached photograph of the holes drilled out. On the VDR North Wall Grid Line 15A there are a number of 10mm dia holes drilled for the bracket to support the dry riser pipe work, the drilling was required to miss the rebar, but has hit the rebar in a number of cases. A metal detector was used but this did not show that the rebar would clash with the drilling.
| 03SR - Stations (RfL) | Cxxx-NCR-000305 | NCR | Couplers in concourse edge beams 533 and 537 out of position |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-05-01 | 2015-04-28 11:58 | -3 | 2015-03-06 11:04 | Structural Engineering - Pre-cast | 750 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The AG16 couplers for 2 no. 152 UC 37 columns supporting roof between GL 12A/AA and 14A/AA in concourse edge beams 533 and 537 have been cast incorrectly. Couplers have been cast in wrong location (as-built survey attached) and out of plumb.
| 03SR - Stations (RfL) | Cxxx-NCR-000307 | NCR | Unauthorised trail of repairs to full height VDR wall |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-07-17 | 2015-06-16 17:19 | -31 | 2015-03-16 11:16 | Structural Engineering - Finishes | 700 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Unauthorised trail of repairs was undertaken to one of the full height VDR walls. Bottom section of the VDR wall was bag washed without acceptance of method and material in oppose to application of acid wash as proposed in NCR 235.
| 03SR - Stations (RfL) | Cxxx-NCR-000308 | NCR | OHLE / dry riser pipe clash on the VDR columns at GL 15A and 20A |  | Contr | LAO | CUH - Custom House Station (East) |  | 2017-02-28 | 2016-10-21 10:05 | -130 | 2015-03-16 15:00 | Electrical - OHLE | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The OHLE and dry riser pipe clash on the VDR columns at GL 15A and 20A (refer to the attached drawings).
| 03SR - Stations (RfL) | Cxxx-NCR-000310 | NCR | Commencement of off site lift manufacture without accepted ITP in place |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-09-18 | 2016-04-21 06:55 | 216 | 2015-03-23 08:16 | Mechanical - Lifts | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Lift manufacture has commenced without ITP being accepted by Cross Rail field engineering team. ITP is currently in final review between __ and Cross Rail L&E Engineering and will be submitted upon acceptance.
| 03SR - Stations (RfL) | Cxxx-NCR-000311 | NCR | DLR Bridge - Site Plank Notching |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-05-08 | 2015-05-07 17:57 | -1 | 2015-03-25 21:51 | Structural Engineering - Pre-cast | 1500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Notches are required to be cut into the architectural precast planks to accommodate the already constructed and painted lifting lugs on the DLR bridge deck steel. Programme constraints on the __ manufacturing schedule of DLR planks and DAM structures DLR bridge structural steel detailing meant the lifting lugs, designed (as per document Cxxx-LAO-S-XCL-CR145_WS157_1-50005) by DAM structures and CAT III checked (Cxxx-LAO-S-XCL-CR145_WS157_1-50005) could not be accommodated in time for co-ordinated notch details to be provided within the __ detailed drawings. As such notching will have to take place on site. __ propose for notches to be cut into the plank to accommodate the 40mm wide and 150mm deep lifting lug. The lugs are located clear of the now reinstated cover plates as seen in the attachement '25-03-15 - Bridge Deck with Plank overlay'. The notch is proposed to be 75mm to allow for construction/installation tollerance and presence of welding (see attached photo taken during trial assembly). Any gaps visable from the underside of the bridge to be filled with approved sealant to colour match both plank (as used on precast components on main frame) and steelwork (anthracite colour as used on cladding components). PLease note planks are due to be installed in preparation for April possession installation date on the 2nd of april 2015
| 03SR - Stations (RfL) | Cxxx-NCR-000312 | NCR | DLR Bridge - Bolt Finishes |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-08-24 | 2015-07-21 18:33 | -34 | 2015-07-13 13:35 | Structural Engineering - Bolted Connections | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | NCR issued as outlined in attached email: RE_ DLR Bolts This NCR should be read with referecne to Cxxx-FCD-000186 - DLR Bridge Hollow Bolt Omission for Traditional Bolts During the trial assembly of the DLR bridge hollow bolts were replaced with traditional bolts as detailed in the closed FCD above. In additon to the above change BZP bolts were used as opposed to the specificed galvanised bolts. This NCR is raised to cover this deviation from the works information.
| 03SR - Stations (RfL) | Cxxx-NCR-000313 | NCR | Missing Post pour Witness points for WBS4 |  | Contr | LOS | CUH - Custom House Station (East) |  | 2015-04-30 | 2015-04-21 19:29 | -9 | 2015-03-30 17:11 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the installation of the pre-cast frame there were ammendments to the following documents: Cxxx-LAO-C-ITP-CR145_WS157_1-50041 Cxxx-LAO-C-ITP-CR145_WS157_1-50088 Post pour inspections became a witness point, however due to a miscommunication Crossrail did not receive an IRF to witness the post pour inspection for concrete and grout.
| 03SR - Stations (RfL) | Cxxx-NCR-000314 | NCR | VDR Bridge Friction Connection Painting |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-05-01 | 2015-05-05 19:54 | 4 | 2015-04-01 16:36 | Structural Engineering - Bolted Connections | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The 3no friction connections on the VDR bridge have been mispainted. All faying surfaces were to be left unpainted with no more than a 10mm encroachment into the faying surface footprint. The faying surface has been painted with Aluminium primer and Metagard L574 sealer.
| 03SR - Stations (RfL) | Cxxx-NCR-000315 | NCR | Lift manufacturing - commencement of works without accepted Quality Plan in place |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-08-15 | 2015-07-17 10:09 | -29 | 2015-04-07 16:45 | Mechanical - Lifts | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - No evidence of program review from Contractor's Quality Manager or Management | Completed |  | Lift manufacture has commenced without Quality Plan being accepted by Crossrail. Quality Plan is currently under review by __ quality team.
| 03SR - Stations (RfL) | Cxxx-NCR-000316 | NCR | DLR Bridge - Roof Construction with non code 1 MCR |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-05-29 | 2015-05-29 15:54 | 0 | 2015-04-08 15:13 | Architectural - Roofing & Exterior Treatment | 3000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | With reference to the incomplete FCD: FCD 191 - Perforated liner sheet omission. The DLR bridge roof was constructed without a code 1 MCR in place for the kalzip roofing system: The liner sheet, as detailed within MCR Cxxx-LAO-A-LRC-CR145_WS157_1-50279 - Material Compliance Record - 3400 __ - DLR Bridge - __ Roof (WBS 5C, 6A), is not as per Spec clause JH43.1212 p) 'Lining Sheet: __ Liner TR35/200S (trough perforated)' Instead a solid liner sheet, shown on drawing Cxxx-LAO-A-DWG-CR145_WS157_1-50281, has been installed and erected as part of the DLR bridge installation works during the April 2015 possession.
| 03SR - Stations (RfL) | Cxxx-NCR-000317 | NCR | DLR Bridge - Deck Connection Stud Hole Misalignement |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-05-21 | 2015-05-18 13:40 | -3 | 2015-04-09 17:22 | Structural Engineering - Bolted Connections | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | See attached DAM NCR 034 for stud misalignment detail and root cause analysis. Attached also is the email (and referenced emails) dated saurday 04/04/2015 17:04 from Cameron Corsby __ outlining __/DAM's remedial works actioned during the April possession. End plate post remedial work photos also attached. Further QA records are to be appended to this NCR when available.
| 03SR - Stations (RfL) | Cxxx-NCR-000318 | NCR | DLR Bridge - Roof Support Col Finish |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-07-31 | 2015-07-17 13:56 | -14 | 2015-04-09 18:08 | Structural Engineering - Finishes | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | The DLR Bridge support columns are below the specified finish as per Cxxx-LAO-S-DDA-CR145_Z-10002 General Notes Sheet 2 of 3 - Item 10 - Acceptable Quality for Visable Steelwork. In particular 'Surface quality of welds', whereby grinding works can be seen to have been used to finish the items prior to painting. These can be seen on the roof support columns along the entire length on the 150mm wide fabricated faces (the weld prepped plates - during the fabrication process). See attached photo. The roof columns were installed as part of the DLR bridge installation works during the april possession. They are in their finished painted state supporting the completed DLR Bridge structural steelwork and finished roof.
| 03SR - Stations (RfL) | Cxxx-NCR-000319 | NCR | Surface Drainage Outlet Positions - Concourse Level - Gridlines 7A-11A |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-05-21 | 2015-05-21 08:57 | 0 | 2015-04-21 08:39 | Civil - Drainage | 700 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Employer's design indicated that the Aco channels would pass over the structural movement joints at GLs 8A, 12A and 16A which is unfeasible. The resulting builder's work holes installed in the concourse level slab for the Aco channel outlets are incorrectly positioned as these were based on continuously laid channels.
| 03SR - Stations (RfL) | Cxxx-NCR-000320 | NCR | Entrance Building Link Bridge - Welds not ground flush |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-07-03 | 2015-07-08 08:39 | 5 | 2015-04-13 15:24 | Structural Engineering - Welding | 1000 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The welds have not been ground flush on the external elevations of the Entrance Building Link Bridge. For architectural reasons these are required to be flush.
| 03SR - Stations (RfL) | Cxxx-NCR-000321 | NCR | Entrance Building - 16no Base plates omitted from shop fabrication works |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-05-21 | 2015-05-22 16:59 | 1 | 2015-04-14 10:56 | Structural Engineering - Structural Engineering - General | 2000 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | In transfering detail from the "final state" CAD model to the "pre-cambered" CAD model, 16no base plates were omitted from the Entrance Building fabrication drawings on the half landing. These plates are required to fix the balustrade.
| 03SR - Stations (RfL) | Cxxx-NCR-000322 | NCR | Hole enlargement -dry riser |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-08-28 | 2015-08-27 16:31 | -1 | 2015-05-12 09:32 | Structural Engineering - Concrete Member | 2000 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The builders work holes shown on the attached drawings need to be increased / drilled to a larger size - this is to incorporate an external sleeve and the fire stopping detail
| 03SR - Stations (RfL) | Cxxx-NCR-000323 | NCR | Hole enlargement |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-09-04 | 2015-08-27 16:30 | -8 | 2015-05-12 14:13 | Structural Engineering - Concrete Member | 1500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Builders work holes for the ventilation ductwork that are shown on the attached drawings require enlarging in order to incorporate the fire stopping detail and the increased ductwork size.
| 03SR - Stations (RfL) | Cxxx-NCR-000324 | NCR | Cracks in the soffit of lattice slab 1427A-1__60-530 (GL 10A-11A) |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-06-12 | 2015-06-02 16:27 | -10 | 2015-04-20 16:39 | Structural Engineering - Pre-cast | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Cracks have been observed in the soffit of lattice slab 1427A-1__60-530. The width of the cracks varies between 0.1mm and 0.3mm (marked on the attached unit drawing).
| 03SR - Stations (RfL) | Cxxx-NCR-000325 | NCR | Hole enlargement/Hole boring |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-07-17 | 2015-07-21 18:08 | 4 | 2015-05-12 16:30 | Structural Engineering - Concrete Member | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Enlargement of builders work holes for refridgerant containment trays /and boring - drill non precast hole - 1 No
| 03SR - Stations (RfL) | Cxxx-NCR-000326 | NCR | CAN-101 Platform Canopy Glass Fitting Modification |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-10-31 | 2015-12-22 08:33 | 52 | 2015-04-25 13:45 | Architectural - Glazing | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the installation of the glass canopy GL13-14 the operatives modified the GM17 glass fittings on site to allow them to be installed. This involed slicing a 5-10mm piece away from a compent to allow it to fit closer to the fixing point.
| 03SR - Stations (RfL) | Cxxx-NCR-000327 | NCR | Blistering to waterproofing membrane on Concourse level at G/L 7A-11A |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-07-24 | 2015-07-24 11:51 | 0 | 2015-04-24 12:17 | Architectural - Roofing & Exterior Treatment | 1000 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Blistering occurred to waterproofing membrane on the Concourse at G/L 7-11A, that was applied on Tuesday 21.04.2015 and noticed on the morning of Wednesday 22.04.2015.
| 03SR - Stations (RfL) | Cxxx-NCR-000328 | NCR | VDR Bridge Friction Connection Splice Plate/Weld Clash |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-06-12 | 2015-06-03 11:32 | -9 | 2015-04-28 10:33 | Structural Engineering - Structural Engineering - General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | While attempting to finish the VDR bridge friction connections it became apparent that the large welds connecting the girder box to the I-Beam had not be sufficiently ground to allow the splice plate to sit flat on the faying surface (see photo).
| 03SR - Stations (RfL) | Cxxx-NCR-000329 | NCR | OHLE pile cap drawings. |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-06-05 | 2015-06-05 13:52 | 0 | 2015-04-28 12:18 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | During construction of the OHLE pilecaps some of the detailed contract Cxxx drawings were not at C revision. The reason for this was that Cxxx were not fully aware of their design responsibility hence the level of importance of design drawing update was reduced. In any case the structural design of the pilecaps and holding down bolts was already in place from the employers design by contract Cxxx. In the absence of Cxxx construction issue drawings the pilecaps were constructed in accordance with the following employers design drawings which were at C revision. Cxxx-ATK-S-DDA-CR145_Z-32590 through 32593 Cxxx-ATK-S-DDD-CR145_Z-36100 through 36102 No changes or additions were required to the employers design during production of the Cxxx detailed design drawings.
| 03SR - Stations (RfL) | Cxxx-NCR-000330 | NCR | ETFE roof off site painting commenced without accepted ITP |  | Crossrail | XRL | CUH - Custom House Station (East) |  | 2015-06-22 | 2015-06-16 16:26 | -6 | 2015-04-29 15:55 | Structural Engineering - Surface Treatment | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Off site painting to ETFE roof structural steelwork was carried out without an accepted ITP.
| 03SR - Stations (RfL) | Cxxx-NCR-000331 | NCR | Cracking to stair stringers at GL20A-21A |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-08-14 | 2015-08-11 13:14 | -3 | 2015-05-01 11:09 | Structural Engineering - Concrete Member | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Cracking has been observed to bottom corner of both stair stringers at gridline 20A-21A (pictures attached).
| 03SR - Stations (RfL) | Cxxx-NCR-000332 | NCR | VDR column 1427A-2APL72-057 dameged during lifting |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-06-20 | 2015-06-23 16:38 | 3 | 2015-05-01 17:29 | Structural Engineering - Concrete Member | 750 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | VDR column 1427A-2APL72-057 on GL20A was dameged during lifting process when column was erected. The extent of damaged has been marked on the attached sketch.
| 03SR - Stations (RfL) | Cxxx-NCR-000333 | NCR | 1427A-1BPL64-001, 002, 025, 075 and 084 - Peikko shoes out of tolerance |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-06-20 | 2015-05-29 17:41 | -22 | 2015-05-01 17:15 | Structural Engineering - Concrete Member | 1500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | In VDR units 1427A-1BPL64-001, 002, 025, 075 and 084 peikko shoes are out of tolerance. For detailed information see attached unit drawings.
| 03SR - Stations (RfL) | Cxxx-NCR-000334 | NCR | ETFE Roof Steelwork Column Paint Finish |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-08-27 | 2015-08-14 13:29 | -13 | 2015-05-07 18:31 | Structural Engineering - Finishes | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | The ETFE roof steelwork column paint finish is severely sub-standard and has suffered excessive transit and erection damage.
| 03SR - Stations (RfL) | Cxxx-NCR-000336 | NCR | VDR Bridge Bolted Connections |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-06-06 | 2015-06-03 11:36 | -3 | 2015-05-07 18:44 | Structural Engineering - Bolted Connections | 750 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Upon the Contractor's VDR bridge bolt check prior to structurally signing off the bridge, it was found that 2no HSFGs had not been tightened to specification. These HSFGs sit in the uppermost location on the crossbeam connection on GL CF/3C and are therefore inaccessible due to the precast lattice. See the attached sketch.
| 03SR - Stations (RfL) | Cxxx-NCR-000337 | NCR | VDR Bridge - Omission of lattice plank bearing ledges for planks 23 and 24 |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-06-07 | 2015-06-03 14:33 | -4 | 2015-05-08 09:06 | Structural Engineering - Structural Engineering - General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Bearing ledges for lattice planks 23 and 24 were omitted in the design of the VDR bridge beams. This has occured across the splice connections.
| 03SR - Stations (RfL) | Cxxx-NCR-000338 | NCR | Application of paint (Flowcoat SF41) onto plant rooms floors without code 1 method statement, ITP and MCR for silica sand. |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-06-22 | 2015-06-16 16:28 | -6 | 2015-05-08 15:23 | Architectural - Flooring | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The ITP and method statement were uploaded onto EB, however the documents were not returned as Code 1 status before application of paint to the plant room floors. The technical information for the silica sand has now been finalised with the supplier and uploaed onto EB (Cxxx-LAO-A-LRC-CR145_WS157_1-50310).
| 03SR - Stations (RfL) | Cxxx-NCR-000339 | NCR | Benchmark for painting of plant rooms floors (Flowcoat SF41) not approved |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-06-22 | 2015-06-16 16:29 | -6 | 2015-05-08 15:26 | Architectural - Flooring | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Benchmark for painting of plant rooms floors (Flowcoat SF41) was not approved as per ITP requirements.
| 03SR - Stations (RfL) | Cxxx-NCR-000340 | NCR | Balllast Board Con__e Panel and Steelwork MCR - Not Approved Prior to Work Commencing |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-06-22 | 2015-06-12 15:28 | -10 | 2015-05-12 13:12 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Ballast Board works commenced onsite prior to the following MCRs being approved on eB; Material Compliance Record - Ballast Boad and Slotted Concrete Post (WBS 11C) Cxxx-LAO-C-LRC-CR145_WS157_1-50539 Rev2.0 Material Compliance Record - Bolted Base Ballast Board Post Steelwork (WBS 11C) Cxxx-LAO-C-LRC-CR145_WS157_1-50551 Rev 1.0
| 03SR - Stations (RfL) | Cxxx-NCR-000341 | NCR | Cxxx OHLE Pile Cap - Damaged HD Bolt Thread |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-11-30 | 2015-11-26 16:16 | -4 | 2015-05-12 19:50 | Civil - Base Course | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | FAO Cxxx / Cxxx __ has damaged the south/east corner M42 HD Bolt thread on OHLE pile cap referenced “1” (Cxxx-OVE-C-DDB-CR001_Z-31100), located in between the eastbound and westbound tracks. OHLE pile cap was construted by Cxxx, refer attached plan and photo.
| 03SR - Stations (RfL) | Cxxx-NCR-000342 | NCR | ETFE roof structural Steelwork fabricated to non accepted drawings |  | Crossrail | XRL | CUH - Custom House Station (East) |  | 2015-06-26 | 2015-06-16 16:56 | -10 | 2015-05-14 22:13 | Structural Engineering - Steel Member | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | ETFE structural steelwork was fabricated using drawings which were not accepted by the Project Manager.
| 03SR - Stations (RfL) | Cxxx-NCR-000343 | NCR | DLR Bridge - Rodding Eye Pipe Penetration Omission |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-08-14 | 2015-08-14 15:53 | 0 | 2015-06-03 16:50 | Structural Engineering - Steel Member | 1500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The penetrations for 2 Number rodding eye pipes (as shown on drawing Cxxx-LAO-P-DWG-CR145_WS157_Z-50026) to pass through the finish retain angle on the DLR Bridge (as shown on Cxxx-LAO-S-DWG-CR145_WS157_1-50184) were not co-ordinated prior to fabrication. As such the holes must be established on site. __ propose for these holes to be established using a 89mm dia hole saw to allow the 75mm diameter pipe to pass into the finishes zone. These works are directly above the DLR track and will be completed from the DLR bridge scaffold platform proposed to be constructed during the June possession.
| 03SR - Stations (RfL) | Cxxx-NCR-000344 | NCR | Hole enlargement |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-09-16 | 2015-09-18 14:10 | 2 | 2015-05-22 15:48 | Structural Engineering - Concrete Member | 2000 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Enlarge holes to accommodate- sleeves and fire protection detail -as per the attached schedule Existing holes are not large enough to allow allocated services to pass through them . certain items that were intended to be installed have been re-designed -ie bip taps - now sit in telescopic housings - therefore larger holes required
| 03SR - Stations (RfL) | Cxxx-NCR-000345 | NCR | Non Pre-loaded bolt assemblies supplied to alternative standard |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-06-21 | 2015-06-16 16:22 | -5 | 2015-05-22 11:06 | Structural Engineering - Structural Engineering - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The non preloaded bolt assemblies have been supplied to a standard which differs from that specified in KM10. The supplier was told to supply in compliance with KM10 and supply a CE marked product. These two stipulations were in conflict with each other - the standards in KM10 (BS 4190) is not a standard which allows CE marking. The supplier has supplied a CE marked product but not in compliance with the specification. __ expected the assemblies to be fully compliant and submit the MCR prior to erection when the bolt certificates arrived on site. This has not been possible with this non-compliance. The MCR is still outstanding and the bolts in question have been identified on site in case future remedial actions require them to be removed.
| 03SR - Stations (RfL) | Cxxx-NCR-000346 | NCR | VDR wall 017 - too small opening for installation hydrant connection box |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-06-25 | 2015-06-16 17:03 | -9 | 2015-05-26 08:17 | Structural Engineering - Concrete Member | 800 |  | Design | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Opening in VDR wall unit 017 is too small for installing hydrant connection box Builderswork hole in VDR wall unit 017 for dry riser hydrant connection box has been sized the same as the box with no allowance for tolerance or clearance to install.
| 03SR - Stations (RfL) | Cxxx-NCR-000347 | NCR | MEP Works Commenced without Code 1 Approved Drawings |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-07-17 | 2015-07-30 13:59 | 13 | 2015-05-26 15:10 | Electrical - Cable Management | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Works to CMS & Fire Alarm System installation commenced without code 1 drawing approval.
| 03SR - Stations (RfL) | Cxxx-NCR-000349 | NCR | Entrance Building Upstand Engineering Error |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-07-01 | 2015-07-01 14:45 | 0 | 2015-06-01 09:33 | Civil - Civil Engineering General | 750 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The Entrance Building's door opening, formed by a drop down section in the Eastern upstand, has been wrongly set out and is therefore 315mm narrower than it should be by design.
| 03SR - Stations (RfL) | Cxxx-NCR-000350 | NCR | ExCeL Bridge Steel Pin Sub Grade |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-07-02 | 2015-06-29 10:21 | -3 | 2015-06-02 15:16 | Structural Engineering - Structural Engineering - General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | FCD140 previously requested that the ExCeL Bridge's steel pin sub grade be changed from S355 to EN355. This allowed the fabricator to lathe the pins smooth more easily. Upon receipt of the certificates, __ have identified the steel as EN24T.
| 03SR - Stations (RfL) | Cxxx-NCR-000351 | NCR | Entrance Building slab waterproofing membrane debonding |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-08-25 | 2015-08-21 09:29 | -4 | 2015-06-02 15:28 | Civil - Civil Engineering General | 1200 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the post pour inspection of the Entrance Building slab it was noted that there were areas of waterproofing membrane debonding - both the membrane from the concrete and the detail strip from the membrane. See the attached photos.
| 03SR - Stations (RfL) | Cxxx-NCR-000352 | NCR | Cxxx - North Track Slab Concrete Damage |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-07-03 | 2015-06-16 17:11 | -17 | 2015-06-03 09:47 | Civil - Base Course | 750 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Approx Location - East Bound Chainage 17270.446 South Face of the East Bound Track slab concrete has been damaged in 3 locations (refer to attached photos)
| 03SR - Stations (RfL) | Cxxx-NCR-000353 | NCR | Dry Riser Welding Flanges to Pipe Work |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-07-31 | 2015-07-23 08:50 | -8 | 2015-06-10 17:18 | Systems - Fire Detection systems and Mains | 1500 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The Dry Riser Pipe behind the inlet breaching valve on Grid Line 7A near the North Track Wall. This pipe has been installed previously in one section below Track Slab, to the Sub Basement - This pipe has a slightly smaller wall thickness and will not take a grooving machine for the pipe clamp bracket.
| 03SR - Stations (RfL) | Cxxx-NCR-000354 | NCR | Roof Steelwork - NSSS tolerances and roof levels |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-07-10 | 2015-06-24 09:27 | -16 | 2015-06-10 18:04 | Structural Engineering - Structural Engineering - General | 2000 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | In order to erect the ETFE roof steelwork to NSSS tolerances and achieve a good line along the front edge of the roof, the column base plate levels were locally adjusted. In some locations this has resulted in the base plates themselves being outside of NSSS tolerances and not having enough halfen bolt thread protrusion through the baseplate to secure it down. Currently the front edge of the roof steelwork is erected to within tolerance and the line is architecturally sound.
| 03SR - Stations (RfL) | Cxxx-NCR-000355 | NCR | Under strength 28 day result for VDR wall base GL20A-23A & GL 28A-30A |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-07-16 | 2015-07-23 09:23 | 7 | 2015-06-16 12:11 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | For the attention of __ (please refer to NCR 276). The 28 day grout cube strength is the under the required strength of 60MPa for the VDR wall base at GL 20A-23A and GL 28A-30A. See attached grout cube results for both pours. The achieved grout strengths for both pours are as follows: GL28A-30A - 28day = 51MPa, 56 day result unavailable. GL20A-23A - 28day = 47MPa, 56 day = 51Mpa
| 03SR - Stations (RfL) | Cxxx-NCR-000356 | NCR | Cracked Drain Pipe |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-07-31 | 2015-07-21 18:25 | -10 | 2015-06-18 19:27 | Civil - Drainage | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | FAO __ Refer attached extract from Drainage CCTV Report showing 2 x Fracture in 600 dia pipe between Manhole SWMH 01 -SWMH 02 at the 41 feet and 62 feet locations. Final air tests have been carried out for this run in accordance with BS EN 1610 cl 13.2 table 3, witnessed by CRL and passed. (refer attached)
| 03SR - Stations (RfL) | Cxxx-NCR-000357 | NCR | Minor Drainage Connection protrusions |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-07-31 | 2015-07-21 18:28 | -10 | 2015-06-18 18:48 | Civil - Drainage | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | FAO __ Refer attached extract of CCTV drainage report showing 3 x Pipe Intrusions locations, these are all at branch connection locations in the upper half of the pipe The locations are between the following manhole numbers; * SWMH 08-09 * SWMH 09-10 * SWMH 10-11
| 03SR - Stations (RfL) | Cxxx-NCR-000358 | NCR | Cross beam endplates misalignment with pipes/conduits |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-09-18 | 2015-09-18 14:12 | 0 | 2015-06-19 15:43 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Further to NCR 294, there are other locations where the cross beam end plates do not align with the cast in conduits and pipes. GL 9AA GL12AA (NCR294) GL12AB GL15AA GL17AA GL20AA GL20AB The attached document shows the extent of the material removal required.
| 03SR - Stations (RfL) | Cxxx-NCR-000359 | NCR | Roof Steelwork - Erection tolerances |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-07-22 | 2015-07-06 16:24 | -16 | 2015-06-22 11:01 | Structural Engineering - Structural Engineering - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Further to NCR 354, a more detailed as built survey of the Roof Steelwork has shown up a number of places where the rafters do not sit on gridline to within tolerance. See attached drawing.
| 03SR - Stations (RfL) | Cxxx-NCR-000360 | NCR | Works commenced on site without code 1 MCR approval |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-07-31 | 2015-08-03 16:55 | 3 | 2015-06-24 09:30 | Electrical - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Lightning protection works commenced wihtout approved MCRs. Whilst MCRs were 'approved' by the CEG functional lead at the time of installation, the MCRs had not been Code 1 on eB.
| 03SR - Stations (RfL) | Cxxx-NCR-000361 | NCR | Roof Steelwork - GL20/AB bent bolts |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-08-20 | 2015-08-18 11:29 | -2 | 2015-06-24 09:41 | Structural Engineering - Bolted Connections | 1500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Please see photo attached. In lining and levelling the ETFE roof steelwork, the base plate and rafter at GL 20 was moved an average of 20mm off grid to the West (NCR 359). The HD bolts at GL20/AB were also marginally out of position by 8mm to the East. The combined effect has resulted in the bolts being bent to the West as the steelwork has been tirfored across. Given the elevation of the roof steelwork, the effect of the tirforing went un-noticed throughout the initial operation and was picked up later.
| 03SR - Stations (RfL) | Cxxx-NCR-000362 | NCR | Glass Breakage |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-08-08 | 2015-08-03 16:56 | -5 | 2015-06-29 13:11 | Architectural - Balustrade | 2000 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A glass panel on GLAA 17-18 in the glass balustrade broke of it's own accord. This was witnessed by CRL & __ staff who were in the vicinity at the time. The weather conditions were warm and direct sunlight was on the area. On inspection of the panel, the fracture of the glass seemed to indicate an impact in the top left or bottom right of the panel (see photo 1). As it was confrimed by witnesses that nobody was in the vicinity, an impact on the top left was ruled out. On inspection of the bottom right, the weld between the face plate and end plate could be seen against the glass face (photo 3). On inspection of another similar base assembly (photo 4) it can be seen that some of the welds have been ground down and others have been missed. As a result of the the slight thermal expansion of the glass due to direct sunlight, it is believed the pressure imposed on th edge of the glass from the weld has caused the panel to fail.
| 03SR - Stations (RfL) | Cxxx-NCR-000363 | NCR | Screed Flatness To HVSR-A, HVSR-B and SRLV-B |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-07-28 | 2015-07-10 10:59 | -18 | 2015-06-30 15:53 | Architectural - Flooring | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Further to Cxxx-LAO-A-IRF-CR145_SUB031, on inspecting the surface flatness of the plantrooms it was found that in three small areas in the HVSR-A, HVSR-B and SRLV-B that the surface flatness falls from SR1 to SR2 finish. These areas are highlighted on the attached drawing.
| 03SR - Stations (RfL) | Cxxx-NCR-000364 | NCR | DLR Bridge - CRL Superstructure Connection Shim Detail |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-10-04 | 2015-09-03 16:40 | -31 | 2015-07-17 13:35 | Structural Engineering - Bolted Connections | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | See attached NCR report
| 03SR - Stations (RfL) | Cxxx-NCR-000365 | NCR | DLR Bridge - CRL Superstructure Connection Seal Detail |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-10-11 | 2015-10-14 09:18 | 3 | 2015-07-17 14:00 | Structural Engineering - Bolted Connections | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | See attached NCR report
| 03SR - Stations (RfL) | Cxxx-NCR-000366 | NCR | Displaced Branch Drainage joints |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-08-06 | 2015-07-21 18:29 | -16 | 2015-07-07 13:18 | Civil - Drainage | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Refer attached CCTV report showing details and locations of displaced drainage joints inside Saddle joints (Flexseal FA150B as per attached MCR Cxxx-LAO-C-LRC-CR145_WS157_1-50126) which have been used at connections between branch pipes and main 450mm diameter and 600mm diameter concrete stormwater pipes.
| 03SR - Stations (RfL) | Cxxx-NCR-000367 | NCR | WBS 3G Drainage Deliverable Records |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-08-06 | 2015-07-17 10:08 | -20 | 2015-07-07 18:16 | Civil - Drainage | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | In compilation of WBS 3G Drainage Deliverable Record Pack (Cxxx-LAO-C-LRC-CR145_WS157_1-50577) a number of missing data was discovered; 1) Installation dates for construction activities missing 2) Test results missing from checksheets
| 03SR - Stations (RfL) | Cxxx-NCR-000368 | NCR | VDR Lattice Plank Openings For Rainwater Pipes |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-08-27 | 2015-08-24 17:04 | -3 | 2015-07-06 17:44 | Civil - Civil Engineering General | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Drawing Cxxx-LAO-SDDA-CR145_Z-32203 shows 2 Nr 150 mm square openings in between GL CF and GL CG for 110 mm RWP outlets on the VDR bridge deck. The drawing does not take into account the lattice plank bearing ledge which closes the lattice plank openings by 75 mm to 75 mm x 150 mm.
| 03SR - Stations (RfL) | Cxxx-NCR-000369 | NCR | Station Entrance - 100mm Dia Branch Drain cracked (MH 01) |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-08-31 | 2015-08-07 08:45 | -24 | 2015-07-08 13:30 | Civil - Drainage | 650 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Refer attached plan and phoones. 100mm dia branch pipe has been damage and cracked.
| 03SR - Stations (RfL) | Cxxx-NCR-000370 | NCR | Cracking To Screed Over CMS - Excel Bridge - West - Central & Northern Sections |  | Contr | LAO | CUH - Custom House Station (East) |  | 2016-03-31 | 2016-04-05 12:53 | 5 | 2015-07-08 16:17 | Architectural - Flooring | 2000 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Cracking has occured on the screed which covers the trunking on the Excel Bridge on the western central and western northern containment runs. The screed reduces in depth over the 90 mm installed trunking and in two cases has cracked where the depth of installed screed is below the recommended 40 mm for Isopol SBR Unbonded Screed. D49 mesh has been installed over the containment providing reinforcement.
| 03SR - Stations (RfL) | Cxxx-NCR-000371 | NCR | Pre-cast element cracking - Concourse Beam at AD/GL16 to 17 |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-11-25 | 2015-11-24 14:26 | -1 | 2015-07-08 16:43 | Civil - Civil Engineering General | 2000 |  | Material | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | Further to NCR 278, a 300mm crack has been surveyed on the underside edge of the concourse beam running from AD/GL16 to GL17, at the GL16 end.
| 03SR - Stations (RfL) | Cxxx-NCR-000374 | NCR | Roof Steelwork - On site paint damage remedials (beams and rafters) |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-09-29 | 2015-08-14 13:28 | -46 | 2015-07-22 17:33 | Architectural - Roofing & Exterior Treatment | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | The ETFE roof steelwork suffered from poor steel surface weld preparation and jig clamp damage during fabrication and installation. This has manifested itself as imperfections in the paintwork.
| 03SR - Stations (RfL) | Cxxx-NCR-000375 | NCR | Concourse Screed Containment |  | Contr | LAO | CUH - Custom House Station (East) |  | 2016-02-05 | 2016-01-26 13:03 | -10 | 2015-07-23 11:55 | Electrical - Cable Management | 50000 |  | Material | Rework | 2 (6-60k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | Screed Containment not in accordance with electrical specification ref: Cxxx-LAO-E-RSP-CR145_WS157 1-50001 Clause JY60.1215.
| 03SR - Stations (RfL) | Cxxx-NCR-000376 | NCR | Builder's Work Hole To Lift Equipment Room 132 |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-08-31 | 2015-09-07 13:51 | 7 | 2015-07-27 14:20 | Civil - Civil Engineering General | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | FAO __-__ Drawing Cxxx-LAO-A-DDD-CR145_1-46606 indicates a 150 x 150 mm builder's work opening in the south west corner of the room. __ drawing Cxxx-LAO-M1-DWG-CR145_WS157_1-50050 indicates the hole for containment as being 250 x 400 mm. The existing hole is required to be enlarged.
| 03SR - Stations (RfL) | Cxxx-NCR-000378 | NCR | Platform Shelter Base Connection Detail |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-09-06 | 2015-09-07 14:05 | 1 | 2015-07-28 15:16 | Structural Engineering - Structural Engineering - General | 750 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Drawing Cxxx-LAO-S-DDD-CR145_1-10303 detail 2 shows an In Situ stitch between precast planks. The construction drawing Cxxx-LAO-C-DWG-CR145_WS157_1-50656 however does not show an In Situ stitch which is what has been constructed on site. There is a clear ambiguity in the design information. In order for the works to progress, the columns of the platform shelters have been installed without the stitch or approved alternative in place.
| 03SR - Stations (RfL) | Cxxx-NCR-000380 | NCR | Platform Plantroom GL8A - Screed Infill |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-10-23 | 2015-09-10 11:12 | -43 | 2015-07-29 10:41 | Civil - Base Course | 750 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A small area of screed and concrete base has been removed at GL8A (Refer attached Drawing and Photo) in platform plant rooms to allow the removal of wall partitions to gain access to allow remedial works for the Cxxx-NCR-000277 (Cracks in columns and beams at movement joints on concourse level works) to be carried out.
| 03SR - Stations (RfL) | Cxxx-NCR-000381 | NCR | Hole enlargement |  | Contr | LAO | CUH - Custom House Station (East) |  | 2016-01-18 | 2016-01-27 13:56 | 9 | 2015-08-08 14:39 | Structural Engineering - Concrete Member | 750 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Enlarge existing builders work holes
| 03SR - Stations (RfL) | Cxxx-NCR-000382 | NCR | hole enlargement |  | Contr | LAO | CUH - Custom House Station (East) |  | 2016-01-18 | 2016-01-25 11:40 | 7 | 2015-08-06 13:48 | Structural Engineering - Concrete Member | 1500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Enlarge holes - via the use of core drilling as per the attached schedule /sketches and pictures marked in orange
| 03SR - Stations (RfL) | Cxxx-NCR-000383 | NCR | Pull out force of 1.5kN used instead of 13.3kN as documented in the ITP for Pull Out testing. |  | Crossrail | XRL | CUH - Custom House Station (East) |  | 2015-10-30 | 2015-10-02 16:24 | -28 | 2015-08-03 13:48 | Civil - Drainage | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | On the 2nd of July 2015 a Cxxx Custom House site surveillance was carried out on the drainage system. Pull out test record sheet provided shows that the tensile pull force on the anchor bolt bracket fixing was 1.5kN, the current Inspection and Test Plan (Cxxx-LAO-M-ITP-CR145_WS157_1-50005 Rev 3.0) item 3.2 specifies that a pull test of 13.3kN tensile pull force should be carried out on the anchor bolts. Works information Volume 2B - Part 20.8 “The Contractor and his subcontractors and suppliers of any tier engaged in supplying, manufacturing, construction, installation, commissioning and testing or any other service connected with the works, shall maintain ITPs appropriate for the services they provide that are accepted by the Supervisor. These accepted ITPs shall stipulate the necessary level and frequency of tests and inspections for each aspect of the works and also stipulate; acceptance criteria…”
| 03SR - Stations (RfL) | Cxxx-NCR-000385 | NCR | Pull out test not carried out randomly across fixings |  | Crossrail | XRL | CUH - Custom House Station (East) |  | 2015-10-30 | 2015-09-15 14:03 | -45 | 2015-08-03 13:55 | Civil - Drainage | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | On the 2nd of July 2015 a Cxxx Custom House site surveillance was carried out on the drainage system. One of the test records provided shows that the tests were not randomly selected across 2.5% (1 in 40) of fixings as specified on item 3.2 of the Inspection and Test Plan (Cxxx-LAO-M-ITP-CR145_WS157_1-50005 Rev 3.0) with respect to the acceptance criteria parameter. The test result provided shows that the test was carried out only on Mezzanine level Grid Lines AF (3A- 10A) AG (10A-11A) whereas the pipe work runs on the Concourse, platform and sub platform levels as well. British Standards Code of Practice for the Selection and Installation of post-installed anchors in Concrete and Masonry; Clause 9.3 Tests to Check the Quality of Installation BS8539:2012 States that: The test procedures should be in accordance with CFA Guidance Note Procedure for site testing construction fixings – 2012 [N1]. Thus; Constructions Fixings Association Guidance Note part 5 Positioning of fixings for proof tests… “Should be chosen as far as possible at random throughout the project or throughout each discrete area in which tests are required”. Works information Volume 2B Part 20.8 states that: “…These accepted ITPs shall stipulate the necessary level and frequency of tests and inspections for each aspect of the works and also stipulate; acceptance criteria…”
| 03SR - Stations (RfL) | Cxxx-NCR-000386 | NCR | Test record sheet signed off before pull out test was carried out |  | Crossrail | XRL | CUH - Custom House Station (East) |  | 2015-08-31 | 2015-08-21 13:55 | -10 | 2015-08-03 13:59 | Civil - Drainage | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | On the review of the Pull Out test record sheet for the mezzanine level provided as a result of the Cxxx Custom House site surveillance on the drainage system, it was identified that the record sheet was signed off before the original test was carried out, records showing 09-02-2015 (date of sign off) and 15-04-2015 (date of test) respectively. Works information Volume 2B Part 13.2 states that: “The Contractor shall provide progressive assurance that the Contractor’s design (where appropriate) and the constructed works comply with the requirements set out in the contract. The Contractor’s progressive assurance will also be used by the Project Manager and Employer to demonstrate that the legal comm__ents and obligations placed on the contract by the Crossrail Act 2008 have been discharged. __ assurance means that there will be continual confirmation of compliance by the generation of contemporaneous records.”
| 03SR - Stations (RfL) | Cxxx-NCR-000387 | NCR | No calibration Certificate made available for pull out test equipment |  | Crossrail | XRL | CUH - Custom House Station (East) |  | 2015-08-31 | 2015-08-27 16:28 | -4 | 2015-08-03 14:02 | Civil - Drainage | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | On the 2nd of July 2015 a Cxxx Custom House site surveillance was carried out on the drainage system, it was observed that there was no appropriate calibration certificate supporting the __ HAT28 tensile tester which was used for the pull out test of the __ screw anchors on the mezzanine level. The __ calibration certificate (Notification no 4516540114) provided for the HAT28 tensile testing system is denoted serial number HT012954B which is different from the one detailed in the pull out test record provided serial number 010571. Works information Volume 2B Part 20.8 states that: “The Contractor shall maintain a schedule of all inspection, measuring and test Equipment used for the works that includes records of the calibration of such Equipment to nationally recognised standards.”
| 03SR - Stations (RfL) | Cxxx-NCR-000388 | NCR | Installation of Pipe work for drainage system carried out without appropriate coordinated installation drawing |  | Crossrail | XRL | CUH - Custom House Station (East) |  | 2015-08-31 | 2015-08-18 08:16 | -13 | 2015-08-03 14:04 | Civil - Drainage | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | On the 2nd of July 2015 a Cxxx Custom House site surveillance was carried out on the drainage system, it was identified during the Cxxx Drainage System surveillance that the installation of the pipe work for the drainage system was not carried out with the appropriate coordinated installation drawing indicating how the drainage system interfaces with other services. Works information Volume 2B 7.7.3 states that: “Prior to commencing the design of any part of the works, the Contractor produces a design statement and submits it to the Project Manager for acceptance. The Contractor does not start design work until the Contractor’s design statement has been accepted by the Project Manager.” More so the Contractor’s Design Statement Cxxx-LAO-M-XST-CR14_WS157_1-50001 Rev4 states that “co-ordinated working drawings are to be produced during Stage J/K”. The document refers to BSRIA Framework for Building Services document which shows that the drawings should be provided with full setting out information for installation.
| 03SR - Stations (RfL) | Cxxx-NCR-000389 | NCR | Platform Canopy Connection Plate Bolt Engagement |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-11-06 | 2015-10-30 15:11 | -7 | 2015-08-13 16:52 | Structural Engineering - Bolted Connections | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There are instances of loose bolts/spinning washers in the connection plates of the platform canopy. This implies that the bolts are not working as the design intends them to. See attached photo.
| 03SR - Stations (RfL) | Cxxx-NCR-000391 | NCR | Platform Canopy Pin Bearing Lengths |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-11-06 | 2015-10-30 15:08 | -7 | 2015-08-13 17:14 | Structural Engineering - Bolted Connections | 750 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | Due to fabrication tolerance, some of the platform canopy connection fin plates are slightly misaligned with the beam fin plates. This has led to the bearing length of the pin needing to be greater than 46mm - the ordered size - in 4no instances. See survey attached.
| 03SR - Stations (RfL) | Cxxx-NCR-000392 | NCR | DLR Bridge - Intumescent Paint Blistering |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-10-20 | 2015-10-15 12:06 | -5 | 2015-08-21 14:23 | Structural Engineering - Surface Treatment | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | __ have observed sporadic paint blisters on the outer faces of the DLR bridge main beams that appear only during hot weater/direct sunlight and dissapear during overcast weather conditions. A __ paint specialist visited site on the 13th of August (with John Walker of crossrail in attendance) to diagnose the problem. Initial thoughts from the site inspection put the cause at a combination of the following: Natural Solvent presence and curing process Extreme hot weather experienced during July/Aug 2015 Eastern and western facing beams capture direct sunlight over the suns rise and set direction 2 hour fire protection required on bridge deck and consequent thickness of solvent based intuemscent paint See attached photo for blisters (although difficult with light conditions to clearly capture blisters) See attached __ paint report and specification
| 03SR - Stations (RfL) | Cxxx-NCR-000393 | NCR | Hole relocation |  | Contr | LAO | CUH - Custom House Station (East) |  | 2016-01-29 | 2016-02-03 16:40 | 5 | 2015-09-24 11:45 | Structural Engineering - Concrete Member | 750 |  | Planning | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Re-routing of Cleaners cupboard Extract Ductwork
| 03SR - Stations (RfL) | Cxxx-NCR-000395 | NCR | Station Earth Mat Resistance |  | Contr | LAO | CUH - Custom House Station (East) |  | 2016-09-30 | 2016-09-13 15:08 | -17 | 2015-08-24 17:23 | Electrical - Electrical Engineering General | 4000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | Initial testing of the two station Earth Mats show that both mats have an earth resistance greater than permissible. Clause JW51.1203 of The Electrical Specification - Cxxx-LAO-E-RSP-CR145_WS157_1-50001, states that the Earth Mats shall have a maximum earth resistance of 1.0ohm each. Our initial readings have shown resistances of approximately 2 and 15ohms. Please note that the testing of earth resistance will need to completed again using a known earth to achieve a more accurate reading. Update: 08/01/2016 Earth test conducted as per supporting doc Cxxx-LAO-E-RGN-CR145_WS157_1-50013. Results of the tests have deemed the earth mats acceptable. Update: 22/06/2016 'Known Earth' at VDP still not confirmed. VDP reundertook tests, however the VDP report is at Code 3. Cxxx report to be reissued following confirmation of VDP 'known earth'.
| 03SR - Stations (RfL) | Cxxx-NCR-000397 | NCR | D73 Opening in Concrete Upstand Position |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-10-05 | 2015-09-24 09:48 | -11 | 2015-08-26 11:23 | Structural Engineering - Concrete Member | 750 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The architecutral intent indicated on Cxxx-LAO-A-DDC-CR145_Z-44208 shows the glazing joint to the north of D73 aligning with with the crank in underside of the stair steelwork. The concrete upstands shown on Cxxx-LAO-S-DDB-CR145_Z-34000 and the setting out of the opening in the upstand for D73 mean that this architectural intent is not possible. It appears the designs have not been coordinated.
| 03SR - Stations (RfL) | Cxxx-NCR-000398 | NCR | Bent Platform Canopy Fin Plates |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-11-27 | 2015-11-27 16:01 | 0 | 2015-08-26 12:24 | Structural Engineering - Steel Member | 2000 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The rear fin plates on top of the cantinlever beams on the platform canopy appear out of alignment when compared with the other 2 fins on the same beam. This is also visible by the variable packaing on the glass canopy bracket as seen on the attached photograph. The fins appear to be within NSSS tolerances but are not architecturally acceptable as the public have a line of sight along the brackets.
| 03SR - Stations (RfL) | Cxxx-NCR-000399 | NCR | Lift Pit 1 embedded RWP air tests |  | Contr | LAO | CUH - Custom House Station (East) |  | 2016-05-17 | 2016-05-18 07:29 | 1 | 2015-08-26 12:20 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __ are unable to achieve acceptable air test results for the 4no embedded RWPs in Lift Pit 1. The full length of the pipe work also requires lining to support the case for the pipe work remaining in the lift shaft. The lining will strengthen the joints and effectively remove the requirement for future maintenance.
| 03SR - Stations (RfL) | Cxxx-NCR-000400 | NCR | Entrance Building - Slab ductwork misplacement and omission |  | Contr | LAO | CUH - Custom House Station (East) |  | 2016-04-15 | 2016-04-07 08:21 | -8 | 2015-10-14 10:43 | Civil - Civil Engineering General | 2000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | There are 3no ducts embedded in the Entrance Building slab which conflict with the architectural wall partitioning and an internal access way. The ducts were misplaced due to the alignment of the partition wall and the pile cap underneath; the ducts could not be taken through the pile cap and were placed as close to it as possible. There are also 3no ducts missing from the Entrance Building slab; this has become evident during MEP design development and the Urban Realm Design Phase.
| 03SR - Stations (RfL) | Cxxx-NCR-000401 | NCR | Drilling additional 75mm holes in precast slabs |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-12-18 | 2016-01-27 13:58 | 40 | 2015-08-27 14:12 | Structural Engineering - Concrete Member | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Numerous additional 75mm holes are required for M&E services. Approx position and number of new holes have been marked on the attached drawing. Exact position of new 75mm holes will be recorded on red-line drawings.
| 03SR - Stations (RfL) | Cxxx-NCR-000402 | NCR | IRSs not issued for Hold Points - Cable Management Systems |  | Contr | LAO | CUH - Custom House Station (East) |  | 2020-01-20 | 2019-12-06 12:20 | -45 | 2019-12-06 08:46 | Electrical - Cable Management | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the installation of the Cable Management System (CMS) for the MOHS rooms, the Client was not made aware of, or invited to inspect the "Installation of Cable Management System" hold point of the CMS Inspection and Test Plan.
| 03SR - Stations (RfL) | Cxxx-NCR-000403 | NCR | OHLE brackets GL15 and GL20 not fabricated to approved drawing |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-11-27 | 2015-11-27 16:07 | 0 | 2015-08-27 16:43 | Structural Engineering - Structural Engineering - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The OHLE brackets at GL15 and GL20 have not been fabricated to accepted fabrication drawing, Cxxx-LAO-S-DWG-CR145_WS157_1-58165 Although the current product is deemed to be architecturally better than that shown on the drawings, it was not accepted via the correct channels. The fabrication of the existing bracket was not possible due to access for welding to the rear of the plate. A rolled section was deemed to be a better solution.
| 03SR - Stations (RfL) | Cxxx-NCR-000404 | NCR | Unapproved filler used to prepare onsite welded joints |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-11-27 | 2015-11-04 12:05 | -23 | 2015-09-02 17:20 | Architectural - General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Due to the size of the platform canopy steelwork, it was proposed and agreed to weld the main beam joint on site to allow them to be delivered to site without specialist escorts. The main sections of the steelwork were painted off site with a clear strip left untouched to allow welding to be carried out. Once the welding was complete and tested, the welds were ground flush as per the architecutral requirements. It was unrealistic to expext the grinding to make the weld completely flush and as a result filler was required to smooth out the area. . See attached email confirmation from __ confirming the filler and paint system are compliant. The use of filler had not been approved prior to it's use in this scenario however the filler has been used elsewhere on the project where it was confirmed as acceptable. See Cxxx-NCR-000374 for the details.
| 03SR - Stations (RfL) | Cxxx-NCR-000405 | NCR | Materials Proposal Schedule |  | Crossrail | XRL | CUH - Custom House Station (East) |  | 2015-12-23 | 2015-12-18 13:19 | -5 | 2015-09-04 14:34 | Materials - Approval | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | A pre-surveillance review of the current MPS Cxxx-LAO-Z-TSC-CR145_WS157_1-50001 rev 8.0 decal code 4, found that it was last up-dated on the 18th of June 2014. The MPS contained a section for Architectural materials, with sixty materials listed, that had no eB numbers.
| 03SR - Stations (RfL) | Cxxx-NCR-000406 | NCR | Material Compliance |  | Crossrail | XRL | CUH - Custom House Station (East) |  | 2016-11-25 | 2016-10-21 09:31 | -35 | 2015-09-04 14:42 | Materials - Approval | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | On reviewing the above architectural materials it was found that the above list had been decal code 2 (“Not accepted. Revise and resubmit. Work may proceed subject to incorporation of changes indicated”) for more than three months, as such the Contractor had therefore been working with documents that were not current
| 03SR - Stations (RfL) | Cxxx-NCR-000407 | NCR | Material storage and Protection |  | Crossrail | XRL | CUH - Custom House Station (East) |  | 2015-11-27 | 2015-11-27 16:03 | 0 | 2015-09-04 14:48 | Materials - General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The glazing on the northern perimeter of the upper level of the station building and the glazed cladding on the station building have not been protected against possible damage from the movement of stored material, and future planned works, i.e. paving and roofing.
| 03SR - Stations (RfL) | Cxxx-NCR-000408 | NCR | Alignment of Builder's Work Holes On Platform |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-10-30 | 2015-10-26 13:47 | -4 | 2015-09-15 09:27 | Civil - Civil Engineering General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | FAO __. The installed builder's work holes to allow the spigots drop down from the Aco Drainage System are aligned on the platform parallel to Gridline AA and AB, however the Aco drainage channel converges from GL25 to GL32 as indicated on drawings Cxxx-LAO-A-DDA-CR145_1-42413, Cxxx-LAO-A-DDA-CR145_1-42414 and Cxxx-LAO-A-DDA-CR145_1-42415 and misses the builder's work holes as a result.
| 03SR - Stations (RfL) | Cxxx-NCR-000409 | NCR | Lack of MEP electrical works witness points during the installation of the BMS in the MOHS rooms |  | Crossrail | XRL | CUH - Custom House Station (East) |  | 2016-09-09 | 2016-09-07 16:17 | -2 | 2015-09-07 14:20 | Electrical - Electrical Engineering General | 1000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | During the installation of the BMS in the MOHS rooms, the CRL MEP Field Engineering Team did not receive any IRFs as stipulated by the Cable Management ITP (referenced below). For example, Inspection number 3.9 states that a check should be carried out to assure that the “CMS is installed as per construction drawing”. This is to be done after each section is completed and should be recorded on the ITP check sheet. This is a CRL witness point and no IRF was received during installation.
| 03SR - Stations (RfL) | Cxxx-NCR-000410 | NCR | Crack to stair stringer (GL 15) |  | Contr | LAO | CUH - Custom House Station (East) |  | 2016-02-26 | 2016-06-03 16:06 | 98 | 2015-09-16 10:23 | Structural Engineering - Concrete Member | 750 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the installation of the balustrade on top of the Northern stair stringer at GL15, the installation of the fixing has caused the face of the stringer to crack. See attached photo. Following a routine crack survey there were also found to be hairline cracks in the stair stringer which have been attributed to balustrade fixings.
| 03SR - Stations (RfL) | Cxxx-NCR-000411 | NCR | Builders work Holes |  | Contr | LAO | CUH - Custom House Station (East) |  | 2016-01-18 | 2016-01-25 11:39 | 7 | 2015-09-25 13:02 | Structural Engineering - Concrete Member | 2000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Enlarge /core drill builders work holes
| 03SR - Stations (RfL) | Cxxx-NCR-000414 | NCR | Inspection Sheets for earth rods and mats installation |  | Crossrail | XRL | CUH - Custom House Station (East) |  | 2016-10-07 | 2016-09-13 15:11 | -24 | 2015-10-08 15:51 | Electrical - Electrical Engineering General | 2000 |  | Testing and Commissioning | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | NCR has been raised to ensure that the Inspection Sheets for the earth mats and rods are part of the hand-over documentation and are available for CRL inspection as required by the Inspection and Test Plan.
| 03SR - Stations (RfL) | Cxxx-NCR-000415 | NCR | Soil Resistivity Report |  | Crossrail | XRL | CUH - Custom House Station (East) |  | 2016-10-07 | 2016-09-19 12:35 | -18 | 2015-10-08 15:43 | Electrical - Electrical Engineering General | 2000 |  | Design | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | NCR has been raised due to the unavailability of a Soil Resistivity report which is part of the Cxxx deliverables a scheduled in Cxxx Custom House Specs and Reports Index Contract within the Works Information Volume 2C
| 03SR - Stations (RfL) | Cxxx-NCR-000416 | NCR | Dry Riser Pipe Work Through Slab Clash With Panel Boxes - Platform Level |  | Contr | LAO | CUH - Custom House Station (East) |  | 2016-02-26 | 2016-05-18 08:31 | 82 | 2015-10-14 07:25 | Fire - Fire Systems & General | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The dry riser pipe work rises through the concrete slab at Platform Level (2-No) between GL5A and GL6A is incased in a paneled box, the pipe work sleeve through the floor cannot be installed as the valves are touching the rear of the box and the front face of the pipe work is touching the front of the core drilled hole through the concrete slab. Please see attached photo for location.
| 03SR - Stations (RfL) | Cxxx-NCR-000417 | NCR | Pipe Sleeves (fire stopping) Required for AC Pipe Work Through Concrete Slabs |  | Contr | LAO | CUH - Custom House Station (East) |  | 2017-05-26 | 2017-06-01 09:44 | 6 | 2015-10-15 12:55 | Mechanical - Heating Ventilation & Air Conditioning | 150 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The AC Pipes with the Insulation passes and feeds through the concrete slabs, as per the __ detail drawing Cxxx-LAO-M-DDD-CR145_Z-56003, the tray holding the AC pipe work and insulation stops either side of the hole through the concrete slab. The fire stopping in the hole would be around the pipe work and the insulation to the pipe work. It is suggested by Crossrail that there should be fire rated insulation around the AC pipe work where the pipes are passing through the holes in the concrete slab. __ have agreed that as per the attached detail, that this is the correct way for the installation.
| 03SR - Stations (RfL) | Cxxx-NCR-000418 | NCR | Escalator works commenced without an accepted ITP. |  | Crossrail | XRL | CUH - Custom House Station (East) |  | 2015-11-27 | 2015-11-26 09:27 | -1 | 2015-10-20 16:18 | Mechanical - Escalators | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | __ have commenced works on site without an accepted ITP. Cxxx-LAO-M1-XCS-CR145_WS157_1-50052 rev 1 has been coded 3.
| 03SR - Stations (RfL) | Cxxx-NCR-000419 | NCR | AM-103 Roof Coping |  | Contr | LAO | CUH - Custom House Station (East) |  | 2016-04-29 | 2016-04-18 09:25 | -11 | 2015-10-22 12:33 | Architectural - Roofing & Exterior Treatment | 50000 |  | Manufacturing Defect | Rework | 2 (6-60k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | The AM-103 roof coping has been delivered and installed to both roofs and has shade/color variances between each of the aluminum anodized panels. Having been asked for evidence of compliance with JZ33.1101 (d) and confirmation that one batch of the correct grade of material was used, the sub contractor was unable to provide the evidence. Control samples were also not produced as per JZ33.1102 (h and I) to provide a benchmark of acceptable limits on site.
| 03SR - Stations (RfL) | Cxxx-NCR-000420 | NCR | ACO Drainage Pipe Work and Outlets Not Lining Up |  | Contr | LAO | CUH - Custom House Station (East) |  | 2016-01-14 | 2016-01-12 10:50 | -2 | 2015-11-01 08:25 | Mechanical - Public Health Engineering | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The drainage pipe work connections and the ACO drainage at the Concourse Level, these outlets from the ACO drainage do not line up with the drainage outlet pipe work, please see the attached photograph.
| 03SR - Stations (RfL) | Cxxx-NCR-000421 | NCR | Builderswork Holes - Concourse Screed Containment |  | Contr | LAO | CUH - Custom House Station (East) |  | 2016-04-08 | 2016-04-07 08:24 | -1 | 2015-11-04 08:38 | Structural Engineering - Pre-cast | 2000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Enlarge /core drill builders work holes
| 03SR - Stations (RfL) | Cxxx-NCR-000422 | NCR | Below Ground Drainage Connection 100mm dia Should be 150mm Sub Platform Level |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-11-30 | 2015-11-26 15:08 | -4 | 2015-11-09 15:52 | Mechanical - Public Health Engineering | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The below ground drainage pipe connection in the Sub Basement (Grid Line 10A) has been supplied as 100mm dia, this should be 150mm dia as per the __ design drainage drawings - Please see the attached marked up photograph.
| 03SR - Stations (RfL) | Cxxx-NCR-000424 | NCR | A full set of IFC drawings, associated data and specifications not maintained on site |  | Contr | LAO | CUH - Custom House Station (East) |  | 2015-12-16 | 2015-12-16 10:15 | 0 | 2015-11-09 15:49 | Mechanical - Lifts | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | A full set of IFC drawings, associated data and specifications were not maintained on site, as required by Clause 13.3 6.1 of the Works Information Volume 2B.
| 03SR - Stations (RfL) | Cxxx-NCR-000425 | NCR | Domestic water MCRs approval |  | Crossrail | XRL | CUH - Custom House Station (East) |  | 2016-02-12 | 2015-12-22 08:40 | -52 | 2015-11-19 09:38 | Mechanical - Public Health Engineering | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | This NCR has been raised to ensure that all MCRs associated with the domestic cold and hot water installation will be approved by CRL prior to the system installation as required by WIv2B part 7.7.8.2. For details refer to the surveillance report ref. no. Cxxx-XRL-O4-RGN-CR001-50019.
| 03SR - Stations (RfL) | Cxxx-NCR-000426 | NCR | Construction drawings (IFC) without required information on them |  | Crossrail | XRL | CUH - Custom House Station (East) |  | 2016-03-31 | 2016-03-21 11:47 | -10 | 2015-11-19 09:45 | Mechanical - Public Health Engineering | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | This NCR has been raised on the grounds of the construction drawings being without setting out information as per the Contractor’s MEP Design Statement. For further information refer to surveillance report ref. no. Cxxx-XRL-O4-RGN-CR001-50019.
| 03SR - Stations (RfL) | Cxxx-NCR-000427 | NCR | Installation of domestic cold and hot water system to P0x status drawing |  | Crossrail | XRL | CUH - Custom House Station (East) |  | 2016-02-26 | 2016-04-19 09:48 | 53 | 2015-11-19 09:49 | Mechanical - Pumps | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | This NCR has been raised for carrying out domestic cold and hot water installations to P0x status drawings which is not in line with WIv2B part 7.7.8.2. For further information refer to surveillance report ref. no. Cxxx-XRL-O4-RGN-CR001-50019.
| 03SR - Stations (RfL) | Cxxx-NCR-000429 | NCR | Non Compliance with Planning Requirements |  | Contr | LAO | CUH - Custom House Station (East) |  | 2016-04-29 | 2016-04-21 06:53 | -8 | 2015-11-26 16:49 | Architectural - Finishes | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Installation of architectural works such as cladding commenced prior to submitting samples to the London Borough of Newham (LBN) for approval in accordance with Schedule 7 and TCPA planning approvals.
| 03SR - Stations (RfL) | Cxxx-NCR-000430 | NCR | GL13 Roof beam support columns movement on GLAA |  | Contr | LAO | CUH - Custom House Station (East) |  | 2016-01-19 | 2016-01-18 12:08 | -1 | 2016-01-05 15:27 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | **Retrospective** The 2no 152 UC 37 columns supporting the roof beam on GLAA at the DLR bridge interface do not align with the cast in couplers in the concourse level beam.
| 03SR - Stations (RfL) | Cxxx-NCR-000431 | NCR | Dry Riser Short Radius Bends |  | Contr | LAO | CUH - Custom House Station (East) |  | 2016-09-16 | 2016-09-07 16:11 | -9 | 2016-01-07 07:00 | Fire - Fire Systems & General | 1000 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | There are some short radius bends used in the construction of the dry riser pipe work, it has been pointed out to our subcontractor (__) that short radius bends can only be used where long radius bends cannot be installed due to space constrictions.
| 03SR - Stations (RfL) | Cxxx-NCR-000432 | NCR | Material installed in Lift Motor Room without approved MCR |  | Crossrail | XRL | CUH - Custom House Station (East) |  | 2016-05-09 | 2016-05-26 09:32 | 17 | 2016-01-07 14:44 | Electrical - Cable Management | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Following a site inspection within the Station Entrance Lift Motor room it was observed that the trunking being installed is not compliant with the M&W Specifications and does not have an approved MCR permitting its use. The Contractor was advised and did not return a response.
| 03SR - Stations (RfL) | Cxxx-NCR-000433 | NCR | Use of Washers not in accoradnce with M&W Specifications |  | Crossrail | XRL | CUH - Custom House Station (East) |  | 2016-03-31 | 2016-01-18 12:11 | -73 | 2016-01-07 15:03 | Electrical - Cable Management | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | On a number of occasions the CRL MEP FE has questioned the lack of washers installed on CMS and CMS supports as required within Specification Cxxx-LAO-E-RSP-CR145_WS157_1-50001 All metalwork should be secured using both washers and shake proof washers.
| 03SR - Stations (RfL) | Cxxx-NCR-000435 | NCR | Installation drawings for lighting system |  | Crossrail | XRL | CUH - Custom House Station (East) |  | 2020-10-15 | 2020-10-21 09:30 | 6 | 2020-10-01 11:36 | Electrical - Lighting | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | The Cxxx-LAO-E-DDA-CR145-62407 rev. P05 was issued for the gate 3 review and has been accepted by CRL. Following that, revision C01 of the drawing was issued as ‘Issued for Construction’. This drawing was a basis for the production of Contractors ‘installation’ drawing reference number Cxxx-LAO-E-DWG-CR145_WS157_1-50054 rev C01. This ‘installation’ drawing shows all setting out information and, as advised by the Contractor, had been derived from a coordinated 3D model. It has been noted that the drawing has some information missing, which were shown on the ‘Issued for construction’ drawings e.g. all wiring, cable containments and description of light fittings. For details refer to surveillance report ref. no. Cxxx-XRL-O4-RGN-CR001-50020
| 03SR - Stations (RfL) | Cxxx-NCR-000436 | NCR | Cxxx-Cxxx coodingation of electrical drawings |  | Crossrail | XRL | CUH - Custom House Station (East) |  | 2020-10-15 | 2020-10-21 09:42 | 6 | 2020-10-01 11:31 | Electrical - General | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The contractor was requested to demonstrate that the system wide contract Cxxx requirements have been coordinated and incorporated in the Cxxx design. The surveillance team was provided with Cxxx drawing ref. no. 650-ALC-E-DDL-CR145_1-00204 rev C01 ‘Issued for Construction’ dated 05 August 2015 showing the plant position in HV Transformer B. For high level containment the drawing refers to Cxxx-ALC-E-DDL-CR145_1-00404 rev C01 ‘Issued for Construction’ which shows the position of cable trays entry and exit to the room. The Cxxx contract electrical containment drawing covering this area is the drawing ref. no. Cxxx-LAO-E-DDA-CR145-62605 rev P05 dated 24 June 2015. This drawings previous revision was C01 and it does not state in the description box what was the reason for reverting it to the preliminary statues. The drawing shows a different routing for the high level containment than the Cxxx drawings and there is not evidence that these drawings have been coordinated. For details refer to document ref. no. Cxxx-XRL-O4-RGN-CR001-50020.
| 03SR - Stations (RfL) | Cxxx-NCR-000437 | NCR | Lifting Tiles on Platform GL 21-22 |  | Contr | LAO | CUH - Custom House Station (East) |  | 2016-09-30 | 2016-09-29 15:16 | -1 | 2016-02-10 16:19 | Architectural - Flooring | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | It has been observed that approximately 6 m2 of tiles between GLs 21 and 22 have lifted from the installed isopol screed. No damaged has occurred to the screed as the bond to the tile bed has delaminated. The tiles lifted due to the ARDEX A38 Screed being laid on saturated base Flowcrete screed and the reaction that followed. Paul Forrester (Business Development Manager at ARDEX), advised that in his opinion the cause of the tile ARDEX expanding was a reaction at the interface of the flowcrete screed and ARDEX screed of the respective cement contents causing expansion of the material and thus the tiles “blowing”. This can be avoided if the base flowcrete screed is hydrated but not saturated. Standing water should therefore be removed from areas to be laid at least 48 hours before laying further screed and areas of fresh laid tiles covered with polythene to prevent rain affecting the water content of the screed. The manufacturer's report quoting the details, experience thereof and laboratory experiments during which the expansion and delamination of the screed was recreated is attached.
| 03SR - Stations (RfL) | Cxxx-NCR-000438 | NCR | Installation Of SMJ At GL21 In Room 606 |  | Contr | LAO | CUH - Custom House Station (East) |  | 2016-04-15 | 2016-04-05 12:39 | -10 | 2016-02-24 14:24 | Architectural - Flooring | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Drawing Cxxx-LAO-A-DDA-CR145_1-42412 C02 does not indicate the inclusion of M__-501 in the floor finish of Room 606 beneath the stairs. Drawing Cxxx-LAO-A-DDA-CR145_1-42412 P06 indicates the SMJ running through the floor. The floor was screeded to the construction revision drawing without the installation of M__-501 Movement Joint prior to the publishing of P06.
| 03SR - Stations (RfL) | Cxxx-NCR-000439 | NCR | Balustrade shoe waterproofing detail (WBS 8) |  | Contr | LAO | CUH - Custom House Station (East) |  | 2017-09-29 | 2017-05-24 16:16 | -128 | 2016-03-04 13:53 | Architectural - General | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The balustrade shoe waterproofing detail shows the waterproofing membrane overlapping the shoe's vertical plate and the fixings. Through design development, the shoe was fabricated as a channel which does not allow the waterproofing membrane to extend across from the structural slab and on to the shoe. Instead, the waterproofing membrane was terminated once lapped up to the screed angle as seen in the attached sketch.
| 03SR - Stations (RfL) | Cxxx-NCR-000441 | NCR | WBS 8F - Entrance Building / VDR bridge handrail chamfer detail |  | Contr | LAO | CUH - Custom House Station (East) |  | 2016-08-26 | 2016-08-24 13:29 | -2 | 2016-03-31 10:35 | Architectural - Handrail | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | The Cxxx and Cxxx Architectural Specifications (post rev 2) call for a 3mm chamfer on all leaner bar handrail arises. This has not been provided. 3mm Radii have instead been provided as per the sub contractor's Code 1 drawings.
| 03SR - Stations (RfL) | Cxxx-NCR-000443 | NCR | Lift 1 Canopies - architectural details |  | Contr | LAO | CUH - Custom House Station (East) |  | 2017-02-03 | 2017-02-10 08:12 | 7 | 2016-04-04 12:49 | Architectural - Roofing & Exterior Treatment | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During a recent architectural inspection of the Lift 1 canopies it was noted by the architect that: 1. The canopy glazing is supported by only two rafters instead of the three shown on the architectural drawing, Cxxx-LAO-A-DDD-CR145_WS157_Z-46913 and fixing bolts for the rigger steelwork are installed in front of the line of the glass. 2. The quality of the fillet welds is thought to be sub standard for architectural steelwork. 3. Mastic seals between the glass joints are not visually acceptable.
| 03SR - Stations (RfL) | Cxxx-NCR-000444 | NCR | VDR Stair Handrail Clearance Against Lighting Columns |  | Contr | LAO | CUH - Custom House Station (East) |  | 2016-05-24 | 2016-05-26 09:17 | 2 | 2016-04-26 09:38 | Architectural - Handrail | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Upon installation of the lighting columns on the VDR stairs, the clearance between the back of the handrail to the face of the lighting column was approx. 15mm. This is not in compliance with the building regulations, british standards or the works information. The access panel to the lighting column is also on the front face behind the handrail and requires approx. 25mm clearance to remove the panel. See attached photo 'NCR-444 001'.
| 03SR - Stations (RfL) | Cxxx-NCR-000445 | NCR | Change in drainage height - backfall within attenuation channel |  | Contr | LAO | CUH - Custom House Station (East) |  | 2016-07-13 | 2016-06-21 07:55 | -22 | 2016-05-04 16:17 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | During the installation of the ACO channels on the East side of the station entrance there was a change in invert level during concrete pouring. As a result there is a 50mm backdrop between SWC004 and SWC003 and a level change of 50mm from SWC004 to SWA004 (see attached Markup)
| 03SR - Stations (RfL) | Cxxx-NCR-000446 | NCR | Coring in station entrance for CCTV feed |  | Contr | LAO | CUH - Custom House Station (East) |  | 2016-05-18 | 2016-05-20 10:44 | 2 | 2016-05-04 16:58 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | The feed for CCTV within the Urban Realm was not highlighted in the original scope during the construction of the Station Entrance foundations. As such 1 no. 127mm core needs to be implemented in the location shown in the attached marked up drawing.
| 03SR - Stations (RfL) | Cxxx-NCR-000447 | NCR | Luminaire installed without Accepted MCR |  | Contr | LAO | CUH - Custom House Station (East) |  | 2016-01-29 | 2016-11-08 07:31 | 284 | 2016-05-09 15:37 | Electrical - Lighting | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | EX14 luminaires installed within Urban Realm, prior to acceptance of MCR. (Cxxx-MCR-002951)
| 03SR - Stations (RfL) | Cxxx-NCR-000448 | NCR | Water ingress to retail units / plant rooms (Entrance Building) |  | Contr | LAO | CUH - Custom House Station (East) |  | 2018-11-30 | 2019-03-25 14:26 | 115 | 2016-05-13 11:21 | Architectural - General | 4000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | During recent period of heavy rain, water ingress to retail units / plant rooms (Entrance Building) was observed. Water is penetrating through four key locations: 1. Stairs - Water is penetrating through the joints where the steel treads overlap. 2. VDR landing - The waterproofing is leaking in the corner of the refuse and LEER rooms. 3. Excel / VDR Bridge - Water is penetrating through the access hatches into the screed containment. 4. Excel / VDR Bridge - Water is penetrating through access hatches with perforated base plates into the screed containment.
| 03SR - Stations (RfL) | Cxxx-NCR-000449 | NCR | Cracking of movement joint concourse beams |  | Contr | LAO | CUH - Custom House Station (East) |  | 2017-06-30 | 2017-06-29 09:45 | -1 | 2016-05-13 12:22 | Civil - Structural Engineering | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Following a general on site survey cracking was observed in the concourse beam at GL12A (AC). Following further investigations cracking has been discovered at the following concourse beam locations: - GL8A (AC) - GL8A (AA) - GL12A (AC) All cracks observed are vertical cracks that are approximately 150mm for the end of the beam. The attached pictures and drawings highlight their locations. Additional information will be provided following a further assessment by __.
| 03SR - Stations (RfL) | Cxxx-NCR-000450 | NCR | Leaner bar posts out of tolerance |  | Contr | LAO | CUH - Custom House Station (East) |  | 2016-10-31 | 2016-10-21 09:36 | -10 | 2016-06-28 20:52 | Architectural - Balustrade | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Vertical posts of the balustrade leaner bar are wider than the horizontal bar. The front face of vertical posts has been aligned and the rear side (closest to the glass) projects outwards. For details and locations refer to the attached report.
| 03SR - Stations (RfL) | Cxxx-NCR-000452 | NCR | Damage to SWA cable feeding ERN 12B |  | Crossrail | XRL | CUH - Custom House Station (East) |  | 2016-10-07 | 2016-09-22 07:07 | -15 | 2016-07-01 14:45 | Electrical - General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | While carrying out inspections the CRL Site Team observed crushing/pinching damage to the SWA sub main cable which feeds Distribution Board ERN12B. The cable is cleated to a ladder rack located in the north East corner of the LVBSR In order to rectify the defect the Contractor will need to remove the cable and pull in a replacement. Photos attached
| 03SR - Stations (RfL) | Cxxx-NCR-000453 | NCR | Corrosion of saddle fixings |  | Contr | LAO | CUH - Custom House Station (East) |  | 2016-12-09 | 2016-12-15 08:06 | 6 | 2016-07-12 13:45 | Electrical - General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Some of the saddle fixings supporting conduits installed at low level of Mezzanine floor are corroded.
| 03SR - Stations (RfL) | Cxxx-NCR-000454 | NCR | DLR Bridge - MCR / schematic not accepted for Electrical Window Controls |  | Contr | LAO | CUH - Custom House Station (East) |  | 2016-11-18 | 2016-11-18 12:04 | 0 | 2016-07-19 12:45 | Electrical - General | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Installation of electrical window controls commenced without accepted documentation - MCR (for Motor Window kit) and schematic / wiring diagram for electrical window control system not accepted by CRL.
| 03SR - Stations (RfL) | Cxxx-NCR-000455 | NCR | Cracked granite tiles - Early Use Access |  | Contr | LAO | CUH - Custom House Station (East) |  | 2017-10-13 | 2017-10-13 15:42 | 0 | 2016-08-09 14:26 | Architectural - Flooring | 2000 |  | Material | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Other | Completed |  | Cracks in some isolated granite tiles installed in BIU area are evident.
| 03SR - Stations (RfL) | Cxxx-NCR-000456 | NCR | Cracked grout between tiles - Early Use Access |  | Contr | LAO | CUH - Custom House Station (East) |  | 2017-10-13 | 2017-10-13 15:44 | 0 | 2016-08-04 12:41 | Architectural - Flooring | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Cracked grout between tiles has been noted in a few locations of Early Use Access.
| 03SR - Stations (RfL) | Cxxx-NCR-000457 | NCR | Section of Busbar too short |  | Contr | LAO | CUH - Custom House Station (East) |  | 2016-09-09 | 2016-08-09 15:58 | -31 | 2016-07-26 07:38 | Electrical - General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | One of the section of Busbar (highlighted on the attached drawing) was delivered approximately 70mm too short.
| 03SR - Stations (RfL) | Cxxx-NCR-000458 | NCR | LV-A and LV-B Distribution Panels |  | Contr | LAO | CUH - Custom House Station (East) |  | 2016-12-22 | 2016-12-15 08:09 | -7 | 2016-08-05 09:20 | Electrical - Switchgear | 20000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | LV-A and LV-B Distribution Panels not manufactured and installed as per the electrical specification
| 03SR - Stations (RfL) | Cxxx-NCR-000459 | NCR | Subplatform Trunking Joint Corrosion |  | Contr | LAO | CUH - Custom House Station (East) |  | 2017-03-17 | 2017-02-22 11:25 | -23 | 2016-08-26 14:30 | Electrical - Cable Management | 1000 |  | Material | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Numerous trunking couplers located within the subplatform have developed surface corrosion. Couplers affected appear to all be adjacent to movement joints and/or penetrations. Corrosion would seem to be due to water passing through the platform slab, and dripping onto the trunking.
| 03SR - Stations (RfL) | Cxxx-NCR-000460 | NCR | Limited Access to Staff WC BMS Cable Tray |  | Contr | LAO | CUH - Custom House Station (East) |  | 2016-12-23 | 2016-11-18 11:49 | -35 | 2016-08-26 14:47 | Electrical - Cable Management | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Concourse staff WC cable tray has limited access due to position of AC unit within the room. Space within the room is also limited.
| 03SR - Stations (RfL) | Cxxx-NCR-000461 | NCR | Mechanical Engineering |  | Contr | LAO | CUH - Custom House Station (East) |  | 2017-03-17 | 2017-03-23 07:22 | 6 | 2016-12-08 12:09 | Mechanical - Mechanical Engineering General | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Little/No access on MFD 30/31 On Mezzanine Level, linked to EF-9A & EF-9B
| 03SR - Stations (RfL) | Cxxx-NCR-000462 | NCR | Using Flexible Connection Ductwork without an MCR for it |  | Contr | LAO | CUH - Custom House Station (East) |  | 2017-06-23 | 2017-05-04 07:00 | -50 | 2017-02-01 15:39 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Usage of unapproved material on site. Flexible ductwork connection to the grilles have been used without an MCR.
| 03SR - Stations (RfL) | Cxxx-NCR-000463 | NCR | Access to Packaged Tank & Booster Pump Set DBP-01 |  | Contr | LAO | CUH - Custom House Station (East) |  | 2017-06-23 | 2017-06-21 08:58 | -2 | 2017-02-05 14:33 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | While carrying out an ITP witness inspection it was observed by the CRL site team that the enclosure housing the twin booster pumps does not offer sufficient maintenance access to the pumps, pipework fittings and electrical connections housed within the junction box, therefore this creates an access/maintenance issue
| 03SR - Stations (RfL) | Cxxx-NCR-000464 | NCR | Using Galvanised Pipework without an Approved MCR |  | Contr | LAO | CUH - Custom House Station (East) |  | 2017-07-28 | 2017-07-11 06:50 | -17 | 2017-03-08 14:53 | Fire - Suppression | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Galvanised Pipework installed does not have an approved MCR
| 03SR - Stations (RfL) | Cxxx-NCR-000465 | NCR | Fire Stopping Compliance |  | Contr | LAO | CUH - Custom House Station (East) |  | 2018-05-16 | 2019-03-06 14:58 | 294 | 2017-05-09 10:43 | Fire - Compartmentation | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | It has been observed in a number of locations throughout the Station that there is not a specified fire stopping detail approved at the interface between a number of CMS/Pipe work and associated sleeves and the structural element being breached. This is primarily due to the proximity of the service sleeve to the edge of the builder's work hole.
| 03SR - Stations (RfL) | Cxxx-NCR-000466 | NCR | Cracks in beams at movement joints locations |  | Contr | LAO | CUH - Custom House Station (East) |  | 2018-05-25 | 2017-12-05 14:23 | -171 | 2017-06-26 11:15 | Civil - Structural Engineering | 250000 |  | Design | Repair | 1 (>60k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | Following a full structural cracking survey at Custom House a number of additional cracks have been found at the structural movement joints. The cracks found are a combination of existing and new, and are present along the gridlines of AA, AC and AD at GL8A, 12A and 16A. __ (__) have instructed __ and __’s in house Engineering Excellence group to undertake a full structural analysis of the frame to determine the root cause to these cracks.
| 03SR - Stations (RfL) | Cxxx-NCR-000467 | NCR | Damage to handrail - GL21 - AF |  | Contr | LAO | CUH - Custom House Station (East) |  | 2018-02-01 | 2018-01-29 16:03 | -3 | 2017-10-24 08:45 | Architectural - Handrail | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | The bottom corner of the Stairs 2 handrail at location GL21-AF has been dented.
| 03SR - Stations (RfL) | Cxxx-NCR-000468 | NCR | Cladding Systems - MCR approval |  | Contr | LAO | CUH - Custom House Station (East) |  | 2018-03-01 | 2018-06-20 14:55 | 111 | 2017-11-01 11:43 | Materials - Approval | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | CRL review of cladding systems revealed that potentially 7 products were installed without accepted Material Compliance Records or without sufficient technical information appended to the existing MCRs.
| 03SR - Stations (RfL) | Cxxx-NCR-000469 | NCR | Celotex FR5000 has been removed from sale and is no longer Class 0 classified; no longer meeting Fire Strategy |  | Crossrail | XRL | CUH - Custom House Station (East) |  | 2018-04-20 | 2018-05-14 23:45 | 24 | 2017-11-03 10:38 | Architectural - General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | A planned Crossrail surveillance was completed at Custom House Station on 24th October 2017 to review Fire Compliance of Cladding Systems and associated materials. During the site visit it was found that Celotex FR5000 had been installed in the base of the Cladding Systems running the length of Concourse and Platform Levels. On investigation it was found that Celotex (Saint-Goban) as of September 1st 2017 have suspended the sale of the 5000 series product range as a Class 0 rating was not achieved when tested in August 2017 (see https://www.celotex.co.uk/5000-test). This removal and de-classification no longer meets Section 7.2 ‘Materials’ of Fire Strategy Report Cxxx-LAO-E1-RGN-CR145_WS157_1-50001 for All Circulation Areas which requires a Class 0 classification. Non-Conformance raised to record either a) justification for its continued use or b) agreement that the product is to be removed and replaced with a compliant product.
| 03SR - Stations (RfL) | Cxxx-NCR-000470 | NCR | __ K15 Insulation Board does not comply with Fire Strategy requirements |  | Crossrail | XRL | CUH - Custom House Station (East) |  | 2018-04-20 | 2018-05-14 23:44 | 24 | 2017-11-03 10:41 | Architectural - General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | A planned Crossrail surveillance was completed at Custom House Station on 24th October 2017 to review Fire Compliance of Cladding Systems and associated materials. On discussion with __ it was confirmed that __ K15 Insulation Board had been installed behind all coloured glass (except Lift 3) for the Curtain Wall on the public side of the wall. On checking, the __A certificate referenced in the __ K15 literature shows the panel to be Euro Class C (attached). This does not meet Section 7.2 ‘Materials’ of Fire Strategy Report Cxxx-LAO-E1-RGN-CR145_WS157_1-50001 for All Circulation Areas which requires a Class B classification. Non-Conformance raised to record either a) justification for its continued use or b) agreement that the product is to be removed and replaced with a compliant product The use of this product without adequate assessment could have resulted from the fact no MCR was ever produced.
| 03SR - Stations (RfL) | Cxxx-NCR-000471 | NCR | Ceiling panel - incorrect installation |  | Contr | LAO | CUH - Custom House Station (East) |  | 2018-02-14 | 2018-01-23 21:48 | -22 | 2017-11-16 09:44 | Architectural - Ceilings & Soffits | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The ceiling panel on the platform soffit between GL15 and GL16 has not been installed as per Cxxx-LAO-A-DDD-CR145_Z-46838. The setting out requires a uniform 25 mm gap between escalator carriage and downstand beams, however the gap at the carriage is 75 mm and the spacing between tubes and panels is not uniform at either end of the bay (160 mm at one end, 115 mm at the other.
| 03SR - Stations (RfL) | Cxxx-NCR-000472 | NCR | Water leak - link bridge between VDR bridge and lift 1 |  | Contr | LAO | CUH - Custom House Station (East) |  | 2018-05-18 | 2018-03-01 15:12 | -78 | 2017-12-13 13:04 | Architectural - General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Dampness was observed on the soffit under the high level link bridge to Lift 1.
| 03SR - Stations (RfL) | Cxxx-NCR-000473 | NCR | Top tread and top riser of VDR stairs de-bonded from the substrate |  | Contr | LAO | CUH - Custom House Station (East) |  | 2018-03-24 | 2018-10-24 15:41 | 214 | 2017-12-14 14:52 | Architectural - Flooring | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During inspection of stairs it became apparent that top tread and top riser on western side of VDR stairs have de-bonded from the substrate.
| 03SR - Stations (RfL) | Cxxx-NCR-000474 | NCR | Excel Bridge Paintwork |  | Contr | LAO | CUH - Custom House Station (East) |  | 2018-09-30 | 2020-08-25 16:22 | 695 | 2018-03-01 10:57 | Architectural - Finishes | 10000 |  | Damaged | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Other | Completed |  | Visible paint deterioration at regular intervals and discrepancies in colour shading were observed on the external cover plates of the Excel Bridge.
| 03SR - Stations (RfL) | Cxxx-NCR-000475 | NCR | Stair Stringers - shrinkage cracks |  | Contr | LAO | CUH - Custom House Station (East) |  | 2018-04-20 | 2018-07-06 13:26 | 77 | 2018-03-01 16:40 | Architectural - Finishes | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | Cracks (greater than allowable 0.15mm and smaller than 0.3mm) appeared at regular intervals on the exposed face of all four stair stringers installed on site.
| 03SR - Stations (RfL) | Cxxx-NCR-000476 | NCR | Exposed Conduit Installed on Underside of Fair Faced Concrete Beam |  | Contr | ATK | CUH - Custom House Station (East) |  | 2018-10-01 | 2018-11-08 13:29 | 38 | 2018-03-01 16:38 | Electrical - Cable Management | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Exposed conduit has been installed on the fair faced concrete soffit next to grid line 21A. The works information requirement is to use concealed conduits cast in to the beams to supply power in this location, but the concealed cable route is either blocked or missing. The concealed route must either be provided, or alternative lighting provided, such as lamp posts adjacent to the stair with power supplied from the undercroft, as discussed on site. The two photos attached show the conduit in October 2016, when the observation CRL-OBS-12593 was first raised, and in February 2018 after the conduit was changed. Neither option is in accordance with the works information.
| 03SR - Stations (RfL) | Cxxx-NCR-000477 | NCR | Repair to ETFE Roof |  | Contr | LAO | CUH - Custom House Station (East) |  | 2018-05-30 | 2018-06-25 16:33 | 26 | 2018-03-15 09:39 | Architectural - Roofing & Exterior Treatment | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | __ Structures UK carried out their annual maintenance inspection of the ETFE roof on 09/02/2018 and submitted their report on 20/02/2018. The maintenance report is attached. 6 nr small holes were recorded in the underside of the 35 pillows which will required to be sealed with __ ETFE tape.
| 03SR - Stations (RfL) | Cxxx-NCR-000478 | NCR | Ductwork Access Hatches |  | Contr | LAO | CUH - Custom House Station (East) |  | 2018-10-26 | 2019-07-23 10:53 | 270 | 2018-04-06 09:46 | Mechanical - Heating Ventilation & Air Conditioning | 2000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | All ductwork installed on site (including Ducting in the HRU room) requires access hatches for internal inspection and cleaning – this requirement is stated within the Cxxx mechanical specification. Currently access hatches have not been provided. JY30.1302 h) The air duct system shall be designed, manufactured and installed in such a way that cleaning of internal surfaces and components is possible. For the purpose of cleaning the ventilation system and its component parts, the recommended location of the access panels, size and type given in EN 12097 "Requirements for ductwork components to facilitate maintenance of ductwork systems" shall be followed. The precise location, size and type of access would be dependent upon the system design and the type of ductwork cleaning, inspection and testing methods to be adopted. The Contractor shall ensure that the air distribution system can be safely maintained, inspected and cleaned.
| 03SR - Stations (RfL) | Cxxx-NCR-000479 | NCR | Accomodation Block Flexible Ductwork |  | Contr | LAO | CUH - Custom House Station (East) |  | 2019-12-29 | 2019-08-06 11:05 | -145 | 2018-04-06 10:00 | Mechanical - Heating Ventilation & Air Conditioning | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Flexible ducts fitted within the SCF and accommodation block are not compliant to specification in regards to length. Cxxx mechanical spec requires the ducts be between 50mm and 300mm. Open ended extract ductwork in SCF is missing a grill – grille or wire mesh needs to be installed as per Cxxx Mechanical Specification. JY30.1402 Ductwork Construction B) iii) Flexible joints shall be 50mm minimum and 300mm maximum lengths and shall not intrude into the airway under any condition. Ductwork shall be supported and aligned to prevent undue stress in the flexible joint. JY30.1402 Ductwork Construction a) The galvanised mild steel sheet ductwork materials, construction and installation shall comply with HVCA DW/ 144 Specification. All necessary ductwork, control, isolating and balancing dampers, grilles to form complete air distribution systems shall be provided. Where site dimensions cannot be obtained in advance of preparation of fabrication drawings, suitable provisions shall be made to accommodate any discrepancies between the drawings and site requirements. The fabrication drawings shall show provisions for dismantling ductwork by bolted, gasketted, flanged joints.
| 03SR - Stations (RfL) | Cxxx-NCR-000480 | NCR | Fracture to Shelter Column Steelwork |  | Contr | LAO | CUH - Custom House Station (East) |  | 2018-06-30 | 2018-09-12 14:11 | 74 | 2018-04-20 08:51 | Architectural - Finishes | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | A fracture has occurred in the eastern column of the northern wall of the shelter located at GL23.
| 03SR - Stations (RfL) | Cxxx-NCR-000481 | NCR | Design Of Platform End Barrier - GL11 Westbound Platform |  | Contr | LAO | CUH - Custom House Station (East) |  | 2018-06-30 | 2018-06-06 13:31 | -24 | 2018-04-20 09:19 | Architectural - Handrail | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The dimensions of the platform end barrier indicated on Cxxx-LAO-A-DDD-CR145_Z-46712 result in the southern leaf extending beyond the platform edge by 190 mm.
| 03SR - Stations (RfL) | Cxxx-NCR-000482 | NCR | Design clash of Cabinet 1 and 2 bases with introduced GRP sections |  | Contr | LAO | CUH - Custom House Station (East) |  | 2018-07-20 | 2018-06-25 08:50 | -25 | 2018-04-20 09:43 | Architectural - Signage | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The flange of the GRP section introduced in the dry riser pipework to ensure isolation between platform and concourse level is 230 mm in diameter. The clear width of the base of Cabinets 1 and 2 is 200 mm resulting in an inability to lower the cabinets into position.
| 03SR - Stations (RfL) | Cxxx-NCR-000483 | NCR | DLR Bridge Bonding |  | Contr | LAO | CUH - Custom House Station (East) |  | 2018-10-01 | 2019-07-08 15:36 | 280 | 2018-05-01 10:00 | Electrical - Earthing & Bonding | 500 |  | Design | Reject | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Current bonding of the DLR bridge, supporting structure and connected PH services are not in accordance with the CRL E&B strategy. CRL Bonding requirements are detailed within – CRL1-XRL-Z7-GPD-CR001-50027
| 03SR - Stations (RfL) | Cxxx-NCR-000484 | NCR | Accessability of ACU within the staff WC |  | Contr | LAO | CUH - Custom House Station (East) |  | 2018-10-01 | 2019-06-04 09:00 | 246 | 2018-05-01 10:05 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Access to AC unit within the ceiling void of the concourse staff WC is limited.
| 03SR - Stations (RfL) | Cxxx-NCR-000485 | NCR | Contractor was unable to provide evidence of offsite signage Manufacturing records |  | Crossrail | XRL | CUH - Custom House Station (East) |  | 2018-07-27 | 2018-07-05 16:44 | -22 | 2018-05-18 07:22 | Architectural - Signage | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Management Problem - No evidence of program review from Contractor's Quality Manager or Management | Completed |  | A planned Crossrail surveillance was undertaken on 09th May 2018 to look at the installation of Signage. On request the Contractor was unable to provide evidence of offsite Signage manufacturing records inline with Cxxx-__-A-ITP-CR145_WS157_1-50037 (Rev 3) including Inspection Numbers; 3.4 welding, 3.7 Electrical Testing, 3.9 Acceptance of Benchmark.
| 03SR - Stations (RfL) | Cxxx-NCR-000486 | NCR | Contractor was unable to provide evidence of onsite signage installation records |  | Crossrail | XRL | CUH - Custom House Station (East) |  | 2018-07-27 | 2018-07-05 16:46 | -22 | 2018-05-18 07:34 | Architectural - Signage | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Verification Problems - Not Defined | Completed |  | A planned Crossrail surveillance was undertaken on 09th May 2018 to look at the installation of Signage. On request the Contractor was unable to provide evidence of onsite installation records inline with Cxxx-__-A-ITP-CR145_WS157_1-50038 (Rev 3) including Inspection Number; 4.3 Fixing to slab; Torque settings and Pull Test Results, value and calculations for pull test, Competency of tester and calibration of test equipment used. As no check sheets were produced it could not be verified that the testing had been completed on installed signage where required.
| 03SR - Stations (RfL) | Cxxx-NCR-000487 | NCR | Incorrect design levels and setting out for NTI support bracketry |  | Contr | LAO | CUH - Custom House Station (East) |  | 2018-06-08 | 2018-06-28 15:02 | 20 | 2018-05-25 09:23 | Architectural - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The underside of NTI screen level (106.38 m) and beam level (106.91 m) shown on Cxxx-LAO-A-DDD-CR145_WS157_Z-47041 result in a clash with the canopy glass support beam along GLAA. The positions of the NTI support beams shown on Cxxx-LAO-A-DDA-CR145_1-42410 and Cxxx-LAO-A-DDA-CR145_1-42412 do not comply with NR/L2/TEL/30130 Section 5.3 due to position of DOO cameras and signage.
| 03SR - Stations (RfL) | Cxxx-NCR-000488 | NCR | Contractor unable to produce evidence of acceptance for Signage Quality Benchmarks |  | Crossrail | XRL | CUH - Custom House Station (East) |  | 2018-08-31 | 2018-09-12 14:16 | 12 | 2018-05-29 08:30 | Architectural - Signage | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | A planned Crossrail surveillance was undertaken on 09th May 2018 to look at the installation of Signage. During the Surveillance the Contractor was asked to supply evidence of acceptance for Signage Benchmarks, the Contractor was unable to supply the evidence, as such it could not be verified that the Benchmarks have been completed.
| 03SR - Stations (RfL) | Cxxx-NCR-000490 | NCR | Asset labels for cables |  | Contr | LAO | CUH - Custom House Station (East) |  | 2018-12-14 | 2018-11-21 10:02 | -23 | 2018-09-19 14:17 | Information Management - Asset Information | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Information required on the labels for cables has been in different layout than specified by CRL Asset Identification Standard. Due to the quantity of text required an additional 5th line was introduced. Additionally where contractor design alternative asset ID was not available acronym ‘NO DAAID’ (no design alternative asset identification) was used in the line 3 on the asset labels.
| 03SR - Stations (RfL) | Cxxx-NCR-000491 | NCR | Subplatform Earth Mat Welding |  | Contr | LAO | CUH - Custom House Station (East) |  | 2019-03-29 | 2019-06-21 10:59 | 84 | 2018-11-16 16:58 | Electrical - Earthing & Bonding | 4000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | Early installation of earth mat included the use of Furse clamps to connect lengths of rebar together into an earth mat, as opposed to the approved method of welding.
| 03SR - Stations (RfL) | Cxxx-NCR-000492 | NCR | Post Mount Luminaires (__ Terminus) rusting |  | Contr | LAO | CUH - Custom House Station (East) |  | 2019-06-07 | 2019-07-22 17:04 | 45 | 2019-01-15 16:40 | Electrical - Lighting | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Rust appearing on __ Terminus Luminaires, mounted atop lighting columns. Rust causing flaking of powder coat paint.
| 03SR - Stations (RfL) | Cxxx-NCR-000493 | NCR | Refrigerant pipework and PVC power cable installed on one tray |  | Contr | LAO | CUH - Custom House Station (East) |  | 2019-10-03 | 2019-12-16 15:41 | 74 | 2019-07-05 08:16 | Mechanical - Heating Ventilation & Air Conditioning | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Refrigerant pipework and PVC power cables for HVRs D, E and F on mezzanine level have been installed on one tray.
| 03SR - Stations (RfL) | Cxxx-NCR-000494 | NCR | Dry Riser Non Conformance Part2 |  | Crossrail | XRL | CUH - Custom House Station (East) |  | 2019-09-10 | 2019-09-04 15:21 | -6 | 2019-08-27 08:52 | Fire - Fire Systems & General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | NCR-000489 was mistakenly cancelled by an ERROR from CRL instead of reworking for evidence. NCR was raised initially by contractor. Please see repeat information. A number of aspects of the dry riser installation are questionable and require rectification or justification. 1. Breeching inlet installed within VDR wall has not been orientated correctly. 2. Breeching inlet signage does not comply with CRL1-XRL-E1-RGN-CR001_Z-50004 Fixed Non-Automatic Fire-Fighting Systems Signage. 3. Pipe labeling was not installed on the dry riser. Pipe labeling shall comply with CRL1-XRL-E1-RGN-CR001_Z-50004 Fixed Non-Automatic Fire-Fighting Systems Signage. 4. Grinnell couplings and fittings have been installed without accepted Material Compliance Record. 5. Dry riser pipe has not been supported / restrained sufficiently at mezzanine level. 6. Hydrant (between GL 3A and 4A) installed at mezzanine level is not safely accessible. 7. Bent/deformed hanger rods at mezzanine level fire main. 8. A Platform hydrant is not secured. 9. Pipe supports are not in contact with pipe. 10. Platform hydrants in cabinets are not restrained sufficiently. 11. Landing valves, isolation valves and drain valves are not secured with straps/padlocks. 12. Isolation valves are not shown in as-built schematic. 13. A valve located in subplatform has not been installed at lowest point. 14. Valve plugs corroded. 15. The installation was tested for 2 hours at 12 bar pressure.
| 03SR - Stations (RfL) | Cxxx-NCR-000495 | NCR | Electric heaters - missing thermostats |  | Contr | LAO | CUH - Custom House Station (East) |  | 2019-10-31 | 2019-11-25 13:38 | 25 | 2019-10-10 12:54 | Mechanical - Heating Ventilation & Air Conditioning | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Electric heaters (CR145-HVA-00076, CR145-HVA-00074, CR145-HVA-00075, CR145-HVA-00933, and CR145-HVA-00934) located in rooms LER 132, CLN Store 407, SCER 732, Escalator 1 and Escalator 2 were installed without thermostats.
| 03SR - Stations (RfL) | Cxxx-NCR-000496 | NCR | Fire strategy and cause and effect matrix |  | Contr | LAO | CUH - Custom House Station (East) |  | 2020-02-17 | 2019-12-12 07:40 | -67 | 2019-11-19 10:17 | Fire - Fire Systems & General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | Fire Alarm Cause and Effect Document - Cxxx-LAO-E1-TSC-CR145_WS157_1-50002 (which is not part of the accepted Fire Strategy Cxxx-LAO-E1-RGN-CR145_WS157_1-50001) was created for allowing quicker commencement of Cause and Effect testing.
| 03SR - Stations (RfL) | Cxxx-NCR-000497 | NCR | Residue and leakage though BWK hole around services onto escalator |  | Contr | LAO | CUH - Custom House Station (East) |  | 2020-03-15 | 2019-12-16 11:23 | -90 | 2019-12-16 09:28 | Architectural - General | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Residue and leakage though BWK hole around services onto escalator surround and base of stairs
| 03SR - Stations (RfL) | Cxxx-NCR-000498 | NCR | Protection of assets and services in plantrooms in trafficked areas |  | Contr | LAO | CUH - Custom House Station (East) |  | 2020-03-15 | 2019-12-16 11:57 | -90 | 2019-12-16 09:47 | Electrical - General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Lack of protection of assets and services in plantrooms in trafficked areas
| 03SR - Stations (RfL) | Cxxx-NCR-000014 | NCR | Woolwich East Box - Test & Anchor Piles - Slump Testing |  | Contr | __R | WOO - Woolwich Station (East) |  | 2015-04-03 | 2015-04-24 08:10 | 21 | 2015-03-20 10:48 | Geotechnical Engineering - Concrete - Bored Pile | 0 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | On commencement of piling on 12/03/2015, two concrete wagons arrived on site at 8.30. The concrete in the wagons was not cone slump tested in accordance with point G1 of the referenced ITP and B4.4.5.1 of SPERW.
| 03SR - Stations (RfL) | Cxxx-NCR-000015 | NCR | Geotechnical Engineering - Change in sequence of test pile and anchor installation |  | Contr | __R | WOO - Woolwich Station (East) |  | 2015-04-07 | 2015-04-24 08:12 | 17 | 2015-03-24 17:24 | Geotechnical Engineering - Concrete - Bored Pile | 0 |  | Planning | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | In reference to Appendix 7 in the Method Statement for Woolwich East Box Piling (Cxxx-__R-C-GMS-CR147-50016), the sequence of pile construction varied from that detailed. Two anchor piles AP2 & AP3 were installed on the first day, which are on opposing corners of the test setup, as instead of adjacent. This sequence was adopted to minimise the likelihood of the piles blowing through.
| 03SR - Stations (RfL) | Cxxx-NCR-000016 | NCR | Geotechnical Engineering - Embedment length of diwidag bars in anchor pile AP2 |  | Contr | __R | WOO - Woolwich Station (East) |  | 2015-04-08 | 2015-03-26 17:41 | -13 | 2015-03-25 10:53 | Geotechnical Engineering - Concrete - Bored Pile | 0 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | In reference to the ITP for piling Cxxx-__R-C-ITP-CR147-50013 inspection point F6 Dywidag Steel within Anchor Piles, two diwidag bars in anchor pile AP2 were not installed to the correct embedment depth (refer TWD Cxxx-__R-C-CER-CR147-50004). The emdbedment depth specified is 24.5m but two of the bars in AP2 were only installed with an embedment depth of 21m.
| 03SR - Stations (RfL) | Cxxx-NCR-000018 | NCR | Woolwich East Box - Curing of Concrete Cubes |  | Contr | __R | WOO - Woolwich Station (East) |  | 2015-05-20 | 2015-05-20 18:14 | 0 | 2015-04-22 15:01 | Geotechnical Engineering - Concrete - Bored Pile | 0 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | All cube samples for the piling works have been stored on site in the __GE stores until being taken away for testing as soon as suitable for transportation Cubes were stored in this manner due to no other adequate means of storage available
| 03SR - Stations (RfL) | Cxxx-NCR-000019 | NCR | Woolwich - East Box: Storage and Damage to Pile Cages |  | Contr | __R | WOO - Woolwich Station (East) |  | 2015-05-06 | 2015-04-30 16:11 | -6 | 2015-04-22 15:07 | Geotechnical Engineering - Concrete - Bored Pile | 0 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | On inspection of the pile cage, some plastic cover skids over the rebar spacers were found to be damaged, either on delivery or storage. Although spacing wheels were installed as standard in these locations, initially the rebar spacers were left in place potentially creating a moisture path from the surface of the pile to the reinforcing. This was found after two number piles (22, 17) had been installed.
| 03SR - Stations (RfL) | Cxxx-NCR-000020 | NCR | PTP Dywidag / Test Pile Cap |  | Contr | __R | WOO - Woolwich Station (East) |  | 2015-05-06 | 2015-04-24 08:19 | -12 | 2015-04-22 15:30 | Geotechnical Engineering - Concrete - Bored Pile | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | 1. The Test Pile Cap was constructed 300mm higher than the Piling Platform Level due to operatives being instructed not to excavation to depth. On excavation for the pile cap it was instructed by CRL that the dig was to not progress deeper than 700mm. 2. The dywidag bar was installed as per the __ drawings. 2.5m above PPL, however this was not long enough for the larger than usual __ test rig. Due to these factors, the dywidag bar was 200mm short of what was required for the S1000 test setup.
| 03SR - Stations (RfL) | Cxxx-NCR-000021 | NCR | Pile Bore Depth |  | Contr | __R | WOO - Woolwich Station (East) |  | 2015-10-01 | 2015-09-28 12:58 | -3 | 2015-04-22 15:33 | Geotechnical Engineering - Concrete - Bored Pile | 0 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On assessment of the Pile Log 22 we can observe that the augers have been retracted after reaching 27.32m. When re-drilling back down (22R) the pile is required to be drilled deeper by 500mm. We have assessed the redrilled pile and can see that the bore has been extended by 300mm to 27.62. This is 200mm short of the Specification requirement.
| 03SR - Stations (RfL) | Cxxx-NCR-000022 | NCR | Documents and Records |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2015-10-01 | 2015-09-15 13:47 | -16 | 2015-04-27 14:08 | Civil - Civil Engineering General | 0 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | During this surveillance the Contractor was asked to supply evidence that the Readiness Review Checklist has been completed: after waiting 5 working days and making further requests for the evidence the Contractor has failed to supply the evidence
| 03SR - Stations (RfL) | Cxxx-NCR-000023 | NCR | Documentation and Records |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2015-09-30 | 2015-09-01 18:48 | -29 | 2015-04-27 14:13 | Civil - Civil Engineering General | 0 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate resources | Completed |  | During the surveillance QS530-01 carried out on the 04/03/2015 the Contractor was asked to supply the evidence of the Schedule for all inspection, measuring and test Equipment used for the works including calibration of the Equipment; at that time the Contractor stated that the schedule was in the process of being compiled. The Contractor was requested to supply the schedule during this surveillance, after waiting 5 working days for the evidence the Contractor has failed to supply the evidence
| 03SR - Stations (RfL) | Cxxx-NCR-000024 | NCR | Woolwich East Box - Wall 1 kicker poured to D-Wall |  | Contr | __R | WOO - Woolwich Station (East) |  | 2015-05-15 | 2015-05-20 10:18 | 5 | 2015-05-01 18:08 | Civil - Structural Engineering | 0 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Kicker to Wall 1, Basement Level, approx. GL Z6/B2 poured up to D-Wall without leaving room for soft joint.
| 03SR - Stations (RfL) | Cxxx-NCR-000025 | NCR | Woolwich East Box: Wall 1 Damage to kicker |  | Contr | __R | WOO - Woolwich Station (East) |  | 2015-05-15 | 2015-10-30 14:27 | 168 | 2015-05-01 17:56 | Civil - Structural Engineering | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Kicker in Wall 1, Basement at approx. GL Z4/B2 cracked whilst cranking existing misplaced starter bars from basement slab. Cracks approximately 1-2mm in width.
| 03SR - Stations (RfL) | Cxxx-NCR-000026 | NCR | Cxxx – Woolwich: East Box– Basement Wall 1 kicker poured to D-Wall |  | Contr | __R | WOO - Woolwich Station (East) |  | 2015-05-20 | 2015-05-20 10:21 | 0 | 2015-05-06 18:05 | Structural Engineering - Concrete Member | 0 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | CRL REF: Cxxx-NCR-0024 Kicker to Wall 1, Basement Level, approx. GL Z6/B2 poured up to D-Wall without leaving room for soft joint. As the Basement slab poured to D-Wall surrounding East Box, kicker will be left as-is
| 03SR - Stations (RfL) | Cxxx-NCR-000027 | NCR | Woolwich West Box - Cxxx defects not picked up in as-built survey |  | Contr | __R | WOO - Woolwich Station (East) |  | 2015-09-02 | 2015-09-28 13:00 | 26 | 2015-07-03 14:32 | Structural Engineering - Structural Engineering - General | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | An Engineer’s survey was carried out to determine the suitability of exisiting starter bars installed by Cxxx. It has become apparent after pouring kickers for walls 3, 7, 8 and 10 that existing problems were not picked up by the initial survey. • Wall 3 – Bar out of position at the northern end of the wall • Wall 7 – 2 bars missing at the southern end of the wall • Wall 8 – Excessive cover on bars at northern end of wall (65mm maximum) • Wall 10 – Bar has 36mm cover at Western end of wall (Minimum 40mm) • Wall 10 – Starter bars are missing at eastern end of wall.
| 03SR - Stations (RfL) | Cxxx-NCR-000028 | NCR | West Box B-2 Slab Wall 4 Reinforcement |  | Contr | __R | WOO - Woolwich Station (East) |  | 2015-06-03 | 2015-06-01 13:28 | -2 | 2015-05-20 14:53 | Structural Engineering - Reinforcement | 0 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Based on the inspection carried out on the 13th of May it was identified that the number of the rebar for Wall Pour 4 had incorrect number of U Bars (12 instead of 11), which had been installed around the door openings. This in turn had resulted in the spacing’s between the first two sets of horizontal bars directly above the door frames both connecting to Wall 3 having a spacing of 100mm. Cause of incident: This non conformity was caused due to misunderstandings by the site operatives of the RC Drawings and local displacement of the reinforcement bars around the door frame and tie bars. This resulted in increased spacing between the bars and hence site operatives where required to install an additional bar to comply with the maxmium spacing requirements.
| 03SR - Stations (RfL) | Cxxx-NCR-000029 | NCR | Woolwich East Box - Wall 1 Concrete Finish |  | Contr | __R | WOO - Woolwich Station (East) |  | 2015-08-31 | 2015-10-30 14:21 | 60 | 2015-05-21 09:36 | Civil - Structural Engineering | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Location - Woolwich East Materials And Workmanship Specification Section KF11 - In Situ And Pre-Cast Concrete For Buildings (Cxxx-OVE-A-RSP-CR147-50002) section KF11.1308 for plain formed surface finishes states "blowholes shall be limited to no more than 5 blowholes of diamter greater than 5mm in any 1m2 of surface. No single blowhole shall be greater than 10mm diameter." Post-pour inspection wall of 1 (gridline B2 between gridline Z4 & Z5 as per attached marked up plan) revels it does not meet the criteria above with up to 40 blowholes greater than 5mm observed in a 1m2 area with blowholes as big as 20mm in diameter (please refer to the photos attached including a sample area)
| 03SR - Stations (RfL) | Cxxx-NCR-000030 | NCR | Cxxx – Woolwich - West Box– Basement -2 Wall 10 kicker poured to D-Wall |  | Contr | __R | WOO - Woolwich Station (East) |  | 2015-06-10 | 2015-06-11 14:23 | 1 | 2015-05-27 08:26 | Structural Engineering - Structural Engineering - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | PART 1 – Details of departure from specified requirements Kicker to Wall 10, Basement Level -2, approx. GL B3/W7 poured up to D-Wall without leaving room for drainage channel.
| 03SR - Stations (RfL) | Cxxx-NCR-000031 | NCR | Missing reinforcement (Bar Mark 29) - Wall 11+14 pour |  | Crossrail | PDP | WOO - Woolwich Station (East) |  | 2015-07-02 | 2015-07-07 09:52 | 5 | 2015-06-18 15:01 | Structural Engineering - Reinforcement | 0 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following the reinforcement inspection of Wall 11+14 which took place on the 27/05/15 it was found that Bar Mark 29 was one number short. There was 13/14 bars installed on wall Y / U intersection located on Cxxx-__R-S-TSC-CR147-50006).
| 03SR - Stations (RfL) | Cxxx-NCR-000032 | NCR | Incomplete drawing revisions |  | Contr | __R | WOO - Woolwich Station (East) |  | 2015-06-19 | 2015-07-07 08:37 | 18 | 2015-06-05 10:10 | Structural Engineering - Structural Engineering - General | 0 |  | Design | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The following drawings & schedules being used on site for the Basement Level works are C02 revs, eB shows that we have only have C01’s on the system at present. Cxxx-__R-S-DWG-CR147-50001 Cxxx-__R-S-DWG-CR147-50002 Cxxx-__R-S-DWG-CR147-50003 Cxxx-__R-S-DWG-CR147-50004 Cxxx-__R-S-DWG-CR147-50005 Cxxx-__R-S-DWG-CR147-50006 Cxxx-__R-S-TSC-CR147-50001 Cxxx-__R-S-TSC-CR147-50002 Cxxx-__R-S-TSC-CR147-50003 Cxxx-__R-S-TSC-CR147-50004 Cxxx-__R-S-TSC-CR147-50005 Cxxx-__R-S-TSC-CR147-50006
| 03SR - Stations (RfL) | Cxxx-NCR-000033 | NCR | Incomplete Drawing Revisions |  | Contr | __R | WOO - Woolwich Station (East) |  | 2015-10-30 | 2015-10-16 07:46 | -14 | 2015-06-08 09:51 | Structural Engineering - Structural Engineering - General | 0 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The following drawings & schedules being used on site are C02 revs, eB shows that we have only have C01’s on the system at present. Cxxx-__R-S-DWG-CR147-50028 Cxxx-__R-S-DWG-CR147-50029 Cxxx-__R-S-DWG-CR147-50033 Cxxx-__R-S-DWG-CR147-50036 Cxxx-__R-S-DWG-CR147-50037 Cxxx-__R-S-DWG-CR147-50038 Cxxx-__R-S-DWG-CR147-50044 Cxxx-__R-S-DWG-CR147-50046 Cxxx-__R-S-DWG-CR147-50050 Cxxx-__R-S-DWG-CR147-50052 Cxxx-__R-S-DWG-CR147-50053 Cxxx-__R-S-DWG-CR147-50054 Cxxx-__R-S-DWG-CR147-50055 Cxxx-__R-S-DWG-CR147-50097 Cxxx-__R-S-TSC-CR147-50028 Cxxx-__R-S-TSC-CR147-50029 Cxxx-__R-S-TSC-CR147-50033 Cxxx-__R-S-TSC-CR147-50036 Cxxx-__R-S-TSC-CR147-50037 Cxxx-__R-S-TSC-CR147-50038 Cxxx-__R-S-TSC-CR147-50044 Cxxx-__R-S-TSC-CR147-50046 Cxxx-__R-S-TSC-CR147-50050 Cxxx-__R-S-TSC-CR147-50052 Cxxx-__R-S-TSC-CR147-50053 Cxxx-__R-S-TSC-CR147-50054 Cxxx-__R-S-TSC-CR147-50055 Cxxx-__R-S-TSC-CR147-50097
| 03SR - Stations (RfL) | Cxxx-NCR-000034 | NCR | Woolwich West Box: Cold joint on Wall 14 on B-2 Level |  | Contr | __R | WOO - Woolwich Station (East) |  | 2015-12-04 | 2015-12-11 14:52 | 7 | 2015-06-17 13:58 | Structural Engineering - Concrete Member | 1500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In the event of premature cessation, NSCS 8.2.1.4 requires remedial works to be agreed with the CA before resumption of placing. The concrete supply was interupted whilst pouring Wall 14 on B-2 Level on Woolwich west box. Wall 14 runs from Y6-Y8 along GL B, and between B-B3 on GL Y8. Despite the interuption, the pour continued without CA approval and this has resulted in a visible joint on the east-west section of the wall.
| 03SR - Stations (RfL) | Cxxx-NCR-000035 | NCR | Woolwich West Box: Concrete placement on Wall 14 on B-2 level |  | Contr | __R | WOO - Woolwich Station (East) |  | 2015-12-04 | 2016-02-19 14:48 | 77 | 2015-06-16 11:06 | Structural Engineering - Concrete Member | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | West Box B-2 Level: NSCS Vol4, Clause 8.2.1.1 states: Concrete shall be placed and fully compacted so as to avoid cold joints, honeycombing, and to minimise segregation, excessive blemishes, or other defect in the hardened concrete. Honey-combing is present on the northern face of Wall 14, running along GL B between Y6-Y8. This suggests that the concrete was not fully compacted. The shape of a join line on the wall also suggests that the concrete was not placed in uniform layers of 400mm, as per Cxxx-__R-C-ITP-CR147-50007 Rev 2, Item 6.6
| 03SR - Stations (RfL) | Cxxx-NCR-000036 | NCR | Woolwich West Box: Surface finish to Wall 2 on B-2 Level |  | Contr | __R | WOO - Woolwich Station (East) |  | 2015-12-04 | 2016-02-19 14:45 | 77 | 2015-06-25 15:39 | Structural Engineering - Concrete Member | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Materials And Workmanship Specification Section KF11 - In Situ And Pre-Cast Concrete For Buildings (Cxxx-OVE-A-RSP-CR147-50002) section KF11.1308 for plain formed surface finishes states "blow-holes shall be limited to no more than 5 blow-holes of diameter greater than 5mm in any 1m2 of surface. No single blow-hole shall be greater than 10mm diameter." Post-pour inspection wall of 2 (on grid-line Y7 as per attached marked up plan - slide 1) reveals it does not meet the criteria above with no single blow-holes greater than 10mm (please refer to the photos attached including a sample area)
| 03SR - Stations (RfL) | Cxxx-NCR-000037 | NCR | Woolwich West Box: Surface finish to Wall 3b |  | Contr | __R | WOO - Woolwich Station (East) |  | 2015-12-24 | 2016-03-15 08:19 | 82 | 2015-06-25 16:16 | Structural Engineering - Concrete Member | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Wall 3b located on West Box basement slab -2 located on Gridlines Y6 & B2, has, upon post pour inspection found to have more blow holes on the surface than is allowed in the specification. NSCS 8.6.1.3 states that no more than 5 blow holes greater than 5mm are allowed within 1m2. The specification also states that there must be no blow holes greater 10mm in diameter, see attached photos which shows blow holes out of specification.
| 03SR - Stations (RfL) | Cxxx-NCR-000038 | NCR | Woolwich West Box: Wall 3 Poured 40 mm High |  | Contr | __R | WOO - Woolwich Station (East) |  | 2015-09-30 | 2015-09-11 07:17 | -19 | 2015-07-02 16:47 | Structural Engineering - Structural Engineering - General | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | As shown on drawing no. Cxxx-OVE-S-DDA-CR147_3-61612 (C01) Wall No. 3 runs along gridline Y6 on B-2 level. As shown on Section A drawing no. Cxxx-OVE-S-DDA-CR147_3-61611 (C01) there is a 50mm soft joint on the underside of the beam. (beam shown on Cxxx-OVE-S-DDB-CR147_Z-63611 (C01)) An issue has become apparent that the 50mm joint cannot be achieved. The wall's pour height was set out 20mm high to ensure a good joint with the soffit of the beam. Also the concrete sub-contractor made an error and poured the Wall a further 20mm high. Both of these factors are now preventing us from installing the soft joint.
| 03SR - Stations (RfL) | Cxxx-NCR-000039 | NCR | Falsework and Rebar Installed - West Box Ticket Level |  | Contr | __R | WOO - Woolwich Station (East) |  | 2015-10-01 | 2015-09-11 07:56 | -20 | 2015-06-30 14:05 | Civil - Civil Engineering General | 0 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | No accepted ITP in place prior to strat of works for falsework and rebar installation at the west box ticket hall level.
| 03SR - Stations (RfL) | Cxxx-NCR-000040 | NCR | Woolwich East Box - Crack to Wall 15 Kicker |  | Contr | __R | WOO - Woolwich Station (East) |  | 2015-06-17 | 2015-11-06 14:42 | 142 | 2015-07-03 07:49 | Structural Engineering - Concrete Member | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Upon post pour inspection the kicker for wall 15, a crack was identified in the finished concrete (approximately 1mm in width). The size of the crack is above the maximium crack width of 0.3mm as identified in the NSCS section 8.5.1.
| 03SR - Stations (RfL) | Cxxx-NCR-000041 | NCR | Woolwich East Box - Cracks in wall 2 |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-07-15 | 2016-07-15 13:58 | 0 | 2015-07-03 07:50 | Structural Engineering - Concrete Member | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Upon post pour inspection of wall pour 2 in the east box basement, 3 significant cracks have appeared on the wall. 2 vertical cracks (crack 1 & 2 as per the attached photo) are present which appear to extend completely through the wall, while one diagonal crack (crack 3) from the corner of the door frame is visible only on one side of the walls. These cracks appear to be larger than the maximium crack width of 0.3mm as identified in the NSCS section 8.5.1.
| 03SR - Stations (RfL) | Cxxx-NCR-000042 | NCR | Woolwich East Box - Failure to submit IRF for Pile Integrity Test |  | Contr | __R | WOO - Woolwich Station (East) |  | 2015-07-17 | 2015-09-23 07:20 | 68 | 2015-07-03 07:58 | Geotechnical Engineering - Concrete - Bored Pile | 0 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The integrity testing on the piles in the Woolwich East box was completed 08/06/15. In contradiction to point J5 on the ITP (Cxxx-__R-C-ITP-CR147-50013), an inspection request was not submitted to crossrail to witness the testing.
| 03SR - Stations (RfL) | Cxxx-NCR-000044 | NCR | Woolwich East Box - Construction of second stage of ground beams without an approved ITP |  | Contr | __R | WOO - Woolwich Station (East) |  | 2015-08-31 | 2015-09-01 18:47 | 1 | 2015-07-03 08:18 | Civil - Civil Engineering General | 0 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | An ITP (Cxxx-__R-C-ITP-CR147-50018) had been approved for the first stage of the construction of the ground beams up to blinding the bottom of the beams. The construction of the second stage of the beams (installing reinforcement) began before approval for the second stage of the ITP has been received.
| 03SR - Stations (RfL) | Cxxx-NCR-000045 | NCR | Woolwich East Box - Installation of communications services without an approved method statement |  | Contr | __R | WOO - Woolwich Station (East) |  | 2015-11-30 | 2015-10-30 14:08 | -31 | 2015-07-03 08:22 | Electrical - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Work commenced on installation of communications services in the East box for the new cabins, without an approved method statement.
| 03SR - Stations (RfL) | Cxxx-NCR-000046 | NCR | Woolwich East Box - Cold joint on basement wall 5 |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-01-22 | 2016-02-19 15:10 | 28 | 2015-07-03 08:33 | Structural Engineering - Concrete Member | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In the event of premature cessation, NSCS 8.2.1.4 requires remedial works to be agreed with the CA before resumption of placing. The concrete supply was interrupted whilst pouring Wall 5 on basement level in the Woolwich East box. Wall 5 runs along the box north of GL B2, and between Z5 & Z6. Despite the interuption, the pour continued without CA approval and this has resulted in a visible pour line in the wall.
| 03SR - Stations (RfL) | Cxxx-NCR-000047 | NCR | Woolwich East Box - Concrete placement on basement wall 5 (Honeycombing) |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-01-22 | 2016-01-22 09:31 | 0 | 2015-07-03 08:42 | Structural Engineering - Concrete Member | 1000 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In reference to KF11.1308 (Plain finishes), wall 5 on the basement level has honeycombing less than 10mm in depth as per the attached photos.
| 03SR - Stations (RfL) | Cxxx-NCR-000048 | NCR | Woolwich East Box - Cranking of Bars on Wall 13 |  | Contr | __R | WOO - Woolwich Station (East) |  | 2015-09-30 | 2015-09-15 13:11 | -15 | 2015-07-03 08:46 | Structural Engineering - Reinforcement | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | In reference to the attached marked up reinforcing drawing Cxxx-__R-S-DWG-CR147-50001, the bar mark 15 U bars on wall B (as highlighted in the attached drawing) were cranked on site prior to approval (please refer to the attached photo). The bar mark 15 U bars (from Wall C) on wall B drawing Cxxx-__R-S-DWG-CR147-50001 in some locations did not align with the spacings of the U bars from Wall A. These U bars were cranked to ensure the lacers (Bark Mark 13) are horizontal and align with the opposing U bars. This occured due to the orignal U bars from wall A not aligning with the U bars from Wall C.
| 03SR - Stations (RfL) | Cxxx-NCR-000049 | NCR | Woolwich East Box - Incorrect cover on wall 10 |  | Contr | __R | WOO - Woolwich Station (East) |  | 2015-07-17 | 2015-11-05 16:07 | 111 | 2015-07-03 08:48 | Structural Engineering - Reinforcement | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | In reference to the drawing Cxxx-__R-S-DWG-CR147-50002 REV C01, the bar mark 23 U bars in wall C (as per the attached drawing) have been installed with incorrect concrete cover (Wall C has been poured but Wall H has not) . At the worst location the cover is only 35mm to the U bar, the specified cover is 50mm as per note 6 on the drawing above, with a minimum required cover of 40mm as per the NSCS Standard CL 10.8.1. Three bars have been installed with cover less than 40mm.
| 03SR - Stations (RfL) | Cxxx-NCR-000050 | NCR | Woolwich East Box: Casting of walls with omitted half-landing connections |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-06-10 | 2016-06-10 08:12 | 0 | 2015-07-06 13:32 | Structural Engineering - Concrete Member | 1500 |  | Design | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The walls in the east box from basement level to ground floor level, adjacent the stairwell half landings, have been cast without the final details for the wall to half landing connections.
| 03SR - Stations (RfL) | Cxxx-NCR-000051 | NCR | Woolwich West Box - Fixing steel to code 3 drawings |  | Contr | __M | WOO - Woolwich Station (East) |  | 2015-10-31 | 2015-09-22 07:59 | -39 | 2015-07-10 11:25 | Structural Engineering - Concrete Member | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The contractor failed to get the Project Manager's approval before fixing steel to unapproved drawings. Steel has been fixed to the walls listed below whilst the drawings were at Code 3 status: Wall 4 and Wall 5 on Drawing Cxxx-__R-S-DWG-CR147-50035 C02 Wall 9 and Wall 10 on Drawing Cxxx-__R-S-DWG-CR147-50036 C02 Wall 47 on Drawing Cxxx-__R-S-DWG-CR147-50041 C01
| 03SR - Stations (RfL) | Cxxx-NCR-000053 | NCR | Woolwich West Box: Visible Spacer Blocks to Wall 14 on B-2 Level |  | Contr | __R | WOO - Woolwich Station (East) |  | 2015-12-04 | 2016-01-20 17:28 | 47 | 2015-07-17 12:29 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | Architectural Specification JE20.1207 clause e) vi): States: No spacers shall be visible. Wall 14 shows incorrect installation of spacer blocks
| 03SR - Stations (RfL) | Cxxx-NCR-000054 | NCR | Short Notice Change - Gallow Brackets |  | Contr | __R | WOO - Woolwich Station (East) |  | 2015-08-14 | 2015-08-13 14:51 | -1 | 2015-07-31 12:53 | Structural Engineering - Diaphragm Walls | 0 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | NCR-PTR-00016 Work to Gallow Brackets (as instructed under Cxxx-PMI-00045) carried out under SNC to Cxxx-__R-C-GMS-CR147-50018 (Woolwich East Box RC Walls & Columns Construction). Cxxx-PMC-00317 states all SNCs must be signed off by CRL, however, template issued under PMC is not valid for Cxxx. As a result, SNC not signed by CRL.
| 03SR - Stations (RfL) | Cxxx-NCR-000055 | NCR | Short Notice Change - Diaphragm Wall Couplers |  | Contr | __R | WOO - Woolwich Station (East) |  | 2015-09-30 | 2015-08-26 18:31 | -35 | 2015-07-31 12:55 | Structural Engineering - Diaphragm Walls | 0 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other management problem | Completed |  | NCR-PTR-00017 Work to diaphragm wall couplers in East Box carried out under SNC to Cxxx-__R-C-GMS-CR147-50030 (Woolwich East Box Construction of RC Slabs). Cxxx-PMC-00317 states all SNCs must be signed off by CRL, however, template issued under PMC is not valid for Cxxx. As a result, SNC not signed by CRL. Modified, un-issued CRL SNC template to be used. Guidance note to be issued by CRL to define what a SNC can be used for.
| 03SR - Stations (RfL) | Cxxx-NCR-000056 | NCR | Woolwich West Box - Discolouration of concrete on wall 4 at B-1 level |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-07-08 | 2016-07-15 08:38 | 7 | 2015-07-27 15:19 | Structural Engineering - Finishes | 0 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Materials And Workmanship Specification Section KF11 - In Situ And Pre-Cast Concrete For Buildings (Cxxx-OVE-A-RSP-CR147-50002) section KF11.1308 for plain formed surface finishes states "Poor application of mould oil leading to discolouration and blemishes of plain concrete finish on north face, excessive blowholes at the top of the pour, compaction looks a bit inconsistent at the top of the wall as well". (please refer to the photos attached including a sample area)
| 03SR - Stations (RfL) | Cxxx-NCR-000057 | NCR | Woolwich West Box - Discolouration of north and south face of concrete on Wall 3 at B-1 Level |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-07-08 | 2016-07-15 08:41 | 7 | 2015-07-27 15:51 | Structural Engineering - Finishes | 0 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Materials And Workmanship Specification Section KF11 - In Situ And Pre-Cast Concrete For Buildings (Cxxx-OVE-A-RSP-CR147-50002) section KF11.1308 for plain formed surface finishes states "Lack off mould oil on south face of wall 3 causing discolouration, and discolouration on north face which was possibly caused by a dirty shutter or excessive mould oil application, excessive blowholes >5mm". (please refer to the photos attached including a sample area)
| 03SR - Stations (RfL) | Cxxx-NCR-000058 | NCR | Woolwich West Box - Poor compaction at toe of wall 3 at B-2 Level |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-04-13 | 2016-04-21 13:53 | 8 | 2015-07-27 15:34 | Structural Engineering - Finishes | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Materials And Workmanship Specification Section KF11 - In Situ And Pre-Cast Concrete For Buildings (Cxxx-OVE-A-RSP-CR147-50002) section KF11.1308 for plain formed surface finishes states "Poor compaction at toe of wall leading to honeycombing of plain concrete finish, blow-holes shall be limited to no more than 5 blow-holes of diameter greater than 5mm in any 1m2 of surface. No single blow-hole shall be greater than 10mm diameter." (please refer to the photos attached including a sample area)
| 03SR - Stations (RfL) | Cxxx-NCR-000059 | NCR | Woolwich West Box - Uncomplete work on wall 4 at level B-2 to B-1 |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-05-13 | 2016-03-16 13:52 | -58 | 2015-07-28 15:18 | Structural Engineering - Finishes | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Materials And Workmanship Specification Section KF11 - In Situ And Pre-Cast Concrete For Buildings (Cxxx-OVE-A-RSP-CR147-50002) section KF11.3101 for fabrication and workmanship states "All fabrication shall be in accordance with the NSCS and all relevant standards referenced therein." (please refer to the attached sketch drawing)
| 03SR - Stations (RfL) | Cxxx-NCR-000060 | NCR | Woolwich East Box - Ground Beam pour 2 (Beam 3, 4, 5) surface cracking |  | Contr | __R | WOO - Woolwich Station (East) |  | 2015-08-14 | 2015-08-25 16:37 | 11 | 2015-07-31 14:22 | Structural Engineering - Concrete Member | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | NCR-PTR-00019 Pour date: 15/07/15 Post pour inspection with Cxxx/__ found cracks with 0.3mm or less. Cracks were found with widths of more than 0.3mm but no more than 0.5mm. One of these cracks is within the boxed cross beam area.
| 03SR - Stations (RfL) | Cxxx-NCR-000061 | NCR | Woolwich East Box - Ground Beam pour 3 (Beam 6) surface cracking |  | Contr | __R | WOO - Woolwich Station (East) |  | 2015-08-14 | 2015-08-25 16:39 | 11 | 2015-07-31 17:31 | Structural Engineering - Concrete Member | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | NCR-PTR-00020 __ Reference No Cxxx-__-NCR-005 Inspection by Cxxx/__ found: - cracks with widths 0.3mm or less - cracks with widths more than 0.3mm but no more than 0.5mm. Cracks on oposite sides of the beam joined along the top of the beam. Please see attached location sketch and photos
| 03SR - Stations (RfL) | Cxxx-NCR-000062 | NCR | Woolwich West Box - Surface Finish to wall 7 at level B-1 |  | Contr | __R | WOO - Woolwich Station (East) |  | 2015-12-24 | 2016-03-15 09:37 | 82 | 2015-08-11 14:48 | Structural Engineering - Finishes | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Materials And Workmanship Specification Section KF11 - In Situ And Pre-Cast Concrete For Buildings (Cxxx-OVE-A-RSP-CR147-50002) section KF11.1308 for plain formed surface finishes states "Poor compaction at toe of wall leading to honeycombing of plain concrete finish, blow-holes shall be limited to no more than 5 blow-holes of diameter greater than 5mm in any 1m2 of surface. No single blow-hole shall be greater than 10mm diameter." (please refer to the photos attached including a sample area)
| 03SR - Stations (RfL) | Cxxx-NCR-000064 | NCR | Woolwich West Box - Rust stain on soffit of B-1 level Slab |  | Contr | __R | WOO - Woolwich Station (East) |  | 2015-12-31 | 2016-01-20 17:37 | 20 | 2015-08-12 17:38 | Structural Engineering - Finishes | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | Materials And Workmanship Specification Section KF11 - In Situ And Pre-Cast Concrete For Buildings (Cxxx-OVE-A-RSP-CR147-50002): Section KF11.1423 states "They shall not leave metallic elements close to the surface that cause a risk of later rust streaking". Section P1.4.8 states "Measures must also be taken to prevent rust-staining form any metallic elements from marking the special concrete finishes". (please refer to the photos attached including a sample area)
| 03SR - Stations (RfL) | Cxxx-NCR-000065 | NCR | Woolwich West Box - Cxxx-IRF-0102 |  | Contr | __R | WOO - Woolwich Station (East) |  | 2015-08-26 | 2015-09-28 13:02 | 33 | 2015-08-12 17:39 | Surveying - Structural surveys | 0 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | CRL were invited to inspect wall 1 and it was not ready at the point/time of inspection. Some of the issues noted at inspection are: - Cutting splices full height of the pour in contact with the back plate of the kwikastrip to ensure concrete encapsulation is achieved - Rebar lacking tie wire - Cleanliness of rebar in-particular around construction joints - Mould oil required on erected shutter - Removal of duct tape on kwikastrips
| 03SR - Stations (RfL) | Cxxx-NCR-000066 | NCR | Woolwich West Box - Cxxx-IRF-0099 |  | Contr | __R | WOO - Woolwich Station (East) |  | 2015-08-26 | 2015-09-28 13:03 | 33 | 2015-08-12 17:39 | Surveying - Structural surveys | 0 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | CRL were invited to inspect wall 4 and it was not ready at the point/time of inspection. Some of the issues noted at inspection are: - Not enough spacers (vertically spaced too wide) - Kicker unscabbled in places, requiring hoovering as well. - Kwikastrip not cleaned, duct tape not removed - Spliced rebar to kwikastrip touching backplate of kwikastrip (no encapsulation) - Not enough tie wire on horizontal bars.
| 03SR - Stations (RfL) | Cxxx-NCR-000067 | NCR | Woolwich West Box - Poor compaction at toe of Wall 1 at B-2 level |  | Contr | __R | WOO - Woolwich Station (East) |  | 2015-12-24 | 2016-03-31 09:48 | 98 | 2015-08-12 17:40 | Structural Engineering - Finishes | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Materials And Workmanship Specification Section KF11 - In Situ And Pre-Cast Concrete For Buildings (Cxxx-OVE-A-RSP-CR147-50002) section KF11.1308 for plain formed surface finishes states "Poor compaction at toe of wall leading to honeycombing of plain concrete finish, blow-holes shall be limited to no more than 5 blow-holes of diameter greater than 5mm in any 1m2 of surface. No single blow-hole shall be greater than 10mm diameter." (please refer to the photos attached including a sample area)
| 03SR - Stations (RfL) | Cxxx-NCR-000068 | NCR | West Box - Wall 11 (Full Height) lack of concrete cover to tie bar holes. |  | Crossrail | PDP | WOO - Woolwich Station (East) |  | 2015-12-24 | 2016-04-01 08:31 | 99 | 2015-08-12 16:13 | Structural Engineering - Concrete Member | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Tie bar holes can be observed to be located within the 'cover' zone of the soffit which presents an issue with regards to fire proofing as in the event of a fire the tie bar holes within the cover zone would be suseptible to fire damage. The central tie bar hole has approx 10-15 mile cover and there is an area directly beneath it which also appears to lack significant compaction.
| 03SR - Stations (RfL) | Cxxx-NCR-000069 | NCR | Wall 7 - Non-compliant concrete finish to surface |  | Crossrail | PDP | WOO - Woolwich Station (East) |  | 2015-12-04 | 2015-12-11 14:38 | 7 | 2015-08-12 15:14 | Structural Engineering - Concrete Member | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On the 15/07/15 it was observed that Wall 7 (Full Height) on the B-2 Slab on the Y10 Grid line had a non compliant plain concrete finish to its east face. Upon observation it appears the shutter had a lack of mould oil / release agent applied causing the plain concrerte finish to have a rough surface with numerous blowholes outside that of the specification requirement. The concrete finish for this wall is non compliant with items 8.2 & 10.5 of Cxxx-__R-C-ITP-CR147-50007 (Rev 5).
| 03SR - Stations (RfL) | Cxxx-NCR-000070 | NCR | West Box - Wall 6 (Half Height) concrete finish |  | Crossrail | PDP | WOO - Woolwich Station (East) |  | 2015-12-24 | 2016-03-02 12:19 | 69 | 2015-08-12 15:35 | Structural Engineering - Concrete Member | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | On the 15/07/15 it was observed that Wall 6 (Half Height) on the B-1 Slab on the between Y6-7 Grid line had a non compliant plain concrete finish to its east & west face. Upon observation it appears the shutter had a lack of mould oil / release agent applied causing the plain concrerte finish to have a very discoloured surfaceon both the east and west faces outside that of the specification requirement. The concrete finish for this wall is non compliant with items 8.2 & 10.5 of Cxxx-__R-C-ITP-CR147-50007 (Rev 5).
| 03SR - Stations (RfL) | Cxxx-NCR-000071 | NCR | Not ready at the point of inspection IRF-0099 (West Box Wall 4 Full Height) |  | Crossrail | PDP | WOO - Woolwich Station (East) |  | 2015-09-30 | 2015-09-01 19:39 | -29 | 2015-08-12 16:29 | Structural Engineering - Concrete Member | 0 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The inspections (IRF-099) had not been checked fully by the __ Site Engineer and required re-inspections following a series of modifications including - Cutting splices full height of the pour in contact with the back plate of the kwikastrip to ensure concrete encapsulation is achieved - Rebar lacking tie wire - Cleanliness of rebar in-particular around construction joints - Spacers missing - Mould oil required on erected shutter - Scabbling of construction joints - Removal of duct tape on kwikastrips
| 03SR - Stations (RfL) | Cxxx-NCR-000072 | NCR | Not ready at the point of inspection IRF-0102 (West Box Wall 1 Full Height) |  | Crossrail | PDP | WOO - Woolwich Station (East) |  | 2015-09-30 | 2015-09-01 19:39 | -29 | 2015-08-12 16:36 | Structural Engineering - Concrete Member | 0 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The initial inspection (IRF-0102) had not been checked fully by the __ Site Engineer and required re-inspections following a series of modifications including - Cutting splices full height of the pour in contact with the back plate of the kwikastrip to ensure concrete encapsulation is achieved - Rebar lacking tie wire - Cleanliness of rebar in-particular around construction joints - Mould oil required on erected shutter - Scabbling of construction joints - Removal of duct tape on kwikastrips
| 03SR - Stations (RfL) | Cxxx-NCR-000074 | NCR | Woolwich East Box - Cracking to Ground Bearing Slab E6 to Z12 (Pour 1) |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-03-01 | 2016-03-02 08:47 | 1 | 2015-10-28 13:49 | Civil - Civil Engineering General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Cracking has occurred to the east box ground slab pour 1 (as per the attached drawing). The cracks are in a regular pattern, simlar to the reinforcement and are greater then 0.3mm in width and up to 0.6mm in width.
| 03SR - Stations (RfL) | Cxxx-NCR-000075 | NCR | Woolwich East Box - Cracking to Ground Bearing Slab E6 to Z12 (Pour 2) |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-03-01 | 2016-03-02 11:45 | 1 | 2015-10-28 13:49 | Civil - Civil Engineering General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Cracking has occurred to the east box ground slab pour 2 (as per the attached drawing). The cracks are in a regular pattern, simlar to the reinforcement and are greater then 0.3mm in width and up to 0.6mm in width.
| 03SR - Stations (RfL) | Cxxx-NCR-000076 | NCR | Woolwich Westbox |  | Contr | __R | WOO - Woolwich Station (East) |  | 2015-12-18 | 2015-12-11 14:42 | -7 | 2015-09-09 08:39 | Structural Engineering - Reinforcement | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | Based on the reinforcement inspection carried of Wall 15 B-2 (GL D-D3; W1-Y5). It was identified that there is insufficient concrete cover along wall 19 and the adjoining corner between wall 19 and wall 14, cover being between 35mm and 40mm rather than the required 50mm. The extent of the poor cover is from B-2 Ground Level to top of kicker approx (150mm vertically).
| 03SR - Stations (RfL) | Cxxx-NCR-000077 | NCR | Woolwich East Box - EC2 Ground beam columns bars |  | Contr | __R | WOO - Woolwich Station (East) |  | 2015-09-17 | 2015-10-15 08:54 | 28 | 2015-09-03 15:24 | Structural Engineering - Reinforcement | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The starters bars for columns EC2 (East box above ground floor beam A and B), have been built according to drawing Cxxx-__R-S-DWG-CR147-50084 C01, 8 bars on each face and none on the sides. The Cxxx intent, drawing Cxxx-OVE-S-DDL-CR147_Z-75701 C01, is 7 bars in each face and 1 on each side. Drawing Cxxx-__R-S-DWG-50019 C02, is consistent with the Cxxx intent drawing.
| 03SR - Stations (RfL) | Cxxx-NCR-000078 | NCR | Insufficient Cover to __ Couplers in East Box Ground Slab |  | Contr | __R | WOO - Woolwich Station (East) |  | 2015-11-12 | 2015-11-06 07:55 | -6 | 2015-10-29 10:06 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A number of female lenton couplers (Bar Mark 26 on Cxxx-__R-S-DWG-CR147-50050) have been installed with concrete cover less than 50mm. At the worst case the cover is approximate 32mm, refer to the attached photo and marked up drawing.
| 03SR - Stations (RfL) | Cxxx-NCR-000083 | NCR | NCR- Woolwich West Box - Incorrect Concrete Placement |  | Contr | __R | WOO - Woolwich Station (East) |  | 2015-12-24 | 2016-02-04 17:26 | 42 | 2015-09-17 16:41 | Structural Engineering - Finishes | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 1.Initial Delay with __ compliance checks over at East box resulting in __ being late to West box. 2. Slump was 170 and well within target range. 3.Wall was poured within 2 hours of batching 4.As pour progressed ops moved onto second wall and began having blockage issues with the skip. Consequently concrete was not placed correctly in correct layer sequence due to rushing to get concrete out of skip before it became too stiff. Internal and external pokers were used in an attempt to spread concrete throughout the wall however unfortunately it was too hard by this point. Following placement of initial pour, a delay in subsequent __ load caused a cold joint to form in the wall. 3m+ vertically and 2.5m horizontally.
| 03SR - Stations (RfL) | Cxxx-NCR-000085 | NCR | Woolwich Station - East Box: Large blow holes at the vertical face of ground slab's opening near GLs E and E1 |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-03-01 | 2016-03-09 16:25 | 8 | 2015-10-26 10:49 | Structural Engineering - Concrete Member | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Several large blow holes have been created at the vertical face of ground slab's opening near GLs E and E1. Their size exceeds the 10mm limit as per the section KF11.1308 of Cxxx - Materials & Workmanship Specification (Cxxx-OVE-A-RSP-CR147-50002 3.0). The required finish of the element is plain. Their size varies from 15mm to 45mm long and 15mm to 40mm deep. No reinforcement has been exposed.
| 03SR - Stations (RfL) | Cxxx-NCR-000086 | NCR | Woolwich Station - East Box: Incorrect installation of starter bars for ground floor walls GL: Z4 - D2 |  | Contr | __R | WOO - Woolwich Station (East) |  | 2015-12-05 | 2015-10-30 16:40 | -36 | 2015-10-26 11:21 | Structural Engineering - Concrete Member | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | During the installation of the basement walls' reinforcement as per drawing Cxxx-__R-S-DWG-CR147-50001 C02, at wall A Gls: Z4 - D2, the change in barmark of vertical bars was not correctly identified and 2no. bars on each face from barmark 01 were installed instead of barmark 03 and 23. The result was to have extra starter bars for the ground walls.
| 03SR - Stations (RfL) | Cxxx-NCR-000087 | NCR | Incorrect installation of 32mm D Wall Couplers in West Box |  | Contr | __R | WOO - Woolwich Station (East) |  | 2015-11-04 | 2015-11-09 19:14 | 5 | 2015-10-21 08:51 | Structural Engineering - Reinforcement | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Along the south D wall at (GL E;W1-W7), in scattered, isolated areas the outside face of couplers have been installed as 32mm couplers rather than 25mm couplers all of which are installed onto 25mm starter bars. There are approx. 20 incorrect couplers along the south face.
| 03SR - Stations (RfL) | Cxxx-NCR-000089 | NCR | Woolwich East Box - Honeycombing to Ground Level Walls GL Z12 |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-01-22 | 2016-01-18 16:15 | -4 | 2015-10-19 18:05 | Structural Engineering - Concrete Member | 2500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In reference to KF11.1308 (Plain finishes), the walls on GLZ12 have honeycombing greater than 10mm in depth.
| 03SR - Stations (RfL) | Cxxx-NCR-000090 | NCR | Woolwich West box - Making good without approval |  | Contr | __M | WOO - Woolwich Station (East) |  | 2015-11-06 | 2015-11-03 13:03 | -3 | 2015-10-23 18:24 | Structural Engineering - Finishes | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Inspection and test Plan Cxxx-__R-C-ITP-CR147-50017 C02, line item 3.1, requires a joint inspection (between __ and CRL) of RC walls to determine and agree making good requirements for each element of the works. During a site inspection on 16th October, making good repairs were found on 2 sections of walls at platform level without the joint inspection having taking place. The following areas are in non-compliance with the ITP: Southern face of wall 23 - evidence of the wall having been 'bag washed' Southern face of wall 1 - wet mortar applied to the wall
| 03SR - Stations (RfL) | Cxxx-NCR-000091 | NCR | Woolwich East Box - Honeycombing to Ground Level Columns GL Z9 & Z10 |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-01-22 | 2015-12-10 16:22 | -43 | 2015-10-20 17:52 | Civil - Civil Engineering General | 2000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In reference to KF11.1308 (Plain finishes), the columns GLZ9 & Z10 (C34, 35, 36, 37, 38, & 39) have honeycombing greater than 10mm in depth.
| 03SR - Stations (RfL) | Cxxx-NCR-000092 | NCR | Woolwich East Box - Honeycombing to Ground Level Columns GL E6 to Z8 |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-04-01 | 2016-03-31 13:33 | -1 | 2015-10-20 18:02 | Civil - Civil Engineering General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In reference to KF11.1308 (Plain finishes), the columns on gridlines E6 to Z8 (C13, C19, C21, C23, C24, C25 & C26) have honeycombing greater than 10mm in depth.
| 03SR - Stations (RfL) | Cxxx-NCR-000094 | NCR | Woolwich East Box - Rust staining of ground floor soffit (Ground Slab Pour 2a) |  | Crossrail | PDP | WOO - Woolwich Station (East) |  | 2016-04-01 | 2016-02-12 08:58 | -49 | 2015-10-21 10:05 | Structural Engineering - Finishes | 3000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | Rust Staining of soffit between Grid Ref [ E1 to (Z4+4.720) ] to [ (D2-150mm) to E ] part of Ground Slab Pour 2a has been observed to be non compliant with KF11.1308
| 03SR - Stations (RfL) | Cxxx-NCR-000095 | NCR | Woolwich East Box - Excessive Blowholes Wall Pours 37, 39, 40 & 41. Also C41 and C42 |  | Crossrail | PDP | WOO - Woolwich Station (East) |  | 2016-05-31 | 2016-05-31 14:43 | 0 | 2015-10-21 10:13 | Structural Engineering - Finishes | 4000 |  | Workmanship | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Wall Pours 37, 39, 40 & 41. Also C41 and C42 on Gridlines Z12 & Z11 respectively have been observed to have more than 5 blowholes of diameter greater than 5mm in 1m² area or 1 No. blowhole + greater than 10mm² for Ground Floor (A2 & B2 defects) which is non compliant KF11 1308.
| 03SR - Stations (RfL) | Cxxx-NCR-000096 | NCR | Woolwich East Box - Excessive Blowholes Column Pours C18, C38 & C39 |  | Crossrail | PDP | WOO - Woolwich Station (East) |  | 2016-04-01 | 2016-03-31 13:44 | -1 | 2015-10-21 10:20 | Structural Engineering - Finishes | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Inadequate/insufficient tooling. | Completed |  | C18, C38 & C39 on the Woolwich East Box have collectively been observed to have more than 5 blowholes of diameter greater than 5mm in 1m² area or 1 No. blowhole + greater than 10mm² for Ground Floor (A2 & B2 defects) which is non compliant KF11 1308.
| 03SR - Stations (RfL) | Cxxx-NCR-000097 | NCR | Woolwich East Box - Excessive Blowholes Column Pours C02, C03, C05, C06 & C07 |  | Crossrail | PDP | WOO - Woolwich Station (East) |  | 2015-11-27 | 2015-12-18 10:36 | 21 | 2015-10-21 10:23 | Structural Engineering - Finishes | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Column Pours C02, C03, C05, C06 & C07 on the Woolwich East Box have collectively been observed to have more than 5 blowholes of diameter greater than 5mm in 1m² area or 1 No. blowhole + greater than 10mm² for Ground Floor (A2 & B2 defects) which is non compliant KF11 1308.
| 03SR - Stations (RfL) | Cxxx-NCR-000098 | NCR | Woolwich East Box - Lack of colour uniformity / excessive discolouration to Ground Floor Column pours C34, C35, C36, C37, C38 & C39 |  | Crossrail | PDP | WOO - Woolwich Station (East) |  | 2016-04-01 | 2016-03-10 17:37 | -22 | 2015-10-21 10:35 | Structural Engineering - Finishes | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Lack of colour uniformity / excessive discolouration caused by dirty shutters to Ground Floor Column pours C34, C35, C36, C37, C38 & C39 along the Z10 Gridline has been observed.
| 03SR - Stations (RfL) | Cxxx-NCR-000099 | NCR | East Box - Honey Combing to C01 & C02 |  | Crossrail | PDP | WOO - Woolwich Station (East) |  | 2015-11-27 | 2015-12-16 14:54 | 19 | 2015-10-21 10:44 | Structural Engineering - Finishes | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A honeycombed appearance due to major grout loss or poor compaction for Ground Floor Column pours C01 & C02 along Gridline E has been observed.
| 03SR - Stations (RfL) | Cxxx-NCR-000100 | NCR | Woolwich East Box - Poor cleaning of Ground Slab Pour 2b & discoloration to soffit |  | Crossrail | PDP | WOO - Woolwich Station (East) |  | 2015-11-25 | 2016-02-12 09:14 | 79 | 2015-10-21 10:51 | Structural Engineering - Finishes | 3000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | Poor cleaning out along edge of soffit along Grid Ref Z4 for Ground Slab Pour 2b. Foreign / loose material to be removed has been observed. Concrete is discoloured compared to other concrete soffits and rust staining evident. Small area of blow holes also located in an approximate region of [Z2-Z3] to [B]
| 03SR - Stations (RfL) | Cxxx-NCR-000101 | NCR | Woolwich West Box - Large areas of honey combing located within both faces of Walls 1,2 & 3 at Platform Level |  | Crossrail | PDP | WOO - Woolwich Station (East) |  | 2016-05-13 | 2016-03-31 09:39 | -43 | 2015-10-21 12:01 | Structural Engineering - Finishes | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Upon Observation of Walls 1-3 at Platform Level in the West Box it was observed that the concrete finish was non compliant with 4 poorly compacted areas of concrete observed 500mm+ in width / length on the North Face of the Wall and 2 areas of the South Face of Walls 1 & 2. The classification of this repair is either a B3 or C3 pending investigation. This observation was first raised with The Contractor on the 11/09/15 but no NCR had been raised on the eB System.
| 03SR - Stations (RfL) | Cxxx-NCR-000103 | NCR | West Box - Wall 23 B3 defect caused by foreign object being incoporated within pour |  | Crossrail | PDP | WOO - Woolwich Station (East) |  | 2015-11-05 | 2015-11-16 09:12 | 11 | 2015-10-22 18:13 | Structural Engineering - Concrete Member | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | It would appear that a foreign object possibly a length of timber had fallen into the pour and ended up being cast in the concrete. Further to this the defect had been repaired without the necessary paperwork and acceptance of preparation from CRL in place. An NCR was raised for this non compliant repair previously
| 03SR - Stations (RfL) | Cxxx-NCR-000104 | NCR | NCRs not raised in a timely manner |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2015-12-22 | 2015-12-04 13:18 | -18 | 2015-10-23 11:45 | Civil - Civil Engineering General | 500 |  | System Defect | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Contractor failed to record NCRs on eB in a timely manner (West Box and East Box). NCRs were not recorded on eB-PTR within 24 hrs. CRL has requested the following NCRs to be raised on 15/10/2015 (see attached emails by Danny McEvoy) and finally raised by CRL on 21/10/2015. As per CRL WI CRL1-XRL-V3-XWI-CR001-50035 _ Cl.20.8: "Where a Defect in a works item is noted that cannot be put back in compliance within the same shift the Contractor shall raise a NCR. Where a specified work activity has not been carried out in accordance with agreed procedural requirements, a NCR is raised. Unless otherwise accepted by the Supervisor, the Contractor shall enter each NCR, including sub-contractor NCRs, in the PTR system." Also, as per __'s internal procedure Cxxx-__R-O4-GPD-CR147-50005 "Nonconformance, Corrective, Preventive and Improvement Actions Procedure" Cl. 3.1 : "NCRs will be raised within 24 hours of the nonconformance being identified."
| 03SR - Stations (RfL) | Cxxx-NCR-000105 | NCR | West Box - Failure to complete infilling of kwikastrips in Patform Soffit / following ITP - Walls 13-21 |  | Crossrail | PDP | WOO - Woolwich Station (East) |  | 2015-12-11 | 2015-11-27 08:10 | -14 | 2015-10-26 08:21 | Fire - Compartmentation | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | It has been observed that the surface preparation and infilling of Kwikastrips within the Platform Soffits on the West Box has not taken place prior to the full construction of secondary walls 13-21. This does not follow the detail in Section 8 of Cxxx-__R-C-ITP-CR147-50007. These works are not consider to be a post pour activity by the Client. Following full construction of these secondary walls a 50mm gap left at the top of the wall for the installation of the soft joint compressible filler severely hinders the ability to prepare and infill the Kwikastrips with mortar. These works are being undertaken to ensure 2hr Fire Rating is achieve at the top of the secondary walls. (These works were instructed by CRL as part of Cxxx-PMI-00141)
| 03SR - Stations (RfL) | Cxxx-NCR-000106 | NCR | Woolwich West Box - Honeycombed appearance on platform walls 12, 13, 15, 17, 19, 21, 22 & 27 |  | Contr | __R | WOO - Woolwich Station (East) |  | 2015-11-09 | 2015-12-10 08:16 | 31 | 2015-10-26 17:52 | Architectural - Finishes | 4500 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Post-pour inspection of walls 12, 13, 15, 17, 19, 21, 22 & 27 (on grid-lines as per sketch) reveals it does not meet the criteria above (please refer to the photos attached for location)
| 03SR - Stations (RfL) | Cxxx-NCR-000107 | NCR | Woolwich West Box - Excessive blowholes on platform walls 26, 27 & 27a |  | Contr | __R | WOO - Woolwich Station (East) |  | 2015-11-10 | 2015-11-26 09:12 | 16 | 2015-10-27 12:59 | Architectural - Finishes | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Materials And Workmanship Specification Section KF11 - In Situ And Pre-Cast Concrete For Buildings (Cxxx-OVE-A-RSP-CR147-50002) section KF11.1308 for formed surface finishes states thatBlowholes shall be limited to no more than 5 blowholes of diameter greater than 5mm in any 1m² of surface. No single blow hole shall be greater than 10mm diameter. Any concrete so affected may not be accepted in the final works. Post-pour inspection of walls 26, 27a & 27 (on grid-lines as per sketch) reveals it does not meet the criteria above (please refer to the photos attached for location)
| 03SR - Stations (RfL) | Cxxx-NCR-000108 | NCR | Woolwich West Box - Missing chamfers for Walls 22a and 27a & Out of tolerance for Wall 15 |  | Contr | __R | WOO - Woolwich Station (East) |  | 2015-12-31 | 2015-11-19 16:39 | -42 | 2015-10-27 14:53 | Architectural - Finishes | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | Cxxx Woolwich Architectural Specification (Cxxx-OVE-A-RSP-CR147-50001) Section JE20.1203 (j) states that exposed arrises shall have chamfered edges.
| 03SR - Stations (RfL) | Cxxx-NCR-000110 | NCR | Woolwich Station - East Box: Discoloration of Basement wall no.15 |  | Contr | __R | WOO - Woolwich Station (East) |  | 2015-11-18 | 2015-11-03 10:56 | -15 | 2015-10-28 10:42 | Structural Engineering - Finishes | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | Discoloration of south side of basement wall no.15
| 03SR - Stations (RfL) | Cxxx-NCR-000111 | NCR | Woolwich Station - East Box: Blowholes at the surfaces of basement RC walls |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-07-15 | 2016-07-19 13:39 | 4 | 2015-10-30 09:12 | Structural Engineering - Finishes | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | After inspection, small (less than 10mm) blowholes covering large areas (over 1m2) of the walls and large blowholes (more than 10mm) have been found at the surfaces of the reinforced concrete walls 1 to 20 at the basement level, apart from walls 12 and 13.
| 03SR - Stations (RfL) | Cxxx-NCR-000112 | NCR | Woolwich Station - East Box: Honeycombing to Basement Walls |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-07-15 | 2016-07-19 13:49 | 4 | 2015-10-30 12:20 | Structural Engineering - Concrete Member | 4000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Honeycombing appearance at reinforced concrete walls, grade A3 ( minor grout loss) and B3 (major grout loss/pour compaction) as per classification in Method Statement "Woolwich Box Concrete Repair and Making Good Concrete Finished Surfaces Method" (Cxxx-__R-C-GMS-CR147-50020 4.0). Class B3 is present at walls 5 and 19. Class A3 is present at the bottom of the majority of walls. Full list to be submitted at a later stage.
| 03SR - Stations (RfL) | Cxxx-NCR-000113 | NCR | Woolwich Station - East Box: Lack of concrete cover at basement walls 3,4 and 15 due to tie bar holes |  | Contr | __R | WOO - Woolwich Station (East) |  | 2015-11-25 | 2015-11-25 13:45 | 0 | 2015-10-30 12:57 | Structural Engineering - Concrete Member | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Tie bar holes can be observed within the cover zone of the reinforcement along the height of basement walls no. 3 (north end), 4(south end) and no.15 (east end), which presents an issue with regards to fire proofing as in the event of a fire the tie bar holes within the cover zone would be susceptible to fire damage.
| 03SR - Stations (RfL) | Cxxx-NCR-000114 | NCR | Woolwich East Box - Cold Joint to Platform Walls on Gridline E1 |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-01-22 | 2016-02-05 14:21 | 14 | 2015-11-02 17:48 | Civil - Civil Engineering General | 6000 |  | Incomplete Works | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During construction of the second lift of the platform walls on gridline E1 (Walls 1, 2, 3, & 4) as per the attached pour sequence drawing), the concrete supply was intrerrupted resulting in an incomplete pour and a cold joint.
| 03SR - Stations (RfL) | Cxxx-NCR-000115 | NCR | Integrity Testing of Existing West Box Pile Beneath Ground Slab |  | Contr | __R | WOO - Woolwich Station (East) |  | 2015-11-16 | 2015-11-09 19:38 | -7 | 2015-11-02 17:18 | Civil - Civil Engineering General | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | As a result of tester turning up to site early CRL were not given an oportunity to witness integrity testing of pile Y2-C as requested.
| 03SR - Stations (RfL) | Cxxx-NCR-000116 | NCR | Woolwich Station - East Box: Ground Secondary Walls 1 and 2 incorrect reinforcement detail |  | Contr | __R | WOO - Woolwich Station (East) |  | 2015-11-17 | 2015-11-13 08:42 | -4 | 2015-11-03 10:03 | Structural Engineering - Reinforcement | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | The ground secondary walls 1 and 2 (between gridlines Z5-Z6-B2-D2, Cxxx-OVE-S-DDA-CR147_1-71610 ) have been incorrectly detailed on the reinforcement drawings (Wall G on: Cxxx-__R-S-DWG-CR147-50008 C01 and Wall AC on: Cxxx-__R-S-DWG-CR147-50012 C01). Above these walls the thickness of the roof slab is 500mm (Cxxx-OVE-S-DDB-CR147_Z-72641 C01) and not 250mm as presented on RC drawings. As a result, the vertical reinforcement bars are too high to fit at the required wall height. Re-bars of wall no. 2 has already been installed, which poses extra work at height to cut them at the required level.
| 03SR - Stations (RfL) | Cxxx-NCR-000117 | NCR | Woolwich Station - West Box - Failed Integrity Test for Pile at Y2-C - Break-down of Pile |  | Crossrail | PDP | WOO - Woolwich Station (East) |  | 2015-11-17 | 2015-12-02 09:31 | 15 | 2015-11-03 12:11 | Civil - Civil Engineering General | 3500 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __ undertook integrity testing of existing piles beneath West Box ground slab which resulted in partial failure of the pile at intersection of gridlines Y2-C. Evidence of the failed test is to be provided by __. A small crack was detected and it was advised that the pile needed to be broken down to a depth of 500mm below the soffit of the beam. There is also no cover on the Southern side of the pile however further investigations showed this is a result of the pile cage not being vertical and cover improves gradually with depth (see photo attached, cover at 500mm below beam soffit approx 40mm). As cover requirements are 50mm, it was recommended to breakdown another 200m. __ to confirm that the new test is compliant The reduced height of the pile requires additional rework to enable tie into the slab, and is to be agreed with the designer
| 03SR - Stations (RfL) | Cxxx-NCR-000118 | NCR | Woolwich East Box - Cold Joint on Platform Wall 18 |  | Contr | __R | WOO - Woolwich Station (East) |  | 2015-11-25 | 2016-01-18 16:22 | 54 | 2015-11-11 17:25 | Structural Engineering - Concrete Member | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During construction of wall 18 on the East box platform as per the attached pour sequence drawing, the concrete did not completely fill all areas of the pour.
| 03SR - Stations (RfL) | Cxxx-NCR-000119 | NCR | woolwich west box-Aggregate Change during slab pour |  | Contr | __R | WOO - Woolwich Station (East) |  | 2015-11-26 | 2015-11-27 08:13 | 1 | 2015-11-12 10:41 | Structural Engineering - Structural Engineering - General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate resources | Completed |  | During the 230m3 pour of the north east ticket hall slab which commenced 06/11/15 and the south west slab 210m3 on the 18/11/15. The __ batching plant based at__ abruptly broke down and consequently could no longer supply us with 20mm G1-A mix. However they could supply us the remainder of our pour from thei__ branch, unfortunately this batching plant can only produce the G1-A mix but with 10mm aggregate Rather than 20mm.
| 03SR - Stations (RfL) | Cxxx-NCR-000120 | NCR | Woolwich East Box - Use of 10mm aggregate concrete mix in ground slab |  | Contr | __R | WOO - Woolwich Station (East) |  | 2015-11-25 | 2015-11-18 13:59 | -7 | 2015-11-11 17:53 | Civil - Civil Engineering General | 500 |  | Equipment Breakdown | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | On 9/9/15 while pouring ground slab 1a as per the attached sequence drawing, the __ batching plant based at Angestein broke down at approximately 1pm and consequently could no longer supply the 20mm aggregate G1-A concrete mix. __ could supply the remainder of the pour from their canning town branch, unfortunately this batching plant can only produce the 10mm aggregate G1-A mix. The last 14m3 of the pour was completed with the 10mm G1-A mix, after verbal approval from the Crossrail engineer.
| 03SR - Stations (RfL) | Cxxx-NCR-000121 | NCR | Plumstead - RMU Building excavated to wrong level |  | Contr | __R | WOO - Woolwich Station (East) |  | 2015-11-27 | 2016-01-28 08:53 | 62 | 2015-11-13 15:56 | Civil - Excavation | 2000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Training Deficiency - Insufficient practice or hands -on experience | Completed |  | The RMU building footprint was excavated to the wrong level and subsequently the CBR testing was carried out on the wrong level. As per drawing Cxxx-OVE-S-DDL-CR148_Z-86208, the RMU building footprint had to be excavated to level 102.365, but it was excavated to level 102.565, in a difference of 200mm.
| 03SR - Stations (RfL) | Cxxx-NCR-000122 | NCR | Woolwich East Box - Missing Reinforcement Detail for Roof Slab Connectino to Wall AU |  | Contr | __R | WOO - Woolwich Station (East) |  | 2015-12-18 | 2015-11-30 08:57 | -18 | 2015-11-17 13:47 | Structural Engineering - Reinforcement | 1500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In reference to the attached marked up drawings (Cxxx-__R-S-DWG-CR147-50090 Marked up, Cxxx-__R-S-DWG-CR147-50014 Marked up) the detail for the connection between wall AU and the roof slab has not been specified. No connection has therefore been installed at this location as per the attached photo.
| 03SR - Stations (RfL) | Cxxx-NCR-000123 | NCR | Woolwich East Box - Platform Walls 1, 2 & 4 out of positional tolerance |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-01-21 | 2016-02-19 15:15 | 29 | 2016-01-07 09:41 | Structural Engineering - Concrete Member | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As per the attached Sketches, Platform Walls 1, 2 & 4 have been constructed out of vertical tolerance.
| 03SR - Stations (RfL) | Cxxx-NCR-000124 | NCR | West Box - Non compliant repair to Platform Level Wall 12 |  | Contr | __R | WOO - Woolwich Station (East) |  | 2015-12-03 | 2015-12-09 16:03 | 6 | 2015-11-19 12:36 | Civil - Civil Engineering General | 1000 |  | Supervision/Management | Reject | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | An area of honey combing on West Box platform level wall 12 and shown on drawing Cxxx-OVE-S-DDA-CR147_4-61613 gridline D2/Y6-Y7 was repaired prior to CRL inspecting the broken back surface. When the repaired area was tapped with a hammer by Crossfail field engineers a section of the concrete patch came away and a quantity of water drained out. As a result Crossrail then instructed contractor to scabble back the entire darkened area shown in the attached picture and redo the repair. However the section which had broken away was repatched anyway.
| 03SR - Stations (RfL) | Cxxx-NCR-000126 | NCR | Plumstead: Terram installation at retaining wall |  | Contr | __R | WOO - Woolwich Station (East) |  | 2015-12-23 | 2015-12-16 18:46 | -7 | 2015-11-25 16:54 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the latest stages of terram installation for Retaining wall's sub-base specific area of approx. 1m by 0.25m was installed not as per requirements proposed in Cxxx-FCD-000145 (Retaining Wall Sub-base battering). Please note that Cxxx-FCD-000145 was not approved yet by PM when installation took place. This incorrect installation of Terram in that specific area (see attachments) led to non-comformance of Terram being exposed at the below blinding levels, which is a not as intended by neither Cxxx-FCD-000145 nor as per original design shown on section “A” of Cxxx-OVE-C-DDL-CR148_Z-10000 [C01]
| 03SR - Stations (RfL) | Cxxx-NCR-000127 | NCR | Woolwich West box - Ticket hall slab code 3 drawing |  | Contr | __M | WOO - Woolwich Station (East) |  | 2015-12-10 | 2015-12-10 11:42 | 0 | 2015-11-26 17:42 | Structural Engineering - Concrete Member | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Steel was fixed in accordance with Cxxx-__R-S-DWG-CR147-50065 C01 which was a Code 1 drawing. The rebar was inspected and approved on 19/10/15. Following several changes a Drawing 50065 was revised to C02 but was code 3, this drawing was also issued on 19/10/15. Subsequently, the rebar was inspected to a Code 3 drawing.
| 03SR - Stations (RfL) | Cxxx-NCR-000128 | NCR | Woolwich West box - Precast concrete prop finish |  | Contr | __M | WOO - Woolwich Station (East) |  | 2016-10-01 | 2016-09-07 08:50 | -24 | 2016-01-11 17:48 | Structural Engineering - Pre-cast | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 2no Type STE-202 precast concrete props were delivered to site with a non-compliant finish. From JE20.1213: A sealer system to provide a clear seal that prevents the concrete dusting, but imparts no sheen to the surface once applied and does not change the colour of the concrete. When the props were delivered, visible streaking was present on all surfaces of the props. This was noted during the installation inspection, however due to programme constraints the props were still cast into position
| 03SR - Stations (RfL) | Cxxx-NCR-000129 | NCR | Woolwich East Box - Minor Grout Loss to Ground Level Columns 8, 9, 10, 11, 12 & 13 |  | Contr | __R | WOO - Woolwich Station (East) |  | 2015-02-28 | 2015-12-10 16:19 | 285 | 2015-12-04 09:23 | Structural Engineering - Concrete Member | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In reference to KF11.1308 (Plain finishes), the Ground Level Columns 8, 9, 10, 11, 12 & 13 have minor grout loss less than 5mm in depth.
| 03SR - Stations (RfL) | Cxxx-NCR-000130 | NCR | Minor Honey combing and Grout loss was identified on East Box- Platform wall-15 South Face |  | Contr | __R | WOO - Woolwich Station (East) |  | 2015-12-22 | 2016-01-18 15:34 | 27 | 2015-12-08 10:34 | Civil - Structural Engineering | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the Post pour pre repair inspection of East box- Platform wall -15 south face, the following Non conformance was rectified 1. Minor Honeycombing at Bottom of the wall- South face of the wall 2. Minor Grout loss on West End Vertical joint- at mid height- South face of the wall See the attached photographs for more clarity.
| 03SR - Stations (RfL) | Cxxx-NCR-000131 | NCR | Woolwich WestBox insufficient starter bar cover wall 45 |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-02-05 | 2016-02-04 12:54 | -1 | 2016-01-04 12:57 | Structural Engineering - Reinforcement | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Based on the reinforcement inspection carried out on Wall 45 Ticket Hall level (GL A;Y10-W7). It Has been identified that there is insufficient concrete cover along wall 45, cover being between 30mm and 40mm rather than the required 50mm.
| 03SR - Stations (RfL) | Cxxx-NCR-000133 | NCR | Woolwich West Box Soffit discolouration |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-07-01 | 2016-05-17 10:27 | -45 | 2016-03-01 08:55 | Structural Engineering - Finishes | 6000 |  | Workmanship | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Lack of cleaning out of falsework pre-pour has produced rust stains upon the soffits of ticket hall slabs and b-1 slabs at the following gridlines; D3-E;Y6-W7 Ticket hall soffit A-B3;Y8-W7 Ticket hall soffit A-B;Y6-Y8 Ticket hall soffit B-B3;Y6-Y8 Ticket hall soffit D3-E;W1-Y5 B-1 soffit
| 03SR - Stations (RfL) | Cxxx-NCR-000134 | NCR | Woolwich Westbox Poor compaction of Wall's 8, 9 & 10 at Basement -2 Level |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-05-06 | 2016-05-03 10:41 | -3 | 2015-12-16 13:19 | Structural Engineering - Finishes | 4000 |  | Workmanship | Rework | 3 (3-6k) | Complete | Supervision - Insufficient supervision | Completed |  | Following on from our post pour inspections the west face of Walls 8, 9 and the east face of Wall 10 were observed to have honeycombing present aroud the toe of each wall which will require Type B2/3 repairs as per the concrete repair RAMS referenced.
| 03SR - Stations (RfL) | Cxxx-NCR-000135 | NCR | Woolwich West box RC precast stair landing dimension change |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-04-30 | 2016-04-01 12:40 | -29 | 2016-01-06 12:46 | Structural Engineering - Structural Engineering - General | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Due to a setting out error, The 700mm thick RC slab landing At ground level +109.350 (GL Y10-W7;B-B3 PLEASE SEE ATTACHED SKETCH) connecting into the precast stair case has been poured at the distance of 1130mm from wall 60 rather than the required 1170mm. Therefore the staircase will be short of the landing by 40mm.
| 03SR - Stations (RfL) | Cxxx-NCR-000136 | NCR | Woolwich West Box - wall 50 Ticket Hall level surface finish |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-05-13 | 2016-04-15 14:54 | -28 | 2016-01-06 16:14 | Structural Engineering - Finishes | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Honeycombing is present on both the east and west face of wall 50, running along (GL D3-D;Y9) It appears to go completely through the wall. This suggests that the concrete was not fully compacted.
| 03SR - Stations (RfL) | Cxxx-NCR-000137 | NCR | Woolwich West Box -Ticket hall- Incorporation of foreign material (timber) in the pour at the toe of wall 50 |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-05-13 | 2016-03-03 13:07 | -71 | 2016-01-06 17:08 | Structural Engineering - Finishes | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | It appears some timber is still present within the toe of the wall at wall 50 (GL D-D3;Y9). The shutter has not been cleaned out adequately prior to the concrete being poured.
| 03SR - Stations (RfL) | Cxxx-NCR-000139 | NCR | Reduced Cover to Copper Earthing Tape and Fixings |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-01-25 | 2016-02-26 13:42 | 32 | 2016-01-11 18:23 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Copper earthing tape and fixings was installed on top of the reinforcement cage and the concrete cover to the copper tape and its fixings did not meet the required 40mm top cover. Cover for structural reinforcement was achieved (40mm) but the copper tape fixings (U-clamp) protrude from the concrete surface. photos attached.
| 03SR - Stations (RfL) | Cxxx-NCR-000140 | NCR | Woolwich East Box - Missing trimmer bars from ground level wall P |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-01-27 | 2016-02-04 17:48 | 8 | 2016-01-13 11:15 | Structural Engineering - Reinforcement | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Ground level walls 11 & 12 have been poured with a startabox to allow for the construction of wall 13. There have been no box outs or similar to allow for installation of the timmer bars around the opeinings in wall 13 (Wall-P on drawing Cxxx-__R-S-DWG-CR147-50009.) Bar Marks 02, 35, 41, 52 as highlighted on drawing Cxxx-__R-S-DWG-CR147-50009 have not been installed.
| 03SR - Stations (RfL) | Cxxx-NCR-000141 | NCR | Plumstead-RMU internal trench starter bars placed in incorrect position |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-02-29 | 2016-03-09 17:22 | 9 | 2016-01-15 13:25 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | Concerning the RMU building adjacent to Plumstead Portal, the reinforcement starter bars for the trenches has been set out and install incorrectly, this is indicated within the attached sketches with a deviation from the proposed arrangement of 200 mm which narrows the trench (refer to sketch).
| 03SR - Stations (RfL) | Cxxx-NCR-000142 | NCR | West Box - Lack of colour conformity associated with the making good for Walls 1 & 2 Half Height on Basement -2 |  | Crossrail | PDP | WOO - Woolwich Station (East) |  | 2016-04-30 | 2016-03-03 16:43 | -58 | 2016-01-19 15:52 | Structural Engineering - Finishes | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following the Making Good of Walls 1 & 2 Half Height along Gridline Y7 and the closure of Cxxx-NCR-000036 a lack of colour conformity to surrounding RC Structures as a result from bag washing can be observed. The result is a darker , mottled finish which is non compliant with the KF11 Specification.
| 03SR - Stations (RfL) | Cxxx-NCR-000143 | NCR | Plumstead - Unplanned Construction Joint in LV6 Chamber Walls |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-02-05 | 2016-03-03 13:50 | 27 | 2016-01-22 09:00 | Civil - Civil Engineering General | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | There is a construction joint in LV6 walls due to the pour not being completed in one go. Unplanned Construction Joint illustrated in attached drawing.
| 03SR - Stations (RfL) | Cxxx-NCR-000144 | NCR | Section 3 of Retaining Wall Base |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-02-10 | 2016-03-16 16:39 | 35 | 2016-01-27 09:31 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Section 3 of retaining wall base, small area approximative 1.5 square meters in the south east corner has being poured lower then tolerance allows.
| 03SR - Stations (RfL) | Cxxx-NCR-000145 | NCR | Woolwich West Box - Non conforming concrete used for B-2 insitu stair pour |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-02-16 | 2016-03-02 12:52 | 15 | 2016-02-02 10:24 | Civil - Structural Engineering | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The concrete used to pour the lower half of cast insitu stairs and half landing in the North West corner of B-2 level slab was oldert than the specified two hours. Initially concrete delivered to site was within specification limits for time and within approved mix slump range of 140-240 however slump was at the upper end being 220mm and not suitable for pouring insitu stairs. As a result of the high slump reading the truck was sent away and a second delivery with a slump closer to 140mm requested. The second deliver arrived around an hour later, was slumped at 140mm and placed in the stairs. However the docket for the second delivery was not checked on arrival and on later inspection it appears rather than a second load being batched it was the same load that returned thus putting it over the allowable 2 hours from batching. (Copy of the delivery docket attached)
| 03SR - Stations (RfL) | Cxxx-NCR-000146 | NCR | Woolwich-Westbox-Non-compliant finish |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-09-21 | 2016-08-23 09:34 | -29 | 2016-02-02 14:11 | Structural Engineering - Finishes | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Stair 1 flight 1 and half landing whilst being poured on 30/1/16 has resulted in a poor surface finish, not meeting spec of a plain finish as per kf11.1308. This is Predominantly due to poor workmanship whilst also a poor supply of concrete is also to blame.
| 03SR - Stations (RfL) | Cxxx-NCR-000147 | NCR | Woolwich westbox - Unplanned stop-end |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-03-03 | 2016-03-09 16:30 | 6 | 2016-02-02 15:08 | Structural Engineering - Structural Engineering - General | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 30/1/16 Stair 1 flight 1 and adjoining half landing was poured (GL W1-Y4; B-C). However Unplanned stop end was installed to half landing, as concrete order was incorrectly cubed by __. Consequently half landing and stair 1 was short, therefore stop end was required to form a construction joint.
| 03SR - Stations (RfL) | Cxxx-NCR-000148 | NCR | Widening "L" Wall on RMU Building |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-02-25 | 2016-03-11 12:49 | 15 | 2016-02-11 15:29 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The starter bars for the L wall (512 mm long ) have been fixed 100 mm offset of the design drawing.
| 03SR - Stations (RfL) | Cxxx-NCR-000149 | NCR | Cxxx Woolwich West Box - Crack in Soffit (Y4/D2-E2) |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-09-01 | 2016-08-08 15:41 | -24 | 2016-03-16 12:17 | Structural Engineering - Finishes | 3000 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Ticket Hall level SW slab was poured 18/11/15, please see Cxxx-BR-S-DWG-CR147-50063 for slab drawing. Following on from our post pour checks shrinkage cracks have been discovered on the soffit (Y4/D2-E2)
| 03SR - Stations (RfL) | Cxxx-NCR-000150 | NCR | Non Compliance Wind-post Anchorage Resin was used at East and West box wind post Installation |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-03-18 | 2016-03-15 15:54 | -3 | 2016-02-19 16:05 | Structural Engineering - Bolted Connections | 2000 |  | Incorrect Installation | Reject | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | For the installation of Wind-posts at East and West box- Woolwich station (8 No. in East Box and 1 No. in West Box), Non-Compliance Anchorage resin (MULTI ANCHOR GREEN PLUS) was used instead of approved resin -__ Super-bond Resin. This Non-Compliance was rectified by Crossrail field engineers and the installation work was stopped. See the attached marked up drawing for Location of installed wind post.
| 03SR - Stations (RfL) | Cxxx-NCR-000151 | NCR | Non Compliance Wind-post was delivered and Installed at East and West box Basement perimeter walls |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-06-03 | 2016-05-03 11:52 | -31 | 2016-02-22 14:43 | Structural Engineering - Structural Engineering - General | 2000 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Further reference to Cxxx-NCR-000150, 20 number of perimeter walls windpost at East and west Box basement level (8 No. in East Box and 1 No. in West Box were installed already) base plate anchor bolts locations are 35mm away from the design position. See the attached Anchor Bolt location Sketch for more clarity. This non- compliance were rectified after installed 9 numbers of windposts.
| 03SR - Stations (RfL) | Cxxx-NCR-000152 | NCR | Block to Block shear ties were used without approved MCR at East Box basement walls. |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-03-21 | 2016-03-14 16:01 | -7 | 2016-03-07 11:09 | Architectural - Brickworks/Blockworks | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Block to Block Shear ties (c/w Debonding sleeves) were used without approved MCR. which was rectified after used the shear tie debonding sleeves at East Box- Basement level walls.
| 03SR - Stations (RfL) | Cxxx-NCR-000153 | NCR | Wind-posts were installed at East and West box Basement level without approved MCR |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-06-17 | 2016-06-02 11:40 | -15 | 2016-02-23 12:26 | Civil - Structural Engineering | 15000 |  | Documentation and Records | Reject | 2 (6-60k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Nine number of Wind-posts were installed on 16/02/2016 & 17/02/2016 at East and West Box basement level ( 8 No. at East box and 1 No. at West Box) without approved MCR accepted by CRL on eB on the date of installation. (Please find the attached sketch for installed wind-post location). The pre-production welds formed part of the MCR (Cxxx-__R-C-LRC-CR147-50114), unfortunately the Windpost Subcontractor did not provide us with the necessary visual inspection weld inspection sheets which should have been produced at the time of fabrication. These inspection sheets we should have received prior to any windposts being installed.
| 03SR - Stations (RfL) | Cxxx-NCR-000155 | NCR | WOO (WB) Gate By Exception for Basement-2 Blockwork, Windposts & Lintels |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2016-12-31 | 2016-06-22 09:59 | -192 | 2016-03-01 13:32 | Architectural - Brickworks/Blockworks | 0 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In order to accelerate blockwork to deliver SLD dates, the technical assurance of blockwork drawings in westbox basement -2 between W1 and W7 has been obtained through the Corssrail By Exception process (CRL1-XRL-O7-GPD-CR001-50023). The By Exception meeting has been held, and the risk of progressing has been recorded and signed off as acceptable by the PM on the Technical Assurance By Exception Gate Risk Assessment Form (Cxxx-__R-O7-GPD-CR147-50001), attached below. The issue of relevant documents/drawings was recorded within Cxxx-CCM-00650, which were then assessed by the relevant attendees at the risk review meeting. Approval of the By Exception process with regards to Blockwork walls at Basement -2 level has been noted in Cxxx-PMC-00813, and record of the relevant drawings being issued at 'C' status ready for construction are recorded in Cxxx-PMC-00830.
| 03SR - Stations (RfL) | Cxxx-NCR-000156 | NCR | Plumstead - RMU Foundation Brickwall out of tolerance |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-03-10 | 2016-03-11 12:44 | 1 | 2016-02-25 15:48 | Civil - Civil Engineering General | 3000 |  | Workmanship | Reject | 4 (0.5-3k) | Complete | External Phenomenon - Weather or ambient condition | Completed |  | RMU Foundation Brickwall running across grid line 3 in drawing Cxxx-OVE-S-DDL-CR148_2-86205 was found to be 15mm low in south edge, when taking the as-builts.
| 03SR - Stations (RfL) | Cxxx-NCR-000157 | NCR | Plumstead - Material used before MCR being coded 1 |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-03-10 | 2016-03-03 15:47 | -7 | 2016-02-25 16:57 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Bed Joint Reinforcement for Brickwork was used before MCR being coded 1 from Crossrail. Note that this material is a standard industry material.
| 03SR - Stations (RfL) | Cxxx-NCR-000158 | NCR | Woolwich Station - East Box: Precast Stairs 2_Wrong reinforcement installation and landing no. 2 thickness |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-06-03 | 2016-06-01 12:45 | -2 | 2016-02-29 14:57 | Structural Engineering - Structural Engineering - General | 2500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Post-delivery initial inspection of pre-cast Stairs 2 was completed by __ as per approved ITP Cxxx-__R-S-ITP-CR147-50028. Main issues identified against RC drawing: -Flight 1 B16 bars have been placed instead of B20 63 T1 Extra B25 protrude at B1 of top landing which are not identified on the drawings - Flight 2 Thickness of top landing is 275mm instead of 250mm (Cxxx-__R-RFI-02048) Extra B25 protrude at B1 of top landing which are not identified on the drawings B16 bars have been placed instead of B20 63 T1 Extra B16 are placed next to B20 69 of bottom landing. If this is B20 85 the size and position is wrong B25 has been used instead of B20 70 B1 - Flight 3 Extra B16 (200mm long) protrude next to B20 76 and B20 70 B1 of bottom landing. Extra B25 protrude at B1 of top landing which are not identified on the drawings. Please see attached report for further details.
| 03SR - Stations (RfL) | Cxxx-NCR-000160 | NCR | Dry Film thickness test for Mild steel wind-post paint was carried out by Non Calibrated Equipment at East Box Baemet level |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-03-25 | 2016-03-21 15:06 | -4 | 2016-02-29 18:35 | Structural Engineering - Finishes | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Inadequate/insufficient tooling. | Completed |  | Ten number of Mild steel wind post Dry Film thickness test for paint was carried out by Non Calibrated Equipment (Thickness Gauge). The technician from __ explained that the equipment is self calibrated and calibration is not necessary until get any damage to equipment ( Thickness Gauge). But this testing activity was refused by CRL representative on site.
| 03SR - Stations (RfL) | Cxxx-NCR-000161 | NCR | Woolwich West Box Incorrect Box out location in W__4 |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-03-31 | 2016-03-24 09:24 | -7 | 2016-03-03 12:11 | Structural Engineering - Structural Engineering - General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A Set out error has resulted in a box out being positioned in the wrong position. W__3 (GL A- B3;Y10) was due to intercept beam W__4 Directly along GL Y10, however it has been incorrectly placed (Please see sketch - Woolwich West Box Incorrect Box out location in W__4 sketch).
| 03SR - Stations (RfL) | Cxxx-NCR-000162 | NCR | No compressive strength testing has been undertaken on the site batched mortar forming the block work construction. |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2016-09-01 | 2016-08-01 14:42 | -31 | 2016-03-10 08:54 | Architectural - Brickworks/Blockworks | 5000 |  | Material | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | During a planned Crossrail surveillance undertaken on 09th March 2016 which looked at the records and installation associated to block work being constructed in the West Box, it was identified that no mortar compressive strength testing has been undertaken to date as batched from the CPI silos, with discussions still on-going with respect to sampling methods to be used (prisms/cubes) and associated UKAS accredited testing. Compressive strength results were tabled as undertaken by CPI; however the results referred to CPI’s production control testing prior to delivery of the dry mix, as such this NCR was raised as per the Crossrail surveillance procedure. Cxxx Woolwich Architectural Specification JZ21.1301 ‘Mortar Testing’ states the following; i) Testing of mortars shall be carried out in accordance with BS EN 1996: Parts 1-2, 2 and 3, BS EN 1052: Part 1, BS 4551 and BS EN 1015, or to equal standards acceptable to the Project Manager. ii) All testing shall be carried out by a UKAS accredited laboratory. v) Samples shall be taken at the point of mixing or use. viii) Half of the samples shall be tested at 7 days, the remainder at 28 days. The 28-day crushing strength of the cubes shall not be less than 3.6N/ mm² for the preliminary test and 2.5N/ mm² for the work test. Inspection and Test Plan Cxxx-__R-C-ITP-CR147-50030 (Rev 2) ‘Windposts and Blockwork’ states that ‘strength testing’ should be undertaken at a frequency of ‘each delivered batch of mortar’ for 7 and 28 day compressive strength as undertaken by a UKAS technician.
| 03SR - Stations (RfL) | Cxxx-NCR-000164 | NCR | WOO (EB) Gate By Exception for Basement Blockwork, Windposts & Lintels |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2016-12-31 | 2016-06-22 10:21 | -192 | 2016-03-10 16:16 | Architectural - Brickworks/Blockworks | 0 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In order to accelerate blockwork to deliver SLD dates, the technical assurance of blockwork drawings in eastbox basement for relevant rooms has been obtained through the Crossrail By Exception process (CRL1-XRL-O7-GPD-CR001-50023) in a meeting held on 16th February 2016. The By Exception meeting has been held, and the risk of progressing has been recorded and signed off as acceptable by the PM on the Technical Assurance By Exception Gate Risk Assessment Form (Cxxx-__R-O7-ZFM-CR147-50001), attached below. The issue of relevant documents/drawings was recorded within Cxxx-CCM-00684, which were then assessed by the relevant attendees at the risk review meeting. Approval of the By Exception process with regards to Blockwork walls at Basement level has been noted and record of the relevant drawings being issued at 'C' status ready for construction are recorded in Cxxx-PMC-00854.
| 03SR - Stations (RfL) | Cxxx-NCR-000165 | NCR | Woolwich Station_East Box_Missing kwikastrip for Stairs 2 landing at SSL +114.460 |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-09-02 | 2016-08-16 08:43 | -17 | 2016-03-11 16:46 | Structural Engineering - Reinforcement | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As shown on the attached snag report, 500mm long part of the kwikastrip for Stairs 2 landing at SSL +114.460 at east side of Roof wall Z was not installed, against the reinforcement drawing Cxxx-__R-S-DWG-CR147-50011 C02.
| 03SR - Stations (RfL) | Cxxx-NCR-000166 | NCR | Paint Thickness for Mildsteel windpost at Basement level were inadequate |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-05-31 | 2016-04-20 16:14 | -41 | 2016-03-14 16:39 | Structural Engineering - Surface Treatment | 10000 |  | Manufacturing Defect | Reject | 2 (6-60k) | Complete | Material/Preservation Problems - Insufficient quantity of material to do the job | Completed |  | __ carried out Dry Film Thickness assessment of the Sigma EP110 zinc phosphate primer, which was applied on Mild steel Windpost. The test was carried out on 10/03/2016 for 10 No. of windpost, which were installed at East Box Basement level. Sixty Dry film thickness reading were taken in accordance with BS EN ISO 2808. The overall mean average of dry film thickness resuted in 74.09 microns. the required dry film thickness is 125 Microns. Find the attached SPG report for further details.
| 03SR - Stations (RfL) | Cxxx-NCR-000167 | NCR | Woolwich Box - Wind Post Manufacturing ITP |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2016-06-03 | 2016-05-17 11:01 | -17 | 2016-03-17 09:02 | Structural Engineering - Steel Member | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | Per WI Vol 2B Part 20 clause 20.8, the Contractor and his subcontractors and suppliers of any tier engaged in supplying, manufacturing, construction, installation, commissioning and testing or any other service connected with the works, shall maintain ITPs appropriate for the services they provide that are accepted by the Supervisor. Wind post Manufacturing ITP has not been submitted and accepted by the Supervisor.
| 03SR - Stations (RfL) | Cxxx-NCR-000168 | NCR | Woolwich West Box: Precast Stair 5 Unit 5 Non-Compliant Landing Size |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-10-07 | 2016-10-07 14:32 | 0 | 2016-06-09 07:20 | Structural Engineering - Pre-cast | 1000 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Overall length of precast stair 5 unit 5 appears to be correct however landing depth outside of the line of the stairs has been poured 1000mm deep rather that 1100mm as shown on the drawings. Refer attached marked up drawing and photo.
| 03SR - Stations (RfL) | Cxxx-NCR-000169 | NCR | Woolwich West Box: Precast Stairs Damaged on Arrival |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-08-10 | 2016-09-22 12:55 | 43 | 2016-04-20 13:00 | Structural Engineering - Pre-cast | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Several of Stair 5 precast stair units have areas of damaged and chipped concrete of varying severity that are outside of the specification for precast concrete finishes.
| 03SR - Stations (RfL) | Cxxx-NCR-000170 | NCR | Woolwich West Box: Decolouration and Indent at Base of Precast Stair Risers |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-05-31 | 2016-05-03 10:17 | -28 | 2016-03-30 16:46 | Structural Engineering - Pre-cast | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | Across all of the stair units produced there is extensive staining and marking. At the base of each riser on the majority of stair units there is a black mark/indent which has been left presumably from the form work used to cast stairs. Sample photos attached.
| 03SR - Stations (RfL) | Cxxx-NCR-000171 | NCR | Woolwich West Box - Incorrect positioning of lifting anchors in PCC stairs |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-05-06 | 2016-05-03 15:29 | -3 | 2016-04-18 15:29 | Structural Engineering - Pre-cast | 3000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Pre-cast stair manufacturers have installed incorrect and out of position lifting eyes in all West Box PCC stair units. Please refer attached marked up drawings showing as built positions of lifting eyes. Drawings also detailsl 10 ton __ lifting anchor, instead a 5 ton spherical anchor by PCT which has been installed.
| 03SR - Stations (RfL) | Cxxx-NCR-000172 | NCR | Plumstead Portal & Sidings - Poor concrete finish for the mass concrete pour under the lintels |  | Contr | __R | PLU - Plumstead Portal (East) |  | 2016-05-31 | 2016-05-05 13:57 | -26 | 2016-03-30 13:22 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After striking the shutter for the duct entry point on the RMU, it was discovered that the concrete face had honeycomb. Note that the concrete was not structural but it was poured to fill the gap between the duct entries.
| 03SR - Stations (RfL) | Cxxx-NCR-000173 | NCR | Plumstead RMU mass infill for duct run |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2016-05-31 | 2016-05-03 16:30 | -28 | 2016-03-31 11:52 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Process based NCR: remedial works carried out to the mass concrete infill for the RMU duct run prior to giving CRL time to inspect the finish of the works. The PM can not determine the extent of remedial works that was required
| 03SR - Stations (RfL) | Cxxx-NCR-000175 | NCR | Woolwich West Box - Damaged secondary Walls GL W1-Y5;A-B2 - Gr Flr - NW Corner of Ticket Hall |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-06-10 | 2016-06-07 08:57 | -3 | 2016-04-07 14:42 | Structural Engineering - Finishes | 7000 |  | Workmanship | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Worker not trained for the work being performed | Completed |  | Within the Westbox Ticket Hall Level the top of the secondary walls have been left damaged following the striking of the soffit shutter for the mezz floor, (GL W1-Y5;A-B2 / Please see attached marked up drawing showing locations). 2 layers of ply was positioned in between the walls and the slab was cast on top due to the loading of the above pour, the secondary walls have a 50mm gap at the top left for fireproofing. This should have allowed the Subcontractor __ enough room to remove the ply, however the removal of the ply has left a number of walls spalled and damaged.
| 03SR - Stations (RfL) | Cxxx-NCR-000176 | NCR | Incomplete Windpost Fabrication Drawings |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2016-06-30 | 2016-05-05 12:43 | -56 | 2016-04-05 13:36 | Architectural - Brickworks/Blockworks | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The __ specification (Cxxx-OVE-S-DDA-CR147_Z-50101) revision C01 clearly states that all structural welds shall be part butt penetration ones. The mild steel windposts inspected during the surveillance (QS530-07 - 17/03/2016) were seen as fillet welds.
| 03SR - Stations (RfL) | Cxxx-NCR-000177 | NCR | Fabrication Drawings not listed in Contractors RIR |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2016-07-01 | 2016-06-29 09:40 | -2 | 2016-04-05 14:02 | Architectural - Brickworks/Blockworks | 500 |  | Documentation and Records | Reject | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | No fabrication drawings attached to Cxxx-FCD-000196 are listed in the Cxxx Register and Issue Record (RIR) or could be found on eB in the post visit surveillance review. Document Management and Acceptance of Field Documentation Procedure (CRL1-XRL-N2-GPD-CRG03-50001) revision 3.0 was issued to the contractor in PMI (Cxxx-PMI-00003) dated 14/04/2015, section 5.12 states It is noted that a construction contract may have inputs from several Contractor designers. Contractor will also develop detailing & fabrication drawings, as-built and redline drawings, temporary works drawings and other construction designs and drawings that need to be accepted by CRL. As such it is the responsibility of the Contractor to combine each of the individual designers and site drawings into a single contract specific Contractor’s RIR.
| 03SR - Stations (RfL) | Cxxx-NCR-000178 | NCR | Woolwich West Box - Honeycombing present NW corner walls |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-06-06 | 2016-05-03 15:04 | -34 | 2016-04-07 14:23 | Structural Engineering - Finishes | 4000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Ticket Hall level walls North West corner GL(W1-Y5;A-B2) generally have a lot of honey combing present due to poor compaction and workmanship, this is predominantly at the base of the walls. (Please see sketch of marked up locations with honeycombing present).
| 03SR - Stations (RfL) | Cxxx-NCR-000179 | NCR | Incomplete windpost MCR |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2016-06-03 | 2016-05-17 11:47 | -17 | 2016-04-05 14:16 | Architectural - Brickworks/Blockworks | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | The post surveillance visit review failed to find details for the painting in the MCR. According to the fabrication drawings for the mild steel windposts included in FCD Cxxx-FCD-000196, the majority of them have stainless steel channels welded to them, however, as for the above painting there are no Welding Procedures and Welder’s Qualification Test Certificates in respective of two different parent materials being welded together included in the MCR. The __ specification (Cxxx-OVE-S-DDA-CR147_Z-50101) revision C01 section 6.7 All structural steelwork (that is not concreted or stainless steel) including connections, should have a corrosion protection treatment comprising:- i). blast cleaning to grade Sa 2 1/2 conforming to BS EN ISO 8501-1. ii). Sigma EP110 epoxy zinc phosphate primer to dry film thickness -125 microns
| 03SR - Stations (RfL) | Cxxx-NCR-000180 | NCR | Windposts were procured without an approved MCR |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2016-06-03 | 2016-05-24 13:04 | -10 | 2016-04-05 14:25 | Architectural - Brickworks/Blockworks | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | With respect to the windpost MCR the Contractor failed to present the required records in the appropriate chronological order, seeking acceptance after the event. The post surveillance visit review found that the EBXX series of windposts were ordered, manufactured and delivered on 09/02/2016, 12/02/2016 and 22/02/2016 respectively, some 5 to 8 days prior to the MCR being approved (17/02/2016). Works Information Volume 2B part 13.3.6 states The Contractor shall utilise the template attached in Appendix 13J (MCR) for the purpose of recording material and product acceptances for the works and submit such records to the Project Manager for acceptance.
| 03SR - Stations (RfL) | Cxxx-NCR-000181 | NCR | Incomplete ITP to verify windposts met specified requirements and lack of inspection authority on delivery note |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2016-06-03 | 2016-06-03 08:15 | 0 | 2016-04-05 14:43 | Architectural - Brickworks/Blockworks | 15000 |  | Supervision/Management | Reject | 2 (6-60k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | The ITP details for inspection of the windposts when delivered to site was incomplete with respect to confirming that the purchase of the mild steel windposts met the specified product requirements. In addition, not all of the records identified the inspection authority which would negate verification of Works Information Volume 2 part 20.8 and ISO 9001:2008 clause 6.2.2, 7.4.3 and 8.2.3.
| 03SR - Stations (RfL) | Cxxx-NCR-000182 | NCR | Windpost fabrication drawing with incorrect detail |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2016-06-03 | 2016-05-17 12:03 | -17 | 2016-04-05 16:01 | Architectural - Brickworks/Blockworks | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | The mild steel windposts (EBXX series) installed on site had steel channels welded to them. Yet the drawings for that detail refers to the EG, WT and WR series windposts (drawing OW21294/SK2 in Cxxx-FCD-000196). There is therefore a discrepancy with the FCD which requires correction to maintain ISO 9001:2008 4.2.3.
| 03SR - Stations (RfL) | Cxxx-NCR-000183 | NCR | Woolwich East Box - Ground Level Wall 35 out of positional tolerance |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-06-03 | 2016-05-17 12:26 | -17 | 2016-05-04 14:45 | Structural Engineering - Concrete Member | 2500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | As per the attached sketch, ground level wall 35 has been constructed out of positional tolerance.
| 03SR - Stations (RfL) | Cxxx-NCR-000184 | NCR | WOO (WB) Gate By Exception for B-2 Room 907 Painting/Decoration |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2016-12-31 | 2016-06-22 10:57 | -192 | 2016-04-13 11:16 | Architectural - Finishes | 0 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In order to accelerate painting to deliver SLD dates, the technical assurance of painting in westbox basement-2 room 907 has been obtained through the Crossrail By Exception process (CRL1-XRL-O7-GPD-CR001-50023). The By Exception meeting has been held, and the risk of progressing has been recorded and signed off as acceptable by the PM on the Technical Assurance By Exception Gate Risk Assessment Form (Cxxx-__R-O7-GPD-CR147-50001), attached below. The acceptance of the procedure which was assessed by the relevant attendees at the risk review meeting is recorded in . Approval of the By Exception process has been noted in Cxxx-PMC-00894.
| 03SR - Stations (RfL) | Cxxx-NCR-000185 | NCR | WOO (EB) Decoration/Paint to RC and Blockwork Walls and RC Soffit on ground floor |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2016-12-31 | 2016-06-22 12:54 | -192 | 2016-04-13 16:37 | Architectural - Finishes | 0 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In order to accelerate painting to deliver SLD dates, the technical assurance of painting in westbox basement-2 room 907 has been obtained through the Crossrail By Exception process (CRL1-XRL-O7-GPD-CR001-50023). The By Exception meeting has been held, and the risk of progressing has been recorded and signed off as acceptable by the PM on the Technical Assurance By Exception Gate Risk Assessment Form (Cxxx-__R-O7-GPD-CR147-50001), attached below. The acceptance of the procedure which was assessed by the relevant attendees at the risk review meeting is recorded in Cxxx-CCM-00699. Approval of the By Exception process has been noted in Cxxx-PMC-00894.
| 03SR - Stations (RfL) | Cxxx-NCR-000186 | NCR | Woolwich West Box Incorrect Box out location in Wall 50 1st Floor |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-09-01 | 2016-06-22 11:16 | -71 | 2016-06-03 14:39 | Structural Engineering - Structural Engineering - General | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Due to a setting out error a box out has been positioned incorrectly within Wall 50 Second floor level (GL Y9;D3-E). Please see Attached photos. The box out was intended for Beam WBC4 running from east to west.
| 03SR - Stations (RfL) | Cxxx-NCR-000187 | NCR | Decorating/ Painting to RC and Blockwork Walls and RC Soffits, East Box Basement |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2016-12-31 | 2016-06-22 12:34 | -192 | 2016-04-18 12:59 | Architectural - Finishes | 0 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In order to accelerate painting to deliver SLD dates, the technical assurance of painting in eastbox basement (rooms 666, 701, 702, 731) has been obtained through the Crossrail By Exception process (CRL1-XRL-O7-GPD-CR001-50023). The By Exception meeting has been held, and the risk of progressing has been recorded and signed off as acceptable by the PM on the Technical Assurance By Exception Gate Risk Assessment Form (Cxxx-__R-O7-ZFM-CR147-50011), attached below. The acceptance of the procedure which was assessed by the relevant attendees at the risk review meeting is recorded in Cxxx-CCM-00702. Approval of the By Exception process has been noted in Cxxx-PMC-00897.
| 03SR - Stations (RfL) | Cxxx-NCR-000188 | NCR | West Box Paint/Decorating to RC and Blockwork Walls and RC Soffit on B-2 |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2016-12-31 | 2016-06-22 12:38 | -192 | 2016-04-18 13:18 | Architectural - Finishes | 0 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In order to accelerate painting to deliver SLD dates, the technical assurance of painting in westbox basement (room 731) has been obtained through the Crossrail By Exception process (CRL1-XRL-O7-GPD-CR001-50023). The By Exception meeting has been held, and the risk of progressing has been recorded and signed off as acceptable by the PM on the Technical Assurance By Exception Gate Risk Assessment Form (Cxxx-__R-O7-ZFM-CR147-50012), attached below. The acceptance of the procedure which was assessed by the relevant attendees at the risk review meeting is recorded in Cxxx-CCM-00703. Approval of the By Exception process has been noted in Cxxx-PMC-00896.
| 03SR - Stations (RfL) | Cxxx-NCR-000189 | NCR | West Box - Surface cracks present within Ground Slab - (GL Y1-W1;A-E) |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-07-21 | 2016-07-19 13:44 | -2 | 2016-04-22 16:04 | Structural Engineering - Concrete Member | 3500 |  | Workmanship | Repair | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | Cracks were discovered during a post pour inspection at the West Box within the Ground Slab between GL Y1-W1;A-E. __ (__ Site Engineer) and __ (CRL FE) undertook an inspection of the cracks some and it was found that the vast majority of them were over 0.3mm acceptable allowance.
| 03SR - Stations (RfL) | Cxxx-NCR-000190 | NCR | West Box - Wall 52 Damaged due to Efco Platforms Mezz level |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-08-31 | 2016-08-16 08:45 | -15 | 2016-04-25 07:24 | Structural Engineering - Concrete Member | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the installation of Efco platforms on Wall 52 at the Mezz Level through existing tie bolt holes concrete had subsequently been damaged exposing rebar in some instances and medium depth spalling in other cases. (It should be noted that the platforms were installed a long time after the concrete had reached its 28 day strength. They have been used for access only and no materials have been landed in it. This damage has purely been cause from the installation of the platforms).
| 03SR - Stations (RfL) | Cxxx-NCR-000191 | NCR | West Box - Wall 55 Mezz Level – Out of tolerance |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-06-17 | 2016-05-17 12:33 | -31 | 2016-05-04 12:12 | Structural Engineering - Concrete Member | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Asbuilt Survey produced by __ has revealed that Wall 55 at the Mezz Level appears to bow inwards from the outside of the structure and is out of tolerance by 15-21mm across a 2 metre section in width. The exact location of the defect is as follows Elevation = +116.138 Between these 2 points (GL: A-B3;W7) N 94175.134 E 33445.098 N 94173.013 E 33438.263 Please see attached asbuilt table, it
| 03SR - Stations (RfL) | Cxxx-NCR-000192 | NCR | West Box - Wall 8 – Ticket Hall Level - Honeycombing to concrete wall |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-06-08 | 2016-05-17 12:56 | -22 | 2016-04-27 08:30 | Structural Engineering - Concrete Member | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | B3 / C1 defect - Honeycombing has been observed along toe of wall and within the center of the wall also.
| 03SR - Stations (RfL) | Cxxx-NCR-000193 | NCR | Painting Works Platform Level Core Rooms East and West Box [selected rooms] |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2016-12-31 | 2016-06-22 12:43 | -192 | 2016-04-26 16:18 | Architectural - Finishes | 0 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In order to accelerate painting to deliver SLD dates, the technical assurance of painting in platform level rooms westbox (rooms 405, 666, 670, 671, 675, 732, 733) and eastbox (rooms 732, 733, 787) has been obtained through the Crossrail By Exception process (CRL1-XRL-O7-GPD-CR001-50023). The By Exception meeting has been held, and the risk of progressing has been recorded and signed off as acceptable by the PM on the Technical Assurance By Exception Gate Risk Assessment Form (Cxxx-__R-O7-ZFM-CR147-50004), attached below. The acceptance of the procedure which was assessed by the relevant attendees at the risk review meeting is recorded in Cxxx-CCM-00708. Approval of the By Exception process has been noted in Cxxx-PMC-00896.
| 03SR - Stations (RfL) | Cxxx-NCR-000194 | NCR | North Woolwich Portal - Beams 19 & 20 - Level 1 - Out of tolerance |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-05-31 | 2018-05-21 08:06 | -10 | 2016-04-27 12:46 | Structural Engineering - Concrete Member | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following a post pour as-built survey of Beams 19 & 20 at Level 1 for the MEP Building it was found they were out of tolerance. The beams deviate from their vertical design position by +49mm to +54mm.
| 03SR - Stations (RfL) | Cxxx-NCR-000195 | NCR | West Box - Soffit Discolouration to Maintenance Slab |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-07-31 | 2016-08-08 15:01 | 8 | 2016-05-12 14:42 | Structural Engineering - Finishes | 2000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | A lack of adequate cleaning out of falsework pre-pour has produced rust stains upon the soffit of the Maintenance Slab within the West Box.
| 03SR - Stations (RfL) | Cxxx-NCR-000196 | NCR | West Box - Stair 5 Flight 4 Top Landing cast in-situ to the incorrect dimensions |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-08-10 | 2016-05-24 13:52 | -78 | 2016-05-12 14:11 | Structural Engineering - Concrete Member | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Drawing Cxxx-__R-S-DWG-CR147-50169 C03, section B, shows the face of the landing at +112.395m landing to be 2990mm from GL B. The face of the landing has instead been constructed 2860mm from GL B. This has reduced the opening for the PCC stairs by 130mm and the stairs do not fit in the current condition.
| 03SR - Stations (RfL) | Cxxx-NCR-000197 | NCR | North Woolwich Portal - Wall 6 - Tie Bolt Holes in Cover Zone |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-08-14 | 2016-06-21 16:33 | -54 | 2016-05-16 16:12 | Structural Engineering - Concrete Member | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | The attached photograph shows the position of tie bolt holes in Wall 6. 2No. Tie bolts were installed incorrectly in the cover zone of the structural opening.
| 03SR - Stations (RfL) | Cxxx-NCR-000198 | NCR | Woolwich East Box - Ground Wall Level Wall 12 Out of Positional Tolerance |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-08-31 | 2016-10-07 09:19 | 37 | 2016-06-02 08:00 | Structural Engineering - Concrete Member | 2500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | As per the attached sketch, ground level wall 12 has been constructed out of positional tolerance.
| 03SR - Stations (RfL) | Cxxx-NCR-000199 | NCR | West Box - Wall 52 - Unplanned CJ within concrete wall pour |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-09-23 | 2016-08-16 09:06 | -38 | 2016-05-26 07:31 | Structural Engineering - Concrete Member | 3000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | The wall was poured 1.2m low without a proper construction joint due to the concrete pour being abandon as the concrete had become to stiff to compact due to the time taken to lift the skip into position by the crane for Wall 52 located at D3-E W7 Level 2.
| 03SR - Stations (RfL) | Cxxx-NCR-000200 | NCR | WOO (EB) Gate by Exception for Rooms 901, 905 & 73 Gr Floor - Screeding Works |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-12-25 | 2016-06-24 10:36 | -184 | 2016-06-08 13:18 | Architectural - Flooring | 0 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In order to accelerate painting to deliver SLD dates, the technical assurance of Rooms 901, 905 & 73 Gr Floor - Screeding Works has been obtained through the Crossrail By Exception process (CRL1-XRL-O7-GPD-CR001-50023). The By Exception meeting has been held, and the risk of progressing has been recorded and signed off as acceptable by the PM on the Technical Assurance By Exception Gate Risk Assessment Form (Cxxx-__R-O7ZFM-CR147-50016), attached below. The acceptance of the procedure which was assessed by the relevant attendees at the risk review meeting is recorded in Cxxx-CCM-00780 . Approval of the By Exception process will be noted in a PMC, reference to be confirmed.
| 03SR - Stations (RfL) | Cxxx-NCR-000201 | NCR | WOO Gate by Exception for BOH Areas East & West Boxes - Screeding Works |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-12-25 | 2016-06-24 10:40 | -184 | 2016-06-08 13:24 | Architectural - Flooring | 0 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In order to accelerate painting to deliver SLD dates, the technical assurance of BOH on the East & west Boxes - Screeding Works has been obtained through the Crossrail By Exception process (CRL1-XRL-O7-GPD-CR001-50023). The By Exception meeting has been held, and the risk of progressing has been recorded and signed off as acceptable by the PM on the Technical Assurance By Exception Gate Risk Assessment Form (Cxxx-__R-O7-ZFM-CR147_WS163-50001), attached below. The acceptance of the procedure which was assessed by the relevant attendees at the risk review meeting is recorded in Cxxx-CCM-00781 . Approval of the By Exception process will be noted in a PMC, reference to be confirmed.
| 03SR - Stations (RfL) | Cxxx-NCR-000202 | NCR | West Box - Wall 52 - Incomplete preparation before repouring unplanned CJ within concrete wall pour |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-10-02 | 2016-08-23 09:38 | -40 | 2016-06-04 15:32 | Structural Engineering - Concrete Member | 2500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Following being poured 1.2m low without a proper construction joint due to the concrete pour being abandon for Wall 52 located at D3-E W7 Level 2 which has been covered by Cxxx-NCR-000199 already it was observed by the CRL FE that preparation of the CJ was unsatisfactory. Not all preparation for cleaning the shutters and removing loose concrete had been achieved in one area of the pour before the pour commenced though it should be noted that much of the preparation for other areas had been progressively inspected throughout the day by CRL.
| 03SR - Stations (RfL) | Cxxx-NCR-000204 | NCR | Plumstead Portal - Substation floor slab levels |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-10-01 | 2017-09-25 14:04 | -6 | 2016-06-21 08:01 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Substation slab was poured outside of tolerances. Drawing Cxxx-OVE-S-DDA-CR148_1-86132 [C02] states in Note 5 "all concrete works to be finished smooth and level within +/- 2mm, where, as shown in the attached as-built survey the tolerances were from -9mm to +7mm.
| 03SR - Stations (RfL) | Cxxx-NCR-000205 | NCR | Gate by Exception for CMS Systems within Rooms WB: 666 781 907 & EB: 666 731 732 |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-01-09 | 2016-09-08 15:26 | -123 | 2016-06-23 15:18 | Electrical - Cable Management | 0 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In order to accelerate the installation of the CMS Systems programme, the technical assurance of the CMS Systems on the East & West Boxes - within Rooms 666 781 907 (WB) & 666 731 732 (EB) has been obtained through the Crossrail By Exception process (CRL1-XRL-O7-GPD-CR001-50023). The By Exception meeting has been held, and the risk of progressing has been recorded and signed off as acceptable by the PM on the Technical Assurance By Exception Gate Risk Assessment Form Cxxx-__R-E-ZFM-CR147-50001. The acceptance of the procedure which was assessed by the relevant attendees at the risk review meeting is recorded in Cxxx-CCM-00721 and noted within Cxxx-PMC-01006.
| 03SR - Stations (RfL) | Cxxx-NCR-000206 | NCR | Gate by Exception for West Box Basement -1 Blockwork within Room 764 |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-01-09 | 2016-07-14 13:17 | -179 | 2016-06-23 15:33 | Architectural - Brickworks/Blockworks | 0 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In order to accelerate the Blockwork programme, the technical assurance of West Box B-1 Blockwork within Room 764 - has been obtained through the Crossrail By Exception process (CRL1-XRL-O7-GPD-CR001-50023). The By Exception meeting has been held, and the risk of progressing has been recorded and signed off as acceptable by the PM on the Technical Assurance By Exception Gate Risk Assessment Form Cxxx-__R-O7-ZFM-CR147-50008. The acceptance of the procedure which was assessed by the relevant attendees at the risk review meeting is recorded in Cxxx-CCM-00700 (& -749 for rev 2) and noted within Cxxx-PMC-00993
| 03SR - Stations (RfL) | Cxxx-NCR-000207 | NCR | Gate by Exception for Blockwork within the East Box on the Ground Floor Rooms 661 761 776 781 782 (E1 - Z5) |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-01-09 | 2016-07-14 13:18 | -179 | 2016-06-23 15:45 | Architectural - Brickworks/Blockworks | 0 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In order to accelerate the installation of Blockwork, the technical assurance of East Box Blockwork at Ground Floor Level for Rooms 661 761 776 781 782 (E1 - Z5) has been obtained through the Crossrail By Exception process (CRL1-XRL-O7-GPD-CR001-50023). The By Exception meeting has been held, and the risk of progressing has been recorded and signed off as acceptable by the PM on the Technical Assurance By Exception Gate Risk Assessment Form Cxxx-__R-O7-ZFM-CR147-50009. The acceptance of the procedure which was assessed by the relevant attendees at the risk review meeting is recorded in Yes, Cxxx-CCM-00701 (& -750 for rev 2) and noted within Cxxx-PMC-00994
| 03SR - Stations (RfL) | Cxxx-NCR-000208 | NCR | Plumstead Portal - Poor finishing on top of chamber C7 |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-09-22 | 2016-10-03 14:29 | 11 | 2016-06-24 14:14 | Civil - Civil Engineering General | 2500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | Finish at the top of C7 chamber was non-compliant. Concrete finish for buried surfaces should be F1 according to Specification for Highway Works Series 1700.
| 03SR - Stations (RfL) | Cxxx-NCR-000209 | NCR | East Box FOSC 1 & FOSC 2 - __ found to be insufficient in depth on the CMS fibre remake loop. |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-09-30 | 2016-08-04 11:05 | -57 | 2016-06-30 08:03 | Electrical - Cable Management | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The __ applied to the CMS fibre remake loop was found to be insufficient and not of the required standard as depicted within the specification, this was on the CMS and __t within the Rooms FOSC1 & 2 east
| 03SR - Stations (RfL) | Cxxx-NCR-000210 | NCR | Woolwich East Box - Precast Stairs 2 manufactured with incorrect reinforcement |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-07-22 | 2016-07-14 08:16 | -8 | 2016-07-05 16:53 | Structural Engineering - Concrete Member | 500 |  | Workmanship | Reject | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | The flights for the Precast Stairs 2 arrived with incorrect starter bars, this was raised to __ as detailed in Cxxx-__R-RFI-02127. Upon reciept of __'s advice Cxxx undertook an __ of the stairs to ascertain whether the reinforccement had been installed correctly. This __ highlighted further issues with a lap lenth in flight 2 as shown in the validation table attached.
| 03SR - Stations (RfL) | Cxxx-NCR-000211 | NCR | North Woolwich Portal – Defective placement of concrete to GF Column GL:C/1a |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-01-03 | 2016-12-09 11:20 | -25 | 2016-09-05 13:51 | Civil - Structural Engineering | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Defects in concrete surface approx. 10 - 45mm deep on beam base to column connection GL: C/1 See Attached Photograph
| 03SR - Stations (RfL) | Cxxx-NCR-000212 | NCR | Woolwich West Box – Honeycombing on Wall 75 Second Floor Level |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-11-12 | 2016-08-23 09:42 | -81 | 2016-07-15 11:20 | Structural Engineering - Concrete Member | 1000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Following the striking of the shutters for Wall 75 Second Floor Level within the West Box 7 areas of poor compaction was identified with defects ranging from B2-C2 as per the concrete repair procedure referenced.
| 03SR - Stations (RfL) | Cxxx-NCR-000213 | NCR | Woolwich Station Screed – Incorrect product type |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-12-04 | 2016-09-26 09:13 | -69 | 2016-09-05 15:04 | Architectural - Flooring | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | As per the Cxxx Architectural Specification Cxxx-__R-A-RSP-CR147-50001 Rev 4.0, there are two types of screed to be used in Woolwich East and West boxes. Isopol SBR as a wearing screed (Clause JM10.1206) and K-Screed in areas to be tiled/rubber floored/waterproofed (Clause JM10.1205). Rooms SMK [47], WC [418], SLR [316] (East Box), SWP III [418], TEP [48] (West Box) all contain Rubber flooring or tiles, as denoted by the levels given on the drawings Cxxx-__R-A-DDD-CR147_WS163-Z-08001 and Cxxx-__R-A-DDD-CR147_WS163-Z-08002. These rooms should have K-Screed installed however they have been screeded in Isopol SBR. They have been screeded to the correct level to receive the correct floor finish as per the above drawings. In addition, drawing Cxxx-__R-A-DDD-CR147_WS163_Z-13003 C01 shows a double sided movement joint between the different screed and floor finish types. No gap has been allowed for this filler to go between the different screeds.
| 03SR - Stations (RfL) | Cxxx-NCR-000214 | NCR | West Box - Lost Permit to Strike - Level 1 Wall 55 |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-11-12 | 2016-07-21 11:54 | -114 | 2016-07-15 09:37 | Structural Engineering - Concrete Member | 0 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Following a Surveillance of the West FRC Concrete QA with CRL's Leigh Holland it was found that there was a Lost Permit to Strike for Wall 55 on Level 1.
| 03SR - Stations (RfL) | Cxxx-NCR-000216 | NCR | Gate by Exception for Public Health Pipework Woolwich East Box - Platform/Basement/Ground |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-03-23 | 2017-03-23 17:22 | 0 | 2016-07-27 12:53 | Mechanical - Public Health Engineering | 0 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In order to accelerate the installation of Public Health pipework, the technical assurance of East Box pipework at Platform, Basement and Ground levels has be obtained through the CRL by Exception process (CRL1-XRL-O7-GPD-CR001-50023). The by Exception meeting has been held and the risk of progressing has been recorded and signed off as acceptable by the PM on the technical assurance by Exception gate risk assessment form Cxxx-__R-O7-ZFM-CR147-50021.
| 03SR - Stations (RfL) | Cxxx-NCR-000217 | NCR | Gate by Exception for Woolwich East Box Ductwrk SLD Room HVTRI&II, FCR, MCC, SSR WB, CER,RR, __R & (FOSC West & East) |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-03-23 | 2017-03-23 17:03 | 0 | 2016-07-27 13:32 | Mechanical - Heating Ventilation & Air Conditioning | 0 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In order to accelerate the installation of Ventilation Ductwork SLD rooms as above, the technical assurance of East Box ductwork and equipment at Basement and Ground levels has be obtained through the CRL by Exception process (CRL1-XRL-O7-GPD-CR001-50023). The by Exception meeting has been held and the risk of progressing has been recorded and signed off as acceptable by the PM on the technical assurance by Exception gate risk assessment form Cxxx-__R-O7-ZFM-CR147-50022.
| 03SR - Stations (RfL) | Cxxx-NCR-000218 | NCR | Installation of temporary fire main North Woolwich portal |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2016-09-23 | 2016-10-10 09:21 | 17 | 2016-07-29 13:30 | Fire - Suppression | 20000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | The contractor has installed a temporary fire main at platform level in the North Woolwich portal. It has come to the project managers attention that there is no requirement for temporary fire suppression at the North Woolwich portal listed in the works information.
| 03SR - Stations (RfL) | Cxxx-NCR-000220 | NCR | Resin applied to wearing screed with no abrasion testing. Screed ITP omitted specified testing (abrasion and roughness). Testing frequency unclear. |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2016-08-30 | 2016-08-31 10:24 | 1 | 2016-08-02 14:06 | Architectural - Flooring | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | A planned Crossrail Quality surveillance was undertaken on 19th July 2016 which looked at Screed Installation and associated testing. The Architectural Specification (Cxxx-__R-A-RSP-CR147-50001) was reviewed against the works and controlling documents. JM10.1206 ‘Wearing Screed’ defines a requirement for ‘Abrasion Resistance’ testing to achieve AR2 to BS 8204: Part 2. JM10.2200 ‘Testing’, in particular JM10.2203 ‘Slip Resistance Testing’ requires ‘Roughness Testing’ using a surface roughness meter. On checking the ITP (Cxxx-__R-C-ITP-CR147-50003), these tests had not been included as an activity. Additionally, in a number of rooms (specifics not provided) resin had already been applied to the wearing screed with no Abrasion Resistance testing completed, as such AR2 compliance has yet to be verified. Furthermore, it was also unclear during the visit how frequent these tests should be undertaken; i.e. testing every room etc. At the time of the visit no Roughness Testing had been completed. Some rooms have already been handed over to follow on Contractors. This NCR was raised resulting from the surveillance due to the omissions and non-testing.
| 03SR - Stations (RfL) | Cxxx-NCR-000221 | NCR | WOO - Wi Mortar failed compressive strengths at 28 days for Wi Columns |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-01-09 | 2016-09-05 14:37 | -126 | 2016-08-12 14:38 | Structural Engineering - Structural Engineering - General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 9 No. of cube test results for 28 day compressive strengths for Wi Mortar which have failed to meet the specification of 40N as detailed within Cxxx-__R-C-ITP-CR147-50033. Failed cube samples include with locations identified on the attached drawings CZ-0510 CZ-0511 CZ-0512 CZ-0513 CZ-0514 CZ-0517 CZ-0518 CZ-0538 CZ-0539 __ Director, __ was contacted once __ had completed our own investigation. With the evidence we provided him he consulted with__ who is the Director of __ (formally__) who produced an independant report on the structural integrity of the Wi Columns which had produced cube strength results lower than the requirement at 28 days. Please find attached - Field cube sample test certs for each sample - A summary of Wi System Cube Test Results - Location plan marked up for failed cube test results - __'s independent report
| 03SR - Stations (RfL) | Cxxx-NCR-000222 | NCR | (North Woolwich Portal) - Incorrect Startabox Centres |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-01-12 | 2016-08-24 15:12 | -141 | 2016-08-15 14:41 | Structural Engineering - Reinforcement | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | __ have installed the startabox continuity system joining the roof slab to walls 6 & 7, approved in Cxxx-__-RFI-00122, with incorrect pull out bar centers. The roof slab specifies 150mm centers however the startabox was installed with 200mm centers. __ then proceeded to drill and fix additional starters bars, as approved in Cxxx-__-RFI-00144. __ operatives installed additional bars in wall 6 at 100mm centers without verification of embedment depth from the client. __ Project Manger Vincent O'Brien inspected works and following survey by __ engineer confirmed that the embedment depths were sufficient to continue works. Attached find embedment survey and __ 200-HY 200 data sheet. Data Sheet specifies 90mm embedment depth for 10mm bar.
| 03SR - Stations (RfL) | Cxxx-NCR-000223 | NCR | North Woolwich Portal - No on-site slump test on final load of concrete for Flood Wall 5 & 6 |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-12-17 | 2016-08-23 11:33 | -116 | 2016-08-19 10:32 | Structural Engineering - Testing | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The final load of C32/40 mix 2 concrete (Delivery No. 1977038876 - 1m3) for the Flood Wall 5 & 6 pour was not correctly slump tested on site.
| 03SR - Stations (RfL) | Cxxx-NCR-000224 | NCR | North Woolwich: Sump Wall Riser Chamfers |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-02-02 | 2016-09-26 09:58 | -129 | 2016-09-05 14:15 | Structural Engineering - Concrete Member | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The MEP Building Walls 1, 2, 3 & 4 have been constructed without chamfered edges leaving an exposed edge of 90 degrees. See Attached Photographs
| 03SR - Stations (RfL) | Cxxx-NCR-000225 | NCR | NWP - Flood Walls 3 & 4 Kickers - Missing Reinforcement |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-12-14 | 2016-08-23 09:50 | -113 | 2016-08-16 10:55 | Structural Engineering - Reinforcement | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The bottom lacer of Flood Wall 3 had been omitted from the kicker. Initial ITP checks from __ did not identify the bottom lacer of Wall 3 and the bottom link of Wall 4 had not been installed. The omission was only realised during the pour at which point the pour was promptly stopped. The link was then installed in the Wall 4 kicker however the Wall 3 kicker had been poured.
| 03SR - Stations (RfL) | Cxxx-NCR-000227 | NCR | Incorrect level of concrete pour - lower mass infill escalator void |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-11-30 | 2016-10-17 14:39 | -44 | 2016-09-01 08:40 | Structural Engineering - Structural Engineering - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The mass concrete infill at the bottom of the escalator void was to be poured as per the details given in Cxxx-FCD-000265, in particular Cxxx-OVE-Cxxx-SITE-SK-038-4. (1) Due to the finish level of the pour (the lower section of the mass infill) being 1 metre below platform level it was difficult to judge the correct amount of concrete to be pumped. As a result, the finish level was up to +25mm in localised areas. (2) upon completion of the pour, the 8 metre stationary line did not blow out, meaning the 4no. concrete operatives were required to manually clean each section of pipe. By the time this was completed (21.00hrs) the concrete in the mass infill had gone off and the required finish was not achieved.
| 03SR - Stations (RfL) | Cxxx-NCR-000228 | NCR | Out of tolerance abrasion test results to Wearing Screed |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-01-16 | 2016-11-07 14:48 | -70 | 2016-10-18 15:09 | Architectural - Flooring | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Cxxx-__R-A-RSP-CR147-50001 Rev 4.0, Section JM10.1206 (k) requires Abrasion Testing to BS8204-2, wearing screed to be evaluated to obtain the Abrasion Resistance. The Standard defines wearing screed as 'screed that serves as flooring', therefore this test should be carried out on a screed with no resin finish applied. The screed sub-contractor had not heard of this test being carried out on screed to receive a resin finish, however due to time constraints and the available areas of screed remaining a UKAS certified testing company was employed to carry out the test on exposed areas of Isopol SBR screed. The 3no. tests carried out resulted in a failure after a very short amount of time, the total test duration is 2850 ±10 revolutions of the abrasion head which approximates to 15 minutes & 50 seconds running time however the maximum time this test was carried out was around 3 minutes/600 revolutions. The testers expressing the opinion that the type of screed being used on the project was not what they would usually test (concrete or hard top industrial warehouse floor). The friction was causing the grains to detach and create a higher wear of the floor. This can be seen in the attached images, the test report is also attached. For comparison, the machine was set up on a concrete slab to demonstrate the correct procedure and outcome (Test 4 in the attached Test Report).
| 03SR - Stations (RfL) | Cxxx-NCR-000229 | NCR | Gate by Exception - Woolwich Box East and West HV Transformer and Switch Rooms Ductwork |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-03-31 | 2018-01-11 15:44 | -79 | 2016-08-30 16:28 | Electrical - General | 0 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In order to accelerate the installation of works as stated above, the technical assurance of East Box electrical works in HV and switch Rooms has be obtained through the CRL by Exception process (CRL1-XRL-O7-GPD-CR001-50023 Rev 2.0). The by Exception meeting has been held and the risk of progressing has been recorded and signed off as acceptable by the PM on the technical assurance by Exception gate risk assessment form Cxxx-__R-O7-ZFM-CR147-50023. CRL have been notified by via Cxxx-CCM-00993 that all we __ have complied with the process and have all the necessary technical assurances in place to proceed with works. The signed document is attached to this NCR
| 03SR - Stations (RfL) | Cxxx-NCR-000230 | NCR | Gate by Exception - Woolwich Box Under Croft and FOSC to CER CMS Routes |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-03-23 | 2017-03-24 13:49 | 1 | 2016-08-30 16:36 | Electrical - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | In order to accelerate the installation of works as stated above, the technical assurance of East Box electrical works in FOSC & CER CMS Routes has be obtained through the CRL by Exception process (Cxxx-__R-O7-ZFM-CR147-50023). The by Exception meeting has been held and the risk of progressing has been recorded and signed off as acceptable by the PM on the technical assurance by Exception gate risk assessment form Cxxx-__R-O7-ZFM-CR147-50026. The acceptance of the procedure which was assessed by the relevant attendees at the risk review meeting is recorded in Cxxx-CCM-00857. Approval of the By Exception process will be noted in a PMC, reference to be confirmed.
| 03SR - Stations (RfL) | Cxxx-NCR-000231 | NCR | CMS - Cable Tray |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-04-12 | 2017-01-19 08:48 | -83 | 2016-08-31 09:17 | Electrical - Cable Management | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | Material installed not in line with description on ITP or has MCR approval
| 03SR - Stations (RfL) | Cxxx-NCR-000232 | NCR | WOO Gate by Exception for Platform Areas East & West Boxes - Builders Work Holes |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-01-03 | 2016-09-28 09:08 | -97 | 2016-09-05 15:19 | Architectural - Brickworks/Blockworks | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In order to accelerate painting to deliver SLD dates, the technical assurance of East Box & West Box Platforms Builders Work Holes has been obtained through the Crossrail By Exception process (CRL1-XRL-O7-GPD-CR001-50023). The By Exception meeting has been held, and the risk of progressing has been recorded and signed off as acceptable by the PM on the Technical Assurance By Exception Gate Risk Assessment Form Cxxx-__R-O7-ZFM-CR147-50028 attached below. The acceptance of the procedure which was assessed by the relevant attendees at the risk review meeting is recorded in Cxxx-CCM-00861. Approval of the By Exception process will be noted in a PMC, reference to be confirmed.
| 03SR - Stations (RfL) | Cxxx-NCR-000233 | NCR | Gate by Exception - North Woolwich Portal AC Package |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-03-23 | 2017-03-23 17:10 | 0 | 2016-09-05 14:06 | Mechanical - Piping | 0 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In order to accelerate the installation of AC works at North Woolwich, the technical assurance of North Woolwich Portal AC package of works has be obtained through the CRL by Exception process (CRL1-XRL-O7-GPD-CR001-50023). The by Exception meeting has been held and the risk of progressing has been recorded and signed off as acceptable by the PM on the technical assurance by Exception gate risk assessment form Cxxx-__R-O7-ZFM-CR146-50001.
| 03SR - Stations (RfL) | Cxxx-NCR-000234 | NCR | Woolwich Station - Incorrect installation of Escalator Track Bracket |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-12-11 | 2016-10-19 14:34 | -53 | 2016-09-12 09:03 | Mechanical - Escalators | 3000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | During the Phase I factory inspect carried out on E2 between the 09/05/16 to 13/05/16. It was noted that the track brackets design had been changed for all three Cxxx Woolwich units. The new design has a bigger cut out for the A track which has resulted in larger shims having to be fitted, although the amount of shims used is in line with the specification. Confirmation that the new bracket design has been communicated to LUL/CRL and approval has been given for this redesign is required before this can be accepted. (see Orton FAT report ORT-WOO-02 for more details)
| 03SR - Stations (RfL) | Cxxx-NCR-000235 | NCR | North Woolwich: Installation of roof screed without an assured design or 'Exception by Gate' process undertaken. |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-01-04 | 2016-09-26 09:36 | -100 | 2016-09-06 16:18 | Architectural - Roofing & Exterior Treatment | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | A decison by the North Woolwich Portal Site Team was taken to proceed at risk and undertake the installation of roof screed without an assured design or 'Exception by Gate' acceptance in place. This was a decison which was undertaken locally within the project.
| 03SR - Stations (RfL) | Cxxx-NCR-000237 | NCR | Refrigeration Containment Tray |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-11-03 | 2016-10-12 09:07 | -22 | 2016-09-15 15:48 | Mechanical - Heating Ventilation & Air Conditioning | 1500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Use of Non-MCR'd __ manufactured HVAC Refrigerant Pipe Containment at North Woolwich Portal (approx 50mts)
| 03SR - Stations (RfL) | Cxxx-NCR-000238 | NCR | Plumstead Portal: Size of mortar bed joint in substation |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-12-15 | 2016-10-06 13:23 | -70 | 2016-09-16 09:51 | Architectural - Finishes | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Due to a build up of tolerances in the blockwork and __ system, the mortar bed thickness between the standard blocks has increased to beyond that stated in the standard BSEN 1996-1-1:2005 8.1.5.
| 03SR - Stations (RfL) | Cxxx-NCR-000239 | NCR | Woolwich West Box – Non complaint finish to soffit First Floor Level - B3-D3 to Y9-W7 |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-12-19 | 2016-12-09 11:23 | -10 | 2016-09-20 11:50 | Structural Engineering - Finishes | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following the delay strinking of propping and forwark for the first floor slab pour between B3-D3 to Y9-W7 it was found that ply board had become stuck to the underside of the slab and requires mechanical removal.
| 03SR - Stations (RfL) | Cxxx-NCR-000240 | NCR | Woolwich East Box - Crack in Blockwork Lintel Room 777 |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-10-06 | 2016-10-07 09:10 | 1 | 2016-09-22 09:14 | Civil - Structural Engineering | 500 |  | Manufacturing Defect | Reject | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | A crack has been identified in the lintel over the southern 2650mm wide opening to room 777 on the East Box Ground Floor. Details are shown in the attached photos and PDF mark up. As per the attached email correspondence with Cxxx, the lintel should be able to take the load imposed upon it by the blockwork
| 03SR - Stations (RfL) | Cxxx-NCR-000241 | NCR | Plumstead Portal: Incorrect movement joint location in substation |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-10-07 | 2016-09-28 17:26 | -9 | 2016-09-23 15:12 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A movement joint has been installed in the wrong location to the Plumstead Portal Substation. The movement joint should have been installed at the intersection of Gridline 3 and Gridline B, to the left of the central wall. It was actually installed to the left of the wall located halfway between Gridline 3 and Gridline 4 on Gridline B.
| 03SR - Stations (RfL) | Cxxx-NCR-000242 | NCR | Removal of ductwork for firestopping of wall joints |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-12-26 | 2017-01-06 14:48 | 11 | 2016-09-27 09:01 | Mechanical - Mechanical Engineering General | 2500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | The installed ductwork services within HV TR1 and TR2 east ground floor does not allow sufficient working space for the firestopping of the wall joints
| 03SR - Stations (RfL) | Cxxx-NCR-000243 | NCR | NWP - Removal of Non Compliant Unbonded Screed to MEP Building Roof |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-03-03 | 2016-11-07 11:05 | -116 | 2016-10-04 17:35 | Architectural - Roofing & Exterior Treatment | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | 08/08/2016 – 09/08/2016: The S/C applied the Isocrete Heavy Duty K-screed to the roof of the MEP Building at North Woolwich Portal which was laid as unbonded with a polythene sheet seperating the screed from the concrete. Without an assured design in place the NWP Site Team decided to work to the details of the drawing Cxxx-__R-A-DDD-CR146_PT004_Z-16002 P02 rather than what was detailed within the specification Cxxx-__R-A-RSP-CR146_PT004-50001 Rev 3.0 JM10.1205 •
| 03SR - Stations (RfL) | Cxxx-NCR-000244 | NCR | West Box - Room 907 Platform Level - Oversized gap for head restraint installation |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-01-01 | 2017-01-03 14:27 | 2 | 2016-10-03 10:52 | Structural Engineering - Structural Engineering - General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Five Secondary concrete walls located within West Box Room 907 have been poured significantly lower than the 50mm specified in clause 7.1 i) on drawing Cxxx-OVE-S-DDA-CR147_Z-50101. As a result head restraint cannot be installed as per Detail 4 on drawing Cxxx-OVE-S-DDD-CR147_Z-14681. Gaps between head of concrete wall and soffit of slab above are as shown on attached “Head Restraints - Oversized Gap Sketch Room 907”
| 03SR - Stations (RfL) | Cxxx-NCR-000245 | NCR | NCR - Gate by Exception for Plumstead Portal Headhouse Internal Blockwork |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2016-12-21 | 2016-12-09 12:19 | -12 | 2016-10-04 10:44 | Architectural - Brickworks/Blockworks | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In order to accelerate the Blockwork works at Plumstead, the technical assurance of the blockwork design has been obtained through the Crossrail by Exception process (CRL1-XRL-07-GPD-CR001-50023) The By Exception meeting has been held, and the risk of progressing has been recorded and signed off as acceptable by the PM on the technical Assurance by Exception Gate Risk assessment form Cxxx-__R-O7-ZFM-CR148_PT005-50001.pdf
| 03SR - Stations (RfL) | Cxxx-NCR-000246 | NCR | Fire Stopping F1 detail drawing (07030) not IFC, and no F2 design in place from specialist designer |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2016-11-08 | 2016-12-09 11:44 | 31 | 2016-10-11 14:59 | Architectural - Brickworks/Blockworks | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | A planned Crossrail Quality surveillance was undertaken on 10th October 2016 to look at installation of fire stopping for Woolwich Station internal walls. At the time of the visit, joint filler and intumescent sealant had been installed in a number of locations. __ drawing Cxxx-__R-A-DDD-CR147_WS163_Z-07030 was made available which provided the Blockwork header fire stopping typical detailing. On checking, this drawing was at a P01 status and not Issued for Construction. In addition, the typical detailing noted a seal depth of 30mm for gaps 31mm-100mm wide. However, an uncontrolled __ specialist detail for the corofill product was presented which defined the following detailing for gap sizes; 30mm-60mm > seal depth 30mm, 60mm-80mm > seal depth 40mm and 80mm-100mm > seal depth 50mm. This uncontrolled documented presented was stated as the F2 design for the header fire stopping detailing, however it had not been processed via any management system. It was noted that a number of areas in Woolwich Station with gaps >60mm had been installed with a 30mm seal depth which is in contradiction to the specialist detail presented. At the time of the surveillance, no F2 specialist design was in place for the fire stopping. The __ Design Management Plan (Cxxx-__R-O7-STP-CR147-50001) includes a process diagram for RIBA F1 to RIBA F2 drawings. This has not been followed for the works witnessed.
| 03SR - Stations (RfL) | Cxxx-NCR-000247 | NCR | WOO - Redrilled holes in close proximity to existing prefabricated drill holes within head restraints |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-04-30 | 2016-11-25 10:45 | -156 | 2016-10-12 15:37 | Civil - Structural Engineering | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Due to hitting reinfiorcement within the soffit of of the basement slab in the east box within rooms 732,733 and 666 site operatives have redrill holes within close proximity of existing holes which encroached within the zone of allowable spacing
| 03SR - Stations (RfL) | Cxxx-NCR-000248 | NCR | CMS Clash in Room 901 |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-04-10 | 2017-04-20 06:54 | 10 | 2016-10-12 14:06 | Electrical - Cable Management | 10000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Clash of electrical CMS within room 901/905 (East).
| 03SR - Stations (RfL) | Cxxx-NCR-000249 | NCR | Protection of AC units |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-12-30 | 2016-11-01 08:18 | -59 | 2016-10-13 08:20 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Cardboard protection on the AC unit in the Battery Room at North Woolwich Portal has fallen off.
| 03SR - Stations (RfL) | Cxxx-NCR-000250 | NCR | Removal of Refrigerant Tray for installation of Electrical Trays |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-01-11 | 2016-11-01 08:24 | -71 | 2016-10-13 12:03 | Mechanical - Mechanical Engineering General | 5000 |  | Planning | Rework | 3 (3-6k) | Complete | Subcontractor Problems - Insufficient work planning by the subcontractors | Completed |  | The installed refrigerant tray in the corridor at the MEP Compound Structure at North Woolwich Portal obstructs the installation of electrical trays above it.
| 03SR - Stations (RfL) | Cxxx-NCR-000251 | NCR | Damaged Drop Rods |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-01-11 | 2016-11-01 08:26 | -71 | 2016-10-13 13:00 | Mechanical - Mechanical Engineering General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | The drop rods installed in the corridor at the MEP Compound Structure at North Woolwich Portal were damaged by an operative driving a mobile tower in the corridor.
| 03SR - Stations (RfL) | Cxxx-NCR-000252 | NCR | NWP - Shrinkage Cracks to MEP Building Roof Soffit |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-03-03 | 2016-12-07 12:53 | -86 | 2016-11-03 16:48 | Structural Engineering - Concrete Member | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The roof slab of the plant building is cracked has been observed to have have shrinkage cracks
| 03SR - Stations (RfL) | Cxxx-NCR-000255 | NCR | Damaged paintwork on finished walls MEP Building |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-11-30 | 2017-01-30 10:46 | 61 | 2016-10-19 10:03 | Electrical - LV Equipment | 1500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | Galvanising paint on conduit bends and threads oversprayed onto finished walls in MEP building at North Woolwich Portal.
| 03SR - Stations (RfL) | Cxxx-NCR-000256 | NCR | __ Cxxx-__R-O7-ZFM-CR148_PT005-50002 - Plumstead Portal Headhouse Internal Screed |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2017-10-01 | 2016-12-09 12:29 | -296 | 2016-10-26 09:22 | Architectural - Flooring | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In order to accelerate the installation of the screed to deliver the SLD dates, the technical assurance to commence the internal screed at Plumstead Portal Headhouse has been obtained through the Crossrail By Exception process (CRL1-XRL-O7-GPD-CR001-50023). The By Exception meeting has been held on the 03-08-16, and the risk of progressing has been recorded and signed off as acceptable by the PM on the Technical Assurance By Exception Gate Risk Assessment Form Cxxx-__R-O7-ZFM-CR148_PT005-50002. The acceptance of the procedure which was assessed by the relevant attendees at the risk review meeting is recorded in Cxxx-CCM-00883 and noted within Cxxx-PMC-01163
| 03SR - Stations (RfL) | Cxxx-NCR-000257 | NCR | __ Cxxx-__R-O7-ZFM-CR148_PT005-50002 Rev 2.0 Plumstead Headhouse Internal Screed |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2017-01-03 | 2017-01-06 13:16 | 3 | 2016-12-20 10:36 | Architectural - Flooring | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In order to accelerate the installation of the screed to deliver the SLD dates, the technical assurance to commence the internal screed at Plumstead Portal Headhouse has been obtained through the Crossrail By Exception process (CRL1-XRL-O7-GPD-CR001-50023). The By Exception meeting has been held on the 03-08-16, and the risk of progressing has been recorded and signed off as acceptable by the PM on the Technical Assurance By Exception Gate Risk Assessment Form Cxxx-__R-O7-ZFM-CR148_PT005-50002. The acceptance of the procedure which was assessed by the relevant attendees at the risk review meeting is recorded in Cxxx-CCM-00883 and noted within Cxxx-PMC-01163
| 03SR - Stations (RfL) | Cxxx-NCR-000258 | NCR | __ Cxxx-__R-O7-ZFM-CR146_WS160-50002 Screed works North Woolwich Portal |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2016-10-01 | 2016-12-06 10:55 | 66 | 2016-10-26 10:48 | Architectural - General | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In order to accelerate the installation of the screed to deliver the SLD dates, the technical assurance to commence the internal screed at North Woolwich Portal has been obtained through the Crossrail By Exception process (CRL1-XRL-O7-GPD-CR001-50023). The By Exception meeting has been held on the 21-09-16, and the risk of progressing has been recorded and signed off as acceptable by the PM on the Technical Assurance By Exception Gate Risk Assessment Form Cxxx-__R-O7-ZFM-CR146_WS160-50002. The acceptance of the procedure which was assessed by the relevant attendees at the risk review meeting is recorded in Cxxx-CCM-00901 and noted within Cxxx-PMC-01165
| 03SR - Stations (RfL) | Cxxx-NCR-000259 | NCR | __ Cxxx-__R-O7-ZFM-CR146_WS160-50004 - Firestopping Works, North Woolwich: SLD rooms 731, 668, 671, 781, 782 |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2017-10-02 | 2016-12-09 15:11 | -297 | 2016-10-26 15:11 | Fire - Compartmentation | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In order to accelerate the installation of the fire stopping works in MEP building first floor SLD rooms the technical assurance of the SLD rooms 731, 668, 671, 781, 782 has been obtained through the Crossrail By Exception process (CRL1-XRL-O7-GPD-CR001-50023). The By Exception meeting has been held on the 21-09-16, and the risk of progressing has been recorded and signed off as acceptable by the PM on the Technical Assurance By Exception Gate Risk Assessment Form Cxxx-__R-O7-ZFM-CR146_WS160-50004. The acceptance of the procedure which was assessed by the relevant attendees at the risk review meeting is recorded in Cxxx-CCM-00902 and noted within Cxxx-PMC-01167.
| 03SR - Stations (RfL) | Cxxx-NCR-000260 | NCR | __ Cxxx-__R-O7-ZFM-CR148_PT005-50003 -Plumstead Portal Headhouse, Substation and RMU Firestopping |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2017-10-02 | 2016-12-09 14:55 | -297 | 2016-10-26 15:29 | Fire - Compartmentation | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In order to accelerate the installation of the fire stopping works for the substation, headhouse and RMU building the technical assurance has been obtained through the Crossrail By Exception process (CRL1-XRL-O7-GPD-CR001-50023). The By Exception meeting has been held on the 21-09-16, and the risk of progressing has been recorded and signed off as acceptable by the PM on the Technical Assurance By Exception Gate Risk Assessment Form Cxxx-__R-O7-ZFM-CR148_PT005-50003. The acceptance of the procedure which was assessed by the relevant attendees at the risk review meeting is recorded in Cxxx-CCM-00898 and noted within Cxxx-PMC-01164.
| 03SR - Stations (RfL) | Cxxx-NCR-000261 | NCR | __ Cxxx-__R-O7-ZFM-CR146_WS158-50002 - WP4A Connaught Support Building - Piling and Substructure |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2017-10-02 | 2016-12-09 14:46 | -297 | 2016-10-26 15:48 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In order to accelerate the ground works including piling, ground beams and RC slab for Connuaght House support building, the technical assurance has been obtained through the Crossrail by Exception process (CRL1-XRL-07-GPD-CR001-50023) The By Exception meeting has been held on the 21-09-16 and the risk of progressing has been recorded and signed off as acceptable by the PM on the technical Assurance by Exception Gate Risk assessment form Cxxx-__R-O7-ZFM-CR146_WS158-50002. The acceptance of the procedure which was assessed by the relevant attendees at the risk review meeting is recorded in Cxxx-CCM-00906 and noted within Cxxx-PMC-01168.
| 03SR - Stations (RfL) | Cxxx-NCR-000262 | NCR | __ Cxxx-__R-O7-ZFM-CR147-50020 - Technical Assurance By Exception Gate Risk Assessment Form: Woolwich Station Fire Stopping |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2017-10-02 | 2016-12-09 14:59 | -297 | 2016-10-26 16:08 | Fire - Compartmentation | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In order to accelerate the installation of the fire stopping works for Woolwich Station the technical assurance has been obtained through the Crossrail By Exception process (CRL1-XRL-O7-GPD-CR001-50023). The By Exception meeting has been held on the 13-10-16, and the risk of progressing has been recorded and signed off as acceptable by the PM on the Technical Assurance By Exception Gate Risk Assessment Form Cxxx-__R-O7-ZFM-CR147-50020. The acceptance of the procedure which was assessed by the relevant attendees at the risk review meeting is recorded in Cxxx-CCM-00915 and noted within Cxxx-PMC-01166.
| 03SR - Stations (RfL) | Cxxx-NCR-000263 | NCR | __ Cxxx-__RO7-ZFM-CR147-50025 West box escalator in-situ brickwork |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2017-10-02 | 2016-12-09 15:06 | -297 | 2016-10-31 12:50 | Architectural - Brickworks/Blockworks | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In order to accelerate the installation of the escalator trusses the brickwork void area around the escalators is required to be complete, the technical assurance of the brickwork has been obtained through the Crossrail By Exception process (CRL1-XRL-O7-GPD-CR001-50023). The By Exception meeting has been held on the 13-10-16, and the risk of progressing has been recorded and signed off as acceptable by the PM on the Technical Assurance By Exception Gate Risk Assessment Form Cxxx-__R-E-ZFM-CR147-50028. The acceptance of the procedure which was assessed by the relevant attendees at the risk review meeting is recorded in Cxxx-CCM-00915 and noted within Cxxx-PMC-01176.
| 03SR - Stations (RfL) | Cxxx-NCR-000264 | NCR | Plumstead Portal: Aborted Concrete Pour - Substation Roof Slab |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-11-15 | 2016-12-12 13:45 | 27 | 2016-11-01 17:14 | Civil - Civil Engineering General | 25000 |  | Incomplete Works | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | When pouring the Plumstead Portal substation roof slab on 28/10/16, the concrete pour had to be aborted as the __ concrete trucks did not arrive in time (2 hours between trucks) and the concrete became unworkable. It was then agreed on site to cancel the pour in order to avoid installing a slab with a cold joint.
| 03SR - Stations (RfL) | Cxxx-NCR-000265 | NCR | Incorectly stored contaiment |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-12-04 | 2017-01-31 09:35 | 58 | 2016-11-04 12:18 | Materials - General | 3000 |  | Material | Reject | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | Containment Incorrectly stored causing damage to material.
| 03SR - Stations (RfL) | Cxxx-NCR-000266 | NCR | Use of non MCR approved galvanising spray |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-02-05 | 2017-02-03 12:04 | -2 | 2016-11-07 16:01 | Mechanical - Heating Ventilation & Air Conditioning | 2500 |  | Material | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient surveillance of subcontractors | Completed |  | Sub-contractors not using MCR approved galvanising spray on __ support brackets on both the ventilation and air conditioning systems in all relevant rooms in North Woolwich Portal.
| 03SR - Stations (RfL) | Cxxx-NCR-000267 | NCR | Incorrect Storage of Materials |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-02-05 | 2017-02-03 11:00 | -2 | 2016-11-07 16:01 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient surveillance of subcontractors | Completed |  | Materials stored in the laydown area at North Woolwich Portal were stored on a pallet, unsecured with open ends in inclement weather. All ductwork was exposed to water and debris ingress.
| 03SR - Stations (RfL) | Cxxx-NCR-000268 | NCR | Incorrect Blockwork Hole Size |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-02-12 | 2017-02-02 16:47 | -10 | 2016-11-14 11:23 | Mechanical - Heating Ventilation & Air Conditioning | 2500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | The blockwork hole used for the routing of the refrigerant pipework to exit the North Woolwich Portal MEP building to connect to the external condenser units on the first floor is incorrect. As per the drawing Cxxx-__R-M-DDA-CR146_PT004_A-12001 First Level, M&E Compound, Mechanical Piped Services, a 600mm __ tray is unable to fit through the 560mm hole.
| 03SR - Stations (RfL) | Cxxx-NCR-000269 | NCR | Woolwich Station - West Box - Incorrect mortar shade in Escalator Void Brickwork (Non-public view) |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-02-13 | 2016-11-22 13:50 | -83 | 2016-11-15 17:06 | Architectural - Brickworks/Blockworks | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Brickwork has been installed in the West Box Escalator void of the Cxxx Woolwich Station. This work was carried out with pre-start paperwork in place, confirming the correct materials to use for the architectural face work. The mortar colour has been agreed through numerous sample panels with the Cxxx architect and Crossrail Architectural team. This was to be CPI __ Coloured mortar ‘Charcoal – E022’. The mortar used for construction was supplied to site in a pre-filled silo. The initial area of brickwork was installed and the scaffold stripped. After this, the brickwork s/c Lee Marley Brickwork realised that the incorrect shade of mortar ‘Charcoal - E021’ was used to fill the silo by the supplier (CPI). CPI has since confirmed that this was their error. Due to the similarity of the shades when wet this difference was not evident during construction. This was also used to complete and sign off the Post Contract Award Brick Sample Panel (JF10.2103).
| 03SR - Stations (RfL) | Cxxx-NCR-000271 | NCR | Woolwich West box - Missed Spine Beam __ Channels |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-07-14 | 2017-06-15 14:03 | -29 | 2016-11-21 17:52 | Civil - Structural Engineering | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The design shows __ channels are to be cast into West Box spine beams W__28 and W__29 to act as anchor points for asymmetric beams. However of the 44 __s to be installed 2 were missed.
| 03SR - Stations (RfL) | Cxxx-NCR-000272 | NCR | Woolwich West Box - Failed Inspection Second Floor Parapet Wall |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2016-12-23 | 2016-12-21 17:06 | -2 | 2016-11-23 16:16 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Supervision - Supervisor does not have sufficient experience | Completed |  | CRL was invited to do an inspection on site in the second floor of the West Box. On arrival to the inspection area the Engineer responsible gave the CRL Field Engineer a drawing which clearly showed 3 horizontal lacer bars in the area to be poured. On inspection of the rebar on site it was noted that there were only 2 horizontal lacer bars installed which was not in accordance to the drawing reference. The __ engineer responsible for the area was asked why there were only 2 lacer bars and a reasonable explanation could not be given. The concrete pour was therefore stopped until the steel work could be rectified as per drawing.
| 03SR - Stations (RfL) | Cxxx-NCR-000273 | NCR | Woolwich Station - Oversized gap for head restraint installation |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-03-12 | 2017-01-10 09:50 | -61 | 2016-12-12 09:38 | Structural Engineering - Structural Engineering - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | Following a survey of wall heights in the Cxxx Woolwich Station carried out as a result of Cxxx-NCR-000244 there are instances of further walls being poured too low. The walls affected are highlighted in the attached Markup.
| 03SR - Stations (RfL) | Cxxx-NCR-000274 | NCR | Woolwich Station - West Box - Damage to concrete from drilling head-restraint holes |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-02-22 | 2016-12-07 13:05 | -77 | 2016-11-24 16:29 | Structural Engineering - Concrete Member | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | The __ Head Restraint team was installing head restraints in Corridor 83 (West Box Ticket Hall), to the required embedment of 150mm as per the ITP. The wall being drilled was only 200mm thick, and as a result of the drilling the concrete on the opposite face to the drilling side has been loosened and fallen away Please see attached images of the affected area.
| 03SR - Stations (RfL) | Cxxx-NCR-000275 | NCR | Materials Handling Procedure __ A/C Installers |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-12-25 | 2017-01-27 13:52 | 33 | 2016-11-25 13:00 | Mechanical - Mechanical Engineering General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient surveillance of subcontractors | Completed |  | Materials handling procedure has not been followed further to request by CRL field engineer Stuart Green concerning the delivery documentation of DX Air Conditioning Units to site. No documentation was visible to support materials delivered to site.
| 03SR - Stations (RfL) | Cxxx-NCR-000276 | NCR | Incomplete progressive Installation Documentation |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-12-25 | 2017-01-27 13:55 | 33 | 2016-11-25 13:07 | Mechanical - Mechanical Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient surveillance of subcontractors | Completed |  | Failure by __ Supervisor to produce progressive Installation Documentation for DX Air Condition System in North Woolwich Portal by __
| 03SR - Stations (RfL) | Cxxx-NCR-000277 | NCR | Calibration Certification records not available upon request |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-01-06 | 2017-01-27 13:54 | 21 | 2016-11-25 13:14 | Mechanical - Mechanical Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient surveillance of subcontractors | Completed |  | __ Subcontractors failed to produce calibration certification of test equipment used on site throughout installation and testing of DX Air Conditioning System.
| 03SR - Stations (RfL) | Cxxx-NCR-000278 | NCR | No Extract Fan delivery assurance documetation - __ |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-01-06 | 2017-01-27 13:50 | 21 | 2016-11-25 13:21 | Mechanical - Mechanical Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient surveillance of subcontractors | Completed |  | Materials Handling Procedure has not been followed resulting in no Delivery Assurance Documentation for Extract Fans at North Woolwich Portal for materials delivered to site.
| 03SR - Stations (RfL) | Cxxx-NCR-000279 | NCR | Poor Workmanship by Hotchkiss Engineers |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-01-06 | 2017-01-31 07:20 | 25 | 2016-11-25 13:30 | Mechanical - Mechanical Engineering General | 2500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | Poor workmanship by Hotchkiss engineers by failing to adequately carryout repair paintwork to damaged/cut ends of galvanised surfaces.
| 03SR - Stations (RfL) | Cxxx-NCR-000280 | NCR | Woolwich Station - West Box - Incorrect Tie installation in Escalator Void Brickwork |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-01-31 | 2016-12-19 11:48 | -43 | 2016-12-01 11:25 | Structural Engineering - Structural Engineering - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | Architectural Brickwork has been constructed in the Woolwich Station West Box. An initial section has been constructed in the escalator void to enable truss installation. The design for this section of work was approved through the __, Cxxx-__R-O7-ZFM-CR147-50025, drawings which have now been Gated. The Structural Engineers markup attached to the __ shows Type 1 ties to be used throughout the void to tie back to the RC Frame and Blockwork. In some cases, Type 2 ties have been installed in this area of brickwork already constructed. The number of Type 2 ties used in the void is approximately 30% of the total number used thus far. This issue was only raised after the access had been removed therefore immediate remediation was not possible.
| 03SR - Stations (RfL) | Cxxx-NCR-000281 | NCR | Plumstead Portal: Application of Anti Graffiti Paint to Sample Panel |  | Contr | __R | WOO - Woolwich Station (East) |  | 2016-12-26 | 2017-01-26 14:41 | 31 | 2016-12-12 16:21 | Architectural - Finishes | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Over application of anti graffiti paint to the sample panel at Plumstead Portal has altered the accepted finish of the brickwork sample.
| 03SR - Stations (RfL) | Cxxx-NCR-000282 | NCR | Woolwich West Box - Holes in Room 905 |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-02-22 | 2017-02-20 14:23 | -2 | 2016-12-13 16:21 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On commence of lifting beams’ installation in room 905 (West Box 2nd floor), Cxxx __-TVP drilled 2 holes through the soffit of the roof slab for the anchor points. However, the holes were drilled completely through the slab (225mm) and damaged the screed at roof level.
| 03SR - Stations (RfL) | Cxxx-NCR-000283 | NCR | Removal of Fire Rated Ducted in West Box - Room HVTR II 782 |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-01-31 | 2017-01-13 13:33 | -18 | 2016-12-16 13:09 | Mechanical - Heating Ventilation & Air Conditioning | 2500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | The fire rated ductwork was installed to progress the installation works, however the location of the fire dampers, was then confirmed as being installed on the roof above the HVTR II 782, and to install the fire dampers and ductwork, from roof level, the fire rated ductwork would have to be removed. There was also no provision to install the fire dampers at roof level, therefore the ductwork in room 782 was removed.
| 03SR - Stations (RfL) | Cxxx-NCR-000284 | NCR | Lagging Materials Used Without an MCR |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-04-07 | 2017-03-24 07:14 | -14 | 2016-12-16 13:25 | Mechanical - Mechanical Engineering General | 0 |  | Planning | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Insulation materials issued for MCR approval are being used on site without the approved MCR.
| 03SR - Stations (RfL) | Cxxx-NCR-000286 | NCR | Plumstead RMU earthing |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-04-06 | 2017-03-24 09:43 | -13 | 2017-02-09 18:03 | Utilities Engineering - Electricity | 3000 |  | System Defect | Reject | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The Plumstead RMU earthing design was completed to __ standards and approved by CRL by Cxxx. On presenation of the RMU rooms to __, the Building Inspector did not recognise the design or the physical arrangements on site, and would not sign the RMU rooms off. The earthing arrangements require redesign and reconstruction, with additional earthing added. __ also stated they would not fit out the DNO metering room
| 03SR - Stations (RfL) | Cxxx-NCR-000287 | NCR | Woolwich Station - East Box - Non-conforming M12 Mortar compressive test results |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-03-03 | 2017-02-21 16:26 | -10 | 2017-01-18 09:46 | Architectural - Brickworks/Blockworks | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | A set of M12 mortar prisms were taken at the start of brickwork wall construction (16/11/16) on the North and South elevations of the Cxxx Woolwich Station. The 28 day prism crush results show an average compressive strength of 6.8N/mm2, much lower than should be expected of an M12 mortar. Each batch is tested by CPI __ (Supplier) and the results supplied demonstrate that the factory prisms taken achieved between 13-19N/mm2 after 28 days. The delivery note shows that this tested batch was delivered to Woolwich Cxxx site. The specification does not give the exact strength that must be achieved for M12 Mortar. As an example, M4 mortar (4N/mm2) must only achieve a minimum of 2.8N/mm2 after 28 days. This mortar has been used in areas below the DPC on both elevations, minimum 150mm (approximately 3 courses) above external FFL. The East box has differing levels and different configurations of brickwork, shown in the attached sketches.
| 03SR - Stations (RfL) | Cxxx-NCR-000288 | NCR | Failure to provide upon request during inspection current valid documentation require to undertake Installation of Domestic Water Systems |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-03-19 | 2017-03-31 09:01 | 12 | 2017-01-18 09:44 | Mechanical - Public Health Engineering | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Quality inspectors requested view of the Method Statement; ITP; drawings and checksheets from the site supervisor in charge of the Installation of the Domestic Water Supply System in the Woolwich Station East Box. The site supervisor was unable to prove he had all the relevant documentation as requested.
| 03SR - Stations (RfL) | Cxxx-NCR-000289 | NCR | __ - Plumstead CER - Foundations, roof slab and Services ducting |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2017-03-01 | 2017-01-30 15:09 | -30 | 2017-01-25 10:30 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In order to progress the construction for the CER building at Plumstead the technical assurance for the RC structural elements namely the foundations & roof slab along with ducting services has been obtained through the Crossrail By Exception process (CRL1-XRL-O7-GPD-CR001-50023). The By Exception meeting has been held, and the risk of progressing has been recorded and signed off as acceptable by the PM on the Technical Assurance By Exception Gate Risk Assessment Form Cxxx-__R-O7-ZFM-CR148_PT005-50009, Rev 1.0 The acceptance of the procedure which was assessed by the relevant attendees at the risk review meeting and recorded and issued via Cxxx-CCM-00972 and noted within Cxxx-PMC-XXXX.
| 03SR - Stations (RfL) | Cxxx-NCR-000290 | NCR | __ Cxxx-__R-O7-ZFM-CR148_PT005-50008 Plumstead Portal metalwork |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2017-02-21 | 2017-02-21 14:40 | 0 | 2017-02-07 09:54 | Architectural - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In order to accelerate the F2 design for architectural metalwork at Plumstead Portal, technical assurance of the metalwork has been obtained through the Crossrail By Exception process (CRL1-XRL-O7-GPD-CR001-50023). The By Exception meeting has been held on the 18-01-2017, and the risk of progressing has been recorded and signed off as acceptable by the PM on the Technical Assurance By Exception Gate Risk Assessment Form Cxxx-__R-O7-ZFM-CR148_PT005-50008. The acceptance of the procedure which was assessed by the relevant attendees at the risk review meeting is recorded in Cxxx-CCM-00977 and noted within Cxxx-PMC-01293.
| 03SR - Stations (RfL) | Cxxx-NCR-000291 | NCR | Workmanship - External brickwork not compliant with benchmark standard |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-04-10 | 2017-04-27 10:12 | 17 | 2017-02-09 12:38 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Following site inspection at North Woolwich Portal the 7 items listed below were identified as Non Conformance 1. & 2. Gaps between mortar and brickwork -External wall, ground level (Photos 1 & 20). 3. Damaged brick - External wall ground level (Photo 3) 4. Damaged mortar - External wall ground level (Photo 4) . 5. Mortar stained - External wall - ground level (Photo 5). 6. Material to surface of brick - External wall ground level (photo 6). 7. Mortar splashes to base of wall - External wall ground level. (Photo 7). See attached ohotographs and drawing
| 03SR - Stations (RfL) | Cxxx-NCR-000292 | NCR | __ Cxxx-__R-O7-ZFM-CR148_PT005-50009 Plumstead CER Architecture |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2017-03-31 | 2017-03-30 12:36 | -1 | 2017-02-15 11:22 | Architectural - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In order to accelerate the F2 design for architecture at Plumstead CER, technical assurance has been obtained through the Crossrail By Exception process (CRL1-XRL-O7-GPD-CR001-50023). The By Exception meeting has been held on the 27/01/2017, and the risk of progressing has been recorded and signed off as acceptable by the PM on the Technical Assurance By Exception Gate Risk Assessment Form Cxxx-__R-O7-ZFM-CR148_PT005-50009. The acceptance of the procedure which was assessed by the relevant attendees at the risk review meeting is recorded Cxxx-PMC-01302.
| 03SR - Stations (RfL) | Cxxx-NCR-000293 | NCR | Incorrectly fitted Electrical Brass Bushes Room 701 East Box (Cxxx-NCR-67) |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-03-22 | 2017-03-03 08:43 | -19 | 2017-02-20 13:43 | Electrical - General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | Room 701 Woolwich Station East Box: Male and female brass bushes are installed incorrectly. The male bush has been installed and was found to be too long and incorrectly installed. This, and the fact that a female bush has been installed on the end of the exposed thread of the male bush; will reduce the amount of effective space to wire through the conduit box into which it is utilised as a means of fixing to the attached trunking. If the male bush had been installed from the conduit box into the trunking there would have been minimal space taken in the conduit box thus allowing a greater number of cables to pass through the bush from the trunking to the conduit box.
| 03SR - Stations (RfL) | Cxxx-NCR-000294 | NCR | Plumstead DX Units Uncontrolled documents - Room 369 Battery Room; Plumstead Portal. |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-04-17 | 2017-04-19 12:11 | 2 | 2017-02-16 07:40 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Use of uncontrolled sketch to install DX units. There was an enlarged segment of drawings with no DeCal signingfying the status of the drawing. Site visit carried out with __ Mechanical Supervisor for Plumstead.
| 03SR - Stations (RfL) | Cxxx-NCR-000295 | NCR | Plumstead Portal DX Unit not installed to design - Room 667 Battery Room |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-04-17 | 2017-04-20 15:25 | 3 | 2017-02-16 08:09 | Mechanical - Heating Ventilation & Air Conditioning | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | Plumstead Portal Battery Room - DX Units pipework and tray installed and not aligning with the approved design drawings. Design has been altered without formal CRL. Deviation from Cxxx-__R-M-DDA-CR148_PT005_2-15001.
| 03SR - Stations (RfL) | Cxxx-NCR-000296 | NCR | No on site Documentation for Supply and Extract Ventilation in Cer room (__ NCR-70) |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-04-17 | 2017-03-06 16:12 | -42 | 2017-02-16 16:41 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | __ Mechanical supervisor was unable to produce workpack documentation for installation of Motorised Fire Dampers in the CER room at Plumstead Portal (Sub-surface level) when requested by Quality Inspector. The workpack documentation must include: Method Statements; ITP's; Drawings; Task Briefing Sheets; Quality Assurance check sheets.
| 03SR - Stations (RfL) | Cxxx-NCR-000297 | NCR | Materials Handling Procedure not being followed - Woolwich Station - East Box |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-03-19 | 2017-03-30 08:21 | 11 | 2017-02-17 11:26 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Site inspectors discovered the materials handling prpcedure was not being followed for the Fire Dampers at Woolwich Station East Box
| 03SR - Stations (RfL) | Cxxx-NCR-000298 | NCR | Documentation for installation of Independent Motorised Dampers - Plumstead CER Room 731 |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-06-30 | 2017-05-25 15:47 | -36 | 2017-02-17 11:51 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Supervision - Supervisor does not have access to all pertinent information | Completed |  | No documentation in place on site for the work that has been installed for the Independent Motorised Fire Dampers installed in the CER Room (701) at Plumstead Portal.
| 03SR - Stations (RfL) | Cxxx-NCR-000299 | NCR | Incorrect use of plumbing pipe clips to support electrical conduit - Room 666 (OHLE) West Box Woolwich Station (__ App NCR No. 078) |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-03-24 | 2017-03-30 13:00 | 6 | 2017-02-22 08:26 | Electrical - General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | __ operative has installed rubber lined water-pipe clips to support electrical conduits in room 666 (OHLE) West Box, Woolwich Station
| 03SR - Stations (RfL) | Cxxx-NCR-000301 | NCR | Slip test fail in FOSC and CIRS Rooms - NWP (__ NCR App. No 93) |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-04-01 | 2017-03-27 14:23 | -5 | 2017-03-02 11:45 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | North Woolwich Portal - Floor Resin in both FOSC rooms at platform level and in CIRS lll in MEP building failed slip resistance test when floor was wet.
| 03SR - Stations (RfL) | Cxxx-NCR-000302 | NCR | Slip test fail in FOSC and CIRS Rooms - NWP (__ NCR App. No 93) |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-05-29 | 2017-05-12 12:47 | -17 | 2017-03-01 09:28 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | North Woolwich Portal - Floor in both FOSC rooms and at platform level in CIRS lll in MEP building failed the slip resistance test when floor was wet
| 03SR - Stations (RfL) | Cxxx-NCR-000303 | NCR | ITP Cxxx-__R-M-ITP-CR148_PT005-50001 procedure from Civils to MEP (__ App. NCR 99) |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-06-30 | 2017-07-05 15:55 | 5 | 2017-03-09 08:08 | Mechanical - Mechanical Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | There is no formal procedure in place identified in ITP Cxxx-__R-M-ITP-CR148_PT005-5001 that permits to partial handover from civils at the point of room readiness to MEP (or 3rd Parties) to carryout installation of services and then return to civils to carryout making good and final finishing.
| 03SR - Stations (RfL) | Cxxx-NCR-000304 | NCR | Failed pendulum test - Non slip resistance test. Rms 411; 777; 670 East Box (__ App NCR 00100) |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-05-29 | 2017-05-22 13:36 | -7 | 2017-03-08 15:29 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Resin floor finsih in Woolwich Station East Box rooms 411; 777 & 670 failed the Pendulum test Non-slip resistance value.
| 03SR - Stations (RfL) | Cxxx-NCR-000312 | NCR | Cable Tray Installation of Site made bends |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2017-04-11 | 2017-05-15 09:32 | 34 | 2017-03-14 13:09 | Electrical - Cable Management | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the surveillance of Woolwich Station we came across site made cable tray bends have been installed in areas CER 731, RR701 and __R 702. This contravenes M&W Specification JY63 Support Components –Cables (Tray) Section JY63.1302 – d) Cable tray and ladder support components shall be manufactured to BS 6946. Not prefabricated on site. 2. Tray has been cut across perforations which contravenes M&W Specification JY63 Support Components –Cables (Tray) Section JY63.3200 Workmanship – d) Cutting of cable tray shall be along a line of plain material i.e. not through perforations.
| 03SR - Stations (RfL) | Cxxx-NCR-000313 | NCR | Cable Tray cut through perforations |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2017-04-11 | 2017-05-17 13:31 | 36 | 2017-03-14 09:48 | Electrical - Cable Management | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __ cable Tray has been cut across perforations where it meets basket tray high level as you enter CER 732. This contravenes M&W Specification JY63 Support Components –Cables (Tray) Section JY63.3200 Workmanship – d) Cutting of cable tray shall be along a line of plain material i.e. not through perforations.
| 03SR - Stations (RfL) | Cxxx-NCR-000314 | NCR | Trunking screws protruding through taped holes |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2017-04-11 | 2017-04-28 09:54 | 17 | 2017-03-14 09:55 | Electrical - Cable Management | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | __ single compartment trunking joining screws protrude beyond the nut into the trunking compartment. Different types and length of screws have been installed. This contravenes M&W Specification JY60 Conduit and cable Trunking section JY60.1306 s) Ensure screws do not protrude through the nuts. v) Screws must not project through the nut.
| 03SR - Stations (RfL) | Cxxx-NCR-000315 | NCR | Basket tray is not identified in ITP |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2017-04-11 | 2017-05-17 14:08 | 36 | 2017-03-14 10:08 | Electrical - Cable Management | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Basket tray has been installed in rooms CER 732, RR701 & __R 702. Upon checking the Approved ITP Cxxx-__R-E-ITP-CR147-50001 it was found that the ITP does not reverence the installation of Basket Tray.
| 03SR - Stations (RfL) | Cxxx-NCR-000316 | NCR | Trunking not fixed above Distribution Boards in CER 731 East Box |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2017-04-11 | 2017-05-17 14:29 | 36 | 2017-03-14 10:26 | Electrical - Cable Management | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As part of the surveillance we entered CER 731 where it was noted single compartment trunking had been installed above two local distribution boards and fixed via screws between the trunking and the Distribution Boards. The trunking should be fixed to supports independent from the distribution boards. Additionally it had been noted that there is one screw visible on the trunking on the right hand side of the Distribution Boards. This contravenes M&W Specification JY60 section: JY60.1306 n) the trunking shall be use purpose made brackets to fix to structural steel, building fabric or suspended rods and JY60.3217 a) Ensure trunking is independently fixed and supported (on steel channel system) from building fabric and c) Use two suitably sized parallel fixings (minimum) per metre.
| 03SR - Stations (RfL) | Cxxx-NCR-000317 | NCR | Earth Continuity Testing of CMS |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2017-04-11 | 2017-05-17 14:56 | 36 | 2017-03-14 10:53 | Electrical - Cable Management | 500 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | During the surveillance testing of completed containment in rooms CER 731, RR701 & __R 702 was discussed. It was mentioned that no continuity tests have been carried out to the completed containment systems in these rooms which has been handover as complete to Cxxx contractors. It was also noted that there are several earth bonds are missing between horizontal and vertical sections of tray and tray to trunking within these rooms which has been captured by CRL Delivery Team on their punch lists. This contravenes Works Information Volume 2B Part 13 – 13.2 Assurance – The Contractor shall provide progressive assurance that the Contractor’s design (where applicable) and “the constructed works” comply with the requirements set out in the contract. __ assurance means that there will be continual confirmation of compliance by the generating of contemporaneous records. In this case continuity testing.
| 03SR - Stations (RfL) | Cxxx-NCR-000318 | NCR | Water ingress between brickwork and concrete through mastic joint sealant North Woolwich Portal |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-05-14 | 2017-04-27 14:31 | -17 | 2017-03-15 14:50 | Civil - Civil Engineering General | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | MEP Building Ground Floor - Brickwork mastic installed at the top of he brickwork underneath the concrete beams is failing and allowing water ingress.
| 03SR - Stations (RfL) | Cxxx-NCR-000319 | NCR | Foul and Waste __ Cast Iron Couplings Not Installed to Manufacturer's Recommendation - East Box (__ App NCR 104) |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-05-20 | 2017-05-25 09:04 | 5 | 2017-03-21 15:29 | Mechanical - Public Health Engineering | 3000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Upon inspection of the __ cast iron couplings in East Box basement level for the foul and waste drainage system, it appears the couplings have not been tightened to the correct torque (20NM) or a gap of 2 - 3mm for work that has been installed, in compliance with maunfacturer's recommendation
| 03SR - Stations (RfL) | Cxxx-NCR-000320 | NCR | __ Cast Iron Pipework and Fittings Installed without Approved MRC Woolwich Stn. (__ App NCR 109) |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-05-20 | 2017-05-19 13:14 | -1 | 2017-03-21 15:51 | Mechanical - Public Health Engineering | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Lack or improper material identification and traceability | Completed |  | __ pipework and fittings have been installed throughout Woolwich Station without an approved MCR in place.
| 03SR - Stations (RfL) | Cxxx-NCR-000321 | NCR | Approved documentation not in place for Sub-platform lagging - __ App NCR 113 |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-06-30 | 2017-06-15 10:42 | -15 | 2017-03-23 08:08 | Mechanical - Public Health Engineering | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | No approved ITP; WPP; TBS in place to enable the installation of lagging to domestic water services pipework throughout all areas of Woolwich Station.
| 03SR - Stations (RfL) | Cxxx-NCR-000322 | NCR | Ramp Screeded incorrectly Lobby 87 inot 907 West Box Basement -2 (__ App NCR 111) |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-06-23 | 2017-06-21 14:23 | -2 | 2017-03-27 08:42 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Woolwich Station, West Box Basement -2 Level. Ramping from lobby 87 into 907 in West Box Basement -2 has been screeded incorrectly. Ramp begins from door connecting 87 to corridor as opposed to starting from at door 87 into 907.
| 03SR - Stations (RfL) | Cxxx-NCR-000323 | NCR | Non-fire rated material on sub-station and Portal roofs - Plumstead & NWP Portals |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-05-29 | 2017-05-18 10:44 | -11 | 2017-03-30 09:31 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | EPS foam used on the Sub-station at Plumstead and North Woolwich Portal roofs.
| 03SR - Stations (RfL) | Cxxx-NCR-000324 | NCR | Installation of non MCR approved cables |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-09-29 | 2017-09-25 12:34 | -4 | 2017-03-31 12:16 | Mechanical - Heating Ventilation & Air Conditioning | 3000 |  | Planning | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Electrical cables connecting the external condensers and room units have been installed in Woolwich Station, North Woolwich Portal and Plumstead Portal without an approved MCR.
| 03SR - Stations (RfL) | Cxxx-NCR-000325 | NCR | Missing Sump pits and seepage UTX |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-07-02 | 2017-07-05 14:13 | 3 | 2017-04-03 14:02 | Mechanical - Public Health Engineering | 3000 |  | Design | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Missing sump pits and seepage drainage in both Woolwich West and East Box.
| 03SR - Stations (RfL) | Cxxx-NCR-000326 | NCR | Stairs (631) between Platform and Basement Level has been installed incorrectly - Woolwich Station West Box |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-10-31 | 2017-11-09 15:00 | 9 | 2017-04-10 15:00 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The staircase (631) between Platform and Basement Level have been installed incorrectly This has caused the top stair to be 15mm out of level with the stair at the bottom of ground to basement staircase.
| 03SR - Stations (RfL) | Cxxx-NCR-000328 | NCR | Non Conformance for Mechanical Protection |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-06-25 | 2017-06-27 15:46 | 2 | 2017-04-26 13:51 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Room DX units have been installed and no mechanical or adequate fire protection has been put in place to protect assets.
| 03SR - Stations (RfL) | Cxxx-NCR-000329 | NCR | Inadequate number of personnel authorised to raise NCRs |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-07-31 | 2017-08-01 08:50 | 1 | 2017-04-26 14:09 | Mechanical - Mechanical Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Improper resource allocation | Completed |  | There are an inadequate number of Cxxx project __K personnel trained and authorised to raise NCR's on the eB system. The present situation means that NCR's can only be raised by a relatively few project personnel who raise the NCR's on behalf of other persons, therefore are not in a position to track progress or witness closure of completed works.
| 03SR - Stations (RfL) | Cxxx-NCR-000331 | NCR | Plumstead Portal: Incorrectly stored building material |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-06-30 | 2017-05-25 13:36 | -36 | 2017-04-28 11:22 | Civil - Civil Engineering General | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | FOSROC __ bags damaged and exposed to environment. Also Chemical Zincrich labelled as Fis not correctly stored and container is displaying signs of corrosion.
| 03SR - Stations (RfL) | Cxxx-NCR-000332 | NCR | Connnaught FRC and Gas Membrane Installation ITP's |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-05-19 | 2017-05-05 11:26 | -14 | 2017-05-05 10:52 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Works progressed onsite for installation of Gas Membrane and FRC works prior to ITP being returned as Code 1 document. Referenced documents: Cxxx-__R-C-ITP-CR146_WS158-50001 Rev 1 Cxxx-__R-C-ITP-CR146_WS158-50006 Rev 1
| 03SR - Stations (RfL) | Cxxx-NCR-000333 | NCR | Spiral Duct - MCR ductwork support clips not identified in ITP- CER Room - Plumstead Portal |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-10-31 | 2017-10-31 08:29 | 0 | 2017-05-11 08:18 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | __ inspections carried out by Quality Inspectors identified the support bracketry used to on the installation of the spiral ducting in the CER room at Plumstead Portal was no MCR was not identified on the ITP and there was no MCR number in the document.
| 03SR - Stations (RfL) | Cxxx-NCR-000334 | NCR | By Exception procedure not folllowed for CMS installation |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2017-06-08 | 2017-06-21 09:28 | 13 | 2017-05-11 12:34 | Electrical - Cable Management | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | A quality surveillance on Cable Management Systems (CMS) took place at Cxxx Woolwich Station. During the surveillance it was identified the Contractor hadn't followed their 'By Exception process: Procedure CRL1-XRL-O7-GPD-CR001-50023 ‘Exception Construction Prior to Gate Acceptance for Station, Shafts and Portals’ for the CMS installed in the following areas: CER 731, SER 701, __R 702 and Corridor 14.
| 03SR - Stations (RfL) | Cxxx-NCR-000335 | NCR | Failed Pendulum Test - SWS Room - North Woolwich Portal. |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-07-11 | 2017-07-17 14:43 | 6 | 2017-05-12 10:25 | Civil - Wearing Course | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Wet Pendulum test in SWS (771) room failed. Platform level; North Woolwich Portal.
| 03SR - Stations (RfL) | Cxxx-NCR-000336 | NCR | The agreed documentation for brickwork benchmark does not include mastic sealant. East box, Woolwich Station |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-06-17 | 2017-06-20 10:52 | 3 | 2017-05-18 14:23 | Architectural - Brickworks/Blockworks | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The agreed benchmark for brickwork does not include mastic. Mastic was covered at a later date where a seperate benchmark was agreed but no supporting documentation was issued. This documentation has to be issued to show the operatives where the benchmark is locateds so they can ensure the physical properties of their workmanship reach the required standard.
| 03SR - Stations (RfL) | Cxxx-NCR-000337 | NCR | __ checks for brickwork have not been completed - East Box, Woolwich Station |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-06-17 | 2017-06-09 11:01 | -8 | 2017-05-18 14:32 | Architectural - Brickworks/Blockworks | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | __ checks for brickwork have not been completed on forms BMS15-F10. Individual Bay Sheets have not been signed off by Lee Marley and __. One final sign-off sheet encompassing an entire elevation is the only one with CRL sign-off - a visual check only.
| 03SR - Stations (RfL) | Cxxx-NCR-000338 | NCR | Tools and materials stacked against finished ductworks - Ground floor, East Box Woolwich Station. |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-06-17 | 2017-06-19 09:27 | 2 | 2017-05-18 15:27 | Electrical - General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper storage of material | Completed |  | Electricians tools and materials stacked against finished ductworks - Corridor 71 - East box Ground Floor, Woolwich Station. No materials or tools should be stored against finished works as this could cause damage and unnecessary re-works and delays to the programme.
| 03SR - Stations (RfL) | Cxxx-NCR-000339 | NCR | Use of Non-MCR approved material (reinforcing steel) - Connaught. |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-06-18 | 2017-06-07 07:59 | -11 | 2017-05-19 10:05 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Reinforced steel is being used on site but the MCR is not approved - Doc Number Cxxx-__R-C-MCR-CR146_WS158-50021
| 03SR - Stations (RfL) | Cxxx-NCR-000340 | NCR | Use of Non- MCR approved material (Mould Oil) - Connaught. |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-06-18 | 2017-06-08 09:15 | -10 | 2017-05-19 10:12 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Mould oil used on this site does not have MCR approval. The document number is Cxxx-__R-C-MCR-CR146_WS158-50035.
| 03SR - Stations (RfL) | Cxxx-NCR-000341 | NCR | Woolwich Station - West Box - Escalator Void Props Prop surrounds - finish did not match accepted sample (__ App NCR 146) |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-06-02 | 2017-05-31 08:39 | -2 | 2017-05-19 15:08 | Architectural - General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Woolwich Station - West Box - Escalator Void Props Precast surrounds - finish did not match accepted sample upon arrival to site
| 03SR - Stations (RfL) | Cxxx-NCR-000342 | NCR | Woolwich Station - West Box - Ticket Hall - Escalator Void Windposts to escalator void blockwork - Defective Welds |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-06-09 | 2017-05-31 08:41 | -9 | 2017-05-19 15:38 | Structural Engineering - Welding | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Woolwich Station - West Box - Ticket Hall - Escalator Void Windposts to escalator void blockwork During an on-site visual inspection of welds by a UKAS Accredited weld inspector of Windposts to be installed in the West Box Escalator void a number of defective welds were identified. 3no windposts were found to have defects, see images and weld report attached. 2no Type B (Dwg Cxxx-__R-S-DWG-CR147-50225) B7 & B9 - Underfilled 1no Type C (Dwg Cxxx-__R-S-DWG-CR147-50226) C5 - Underfill noted in Butt Weld
| 03SR - Stations (RfL) | Cxxx-NCR-000343 | NCR | Failed pendulum test - Non slip resistance test. Rms 666a; 663; 670 East Box (__ App NCR 00153) |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-06-30 | 2017-06-27 11:23 | -3 | 2017-05-19 15:50 | Architectural - Flooring | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Resin floor finish in Woolwich Station East Box rooms 666a; 663 & 670 failed the Pendulum test Non-slip resistance value. Room 670 was opened previously as part of Cxxx-NCR-000304, however in order to close this previous NCR it has been transferred to this one.
| 03SR - Stations (RfL) | Cxxx-NCR-000344 | NCR | Fire Damper Penetrations and insufficient gap for Ifre sealing. Woolwich Station |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-08-20 | 2017-08-10 07:37 | -10 | 2017-05-22 05:56 | Mechanical - Heating Ventilation & Air Conditioning | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | Fire Dampers have been installed in various locations throughout the Woolwich Station site with insufficient gap allowed to enable the recommended spacing for Fire seal to be installed.
| 03SR - Stations (RfL) | Cxxx-NCR-000345 | NCR | Woolwich Station - West Box - Ticket Hall - WI Beam for poster recess on South Elevation brickwork installed at incorrect level |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-06-12 | 2017-06-06 10:20 | -6 | 2017-05-22 08:25 | Architectural - Brickworks/Blockworks | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Woolwich Station - West Box - Ticket Hall The WI Beam to create the 9m poster recess on the South Elevation brickwork has been installed at the incorrect level. The beam was installed 1no course higher (approx 215mm) than proposed in the __ design, see attached markup. The original recess dimensions are shown in Section Cxxx-__R-A-DDB-CR147_WS163_Z-01053. This WI Beam provides the structural support to drill and fix a masonry support for preceding brickwork to be installed above.
| 03SR - Stations (RfL) | Cxxx-NCR-000346 | NCR | Non MCRed approved galvanised pipe for sump pump drainage |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-10-27 | 2017-11-08 10:31 | 12 | 2017-05-24 08:51 | Mechanical - Public Health Engineering | 5000 |  | Planning | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Sump pump pressurised drainage pipework not MCR approved. The only MCR that has been approved for the pressurised sump pipework installation is __ steel reviewed under CRL-MCR-002969. What has been installed is Prakash Surya manufactured pipe.
| 03SR - Stations (RfL) | Cxxx-NCR-000347 | NCR | WOO West Box - Water Leakage into CER Room |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-08-30 | 2017-07-11 15:00 | -50 | 2017-06-01 10:16 | Civil - Drainage | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Due to incomplete works of completing all the permanent bunds on the Mezz Level Roof above the CER room there was water leakage into the CER Room and other areas at Basement Level across the Bank Holiday weekend which saturated the Ply and Cordex floor protection following heavy rainfall. Rainfall had flowed through Mezz Level penetrations down a riser at Ticket Hall Level to Basement Level.
| 03SR - Stations (RfL) | Cxxx-NCR-000348 | NCR | Inadequate mechanical protection of MAP Dampers - Room 777 East Box |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-07-01 | 2017-07-04 12:13 | 3 | 2017-06-01 13:55 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Inadequate mechanical protection of MAP Dampers installed in the floor slab of room 777 East Box. All equipment installed in this project requires adequate mecahincal protection until brought into service.
| 03SR - Stations (RfL) | Cxxx-NCR-000349 | NCR | Woolwich Station - West Box - Escalator Void - Precast Concrete Prop Surrounds - Design does not suit brick gauge on site |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-07-07 | 2017-06-09 10:59 | -28 | 2017-06-07 15:02 | Structural Engineering - Pre-cast | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | PCC Prop surrounds delivered to site do not suit brick gauging against the previously installed props in the escalator void due to incorrect design. The units have been fabricated as per the accepted drawing, however this design drawing did not take into account the change to 4no segments instead of 2no or the as-built tolerance of the prop and the surrounding brickwork.
| 03SR - Stations (RfL) | Cxxx-NCR-000350 | NCR | North Woolwich Portal - I&E Stairs - Non-conforming grout cubes |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-07-08 | 2017-06-08 13:53 | -30 | 2017-06-08 12:29 | Structural Engineering - Structural Engineering - General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | NWP I&E Stairs Cubes made for grouted couplers in the Westbound track capping beam have not reached the specified strength. The final 56 day cube results for compressive strength are 44.6 N/mm2 and 44.9 N/mm2. The concrete specified for the capping beam is C40/50
| 03SR - Stations (RfL) | Cxxx-NCR-000351 | NCR | Woolwich Station - West Box - Ticket Hall Screed incorrect level |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-07-14 | 2017-06-20 11:00 | -24 | 2017-06-14 07:27 | Architectural - Flooring | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Screed in West Box Ticket Hall installed to wrong level. This will have a knock on effect on the preceding trades (Terrazzo tiling). The screed has been installed between 3-10mm above finsihed screed level in places.
| 03SR - Stations (RfL) | Cxxx-NCR-000352 | NCR | Incorrect Installation of Cxxx IP Rated Junction Box |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-09-18 | 2017-06-26 09:38 | -84 | 2017-06-20 14:48 | Communications and Control Systems - CCTV | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | We recently discovered that one of the Cxxx free issue CCTV – PA/VA – Door Contact Junction Boxes (JB) had been installed incorrectly and has meant that through this has altered the design of the JB. These JB are Ingress Protection Rated (IP) and as such come with a mounting arrangement which means that after installation the IP rating is maintained. It has come to light that one and potentially more of these JB’s has had an additional set of fixing holes drilled into the backing of the housing to allow for fixing and then screwed to the wall without an IP washer meaning the IP rating hasn’t been maintained. The JB’s not been IP rated isn’t the issue as these are installed internally and in rooms where IP rating isn’t a requirement, the issue is that the product has been altered and installed in an incorrect procedure.
| 03SR - Stations (RfL) | Cxxx-NCR-000353 | NCR | Damage to Air Handling Unit Sections |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-09-25 | 2017-10-12 12:59 | 17 | 2017-06-27 13:24 | Mechanical - Heating Ventilation & Air Conditioning | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Some air handling unit sections were damaged during the offloading and movement of the sections into their allocated rooms/locations. The damage includes: AHU W01 - Fan front face panel AHU W02 - Top panel of the fan and filter block AHU E02B - Lower section filter door
| 03SR - Stations (RfL) | Cxxx-NCR-000354 | NCR | Connaught CER Installation Drawing Status |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-08-07 | 2017-08-18 08:27 | 11 | 2017-07-05 15:50 | Mechanical - Heating Ventilation & Air Conditioning | 5000 |  | Documentation and Records | Rework | 3 (3-6k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | In order to achieve the Connaught CER SLD handover date, installation to PX status drawings has commenced for the Support Building, CER. It is noted the drawings used for installation will be IFC, however, the contractor notes the duration of time between obtaining such copies and requirements for installation results in 'hard copy' drawings with the C status omission. The latest RiR Cxxx-__R-Z-LRG-CR146_WS158-50003 (Rev 4.0) shows IFC status for the service drawings aforementioned.
| 03SR - Stations (RfL) | Cxxx-NCR-000355 | NCR | AHU and damper not protected |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-07-25 | 2017-07-18 11:49 | -7 | 2017-07-04 11:04 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | The installed AHU-W02 located in HRU 763 on Level +1 at West Box has not been protected. The installed damper mounted through the floor of HRU 764 on Basement -1 at West Box has not been protected.
| 03SR - Stations (RfL) | Cxxx-NCR-000356 | NCR | Woowlcih Station - West Box - Escalator Void Soffit - Out of tolerance |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-08-06 | 2017-07-14 09:41 | -23 | 2017-07-07 06:16 | Structural Engineering - Concrete Member | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Woolwich Station - West Box - RC Soffit slab above escalator void installed to wrong level. This will have an effect on the subsequent acoustic panels installation on the soffit of escalator void. The slab was poured out of tolerance of up to 25mm below soffit design level in some areas.
| 03SR - Stations (RfL) | Cxxx-NCR-000357 | NCR | Proceeding with works on the Escalator Soffit Installation (Phase 1) without an accepted ITP & MCR |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-10-06 | 2017-10-09 11:39 | 3 | 2017-07-08 11:18 | Architectural - Ceilings & Soffits | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Works on the escalator soffit installation by the contractor __ commenced without both an approved ITP (Cxxx-__R-Y-ITP-CR147-50011) and an unapproved supporting document (Cxxx-__R-Y-MCR-CR147-50020). The situation with the MCR was caused late design change utilising HKD push-in anchors. All MCR's and Supporting Documents are now approved.
| 03SR - Stations (RfL) | Cxxx-NCR-000358 | NCR | WOO - Doors - Incorrect F2 Design Door Installation (East Box Sub Basement) |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-06-04 | 2017-12-20 13:49 | -166 | 2017-11-16 13:18 | Architectural - Doors | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Doors 3-85a 3-86a and 3-791 in East box Basement Level were installed as per __ __ F2 Drawings Cxxx-__R-C-DWG-CR147-50088 Cxxx-__R-C-DWG-CR147-50089 & Cxxx-__R-C-DWG-CR147-50100 respectively
| 03SR - Stations (RfL) | Cxxx-NCR-000359 | NCR | No process for accepting a room from the transition of Civils to MEP |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-02-28 | 2018-02-22 13:15 | -6 | 2017-07-11 14:16 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Despite recent discussions within the __ quality team there is still no process for accepting a room from the transition of Civils to MEP team. Despite the __ quality team attending site before CRL attendance. This is a requirement on all ITPs
| 03SR - Stations (RfL) | Cxxx-NCR-000360 | NCR | FCU taken down by others in Room 801 West Box |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-10-18 | 2017-10-31 15:42 | 13 | 2017-07-20 08:11 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient surveillance of subcontractors | Completed |  | An installed Fan Coil Unit and corresponding fixings and bracketary has been taken down by others in West Box Room 801. The Fan Coil Unit has been left on the floor, please see attached photos.
| 03SR - Stations (RfL) | Cxxx-NCR-000361 | NCR | Connaught - Pile No. 59 out of position |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-09-26 | 2017-09-20 13:39 | -6 | 2017-09-12 12:45 | Civil - Structural Engineering | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Following pile installation at Connaught as-built survey found that pile 59 highlighted in the attached sketch was out of position and out of tolerance. Installed position given by the below figures; Easting: 0.012 (12mm) Northing: 0.317 (317mm) Height: This was within Tolerance (please see attached sketch)
| 03SR - Stations (RfL) | Cxxx-NCR-000362 | NCR | Woolwich Station - West Box North Elevation Steelwork - No associated documentation prior to starting work |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-09-13 | 2017-08-03 11:08 | -41 | 2017-08-02 15:46 | Architectural - Brickworks/Blockworks | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Metalwork sub-contractor installed RHS beam and fixings onto West Box External North Elevation without approved ITP and associated MCRs.
| 03SR - Stations (RfL) | Cxxx-NCR-000363 | NCR | Damper access impeded by CMS |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-02-28 | 2017-11-10 08:37 | -110 | 2017-08-02 08:26 | Electrical - Cable Management | 6000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Supervision - Insufficient supervision | Completed |  | CMS has been not installed to approved drawings causing clashes with ductwork and access panels to duct hatches. This will impair the maintainability of the dampers and their actuators in various location throughout this station. See attached drawing Cxxx-__R-E-DDD-CR147_WS163_1-25002 as example
| 03SR - Stations (RfL) | Cxxx-NCR-000364 | NCR | WOO - East Box - Gr Floor Level - Room 776 - Out of tolerance Screed / Resin Flooring. |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-03-16 | 2017-11-16 16:32 | -120 | 2017-11-16 10:24 | Architectural - Flooring | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Located on the East Box Ground Level a previously installed wall which divided rooms (776/761) has been removed. Upon recent inspection, it was noted that there was a clear visual difference in levels of screed where the wall in question was demolished which does not comply with Cxxx-__R-C-ITP-CR147-50003 Rev 5 Inspection Point 5. The Construction Assurance Manager and Package Engineer for Screeding check the screed tolerance using a spirit level and tape measure as it was very clear there was an issue in particular within the footprint of the demolished wall running North to South. The workmanship by the Contractor TCS of the repair is was identified to be unsatisfactory, there was no saw cuts present which is what one would expect to see on such a repair. The repair seemed to be confined to the footprint of the demolished blockwork wall. The room is on average 5mm out tolerance with one small 15mm out of tolerance where the wall separating the rooms previously was. Resin was then applied to the flooring before CRL had the opportunity to check the floor screed level.
| 03SR - Stations (RfL) | Cxxx-NCR-000365 | NCR | Failure to follow ITP Intervention Points - PCC Panel Production for Ticket Hall Main Entrance |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-12-06 | 2017-10-10 13:56 | -57 | 2017-08-08 14:14 | Structural Engineering - Pre-cast | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | It had been brought to the attention of the Cxxx Construction Assurance Team that multiple actions at 'Intervention Pre Construction Hold Points had not been completed on the 'Inspection Test Plan - __ Entrance Panels - Manufacture', eB Ref, Cxxx-__R-A-ITP-CR147-50009 Rev 1.0.
| 03SR - Stations (RfL) | Cxxx-NCR-000366 | NCR | Use of Gaslvanised Lintels in Substation at Plumstead Portal |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-10-07 | 2017-08-15 12:30 | -53 | 2017-08-08 07:55 | Civil - Civil Engineering General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | In order to achieve the handover dates for the Plumstead Portal Substation Transformer Bays and to allow for delivery and installation of the transformers on time galvanised lintels were installed to the builders work openings to these areas.
| 03SR - Stations (RfL) | Cxxx-NCR-000369 | NCR | Fire Main Hydrant System Installation without approved ITP in place - Plumstead Portal |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-12-27 | 2017-10-31 14:56 | -57 | 2017-09-28 12:08 | Mechanical - Public Health Engineering | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | Installation works have been carried out on the Fire Main Hydrant system at Plumstead Portal
| 03SR - Stations (RfL) | Cxxx-NCR-000370 | NCR | Connaught: No Approved Code 1 MCR at the point of inspection for __ Wall Ties |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-11-07 | 2017-08-23 08:05 | -76 | 2017-08-09 13:52 | Architectural - Brickworks/Blockworks | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Following an Inspection by the CRL Architect on the 07-08-17 for External Brick sample Panel for Connaught Court Yard it found that there was __ Wall Ties in use without an Approved Code 1 MCR in place.
| 03SR - Stations (RfL) | Cxxx-NCR-000371 | NCR | PLU Substation: Brick Mortar Dust covering LV Switching Gear |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-12-10 | 2017-11-23 09:53 | -17 | 2017-08-12 12:34 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | Cxxx have failed to provide a dust free environment for the LV Switchgear. Some brick works carried out external to the room has inadvertently blown dust inot the room through an unsealed opening in the blockwork brick clad wall.
| 03SR - Stations (RfL) | Cxxx-NCR-000372 | NCR | North Woolwich Portal |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-10-20 | 2017-11-10 08:50 | 21 | 2017-08-16 16:31 | Systems - Drainage/Pumping Systems | 3000 |  | Design | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | The public health services, in particular rainwater and condensate drainage show dissonance between installation and drawing representation. Deviation from the public health drawings occurred due to electrical and public health service in-congruence.
| 03SR - Stations (RfL) | Cxxx-NCR-000373 | NCR | Elevation of Light Fittings - 731 CER Room - East Box |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-10-16 | 2017-11-10 08:41 | 25 | 2017-08-17 10:21 | Electrical - Lighting | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | __s- It has become apparent that Luminaire elevation in CER Room (731) is at 2870mm AFFL as detailed in Dwg Cxxx-__R-E-DDA-CR147_WS163_3-82201 (Lighting setting out details) state all luminaires should be mounted at 2800mm. Dwg Cxxx-__R-E-DDA-CR147_WS163_3-22001 shows luminaires should be mounted at 2400mm AFFL.
| 03SR - Stations (RfL) | Cxxx-NCR-000374 | NCR | Random Galvanising Spray Paint to the Installed Ductwork |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-09-18 | 2017-10-10 07:36 | 22 | 2017-08-21 12:40 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | In the East Box Basement Level FAN II - Room 778, the ductwork that connects to the AHU has been sprayed with Galvanised paint over the flat duct surface, the ductwork at this point required no spray paint, and is not required sprayed for any reason.
| 03SR - Stations (RfL) | Cxxx-NCR-000375 | NCR | Protection of Open Ends to Ductwork |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-09-19 | 2017-10-10 13:31 | 21 | 2017-08-22 05:08 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Ductwork sections awaiting installation on site have unprotected open ends.
| 03SR - Stations (RfL) | Cxxx-NCR-000376 | NCR | Ductwork Materials Storage on Site |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-09-19 | 2017-10-11 14:07 | 22 | 2017-08-22 05:36 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper storage of material | Completed |  | Storage of ductwork in general across all sites as this deviates from the stipulated procedure in the code 1 GMS.
| 03SR - Stations (RfL) | Cxxx-NCR-000377 | NCR | Access to Motorised Fire Damper - East Box Corridor Ground Floor Battery Room 783 |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-12-20 | 2017-12-12 15:08 | -8 | 2017-08-22 06:15 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Crossrail are concerned regarding the access to the motorised fire damper from the corridor to the Battery Room 783, this is impeded by the Electrical trays installed below the damper.
| 03SR - Stations (RfL) | Cxxx-NCR-000378 | NCR | Earth tray obscures refrigerant pipework |  | Contr | SKC | WOO - Woolwich Station (East) |  | 2017-11-23 | 2017-11-29 09:18 | 6 | 2017-08-25 08:12 | Electrical - Earthing & Bonding | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Earth tray has been installed at low level in the West Box Mezzanine plantroom. This is not shown on the model or on any drawings. Due to this tray position, alternative route / detail for the refrigerant pipework required.
| 03SR - Stations (RfL) | Cxxx-NCR-000379 | NCR | NWP - C32/40 Concrete used for LV and Comm's Chambers |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-12-22 | 2017-09-05 15:06 | -108 | 2017-08-24 15:22 | Structural Engineering - Concrete Member | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other management problem | Completed |  | LV004, LV005 were installed using an unapproved ST4 mix due to the mixes not being approved at that time. LV002, LV003 and COM04 were installed using the approved C32/40 Concrete at North Woolwich afterwards.
| 03SR - Stations (RfL) | Cxxx-NCR-000380 | NCR | WOO - Commencement of works without approved documentation (__) - System S05d. |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-12-22 | 2017-10-18 15:04 | -65 | 2017-08-24 15:45 | Architectural - Finishes | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Works on the escalator void wall panels installation by the contractor __ commenced without: - an approved ITP [Cxxx-__R-Y-ITP-CR147-50012]; - an approved MCR for the system S05d (MCR wasn’t submitted to __ yet); - C01 drawings [Cxxx-__R-Y-DWG-CR147-50180 Rev P01]; - an approved Structural check report [Cxxx-__R-Y-RGN-CR147-50025];
| 03SR - Stations (RfL) | Cxxx-NCR-000381 | NCR | Plumstead Portal - Substation Drainage Manhole Covers - Failed concrete cube results |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-09-30 | 2017-09-25 14:00 | -5 | 2017-08-31 12:30 | Structural Engineering - Concrete Member | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Gen3 S1 concrete used for manholes at the Plumstead Sidings Substation has failed to achieve design strength of 20N/mm2 after 56 days. Cube results and locations attached.
| 03SR - Stations (RfL) | Cxxx-NCR-000383 | NCR | Woolwich Station - East Box - Rm 781 Incomplete door swing due to finish floor height |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-03-31 | 2018-03-05 15:33 | -26 | 2017-09-06 13:26 | Architectural - Flooring | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | On the East Box Ground Level room 781, the __ __ permanent door which has been installed, does not open fully due to incorrect screed level. The door only opens 600mm from the closing position (furthest point of the swing) as shown in the attached mark up.
| 03SR - Stations (RfL) | Cxxx-NCR-000384 | NCR | Cable Gland too close to panel structure (TXB-NOW/LVSB/B) SWA B001 - North Woolwich Portal |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-10-07 | 2017-10-11 12:00 | 4 | 2017-09-07 13:01 | Electrical - General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | Cable gland terminated too close to panel structure. The position of the cable gland prevents adequate clearance between the panel fixing bolts/panel structure.
| 03SR - Stations (RfL) | Cxxx-NCR-000385 | NCR | Installation of Non MCR Approved Galvanised Steel Pipework for Fire Main |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-01-31 | 2018-01-29 16:03 | -2 | 2017-09-07 15:13 | Mechanical - Public Health Engineering | 60000 |  | Documentation and Records | Rework | 2 (6-60k) | Complete | Material/Preservation Problems - Other | Completed |  | Installation of Non MCR approved gavlanised steel pipe work on the Fire Main System in East and West Box (all areas); Woolwich Station
| 03SR - Stations (RfL) | Cxxx-NCR-000386 | NCR | CMS inhibiting Cxxx Actuators Rm 905 Ground Level - East Box |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-12-15 | 2017-12-15 14:10 | 0 | 2017-09-11 10:38 | Electrical - General | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | CMS has been installed too close to the Cxxx Actuator to allow full operational access.
| 03SR - Stations (RfL) | Cxxx-NCR-000387 | NCR | AHU unprotected on West Box Mezzanine |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-12-11 | 2017-12-08 09:24 | -3 | 2017-09-12 08:26 | Mechanical - Heating Ventilation & Air Conditioning | 3000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | AHUs on West box mezzanine level are unprotected with evidence of material and tool storage inside the AHU compartments. There are also open pipe ends and damage to coils. Please see attached photos.
| 03SR - Stations (RfL) | Cxxx-NCR-000388 | NCR | North Woolwich Portal - Incorrect pull-out test requirement for lifting of waler beam |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-10-14 | 2017-09-18 10:27 | -26 | 2017-09-14 14:53 | Structural Engineering - Testing | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | __ had an approved temporary works scheme in place for the removal of the concrete sections that were part of the old waler beam that obstructed the installation of the drainage at the North of the MEP Building. The RAMs and lift plan were being developed concurrently with the temporary works document, as the time frame was tight, due to the road closure elapsing at the end of August 2017. __ Construction collaborated with __ Concrete cutting to develop the RAMs, __ Concrete Cutting added their section into the RAMs, which noted a pull out test of 25kN prior to lifting. This was above the approved temporary works calculation of 12.66kN (~13kN) which had been checked and approved by __. As a result, the pull out test was not undertaken to 25kN, only the 13kN listed in the approved TW document prior to lifting of the waler beam.
| 03SR - Stations (RfL) | Cxxx-NCR-000389 | NCR | Quality of galvanised pipework |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-12-19 | 2017-12-12 12:22 | -7 | 2017-09-20 14:54 | Mechanical - Piping | 3000 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Lack or improper material identification and traceability | Completed |  | The galvanising on the installed fire main pipework at West Box Basement -2 is very poor. There is pitting and debonding occurring over the entire length of the pipe on all sections inspected both in storage and installed.
| 03SR - Stations (RfL) | Cxxx-NCR-000390 | NCR | Plumstead Portal - Brickwork - Misalignment of brickwork joints |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-11-01 | 2017-10-09 10:05 | -23 | 2017-10-02 10:41 | Architectural - Brickworks/Blockworks | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Vertical joints of brickwork installed on 27/09/17 are out of alignment with previous sections installed, up to 20mm in some areas. Quality of workmanship outside of the agreed benchmark and Architectural specification.
| 03SR - Stations (RfL) | Cxxx-NCR-000392 | NCR | Plumstead Portal - LV Route Change from ducts to troughs |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-12-31 | 2017-11-08 11:44 | -53 | 2017-10-03 06:51 | Civil - Utilities Engineering | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | LV cable ducts between LV7 and LV8 chamber have been installed as per CRL Design drawing Cxxx-OVE-U-DDA-CR148_1-80501. Due to the steepness of gradient between these two chambers, a joint which is located on the transition is found to be open within the coupler after a CCTV survey was carried out. As these ducts are not design to be watertight and the LV cables are not designed to be submerged in water continuously, FCD (Cxxx-FCD-000569) was approved to replace the entire duct run with a trough route.
| 03SR - Stations (RfL) | Cxxx-NCR-000393 | NCR | WOO - East Box - Gr Floor Level - Room 578 - Out of tolerance Screed / Resin Flooring. |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-02-01 | 2017-11-10 08:45 | -83 | 2017-10-04 07:45 | Architectural - Flooring | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Located on the East Box Ground Level a previously installed wall which divided rooms has been removed (Room 578). This wall was removed as per Cxxx-FCD-000472. Upon recent inspection, it was noted that there was a clear visual difference in levels of screed where the wall in question was demolished which does not comply with Cxxx-__R-C-ITP-CR147-50003 Rev 5 Inspection Point 5. The Construction Assurance Manager and Package Engineer for Screeding check the screed tolerance using a spirit level and tape measure as it was very clear there was an issue in particular within the footprint of the demolished wall. See attached photos.
| 03SR - Stations (RfL) | Cxxx-NCR-000394 | NCR | Back Falling Pipe and Rodding Eye Tee is Wrong Way Round - North Woolwich Portal |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-10-24 | 2017-11-01 16:21 | 8 | 2017-10-10 08:15 | Mechanical - Public Health Engineering | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Rain water pipework has been installed with the fall in the wrong direction.
| 03SR - Stations (RfL) | Cxxx-NCR-000395 | NCR | Pipe support studding Installed through CMS supports - North Woolwich Portal |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-01-04 | 2017-12-12 09:00 | -23 | 2017-10-06 09:30 | Mechanical - Public Health Engineering | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Studding for Pipe support bracketry has been installed passing through CMS support brackets.
| 03SR - Stations (RfL) | Cxxx-NCR-000396 | NCR | Connaught - Cracked Wi System Column Blocks |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-10-23 | 2017-10-11 09:03 | -12 | 2017-10-09 17:00 | Architectural - Brickworks/Blockworks | 500 |  | System Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | It was identified onsite that several Wi System blocks one particular column had cracked following install and curing.
| 03SR - Stations (RfL) | Cxxx-NCR-000397 | NCR | WOO - SOR Room 751 - Non complaint finishes / reworks |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-05-29 | 2018-05-04 13:08 | -25 | 2017-10-18 15:39 | Architectural - General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | It has been identified that SOR Room 751 on the West Box Ticket Hall had it6s walls painted using an LUL Approved mioneral based paint produced by Keim - this wall finish did not comply with the Works Infiormation. The specified wall finish within this location was suppose to be a plaster board finish (IWS-109)
| 03SR - Stations (RfL) | Cxxx-NCR-000398 | NCR | Light fitting clashing with Ducting - Room 779 Basement Level Fan Room 3 East Box - Woolwich Station |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-12-11 | 2017-12-08 09:44 | -3 | 2017-10-12 07:17 | Electrical - Lighting | 3000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | A light fitting is clashing with fire rated ducting in Room 779. This ducting will require a minimum of 50mm lagging and there must be a minimum of 200mm between this light fitting and services (i.e. ducting; etc.).
| 03SR - Stations (RfL) | Cxxx-NCR-000399 | NCR | WOO - East Box - Basement Level - Room 780 - Out of tolerance Screed / Resin Flooring. |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-11-16 | 2017-10-31 11:35 | -16 | 2017-10-17 10:29 | Architectural - Flooring | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Located on the East Box Basement Level a previously installed wall which divided rooms has been moved (Room 780). This wall was moved as per 'Cxxx-FCD-000429 - Woolwich Station - East Box PFR Rearrangement - Blockwall Relocation'. Upon inspection, it was noted that there was a clear visual difference in levels of screed where the wall in question was demolished which does not comply with Cxxx-__R-C-ITP-CR147-50003 Rev 5 Inspection Point 5. The Construction Assurance Manager and Package Engineer for Screeding check the screed tolerance using a spirit level and tape measure as it was very clear there was an issue in particular within the footprint of the demolished wall. See attached photos.
| 03SR - Stations (RfL) | Cxxx-NCR-000400 | NCR | SWA Visible through Gland Compression Seal BO09 - North Woolwich Portal |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-02-23 | 2018-01-25 14:12 | -29 | 2017-10-18 12:49 | Electrical - General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Cable BO09 - HV Battery Charger - NWP. The SWA is visible through the compression section of the cable gland.
| 03SR - Stations (RfL) | Cxxx-NCR-000401 | NCR | SWA Cable Shroud does not form a tight seal around cable BO09 - North Woolwich Portal |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-02-23 | 2018-01-25 14:14 | -29 | 2017-10-18 13:13 | Electrical - General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Cable BO09 - HV Battery Charger supply cable - NWP. The cable shroud has been cut incorrectly thus not achieving a seal between the shroud and the cable.
| 03SR - Stations (RfL) | Cxxx-NCR-000402 | NCR | SWA Outer Sheath Damaged - BO09 HV Battery Charger - North Woolwich Portal |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-02-16 | 2018-01-22 14:01 | -25 | 2017-10-18 13:42 | Electrical - General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | SWA Cable BO09 (Supply cable to HV Battery Charger) is damaged and had an inadequate repair carried out by the use of PVC Insulation tape.
| 03SR - Stations (RfL) | Cxxx-NCR-000403 | NCR | Woolwich West Box - Room 751 SOR - Proceeding with works on wall finishes without documentation acceptance in place. |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-01-26 | 2017-11-29 11:00 | -58 | 2017-10-18 16:23 | Architectural - Walls | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Rework on Woolwich West Box - Room 751 SOR proceeded over the weekend on the 14/10/17 without any documentation approvals in place, ie ITP & MCR or acceptance of Cxxx-FCD-00403.
| 03SR - Stations (RfL) | Cxxx-NCR-000404 | NCR | Containment and Cabling impeding access to Motorised Fire Damper - Room 777 East Box |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-11-29 | 2019-10-25 14:23 | -35 | 2017-10-24 08:28 | Electrical - General | 3000 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Access to Motorised Fire Damper is impeded by installation of containment and cabling in room 761.
| 03SR - Stations (RfL) | Cxxx-NCR-000405 | NCR | CMS Overhanging Fire Rated Duct restricting access to Inspection Hatch - Room 780 (PFR) East Box. |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-05-31 | 2018-04-10 12:24 | -51 | 2017-10-24 10:04 | Electrical - General | 3000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | CMS route impedes access to the Fire Rated Duct making access to the Inspection Hatch difficult.
| 03SR - Stations (RfL) | Cxxx-NCR-000406 | NCR | CMS Installed too close beneath ductwork to allow reasonable access to Fire Rated Ductwork - Corridor 71 (CIR-S) |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-05-31 | 2018-04-13 13:29 | -48 | 2017-10-24 11:09 | Electrical - General | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Electrical CMS installed beneath Fire Rated Ductwork in such a manner at to take away reasonable access to install lagging.
| 03SR - Stations (RfL) | Cxxx-NCR-000407 | NCR | Supporting Framework for DX Units Partially Removed and Damaged. Rooms 662 & 662 West Box |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-04-20 | 2018-04-12 16:56 | -8 | 2017-10-25 14:45 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Threaded rod hangers have been bent out of shape and taped back to existing CMS supports. These rods must be replaced.
| 03SR - Stations (RfL) | Cxxx-NCR-000408 | NCR | Access to Inspection Hatch either side of ESD impaired by CMS support hanger - INS I 631 West Box |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-06-29 | 2018-06-22 11:33 | -7 | 2017-10-25 15:15 | Electrical - General | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | CMS unistrut support hanger impairs access to inspection hatch in ductwork. The __ hanger is situated directly in front of the access panel thus preventing visual inspection of the internal section of the ductwork.
| 03SR - Stations (RfL) | Cxxx-NCR-000409 | NCR | FCU removed and re-installed in wrong orientation - Room 801 West Box |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-05-31 | 2018-05-17 10:33 | -14 | 2017-10-26 09:21 | Mechanical - Heating Ventilation & Air Conditioning | 1500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | FCU - W04 in Room 801 (West Box) was removed to enable installation of Busbars then re-installed in the wrong orientation, impacting on the fresh air supply ducting and condensate drain pipe.
| 03SR - Stations (RfL) | Cxxx-NCR-000410 | NCR | Installation of Remaining Sections of Ductwork Installation Impeded by CMS and CMS supports - Corridor outside Room 731 (CER) |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-05-30 | 2018-04-13 13:33 | -47 | 2017-10-26 10:10 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Installation of the remaining sections of ductwork is greatly impaired by the installation of Ladder Rack and supporting bracketry.
| 03SR - Stations (RfL) | Cxxx-NCR-000412 | NCR | WOO - System S05d - Scuffed Escalator Soffit Panels |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-10-31 | 2019-08-23 10:24 | -69 | 2017-10-26 14:01 | Architectural - Finishes | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following a final inspection of System S05d with CRL a scuff mark was found on one of the panels which CRL Architects have requested is replaced when the contractor returns to site when they undertake the second phase of the installation works for this system. The defective cladding panel is located on the soffit at lower escalator area. Please see attached: Inspection Record with CRL comments; Pictures; Markup of installation drawing and C01 drawing.
| 03SR - Stations (RfL) | Cxxx-NCR-000414 | NCR | Rainwater Drain Pipe and Condensate Drain Pipe re-routed without formal approval - NWP |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-01-28 | 2018-01-27 12:56 | -1 | 2017-10-30 15:38 | Mechanical - Public Health Engineering | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Rainwater Drain pipes and Condensate Drain pipes have been re-routed without formal CRL Approval. Additional CMS installed impeding installation of Rainwater and Condensate Drain pipes as per approved design.
| 03SR - Stations (RfL) | Cxxx-NCR-000415 | NCR | WOO - SOR Room 751 - CMS covered in mortar from rendering works to rectify non compliant wall finish |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-02-09 | 2018-02-19 09:33 | 10 | 2017-11-01 17:46 | Architectural - Walls | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | Following rendering works captured of the non-compliant wall finished captured within Cxxx-NCR-000397 it was found that operatives responsible for the rendering works on the weekend of the 14/10/17 were very careless and did not adequately cover the CMS within the SOR Room 751 leaving mortar splashed across the CMS.
| 03SR - Stations (RfL) | Cxxx-NCR-000416 | NCR | Unauthorised drilling of holes in Radio Panel Gland Plate - NWP |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-06-01 | 2018-06-01 10:43 | 0 | 2017-11-03 08:41 | Electrical - General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | A hole was drilled in the gland plates of both Radio Panels located in the CER room at North Woolwich Portal. The contractor responsible for these panels specifies that there should be no unauthorised holes drilled in these panel. The panels were supplied with pre-drilled holes to mitigate the risk of damage to internal components by swarf from drillings and hole-cutting.
| 03SR - Stations (RfL) | Cxxx-NCR-000422 | NCR | PLU - Defective Blockwork / Cracks to mortar due to load from CMS Install - BAT 667 Room |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-02-11 | 2018-01-31 16:08 | -11 | 2017-11-03 09:44 | Architectural - Walls | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Cracks to mortar joints within a blockwork wall within the BAT 667 Room in Plumstead Headhouse his cracking appears to be caused by the loading of the cantilever brackets installed for CMS.
| 03SR - Stations (RfL) | Cxxx-NCR-000423 | NCR | Dampers missing on Standby/Duty AHUs |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-03-30 | 2018-03-26 07:26 | -4 | 2017-11-08 10:36 | Mechanical - Heating Ventilation & Air Conditioning | 3000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Motorised Volume Control Dampers are not installed on the Standby/Duty AHUs in East and West Box (AHU-E02A, AHU-E02B, AHU-W03A, AHU-W03B), missing dampers are highlighted on attached schematic.
| 03SR - Stations (RfL) | Cxxx-NCR-000424 | NCR | Platform Support Rooms dampers clash with cladding |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-04-30 | 2018-04-27 10:47 | -3 | 2017-11-08 14:13 | Mechanical - Heating Ventilation & Air Conditioning | 5000 |  | Planning | Rework | 3 (3-6k) | Complete | Design Problem - Not Defined | Completed |  | 14 No. dampers in platform support rooms are not installed flush on the wall and are protruding out by 30mm, this clashes with the cladding and cladding bracketry.
| 03SR - Stations (RfL) | Cxxx-NCR-000425 | NCR | Escalator Truss Support Rebate - West Box Groung Level |  | Contr | __R | WOO - Woolwich Station (East) |  | 2017-12-08 | 2017-12-06 10:58 | -2 | 2017-11-08 11:08 | Civil - Civil Engineering General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The escalator truss requires a rebate of 300*40mm along the edge of the ticket hall slab, as shown in Cxxx-__R-M1-DWG-CR147-50048 Detail of Upper Landing Support, to accommodate the truss supports and bring the escalator floor plates in line with the rest of the ticket hall finish floor level. Cxxx-__R-S-DWG-CR147-50064 & Cxxx-__R-M1-DWG-CR147-50048
| 03SR - Stations (RfL) | Cxxx-NCR-000426 | NCR | External Manual Bypass Scratches |  | Contr | SKC | WOO - Woolwich Station (East) |  | 2018-11-16 | 2018-10-03 13:11 | -44 | 2017-11-08 15:21 | Electrical - Switchgear | 300 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Some of the UPS gear (External Manual Bypass) has been scratched during the transition of the equipment and it have been noticed today 08.11.17 when they got unwrapped. this affects, PP.Substation, P.Portal and North Woolwich Portal. Possibly it has been dragged along the floor.
| 03SR - Stations (RfL) | Cxxx-NCR-000427 | NCR | __ Pipework Installed Incorrectly - West Box PFR 779 |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-05-30 | 2018-04-20 12:59 | -40 | 2017-11-08 16:10 | Fire - Detection | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | 2 x 22mm __ pipes at the top of the 779 lift shaft in West Box are entering and exiting through a single penetration, leaving inadequate clearance for fire stopping of both pipes. There is a third pipe to be installed, so a total of 3nr penetrations will be required, 1nr for each of the pipes. Existing sleeves on the pipes are also too short and should protrude by 50mm minimum each side of the wall
| 03SR - Stations (RfL) | Cxxx-NCR-000428 | NCR | Access to Motorised Fire Dampers Impaired by Electrical Containment - SOR Rm, West Box |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-05-31 | 2018-04-24 12:41 | -37 | 2017-11-16 15:46 | Electrical - Electrical Engineering General | 3000 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Access to Motorised Fire Dampers for maintenance purposes has severely been impaired by the installation Electrical Containment.
| 03SR - Stations (RfL) | Cxxx-NCR-000429 | NCR | No Approved Benchmarking for __ Installation - Woolwich Station |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-05-01 | 2018-04-12 08:40 | -19 | 2017-11-17 08:55 | Fire - Detection | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | __ pipework has been installed on the platform level of Woolwich station without having an approved Benchmarking. A section of __ pipework needs to be completed and presented for assessment by Crossrail.
| 03SR - Stations (RfL) | Cxxx-NCR-000430 | NCR | No Access to Dampers in SMK Room (47) - West Box |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-05-30 | 2018-04-18 06:50 | -42 | 2017-11-17 09:56 | Electrical - Electrical Engineering General | 3000 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | There is no adequate access to the Motorised Fire Dampers in the SMK Room (47) due to the installation of CMS.
| 03SR - Stations (RfL) | Cxxx-NCR-000431 | NCR | Electrical Equipment Left Out In The Rain- UPS ATS |  | Contr | SKC | WOO - Woolwich Station (East) |  | 2017-12-20 | 2018-01-29 11:22 | 40 | 2017-11-20 14:12 | Electrical - LV Equipment | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper storage of material | Completed |  | electrical equipment, UPS ATS left out in the rain, without proper protection for the whole weekend (17-20 November).
| 03SR - Stations (RfL) | Cxxx-NCR-000432 | NCR | Access to Dampers is Impeded by CMS - Rm 664 (ESR1) East Box |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-05-31 | 2018-05-15 06:43 | -16 | 2017-11-21 15:32 | Electrical - General | 2000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Access to Dampers into Room 664 (ERS l) is impeded by installation of CMS.
| 03SR - Stations (RfL) | Cxxx-NCR-000433 | NCR | Access to Damper by CMS in Room 412 (MAE) West Box. |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-05-30 | 2018-05-08 06:24 | -22 | 2017-11-22 09:23 | Electrical - General | 2000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Access to Dampers outside room 412 (MAE) in the West Box Goudne floor has been impeded by the installation of CMS.
| 03SR - Stations (RfL) | Cxxx-NCR-000434 | NCR | Access to Damper impaired by installation of CMS outside room 761 West Box ground level |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-05-31 | 2018-04-24 09:54 | -37 | 2017-11-22 10:38 | Electrical - General | 2000 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Access to inpect and maintain Damper outside room 761 (MCC) ground level, West Box has been impaired the installation of CMS.
| 03SR - Stations (RfL) | Cxxx-NCR-000435 | NCR | Woolwich Station - East Box - Rm 666 Incomplete door swing due to finish floor height |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-05-30 | 2018-03-05 15:37 | -86 | 2017-11-22 11:30 | Architectural - Flooring | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | On the East Box Basement Level Room 666, the __ __ permanent door which has been installed, does not open fully due to incorrect screed level. The door only opens 600mm from the closing position (furthest point of the swing) as shown in the attached mark up
| 03SR - Stations (RfL) | Cxxx-NCR-000436 | NCR | Access to Ductwork Inspection hatches Impaired by CMS - Corridor 6, West Box |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-05-31 | 2018-04-10 12:31 | -51 | 2017-11-22 12:28 | Electrical - General | 3000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Due to the heavy congestion of services in Corridor 6 (West Box) access to Ductowrk Inspection Hatches is to be extremely restricted
| 03SR - Stations (RfL) | Cxxx-NCR-000437 | NCR | Access to Dampers Impeded by Installation of CMS - Room 663 (SRLV ll) East Box |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-06-28 | 2018-05-15 06:44 | -44 | 2017-11-22 15:35 | Electrical - General | 3000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Access to dampers into room 663 (SRLV ll) East Box is impaired by installation of CMS.
| 03SR - Stations (RfL) | Cxxx-NCR-000438 | NCR | Installation of Toilet to Unapproved drawing -NWP |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-04-30 | 2018-04-06 14:36 | -24 | 2017-11-23 10:49 | Mechanical - Public Health Engineering | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | A toilet have been installed at North Woolwich Portal without an approved drawing.
| 03SR - Stations (RfL) | Cxxx-NCR-000439 | NCR | CONN - Proceeding with work without an accepted ITP in place for Structural Fire Stopping Works |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-05-01 | 2018-04-16 11:23 | -15 | 2017-11-23 12:17 | Fire - Compartmentation | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Works at Connaught has been allowed to proceed without an ITP submitted and accepted at Code 1 by CRL on some of the SLD Rooms handed overn such as Room 404.
| 03SR - Stations (RfL) | Cxxx-NCR-000440 | NCR | WOO - Terrazo Flooring - Central Platform - Proceeding with works without code 1 accepted approvals in place. |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-04-22 | 2018-04-19 11:17 | -3 | 2017-11-23 15:59 | Architectural - Flooring | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Works has been allowed to proceed on Woolwich Station Central Platform without a series of approvals in place. Currently there is no - F2 Design - 2 Unapproved MCR's including Movement Joint & Matwell System - No signed accepted benchmark - No completed tile testing as requested by CRL's Leigh Holland on the 10/07/17
| 03SR - Stations (RfL) | Cxxx-NCR-000441 | NCR | Material used within the Works without MCR Approval for Installation of __ |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2018-02-28 | 2018-01-29 16:55 | -30 | 2017-11-30 14:51 | Mechanical - Mechanical Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | A planned Crossrail surveillance was undertaken on 29th November 2017 to look at Installation of __. During the site visit it was identified that __ Resin anchors have been installed to fix the damper flange plates to the blockwork wall. CRL-MCR-004656 was presented by the contractor to demonstrate approval for this particular fixing system. On checking eB it was found that the MCR is not approved. The accepted ITP, Cxxx-__R-M-ITP-CR147-50014, under section 2.1 requires submission and code 1 acceptance of all MCRs for materials to be installed in the works. This is a hold point for Hotchkiss and __.
| 03SR - Stations (RfL) | Cxxx-NCR-000442 | NCR | (Architectural) Failure to follow ITP Intervention Points - PCC Panel Production for Ticket Hall Main Entrance |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-06-04 | 2018-06-01 10:03 | -3 | 2017-12-05 14:47 | Architectural - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | It had been brought to the attention of the Cxxx Construction Assurance Team that multiple actions at 'Intervention Pre Construction Hold Points had not been completed on the 'Inspection Test Plan - __ Entrance Panels - Manufacture', eB Ref, Cxxx-__R-A-ITP-CR147-50009 Rev 1.0.
| 03SR - Stations (RfL) | Cxxx-NCR-000443 | NCR | No load calculations to validate and support pull testing performance of Fisher Anchors supporting FR Ductwork |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2018-04-16 | 2018-04-16 19:33 | 0 | 2017-12-11 22:53 | Mechanical - Mechanical Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | A planned Crossrail surveillance was completed on __ installation. Fisher Anchors has been installed in the soffit to support the Fire Rated Ductwork. The Fisher Anchors had been Pull Tested to 4.5kN, similar to the __ HUS3 anchors used to support the Galvanised Ductwork. Calculations were requested to support the 4.5kN Proof Loading for the Fisher Anchors. The ITP makes reference to Pull test procedure Cxxx-__R-04-GPD-CR147-50022 Revision 1.0. On checking, this procedure did not include calculations for the Fisher Anchors, only __ HUS3 to 4.5kN. A request was made for the calculations for the Fisher Anchors. None were provided. As such the installation cannot be confirmed against the required design loads. Until such time as calculations are completed and validated, and the Fisher Anchors Proof Loaded to the output requirements, the installation of the Fire Rated Ductwork is at risk. M&W Specification JY90.1306 requires loading details for all types of fixings when securing to the building fabric.
| 03SR - Stations (RfL) | Cxxx-NCR-000444 | NCR | __ resin anchors fixed into Blockwork Mortar Joints for Non and FR Ductwork invalidating ETA. Wrong system used. |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2018-04-30 | 2018-04-22 07:24 | -8 | 2017-12-11 23:01 | Mechanical - Mechanical Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | A planned Crossrail surveillance was completed on __ installation. It was observed that a __ HY200 chemical fixing system had been used to fix Damper Flange Plates into Blockwork Mortar joints ONLY where the pre fabricated holes clashed with the vertical blockwork joint (see picture). In addition, this was the same for the Fire Rated Ductwork where the system has been secured to the blockwork wall (see picture). It was stated that 6mm rods had been used with the __ HY200 System. The fixing into mortar joints was clarified with the __ Crossrail Project Engineer Representative where the following was confirmed (see email attached): - the wrong system has been used with HY200 for concrete and HY270 for blockwork - fixings are not suitable into mortar joints (additional testing required to validate as ETA void) - 6mm rods are not covered by an ETA and are typically only used for light duty applications - In addition no loading calculations had been completed for fixing into blockwork using the chemical anchor system. Furthermore, it is not known what torque had been applied with hand tightening undertaken, where resin systems are governed by the size of the anchor and resin used. JY90.3205 states that fixings should not be secured into mortar joints. The current installation is non compliant and needs further validation and assessment. As the surveillance was based on a sample, it is unknown how many areas have been installed into mortar joints with the wrong resin system. This should be investigated as part of closure to this NCR.
| 03SR - Stations (RfL) | Cxxx-NCR-000445 | NCR | not UKAS Accredited for Air Leakage Testing |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2018-02-28 | 2018-02-23 14:15 | -5 | 2017-12-20 08:48 | Mechanical - Mechanical Engineering General | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Not Defined | Completed |  | A planned Crossrail surveillance was completed on __ installation. Air Leakage test records were provided by __ and Hotchkiss. It was noted that the testing had been carried out by Hotchkiss personnel. A post surveillance request was made for Hotchkiss UKAS Schedule of Accreditation to confirm UKAS Accreditation for Air Leakage testing. It was responded that Hotchkiss are not UKAS Accredited to undertake such testing. It was further confirmed that no PMs Acceptance is in place confirming an alternative proposal to testing.
| 03SR - Stations (RfL) | Cxxx-NCR-000446 | NCR | No F2 Design Provided for Hotchkiss Angle Welded Supports for Floor Mounted Ductwork |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2018-03-30 | 2018-03-09 14:13 | -21 | 2017-12-20 08:56 | Mechanical - Mechanical Engineering General | 3000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | A planned Crossrail surveillance was completed on __ installation. It was observed that painted angles were supporting floor mounted ductwork (see photos). The supports had been welded and painted with galvanised paint with the fabrication completed by Hotchkiss. The F2 design drawings were requested for the fabricated supports; showing acceptance by __ __’s F1 Designer per the __ Design Management Plan. After multiple requests, no accepted F2 design was provided, as such it cannot be confirmed that this was in place prior to fabrication and installation.
| 03SR - Stations (RfL) | Cxxx-NCR-000447 | NCR | Intumescent Sealant (structural Fire Stopping) All Sites & Portals |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-11-29 | 2019-08-28 13:16 | -93 | 2018-01-16 15:00 | Fire - Suppression | 2900 |  | System Defect | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The CRL specified and approved __ products - C144 LUFF and intumescent sealant have been installed at Cxxx in accordance with the manufacturer’s instructions and installation details Please refer to Cxxx-__R-FCD-020012 with all information All details have been approved inspected on site and benchmarks approved Since the initial installations numerous locations have been identified where the products have cracked and or de-laminated separated from the building structure
| 03SR - Stations (RfL) | Cxxx-NCR-000448 | NCR | Intumenscent Sealant (Structural Fire Stopping) North Woolwich Portal |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-07-15 | 2018-05-14 08:23 | -62 | 2018-01-16 15:16 | Fire - Suppression | 6000 |  | System Defect | Repair | 3 (3-6k) | Complete | External Phenomenon - Other | Completed |  | The CRL specified and approved __ products - C144 LUFF and intumescent sealant have been installed at Cxxx in accordance with the manufacturer’s instructions and installation details Please refer to Cxxx-__R-FCD-020012 with all information All details have been approved inspected on site and benchmarks approved Since the initial installations numerous locations have been identified where the products have cracked and or de-laminated separated from the building structure
| 03SR - Stations (RfL) | Cxxx-NCR-000449 | NCR | Intumescent Sealant (Structural Fire Stopping) Connaught |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-11-30 | 2018-08-09 15:05 | -113 | 2018-01-16 15:21 | Environmental - Landscape | 500 |  | System Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The CRL specified and approved __ products - C144 LUFF and intumescent sealant have been installed at Cxxx in accordance with the manufacturer’s instructions and installation details Please refer to Cxxx-__R-FCD-020012 with all information All details have been approved inspected on site and benchmarks approved Since the initial installations numerous locations have been identified where the products have cracked and or de-laminated separated from the building structure
| 03SR - Stations (RfL) | Cxxx-NCR-000450 | NCR | Intumescent Sealant (Sturctural Fire Stopping) Plumstead Portal |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-11-30 | 2018-09-14 08:59 | -77 | 2018-01-16 15:27 | Fire - Suppression | 500 |  | System Defect | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The CRL specified and approved __ products - C144 LUFF and intumescent sealant have been installed at Cxxx in accordance with the manufacturer’s instructions and installation details Please refer to Cxxx-__R-FCD-020012 with all information All details have been approved inspected on site and benchmarks approved Since the initial installations numerous locations have been identified where the products have cracked and or de-laminated separated from the building structure
| 03SR - Stations (RfL) | Cxxx-NCR-000451 | NCR | Damage to Electrical Panels - Plumstead |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-11-30 | 2018-09-24 09:34 | -67 | 2018-01-17 10:26 | Electrical - LV Equipment | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | Damage to panels in room 667 in Plumstead Bypass Return Switch smashed and damage to casing on battery cabinet
| 03SR - Stations (RfL) | Cxxx-NCR-000452 | NCR | Water ingress Rm 666 Plumstead Headhouse |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-03-18 | 2018-02-23 14:38 | -23 | 2018-01-17 10:39 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Evidence of water ingress in Room 666 at Plumstead Headhouse pooling next to an electrical panel.
| 03SR - Stations (RfL) | Cxxx-NCR-000453 | NCR | Damaged termination stud fixing on 11kV/0.44kVTransformer - Plumstead |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-08-31 | 2018-08-29 08:33 | -2 | 2018-01-17 11:22 | Electrical - LV Equipment | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Damaged stud fixings and moisture ingression on transformer secondary termination chambers at Plumstead portal. Ref: Cxxx-__R-O4-RGN-CR148_PT005-50041 (Report Plumstead Substation - Sheared Studs on Cxxx Transformer (Initial Investigation
| 03SR - Stations (RfL) | Cxxx-NCR-000455 | NCR | Civils Benchmark schedule Contents Listing - Woolwich Station |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-06-18 | 2018-04-22 07:20 | -57 | 2018-01-19 10:22 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The contents of the Samples; Mock-ups; Prototypes; Test Plans and Benchmarks Schedule is not sufficiently populated with eB approved Benchmarks (Doc No: Cxxx-__R-O4-TSC-CR147-50008)
| 03SR - Stations (RfL) | Cxxx-NCR-000456 | NCR | MEP Benchmark Schedule Contens Listing - Woolwich Station |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-04-30 | 2018-04-18 06:23 | -12 | 2018-01-19 10:29 | Electrical - Electrical Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | The contents of the MEP Samples; Mock-ups; Prototypes; Test Plans and Benchmarks Schedule is not sufficiently populated with eB approved Benchmarks (Doc No: Cxxx-__R-O4-TSC-CR147-50009)
| 03SR - Stations (RfL) | Cxxx-NCR-000457 | NCR | Platform Smoke Plenum - Continuation of works over the stated ITP test length |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-03-01 | 2018-02-23 13:39 | -6 | 2018-01-30 10:21 | Mechanical - Heating Ventilation & Air Conditioning | 0 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | The installation of the platform smoke extract plenum does not follow the ITP testing parameters, Cxxx-__R-M-ITP-CR147-50022. The smoke extract plenum has not been tested before commencing with further installation.
| 03SR - Stations (RfL) | Cxxx-NCR-000458 | NCR | Incorrectly sized Support Brackets for DOO CCTV's - Platform all areas |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-05-08 | 2018-04-10 13:56 | -28 | 2018-02-07 11:17 | Communications and Control Systems - CCTV | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The support bracketry for the DOO CCTV's mounted in all areas of the Woolwich Station Platform have been manufactured to the incorrect dimension as provided by __ site engineers.
| 03SR - Stations (RfL) | Cxxx-NCR-000459 | NCR | Inadequate staffing levels - Document controllers Cxxx |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-08-18 | 2018-03-27 11:54 | -144 | 2018-02-19 10:42 | Information Management | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Improper resource allocation | Completed |  | Due to staffing issues Cxxx have a significant backlog of documentation to be uploaded to eB and BC
| 03SR - Stations (RfL) | Cxxx-NCR-000460 | NCR | Damaged Battery PP.Substation |  | Contr | SKC | WOO - Woolwich Station (East) |  | 2018-08-31 | 2018-06-29 09:04 | -63 | 2018-02-26 09:33 | Electrical - Power Distribution | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | there is a damaged battery, number 14, at the Plumstead Portal Substation
| 03SR - Stations (RfL) | Cxxx-NCR-000461 | NCR | Inadequate unistrut supports for Ductwork and CMS - Sump area East Bound Entrance |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-10-27 | 2018-10-23 14:31 | -4 | 2018-02-27 12:00 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The sump pump supply and extract ductwork and some CMS are inadequately supported. There appears to be sections of unistrut which are hanging off the wall with only a single fixing holding it in place. Ref: Observation CRL-OBS-21314
| 03SR - Stations (RfL) | Cxxx-NCR-000462 | NCR | HDK Anchors Pull-tested at incorrect values - __ - West Box Woolwich Station |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-05-04 | 2018-05-01 11:50 | -3 | 2018-03-05 09:15 | Civil - Civil Engineering General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | __ installed HILTI HKD anchors that are not mentioned in section 5.0 of the current ITP (Cxxx-__R-Y-ITP-CR147-50016 Rev 1.0) and the Method Statement (Cxxx-__R-Y-GMS-CR147-50009 Rev 1.0) for the installation of CMS housing in the West Box Ticket Hall. On the same day after installation of the anchors a pull out test by a third party entity was performed to this type of anchor with a greater pull out force than required. The HKD anchors were tested to values up to 4kN load leading to destruction when the specified value for this anchor should be of 0.5kN. (see pull-out test report attached with areas mentioned highlighted).
| 03SR - Stations (RfL) | Cxxx-NCR-000463 | NCR | Plinth-Bench Installation (C2-C3) |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-05-23 | 2018-03-29 10:53 | -55 | 2018-03-12 10:55 | Architectural - Signage | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | We installed 5nr plinths at platform level as planned, however 1nr plinth, between columns C2-C3, was sitting too high above the pit once fitted. When the pit was originally uncovered, like all other locations the team double-checked measurements, depth and level. Although all measurements, as well as the required depth were correct, we were not willing to install the plinth until the base of the pit was made good. It was not level and not in a suitable position. Pictures attached for reference.
| 03SR - Stations (RfL) | Cxxx-NCR-000464 | NCR | Lack of coordination between services and architecture in West Box SLR 316 |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-07-31 | 2018-08-08 15:09 | 8 | 2018-03-13 14:25 | Mechanical - Heating Ventilation & Air Conditioning | 6000 |  | Planning | Rework | 3 (3-6k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | The fire rated ductwork had to be changed and raised to accommodate the false ceiling to be installed in West Box SLR 316.
| 03SR - Stations (RfL) | Cxxx-NCR-000465 | NCR | Damaged refrigerant pipework lagging |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-06-12 | 2018-05-21 08:33 | -22 | 2018-03-14 10:46 | Mechanical - Heating Ventilation & Air Conditioning | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Refrigerant pipework lagging has been damaged at Plumstead Portal by other trades working around it and storing materials on top of it.
| 03SR - Stations (RfL) | Cxxx-NCR-000466 | NCR | Attenautor Plinths levels are out of tollerance TVF Rm 905 - West Box |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-05-14 | 2018-04-16 08:29 | -28 | 2018-03-15 11:11 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The Attenuator Plinths in Tunnel Fan Room 905 do not meet the tollerance required in the __ Specification Cxxx-__-H-RSP-CRG03-50011 (attached).
| 03SR - Stations (RfL) | Cxxx-NCR-000467 | NCR | Contaminated DX Pipework |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-05-21 | 2018-04-13 13:26 | -38 | 2018-03-22 09:58 | Mechanical - Heating Ventilation & Air Conditioning | 6000 |  | Damaged | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | DX Pipework on the CU-01, CU-02 and CU-07 circuits has been contaminated at North Woolwich Portal. This is due to a power failure (cause unknown at present) during the process of vacuuming the system. When the power to the pumps was cut, the vacuum within the pipework caused air and oil from the pump to be drawn into the system through the tube.
| 03SR - Stations (RfL) | Cxxx-NCR-000468 | NCR | Cracked Mastic at Movement Joint - North Woolwich Portal |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-05-31 | 2018-05-29 12:15 | -2 | 2018-03-26 08:42 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | From visual inspection of the external North Woolwich portal brickwork it appears that in some locations at the vertical control joints the mastic has detached from the brick following its contraction. __ invited structural engineer MM to inspect this. MM submitted a report stating “no cracking was visible in the wall and that the movement measured at the vertical control joints is within the acceptable limits so we can conclude that there are no issues on the structural performance of the wall”.
| 03SR - Stations (RfL) | Cxxx-NCR-000469 | NCR | Relocation of Cxxx Asset without prior formal approval - NWP |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-04-27 | 2018-04-10 13:58 | -17 | 2018-03-28 09:28 | Communications and Control Systems - General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | An RJ45 socket outlet was relocated in the CER Room in North Woolwich Portal without prior formal approval from the asset owner (Cxxx) to enable installation of a Marchalling Cabinet.
| 03SR - Stations (RfL) | Cxxx-NCR-000470 | NCR | Relocation of Cxxx Asset without prior formal approval - Plumstead Portal |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-04-27 | 2018-04-10 13:59 | -17 | 2018-03-28 09:34 | Communications and Control Systems - General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | An RJ45 socket outlet for CCTV was relocated on the Platform Area at Plumstead Portal without prior formal approval from the asset owner (Cxxx) to enable installation of Mechanical Pipework.
| 03SR - Stations (RfL) | Cxxx-NCR-000471 | NCR | Fire Rated Ductwork Insulation Workmanship |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-05-10 | 2018-04-13 13:39 | -27 | 2018-04-10 14:54 | Mechanical - Heating Ventilation & Air Conditioning | 3000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A surveillance was carried out looking at the fire rated ductwork insulation. A report was written showing clashes with bracketry and conduits and with parts of the insulation not fully sealed.
| 03SR - Stations (RfL) | Cxxx-NCR-000472 | NCR | Damage to VRF units in East Box ESR (664) |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-06-10 | 2018-05-17 10:23 | -24 | 2018-04-11 08:38 | Mechanical - Heating Ventilation & Air Conditioning | 3000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Both VRF units in room 664 in the East Box Basement have been damaged by other trades. Both appear to have been trodden on, causing significant dents in the unit casings.
| 03SR - Stations (RfL) | Cxxx-NCR-000473 | NCR | Torque Wrench Calibration Certificate Outdated |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2018-06-22 | 2018-06-21 13:58 | -1 | 2018-04-12 10:43 | Mechanical - Public Health Engineering | 1500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | A planned Crossrail surveillance was undertaken on 11th April 2018 to look at onsite installation of Pumped Drainage at Woolwich Station. The torque wrench used on site was checked post surveillance. The calibration certificate was made available for this (serial number 16123371). The date of calibration is 17/1/17, expiring 17/1/18. Torqueing was completed on 9/3/2018. On aligning the date of the calibration with the date of torqueing, it was found that the torqueing was done after the expiry date. Therefore the bolt connections completed with this wrench cannot be confirmed at the correct torque value. The bolt connections torqued with this outdated wrench need to be redone with an in date wrench and records produced to demonstrate that torques can be confirmed at the correct value.
| 03SR - Stations (RfL) | Cxxx-NCR-000474 | NCR | Fire Rated Ductwork Installed without consideration for fire stopping |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-05-12 | 2018-04-18 06:45 | -24 | 2018-04-12 13:52 | Mechanical - Heating Ventilation & Air Conditioning | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Fire rated ductwork passing through builders work hole from West Box Ground CIR-S 72 into corridor does not have sufficient clearance for fire stopping
| 03SR - Stations (RfL) | Cxxx-NCR-000475 | NCR | Connaught __ Earth tape snapped |  | Contr | SKC | WOO - Woolwich Station (East) |  | 2018-07-31 | 2018-06-12 14:19 | -49 | 2018-04-13 08:44 | Electrical - Earthing & Bonding | 500 |  | Damaged | Reject | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | the earth tape which connects the Earth Rods for the __ network at Connaught has been snapped
| 03SR - Stations (RfL) | Cxxx-NCR-000476 | NCR | West Box 763 Attenuator Dent |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-12-21 | 2018-12-19 14:34 | -2 | 2018-04-26 13:56 | Mechanical - Heating Ventilation & Air Conditioning | 3000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | The Heat Rejection Exhaust Attenuator in West Box 763 has been dented.
| 03SR - Stations (RfL) | Cxxx-NCR-000477 | NCR | Replace a 32A - 230V S/O with a 16A 230V "Protected" S/O - Plantrooms NWP |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-06-29 | 2018-06-11 10:30 | -18 | 2018-04-30 13:38 | Electrical - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | JV22.1302 clauses G; H & I require a "protected" 16A 230V Socket Outlet to be provided in the Plant rooms for use of specialist test equipment that may not readily be available to operate from 110V. The sockets provided are 32A instead of 16A and are not "Protected" (Locally). These require replacing with appropriate products. Also note that there are no 16A 230V sockets fitted in the Transformer Rooms. It this has been agreed with Cxxx then this is not an issue.
| 03SR - Stations (RfL) | Cxxx-NCR-000478 | NCR | No access to joint where bare copper Lightning Conductor tape connects to PVC covered Copper Tape - Woolwich Station |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-09-28 | 2018-09-24 09:07 | -4 | 2018-04-30 14:05 | Electrical - General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Lightning Protection copper tape changes from bare copper to PVC covered. There is no access to the joint allowed for in the external brickwork. Mitigation required to resolve the issue.
| 03SR - Stations (RfL) | Cxxx-NCR-000479 | NCR | M&E Drawings used on site are at "P" Revision and some have been bolwn up without incorporating any title block |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-06-29 | 2018-06-08 09:13 | -21 | 2018-04-30 14:17 | Electrical - General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | M&E Drawings have been used on site at P revision and some have been blown up for site use without including a title block to the drawings therefore drawings used for construction and managing the co-ordination needs further information on assurance.
| 03SR - Stations (RfL) | Cxxx-NCR-000480 | NCR | Thresholds NCR Connaught |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-08-09 | 2019-07-25 05:54 | -15 | 2018-05-09 13:33 | Architectural - Doors | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Management Problem - Improper resource allocation | Completed |  | Door threshold not installed on external doors
| 03SR - Stations (RfL) | Cxxx-NCR-000482 | NCR | Broken Concrete Cover to Manhole C201 |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-06-07 | 2018-06-06 15:27 | -1 | 2018-05-10 12:00 | Civil - Drainage | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Precast biscuit of manhole C201 was partially broken while breaking ground and removing the existing blinding concrete in the car parking area.
| 03SR - Stations (RfL) | Cxxx-NCR-000483 | NCR | Incorrect installation of anti-vandal guard at NWP |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-10-31 | 2018-09-18 11:14 | -43 | 2018-05-11 12:01 | Electrical - General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | After fixing of anti-vandal guard on brickwork, it was observed that there has been damage to the brickwork possibly during drilling of holes. Futhermore, type of screws used have not been torx screws in all cases
| 03SR - Stations (RfL) | Cxxx-NCR-000484 | NCR | Intumescent Sealant (Structural Fire Stopping) North Woolwich Portal |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-02-28 | 2018-11-26 16:26 | -94 | 2018-05-14 13:01 | Fire - Suppression | 500 |  | System Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The CRL specified and approved __ products - C144 LUFF and intumescent sealant have been installed at Cxxx in accordance with the manufacturer’s instructions and installation details Please refer to Cxxx-__R-FCD-020012 with all information All details have been approved inspected on site and benchmarks approved Since the initial installations numerous locations have been identified where the products have cracked and or de-laminated separated from the building structure
| 03SR - Stations (RfL) | Cxxx-NCR-000485 | NCR | Connaught Stainless Steel Lintel |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-03-04 | 2019-01-16 13:37 | -47 | 2018-05-15 16:33 | Architectural - Brickworks/Blockworks | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | Staining to Stainless steel lintel observed
| 03SR - Stations (RfL) | Cxxx-NCR-000486 | NCR | Incorrectly (Internal) Pre-cast concrete panels (P1; P2; P14 & P15) Ticket Hall West Box |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-09-28 | 2018-08-02 08:31 | -57 | 2018-05-17 13:50 | Civil - Civil Engineering General | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Pre-cast concrete panels to be fitted internally in the ticket hall in the West Box at Woolwich Station have been incorrectly cast resulting in an uneven finish.
| 03SR - Stations (RfL) | Cxxx-NCR-000487 | NCR | Main LV Feeder Cables Routed to wrong panels - Plumstead Substation |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-07-29 | 2018-06-08 09:17 | -51 | 2018-05-30 11:02 | Electrical - LV Equipment | 3000 |  | System Defect | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Cables B005/1/2/3/4 require jointing at Plumstead Sub-station, SRLV2 313 LVSB switchroom as they were crossed during installation, after investigation it was found that the headhouse layout drawing identified room 665 as SRLV1 which has PLU/LVSB/B switchboard, however the sub-station layout drawing shows PLU/LVSB/A located in room SRLV2 313.
| 03SR - Stations (RfL) | Cxxx-NCR-000489 | NCR | Battery MCCB's have been drilled on the sides to allow routing of signal cables, East Box, Battery Room 783 |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-08-30 | 2018-08-13 14:24 | -17 | 2018-06-06 14:37 | Electrical - General | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Battery MCCB's have been drilled on the sides to allow routing of signal cables. This solution has been implemented by __ operatives.
| 03SR - Stations (RfL) | Cxxx-NCR-000490 | NCR | Heat Rejection Ductwork Condenser/Chiller alignment |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-11-30 | 2018-10-08 12:45 | -53 | 2018-06-08 09:31 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | The East Box Ground Level 763 houses condensers and chillers. Both systems and units have heat rejection ductwork that doesn't align with the exhaust fan from the units, resulting in potential for increased pressure build up as air isn't dispersed appropriately.
| 03SR - Stations (RfL) | Cxxx-NCR-000491 | NCR | Chilled Water System Pipework Modification |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-11-30 | 2018-10-08 12:43 | -53 | 2018-06-08 09:41 | Mechanical - Piping | 5000 |  | Workmanship | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | CRL have identified varying areas in both chilled water plantrooms where a betterment to the current design/pipe routing can be achieved. Upstream and downstream dimensions for locations of balancing valves will be modified along with orientation of gauges in pursuit of a more effective and user friendly product.
| 03SR - Stations (RfL) | Cxxx-NCR-000492 | NCR | Damaged batteries in Plumstead Portal Headhouse |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-11-16 | 2018-10-01 12:55 | -46 | 2018-06-12 07:37 | Electrical - Power Distribution | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | There are three damaged batteries, numbered 16, 17 and 18, in UPS 1 lighting, battery room 667 at Plumstead Portal Headhouse
| 03SR - Stations (RfL) | Cxxx-NCR-000493 | NCR | Poor quality paint finish to Handrails on E&I Stairwells - Woolwich Station |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-11-29 | 2019-10-24 15:18 | -36 | 2018-06-26 09:50 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The handrails for the E&I stairwells at Woolwich station were sent to __ to be prepared and painted. The finished product was very poor. Instead of the handrails being painted seperately from the fixing brackets they were attached and the fixing screws were painted over. The welds on the handrails had not been ground down to provide a smooth and level finish.
| 03SR - Stations (RfL) | Cxxx-NCR-000494 | NCR | Discoloured Bronze Cladding Panel at Entrance to Woolwich Station |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-06-28 | 2019-03-14 16:38 | -106 | 2018-06-27 14:54 | Architectural - Finishes | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | __ installed a bronze panel, part of the West Box main entrance bronze cladding system on the 13/06/2018 that was exposed to elements which made it discoloured when compared to the remaining panels to be installed. All panels should have the same finish taking into consideration that natural weathering will affect the aspect of the whole system in time.
| 03SR - Stations (RfL) | Cxxx-NCR-000495 | NCR | Damaged Louvres for Plantroom Turrets- West Box |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-11-30 | 2018-11-26 15:15 | -4 | 2018-07-06 08:35 | Architectural - General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | During transport one of the crates of louvres partially collapsed causing damage to the finish of the louvres.
| 03SR - Stations (RfL) | Cxxx-NCR-000496 | NCR | Non-Compliant CMS Lidding at wall penetrations - All Areas |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-11-30 | 2018-10-19 08:46 | -42 | 2018-07-11 15:05 | Electrical - Cable Management | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Where CMS passes through penetrations the correct lidding procedure is not being followed. This is resulting in installations which are non-compliant and compromising the Firestopping system.
| 03SR - Stations (RfL) | Cxxx-NCR-000497 | NCR | Cleaning Water Run-off to Unprotected Bronze Panels -Station Entrance - West Box |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-08-22 | 2018-08-28 14:29 | 6 | 2018-07-16 13:21 | Architectural - General | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Location: West Box Entrance Portal South and North Column rear elevation. After panels installed by __, pre-cast panels contractor came on site on the 11th of July to clean the pre-cast panels and spilled water over the bronze panels. Panels were unprotected and no notice was given to protect the panels against water spilled during the cleaning process. After the incident __ was called in to assess the damage and poured water over the affected panels to attempt to clean the dust left by the pre-cast cleaning process. All panels should have the same finish taking into consideration that natural weathering will affect the aspect of the whole system in time.
| 03SR - Stations (RfL) | Cxxx-NCR-000499 | NCR | Damaged Electrical Field Cabinet - North Woolwich Portal |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-10-23 | 2018-09-04 15:18 | -49 | 2018-07-25 05:37 | Electrical - General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | AN Electrical Field Cabinet situated at the I&E Stairs (Ground Level) sustained damaged to the fibreglass structure.
| 03SR - Stations (RfL) | Cxxx-NCR-000502 | NCR | Plumstead Head House Roof |  | Contr | __R | WOO - Woolwich Station (East) |  | 2020-05-29 | 2020-08-06 09:21 | 69 | 2018-08-08 11:31 | Architectural - Roofing & Exterior Treatment | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | The paved walkway on the roof of Plumstead Head House has been blocked by services equipment. The paved walkway is intended to provide a wearing surface for the pedestrian route between door D1-01 and the top of the external intervention stair. Refer to Cxxx-EWN-01241.
| 03SR - Stations (RfL) | Cxxx-NCR-000504 | NCR | Trespa Frame Panelling - Poor quality Installation - Plumstead |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-03-28 | 2018-12-07 12:34 | -111 | 2018-08-14 13:34 | Architectural - Finishes | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The installation of panels on the Trespa frame is of poor quality. Panels are mis-aligned; of different dimensions and incomplete (some panels are still to be installed).
| 03SR - Stations (RfL) | Cxxx-NCR-000505 | NCR | The Contractor has commenced manufacturing without an accepted ITP |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2018-09-17 | 2018-09-05 07:50 | -12 | 2018-08-20 08:32 | Architectural - Glazing | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | A planned Crossrail surveillance was undertaken on 16th August 2018. This looked at the Glazed roof installation at Woolwich Station. On checking the ITPs for these works it was found that the Contractor had no ITP in place for the Offsite manufacturer of the Steelwork that supports the glazed roof lights.
| 03SR - Stations (RfL) | Cxxx-NCR-000506 | NCR | Accessories missing from Comms UPS - ESR 664 Rooms (East & West box) |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-06-28 | 2019-06-25 06:47 | -3 | 2018-08-23 07:50 | Electrical - LV Equipment | 2500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Following installation of the 160kVA UPS comms panels and completion of cable installation works on site, a visual inspection within the panels revealed that the cable mesh for mechanical protection of cables in the top section of the panels as well as side/bottom kick plates were missing
| 03SR - Stations (RfL) | Cxxx-NCR-000507 | NCR | Excessive gapping between Pre-cast Concrete Panels and Face Brickwork at Station Entrance |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-11-29 | 2020-11-23 09:38 | 360 | 2018-08-24 09:51 | Architectural - Finishes | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | There is excessive gapping between the Pre-cast concrete panels and the face brickwork at Woolwich Station Main Entrance enabling birds to roost/nest in the void.
| 03SR - Stations (RfL) | Cxxx-NCR-000508 | NCR | Noncompliance with the requirements of BS 9999 and BS8300 |  | Contr | __R | WOO - Woolwich Station (East) |  | 2020-04-30 | 2020-12-10 10:26 | 224 | 2018-08-30 13:41 | Architectural - Doors | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | BS 8300 clause 6.4.1 and BS 9999 clause 17.6.2 require the minimum clear width of the primary leaf of a double door to be 800mm. The door schedule lists some double door-sets where the clear opening of the primary leaf is less than 800mm, which does not comply with these requirements. BS 9999 21.2.7.2 requires doors between firefighting stairs and firefighting lobbies to be free from fastenings. The door and ironmongery schedules indicate some doors in firefighting shafts having locks, which will not comply with this requirement. BS 9999 16.5.2 requires doors on escape routes serving more than 60 people to be fitted with panic exit devices in accordance with BS EN 1125 – i.e. push bars. The current door proposals do not fully comply with this requirement.
| 03SR - Stations (RfL) | Cxxx-NCR-000509 | NCR | Installation of Insulated Pin Rack in Vertical Trunking Runs - East Box Riser - Basement |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-08-30 | 2019-08-19 08:24 | -11 | 2018-09-05 08:44 | Electrical - Cable Management | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | Verticle trunking sections require the installation of Insulated Pin Racks inserted at 3000mm spacings as per Crossrail Specification JY60 Conduit and Cable Trunking Clause JY60.1306.x
| 03SR - Stations (RfL) | Cxxx-NCR-000510 | NCR | The Contractor carried out impact testing in lieu of UKAS Accreditation. |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2018-10-04 | 2018-10-08 14:33 | 4 | 2018-09-06 12:06 | Architectural - Glazing | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | A planned Surveillance was carried out on Western Ticket Hall Glass Roof Installation and Assurance. The Contractor submitted ‘Off-site impact testing of glazing roof lights’ Cxxx-__R-Y-RGN-CR147-50071 (Rev 1) Decal Code 4. The testing to be carried as required in Cxxx Architectural Specification clause JH13. “ii) Overhead glazing/ panels in canopies and in roofs with maintenance access and unspecified general access shall, as a minimum, be designed to accommodate a concentrated load of 1.2kN acting over an area of 200mm x 200mm”. The testing was carried out by __ at their premises in Winterswijk Holland. Also in attendance were __ Ltd (CCL) who was instructed by __ Projects to act as the ‘Competent Person’ to oversee the testing of the roof light portal glazing sample. On checking neither __ nor __ Ltd are UKAS accredited to carry out the testing and there is no Project Managers Acceptance is in place for __/__ Ltd to undertake Glass Impact testing in lieu of UKAS Accreditation.
| 03SR - Stations (RfL) | Cxxx-NCR-000511 | NCR | Plumstead Portal - ponding issue on roof under the paving slabs |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-05-31 | 2019-04-08 13:19 | -53 | 2018-09-12 09:24 | Civil - Drainage | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Waterproofing and paving slabs were installed on Plumstead Portal roof as per Cxxx-__R-FCD-02136. Rain water causing ponding issue and stagnant water collecting on top of the waterproofing membrane under the paving slabs.
| 03SR - Stations (RfL) | Cxxx-NCR-000512 | NCR | Waterproofing System debonding from the screed substrate on roof floor level of East Box |  | Contr | __R | WOO - Woolwich Station (East) |  | 2020-01-17 | 2019-12-05 14:46 | -43 | 2018-09-11 15:00 | Architectural - Roofing & Exterior Treatment | 3000 |  | System Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Waterproofing System debonding from the screed substrate on roof floor level of East Box between grid lines B_B3 / E1_Z2, B_B3 / Z4_Z5 and B_B3 / Z9_Z10
| 03SR - Stations (RfL) | Cxxx-NCR-000515 | NCR | Local Isolators for Condensate Units - Plumstead Portal |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-10-31 | 2019-07-03 06:19 | -120 | 2018-09-21 10:38 | Electrical - General | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | There are no means of local isolation for the roof mounted condensor units at Plumstead Portal
| 03SR - Stations (RfL) | Cxxx-NCR-000516 | NCR | Un-sleeved cables passing through penetrations - All areas |  | Contr | __R | WOO - Woolwich Station (East) |  | 2018-11-01 | 2018-10-12 12:18 | -20 | 2018-10-02 09:56 | Electrical - Cable Management | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Cables have been installed without a sleeve where they pass through penetrations and have been Fire-stopped in contravention to specification JY61 LV Cables and Wiring: m) Cables passing through walls shall be provided with sleeves, and suitably sealed with acceptable fire-resisting material after installation.
| 03SR - Stations (RfL) | Cxxx-NCR-000517 | NCR | LV Swithchboard Labelling - All Areas |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-11-29 | 2020-08-19 14:34 | 264 | 2018-10-10 12:05 | Electrical - LV Equipment | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | ACB Red labels to be fitted. Manufacturers name plate not fitted (Optional). Switchboard LV-A (or B) label to be upgraded. Permit to Work label to be fitted top of Fire Alarm Panel __. Permit to Work label to be fitted to HV & LV Battery Charger MCCB's. SID Numbers to be fitted to all outgoing MCCB's. TEB earth cables to be Black/Red sheathed to identify as Red Bonds at MEB. Temporary danger labels also to be fitted ASAP to prevent disconnection. Permanent safety labels also to be fitted.
| 03SR - Stations (RfL) | Cxxx-NCR-000518 | NCR | Electrical trunking internal bends – All sites & portals |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-07-31 | 2019-04-23 09:26 | -99 | 2018-10-16 10:15 | Electrical - Cable Management | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Vertical rising Electrical Trunking supported by channel from the wall requires an external lid type bend installed when an internal bend is installed to reduce the risk of cable damage when the lid is removed.
| 03SR - Stations (RfL) | Cxxx-NCR-000519 | NCR | Rainwater Ingress at I&E Staircase - NWP |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-11-22 | 2019-12-09 09:57 | 17 | 2018-10-24 06:34 | Architectural - Roofing & Exterior Treatment | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Rainwater is ponding in the guttering of the roofing on the I&E Staircases at North Woowich Portal causing it to enter the structures.
| 03SR - Stations (RfL) | Cxxx-NCR-000520 | NCR | I&E Stairs: Risers missing; Uneven treads; Protruding tread supports. |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-05-31 | 2019-03-22 10:04 | -70 | 2018-10-24 07:14 | Architectural - General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Various stair treads in the I&E Staircase have risers missing; uneven size stair treads and protruding stair tread support brackets.
| 03SR - Stations (RfL) | Cxxx-NCR-000521 | NCR | Ponding in the I&E Staircase footwell |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-11-29 | 2019-10-29 16:06 | -31 | 2018-10-24 09:28 | Architectural - Flooring | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Previous Construction - Problems based on previous construction errors | Completed |  | Water gathers in the footwell of the I&E Staircase following rainfall. This could casue serious injury if there is and evacuation during excessively cold weather which could cause the water to freeze.
| 03SR - Stations (RfL) | Cxxx-NCR-000522 | NCR | Pooly fitting cladding panels; uncapped screws; dented cladding panels |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-05-31 | 2019-05-20 08:13 | -11 | 2018-10-24 09:49 | Architectural - Finishes | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Some of the cladding panels on the I&E staircase are pooly fitted causing large gaps which enable water to enter the I&E staircase. There are several uncapped screws extending into the general walkway and stairs of the I&£ Staircase which could possibly cause injury to persons using the staircase. There is some evidence of damage to some of the cladding panels on the I&E staircase.
| 03SR - Stations (RfL) | Cxxx-NCR-000523 | NCR | Smoke Downstand Works - Non-compliant / Unfinished Details |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-02-28 | 2018-12-14 16:42 | -76 | 2018-11-06 13:22 | Architectural - Finishes | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The final inspection carried-out between __ and __ on 2nd November 2018 the following issues were identified: - Drypack not finished between SS plates and soffit; - Mastic not finished between 1st central glass panel and the last left hand side panel (front and back faces); - Bottom trims were disaligned; - Glass panels weren’t cleaned; - Mastic joint with unacceptable finish on the back of the glass (face of the glass that’s facing the escalator)
| 03SR - Stations (RfL) | Cxxx-NCR-000525 | NCR | Cat 6 Cables - Exceed the Recommended 90m Rule |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-11-20 | 2019-10-16 10:20 | -35 | 2018-11-22 14:42 | Communications and Control Systems - CCTV | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The following cables have been installed in designed containment which results in them exeeding the 90m rule: ComLot – CTV-WOO-CTV00-02001 1. Cable ID – CR147-DAT-01964 which feeds CAM-0059 (East Box External) which is 106.4M. 2. This is due to the 901 room acoustic CMS route been the only available option. ComLot – CTV-WOO-CTV00-02003 3. Cable ID – CR147-DAT-01929 which feeds CAM-0314 (East Bound Platform) which is 120.4M. 4. Cable ID – CR147-DAT-01888 which feeds CAM-0328 (East Bound Platform) which is 123.2M. 5. Cable ID – CR147-DAT-01929 which feeds CAM-0330 (East Bound Platform) which is 118.1M. 6. Cable ID – CR147-DAT-01930 which feeds CAM-0315 (West Bound Platform) which is 119.3M. 7. Cable ID – CR147-DAT-01889 which feeds CAM-0329 (West Bound Platform) which is 128.6M. 8. Cable ID – CR147-DAT-01891 which feeds CAM-0331 (West Bound Platform) which is 124.6M. 9. Cable ID – CR147-DAT-01955 which feeds CAM-0336 (West Bound Platform) which is 98.2M.
| 03SR - Stations (RfL) | Cxxx-NCR-000526 | NCR | Broken Castel Key for Lift No. 3 Room 579 - West Box |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-02-24 | 2019-02-07 15:56 | -17 | 2018-11-26 10:12 | Electrical - LV Equipment | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | The Castel Key for lift No.3 located within room 579 (West Box) has been damaged and is unserviceable therefore must be replaced.
| 03SR - Stations (RfL) | Cxxx-NCR-000527 | NCR | Pull test requirment and torque values are not referenced on the ITP |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2019-05-31 | 2019-04-25 08:16 | -36 | 2018-11-30 12:00 | Architectural - Signage | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | During a planned surveillance on Signage Installation and Manufacturing Assurance, it was found that the ‘Signage Installation’ Cxxx-__R-A-ITP-CR147-50011 had no reference to the requirement for pull testing. I was also found that the line item for Torqueing of fixings states; ‘Fixings to be torqued to the value stated on approved construction drawings’. On checking ‘Projected Illuminated Sign Technical Design Pack’ Cxxx-__R-A-XPA-CR147-50005 (Rev 1) Code 1, no reference has been made to the torque values of the fixings.
| 03SR - Stations (RfL) | Cxxx-NCR-000528 | NCR | Vitrine Fitted Glass Panels Incorrectly Fabricated |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-08-30 | 2019-05-15 13:38 | -107 | 2019-01-14 15:12 | Architectural - Finishes | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | At Woolwich Station, West Box Retail Unit Curtain Wall: Top row of glass panels to retail unit curtain wall have the wrong DMP patterns installed. See drawings attached with correct pattern to be installed and photos of current installation.
| 03SR - Stations (RfL) | Cxxx-NCR-000529 | NCR | Handrail support bracket - Irregular dimensionand designs - West Box |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-04-15 | 2019-02-07 16:50 | -67 | 2019-01-15 12:56 | Architectural - Handrail | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | At Woolwich Station, West Box Portal, the depth of the support bracket shown on the two designs is not the same, as a result the handrails are closer to the rooflights flashings, causing a clash.
| 03SR - Stations (RfL) | Cxxx-NCR-000530 | NCR | Installed Non Compliant SY Cable |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2019-08-30 | 2019-07-03 07:01 | -58 | 2019-01-25 12:25 | Electrical - LV Equipment | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | SY Cable has been used to supply the AHU from the HVAC Drive. SY Cable has neither BS or European Standard approval
| 03SR - Stations (RfL) | Cxxx-NCR-000531 | NCR | The Contractor has commenced manufacturing without an accepted ITP |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2019-04-12 | 2019-03-20 08:44 | -23 | 2019-02-07 09:01 | Architectural - Glazing | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | A planned Crossrail surveillance was undertaken on 6th February 2019. This looked at the Glazed Cladding installation in Ticket Hall. On checking the ITPs for these works it was found that the Contractor had no ITP in place for the Offsite manufacturer of the glass Cladding System.
| 03SR - Stations (RfL) | Cxxx-NCR-000532 | NCR | Broken door handle on Q2 neutral switch panel – Plumstead Substation, UPS 312 room |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-06-28 | 2019-05-21 13:15 | -38 | 2019-02-07 11:25 | Electrical - LV Equipment | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | The door handle on Q2 neutral switch panel located within Plumstead Substation UPS 312 room has been damaged therefore, must be replaced
| 03SR - Stations (RfL) | Cxxx-NCR-000533 | NCR | Damaged CCTV Camera - Ticket Hall |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-06-28 | 2019-03-22 07:45 | -98 | 2019-02-11 11:43 | Communications and Control Systems - CCTV | 3000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | CCTV Camera WOO-OO-CAM-0020 has been damaged by (what appears to be a collission with a MEWP) subcontractors working in vacinity in the Ticket Hall - West Box
| 03SR - Stations (RfL) | Cxxx-NCR-000534 | NCR | Handrail support bracket design - inconsistent drawing dimensions |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-05-31 | 2019-02-28 08:42 | -92 | 2019-02-11 15:49 | Architectural - Handrail | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | At Woolwich Station, West Box Portal, the depth of the support bracket shown on the two designs is not the same, as a result the handrails are closer to the rooflights flashings, causing a clash.
| 03SR - Stations (RfL) | Cxxx-NCR-000535 | NCR | Excessive gapping on E&I Stair handrail. - NWP |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-08-30 | 2019-10-04 09:36 | 35 | 2019-03-12 07:47 | Architectural - General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The Stair handrails on the E&I stairs at North Woolwich Portal do not comply with building regulations in the the gapping is greater than 100mm.
| 03SR - Stations (RfL) | Cxxx-NCR-000536 | NCR | Corrosion of Architectural Metalwork on Intervention Stairs (External) |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-07-31 | 2019-04-25 14:51 | -97 | 2019-03-12 11:25 | Architectural - Handrail | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Site modified intervention stairs metalwork causing corrosion due to poorly finished paintwork.
| 03SR - Stations (RfL) | Cxxx-NCR-000537 | NCR | Flashing to E&I Stairs at Plumstead Portal |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-08-30 | 2019-09-03 08:31 | 4 | 2019-03-14 11:27 | Architectural - Roofing & Exterior Treatment | 3000 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The roof section on the E&I stairs require stepped flashing to ensure water-tight seal in accrodance with Specification JF10.1314 and JH20.1316
| 03SR - Stations (RfL) | Cxxx-NCR-000538 | NCR | Poor quality manufacture of Headhouse Doors - Connaught |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-10-31 | 2019-10-08 10:00 | -23 | 2019-03-21 10:39 | Architectural - Doors | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Defects identified on the Headhouse doors (manufactured by LHW) are as listed: 1. Door lining angle steel is buckled. 2. The drop bolt does not reach the ground and therefore is ineffective. 3. Finished paintwork on the doors is chipped. 4. The top bolt latch has been removed and must be replaced. 5. Where the door has been drilled on site there has not been satisfactory repair to the paintwork. 6. There are fixing bolts missing from the door frame andchors. 7. Poor welding finish to the door hinges. 8. Doors poorly aligned at the top. 9. Poor quality paint finish causing superficial rust to appear on doors.
| 03SR - Stations (RfL) | Cxxx-NCR-000539 | NCR | Incomplete Gate and fence foundation Design - Woolwich Station |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-11-29 | 2019-09-10 13:06 | -80 | 2019-03-26 07:47 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The design for the gate and fence foundation is incomplete although, through mutual agreement with CRL work has commenced on the gate and fence foundation works.
| 03SR - Stations (RfL) | Cxxx-NCR-000540 | NCR | Roof Waterproofing System Damage - West Box |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-10-31 | 2019-12-05 15:00 | 35 | 2019-04-15 13:33 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The roof waterproofing system on the roof of the West Box 1st floor section has been damaged as a result of scaffolding tubes being allowed to drop onto it during the striking of scaffold. This has damaged the surface waterproofing membrane but not the inner membrane (See attached photographs and drawing).
| 03SR - Stations (RfL) | Cxxx-NCR-000541 | NCR | Poorly fitted External Door Trims - Connaught MEP Building |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-08-30 | 2019-08-07 15:34 | -23 | 2019-04-18 08:59 | Architectural - Doors | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | External door trims have been fittied to the external doors on the MEP building at Connaught has been carried out to a poor standard. There ae instances where some are over-lapping the door trim or spaced out from the door lining because they do not fit in the space between the door hinge and the wall (see photos attached).
| 03SR - Stations (RfL) | Cxxx-NCR-000542 | NCR | Station-Fire Main; installation commenced without an accepted F2 Design in place. |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2019-07-31 | 2019-06-03 08:39 | -58 | 2019-04-23 13:29 | Fire - Fire Systems & General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | During planned surveillance on Fire Systems Installation, the Contractor presented the Contractors Declaration Certificate; ‘Woolwich Station – East End– __ Ltd - F2 Firemain Layouts’ (50008 to 50019)’ Cxxx-__R-E1-CER-CR147-50001 (Rev 1) dated 23/03/2018, that contained the accepted F2 design drawings for the Firemain Installation. The Contractor also presented the accepted Installation Release Notice (IRN) Cxxx-__R-O9-NOX-CR147-50003 (Rev 1) for the completed installation that was dated 29/06/2018 as such the installation had commenced with no accepted F2 design in place.
| 03SR - Stations (RfL) | Cxxx-NCR-000543 | NCR | The Contractor commenced installation of Watermist Fire Suppression System without an accepted F2 Design in place |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2019-07-31 | 2019-06-03 08:48 | -58 | 2019-04-23 13:47 | Fire - Fire Systems & General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | During planned surveillance on Fire Systems Installation, the Contractor presented the Contractors Declaration Certificate; ‘Woolwich Station – Fireworks (Hydramist)’ Cxxx-__R-M-CER-CR147-50097 (Rev 3) dated 01/04/2019, that contained the accepted F2 design drawings for the Hydramist Fire Suppression installation. The Contractor also presented the accepted IRNs Cxxx-__R-O9-NOX-CR147-*50001 (Rev 1), *50002 (Rev 1), *50027 (Rev 1) and *50029 (Rev 1) for the completed installation dated 28/01/2019 as such the installation had commenced with no accepted F2 design in place.
| 03SR - Stations (RfL) | Cxxx-NCR-000544 | NCR | The Contractor commenced installation of Fire Alarm and Detection System without an accepted F2 Design in place |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2019-05-22 | 2019-05-24 07:29 | 2 | 2019-04-24 08:04 | Fire - Fire Systems & General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | During planned surveillance on Fire Systems Installation, The Contractor presented the Designers Declaration Certificate ‘F2 Fire Alarm and Detection Drawings’ Cxxx-__R-O9-CER-CR147-50001 (Rev 3) dated 06/02/2019, that contained F2 design drawings for the Fire Alarm/Detection installation. The Contractor also presented the accepted IRN Cxxx-__R-O9-NOX-CR147-50035 (Rev 1) for the completed installation, dated 12/12/2018 as such the installation had commenced with no accepted F2 design in place.
| 03SR - Stations (RfL) | Cxxx-NCR-000545 | NCR | LV Cable Glands not in compliance with Cxxx Earthing Strategies - MEP Building , Connaught |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-06-28 | 2019-04-26 11:05 | -63 | 2019-04-25 12:11 | Electrical - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Connaught support building: The MCC's located within the two LV switchrooms have their incoming sub-main cables glanded using insulating glands. As such, these are bonded to neither __ earth or traction earth. Currently, these sub-main cables are glanded but not terminated.. However, this is not in line with the Cxxx and Cxxx earthing strategies.
| 03SR - Stations (RfL) | Cxxx-NCR-000546 | NCR | Damaged Cxxx radio cable FD-038 |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-10-31 | 2019-06-19 06:59 | -134 | 2019-05-10 09:47 | Communications and Control Systems - Radio | 3000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Damage to FD-038 radio cable in multiple locations. One where the cable leaves the CER and drops down onto trackside due to the CMS bends see attached picture of route and also where it enters the UTX to come through to the sub-platform. Would it be possible to piece in some LCF-12 from within the sub-platform back up to the CER approx. length would be 30 metres. Cxxx tester report of the damage is below FD038 is failing in multiple locations in the high band testing (specifically at 9m and 20m from the radio cabinet end) and needs to be replaced.
| 03SR - Stations (RfL) | Cxxx-NCR-000547 | NCR | Extract Fan Control Unit for EF01A & EF01B - Connaught Headhouse |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-12-20 | 2019-12-16 14:09 | -4 | 2019-05-15 12:47 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The following issues were identified by CRL Mechanical Field Engineer in the Connaught Headhouse regarding the Extract Fan Control Unit for EF01A & EF02: • No System identification (for VSD’s). • No Fan running indication. • No Fan Fault Indication. • No Lamp test functionality. • No Hand/Off/Auto operation selector switch. • No Electrical safety signage
| 03SR - Stations (RfL) | Cxxx-NCR-000548 | NCR | UPS SCADA Battery Breaker Alarm NWP |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-10-31 | 2020-04-27 06:58 | 179 | 2019-05-15 14:41 | Communications and Control Systems - SCADA/Central Management System | 3000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | There is no "Breaker Open" alarm from the UPS Panel to the SCADA Panel.
| 03SR - Stations (RfL) | Cxxx-NCR-000549 | NCR | Relocation of MFD for Maintenance Access Rm 664 East Box |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-12-23 | 2019-11-05 08:59 | -48 | 2019-05-20 11:12 | Mechanical - Heating Ventilation & Air Conditioning | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Relocate MFD-E3-16 from corridor the room 664 for maintenance access due to number of services in corridor impeding access for maintenance.
| 03SR - Stations (RfL) | Cxxx-NCR-000550 | NCR | Water ingressing cable ductworks - Headhouse Connaught |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-11-29 | 2019-11-13 13:26 | -16 | 2019-05-20 12:45 | Civil - Utilities Engineering | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Water is ingressing the cable ductworks between Draw Pit DPLV04 and the Headhouse at Connaught.
| 03SR - Stations (RfL) | Cxxx-NCR-000551 | NCR | UPS SCADA Battery Breaker Alarm Connaught |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-10-31 | 2020-04-27 06:59 | 179 | 2019-05-28 11:14 | Communications and Control Systems - SCADA/Central Management System | 3000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The UPS Battery Breaker Monitoring Alarm must be taken from the UPS Battery Breaker instead of it's current location in the UPS panel.
| 03SR - Stations (RfL) | Cxxx-NCR-000553 | NCR | Substandard and Non Compliant Work in Termination Box in Lift 3 Shaft /LEER Connection Box |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-10-31 | 2019-06-25 07:37 | -128 | 2019-05-29 06:10 | Electrical - General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The termination work in Lift 3 Shaft/LEER Connection Box does not comply with BS7671 and is of very poor quality.
| 03SR - Stations (RfL) | Cxxx-NCR-000554 | NCR | Replace Main Earth Cables to Comply with NR Specification - Connaught Headhouse |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-10-31 | 2019-06-25 14:24 | -128 | 2019-05-29 08:15 | Electrical - Earthing & Bonding | 2500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Replace current 16mm2 main earth cable from MEP building to the Headhouse at Connaught in comoliance with NR specification PAN/E&P-E/EE/ESD/0102 section 5.3
| 03SR - Stations (RfL) | Cxxx-NCR-000555 | NCR | Replace Water damaged CCTV Camera 009 West Box East Elevation External |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-11-29 | 2019-06-19 06:57 | -163 | 2019-05-29 08:29 | Communications and Control Systems - CCTV | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | Water has ingressed CCTV camera 009 mounted externally on the East Wall of the West Box at Woolwich Station and caused internal damage requiring replacement.
| 03SR - Stations (RfL) | Cxxx-NCR-000556 | NCR | Woolwich Station Door Contacts Junction Boxes to be Replaced |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-11-29 | 2019-06-19 06:54 | -163 | 2019-05-29 08:48 | Communications and Control Systems - General | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The Junction Boxes for the door contacts at Woolwich Station have been drilled with a single 16mm hole located in the centre of the boxes. These boxes (16 off) need to be replaced so the boxes can be drilled for 2x20mm holes per box. All 16 boxes must be replaced.
| 03SR - Stations (RfL) | Cxxx-NCR-000557 | NCR | Relocate MFD-W3-04 to Enable Maintainance - Rm 664 West Box |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-11-29 | 2019-11-01 10:56 | -28 | 2019-06-17 10:12 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | The current location of MFD-W3-W04 is situated directly above a UPS panel thus restricting maintainable access.
| 03SR - Stations (RfL) | Cxxx-NCR-000558 | NCR | Relocate secondary containment and Fan Coil Unit to enable access to MFD's - Rm 801 - West Box |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-11-29 | 2019-11-11 11:54 | -18 | 2019-06-17 11:07 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Relocate containmentand FCU in room 801(West Box) to enable maintainable access to MFDs MFD-W1-35; MFD-W1-49; MFD-W1-18 & MFD-W1-16
| 03SR - Stations (RfL) | Cxxx-NCR-000559 | NCR | Relocate secondary containment and supports to enable access to MFD's - West Box Ground Floor |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-11-29 | 2019-11-04 08:27 | -25 | 2019-06-17 13:17 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | Due to lack of co-ordination and approved drawings at time of installation has caused issues of restricted access to Motorised Fire Dampers in rooms and corridors in the following areas or the ground floor - West Box: MFD-W1-11 (Rm 407); MFD-W1-12 & MFD-W1-50 Corr. (SVlll Rm 73); MFD-W1-04, MFD-W1-05 & MFD-W1-W1-14 (SMK Rm 47).
| 03SR - Stations (RfL) | Cxxx-NCR-000560 | NCR | Damaged RWP Panels - East Box |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-11-29 | 2019-12-03 09:28 | 4 | 2019-06-18 09:55 | Architectural - Finishes | 2500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Superficial damage has occurred either during the storage or installation of the RWP Panels on the North and South face of the East Box at Woolwich Station
| 03SR - Stations (RfL) | Cxxx-NCR-000561 | NCR | Replace Main Earth Cables from LVSB to MEB - NWP |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-07-15 | 2019-07-19 11:32 | 4 | 2019-07-01 12:27 | Electrical - Earthing & Bonding | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Replace current 70mm Main Earth Cables (EC118 & ECxxx) with 300mm Earth Cables. EC118 from LVSR "A" EB to Switchboard "A" ECxxx from LVSR "B" EB to Switchboard "B"
| 03SR - Stations (RfL) | Cxxx-NCR-000562 | NCR | Inaccessible Duct Sensor - Plumstead |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-11-29 | 2019-10-24 07:27 | -36 | 2019-07-11 13:44 | Mechanical - Heating Ventilation & Air Conditioning | 1000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The smoke sensor on the Air Intake on the roof of Plumstead Portal is located in an un-mailntainable location.
| 03SR - Stations (RfL) | Cxxx-NCR-000563 | NCR | Relocation of MFD 07 to enable access for maintenance - Plumstead |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-12-20 | 2019-12-11 10:08 | -9 | 2019-07-16 13:35 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | Relocate MFD 07 from current position in room 666 to the roof of the Plumstead Headhouse to enable access for service and maintenance.
| 03SR - Stations (RfL) | Cxxx-NCR-000564 | NCR | Excessive radial movement and missalignment of Platform End Gates on the E&I Stairs - NWP |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-11-29 | 2019-11-25 11:54 | -4 | 2019-07-29 10:35 | Architectural - Doors | 3000 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There is excessive movement on the Platform End Gates at the E&I stairs allowing the gate nearest the trackside to swing out over the edge of the platform potentially a safety issue (see attached photograph: Radial Movement Pic1). The platform end gates are also missaligned when in the normally closed position (see attached photographs: Missalignment. Pic 1 & Pic 2)
| 03SR - Stations (RfL) | Cxxx-NCR-000565 | NCR | Cxxx Cable Markers Over Painted and Illegible - Woolwich Station |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-11-29 | 2019-08-20 11:56 | -101 | 2019-07-29 12:52 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | Cxxx Cable markers have been painted over due to failure to adequately mask all relevant surfaces prior to spray painting in the vacinity, leaving the cable markers illegible
| 03SR - Stations (RfL) | Cxxx-NCR-000566 | NCR | FT DATA CABLE REQUIRED TO REPLACE LINK FOR WOO-03-RIL-00301 - Woolwich Station |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-11-29 | 2019-08-19 12:38 | -102 | 2019-08-02 14:00 | Communications and Control Systems - General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The RHPS located on the platform has a damaged cable somewhere along the run between the platform and the CER, we are unable to locate the damaged area due to CMS being closed up, and need to pull in a new cable.
| 03SR - Stations (RfL) | Cxxx-NCR-000568 | NCR | Plumstead doors D2-06, D2-07, D2-08, D2-10, D2-11, D2-12, D2-13 - Door hinges not consistant with Drawings. - PLU |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-12-20 | 2019-12-16 12:03 | -4 | 2019-08-13 14:05 | Architectural - Doors | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Plumstead doors D2-06, D2-07, D2-08, D2-10, D2-11, D2-12, D2-13 have been installed with 3 hinges on each leaf which is different from the 4 shown in door drawings – NCR to __ __
| 03SR - Stations (RfL) | Cxxx-NCR-000569 | NCR | __ __ Connaught support building doors – issues with push pads not correctly opening doors |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-11-29 | 2019-10-29 15:59 | -31 | 2019-08-13 12:21 | Architectural - Doors | 5000 |  | Manufacturing Defect | Repair | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | __ __ Connaught support building doors – issues with push pads not correctly opening doors
| 03SR - Stations (RfL) | Cxxx-NCR-000570 | NCR | Miss-aligned Appeture for Lift Maintenance Panel in Bronze Wall cladding - West Box |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-11-29 | 2020-08-28 11:15 | 273 | 2019-08-06 14:33 | Architectural - Finishes | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | An appetture has been prefabricated in the Bronze Wall cladding for the Lift Maintenance Panel in the West Box platform level making it impossible to open the maintenance panel.
| 03SR - Stations (RfL) | Cxxx-NCR-000571 | NCR | Miss-alignement with prefabrication of Telephone and Socketoutlet Appettures in Bronze Cladding |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-11-29 | 2020-08-14 14:55 | 259 | 2019-08-06 14:51 | Architectural - Finishes | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | There has been several locations on the station platform level whereby the prefabricated appettures cut into the Bronze Wall Cladding are miss-aligned making it impossible to access the telephones or socketoutlets located behind the cladding.
| 03SR - Stations (RfL) | Cxxx-NCR-000572 | NCR | Fireworks Incorrect Nozzle Height Room 407 - West Box |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-11-29 | 2019-11-01 10:07 | -28 | 2019-08-12 08:20 | Fire - Fire Systems & General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | The nozzle height within room 407 West Box has been installed at the incorrect height.
| 03SR - Stations (RfL) | Cxxx-NCR-000573 | NCR | Watermist Issues Raised by CRL Inspectors - East and West Box |  | Contr | __R | WOO - Woolwich Station (East) |  | 2020-04-30 | 2021-02-22 14:23 | 298 | 2019-08-12 08:41 | Fire - Fire Systems & General | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | Issues raied by CRL field inspector as follows: 1. Copper pipework feed pipe to the system. Should this be fire protected? 2. Valves to be locked and strapped. 3. Each pump panel to individual TAG indification. 4. Manifolds to be labelled. 5. Blank off inlet pressure and inlet valve fault status indicators in control panels. 6. Wall mounted specific system scchematic drawings to be installed. 7. Label pump panel covers to state that there are LV power calbeswithin pump panel. 8. Add amber fault light to each panel, no external fault indiction shown or visible.
| 03SR - Stations (RfL) | Cxxx-NCR-000574 | NCR | Internal Panel Socket Outlets Wired in Single Insulated Cables - Woolwich Station |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-11-29 | 2019-10-30 09:03 | -30 | 2019-08-12 12:41 | Electrical - General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Socket Outlets installed inside Electrical Panels ahve been wired in single insulated cables that are unshielded and unprotected from touch.
| 03SR - Stations (RfL) | Cxxx-NCR-000575 | NCR | Damage to Lift Door on Level Basement -2 in the West Box |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-11-29 | 2019-12-06 16:55 | 7 | 2019-08-12 13:07 | Architectural - Finishes | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | A lift door has been dtruck by a solid object causing 2 serious dents in one of the doors on the lift at basement level -2 in the West Box ofthe Woolwich Station
| 03SR - Stations (RfL) | Cxxx-NCR-000576 | NCR | Additional Door Monitoring Devices - All sites |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-11-29 | 2019-08-28 09:28 | -93 | 2019-08-23 07:57 | Communications and Control Systems - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The original design for door monitoring devices was vague in that it did not detail the requirement for instances where there were instances of double doors, the design still only asked for one monitoring device therefore, there was the possibility of a second door being un-monitored. Both sections of these doors require monitoring for security to be assured.
| 03SR - Stations (RfL) | Cxxx-NCR-000577 | NCR | ATS Status Indication Lighting Design - All Sites |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-11-29 | 2020-08-29 16:50 | 274 | 2019-08-28 12:20 | Electrical - Switchgear | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The wiring supply to the status indication lights on the ATS panels has been taken from the "Incoming" side of the isolator switches instead of the "Load" side therefore even when the supply is switched off the indication lights show the power is still on.
| 03SR - Stations (RfL) | Cxxx-NCR-000578 | NCR | Damaged Door E1-787b RSR Rm East Box Ground Level |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-12-03 | 2019-12-13 15:45 | 10 | 2019-09-04 12:06 | Architectural - Doors | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | The Door E1-787b on the RSR Room East Box Ground floor has sustained damage (see attached photograph)
| 03SR - Stations (RfL) | Cxxx-NCR-000579 | NCR | Scratched Vitrine Panel - West Box |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-11-29 | 2019-12-10 09:29 | 11 | 2019-09-11 11:34 | Architectural - Finishes | 500 |  | Damaged | Reject | 4 (0.5-3k) | Complete | Subcontractor Problems - Other | Completed |  | A Vitrine panel has been delivered to site with Scratches inflicted either during packing or transportation to site.
| 03SR - Stations (RfL) | Cxxx-NCR-000581 | NCR | WB Stair 577 Service Door Damaged Door Closer |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-11-29 | 2019-11-22 13:29 | -7 | 2019-09-23 14:08 | Architectural - Finishes | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | The door closer on service to door service stairs 577 has been damaged (see attached photograph).
| 03SR - Stations (RfL) | Cxxx-NCR-000582 | NCR | Cracked Decorative Planters - West Box |  | Contr | __R | WOO - Woolwich Station (East) |  | 2020-05-29 | 2020-08-06 11:49 | 69 | 2019-09-24 07:16 | Architectural - General | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Decorative planters situated at the entrance to Woolwich Station have developed cracks.
| 03SR - Stations (RfL) | Cxxx-NCR-000583 | NCR | Install Manual Light Switch in Room 670 in Line with Control Dwg. East Box |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-11-29 | 2019-10-18 12:44 | -42 | 2019-09-30 09:48 | Electrical - Lighting | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Install manually operated light switch in line with control drawing which was missed off the installation drawing.
| 03SR - Stations (RfL) | Cxxx-NCR-000584 | NCR | HV - RTU Power Supply Modification - Change Normal Power Supply to Essential Power Supply - Plumstead |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-11-29 | 2020-02-20 16:07 | 83 | 2019-10-03 12:58 | Electrical - General | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The current power supplies to HV RTU panels LV-A & LV-B come from a "Normal" power supply; therefore are liable to cause a loss of power when there is any interruption to these supplies. The supplies for these panels need to be sourced from an essential supply as detailed in FCD-PTR-00833 (see attached)
| 03SR - Stations (RfL) | Cxxx-NCR-000585 | NCR | HV - RTU Power Supply Modification - Change from Normal Supply to Essential Supply - NWP |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-12-02 | 2020-02-26 14:50 | 86 | 2019-10-03 14:20 | Electrical - General | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The power supply to the HV - RTU Panels is currently from a "Normal" source therefore, in the event of an interruption to the power supply this may cause nuicance tripping. The power to theses panels will be modified to be sourced from an Essential supply as detailed in Cxxx-FCD-001182 - North Woolwich Portal - HV RTU Power Supply Modification FCD
| 03SR - Stations (RfL) | Cxxx-NCR-000586 | NCR | Door D3-09 - Frame not plumb - Plumstead |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-12-07 | 2019-11-22 13:37 | -15 | 2019-10-08 12:54 | Architectural - Doors | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Door-frame for door D3-09 has been installed out of plumb.
| 03SR - Stations (RfL) | Cxxx-NCR-000587 | NCR | Fire rated doors not displaying the correct pre-fix certificate labels - Plumstead |  | Contr | __R | WOO - Woolwich Station (East) |  | 2020-05-29 | 2020-04-29 11:24 | -30 | 2019-10-08 13:12 | Architectural - Doors | 3000 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Doors D2-11, D2-12, D2,13, D2-08 lack the prefixed certifire labels and therefore do not comply with the MCR forthe fire doors.
| 03SR - Stations (RfL) | Cxxx-NCR-000588 | NCR | Door D2-15 Slave leaf clashes with adjacent electrical fitting therefire is unable to open to fully as designed - Plumstead |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-12-07 | 2019-11-22 13:42 | -15 | 2019-10-08 13:34 | Architectural - Doors | 3000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Door D2-15 slave leaf clashes with an adjacent electrical fitting preventing it from opening to the designed extent also, there is damage to the finishes to the door leaf.
| 03SR - Stations (RfL) | Cxxx-NCR-000589 | NCR | Plumstead Door D1-04 Issues listed |  | Contr | __R | WOO - Woolwich Station (East) |  | 2020-03-28 | 2020-05-21 08:25 | 54 | 2019-10-10 14:17 | Architectural - Doors | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Issues identified with Door D1-04 •The deadbolt on the door mechanism to D1-04 engages with a keep on the other leaf which, with the T Bar to the closing stile, makes it difficult to open the door using the right hand push-bar, which does not meet the requirements of BS 9999 16.5.2. The door/ironmongery schedules specify ironmongery set RE4, which stipulates plain meeting stiles, so this door does not comply with this requirement. •The hinges to door D1-04 do not conform to the MCR for security doors (Cxxx-__R-A-MCR-CR148_PT005-50052) which shows type FM-3500 continuous hinges the full height of the door. •The hinges to door D1-04 are grade 12 hinges, which do not conform to the draft MCR for fire doors, which refers to grade 13 hinges.
| 03SR - Stations (RfL) | Cxxx-NCR-000590 | NCR | Plumstead Door D3-11 Issues listed |  | Contr | __R | WOO - Woolwich Station (East) |  | 2020-09-30 | 2020-10-01 15:19 | 1 | 2019-10-10 14:31 | Architectural - Doors | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Issues for Door D3-11 •The door/ironmongery schedules specify ironmongery set RE4 for this door, requiring plain meeting stiles, so this door does not comply with this requirement. This makes it difficult to open the door using the left hand push-bar. Refer to the requirements of BS 9999 16.5.2 for opening to be possible using a single mechanism and BS EN 1125:2008 4.1.2 on speed of opening.
| 03SR - Stations (RfL) | Cxxx-NCR-000591 | NCR | __ Bronze Pannelling to Columns at the Platform (S02a) |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-12-09 | 2020-09-16 07:49 | 282 | 2019-10-10 15:01 | Architectural - Finishes | 6000 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Contamination | Completed |  | The Bronze cladding has been damaged, caused by floor grouting; scuffing and tarnishing as identified in Cxxx-WK-00236).
| 03SR - Stations (RfL) | Cxxx-NCR-000592 | NCR | Incorrect Test Results - Cxxx-__R-E-RGN-CR147-50253 |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-11-29 | 2020-08-19 14:42 | 264 | 2019-10-21 09:52 | Electrical - General | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | The test resdults recorded on Page 4 of document Cxxx-__R-E-RGN-CR147-50253 are incorrect. They state the protection device is a 100A device when in actual fact the protection device is a 40A device.
| 03SR - Stations (RfL) | Cxxx-NCR-000593 | NCR | Fire Stopping Labels - NWP |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-12-31 | 2020-01-16 08:45 | 16 | 2019-11-01 11:11 | Fire - Compartmentation | 7000 |  | Equipment Breakdown | Rework | 2 (6-60k) | Complete | Supervision - Other | Completed |  | It has been identified that firestopping labels are peeling off in several locations. It is believed that this is caused by painters taking the labels off to avoid painting over them, and the reinstalling them without the needed standards.
| 03SR - Stations (RfL) | Cxxx-NCR-000594 | NCR | Fire Stopping Labels - PLU |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-12-31 | 2020-01-22 13:30 | 22 | 2019-11-01 11:39 | Fire - Compartmentation | 7000 |  | Equipment Breakdown | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | It has been identified that firestopping labels are peeling off in several locations. It is believed that this is caused by painters taking the labels off to avoid painting over them, and the reinstalling them without the needed standards.
| 03SR - Stations (RfL) | Cxxx-NCR-000595 | NCR | Fire Stopping Labels - East Box |  | Contr | __R | WOO - Woolwich Station (East) |  | 2020-01-30 | 2020-03-26 15:41 | 56 | 2019-11-01 11:42 | Fire - Compartmentation | 7000 |  | Equipment Breakdown | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | It has been identified that firestopping labels are peeling off in several locations. It is believed that this is caused by painters taking the labels off to avoid painting over them, and the reinstalling them without the needed standards.
| 03SR - Stations (RfL) | Cxxx-NCR-000596 | NCR | Fire Stopping Labels - West Box |  | Contr | __R | WOO - Woolwich Station (East) |  | 2020-01-30 | 2020-02-07 11:36 | 8 | 2019-11-01 11:44 | Fire - Compartmentation | 7000 |  | Equipment Breakdown | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | It has been identified that firestopping labels are peeling off in several locations. It is believed that this is caused by painters taking the labels off to avoid painting over them, and the reinstalling them without the needed standards.
| 03SR - Stations (RfL) | Cxxx-NCR-000597 | NCR | Door D1-74a Defective Manufacture. - West Box |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-11-30 | 2020-02-07 12:03 | 69 | 2019-11-04 15:44 | Architectural - Doors | 5000 |  | Manufacturing Defect | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Door D1-74a has been defectively manufactured. Issues as follows: Defects on door D1-74a in Woolwich West Box: - High level dog-bolts not coordinated with frame recesses on both sides. - Non functioning bolts due to misaligned or missing sockets. - Site modification to keep on slave leaf. No site modifications should be necessary because the door-set should be checked as coordinated and in good order before being shipped from the factory.
| 03SR - Stations (RfL) | Cxxx-NCR-000598 | NCR | MD41 Removal of Door Contact - West Box Ticket hall |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-12-08 | 2019-11-12 12:31 | -26 | 2019-11-08 07:18 | Communications and Control Systems - SCADA/Central Management System | 1500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | MD41 Located within the West Box Ticket Hall has had the SCADA monitoring door contact reomved by person's unknown to enable work to be carried out on the door frame. This cause the contact to send an alarm signal to the RCC and required Cxxx to rework this asset.
| 03SR - Stations (RfL) | Cxxx-NCR-000600 | NCR | Contractor could not provide Door Manufacturing ITP and supporting deliverables. |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2019-12-21 | 2020-03-10 09:51 | 80 | 2019-11-11 12:39 | Architectural - Doors | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | During a planned Crossrail Fire Door Installation and Assurance Quality Surveillance on request the Contractor was unable to provide the Door Manufacturing ITP including supporting deliverables.
| 03SR - Stations (RfL) | Cxxx-NCR-000601 | NCR | The Contractor has no Approved drawings in place for the door sets |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2019-12-21 | 2020-08-28 09:11 | 251 | 2019-11-11 12:46 | Architectural - Doors | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | During a planned Crossrail Fire Door Installation and Assurance Quality Surveillance, on request the Contractor was unable to provide approved drawings for the door set installed.
| 03SR - Stations (RfL) | Cxxx-NCR-000602 | NCR | The Contractor was unable to provide formal acceptance of Samples and Benchmarks in line with the Architectural Specification Cxxx-__R-A-RSP-CR147-50001 JL20.220 |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2019-12-21 | 2019-12-12 11:53 | -9 | 2019-11-11 12:53 | Architectural - Doors | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | During a planned Crossrail Fire Door Installation and Assurance Quality Surveillance on request the Contractor was unable to provide formal acceptance of Samples and Benchmarks for the door sets in line with the Architectural Specification Cxxx-__R-A-RSP-CR147-50001 JL20.220
| 03SR - Stations (RfL) | Cxxx-NCR-000603 | NCR | The Contractor has not revised the Door schedule and Ironmongery for more than 18 months |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2020-03-31 | 2021-02-17 14:54 | 323 | 2019-11-11 12:58 | Architectural - Doors | 2500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | During a planned Crossrail Fire Door Installation and Assurance Quality Surveillance it was found that the Contractor has not revised the Door schedule Cxxx-__R-A-TSC-CR147-50002 (Rev 8) for more than 18 months (31/01/2018). It was also found that the Door Ironmongery Schedule Cxxx-__R-A-TSC-CR147_WS163-50001(Rev 4) had not been revised for more than 2 years (16/01/2017).
| 03SR - Stations (RfL) | Cxxx-NCR-000604 | NCR | Door Quality Issues E4-6431, E4-630, E4-632, E4-633 East Box |  | Contr | __R | WOO - Woolwich Station (East) |  | 2020-05-29 | 2020-08-28 11:43 | 91 | 2019-11-13 11:50 | Architectural - Doors | 5000 |  | Manufacturing Defect | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Quality issues had been identified on the following doors: - E4-631, E4-630, E4-632, E4-633 - These doors are installed as Stainless Steel and should be PPC. - Holes have been over drilled where push plates and kick plates are located. - Jig manufacturing errors have left incorrect hinge locations.
| 03SR - Stations (RfL) | Cxxx-NCR-000605 | NCR | Temporary Services Cables supported on Cxxx Support Brackets - Plumstead |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-12-20 | 2019-11-21 08:36 | -29 | 2019-11-19 14:13 | Electrical - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Site temporary cabels and services have been suspended from Cxxx equpiment support bracketry as identified in CRL-OBS-29793 (attached).
| 03SR - Stations (RfL) | Cxxx-NCR-000606 | NCR | Installation of 1Nr Short Circuit Isolator in Fire Loop Zone. - Connaught |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-12-20 | 2020-01-23 13:57 | 34 | 2019-11-21 11:39 | Fire - Detection | 1000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | The Head-house fire detection system loop requires 1Nr Short Circuit Isolator within this Fire Zone, to maintain audibility in the event of a Short Circuit fault condition in the loop.
| 03SR - Stations (RfL) | Cxxx-NCR-000607 | NCR | CMS requires Fire Services Labelling - Connaught Head-house |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-12-20 | 2020-02-17 14:52 | 59 | 2019-11-21 11:43 | Fire - Fire Systems & General | 1000 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | All CMS require Fire Services Labelling
| 03SR - Stations (RfL) | Cxxx-NCR-000608 | NCR | __ Isolators require "FIRE ALARM DO NOT SWITCH OFF Labels |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-12-20 | 2020-02-10 10:32 | 52 | 2019-11-21 11:47 | Fire - Fire Systems & General | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | __ Isolators require "FIRE ALARM DO NOT SWITCH OFF" labels.
| 03SR - Stations (RfL) | Cxxx-NCR-000609 | NCR | All Self-Closing Doors to be Tested - NWP |  | Contr | __R | WOO - Woolwich Station (East) |  | 2019-12-20 | 2020-01-20 15:46 | 31 | 2019-11-21 13:15 | Architectural - Doors | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | All fire doors need to be tested for self-closing to position of fully closed.
| 03SR - Stations (RfL) | Cxxx-NCR-000610 | NCR | All Fire Services CMS to be Labelled with RED Treffolyte Labels Stating "FIRE ALARM SERVICES" - NWP |  | Contr | __R | WOO - Woolwich Station (East) |  | 2020-04-30 | 2020-03-04 10:23 | -57 | 2019-11-21 13:23 | Fire - Fire Systems & General | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | All Fire Services CMS to be Labelled with RED Treffolyte Labels Stating "FIRE ALARM SERVICES".
| 03SR - Stations (RfL) | Cxxx-NCR-000611 | NCR | Fire Damper Control Panel Mounted Too High - NWP |  | Contr | __R | WOO - Woolwich Station (East) |  | 2020-06-30 | 2020-04-07 12:21 | -84 | 2019-11-21 13:41 | Fire - Fire Systems & General | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The Fire Damper Control Panel situated on the Platform level at NWP has been mounted too high making it non-maintainable.
| 03SR - Stations (RfL) | Cxxx-NCR-000613 | NCR | Conduits and Cable Tray Surface Mounted on the Floor of Corridor 90 Level -2 West Box |  | Contr | __R | WOO - Woolwich Station (East) |  | 2021-09-09 | 2021-09-09 14:15 | 0 | 2019-12-04 14:19 | Communications and Control Systems - General | 3000 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Floor mounted conduits and cable tray in corridor90 level -2 in the West Box of Woolwich Station have the potential to cause a tripping hazard and sustain damage to this containment.
| 03SR - Stations (RfL) | Cxxx-NCR-000614 | NCR | LEER Panel Supply Cable Single Insulated |  | Contr | __R | WOO - Woolwich Station (East) |  | 2020-07-31 | 2020-06-01 08:51 | -60 | 2019-12-10 15:54 | Electrical - General | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Cables from local isolators to the LEER Panels has exposed single insulated cores which are unprotected from touch.
| 03SR - Stations (RfL) | Cxxx-NCR-000615 | NCR | Metal Walkway Grating to be Rectified - 1st Floor West Box |  | Contr | __R | WOO - Woolwich Station (East) |  | 2020-04-30 | 2020-08-14 11:58 | 106 | 2019-12-11 12:12 | Architectural - Finishes | 5000 |  | Manufacturing Defect | Repair | 3 (3-6k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | The metal walkway grating on the 1st floor West Box does not extend to the designed limit as shown in drawings Cxxx-__R-A-DWG-CR147-50068 C02 and Cxxx-__R-A-DWG-CR147-50068 C02 (see attached).
| 03SR - Stations (RfL) | Cxxx-NCR-000617 | NCR | Roof Copings Blown Not Porperly Installed - NWP |  | Contr | __R | WOO - Woolwich Station (East) |  | 2020-04-30 | 2020-03-10 09:53 | -51 | 2020-01-23 13:52 | Architectural - General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Some roof copings have been blown off the roof at NWP MEP building.
| 03SR - Stations (RfL) | Cxxx-NCR-000618 | NCR | Change out Waterproof Manual Call Points from KAC and replace with STI - All Areas |  | Contr | __R | WOO - Woolwich Station (East) |  | 2020-04-30 | 2020-03-13 08:45 | -48 | 2020-01-24 11:01 | Fire - Fire Systems & General | 3000 |  | Material | Rework | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | Due to lack availability of material KAC type manual call points were installed instead of STI weatherproof call points. The STI call points are now available and will replace the KAC manual call points.
| 03SR - Stations (RfL) | Cxxx-NCR-000619 | NCR | Door 2-577 Superficial Damage - West Box |  | Contr | __R | WOO - Woolwich Station (East) |  | 2020-03-28 | 2020-08-17 08:43 | 142 | 2020-01-28 13:57 | Architectural - Doors | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Door 2-577 has sustained superficial damage due to construction activities and lack of adequate care and protection.
| 03SR - Stations (RfL) | Cxxx-NCR-000620 | NCR | Failure to provide adequate protection - __ Telephone Tel 1031 - East Box |  | Contr | __R | WOO - Woolwich Station (East) |  | 2020-03-28 | 2020-04-08 08:09 | 11 | 2020-01-28 15:16 | Communications and Control Systems - Telephony | 2000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | __ telephone Tel 1031 (East Box) has sustained damage due to inadequate protection.
| 03SR - Stations (RfL) | Cxxx-NCR-000621 | NCR | Cxxx Labelling - Outstanding labels. |  | Contr | __R | WOO - Woolwich Station (East) |  | 2020-02-18 | 2020-02-14 08:20 | -4 | 2020-02-04 13:39 | Electrical - General | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Further to daily ‘Cxxx/Cxxx Common Incentive Framework’ meetings it became apparent that approximately 131nr asset/cable labels are not available on site. Neither Cxxx or Cxxx can confirm if the respective labels were ever delivered to site. So to move the asset labelling installation to completion we agreed to raise this NCR as a record. Labels (both white and yellow) are require for all item listed in the attached spreadsheets.
| 03SR - Stations (RfL) | Cxxx-NCR-000622 | NCR | Complete Application of Anti-Graffiti Paint at Connaugh MEP building and Headhouse |  | Contr | __R | WOO - Woolwich Station (East) |  | 2020-03-27 | 2020-02-11 15:04 | -45 | 2020-02-06 13:17 | Architectural - Walls | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | MEP face brickwork levels below DPC require painting with Anti-Graffiti paint. Also all outstanding areas of face brickwork areas of the Headhouse, require covering with Anti-graffiti paint to ensure all exposed face brickwork is covered.
| 03SR - Stations (RfL) | Cxxx-NCR-000623 | NCR | Complete Application of Anti-Graffiti Paint at NWP MEP Building External Face Brickwork |  | Contr | __R | WOO - Woolwich Station (East) |  | 2020-03-27 | 2020-02-12 14:47 | -44 | 2020-02-06 13:48 | Architectural - Walls | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | MEP face brickwork requires application with Anti-Graffiti Paint to areas as per approved design.
| 03SR - Stations (RfL) | Cxxx-NCR-000624 | NCR | Door D3-09 - Frame not plumb - Plumstead |  | Contr | __R | WOO - Woolwich Station (East) |  | 2020-05-29 | 2020-09-25 07:51 | 119 | 2020-02-18 11:41 | Architectural - Doors | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Door-frame for door D3-09 has been installed out of plumb.
| 03SR - Stations (RfL) | Cxxx-NCR-000625 | NCR | Defective Protection Layer of Roof Waterproofing System - West Box |  | Contr | __R | WOO - Woolwich Station (East) |  | 2020-04-25 | 2020-05-18 06:49 | 23 | 2020-02-25 09:22 | Architectural - Roofing & Exterior Treatment | 2500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Water trapped below roofing protection layer over West Box Ticket Hall maintenance corridor No. 756 - 1st Floor Level (as shown in attached marked up drawing)
| 03SR - Stations (RfL) | Cxxx-NCR-000626 | NCR | Upgrade Power Supply Cables and Xylem Cables to Sump Pumps - NWP |  | Contr | __R | WOO - Woolwich Station (East) |  | 2020-04-28 | 2020-04-21 14:09 | -7 | 2020-02-28 09:17 | Electrical - General | 30000 |  | Design | Repair | 2 (6-60k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Upgrade current Power supply cables and Xylem cables to Sump Pumps at NWP.
| 03SR - Stations (RfL) | Cxxx-NCR-000627 | NCR | Upgrade Power Supply and Xylem Cables to Sump Pumps - PLU |  | Contr | __R | WOO - Woolwich Station (East) |  | 2020-04-28 | 2020-03-26 15:18 | -33 | 2020-02-28 09:34 | Electrical - General | 30000 |  | Design | Repair | 2 (6-60k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | Upgrade current Power supply cables and Xylem cables to Sump Pumps at Plumstead Portal
| 03SR - Stations (RfL) | Cxxx-NCR-000628 | NCR | Platform Doors Not Compliant with MCR or App. Drawings - Plumstead |  | Contr | __R | WOO - Woolwich Station (East) |  | 2020-08-28 | 2020-07-17 10:09 | -42 | 2020-03-09 11:28 | Architectural - Doors | 6000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | The hinges of the platform doors installed at Plumstead Portal are not as discribed in the MCR or the approved Drawings.
| 03SR - Stations (RfL) | Cxxx-NCR-000629 | NCR | FCU's Installed Without Neon Indicators |  | Contr | __R | WOO - Woolwich Station (East) |  | 2020-07-28 | 2020-03-31 08:15 | -119 | 2020-03-30 12:40 | Electrical - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | FCU's have been installed without Neon Indicators instead of having Neon Indicators as required in project specifications as per CRL1-XRL-M-RSP-CR001-50085 JY74 and in particular clause JY74.1403 g ii
| 03SR - Stations (RfL) | Cxxx-NCR-000630 | NCR | Cxxx / Cxxx Vertical Pipework Support Brackets Track Side of the Flood Wall - NWP |  | Contr | __R | WOO - Woolwich Station (East) |  | 2020-04-30 | 2020-08-03 10:10 | 95 | 2020-04-03 13:16 | Fire - Fire Systems & General | 3000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The __ pipework dropping to track level from the flood wall cannot be adequately secured to the top of the wall structure to support the vertical weight of Cxxx pipe.
| 03SR - Stations (RfL) | Cxxx-NCR-000631 | NCR | Platform Doors Not Compliant with MCR or Approved Drawings - NWP |  | Contr | __R | WOO - Woolwich Station (East) |  | 2020-08-28 | 2020-07-17 06:44 | -42 | 2020-04-06 10:16 | Architectural - Doors | 6000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | The hinges of the platform doors installed at Nothr Woolwich Portal are not as described in the MCR or the approved Drawings.
| 03SR - Stations (RfL) | Cxxx-NCR-000632 | NCR | Woolwich Station East & West Box Sump System Non-Compliance. |  | Contr | __R | WOO - Woolwich Station (East) |  | 2020-07-31 | 2020-09-15 09:56 | 46 | 2020-04-08 10:15 | Electrical - General | 30000 |  | Design | Repair | 2 (6-60k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | LV non-compliance to BS7671 as depicted in the tech note Discrimination non-compliance to CRL spec
| 03SR - Stations (RfL) | Cxxx-NCR-000633 | NCR | 110V socket Circuit Ref DBTX01-5L2 to comply AMTECH Calculations - PLU |  | Contr | __R | WOO - Woolwich Station (East) |  | 2020-07-21 | 2020-05-22 08:09 | -60 | 2020-04-22 11:53 | Electrical - General | 6000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The 110V socket Circuit Ref DBTX01-5L2 has a circuit length of 88m exceeding the maximum circuit length by approximately 38m, as a result the circuit voltage drop exceeds the maximum of 8%.
| 03SR - Stations (RfL) | Cxxx-NCR-000634 | NCR | Water Ingress in the I&E Stair Roof - NWP |  | Contr | __R | WOO - Woolwich Station (East) |  | 2020-08-17 | 2020-08-06 10:31 | -11 | 2020-05-19 13:03 | Architectural - Roofing & Exterior Treatment | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The roof of I&E staircases at North Woolwich Portal it was observed a rainwater leak causing it to enter to the structure.
| 03SR - Stations (RfL) | Cxxx-NCR-000636 | NCR | Clarification to Naming Conventions for Power Supplies. |  | Contr | __R | WOO - Woolwich Station (East) |  | 2020-08-31 | 2020-07-17 10:30 | -45 | 2020-06-12 06:24 | Electrical - General | 2500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Address anomalies in the labelling of electrical equipment in the LVSR rooms with a view to replace the asset labelling and electrical labelling in compliance with Naming Conventions as directed in Cxxx-PMI-00627 (See attached).
| 03SR - Stations (RfL) | Cxxx-NCR-000637 | NCR | Clarification to Naming Conventions for Power Supplies. - NWP |  | Contr | __R | WOO - Woolwich Station (East) |  | 2020-08-31 | 2020-07-10 15:25 | -52 | 2020-06-12 08:55 | Electrical - General | 2500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | Address anomalies in the labelling of electrical equipment in the LVSR rooms with a view to replace the asset labelling and electrical labelling in compliance with Naming Conventions as directed in Cxxx-PMI-00627 (See attached).
| 03SR - Stations (RfL) | Cxxx-NCR-000638 | NCR | Clarification to Naming Conventions for Power Supplies. - PLU |  | Contr | __R | WOO - Woolwich Station (East) |  | 2020-08-31 | 2020-08-07 08:14 | -24 | 2020-06-12 09:02 | Electrical - General | 2500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Address anomalies in the labelling of electrical equipment in the LVSR rooms with a view to replace the asset labelling and electrical labelling in compliance with Naming Conventions as directed in Cxxx-PMI-00627 (See attached).
| 03SR - Stations (RfL) | Cxxx-NCR-000639 | NCR | Clarification to Naming Conventions for Power Supplies. - Woolwich Station |  | Contr | __R | WOO - Woolwich Station (East) |  | 2020-08-31 | 2020-10-20 13:08 | 50 | 2020-06-12 09:12 | Electrical - General | 2500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Address anomalies in the labelling of electrical equipment in the LVSR rooms with a view to replace the asset labelling and electrical labelling in compliance with Naming Conventions as directed in Cxxx-PMI-00627 (See attached).
| 03SR - Stations (RfL) | Cxxx-NCR-000641 | NCR | PRV Settings Evidence not issued - Plumstead Headhouse |  | Contr | __R | WOO - Woolwich Station (East) |  | 2020-08-17 | 2020-08-05 15:08 | -12 | 2020-06-18 10:26 | Mechanical - Public Health Engineering | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | No evidence or check sheet issued to demonstrate the PRV settings are set. Plumstead Portal Headhouse
| 03SR - Stations (RfL) | Cxxx-NCR-000642 | NCR | Non Demonstration of Fault Auto Evidence - Plumstead |  | Contr | __R | WOO - Woolwich Station (East) |  | 2020-08-17 | 2020-06-29 11:02 | -49 | 2020-06-18 09:58 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Inspection points not adequate | Completed |  | No evidence or check sheet issued to demonstrate the HVAC Twin Fans when in fault that an Auto change over occurs.
| 03SR - Stations (RfL) | Cxxx-NCR-000643 | NCR | Non-Compliance of LV Systems Power Factor (PF) |  | Contr | __R | WOO - Woolwich Station (East) |  | 2020-09-08 | 2021-07-03 15:18 | 298 | 2020-07-10 10:28 | Electrical - Power Distribution | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | The PF of the LV system at Connaught was recorded during the harmonic test surveys carried out across these sites. The PF recorded was not compliant with the Crossrail requirement. The Crossrail requirement is detailed in CRL1-XRL-M-RSP-CR001-50082, JY71 LV Switchgear and Distribution JY71.1201 e). The PF on the LVA system is lagging but is less than the required 0.98 minimum lagging power factor. The PF on the LVB system is leading and this is unacceptable because the requirement is for a minimum 0.98 lagging power factor.
| 03SR - Stations (RfL) | Cxxx-NCR-000644 | NCR | Non-Compliance of LV Systems Power Factor (PF) - NWP |  | Contr | __R | WOO - Woolwich Station (East) |  | 2020-09-08 | 2021-07-03 15:24 | 298 | 2020-07-10 10:35 | Electrical - Power Distribution | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | The PF of the LV system at North Woolwich Portal was recorded during the harmonic test surveys carried out across these sites. The PF recorded was not compliant with the Crossrail requirement. The Crossrail requirement is detailed in CRL1-XRL-M-RSP-CR001-50082, JY71 LV Switchgear and Distribution JY71.1201 e). The PF on the LVA system is lagging but is less than the required 0.98 minimum lagging power factor. The PF on the LVB system is leading and this is unacceptable because the requirement is for a minimum 0.98 lagging power factor.
| 03SR - Stations (RfL) | Cxxx-NCR-000645 | NCR | Non-Compliance of LV Systems Power Factor (PF) - PLU |  | Contr | __R | WOO - Woolwich Station (East) |  | 2020-09-08 | 2021-07-03 15:29 | 298 | 2020-07-10 10:43 | Electrical - Power Distribution | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | The PF of the LV system at Plumstead Portal and Substation was recorded during the harmonic test surveys carried out across these sites. The PF recorded was not compliant with the Crossrail requirement. The Crossrail requirement is detailed in CRL1-XRL-M-RSP-CR001-50082, JY71 LV Switchgear and Distribution JY71.1201 e). The PF on the LVA system is lagging but is less than the required 0.98 minimum lagging power factor. The PF on the LVB system is leading and this is unacceptable because the requirement is for a minimum 0.98 lagging power factor.
| 03SR - Stations (RfL) | Cxxx-NCR-000650 | NCR | Inaccurate As-built Earthing Schematic Drawing - NWP |  | Contr | __R | WOO - Woolwich Station (East) |  | 2020-10-04 | 2020-08-13 07:33 | -52 | 2020-08-05 14:01 | Electrical - Earthing & Bonding | 2000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | During on-site inspection CRL/RFL have found several inaccuracies with the as-built marked up Earthing Schematic drawing number presented Cxxx-__R-E-DDE-CR146_PT004_Z-10004 REV X03
| 03SR - Stations (RfL) | Cxxx-NCR-000651 | NCR | Use of Non-Adopable Pipe Material - NWP |  | Contr | __R | WOO - Woolwich Station (East) |  | 2020-08-26 | 2020-10-13 13:32 | 48 | 2020-08-12 15:02 | Civil - Drainage | 3000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The pipe material used on the below ground drainage installation has not been designed to meet the requirements of the __ sewerage sector guidance and is therefore not considered adoptable under Section 102 of the Water Industry Act 1991. Requirements for installation of below ground drainage to an adoptable standard is contained within Cxxx-XRL-Z8-ACT-CR001-50005 Cxxx - Book 4 - Vol 2C Technical Works Information and Vol 3 Site Information - __ Group Ltd : Woolwich Box and Portal Fit-Out the works information.
| 03SR - Stations (RfL) | Cxxx-NCR-000652 | NCR | Electrical Completions Report - PLU - Outstanding issues |  | Contr | __R | WOO - Woolwich Station (East) |  | 2020-09-16 | 2020-08-28 09:40 | -19 | 2020-08-17 14:26 | Electrical - Lighting | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | The NCR is as a result of not having maintained the 25% spare capacity which is a requirement within the CRL specification.
| 03SR - Stations (RfL) | Cxxx-NCR-000653 | NCR | Door opening forces - WOO |  | Contr | __R | WOO - Woolwich Station (East) |  | 2021-09-09 | 2021-07-23 13:58 | -48 | 2020-08-19 09:59 | Architectural - Doors | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The Cxxx Standards baseline includes Standard LUL1-134 Premises Doorsets and Glazing, this standard requires Building Regulations to be met for all doors. ADM2 sets maximum opening force requirements for manually operated doors. Architectural Specification Cxxx-__R-A-RSP-CR147-50001 sections JL20.1326 and JP21.1304 require that that the maximum opening pressures required to open fire rated or non-fire rated doors on disabled access routes are in accordance with the requirements of BS 8300. ADM2 and BS8300 Section 6.5.2 limit the opening force at the leading edge of the door to not more than 30 N from the door in the closed position to 30° open, and not more than 22.5 N from 30° to 60° of the opening cycle. BS8300 Section 6.5.6.1 limits the release forces for panic exit devices operated by a horizontal bar to no greater than 80 N. A spot-check on doors 4-631 as installed on escape route ESS II (SID number 1/518) from the platforms found the forces required to open the doors substantially exceeded the BS8300 requirement, therefore these doors as designed and installed do not comply with the Works Information. All public operated doors, escape doors and doors to staff accommodation must comply with the requirements of BS8300, so to ensure compliance the contractor should measure and report the opening forces on these doors and rectify any additional non-compliances found. This non-compliance has implications for safe operation of the station and requires confirmation that all relevant doors meet BS8300 manual operation forces in their end commissioned state. Rectification of this noncompliance is necessary before passenger operations.
| 03SR - Stations (RfL) | Cxxx-NCR-000654 | NCR | Damage to Ruggerised Telephone - Sump Pump Room 771 - PLU Portal |  | Contr | __R | WOO - Woolwich Station (East) |  | 2020-10-20 | 2020-09-08 10:05 | -42 | 2020-08-21 09:29 | Communications and Control Systems - Telephony | 3000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | The telephone in Room 771 - Sump pump room - Plumstead Portal was provided with protection during time of installation but had since incurred damage by persons unknown.
| 03SR - Stations (RfL) | Cxxx-NCR-000655 | NCR | Non-compliant handrail I&E Stairs - North Woolwich Portal |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2020-09-26 | 2020-10-14 10:40 | 18 | 2020-08-29 16:43 | Architectural - Handrail | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | This NCR has been raised at the request of RFLi. The Intervention and Escape stairs have not been designed to S1371 Station Capacity Planning document. As per the S1371 standard the handrail and landing on the I&E stairs are non-compliant. The stairs have been designed to __ Group Standards, Approved document B, BS9999, Technical specifications Infrastructure
| 03SR - Stations (RfL) | Cxxx-NCR-000656 | NCR | Non-compliant handrail Escape Stairs- Plumstead Portal |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2020-09-26 | 2020-10-14 12:17 | 18 | 2020-08-29 17:09 | Architectural - Handrail | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Two outer rail handrails on the escape staircase at Plumstead Portal are approximately 20 to 30mm short of the 300mm requirement. All other handrails comply with the 300mm requirement.
| 03SR - Stations (RfL) | Cxxx-NCR-000657 | NCR | Damaged Sump Room Doors D2-771 - NWP |  | Contr | __R | WOO - Woolwich Station (East) |  | 2020-12-02 | 2020-12-10 09:12 | 8 | 2020-09-23 15:05 | Architectural - Doors | 6000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Sump Room Doors (D2-771) are distorted and unable to close fully.
| 03SR - Stations (RfL) | Cxxx-NCR-000658 | NCR | WOO-W Fan room Design Assumptions |  | Contr | __R | WOO - Woolwich Station (East) |  | 2020-10-22 | 2021-01-21 12:48 | 91 | 2020-09-24 08:46 | Environmental - Noise and Vibration | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Design stage calculations demonstrated compliance with D25 requirements at receptor R11. Subsequently, it was found that the calculations did not adequately represent the contribution of breakout noise from the fan room and, if updated, D25 compliance would not have been demonstrated at that stage of the design.
| 03SR - Stations (RfL) | Cxxx-NCR-000659 | NCR | Door opening forces - PLU Portal |  | Contr | __R | WOO - Woolwich Station (East) |  | 2020-11-28 | 2021-07-17 10:43 | 231 | 2020-09-29 10:35 | Architectural - Doors | 3000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The Cxxx Standards baseline includes Standard LUL1-134 Premises Doorsets and Glazing, this standard requires Building Regulations to be met for all doors. ADM2 sets maximum opening force requirements for manually operated doors. Architectural Specification Cxxx-__R-A-RSP-CR147-50001 sections JL20.1326 and JP21.1304 require that that the maximum opening pressures required to open fire rated or non-fire rated doors on disabled access routes are in accordance with the requirements of BS 8300. ADM2 and BS8300 Section 6.5.2 limit the opening force at the leading edge of the door to not more than 30 N from the door in the closed position to 30° open, and not more than 22.5 N from 30° to 60° of the opening cycle. BS8300 Section 6.5.6.1 limits the release forces for panic exit devices operated by a horizontal bar to no greater than 80 N. A spot-check on doors 4-631 as installed on escape route ESS II (SID number 1/518) from the platforms found the forces required to open the doors substantially exceeded the BS8300 requirement, therefore these doors as designed and installed do not comply with the Works Information. All public operated doors, escape doors and doors to staff accommodation must comply with the requirements of BS8300, so to ensure compliance the contractor should measure and report the opening forces on these doors and rectify any additional non-compliances found. This non-compliance has implications for safe operation of the station and requires confirmation that all relevant doors meet BS8300 manual operation forces in their end commissioned state. Rectification of this noncompliance is necessary before passenger operations.
| 03SR - Stations (RfL) | Cxxx-NCR-000660 | NCR | Non-Compliance of LV Systems Power Factor (PF) - WOO |  | Contr | __R | WOO - Woolwich Station (East) |  | 2021-09-01 | 2021-07-03 15:39 | -60 | 2020-10-09 12:45 | Electrical - Power Distribution | 2500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | The installed cable one single cable (1x 150mm2 4C) between each main LV switchboards (LVA and LVB) at Woolwich Station (East and West Box) and the PFC cabinet is not protected by the 630A protective devices within the main LV switchboards. This is because the current carrying capacity of the installed cable is less than the rating of the protective device (630A) protecting it.
| 03SR - Stations (RfL) | Cxxx-NCR-000661 | NCR | Plumstead portal external gate to secure compound - Door monitoring junction Box |  | Contr | __R | WOO - Woolwich Station (East) |  | 2020-12-09 | 2020-12-16 16:32 | 7 | 2020-11-11 11:39 | Electrical - General | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | incorrect IP rated washers have been installed which has allowed the water ingress from the conduit and associated fittings. Junction box will need to be replaced and terminated.
| 03SR - Stations (RfL) | Cxxx-NCR-000662 | NCR | Lighting Single Point of Failure - WOOLWICH STATION |  | Contr | __R | WOO - Woolwich Station (East) |  | 2021-01-31 | 2021-01-21 13:56 | -10 | 2020-11-11 11:47 | Electrical - Lighting | 6000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The following areas at Woolwich Station have been identified as being non-compliant with CRL single point of failure (SPoF) requirements, LU 1-066 standard requirements and F1 design. West Box Escalator Equipment Room (EER) : The room is served by 8no luminaires connected on one emergency lighting circuit and loss of this circuit will result in total room darkness. LU 1-066 standard requires rooms greater than 50mm2 to be served by at least 2 circuits in line the F1 design. The installation is therefore not complaint with CRL single point of failure (SPoF) requirements, LU 1-066 standard requirements and F1 design. The remedial works are included in Cxxx-FCD-001400. East Box Maintenance Stairs (MNS II) The maintenance stairs are served by 11no luminaires connected on one emergency lighting circuit and loss of this circuit will result in the total darkness of the stairs. The installation is therefore not complaint with CRL single point of failure (SPoF) requirements. The remedial works are included in Cxxx-FCD-001400.
| 03SR - Stations (RfL) | Cxxx-NCR-000663 | NCR | Bronze clad door selectors |  | Contr | __R | WOO - Woolwich Station (East) |  | 2021-09-30 | 2021-09-29 14:24 | -1 | 2020-12-08 13:00 | Architectural - Doors | 25000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The station escape doors must close fully irrespective of which leaf is used for escape, in order to maintain fire protection to the escape route. The door selectors that have been installed have been found not to work in all circumstances. For example on the bronze faced doors at platform level, when the passive leaf is used for escape the opening of the passive leaf does not open the active leaf far enough for the selector to work, so the passive leaf is prevented from closing by catching on the flat side of the mortice latch of the active leaf. In addition to the incompatibility of the door design and the selectors, the selectors are not proving robust. Both styles of selector used on the Cxxx sites so far are easily damaged and then fail to work. BS9999 requires fire doors to close fully. The consequence of the door selectors not working, for whatever reason, is that the fire rating of the door will be voided. If the design of the doors requires a selector, the selector must be dependable and work in all circumstances.
| 03SR - Stations (RfL) | Cxxx-NCR-000664 | NCR | Gate Connaught Support Building |  | Contr | __R | WOO - Woolwich Station (East) |  | 2021-02-05 | 2021-03-26 07:13 | 49 | 2021-01-22 15:51 | Architectural - General | 2000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The lock latch at the Connaught Support Building external gate is faulty.
| 03SR - Stations (RfL) | Cxxx-NCR-000665 | NCR | __ enclosures causing damage to Cxxx assets |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2021-10-28 | 2021-09-21 12:31 | -37 | 2021-02-03 13:02 | Communications and Control Systems - Public Address Systems | 5000 |  | Damaged | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | enclosure doors housing Cxxx PHP assets x4 (00002, 00302, 00305 & 00306) not closing correctly and causing damaging including scratching/ scuffing.
| 03SR - Stations (RfL) | Cxxx-NCR-000666 | NCR | Damaged Containment WB Roof |  | Contr | __R | WOO - Woolwich Station (East) |  | 2021-03-31 | 2021-03-15 13:28 | -16 | 2021-03-01 13:56 | Architectural - Roofing & Exterior Treatment | 2500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Damaged containment on the west box roof, it will need to have re-works carried out to correct
| 03SR - Stations (RfL) | Cxxx-NCR-000667 | NCR | BMS Monitoring of VRF Indoor FCU Electrical Isolation |  | Contr | __R | WOO - Woolwich Station (East) |  | 2021-03-26 | 2021-03-15 08:34 | -11 | 2021-03-12 10:43 | Mechanical - Mechanical Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Following on from CRL/__ meetings on 03/03/21 & 10/03/21 refer to document Cxxx-__R-M-MRC-CR147-50011. The requirements set out in JW60.1200 xviii) are not being met with regards to __ VRF FCU’s, namely if either the RUN or STANDBY FCU is electrically isolated it does not show as in fault on the BMS software.
| 03SR - Stations (RfL) | Cxxx-NCR-000668 | NCR | Replacement TVS Doors - __ SR3 Steel Doors |  | Contr | __R | WOO - Woolwich Station (East) |  | 2021-06-24 | 2021-10-29 15:02 | 127 | 2021-04-15 20:30 | Architectural - Doors | 60000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | 8 doors with the WOO Eastbox Tunnel Ventilation System area are failing under pressurised conditions and require replacing as the integrity of the door structure has been damaged.
| 03SR - Stations (RfL) | Cxxx-NCR-000669 | NCR | Faulty door handle on door CR505-BAF-00079 026 - Plumstead Portal |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2021-07-13 | 2021-06-30 07:31 | -13 | 2021-06-29 15:04 | Architectural - Doors | 1500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Faulty door handle on door CR505-BAF-00079 026 - Plumstead Portal PFU-2-00019 Door System (Arch) at Plumstead Portal FAC-2-040 Plumstead Portal
| 03SR - Stations (RfL) | Cxxx-NCR-000670 | NCR | Air Handling Unit (AHU) breakdown into components - L7515 - Air Handling Unit (AHU) |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2021-08-16 | 2021-08-14 13:51 | -2 | 2021-07-26 08:59 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Not Defined | Completed |  | The current iteration of CRL1-XRL-Z3-ADDSD-CR001-50113 Rev 9 details L7515 - Air Handling Unit (AHU) as that they will typically provide more than one HVAC function e.g. air movement, heating, cooling, filtration and will have no sections of ducting between these functions. The requirement is currently to have the maintainable items within the Air Handling Unit to be tagged and labelled (as required) as separate items, these include the individual fans, filters etc. The base function of an AHU is to supply conditioned air. As detailed there are no sections of ducting between these components hence they are a single entity. The components within the AHUs are integral to the system as a whole not as individual components. If a maintainable component breaks within the AHU the system does not operate as a whole and has to switch to the standby unit. All components (fans, motors etc.,) are branded by the manufacturer of the AHU and this is where the IM will procure replacement parts if required. The requirement for asset identification is to make the maintenance of the units simple. The IM is directed to one source of information from one asset tag (not numerous ones). Please note that filters are considered consumables and are not asset identified. Cxxx created AHU assets in AIMS in early June 2017 as individual systems (not broken down into components). All details for AHUs are captured within CRL-MCR-004653. This includes drawings and technical information from Flacktwoods. Cxxx are asking for the asset identification requirement to be a Use as Is with one identification for an individual Air Handling Unit.
| 03SR - Stations (RfL) | Cxxx-NCR-000671 | NCR | Hattersley valve range - individual Model identifiers |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2021-09-20 | 2021-09-07 06:42 | -13 | 2021-09-06 08:42 | Mechanical - Piping | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | The current iteration of CRL1-XRL-O6-STD-CR001-00031_Rev12 (CR-STD-015 ASSET IDENTIFICATION STANDARD) details the structure for the Equipment Numbers and naming of the individual Model identifiers for ‘L7172 - Valves’ to be created by the contractors. Section 6.2 Equipment Name Structure. Cxxx used an equipment number(s) generated by another CRL project as the model number(s) already existed within eB and AIMS. The model(s) used were for valves manufactured by Hattersley, and as per the data sheet attached to the Cxxx MCR did not contain unique part number for each size of the valve; for example EQ00007105 ’FIG.100’ which is a ‘Ball Valve - Compression Ended DZR - Lever Operated’ valve procured from Hattersley. This instance of valve comes in multiple sizes from 1/4" to 2" which is the differentiator when procurement is made. Cxxx did not create a new equipment number via an ERF request, creating a bespoke model number for each size for the Hattersley range I.e giving FIG.100-1/4” to FIG.100-2” Cxxx have captured all the dimensional information for each valve within the asset description and the attribute meta data, this will allow the end user to find the manufacturer of the equipment and the size required to facilitate the valve function if/when a replacement is required. This has only been in this manner for the Hattersley valves, all other valves in use upon Cxxx have either been created with bespoke model numbers, to include the size, or a unique produced number was available via the manufacturers data sheet(s). See affected EQs
| 03SR - Stations (RfL) | Cxxx-NCR-000672 | NCR | Cxxx Connaught Support Building - Surge Protection Fault |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2021-10-26 | 2021-10-12 09:05 | -14 | 2021-10-12 08:45 | Electrical - LV Equipment | 5000 |  | Damaged | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | Surge Protection Fault to surge protection unit within LVA switchboard located in Switch Room 1/611.
| 03SR - Stations (RfL) | Cxxx-NCR-000673 | NCR | Cxxx North Woolwich Portal - Surge Suppression Unit Fault to Asset TAG: CR146-LPS-00001 |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2021-10-27 | 2021-10-13 09:34 | -14 | 2021-10-13 09:25 | Electrical - LV Equipment | 5000 |  | Damaged | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | Surge Protection Fault to surge protection unit within LVB switchboard at North Woolwich Portal.
| 03SR - Stations (RfL) | Cxxx-NCR-000674 | NCR | Cxxx Plumstead Portal - Leaking Roof Ladder Hatch Located at A/081 |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2021-11-09 | 2021-10-26 15:00 | -14 | 2021-10-26 14:47 | Architectural - Security | 2000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Plumstead Portal: Leak from Ladder Roof Hatch CR505-BAF-00054 over Lobby Room A/081. Civils investigated and also observed Hydraulic Hatch Opening System oil leak under pressure and hatch not opening or closing properly.
| 03SR - Stations (RfL) | Cxxx-NCR-000675 | NCR | Cxxx Connaught Support Building - Bus Coupler Installation- 3 pole MCCB and solid neutral bus-coupler |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2021-11-25 | 2021-11-11 13:50 | -14 | 2021-11-11 13:40 | Electrical - LV Equipment | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | A 3 pole and solid neutral bus-coupler has been installed on the LV-B Switchboard at the Connaught support building. This does not align with all other Cxxx sites and is not as per the Crossrail works information. A 4 pole MCCB is required to be installed.
| 03SR - Stations (RfL) | Cxxx-NCR-000676 | NCR | 1/230 (Passage) O/S 1/667 (UPS Room) leak in Plumstead Portal |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2021-12-04 | 2021-11-20 13:51 | -14 | 2021-11-20 13:42 | Architectural - Roofing & Exterior Treatment | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Plumstead portal leaking penetration by the door 1/230 in the lobby area . Also on the Ground Floor Level at PLP, at the locations below : • 1/666 Switch Room • 1/440 Toilet • Outside 1/778 Riser • Outside 1/667 UPS Room
| 03SR - Stations (RfL) | Cxxx-NCR-000677 | NCR | Cxxx Woolwich Station: Accessibility & Maintainability of Fire Header Tanks |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2022-10-19 | 2022-10-05 12:07 | -14 | 2022-10-05 11:58 | Fire - Suppression | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Space for accessibility & maintainability of Fire Header Tanks in 1/361 (East Ticket Hall) and 1/360 (West Ticket Hall) not acceptable. Remedial works as detail in meeting held between CRL and RFLi on 05 August to be undertaken.
| 03SR - Stations (RfL) | Cxxx-NCR-000678 | NCR | CRL-NDF-00159 Cxxx Woolwich Station - Defective Tubular Heater Above Door SID 1/230 |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2022-11-28 | 2022-11-14 13:57 | -14 | 2022-11-14 13:52 | Electrical - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The Overhead Tubular Heater above Door SID - 1/230 in Ticket Hall by Gate Line near SCU not functional. Heater keeps tripping __. Supply feeding heater has been checked by technician and is ok.
| 03SR - Stations (RfL) | Cxxx-NCR-000679 | NCR | CRL-NDF-00179 Cxxx Plumstead Sub-Station - Water Ingress to Cxxx LV Cable Box |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2022-11-28 | 2022-11-14 14:16 | -14 | 2022-11-14 14:04 | Electrical - Transformers | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Cxxx Plumstead Sub-Station - Water Ingress to Cxxx LV Cable Box: Details: Following Investigation water ingress found to be continuing as per pre handover checks. LV busduct connection to LV cable box letting in water. CRL defect to be raised to rectify IP Rating non-compliance.
| 03SR - Stations (RfL) | Cxxx-NCR-000680 | NCR | Cxxx - Woolwich Box and Portal Fit-Out - Defective Door Isolator Switching Mechanism |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2022-12-12 | 2022-11-28 14:01 | -14 | 2022-11-28 13:57 | Electrical - LV Equipment | 500 |  | Equipment Breakdown | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Investigate/Replace door switching mechanism for ATS-6 - Supply B cabinet.
| 03SR - Stations (RfL) | Cxxx-NCR-000681 | NCR | Cxxx - Woolwich Box and Portal Fit-Out - Traffolyte Labels to A/C Interface Panels |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2022-12-22 | 2022-12-08 16:42 | -14 | 2022-12-08 16:36 | Electrical - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | The Cxxx A/C Interface Panels have LIVE 230V Circuits inside when the Main Isolator for the panel is in the ‘OFF’ position. BS7671 compliant multiple supplies labels are not installed on the A/C Interface Panel doors indicating there are LIVE 230V Circuits inside.
| 03SR - Stations (RfL) | Cxxx-NCR-000682 | NCR | Cxxx - Woolwich Box and Portal Fit-Out - Multiple Lights Out at WOO Station Ticket Hall |  | Crossrail | XRL | WOO - Woolwich Station (East) |  | 2023-01-30 | 2023-01-19 13:06 | -11 | 2023-01-16 13:15 | Electrical - Lighting | 500 |  | Equipment Breakdown | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Detailed Description of Defect: Multiple lights out at WOO station ticket hall. Technicians reported “We reset __ 10L3 to see if that would work but the strip would still not illuminate. After looking at Lightscape through the BMS system, the only failure was LCM-11-B lamp12. We checked this lamp/ballast and it was found working which would suggest there is an error with the DALI system. Due to it being multiple lamps within the one strip this may also indicate a local controller is in fault”.
| 05SY - Systemwide | Cxxx-NCR-000001 | NCR | Start of Works without Accepted ITP |  | Contr | SKC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-01-29 | 2015-01-13 07:24 | -16 | 2014-12-23 16:20 | Track - Track General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Construction of the Connaught DFF demonstration track commenced without an accepted ITP in place.
| 05SY - Systemwide | Cxxx-NCR-000002 | NCR | Delivery of non-qualified products (Direct Fastenings Baseplates) |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-09-03 | 2015-09-02 08:25 | -1 | 2015-02-17 18:41 | Track - Track General | 10000 |  | Material | Rework | 2 (6-60k) | Complete | Verification Problems - Other | Completed |  | 1100 No. Delkor Alt 1 RF 196 baseplates (+ balance of 2000 No. to come) non-compliant baseplates (failed qualification test) have been delivered to site at Connaught. Please see attached __ NCR report and Supplier's NCR report.
| 05SY - Systemwide | Cxxx-NCR-000003 | NCR | Connaught Tunnel - Track Slab Concrete Test Cube Storage |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-06-26 | 2015-05-22 14:04 | -35 | 2015-03-19 16:16 | Materials - Approval | 1000 |  | Material | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Not Defined | Completed |  | The Contractor has provided an on-site facility for __ to store test equipment and manufactured cubes before transportation back to the laboratory. On review of the facility it was noticed that the cabin had no max/min temperature control in place and no records to detail acceptable curing conditions (20±5oC) as required for initial curing of concrete samples. Additionally the store had 4 no. stripped cubes sitting on the side not covered (photo available), which were manufactured following concreting on the 17th March; the cabin had no water tank present. The temperature measured in the cabin was recorded as 11oC. The non storage of cubes in accordance with BS 12390 could have an impact on the compressive strength results (28 days) of the cubes.
| 05SY - Systemwide | Cxxx-NCR-000004 | NCR | Materials Compliance - Contractor Verification and Validation Process |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-06-11 | 2015-05-18 09:20 | -24 | 2015-03-18 09:29 | Materials - Approval | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Not Defined | Completed |  | The Systemwide Materials Compliance Process Surveillance Report issued on 11-Mar 2015 under Cxxx-PMC-00651 identified a number of deficiencies with the Contractors materials compliance verification and validation activities as described in Works Information Volume 2B Part 20.7 which states that verification of the quality and material traceability of each element of the works shall be the responsibility of the Contractor and shall be achieved through checks, tests, inspections, audits and reviews. The Contractors 'Approval and Acceptance of Materials, Products and Plant’ procedure Cxxx-__-O4-GPD-CRG03-50016 Rev 2 details how this will be achieved in Appendix 1. At the time of surveillance no evidence could be obtained to demonstrate that checks had been carried out by the Contractor on material traceability or quality related certification of products, related materials or suppliers.
| 05SY - Systemwide | Cxxx-NCR-000005 | NCR | DFT Slab Crack Inducer Installation |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-08-07 | 2015-07-27 15:44 | -11 | 2015-04-14 15:07 | Civil - Track | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | A profiled metal section was cast into the top of the slab track to assist with the formation of crack inducer relief joints at designated locations as shown on drawing Cxxx-__-R4-DDA-CR146_Z-23719. The intension was to remove the metal strip prior to the concrete setting. At panels C90 and C89 the profiled metal strip used to form the stress relief joint was not be removed post completion of the concrete pour and remains embedded in the surface of the slab track. (See photographs attached).
| 05SY - Systemwide | Cxxx-NCR-000006 | NCR | Flooding to the Royal Docks Management Authority Ltd’s (RoDMA) Plant Rooms |  | Contr | SKC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-11-20 | 2015-12-02 13:32 | 12 | 2015-05-07 17:36 | Consents - Environment | 50000 |  | Supervision/Management | Rework | 2 (6-60k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | As part of Cxxx’s dewatering operations at Connaught Tunnel, __ commenced a trial pumped diversion of some of the dewatering waters into the __ sewer system, via a storm water gully, as a controlled discharge within the approved consent limit [Case Ref RBEC0JE4]. However, the discharge was made into the incorrect sewer location, that was not on the consent.
| 05SY - Systemwide | Cxxx-NCR-000007 | NCR | Concrete cubes exceeded time allowed to remain in their moulds |  | Contr | SKC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-06-30 | 2015-06-09 14:33 | -21 | 2015-05-15 09:24 | Civil - Track | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | BS EN 12390-22009 part 2 requires that test specimens remain in their mould no longer than 3 days. Concrete cube sets 17 and 18, cast on 30/04/2015 were found in their moulds on 05/05/2015, exceeding by 2 days the maximum time allowed before stripping them.
| 05SY - Systemwide | Cxxx-NCR-000008 | NCR | DFT Post Concrete Pour Inspections and Associated Records |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-09-09 | 2015-08-28 12:12 | -12 | 2015-05-20 12:39 | Track - Track General | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | On the 13th May 2015, a surveillance was carried at Connaught site office on the post concrete pour inspection regime carried out to date for the Direct Fix Track (DFT). The surveillance consisted of an inspection of the recorded checks on Inspection and Test Plan (ITP) check sheets being completed by the Contractor as detailed in section 5 of ITP, reference Cxxx-__-R4-ITP-CRG03-50001 Rev 4.0. It was identified that there are no completed post concrete inspection records for the sections of DFT slab constructed to date. Furthermore, it was identified that the Contractor is not carrying out the void checks to the underside of the baseplates every 100m, in accordance with item 5.3 of the ITP, reference Cxxx-__-R4-ITP-CRG03-50001 Rev 4.0.
| 05SY - Systemwide | Cxxx-NCR-000009 | NCR | Defective T-Head Screws HS32-55 associated with 27KN/mm2 baseplates for Connaught Tunnel |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-07-15 | 2015-07-15 15:27 | 0 | 2015-05-27 16:23 | Track - Rails and Sleepers | 500 |  | Manufacturing Defect | Reject | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | From the batch of T-Head Screws delivered on 15/04/2015, which has not yet been used, 8 No have been found with no thread.
| 05SY - Systemwide | Cxxx-NCR-000010 | NCR | Slump test out of tolerance |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-07-21 | 2015-07-20 14:07 | -1 | 2015-05-27 16:24 | Track - Track Bed | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | One batch of concrete was slumped at the back of the ready mix delivery truck and was within the tolerance. After transfer into the MPV and transport to site, the concrete slump tests performed on two samples (taken from the MPV) of the concrete used for the EB Connaught permanent works were 60 and 70mm, out of the range of an S3 mix (80-170 mm). However the concrete was used between CH18371 and 18386
| 05SY - Systemwide | Cxxx-NCR-000011 | NCR | Time between concrete batching time and concrete placing exceeded |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-07-28 | 2015-07-20 08:54 | -8 | 2015-05-27 16:24 | Track - Track Bed | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Cage 160 was already half concreted when the MPV broke down after discharging one load of concrete. This caused a delay on the next concrete transfer from ready mix truck to MPV. At the time of pouring the concrete, the maximum time of 2 hours from batch time was exceeded by 20 min. However, it was assessed that the concrete was still compacting (pictures and video available) and therefore the conrete was poured to avoir a cold joint in the cage as it would have taken an hour longer to get a new concrete load. Time exceeded the 2 hours specified.
| 05SY - Systemwide | Cxxx-NCR-000012 | NCR | No concrete under one baseplate on cage 153 |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-08-11 | 2015-08-11 08:01 | 0 | 2015-05-27 16:26 | Track - Track Bed | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Second baseplate from low to high chainage on the right rail of cage 153 (CH18377.5). There is a void of approximately 20mm under the baseplate (pictures available).
| 05SY - Systemwide | Cxxx-NCR-000013 | NCR | Damaged Concrete After Metal Profil Crack Inducer Removal |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-07-28 | 2015-07-28 15:27 | 0 | 2015-05-27 16:23 | Track - Track General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Connaught Tunnel Area 2 CH18464.966 (between cages C135 and C137). After removal of the metal profil to create the crack inducer, the concrete around the joint appears to be damaged or not properly finished. (pictures available)
| 05SY - Systemwide | Cxxx-NCR-000014 | NCR | Records |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-07-29 | 2015-07-29 15:36 | 0 | 2015-05-29 13:05 | Civil - Track | 1000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | During a planned surveillance a review found the ITP does not stipulate at which stage the post pour checks are to be carried out: the checks that include: concrete level, slab dimensions, concrete finish, free from cracks and the curing process undertaken. The checks on the above check sheets appear to have been carried out on one visit per check sheet as there no dates against individual checks. The post pour checks must be progressive, with the curing process commencing on completion of concreting works. Any cracking of the concrete may not become apparent for several days. Increased post pour checks will highlight potential quality related issues that can be prevented in future pours.
| 05SY - Systemwide | Cxxx-NCR-000015 | NCR | Inspection and Test Plan (ITP) |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-08-18 | 2015-08-26 08:06 | 8 | 2015-05-29 13:06 | Civil - Track | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Verification Problems - Inspection points not adequate | Completed |  | On reviewing the Inspection and Test Plan (ITP) ITP Cxxx-__-R4-ITP-CRG03-50001 rev 4.0 it was noted that the post pour concrete checks do not include, how it is determined that the concrete has cured sufficiently to remove the formwork, rail jigs and protection. The Method Statement (MS) Cxxx-__-R4-GMS-CRG03-50005 rev 4.0 decal code 1 states: (1) Shutters will be removed 12 hours (subject to concrete strength confirmation) after concreting by the team in charge of transferring all the material forward to the construction front. (2) Transfer formwork to next construction block by means of the MPV. After 16 hours (subject to concrete strength confirmation) (3) Re-fasten rails/baseplates. After 14 days (subject to concrete strength confirmation). As this is a validation process, it must be recorded and as such be an activity within the ITP, with a hold point intervention for the Contractor.
| 05SY - Systemwide | Cxxx-NCR-000016 | NCR | Displaced Rebar Cage |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-07-29 | 2015-07-02 09:19 | -27 | 2015-06-08 09:43 | Track - Track Bed | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Connaught Tunnel Area 3 CH18080.166 (between cage C210 and C211) During concreting operation the rebar cage slightly slid longitudinally, causing the rebar to touch the plastic duct of the duct crossing.
| 05SY - Systemwide | Cxxx-NCR-000017 | NCR | Quality of Received Reinforcement Cages |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-07-29 | 2015-07-28 08:11 | -1 | 2015-06-08 11:05 | Track - Track Bed | 5000 |  | Manufacturing Defect | Rework | 3 (3-6k) | Complete | Subcontractor Problems - Other | Completed |  | Connaught Tunnel – Reinforcement Cages for Areas 4 to 7 • Some cages have arrived with dimensions out of tolerances (see attached report). • Some cages have arrived damaged (crushed chairs). • Cages are not sufficiently stiff (chairs not adequate).
| 05SY - Systemwide | Cxxx-NCR-000018 | NCR | Remedial works implemented without CRL acceptance of proposal |  | Contr | SKC | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-07-29 | 2015-07-22 07:57 | -7 | 2015-06-10 17:21 | Track - Track Bed | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | A technical solution was proposed in response to Cxxx-NCR-0005, but has been implemented on site before the solution was accepted by CRL.
| 05SY - Systemwide | Cxxx-NCR-000020 | NCR | Concrete Slump Issue |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-09-23 | 2015-09-25 13:21 | 2 | 2015-06-17 11:38 | Track - Track Bed | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | On the 16/06/2015 at 10:08 during concreting operation at Connaught Tunnel Area 4 from CH 17642.660 to 17657 (cages 293 to 295) the slump test results from the delivery truck was 100mm (Delivery note: 10161251; fleet number: RX14SXP; Batch time: 08:51). The laod was then pumped into the MPV and brought to site. Slump tests from the MPV was 70mm which is out of the S3 slump limit.
| 05SY - Systemwide | Cxxx-NCR-000021 | NCR | Commencing Works without an Accepted ITP |  | Crossrail | XRL | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-08-19 | 2015-08-28 17:14 | 9 | 2015-06-18 11:18 | Civil - Track | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The Inspection and Test Plan for the manufacture of the switching and crossings (S&C’s) at Victoria Dock Portal and Custom House was received from the Contractor on 11th June 2015. Whilst an inspection and test plan was in place for the manufacturing process, it is understood that the manufacture of the S&C’s commenced without first obtaining a Code 1 acceptance of the Inspection and Test Plan from the Supervisor. In accordance with Works Information, Volume 2B, Part 20.8, The Contractor shall not start the relevant works until the Supervisor has accepted the ITP.
| 05SY - Systemwide | Cxxx-NCR-000022 | NCR | Anchor Dowels Setting |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-07-30 | 2015-07-20 08:56 | -10 | 2015-06-23 17:08 | Track - Track Bed | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Connaught Tunnel Eastbound cages 329 & 330 Some of the anchor dowels installed under those cages are up to 7mm lower than the tolerance specified on the drawing Cxxx-__-R4-DDA-CR146_Z-10320. In cage 329, we have 6 dowels which are protruding 73mm to 79mm from the stage 1 concrete instead of the minimum 80mm. In cage 330 we have 7 dowels which are protruding 73 to 78mm from the stage 1 concrete instead of the minimum 80mm. Design Team to review.
| 05SY - Systemwide | Cxxx-NCR-000023 | NCR | Water Seeping Through The Slab |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2016-05-10 | 2016-05-10 12:39 | 0 | 2015-07-01 14:40 | Civil - Track | 5000 |  | System Defect | Repair | 3 (3-6k) | Complete | External Phenomenon - Other | Completed |  | It has been noted that water has made its way up through the track slab and through the side of slab on cage 169 (approximately at CH18294).There appears to be a slow trickle of water coming through. It has also been noted that the water is coming from underneath some slabs on the East ramp (approximately at CH18350). Photographs will be sent in due course.
| 05SY - Systemwide | Cxxx-NCR-000024 | NCR | Commencing Works without an accepted ITP - SBC |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-10-06 | 2015-09-25 13:39 | -11 | 2015-07-01 15:08 | Track - Rails and Sleepers | 1000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | The manufacture of the STS Sleepers commenced without first obtaining a Code 1 acceptance from the Supervisor.
| 05SY - Systemwide | Cxxx-NCR-000025 | NCR | Unplanned Concrete Joint |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-07-31 | 2015-07-15 09:11 | -16 | 2015-07-01 16:31 | Track - Track Bed | 2500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Insufficient quantity of material to do the job | Completed |  | 22/06/2015 16:00 Due to a problem with concrete supply, the bay C275 could not be completed and an unplanned stop end had to be installed within the cage.
| 05SY - Systemwide | Cxxx-NCR-000026 | NCR | Defective S312 Twin Booted Sleepers Received |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-09-16 | 2015-09-11 14:14 | -5 | 2015-07-13 11:54 | Track - Rails and Sleepers | 2000 |  | Manufacturing Defect | Reject | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | In the batch of received S312 Twin Booted Sleepers received on site at Connaught West Compound • 2 x S312 BOOTED SLEEPERS CRACKED AROUND TIE BAR • 1 x S312 BOOTED SLEEPER EXPOSED COIL REINFORCING Pictures attached
| 05SY - Systemwide | Cxxx-NCR-000027 | NCR | S 312 V Twin Block Sleepers Temporary Marking |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-10-14 | 2015-10-13 12:44 | -1 | 2015-07-13 15:10 | Track - Rails and Sleepers | 1000 |  | Material | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Not Defined | Completed |  | During on inspection of the received sleepers on the 30/06/2015, it was noticed that only one end of the sleepers has been marked, making it difficult to differentiate them when stacked together. Sleepers should be stencilled with the colour code for the different types (S1, S2, S3 - in relation to the resilience) on both sleeper ends as agreed during the FAT held on the 26/06/2015 in their factory.
| 05SY - Systemwide | Cxxx-NCR-000028 | NCR | Reinforcement Cages 235 & 236 Fabricated as the Wrong Type |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-09-11 | 2015-07-15 09:12 | -58 | 2015-07-13 15:08 | Track - Track Bed | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | On the 29/06/2015 at Connaught EB Area 4, it was noted during the final inspection that cages 235 & 236 (CH17944 – CH17955) were type 6 instead of type 2.
| 05SY - Systemwide | Cxxx-NCR-000029 | NCR | Damaged PRD Transversal Strips |  | Contr | __ | ZAW - Asset Wide (All Locations) (Technical (Systemwide)) |  | 2015-09-11 | 2015-09-15 09:16 | 4 | 2015-07-13 11:33 | Track - Track Bed | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | EB Connaught tunnel Cages CH 17778 – CH 17960 Transversal strips of PRD coming out of the cast track slabs are contaminated with mud and damaged by concrete leftovers from the pours of those slabs (EB section concreted against tunnel wall). Pictures attached.