| 03SR - Stations (RfL) | Cxxx-NCR-000651 | NCR | Damaged waterproofing in HRU |  | Contr | SKC |  |  | 2017-10-30 | 2017-11-13 08:35 | 14 | 2017-07-22 11:05 | Civil - Civil Engineering General | 3000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The __ 800NA waterproofing membrane in the HRU room has been damaged by the penetration of bolts used to set bracketry. The bolts were removed in order to repair the membrane, however water pooled over the area for an extended period, causing it to ingress under the membrane and making the adhesive ineffective.
| 03SR - Stations (RfL) | Cxxx-NCR-000652 | NCR | ESS - Steel to steel B21 to B8 connection |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2017-10-27 | 2017-09-04 16:37 | -53 | 2017-07-21 14:30 | Structural Engineering - Bolted Connections | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Up on review of the Shaft Steelwork - Lower Fan Level B2 and Upper Fan Level B1 General arrangement package Cxxx-SKC-S-DWG-CR094_WS110-50021, Cxxx identified that Steel to steel B21 to B8 connection has not been incorporated on the steel to steel design pack. The general arrangement drawing specifies 2no. M20 bolts on a fin plate connection which means that the bolts are subject to an eccentric moment as the support point is taken at the centre of the B8 beam.
| 03SR - Stations (RfL) | Cxxx-NCR-000653 | NCR | LPS - Beam poured by Cxxx not level |  | Contr | SKC |  |  | 2017-09-02 | 2017-08-07 07:33 | -26 | 2017-07-22 12:05 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A beam on gridline 6 poured by Cxxx has not been installed straight and is 35mm higher on the northern size compared to the south side. It was only discovered once the formwork was installed for the slab south of the PR riser.
| 03SR - Stations (RfL) | Cxxx-NCR-000654 | NCR | Limmo - Earthing IRN - Works proceeded ahead of MCR approval |  | Contr | SKC |  |  | 2017-08-28 | 2017-09-18 08:15 | 21 | 2017-07-24 17:52 | Electrical - Earthing & Bonding | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Ahead of the MCR approval of the straight in-line mechanical connectors, they have been installed in the transformer rooms and B6 HV1 and HV2 trenches.
| 03SR - Stations (RfL) | Cxxx-NCR-000655 | NCR | ESS - Steel to steel B12 to wall connection at B1 slab |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2017-10-03 | 2017-08-10 13:37 | -54 | 2017-07-25 13:31 | Structural Engineering - Bolted Connections | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | B12 to wall steel connection at B1 slab (see attached exact location on the marked up sketch) has not been installed as per the approved design. Steel to steel design package Cxxx-SKC-C-XCL-CR094_WS110-50005, specifies 3M24s bolts for this connection, however, currently the installed bolts are 3M20s as per the General arrangement drawing package Cxxx-SKC-S-DWG-CR094_WS110-50021.
| 03SR - Stations (RfL) | Cxxx-NCR-000657 | NCR | Mile End Shaft - Lack of ITP check sheets for Fire Protection Installation |  | Contr | SKC |  |  | 2019-01-28 | 2019-06-12 07:52 | 135 | 2018-05-30 11:33 | Fire - Fire Systems & General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | are unable to provide the check sheets required as per ITP Cxxx-SKC-C-ITP-CR094_WS109-50020 rev 3.0 Mile End Shaft Internal and Headhouse Fire Protection for Pre-Construction checks 50020-A and 50020B Fire Protection Installation.
| 03SR - Stations (RfL) | Cxxx-NCR-000658 | NCR | Penetration into Lift Shaft B00 |  | Contr | SKC |  |  | 2017-11-30 | 2017-08-10 13:33 | -112 | 2017-07-28 07:21 | Civil - Civil Engineering General | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Management Problem - Other management problem | Completed |  | It has been identified that 1 No. penetration into the lift core on B00 has not been installed. Please refer to Cxxx-JUL-S-DDB-CR094_SH005-01400 shown in red cloud. Please also see the attached photo showing the location of the existing rebar. Penetration is required for __ CMS.
| 03SR - Stations (RfL) | Cxxx-NCR-000659 | NCR | Stepney Green Slip Resistance |  | Contr | SKC |  |  | 2017-10-31 | 2017-09-26 12:01 | -35 | 2017-07-28 13:06 | Architectural - General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Further to detailed discussions with the Employer, and notwithstanding Cxxx-EWN-02037, the Contractor raises this NCR in order to capture the single only test result for the intervention stair case that does not achieve PTV 36 (i.e. PTV 35). This is as detailed in Cxxx-SKC-O4-RGN-CR094_WS108-50022 (Intervention Stairs Slip Testing). It is noted that the Escape Stairs Slip Testing achieve PTV 36+ as detailed in Cxxx-SKC-O4-RGN-CR094_WS108-50023.
| 03SR - Stations (RfL) | Cxxx-NCR-000660 | NCR | Drain Behind Blockwork Wall SRLV1 Level B2 |  | Contr | SKC |  |  | 2017-12-22 | 2017-11-14 07:57 | -38 | 2017-07-28 14:07 | Architectural - Brickworks/Blockworks | 1000 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | This NCR is raised in order to capture the fall issue behind the block work wall within SRLV1. 08/11/2017 The Contractor notes the following: - CRL inspected the drainage channel behind SRLV1 and raised the issue with the fall of the D Wall Drainage Channel GL12 – 10 on level B2. - Further to Cxxx-EWN-02194 and based on CRL inspection at the time it is noted that the fall along the drainage channel may not be adequate. - The D-Wall Drainage has been constructed in accordance with the falls as detailed within Cxxx-JUL-P-DDA-CR094_SH005-01532 and Cxxx-JUL-P-DDA-CR094_SH005-01533. Note Cxxx-SKC-A-DDA-CR094_SH005_3-00283 was used for reference.
| 03SR - Stations (RfL) | Cxxx-NCR-000661 | NCR | Concrete wall poured too long |  | Contr | SKC |  |  | 2017-11-27 | 2017-11-27 17:17 | 0 | 2017-08-09 17:09 | Civil - Civil Engineering General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | The concrete wall which separates the Transformer room 1 and 2 has been poured too long. Approximately 50mm too long. This prevents us from installing the external grillage which spans across the transformer rooms.
| 03SR - Stations (RfL) | Cxxx-NCR-000662 | NCR | ESS - Flooring - Incorrect Screed Angles Installd at Thersholds |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2017-09-29 | 2017-09-29 08:54 | 0 | 2017-08-02 12:33 | Architectural - Flooring | 1000 |  | Material | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The subcontractor has installed non-galvanised mild steel angles that have been installed in the HV 1&2, LV 1&2, TR 1&2, rooms on the GF which should have been a galvanised finished mild steel restraint (as per clause JM10.1205 of Eleanor Street Shaft Architectural Specification) but was installed without an approved MCR.
| 03SR - Stations (RfL) | Cxxx-NCR-000663 | NCR | Door DB1.19 - Opening restricted to 90 degrees |  | Contr | SKC |  |  | 2017-11-27 | 2017-10-14 13:09 | -44 | 2017-08-05 07:45 | Architectural - Doors | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Door DB1.19 for SR 11kV HV2 is specified as full 180 degree opening for both leaves. The arrangement of CMS leaving the LV Switchroom to the West of the door is such that the West leaf of the door can open to only just beyond 90 degrees. The CMS arrangement is necessary to take the services from SR LV2, and the gradient on the tray ensures bending radii of the cables are not exceeded. LV Sub-main and earthing cables have been installed on this CMS. will install the closer restictor to ensure that the door does not open beyond 90 degrees and as such cannot be damaged. See attached sketch demonstrating that this will not prevent the movement of plant and equipment in and out of the room.
| 03SR - Stations (RfL) | Cxxx-NCR-000664 | NCR | No MCR for single compartment Trunking |  | Crossrail | XRL |  |  | 2017-09-04 | 2017-09-04 15:07 | 0 | 2017-08-04 10:49 | Electrical - Cable Management | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Surveillance on Electrical Installation was carried out at Cxxx Limmo Shaft. It was agreed to check Corridor B1 and associated rooms. Whilst in Corridor B1 it was noted that single compartment trunking was being installed between the primary cable management system (CMS) and various rooms including the Battery room. Post site visit the Contractor forwarded the MPS Register which upon checking did not have a MCR for single compartment trunking. The Contractor confirmed no MCR was in place for the trunking. The Contractor has since compiled a MCR No: CRL-MCR-005293 which is in the system waiting to be approved.
| 03SR - Stations (RfL) | Cxxx-NCR-000665 | NCR | Intervention Stair Gap Between RC and Stairs |  | Contr | SKC |  |  | 2017-10-03 | 2017-10-13 13:45 | 10 | 2017-08-04 15:01 | Civil - Civil Engineering General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The Contractor notes that the top 2 steps have been installed to the intervention stairs and there is an approximately 97mm gap between the RC roof slab. See attached photos.
| 03SR - Stations (RfL) | Cxxx-NCR-000666 | NCR | Ducting brackets installed not covered under MCR |  | Contr | SKC |  |  | 2017-10-23 | 2017-10-24 08:19 | 1 | 2017-08-14 15:29 | Mechanical - Mechanical Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Lack or improper material identification and traceability | Completed |  | The Material Compliance Record for bracketry used to fix the ductwork (CRL-MCR-001160) states the material to be "Mild steel sections cut to length and drilled, Coating hot dip galvanized after manufacture to form duct work support brackets and fan support frames". It has been observed on site that a number of brackets have a painted finish.
| 03SR - Stations (RfL) | Cxxx-NCR-000667 | NCR | NCR - MES - Asset Management Information |  | Contr | SKC |  |  | 2018-04-30 | 2018-04-25 09:35 | -5 | 2017-08-14 14:41 | Electrical - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following the VAP carried out by Asset Information Team a report a number of non-conformances were identified. These non-conformances are covered in the attached report.
| 03SR - Stations (RfL) | Cxxx-NCR-000668 | NCR | ESS - Surface cracking in VE1 slab |  | Contr | COS | ELS - Eleanor Street Shaft (Central) |  | 2017-09-29 | 2017-12-14 14:47 | 76 | 2017-08-14 11:14 | Civil - Civil Engineering General | 1000 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As per the works information (RFI 1023 &PMI 1122), the concrete level within adit VE1 was required to be built up by circa 80mm. This was undertaken using five star non shrink grout as per the approved MCR. Surface cracking between 1-2mm (max) was thereafter noticed. Cxxx notes that the Cxxx Civil/Structural specification Cxxx-JUL-S-RSP-CR094_SH007_Z-50001 calls out the following control measures for cracking: 1) KF10.3214 Construction Joints - "Shall be formed where shown on drawings". The Cxxx design intent and the Cxxx design does not show any construction joints. 2) KF10.3215 Shrinkage Cracking - "The maximum bay length for a single pour shall not be greater than 12000mm". This was not exceeded 3) KF10.3216 Movement Joints - "Shall be constructed at the locations in accordance with the details and dimension shown on the drawings". No movement joints were shown on either the Cxxx design intent and the Cxxx design. Furthermore, the design intent or PMI did not ask for any rebar to be installed, therefore none was.
| 03SR - Stations (RfL) | Cxxx-NCR-000669 | NCR | Ductwork joints through firestopped penetrations |  | Contr | SKC |  |  | 2017-11-27 | 2017-10-20 12:07 | -38 | 2017-08-16 13:12 | Mechanical - Mechanical Engineering General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Cxxx-EWN-02068 states the Project Manager has concerns with ductwork joints that are situated in the middle of penetrations.
| 03SR - Stations (RfL) | Cxxx-NCR-000670 | NCR | Installation of systemwide doors without approved MCR |  | Contr | SKC |  |  | 2017-12-25 | 2017-11-07 13:12 | -48 | 2017-08-15 13:04 | Architectural - Doors | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Doors DB1.06, DB1.10, DB1.15 DB1.17, DB1.19 and DB1.26 have been installed under a Material Compliance Record at Code 3 (Cxxx-SKC-C-LRC-CR144_WS155-50012)
| 03SR - Stations (RfL) | Cxxx-NCR-000671 | NCR | ESS: Ductwork Brackets installed with non-approved MCR |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2017-11-27 | 2017-10-26 06:30 | -32 | 2017-08-16 16:33 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Within the AARP Riser at Eleanor Street Shaft B1-B5, Supply and Extract Ductwork has been supported vertically with a non-MCR approved bracket.
| 03SR - Stations (RfL) | Cxxx-NCR-000673 | NCR | ESS - First floor BWIC alterations |  | Contr | COS | ELS - Eleanor Street Shaft (Central) |  | 2017-11-15 | 2017-09-21 07:07 | -55 | 2017-08-17 08:35 | Architectural - Masonary | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | During the installation of the mechanical MAP BSK4 dampers at Cxxx ESS, it has been noticed that amendments to the BWIC openings are required on the first floor level. The affected locations are: • BW-MA-49 • BW-MA-50 • BW-MA-25 • BW-MA-29 The BWIC openings were built to the attached BWIC schedule by the blockwork contractor. However it later transpired that the specialist damper installation contractor had additional spacing requirements for installing the dampers, which are set by the manufacturer – see attached document “BSK4 in wall install instructions 2017”. BW-MA-49 & BW-MA-50 are scheduled as 500 x 500 and only separated by a 150mm block, however these need to be separated by a minimum of 200mm and the opening size enlarged to 520x520mm. Cxxx propose to remove the firestopping, top 3 courses of blockwork and lintel and then modify the opening size and position so that it meets the minimum requirements. The firestopping, blockwork and lintel will be replaced with a longer length so that 150mm bearing length is achieved on both sides. See attached picture for location of BWIC openings. BW-MA-25 is scheduled to be 370 x 370, however it is only 360 x 360mm. Therefore Cxxx propose to cut the blocks back by 10mm in situ. The lintel above the BWIC opening will still maintain the minimum bearing length of 150mm. BW-MA-29 is scheduled to be 470 x 470mm, however it has been built as 470 (wide x 500 (high). Cxxx propose to make a shutter and fill in the bottom of the BWIC opening by 30mm using five star grout and thereby forming a 470 x 470 opening. Please can CRL confirm the proposal is acceptable.
| 03SR - Stations (RfL) | Cxxx-NCR-000674 | NCR | Windpost Handover Records |  | Contr | SKC |  |  | 2017-12-16 | 2017-10-11 08:37 | -66 | 2017-08-18 14:09 | Architectural - Brickworks/Blockworks | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | NCR is raised in order to capture the wind post handover records issue (refer Cxxx-SKC-O4-LRC-CR094_WS108-50020).
| 03SR - Stations (RfL) | Cxxx-NCR-000676 | NCR | Limmo - External drainage and access road - By Exception Technical Assurance Process |  | Contr | SKC |  |  | 2018-02-26 | 2018-01-08 14:51 | -49 | 2017-08-24 10:04 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In order to meet the Limmo construction programme the design technical assurance of the external drainage and access road drawings has been obtained through the CRL By Exception process (CRL1-XRL-O7-GPD-CR001-50023). Refer completed Technical Assurance By Exception Gate Risk Assessment form (Cxxx-SKC-D-RGN-CR144_WS155-50005 Rev 1.0) appended to this NCR for details of the drawings and scope.
| 03SR - Stations (RfL) | Cxxx-NCR-000677 | NCR | ESS - Secondary Lining Fibre content |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2017-11-14 | 2017-10-20 14:23 | -25 | 2017-09-05 06:53 | Civil - Tunnelling | 1500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Quality handover package Cxxx-SKC-C-RGN-CR094_WS110-50192 rev 3, code 3 and Cxxx-SKC-C-RGN-CR094_WS110-50213 rev 1 code 1 has records showing steel fibre content over 30kg/m^3 the specified amount as per KF10. Package 50192 has been superseded by handover package 50213 containing all checksheets from 50192 and including shaft checksheets also. While Pack 50213 has been accepted by CRL and Cxxx when submitted in 2015, package 50192 was never cancelled and not made known as superseded. As pack 50192 was not cancelled it was highlighted by (different site team) as code 3 as had been attempted to close comments leading to submission of 50192 rev 3. There was no knowledge of existing pack 50213 that superseded it, hence 50192 rev3 submission. Upon re-submission of 50193 CRL questioned the fibre content mass range as some had ranged 1.5 times the recommended 30kg/m^3. steel fibre quantities range from 25kg/m^3 - 50kg/m^3.
| 03SR - Stations (RfL) | Cxxx-NCR-000678 | NCR | ESS - Structural steel connections |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2018-05-14 | 2018-05-09 13:07 | -5 | 2017-09-05 13:50 | Structural Engineering - Steel Member | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Cxxx has installed a number of steel connections that did not meet the shaft steel to steel Cxxx-SKC-C-XCL-CR094_WS110-50005 and steel to concrete design Cxxx-SKC-C-XCL-CR094_WS110-50007 package. The design packages have been updated in order to reflect the installed connections. Please see below list with the connections that have been updated on the above mentioned design packages: Shaft Structure - Upper Attenuator Level B3, Cxxx-SKC-S-XCS-CR094_WS110-50004: Cast in plate for B8 straight fin plate included in Shaft Structural Connections with Concrete Cxxx-SKC-C-XCL-CR094_WS110-50007 Rev7 (Review Comment 9 a, b, c) B8 straight fin plate – calculation included in Shaft Steel Connections Cxxx-SKC-C-XCL-CR094_WS110-50005 Rev 6 (Review Comment 9d) B21 to B8 – calculation included in Shaft Steel Connections Cxxx-SKC-C-XCL-CR094_WS110-50005 Rev 6 (Review Comment 10a) B12 to B8 – calculation included in Shaft Steel Connections Cxxx-SKC-C-XCL-CR094_WS110-50005 Rev 6 (Review Comment 10b) Shaft Steelwork - Lower Fan Level B2 and Upper Fan Level B1, Cxxx-SKC-S-XCS-CR094_WS110-50005: Cast in plate for B8 straight fin plate Shaft Structural Connections with Concrete Cxxx-SKC-C-XCL-CR094_WS110-50007 Rev7 (Review Comment 7 a, b, c) B8 straight fin plate – calculation included in Shaft Steel Connections Cxxx-SKC-C-XCL-CR094_WS110-50005 Rev 6 (Review Comment 7 d) B21 connection with concrete - included in Shaft Structural Connections with Concrete Cxxx-SKC-C-XCL-CR094_WS110-50007 Rev7 (Review Comment 9) B12 to B8 - calculation included in Shaft Steel Connections Cxxx-SKC-C-XCL-CR094_WS110-50005 Rev 6 (Review Comment 11) B8 to wall - calculation included in Shaft Steel Connections Cxxx-SKC-C-XCL-CR094_WS110-50005 Rev 6 (Review Comment 22) B12 to B8 - calculation included in Shaft Steel Connections Cxxx-SKC-C-XCL-CR094_WS110-50005 Rev 6 (Review Comment 23) B5 to B8 - calculation included in Shaft Steel Connections Cxxx-SKC-C-XCL-CR094_WS110-50005 Rev 6 (Review Comment 24) B3 to B3 - calculation included in Shaft Steel Connections Cxxx-SKC-C-XCL-CR094_WS110-50005 Rev 6 (Review Comment 25) B12 to B8 - calculation included in Shaft Steel Connections Cxxx-SKC-C-XCL-CR094_WS110-50005 Rev 6 (Review Comment 27) B3 to B5 - calculation included in Shaft Steel Connections Cxxx-SKC-C-XCL-CR094_WS110-50005 Rev 6 (Review Comment 23) Cxxx notes that the calculation for the above connectioon have been included on the update Cxxx-SKC-C-XCL-CR094_WS110-50005 and Cxxx-SKC-C-XCL-CR094_WS110-50007 packages which are currently under review from CRL/Cxxx. The acceptance of these will close this NCR.
| 03SR - Stations (RfL) | Cxxx-NCR-000679 | NCR | Incomplete Install of B6 manhole by Cxxx |  | Contr | SKC |  |  | 2018-01-29 | 2017-12-21 12:57 | -39 | 2017-09-06 17:48 | Civil - Drainage | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Previous Construction - Problems based on previous construction errors | Completed |  | Drawing Cxxx-SKC-P-DDD-CR144_SH011_Z-00548 which depicts drainage installation works on B6 as part of Cxxx scope shows a manhole with six pipes entering and one exiting. Of the three pipes entering, three are shown as having a backdrop, a detail which includes a tumbling bay junction including a rodding eye for future maintenance purposes. Only one of these tumbling bays appears to have been installed and this has not been installed with a rodding eye. The pipe which has been installed was damaged upon inspection so it may not be possible for a rodding eye to be installed.
| 03SR - Stations (RfL) | Cxxx-NCR-000682 | NCR | ATX Area - Incorrect Bolts |  | Contr | SKC |  |  | 2017-12-22 | 2017-09-14 10:33 | -99 | 2017-09-07 14:12 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The sub-contractor __ has installed __ HUS3-H in the ATX areas. The contractor notes that these bolts should’ve been __ HUS3-HF which provide a thicker galvanised finish. The Contractor proposes that the bolts are changed out to HIT-HY 200-A + HIT-V-F (8.8) M1 (refer sheet attached confirming the F2 arrangement checked by the subcontractors designers for use within the existing holes). The Contractor further notes that with the use of the existing holes, this arrangement limits the risk of conflicting with rebar with new holes. 08/09/2017 The Contractor notes the following: 1. Amended fixing arrangements is the revised F2 detail undertaken by the subcontractors designers. 2. Correct, holes will be re drilled to embedment depth of 100mm. 3. That in accordance with Table 4.1 with a 12mm anchor rod used a 14mm dia hole is required (i.e. to allow for the injection)l. It is noted that the current hole is already 14mm. 4. That the __ designers have undertaken the calculations as per the attachment and accept this design suitable as their F2 detail (i.e. warranted by __ designers).
| 03SR - Stations (RfL) | Cxxx-NCR-000683 | NCR | FIS - Blockwork in curved infill walls at B4 adits |  | Contr | SKC |  |  | 2017-10-20 | 2017-09-19 12:56 | -31 | 2017-09-11 12:49 | Architectural - Brickworks/Blockworks | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | installed the blockwork adit infills on B4 as per the gated F1 design and noticed issues resulting in poor fire compartmentation. In order to rectify this, consulted with the F1 Designer, and were advised to relocate the walls to the positions hightlighted in the following attachments: • Westbound_adit_wall.pdf • Eastbound_adit_wall.pdf CRL to confirm this solution is acceptable. Other attachments: • Cxxx-SKC-A-DDA-CR086_SH003_5-20205.pdf • Cxxx-SKC-A-DDD-CR086_SH003_Z-20741.pdf • RFI-466_1.pdf • RFI-466_2.pdf
| 03SR - Stations (RfL) | Cxxx-NCR-000684 | NCR | Damaged LV Sub-main cable |  | Contr | SKC |  |  | 2017-12-22 | 2017-10-06 07:36 | -77 | 2017-09-13 16:08 | Electrical - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Cable B-005 from the LV panel B to the ATS (Sump Pump CP) has been damaged, it seems the cable was nicked and when whilst being pulled the outer sheath burst due to the force applied possibly due to change of direction. The cable is to be removed and be replaced by another FP600S cable.
| 03SR - Stations (RfL) | Cxxx-NCR-000685 | NCR | ESS - Soil Pipe Installation Ground Floor WC |  | Crossrail | XRL | ELS - Eleanor Street Shaft (Central) |  | 2017-12-21 | 2017-12-19 14:53 | -2 | 2017-09-14 07:20 | Civil - Drainage | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The soil pipe for the Eleanor Street ground floor WC has been extended in a continuous length through the floor slab in clay instead of terminating below finished floor level and being extended in cast iron. This has led to an increase in invert level of the branch connection for the WC as well as increasing the chance of damage occurring to the clay pipe.
| 03SR - Stations (RfL) | Cxxx-NCR-000688 | NCR | FIS - Earthing Test |  | Contr | SKC |  |  | 2017-10-20 | 2017-10-03 08:59 | -17 | 2017-09-25 13:19 | Electrical - Earthing & Bonding | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Whilst carrying out the testing on the electrical earth nest at the Fisher Street shaft, didn’t invite CRL to come a witness the testing via an IRF. will re-test the earthing nest in the presence of a CRL representative and an IRF will be submitted.
| 03SR - Stations (RfL) | Cxxx-NCR-000689 | NCR | ESS - Structural calculation package for facade connections |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2017-11-27 | 2018-01-04 10:29 | 38 | 2017-09-28 09:15 | Architectural - General | 1000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Cxxx progressed to the installation of the facade as per Cxxx-SKC-S-DWG-CR094_WS110-50025 on the basis that all the concerns raised by Cxxx have been addressed. However, the Façade Structural calculations Cxxx-SKC-S-XCL-CR094_WS110-50002 are currently code 3. Cxxx notes also Cxxxs comment that design of the Façade connection to Cxxx structure is a Cxxx Design Item. Cxxx to satisfy themselves that the details in the above drawings are structurally adequate. This NCR should be closed upon submission and acceptance of the package.
| 03SR - Stations (RfL) | Cxxx-NCR-000690 | NCR | ESS - External Drainage at Eleanor Street - Design Change |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2018-03-16 | 2017-10-17 14:24 | -150 | 2017-10-16 12:40 | Civil - Drainage | 6000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Cxxx commenced excavating at Eleanor street as part of the drainage works in order to install the C1 to C16 combined sewer connection. During construction, the design was changed from a 300mm pipe to a 525mm, therefore, the works had to be stopped and the pipes removed. Please note that, the excavated area has been backfilled. Please also note: Installation started with an accepted design. Only 2 300mm pipes were laid. The manhole was not broken into and no connection to the existing sewer was made.
| 03SR - Stations (RfL) | Cxxx-NCR-000695 | NCR | Landscaping geotextile |  | Contr | SKC |  |  | 2018-11-14 | 2017-11-13 08:41 | -366 | 2017-10-31 17:52 | Civil - Landscaping | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The landscaping drawings reference an NW15 geotextile for all areas of the Lytag mound and Gabion baskets. An NW8.5 product was installed under approximately 30% of the Lytag mound before it was noticed that the product had deviated from the approved product. Note - the Gabion baskets are mentioned in the attached RFI, although it has been confirmed that this material is the specified NW15. The Contractors Designers were engaged to judge the suitability of the material under the Lytag mound. They confirmed that the NW8.5 material was appropriate for the areas installed.
| 03SR - Stations (RfL) | Cxxx-NCR-000696 | NCR | Gabion basket limestone |  | Contr | SKC |  |  | 2018-12-01 | 2017-12-19 13:51 | -347 | 2017-11-01 09:05 | Civil - Landscaping | 5000 |  | Manufacturing Defect | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | Despite a sieve analysis confirming that 100% of material is retained at the 75mm sieve, the limestone aggregate is being delivered with a proportion smaller than the specified material.
| 03SR - Stations (RfL) | Cxxx-NCR-000697 | NCR | Mile End Fencing |  | Contr | SKC |  |  | 2019-07-29 | 2019-07-23 10:26 | -6 | 2017-11-02 15:06 | Architectural - General | 5000 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There are three change of direction locations in the Mile End security fence alignment, which are not 90 degrees. In two of these locations the Contractor has installed single posts and modified the fence panels to make up for the change of direction and in one location there are two posts next to each other in order to make the transition in alignment. It is to our understanding that according to CRL this is not acceptable and all changes of direction different than 90 degrees, should be made utilising a custom made post, which consists of 2 no. posts welded together at the correct angle. No onsite modification should be made to panels and/or connecting fittings. See the attached photos. Update 22/11/2017 During a meeting at STG with CRL, held on 17/11/2017, a proposed detail was presented for the location, where 2 separate posts are used to form a change of direction. It was agreed to proceed with the implementation of this detail. More information is to be found in the attached communication with the specialist subcontractor. For the remaining locations it was agreed that the posts already installed are to remain and remedial works are to be done to the panels and connectors. The specialist subcontractor is to undertake these remedials in due course. Update 06/12/2017 - Please see attached 'Lang and Fulton proposal.pdf' - drawing produced by manufacturer detailing the issue with the two separate posts. Regarding the attached email: - The level variations are determined by the terrain characteristics, we propose to use 'as-is', the panels are at maximum height given the dimensions. Regarding the holes in the posts - these will be filled with the same colour caps to prevent moisture accessing the posts. Regarding the gate and gate accesories - the installed is as per the approved design as described in Materials and Product Compliance Record – Lang and Fulton Navara fencing and gate system Cxxx-SKC-C-LRC-CR094_WS109-50168, which has been approved.
| 03SR - Stations (RfL) | Cxxx-NCR-000699 | NCR | Gabion basket vertical alignment |  | Contr | SKC |  |  | 2017-12-22 | 2017-12-19 16:48 | -3 | 2017-11-13 10:59 | Civil - Landscaping | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | The top layers of the East Gabion baskets have been installed out of vertical alignment. Currently, the top baskets won't finish flush with the facade. The Contractor will remove and re-align all baskets necessary to achieve a flush finish with the facade.
| 03SR - Stations (RfL) | Cxxx-NCR-000700 | NCR | ESS - Blocked B5 drainage |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2018-09-28 | 2018-09-25 13:58 | -3 | 2017-11-16 13:25 | Civil - Drainage | 6000 |  | Damaged | Repair | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | B5 base drainage route from CG9 and CG8 to CP1 is blocked.
| 03SR - Stations (RfL) | Cxxx-NCR-000701 | NCR | Stepney Green Shaft - ITECH Roof Drawings |  | Contr | SKC |  |  | 2018-03-31 | 2018-05-04 10:03 | 34 | 2017-11-24 14:47 | Architectural - Roofing & Exterior Treatment | 3000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | On a surveillance undertaken on 04/10/2017 for the ITECH Roof works in Stepney Green Shaft, it was noted that the relevant F1 drawings were at Preliminary status (P0X) and therefore not issued for construction (IFC).
| 03SR - Stations (RfL) | Cxxx-NCR-000702 | NCR | ESS - Headhouse steel to steel connections |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2018-02-23 | 2018-04-13 12:53 | 49 | 2017-11-24 17:02 | Structural Engineering - Structural Engineering - General | 1000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Cxxx has installed a number of steel connections that did not meet the Headhouse steel to steel Cxxx-SKC-C-XCL-CR094_WS110-50008 design calculation package. The design package has been updated in order to reflect the installed connections. Please see below list with the connections that have been updated on the above mentioned design package which is currently under review from CRL/Cxxx: - New Detail 42A (page 16/1) - New Detail 42B (page 16/2) - Detail 43 (page 26 and 27) - Detail 47A (page 50, 51) - New Detail 47B (page 52) - Detail 47 (page 56) - New Detail 48A (page 59/1) - New Detail 63B (page 82/1) - New Alternative Detail 64 (page 87) - New Alternative Detail 65A (page 98) with 2M30 bolts. - Detail 90 – no longer required (page 139-144) - New Detail B12 to B2 column end plates to web (page 150) - New Detail – FCD 450 additional braces (page 157) Cxxx notes that the acceptance of the above mentioned calculation package should close this NCR.
| 03SR - Stations (RfL) | Cxxx-NCR-000704 | NCR | Mile End Shaft - Adit/Tunnel Drainage interface |  | Contr | SKC |  |  | 2019-07-29 | 2019-07-22 19:30 | -7 | 2017-11-29 12:00 | Civil - Drainage | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Following site walk on 20/09/17, , CRL, Cxxx, CEG: 1. B8 drainage plan: Cxxx-SKC-P-DWG-CR094_WS109-50005 shows a fall in the base slab (bottom of trench) towards the center of the shaft (away from the tunnel). The fall of the trench appears to be toward the door as opposed to back into the shaft. 2. There is no drainage installed at the shaft end of the adit to collect water and divert it to the channel in the B9 level below as indicated on drawing Cxxx-SKC-P-DWG-CR094_WS109-50005. 3. The floor of the B9 trench should be screeded to fall to manage the water, however that is likely impractical now with the HV cables running through on __.
| 03SR - Stations (RfL) | Cxxx-NCR-000705 | NCR | Mile End Shaft – Firestopping Rfl VAP (10/10/2017) |  | Contr | SKC |  |  | 2018-05-28 | 2018-07-02 12:00 | 35 | 2017-11-29 14:28 | Fire - Fire Systems & General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following VAP Observation report No. RAH/MES10102017 which was communicated via Cxxx-PMC-02490, Items 11,12, 13 and 14 of the report refer to issues with the installation of firestopping.
| 03SR - Stations (RfL) | Cxxx-NCR-000706 | NCR | Outer Roof Balustrade Post and Handrail Height Out of Tolerance |  | Contr | SKC |  |  | 2018-06-25 | 2018-02-12 18:27 | -133 | 2017-11-30 18:00 | Architectural - Balustrade | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The contractor notes that as per Cxxx-JUL-A-DDA-CR094_SH005_B-00323 (shows a typical balustrade height guideline), that the balustrade on the outer wall of the roof does not match the F1 detailing. As discussed with the CRL architect (__) on a site inspection on 29/11/17, the proposed solution is to install a 100mm kickplate for the full length of the balustrade. This will reduce the gap between the upstand and the knee rail to less than 500mm.
| 03SR - Stations (RfL) | Cxxx-NCR-000707 | NCR | B5 Trench Out of Tolerance |  | Contr | SKC |  |  | 2018-03-19 | 2018-04-16 14:13 | 28 | 2017-12-01 12:34 | Civil - Structural Engineering | 3000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Previous Construction - Problems based on previous construction errors | Completed |  | The trench constructed by Cxxx in the B5 corridor is out of tolerance. The duraslab doesn not sit steady when placed in the trench. 02/12/17 1) The slab is mass fill with nominal mesh on the surface (50mm cover min). Once we have cut this section out, an angle will be installed and grout will be poured to fill this in thus keeping with the current cover currently observed on site. 2) Adjusted
| 03SR - Stations (RfL) | Cxxx-NCR-000708 | NCR | Damaged floor finish in PFR on Level B00 and MCC Room on Level B2 |  | Contr | SKC |  |  | 2018-02-26 | 2018-02-19 15:36 | -7 | 2017-12-03 15:57 | Architectural - Flooring | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Roughly about 0.5 -1 m2 damaged resin floor was identified in PFR and MCC room respectively in Level B00 and B2.
| 03SR - Stations (RfL) | Cxxx-NCR-000709 | NCR | ESS - Cracked Lift Ramp Grout |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2018-02-28 | 2018-03-02 14:36 | 2 | 2017-12-05 11:41 | Architectural - Flooring | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Grout forming the lift ramps on the lift lobbies has cracked.
| 03SR - Stations (RfL) | Cxxx-NCR-000711 | NCR | Stepney Green Headhouse Beams Fabrication And Installation Deviation from Design |  | Contr | SKC |  |  | 2018-02-26 | 2018-02-13 15:55 | -13 | 2017-12-14 16:51 | Civil - Structural Engineering | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The contractor notes that the beams installed by __ deviate to what is prescribed on the F2 drawing pack Cxxx-SKC-S-DWG-CR094_WS108-50073. The contractor also notes that the additional holes have been drilled to accommodate the beam installation. This has been checked by their designers in the attached email. This has been confirmed that there will be no affect on the beam structurally. The contractor proposes to leave as is. 20/12/17 Additional holes have been drilled in the beams to facilitate the galvanizing treatment. There are 2 additional holes per side beam in the web of the beam Additional holes have been drilled on site to allow for the tolerances for installation of the top beams. Each beam on the top has 4 additional holes in the flange of the beam. The holes drilled on site will be galvanise repaired as per the ITP. Message attached confirms that these additional holes structurally do not affect the beam.
| 03SR - Stations (RfL) | Cxxx-NCR-000712 | NCR | LPS - Damaged Attenuator in PFR room |  | Contr | SKC |  |  | 2018-08-27 | 2018-08-20 11:04 | -7 | 2017-12-19 08:50 | Mechanical - Mechanical Engineering General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | An attenuator due to be installed in the PFR room has been damaged. The attenuator has been taken to the PFR room, where repair methods are to take place.
| 03SR - Stations (RfL) | Cxxx-NCR-000713 | NCR | STG, LIM, ELS, FIS shafts Drainage - construction to stage E design specifications |  | Contr | SKC |  |  | 2018-07-08 | 2018-02-06 08:22 | -152 | 2017-12-20 11:04 | Civil - Drainage | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Cxxx specifications currently being referenced for drainage at STG, LIM, ELS, FIS sites. These are only valid to RIBA E and require further Contractor design.
| 03SR - Stations (RfL) | Cxxx-NCR-000714 | NCR | FIS - Insulated Render Level on Catton St & Fisher St Elevations |  | Contr | SKC |  |  | 2018-02-09 | 2018-01-11 15:27 | -29 | 2017-12-20 16:57 | Architectural - Walls | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | The termination level for the external insulated render was set-out at +128,940 on both Catton Street and Fisher Street sides of the headhouse (North and South elevation). It was taken from drawing Cxxx-SKC-A-DDC-CR086_SH003_Z-20403 that the render terminated at the top of the cladding and allowance was not given for the capping detail. The enlarged detail shown on Cxxx-SKC-A-DDD-CR086_SH003_Z-20753 shows a gap between the render and the cladding to allow for installation of an ‘anodised aluminium capping’. This gap is clarified on drawing Cxxx-SKC-A-DDC-CR086_SH003_Z-20412 as being 100mm above the top of cladding. Therefore at a level of +129.040. The Render has therefore been terminated 100mm lower than design. This has no effect to the performance of the insulated render and is expected to have minimal impact on the cladding installation. propose to use as is.
| 03SR - Stations (RfL) | Cxxx-NCR-000715 | NCR | ESS VE1 water ingess |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2018-03-16 | 2018-04-20 12:09 | 35 | 2018-01-12 11:54 | Civil - Tunnelling | 6000 |  | Workmanship | Repair | 3 (3-6k) | Complete | External Phenomenon - Other | Completed |  | Adit VE1 is experiencing excessive water ingress - propose resin injection to reduce / stop the water
| 03SR - Stations (RfL) | Cxxx-NCR-000717 | NCR | LPS - FAN II - Cabling installed prior to acceptance of CMS inspection |  | Contr | SKC |  |  | 2018-05-25 | 2018-08-28 16:45 | 95 | 2018-01-19 15:34 | Electrical - Cable Management | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | In the Fan II room on level B1, cabling has been installed on CMS which has not been inspected by CRL FE. The cabling is to be removed and to be re-installed following acceptance of the CMS installation.
| 03SR - Stations (RfL) | Cxxx-NCR-000718 | NCR | Stepney Green - NCR further Cxxx-FCD-001094 |  | Contr | SKC |  |  | 2018-05-28 | 2018-02-23 12:22 | -94 | 2018-02-01 20:29 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | note that the builderswork openings requested within Cxxx-FCD-001094 and Cxxx-NCR-000658 within the lift shaft, have been installed on the opposite side of the wall to that detailed and requested. note that Cxxx are aware of this and have accepted this as per the response Cxxx-FCD-001094, this NCR is just being raised to capture the change. Cxxx-FCD-001094 shows the correct setting out of these openings.
| 03SR - Stations (RfL) | Cxxx-NCR-000719 | NCR | Ambiguity in Drawing Cxxx-SKC-D-DDD-CR144_SH011_Z-00003 Details Regarding Pipe Surround Material |  | Contr | SKC |  |  | 2018-05-31 | 2018-07-23 13:17 | 53 | 2018-03-13 08:18 | Civil - Drainage | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The 150mm half perforated filter pipe from S5b to S5c has been laid and surrounded with 10/20mm filter material wrapped in a geotextile membrane. The detail for Filter Drains Adjacent Traffic Areas on drawing Cxxx-SKC-D-DDD-CR144_SH011_Z-00003 rev C01 shows two contradictory information : -The drawing shows the filter material to be Type A to SHW Clause 505, being a 0/20mm designation according to SHW Series 500. -The key of the drawings shows the filter material to be a Granular material to SHW Clause 503.3 being a 10/20mm designation.
| 03SR - Stations (RfL) | Cxxx-NCR-000720 | NCR | Manhole S5c - No Engineering Brick Installed |  | Contr | SKC |  |  | 2018-05-31 | 2018-07-30 15:18 | 60 | 2018-03-13 08:39 | Civil - Drainage | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Manholes S5B and S5C had been installed per the Setting Out drawing. Manhole S5B is made up of concrete rings with concrete surround, concrete cover, 3 courses of engineering brick, mortar haunching and the iron cover and frame. A hydrophilic strip has been installed between the cover slab and chamber section. This aligns with the Typical Precast Concrete Manhole in drawing Cxxx-SKC-D-DDD-CR144_SH011_Z-00001 Rev C01. Manhole S5C has been constructed similar to S5B; no courses of engineering bricks has been installed between the cover slab and haunching/cover and frame. The drawing detail in *00001 requires ‘Class B Engineering Brickwork. 3 No. Courses Max 1 Course Min’. This is also detailed in the ITP under Inspection Number 2.2.7.
| 03SR - Stations (RfL) | Cxxx-NCR-000721 | NCR | CSJV undertaking Air Leakage Testing in lieu of UKAS accredited party without PMs acceptance |  | Contr | SKC |  |  | 2018-07-31 | 2018-07-30 15:24 | -1 | 2018-03-13 08:43 | Civil - Drainage | 2000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not trained for the work being performed | Completed |  | No Project Manager's Acceptance is in place for to undertake Air Leakage Testing in lieu of UKAS Accreditated company.
| 03SR - Stations (RfL) | Cxxx-NCR-000722 | NCR | Stepney Green - Bracket size to Steel Beams on Headhouse Steel |  | Contr | SKC |  |  | 2018-03-27 | 2018-02-26 18:14 | -29 | 2018-02-13 10:37 | Structural Engineering - Structural Engineering - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During inspection of the brackets on the head house structural steel, it has become apparent that two brackets have deviated from the F2 design. The size of these brackets are smaller than the original design and as such change the design. 'Attachment to Cxxx-NCR-000722' highlights the issue. __ have provided calculations to prove that these brackets sizes satisfy the design requirements. This is detailed in attachments 'S09344-__-00-BR-SC-Y-0003' and 'Section 7-7 cleat bracket detail'. propose a use as is classification to close this issue. Once Cxxx/CRL have reviewed and accepted this detail will update the F2 drawings to show the as built conditions.
| 03SR - Stations (RfL) | Cxxx-NCR-000723 | NCR | Manholes west of headhouse too high |  | Contr | SKC |  |  | 2019-02-01 | 2018-04-16 13:25 | -291 | 2018-02-26 13:55 | Civil - Drainage | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Over a year ago manholes S17, S8 and S18 were installed to design levels. At a later date the specification and drawing were changed which resulted in the heights being changed. As a result of this design change S18 is now too high in regards to the finish floor level as revealed by an onsite survey. Currently only up to the "biscuit" is installed. The contractor will reduce the current level to ensure that the cover level will match the floor level of the pavement. Please see attached drawings. The invert levels of pipes shall remain the same and connect in the same way to the rest of the drainage system.
| 03SR - Stations (RfL) | Cxxx-NCR-000724 | NCR | Incorrect Height of West Gabion Wall Handrails |  | Contr | SKC |  |  | 2018-05-31 | 2018-03-23 14:13 | -69 | 2018-02-23 10:17 | Civil - Landscaping | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | During a joint inspection with CRL for the benchmarking of the keeklamp handrails on the west gabion wall, it's been noted that the handrails were 1m high instead of the 1.1m stated on the drawings. This has been measured from mid of the top horizontal tube to the base.
| 03SR - Stations (RfL) | Cxxx-NCR-000725 | NCR | Stepney Green - Headhouse Grillage F2 Drawings |  | Contr | SKC |  |  | 2018-07-30 | 2018-06-29 11:53 | -31 | 2018-02-25 12:57 | Civil - Civil Engineering General | 3000 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | During installation of the roof grillage attached to the head house structural at Stepney Green Shaft it has become apparent that s subcontractor __ are not working to the F2 Details Package, Cxxx-SKC-S-DWG-CR094_WS108-50080, have submitted to CRL for acceptance. Although the F2 Details Package was developed by __ it appears that a breakdown in communication has occurred within __s internal departments as the separate fabrication team has been installing to a separate drawing, SO2183-01 attached. Upon initial review of S02183-01, with the Design Manager, the drawing does not stray from the F1 intent and as such propose a 'use as is' disposition. HI Comments 09/03/2018 Upon inspection with the CEG architect, the remedial action will follow as 1. Gap between the grills varies. Ensure the gap is consistent at 40-60mm. 2. Bottom level grills on the West side requires a 40-60mm gap between the grill and the FFL. This will require re-fabrication 3. Cxxx will update the F2 drawing pack Cxxx-SKC-S-DWG-CR094_WS108-50080 to reflect the as built condition.
| 03SR - Stations (RfL) | Cxxx-NCR-000726 | NCR | Stepney Green - Firemain Installed to Superseded Drawings |  | Contr | SKC |  |  | 2018-06-16 | 2018-07-06 12:12 | 20 | 2018-03-06 17:05 | Mechanical - Piping | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | On levels B4 and B5 the firemain has been installed to outdated drawings. As such, the 200mm and 150mm pipes are installed on the wrong side of the B4 and B5 corridors, remedial action is required to rectify this defect.
| 03SR - Stations (RfL) | Cxxx-NCR-000727 | NCR | Damaged UPS LCD |  | Contr | SKC |  |  | 2018-12-21 | 2018-07-18 09:57 | -156 | 2018-03-12 08:54 | Electrical - General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | In the ESR/Batt room on level B1 it has been noticed the LCD on one the UPS is damaged
| 03SR - Stations (RfL) | Cxxx-NCR-000729 | NCR | ESS - Concrete cut on the pressurizsation riser opening |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2018-05-25 | 2018-05-09 13:31 | -16 | 2018-03-16 16:43 | Civil - Civil Engineering General | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | 2 no. openings have been cut to increase the clear opening on the pressurization riser on the stair core. The openings have been increased by 20mm on one side on the opening. This has an impact on the reinforcement cover.
| 03SR - Stations (RfL) | Cxxx-NCR-000730 | NCR | ESS - Additional Gully between MH S7 and S6 |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2018-04-03 | 2018-04-09 14:18 | 6 | 2018-03-20 11:47 | Civil - Drainage | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | During the installation of the surface water drainage run between Manholes S7 and S6 as shown on Cxxx-SKC-D-DDA-CR094_SH007_1-00002, two gully connections have been installed as shown on P10 of the drawing instead of the single connection shown on P11. Cxxx propose to leave as is and install both gullies as this will have no negative effect on the drainage of the road. The falls of the channel on the road will be profiled to ensure all areas of the road and channel fall towards a gully. Cxxx's designers have confirmed the above is acceptable.
| 03SR - Stations (RfL) | Cxxx-NCR-000731 | NCR | Stepney Green - Implementation of Cxxx-FCD-000933 |  | Contr | SKC |  |  | 2018-07-31 | 2018-04-06 11:27 | -116 | 2018-03-20 17:50 | Civil - Structural Engineering | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Further to Cxxx-FCD-000933 the contractor has implemented this PTR as described, despite another proposal being requested due to the fall on the floor meaning water would fall away from the gullies. This was completed due to the precedent being set for the fall levels on B02 falling the same as within approved Cxxx-FCD-000622.
| 03SR - Stations (RfL) | Cxxx-NCR-000732 | NCR | ESS - incorrect alignment of draiange run MH S7 - S6 |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2018-04-03 | 2018-04-10 13:21 | 7 | 2018-03-20 11:43 | Civil - Drainage | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The 450mm drainage run between MH S7 and S6 has been installed slightly out of alignment. This results in a minor movement to the position of MH S6, which has to move towards the viaduct by 400mm. Cxxx therefore propose to leave as is. Cxxx note that this will not affect any of the other drainage or buried services. Cxxx's designers have confirmed that the move is acceptable.
| 03SR - Stations (RfL) | Cxxx-NCR-000733 | NCR | Stepney Green - RC Drainage Upstand Surrounding Blockwork Gully |  | Contr | SKC |  |  | 2018-04-09 | 2018-03-27 15:52 | -13 | 2018-03-22 12:29 | Civil - Drainage | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Cxxx note that the blockwork gully detail as depicted on detail 07 on Cxxx-SKC-A-DDD-CR094_SH005_Z-00712 has been changed from a blockwork detail to a concrete detail matching the drainage channel. This was changed for construct-ability purposes. Cxxx note that this was discussed and informally agreed previously between CRL and . This NCR has been raised to document the un-formalised change.
| 03SR - Stations (RfL) | Cxxx-NCR-000734 | NCR | Fisher Street Shaft - Support of Refrigerant Pipework |  | Contr | SKC |  |  | 2018-05-31 | 2018-04-11 13:12 | -50 | 2018-04-04 06:52 | Materials - General | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Cxxx Fire-stopping drawings: SKC-E-DDD-CR086_SH003-01610 SKC-E-DDD-CR086_SH003-01611 Indicates refrigerant pipework being supported on CMS Trays when traversing through penetrations. The current installation on site shows the pipework without adequate CMS Support and therefore liable to damage.
| 03SR - Stations (RfL) | Cxxx-NCR-000735 | NCR | ESS - Doors fire rating |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2018-07-27 | 2018-08-17 13:35 | 21 | 2018-04-10 17:49 | Architectural - Doors | 20000 |  | Design | Repair | 2 (6-60k) | Complete | Management Problem - Inadequate supervision | Completed |  | Cxxx has fabricated and installed all the staircase doors on every floor as per the Eleanor Street - Door Schedule Rev 2 code 1, as well as the fire safety plans for each level (C01 dwgs) where they both specified the doors on the staircases (D01.01, D00.1, DB1.01, DB2.01, DB3.01, DB4.01, DB5.01) to have 30min fire rating. The update door schedule Rev 4 code 1 and fire safety plans specify 60mins fire rating. Further to that, on the first floor, 3 doors found to meet the door schedule and fire safety plan requirements. In particular, D01.05 found to be 30min instead of 60 and D01.10 and D01.09 120min instead of 90min.
| 03SR - Stations (RfL) | Cxxx-NCR-000737 | NCR | Incoming water main |  | Contr | SKC |  |  | 2018-05-22 | 2018-05-30 08:23 | 8 | 2018-04-24 11:18 | Civil - Sewage/Water services | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | The 50DIA incoming water main ducting, as detailed in Cxxx-SKC-P-DDA-CR144_SH011-00566, has not been cast into the floor slab.
| 03SR - Stations (RfL) | Cxxx-NCR-000738 | NCR | ESS - CRL-OBS-15493 - CMS Tee Sections |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2019-07-15 | 2019-08-29 09:22 | 45 | 2018-04-25 13:38 | Electrical - Cable Management | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | NCR being raised to cover the scope of CRL-OBS-15493 - CMS Tee Sections. CRL-OBS-15493 Description: Standard Trunking T pieces used on multi compartment trunking. This reduce the capacity of the trunking at these points by 50%. No compliant with specification.
| 03SR - Stations (RfL) | Cxxx-NCR-000739 | NCR | CRL-OBS-21466 - Panel Compliance to BSEN61439 |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2019-06-03 | 2019-02-25 20:08 | -98 | 2018-04-25 13:34 | Electrical - Electrical Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | NCR being raised to cover the scope of CRL-OBS-21466 - Panel Compliance to BSEN61439. CRL-OBS-21466 Description: Switchboards are to be manufactured to BSEN60439 (superseded by and now accepted as BSEN61439). This standard refers to Main & Distribution busbars. MCC002 appears to have been built utilizing cables to link from the Main busbar to the circuit breakers instead of Distribution Busbars. This is none compliant with BSEN61439. Please investigate all panels manufactured by the same company and advise measures to correct. Update: 12/12/2018 Following from a meeting with CEG, it has been agreed to raise Cxxx-RFI-001327 to enable closure of this NCR.
| 03SR - Stations (RfL) | Cxxx-NCR-000740 | NCR | CRL-OBS-21465 - MCC Panel Thermal Imaging |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2019-06-03 | 2019-06-12 07:55 | 9 | 2018-04-25 13:41 | Electrical - Electrical Engineering General | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | NCR being raised to cover the scope of CRL-OBS-21465 - MCC Panel Thermal Imaging. CRL-OBS-21465 Description: JY71/JY72 requires switchboards to facilitate thermal imaging whilst the board is "ON LOAD". All busbars are protected with full metallic screens preventing the latter. Please check other MCC panels from the same manufacturer and correct. Update 12/12/2018 As discussed and agreed with CEG the panels are being modified as per Cxxx-RFI-001326 to enable closure of this NCR.
| 03SR - Stations (RfL) | Cxxx-NCR-000741 | NCR | CRL-OBS-21464 - Front Access to panels |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2019-04-29 | 2019-05-08 11:50 | 9 | 2018-04-25 13:44 | Electrical - Electrical Engineering General | 1000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | NCR being raised to cover the scope of CRL-OBS-21464 - Front Access to panels JY72/JY71 requires all switchboards to be top entry front access. It was noted during the VAP that access to the busbars was restricted. It was also noted that the incoming circuit breaker was mounted on a panel concealing equipment behind it. Further inspection identified doors to the rear of the panel. This panel is mounted just 50mm from the wall. Contractor to explain why the MCC has doors on the rear of the panel which cannot be opened, and how busbar connections are to be maintained. Please also check all other MCC panels from the same manufacturer for this same issue. Update 12/12/2018: Following a meeting with CEG it was explained and agreed that the MCC panels Access and Maintenance strategy shall be from the front ONLY. Please note these are modular panels therefore every section is constructed for panel removal. This will be made clear it the respective O&M manuals for each of the shafts. Document references as per below: Cxxx-SKC-K2-OMT03-CR094_SH006-50013 - PFU-2-00896 - Building Management System (BMS) at Mile End Park Shaft Cxxx-SKC-K2-OMT03-CR094_SH007-50006 - PFU-2-00891 - Building Management System (BMS) Cxxx-SKC-K2-OMT03-CR094_SH005-50020 - PFU-2-00904 - Building Management System (BMS) at Stepney Green Shaft Cxxx-SKC-K2-OMT03-CR144_SH011-50006 - PFU-2-00894 - Building Management System (BMS) at Limmo Peninsula Shaft Cxxx-SKC-K2-OMT03-CR086_SH003-50011 - PFU-2-00893 - Building Management System (BMS) at Fisher Street Shaft
| 03SR - Stations (RfL) | Cxxx-NCR-000744 | NCR | ESS - CRL-OBS-21460 - Earthing and Bonding of LV Panels |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2018-09-24 | 2019-04-16 13:39 | 204 | 2018-04-25 13:52 | Electrical - Earthing & Bonding | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | NCR being raised to cover the scope of CRL-OBS-21460 - Earthing and Bonding of LV Panels CRL-OBS-21460 Description: The earthing & bonding of the LV switchboards does not appear to be inline with the Cxxx earthing strategy document issued as part of the works information. In 2015, Cxxx amended this and issued their requirement. Contractor to investigate and confirm that the installation is compliant with the Cxxx requirement.
| 03SR - Stations (RfL) | Cxxx-NCR-000746 | NCR | Louvre support steel ITP |  | Contr | SKC |  |  | 2018-06-01 | 2018-05-16 06:50 | -16 | 2018-05-04 13:01 | Architectural - General | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | Louvre support steel works commencing without review of the latest ITP revision. An advanced copy of the ITP was forwarded to __ for review and the ITP has been reviewed and approved by the quality team.
| 03SR - Stations (RfL) | Cxxx-NCR-000747 | NCR | Grasscrete - No concrete cubes taken for the first three pours |  | Contr | SKC |  |  | 2018-09-28 | 2018-09-27 09:11 | -1 | 2018-05-09 14:57 | Civil - Concrete Pavement | 1500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | No concrete cubes have been taken for the first three grasscrete pours, failing to comply with Grasscrete ITP requirement – item 3.4.9
| 03SR - Stations (RfL) | Cxxx-NCR-000748 | NCR | ESS - B21 connection with concrete (Cast in plate for B21 beam) |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2018-07-28 | 2018-05-29 07:06 | -60 | 2018-05-14 10:49 | Structural Engineering - Bolted Connections | 2000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In Cxxx-SKC-S-XCS-CR094_WS110-50005 review comment 9, it was identified that no reference to connection B21 to the wall has been included in the Cxxx Shaft Steel to Concrete Calculations Rev 5 Cxxx-XCS-CR094_WS110-500007. Cxxx responded that the connection for the B21 to concrete is included on detail 21 as well as that this has been checked by RCA and confirmed suitable. However, no reference to B21 was added to detail 21 in the Shaft Steel to Concrete calculations Cxxx-XCS-CR094_WS110-500007 Rev 6 as well to the drawings on the back of the shaft steel to concrete pack.
| 03SR - Stations (RfL) | Cxxx-NCR-000749 | NCR | Installing Water Main and Fire Main without an Approved MCR |  | Contr | SKC |  |  | 2018-06-26 | 2018-06-13 09:30 | -13 | 2018-06-12 15:04 | Civil - Landscaping | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | The materials (63mm and 150mm PE pipes) for the fire and water mains have been installed without an approved MCR.
| 03SR - Stations (RfL) | Cxxx-NCR-000750 | NCR | ESS - Use of __ Extra Strength Compound |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2018-07-31 | 2018-05-21 08:43 | -71 | 2018-05-17 17:29 | Fire - Compartmentation | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Eleanor Street Architectural Specification: Cxxx-SKC-A-RSP-CR094_WS110-50005 clause: JP10.3205 states: Floors Where Loadbearing is Required a) Service pipes and cable trays shall be sealed all round where they pass through floors with an accepted material made for the purpose and tested. b) Completely fill the space to a minimum depth of 100mm introducing mild steel support brackets and mesh; leave no gaps and finish neatly. The manufacturer shall provide certified proof of suitability of all materials used On review of the lift lobby floor penetrations Cxxx's specialist subcontractor has installed __ Extra Strength Compound which as per the manufacture's installation guidance does not require mesh or support angles. Therefore no angles or mesh have been installed. Further to the above no Materials Compliance Report has been submitted for this product prior to it being installed.
| 03SR - Stations (RfL) | Cxxx-NCR-000751 | NCR | Stepney - CMS Support Bracketry in TVA |  | Contr | SKC |  |  | 2018-08-27 | 2018-06-18 08:34 | -70 | 2018-05-30 09:03 | Electrical - Cable Management | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Please find attached the Stepney Green corrosivity risk assessment document Cxxx-SKC-C-RGN-CR094_WS108-50010. This document specifies demarcation points of C2 and C5 corrosivity areas, the Contractor wishes to raise a non-compliance against the grade of unistrut fixings used in the TVA, classed as a C5 area. Central Engineering Group have advised that the corrosivity risk assessments are to categorise Shaft/BOH and platform areas as C2 and tunnels as C5 and not have a mix of C2, C3, C4 and C5 at the various areas. On this basis, at Stepney Green Shaft, the tunnel ventilation area on levels B00 to B04 is classed as a C5 corrosivity area as part of the Stepney Green corrosivity risk assessment. The Stepney Green corrosivity risk assessment document makes note that the TVA area is provided with air flow via the operation of the tunnel ventilation system which would reduce the classification from C5 to C4. See appendix 1 of the Stepney Green corrosivity risk assessment (attached): items number 30, 31 (page 14), 55 (page 17), 76 (page 20), 99 page 23 and 112 (page 25). To achieve compliance with the works information “deep hot dipped galvanized” tray and ladder has been installed in the TVA as this provides sufficient design life for a C5 area in accordance with CRL guidance document CRL1-XRL-M-RGN-CR001-50013. The associated unistrut support bracketry and fixings supporting the tray/ladder are “hot dipped galvanised” and as such not adequate for use in a C5 area. See CRL-MCR-000790 for unistrut product used for the support fixings. It is noted that the unistrut supports fixings and bracketry are compliant in a C4 area (see CRL1-XRL-M-RGN-CR001-50013), on the basis that the Designer has risk assessed the TVA area as being a C4 zone the Contractor suggests that no change is required and that the provided installation is compliant.
| 03SR - Stations (RfL) | Cxxx-NCR-000752 | NCR | Stepney Green - TVA Hanging Beam |  | Contr | SKC |  |  | 2018-06-05 | 2018-05-30 17:09 | -6 | 2018-05-22 16:59 | Structural Engineering - Welding | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Upon joint inspection of TVA Hanging Beam by Cxxx and Cxxx it was discussed that one of the hanging beams, although welded fit for purpose and signed off by the welding inspector was not visually welded to the same standard as the other welds. The location of this weld is shown on attached marked up copy of Cxxx-JUL-S-DDA-CR094_SH005-50201. It was discussed to either prove the weld was fit for purpose or replace the weld. Cxxx had welding availability and clear access to complete these work so decided to replace the weld to satisfy the Cxxx concerns. The attached welding report shows that the weld has been completed tested and accepted resolving any concerns by Cxxx.
| 03SR - Stations (RfL) | Cxxx-NCR-000753 | NCR | Stepney Green - Builderswork Opening Clash with Refuge Area Steelwork |  | Contr | SKC |  |  | 2018-06-30 | 2018-07-23 19:02 | 23 | 2018-05-22 17:29 | Architectural - Brickworks/Blockworks | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | Cxxx note that an opening on B5 has been missed during the installation of the blockwork at Stepney Green on B5 as indicated on the attached marked up copy of Cxxx-SKC-E-DDL-CR094_SH005-00650. Cxxx also note that this opening in its original location will clash with the structural steelwork installed for the refuge area. As such Cxxx will need to lower this opening to avoid the clash. This change has been accepted by the Cxxx designer as per attached response to RFI. Cxxx also note that the builderswork drawing indicated the opening is 350mm by 350mm, whereas to ensure minimum firestopping requirements are met the opening will need to be 400mm x 400mm
| 03SR - Stations (RfL) | Cxxx-NCR-000754 | NCR | Doors DB2.06 & DB3.06 - gap between frame and structural opeing exceeds 15mm |  | Contr | SKC |  |  | 2018-06-06 | 2018-06-11 15:13 | 5 | 2018-05-23 07:05 | Fire - Compartmentation | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Cxxx-SKC-A-RSP-CR144_WS155-50001 Clause JL20.3209 part b) states: "Gaps to head and jambs of doors to frames shall be consistent, of minimal dimensions and shall maintain the performance and functional requirements of the door(s)." The door openings for DB2.06 and DB3.06 are not plumb as a result of construction by Cxxx. As a result, when the doors have been installed, with the frames plumb, the gap between the jamb and frame exceeds 15mm in places, up to but not exceeding 30mm. would propose using __ C144 and __ intumescent mastic as would be used in a normal example.
| 03SR - Stations (RfL) | Cxxx-NCR-000755 | NCR | ESS - Starting work without IFC Drawings |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2018-06-12 | 2018-06-14 11:10 | 2 | 2018-05-29 08:44 | Civil - Roadworks Formation | 2000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | In order to meet the requirements of Cxxx-PMI-01467, and Cxxx-PMI-01486, Cxxx are proceding with the construction of the road and new area without Issued for Construction Drawings. Individual elements of the design are being accepted via the PTR process, See: Cxxx-FCD-001288, Cxxx-FCD-001289, Cxxx-FCD-001298, further PTR's will be raised for individual elements of the works. Cxxx will continue to do this in order to meet the programme.
| 03SR - Stations (RfL) | Cxxx-NCR-000756 | NCR | ESS - Lighting columns installed without an accepted ITP |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2018-06-14 | 2018-06-27 09:23 | 13 | 2018-05-31 09:06 | Civil - Street Architecture | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | The lighting columns at Eleanor Street were installed without their installation being detailed on a ITP. The ITP for the roadworks: Cxxx-SKC-C-ITP-CR094_WS110-50077 did not specify the requirements for their installation.
| 03SR - Stations (RfL) | Cxxx-NCR-000757 | NCR | Limmo Peninsula Shaft - Redlining on P Status Drawings |  | Contr | SKC |  |  | 2020-10-19 | 2020-11-19 09:56 | 31 | 2018-06-05 15:58 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | These drawings have reverted to/remained at P status due to instructions, including Cxxx-PMI-1408/1409/1421. Due to the timescales involved in converting these to C status has opted to issue redline information on P status drawings. will ensure that other than this the procedure for obtaining C status drawings and subsequent as-builts (based on these P status redlines) is as per the Crossrail Management of Redlines and As Builts Procedure. will also review and check that there are no further changes to these drawings once they are redlined.
| 03SR - Stations (RfL) | Cxxx-NCR-000758 | NCR | ESS - Use of Unapproved CRL-MCR-006117 (LS-AFS Automatic Float Switch) |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2018-08-27 | 2018-07-03 14:43 | -55 | 2018-06-05 16:21 | Materials - Approval | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | At ESS, CRL-MCR-006117 Sontay High and Low Level Float Alarm (LS-AFS Automatic Float Switch) has been installed without being approved.
| 03SR - Stations (RfL) | Cxxx-NCR-000759 | NCR | Firemain Tank too Large |  | Contr | SKC |  |  | 2018-09-28 | 2019-01-28 08:16 | 122 | 2018-06-06 14:23 | Mechanical - Public Health Engineering | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Firemain tank installed at LPS is too large for the space and does not allow for access into the tank for maintenance purposes.
| 03SR - Stations (RfL) | Cxxx-NCR-000760 | NCR | LPS - Use of Unapproved CRL-MCR-006117 (LS-AFS Automatic Float Switch) |  | Contr | SKC |  |  | 2018-08-31 | 2018-08-08 11:30 | -23 | 2018-06-06 15:36 | Materials - Approval | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | At LPS, CRL-MCR-006117 Sontay High and Low Level Float Alarm (LS-AFS Automatic Float Switch) has been installed without being approved.
| 03SR - Stations (RfL) | Cxxx-NCR-000762 | NCR | Stepney Green - Incorrectly Screeding the __ Storage Room |  | Contr | SKC |  |  | 2018-08-27 | 2018-08-15 10:17 | -12 | 2018-06-07 14:50 | Architectural - Flooring | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Previous Construction - Problems based on previous construction errors | Completed |  | Cxxx note that screed was installed in the __ Storage Room when as per Cxxx-SKC-A-DDA-CR094_SH005_6-00211, the room should've only been FL-101 - Epoxy Resin on Concrete Slab.
| 03SR - Stations (RfL) | Cxxx-NCR-000763 | NCR | Stepney Green - Missalignment of Drainage and Builderswork between S5 and Headhouse |  | Contr | SKC |  |  | 2018-10-29 | 2018-07-25 10:48 | -96 | 2018-06-12 10:02 | Civil - Drainage | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | note that between S5 and RWP a minor S bend (2 45 degrees) has been installed between the perimeter wall and the manhole. Please refer to attached marked up drawing and photograph. This has been completed as the RWP through the wavy wall had to be post cored. As part of the Cxxx stipulation the core hole had to not impact the reinforcement. As such the opening was raised to avoid the horizontal reinforcement. This has meant that the fall between the two pipes was greater than the design fall and as such supply chain a S bend to maintain the design fall and the correct invert levels. As this bend is minor note that the length of pipe is still rob-able/jet-able and as a purely rain water pipe foresee no issues with this arrangment and as such can CEG please confirm this is acceptable. HI Update 23/07/2018 Further to rejection use as is, will adjust the pipework removing the S bend and install the pipe circa 50 mm higher as it enters the manhole and ensure that the benching matches this changed. Can CEG/CRL please confirm that this is acceptable.
| 03SR - Stations (RfL) | Cxxx-NCR-000764 | NCR | Eleanor Street Shaft - Redlining on P Status Drawings |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2020-10-12 | 2020-09-30 12:00 | -12 | 2018-06-13 15:22 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | These drawings have reverted to/remained at P status due to instructions, including Cxxx-PMI-1408/1409/1432. Due to the timescales involved in converting these to C status has opted to issue redline information on P status drawings. will ensure that other than this the procedure for obtaining C status drawings and subsequent as-builts (based on these P status redlines) is as per the Crossrail Management of Redlines and As Builts Procedure. will also review and check that there are no further changes to these drawings once they are redlined.
| 03SR - Stations (RfL) | Cxxx-NCR-000765 | NCR | Stepney Green Shaft - Redlining on P Status Drawings |  | Contr | SKC |  |  | 2020-10-12 | 2020-11-19 09:54 | 38 | 2018-06-19 08:57 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | These drawings have reverted to/remained at P status due to instructions, including Cxxx-PMI-1408/1409/1434. Due to the timescales involved in converting these to C status has opted to issue redline information on P status drawings. will ensure that other than this the procedure for obtaining C status drawings and subsequent as-builts (based on these P status redlines) is as per the Crossrail Management of Redlines and As Builts Procedure. will also review and check that there are no further changes to these drawings once they are redlined.
| 03SR - Stations (RfL) | Cxxx-NCR-000766 | NCR | Fisher Street Shaft - Redlining on P Status Drawings |  | Contr | SKC |  |  | 2020-10-12 | 2020-10-06 18:02 | -6 | 2018-06-19 08:58 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | These drawings have reverted to/remained at P status due to instructions, including Cxxx-PMI-1408/1409/1433. Due to the timescales involved in converting these to C status has opted to issue redline information on P status drawings. will ensure that other than this the procedure for obtaining C status drawings and subsequent as-builts (based on these P status redlines) is as per the Crossrail Management of Redlines and As Builts Procedure. will also review and check that there are no further changes to these drawings once they are redlined.
| 03SR - Stations (RfL) | Cxxx-NCR-000768 | NCR | ESS - ESS SCADA Spare Capacity |  | Contr | SKC |  |  | 2018-08-28 | 2018-11-19 08:23 | 83 | 2018-06-19 08:50 | Electrical - Cable Management | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | With reference to DWG: Cxxx-SKC-E-DWG-CR094_WS110-50089. Following a site inspection with CRL Field Engineers it was identified that the Comms/SCADA section of Trunking appeared to be over-populated resulting in compromised spare capacity and ability to fit trunking lidding.
| 03SR - Stations (RfL) | Cxxx-NCR-000769 | NCR | Stepney Green - PFR/TVC Doors |  | Contr | SKC |  |  | 2018-08-10 | 2018-08-28 10:40 | 18 | 2018-06-26 14:34 | Architectural - Doors | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Please see attached RFI to designers. note that wish to implement this RFI. Can CRL please confirm this is acceptable
| 03SR - Stations (RfL) | Cxxx-NCR-000770 | NCR | Stepney Green - B3 Intervention Stair Door |  | Contr | SKC |  |  | 2018-08-20 | 2018-07-23 15:57 | -28 | 2018-06-26 15:36 | Architectural - Doors | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | note that the angle supporting the lintel in the B3 intervention door was cut. This meant that the bearing was not 150mm as per the required minimum bearing. have discussed a proposal for remedial as per the attached RFI to designers who have accepted the proposal. Can CRL please confirm that this is an acceptable remedial option.
| 03SR - Stations (RfL) | Cxxx-NCR-000771 | NCR | Fencing ITP |  | Contr | SKC |  |  | 2018-07-23 | 2018-07-18 10:23 | -5 | 2018-06-25 14:28 | Architectural - Security | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | SR2, unrated and timber hoarding works have been undertaken without a coded and approved ITP.
| 03SR - Stations (RfL) | Cxxx-NCR-000772 | NCR | SR2 fencing mesh overlap |  | Contr | SKC |  |  | 2018-07-27 | 2018-08-09 09:40 | 13 | 2018-06-29 17:48 | Civil - Landscaping | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | SR2 mesh overlap was observed 13mm less than the 58mm specified.
| 03SR - Stations (RfL) | Cxxx-NCR-000773 | NCR | ESS - Eleanor street permanent gate installed without an accepted ITP |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2018-07-18 | 2018-10-31 07:39 | 105 | 2018-07-04 13:41 | Architectural - Doors | 1000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Eleanor street permanent gate installed without an accepted ITP
| 03SR - Stations (RfL) | Cxxx-NCR-000774 | NCR | ESS - Dished drainage channels along main road (Eleanor street) cracked |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2018-08-31 | 2018-11-02 10:26 | 63 | 2018-07-04 14:06 | Civil - Civil Engineering General | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Dished drainage channels along main road (Eleanor street) cracked
| 03SR - Stations (RfL) | Cxxx-NCR-000775 | NCR | No MCR for ELS Gate Works |  | Crossrail | XRL | ELS - Eleanor Street Shaft (Central) |  | 2018-07-31 | 2018-11-27 07:49 | 119 | 2018-07-09 11:16 | Materials - Approval | 1000 |  | Planning | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Works to the Eleanor Street gate were started without an accepted MCR. Cxxx were given the opportunity to raise this NCR but declined.
| 03SR - Stations (RfL) | Cxxx-NCR-000776 | NCR | ESS - High Expansion Intumescent Matic used without an approved MCR |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2018-09-30 | 2018-08-01 14:46 | -60 | 2018-07-10 12:20 | Fire - Compartmentation | 1000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Upon inspection of the GL H Soft Seal fireproofing Cxxx have discovered that it's specialist subcontractor has installed __ High Expansion Sealant around the Soft Seal. This is an approved detail - see the data sheet attached to the soft seal MCR: Cxxx-SKC-C-LRC-CR094_WS110-50137. __ High Expansion Sealant is also approved on the LU product approval register, certificate no 2454. This sealant while part of the Firepro Range was not covered under the original soft seal MCR, as the standard white acoustic intumescent was covered instead. As the High Expansion Mastic is black in colour it will be visibly different. This NCR is raised to clarify these details.
| 03SR - Stations (RfL) | Cxxx-NCR-000777 | NCR | Installation proceeded without the approval of MCR 6719 |  | Contr | SKC |  |  | 2018-12-21 | 2018-08-28 14:28 | -115 | 2018-07-13 12:05 | Fire - Detection | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Lack or improper material identification and traceability | Completed |  | __ VLP Aspirating Smoke Detector has been installed prior to the acceptance of the MCR
| 03SR - Stations (RfL) | Cxxx-NCR-000778 | NCR | The Contractor was unable to supply evidence of Door Prototypes acceptance |  | Crossrail | XRL |  |  | 2018-08-31 | 2018-09-03 09:11 | 3 | 2018-07-17 12:21 | Architectural - Doors | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other management problem | Completed |  | A planned Crossrail surveillance was undertaken on 11th July 2018 at Cxxx Stepney Green Shaft to look at the installation of Doors. On request the Contractor unable to provide evidence of acceptance for Door Set Prototypes. As such it could not be verified that the Prototypes had been produced and acceptance was in place.
| 03SR - Stations (RfL) | Cxxx-NCR-000779 | NCR | The Contractor was unable to supply evidence of Door sample acceptance. |  | Crossrail | XRL |  |  | 2018-08-28 | 2018-09-03 09:12 | 6 | 2018-07-17 12:27 | Architectural - Doors | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | A planned Crossrail surveillance was undertaken on 11th July 2018 at Cxxx Stepney Green Shaft to look at the installation of Doors. On request the Contractor unable to provide evidence of acceptance for Door Set Samples.
| 03SR - Stations (RfL) | Cxxx-NCR-000780 | NCR | Title Contractor has not installed Door Sets to the drawing. |  | Crossrail | XRL |  |  | 2019-10-31 | 2019-09-13 14:55 | -48 | 2018-07-17 12:38 | Architectural - Doors | 10000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | On checking the drawing ‘Typical Door Details’ Cxxx-SKC-A-DDD-CR094_SH005_*Z-00725 (Rev C01) it was found that in all cases the above door sets have been incorrectly installed. The drawing shows that the gap between the substructure and door frame head and jamb is 15mm the door sets checked had gaps of approximately 5mm, in some cases the mastic has lapped the edge of the door jamb and the gap could not be correctly assessed. As the gap between the substructure and door frame head and jamb is considerably smaller than shown on drawing *Z-00725 as such it is not known if the fire stopping has been installed as shown and provide the correct fire and acoustic performance
| 03SR - Stations (RfL) | Cxxx-NCR-000781 | NCR | Contractor is installing Door Sets using Code 3 Door schedule. |  | Crossrail | XRL |  |  | 2018-09-30 | 2018-10-02 14:21 | 2 | 2018-07-17 12:42 | Architectural - Doors | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | A planned Crossrail surveillance was undertaken on 11th July 2018 at Cxxx Stepney Green Shaft to look at the installation of Doors. On reviewing the ‘Stepney Green Shaft - Door Schedule’ Cxxx-SKC-A-TSC-CR094_WS108-50001 (Rev 2) it was identified that the document had been at a Decal Code 3 status for at least 6 months. Further checks revealed that Revision 1 has also been at Code 3 since16/11/2015.
| 03SR - Stations (RfL) | Cxxx-NCR-000782 | NCR | Contractor was unable to supply check sheets for fire stopping around Door Sets |  | Crossrail | XRL |  |  | 2018-12-31 | 2019-02-05 15:11 | 36 | 2018-07-17 12:46 | Architectural - Doors | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | A planned Crossrail surveillance was undertaken on 11th July 2018 at Cxxx Stepney Green Shaft to look at the installation of Doors. On request the Contractor was unable produce fire stopping check sheets for the sampled door sets. The ITP ‘Firestopping Installation to Stepney Green Shaft and Headhouse, *50015 (Rev 4) inspection number 4.1 states verifying documents; Quality Control Report, Check Sheets; QCR07, QCR05, QCR02, Fire Stop Register and photo of Fire Stop Label.
| 03SR - Stations (RfL) | Cxxx-NCR-000783 | NCR | Installing External Lights without approved MCR; CRL-MCR-005871 |  | Contr | SKC |  |  | 2018-12-21 | 2018-09-17 15:42 | -95 | 2018-07-19 10:30 | Electrical - Lighting | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | The external lighting bollards have been installed prior to the approval of the MCR.
| 03SR - Stations (RfL) | Cxxx-NCR-000784 | NCR | Stepney Green - Intervention Stair door clash with Lintel Angle |  | Contr | SKC |  |  | 2019-06-24 | 2019-05-31 15:58 | -24 | 2018-07-25 10:37 | Architectural - Doors | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Further to the attached RFI998 to Cxxxs designer, note that the steel angle supporting the lintel for the door opening on B1, B2 and B4 intervention stair door (DB4.01, DB2.01 and DB1.01) protrudes into the opening due to the lintel not being notched. As such the door frame clashes with the angle. have got acceptance from the manufacturer and fire engineer (as attached) that it is acceptable to notch the door frame by circa 10mm to allow the frame to fit. Following this the door frame would be fire stopped as per detail captured in Cxxx-SKC-A-DDD-CR094_SH005_Z-00725 and Door - Steel Plate. note that this has been accepted by both designer and by the manufacturer. As such can CEG/CRL please confirm this an acceptable solution. Response 21/11/2018 The angle will be protected from both sides by 2hr fireboard continuous along the frame of the door. This will provide a 2hr fire rating. The doors themselves are only 30 minute fire rating. Please see attached email from Fire stopping contractor stating that they will certify then application of the fireboard covering the notched area (as per detail attached). 15/02/2019 Fire Engineer has assessed proposal and has no objections.
| 03SR - Stations (RfL) | Cxxx-NCR-000785 | NCR | ESS - Manhole Water Tests |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2018-09-28 | 2018-12-05 10:41 | 68 | 2018-07-30 12:10 | Civil - Drainage | 3000 |  | System Defect | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Following the water testing of manholes C1 & S7 at Eleanor Street on 23/07/18. The manholes have failed to meet the requirements of BS EN 1610. Cxxx note that BS EN 1610 sets out a more stringent set of requirements than required by the Cxxx Drainage Specification: Cxxx-SKC-D-RSP-CR094-50002 JR12.2200 Manhole C1 passed the Cxxx specified testing but began dropping after the water level reached over 1000mm above the crown of the pipework. Manhole S7 dropped 120mm over a 30min period and therefore failed both tests. CRL have requested that Cxxx change their testing to follow the requirements set out in BS EN 1610.
| 03SR - Stations (RfL) | Cxxx-NCR-000786 | NCR | Stepney Green - PFR Stairs Base Plate Clash |  | Contr | SKC |  |  | 2018-10-29 | 2018-08-16 15:07 | -74 | 2018-08-03 07:21 | Architectural - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Upon install of the PFR stairs, it was evident of a clash between 2no baseplates for the stairs and the framework that supports the ductwork in this room by 100mm.
| 03SR - Stations (RfL) | Cxxx-NCR-000787 | NCR | ESS - Door Swing Clashing with Resin Flooring |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2018-09-28 | 2018-09-06 08:25 | -22 | 2018-08-10 14:27 | Architectural - Flooring | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | In two locations within the head-house, there are doors that are clashing with the resin flooring. These are in the Welfare Room & Fan Equipment Room (FER). (See Attached Plan: Cxxx-SKC-A-DDA-CR094_SH007_1-00201)
| 03SR - Stations (RfL) | Cxxx-NCR-000789 | NCR | Vandex Installation on eposed D-wall |  | Contr | SKC |  |  | 2019-02-28 | 2019-03-05 16:43 | 5 | 2019-01-28 11:12 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Upon inspection of Vandex __75 Waterproofing mortar on the exposed D-wall within the TVA (B00) it was noticed that small hairline cracks had appeared within the finish.
| 03SR - Stations (RfL) | Cxxx-NCR-000790 | NCR | Stepney - Shakeproof washers on ductwork installation |  | Contr | SKC |  |  | 2018-12-31 | 2019-08-15 05:31 | 227 | 2018-09-05 12:13 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Requirement of JY90 MEP Specification Fixing to Building Fabric (CRL1-XRL-M-RSP-CR001-50089) clause JY90.3210 Fixing to Metalwork for shakeproof washers have not been installed.
| 03SR - Stations (RfL) | Cxxx-NCR-000791 | NCR | ESS: Removal of Ground Floor Lighting without FCD |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2018-09-28 | 2018-11-07 20:26 | 40 | 2018-09-04 14:12 | Electrical - Lighting | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | 4 x Ground Floor Tunnel Ventilation Area Lights removed without a PMI and subsequent FCD being raised.
| 03SR - Stations (RfL) | Cxxx-NCR-000792 | NCR | Stepney - Ductwork support spacing in risers |  | Contr | SKC |  |  | 2018-09-19 | 2018-09-26 11:31 | 7 | 2018-09-05 09:49 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | With reference to the ductwork installation in risers at Stepney Green Shaft the Contractor is raising an NCR against clause JY30.3102 stating the following: JY30.3102 Specific Requirements aa) Supports for vertical ductwork in buildings shall be generally located at each floor slab but subject to a maximum spacing of 4 metres. Please find attached markup up F2 construction drawings specifying the brackets at every level and at a maximum of circa 5.8m spacing in the risers. The install has been done to the specialist designer’s detail and as stated in the preceding clause from the M&W spec: JY30.1422 Ductwork Supports a) Ductwork shall be supported in accordance with DW 144 Part 6 Section 19 as appropriate. See extract from DW 144 part 6: “The design of supports for vertical ducts is dictated by site conditions, and they are often located to coincide with the individual floor slabs, but if the spacing exceeds 4 metres the system designer must specify their requirements.” Based on the above the install and design is compliant to clause JY30.1422.
| 03SR - Stations (RfL) | Cxxx-NCR-000793 | NCR | Use of 2no. 150mm filter pipes between S29 and S28 instead of 1no. 225mm pipe. |  | Contr | SKC |  |  | 2018-10-16 | 2019-01-16 08:24 | 92 | 2018-10-02 14:08 | Civil - Drainage | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | Due to a change in the design after having already procured the materials, have installed 2no. 150mm filter pipes (top half perforated) side by side between S28 and S29 instead of the 1no. 225mm filter pipe (top half perforated) shown on drawing Cxxx-SKC-D-DDA-CR144_SH011_Z-00011.
| 03SR - Stations (RfL) | Cxxx-NCR-000796 | NCR | Gap between handrail kickplate and middle rail exceeding 500mm at Plenum walkable gutter |  | Contr | SKC |  |  | 2018-10-31 | 2019-02-21 07:32 | 113 | 2018-09-25 13:38 | Architectural - Handrail | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | The gap between the kickplate and the lower handrail is 540mm. The maximum gap allowed as per the British Standards is 500mm.
| 03SR - Stations (RfL) | Cxxx-NCR-000797 | NCR | ESS - Staircase Opposed Blade Dampers |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2018-11-06 | 2019-01-16 09:33 | 71 | 2018-09-26 09:35 | Mechanical - Mechanical Engineering General | 10000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Management Problem - Inadequate supervision | Completed |  | Eleanor Street Mechanical Service Schedule (Cxxx-SKC-M-RSP-CR094_WS110-50002) Rev2.0 page 23 requires intervention staircase grills to have "a separate volume control damper to be positioned before the grille" as such amendments have to be made to the currently installed 4x staircase grilles within the stairwell to successfully complete balancing of the pressurisation system.
| 03SR - Stations (RfL) | Cxxx-NCR-000798 | NCR | Travellers Site - Drainage Defects |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2018-12-17 | 2018-10-24 09:07 | -54 | 2018-10-03 15:54 | Civil - Drainage | 25000 |  | Incorrect Installation | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following the remedial work carried out to the travellers site drainage there are three pipe bellies that remain. These are: Plot 7 (Plot F) (FF1 – FF2) 10% Belly (Reason: drainage run is under chalet) Plot 10 (Plot I) (FI3-VCP – FI1) 20% Belly (Reason: drainage run is encased in concrete and not currently in use) Plot 12 (Plot K) (FK3-VCP – FK1) 15% Belly (Reason: drainage run is encased in concrete and not currently in use) Cxxx-SKC-O4-LRC-CR094_WS110-50099 Covers the remaining remedial works successfully carried out and accepted by LBTH. Cxxx-SKC-A-DWG-CR094_WS110-50050 and Cxxx-SKC-A-DWG-CR094_WS110-50051 are the plan drawings for the drainage.
| 03SR - Stations (RfL) | Cxxx-NCR-000799 | NCR | ESS - Brickwork around manhole C2 |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2018-12-21 | 2018-10-10 08:00 | -72 | 2018-10-03 17:25 | Civil - Streets & Highways | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following on from Cxxx-FCD-001379, due to design changes in the levels of the road, the number of courses of brickwork required around MH C2 have increased to 6. Sewers For Adoption Series 7 states 1 to 4 courses. Cxxx-SKC-D-DDD-CR094_SH007_Z-00002 states 1 - 3 courses.
| 03SR - Stations (RfL) | Cxxx-NCR-000800 | NCR | W__O Safety Grip Flex noncompliance within shaft |  | Contr | SKC |  |  | 2019-03-25 | 2018-12-13 11:37 | -102 | 2018-11-27 10:19 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | As per Mile End architectural specification (Cxxx-SKC-A-RSP-CR094_WS109-50001) clause JM60.1207 and drawings (for example Cxxx-SKC-A-DDA-CR094_SH006_1-00206) we have installed ‘Safety Grip Flex' on our landings in accordance with the manufacturer written recommendations. This was accepted code 1 but after a site visit for a benchmark. CSG raised some concerns over the suitability of the product. Further investigation has revealed that this product contains polyurethane which is not allowed under LU regulations. One landing has been painted so approximately 4m2 weighing at approximately 4.5 kg.
| 03SR - Stations (RfL) | Cxxx-NCR-000801 | NCR | ESS_LV panel labels to be amended |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2019-10-31 | 2020-05-01 07:30 | 183 | 2018-10-14 12:19 | Electrical - LV Equipment | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Upon review of the LV panel ID labels for the outgoing circuits, it has been found that some of these labels needs to be changed to reflect the correct load description. Circuit reference that require change of labels. Outgoing circuit breaker A-25 Outgoing circuit breaker A-20 Outgoing circuit breaker A-17 Outgoing circuit breaker A-16 Outgoing circuit breaker A-23 Outgoing circuit breaker B-26 Outgoing circuit breaker B-25 Outgoing circuit breaker B-23 Outgoing circuit breaker B-20 Outgoing circuit breaker B-17 Outgoing circuit breaker B-16 Outgoing circuit breaker B-13
| 03SR - Stations (RfL) | Cxxx-NCR-000802 | NCR | Stepney Green - Incorrect Fire Stopping Detail Applied to Cable Trunking |  | Contr | __R |  |  | 2019-04-30 | 2019-05-10 12:12 | 10 | 2018-10-31 13:56 | Fire - Compartmentation | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Within cable trunking the fire stopping subcontractor has installed Quelfire QF1. The detail calls for only mineral fibre (__ RWA45) under compression within the section of trunking transitioning fire compartments. Other electrical trades still have cables to pull through these sections of trunking. The incorrect detail has been applied to 4 sections of trunking.
| 03SR - Stations (RfL) | Cxxx-NCR-000804 | NCR | Concrete cubes not taken for another grasscrete concrete pour |  | Contr | SKC |  |  | 2018-12-14 | 2018-12-05 14:09 | -9 | 2018-11-09 11:20 | Architectural - Landscape Architectural | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Concrete cubes were not taken for 1 further concrete pour. are therefore unable to prove that the concrete used has achieved the required design strength. See attached marked up drawing to identify the relevant grasscrete bays.
| 03SR - Stations (RfL) | Cxxx-NCR-000805 | NCR | Mile End - Resin Flooring |  | Contr | SKC |  |  | 2019-01-18 | 2019-03-13 14:01 | 54 | 2018-11-21 11:10 | Architectural - Flooring | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | The resin floor in area in the HV Riser 1 on Level 10 (2/822) has started to flake and come off. It would appear this is either because the concrete in this area was not prepared properly before the application of the resin coats, or mechanical damage has occurred in this area due to something dropping on it.
| 03SR - Stations (RfL) | Cxxx-NCR-000806 | NCR | S11 and S15 Manhole Cover Levels |  | Contr | SKC |  |  | 2019-02-25 | 2019-04-11 12:05 | 45 | 2018-11-28 16:40 | Civil - Drainage | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | notes there is incorrect design information for the cover levels of manhole S11 and S15 in relation to the finished surface level. The design height of S11 cover level is 110.35m, however the surface level at this position (based on the contours) is approximately 110.18m, creating a difference of 170mm. This manhole has already been constructed by sub-contractor Klinbridge, who have built it to the specified design level. Similarly, the design height of S15 cover level is 110.24m, however the surface level at this position (based on the contours) is approximately 110.15m, creating a difference of 90mm. This manhole has also already been constructed by sub-contractor Klinbridge, who have built it to the specified design level. The level difference between the manholes and the required surface level is significant and will create an issue when we are constructing the finished surface in this area.
| 03SR - Stations (RfL) | Cxxx-NCR-000807 | NCR | Broken Pipe S1-S5 |  | Contr | SKC |  |  | 2019-05-31 | 2019-06-12 07:58 | 12 | 2019-01-18 15:26 | Civil - Drainage | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | During the flushing out of the drainage system in Limmo Peninsula, a piece of the backdrop Tee piece going from S1 into S5 broke (See attached photos and drawings)
| 03SR - Stations (RfL) | Cxxx-NCR-000808 | NCR | No benchmark survey taken for all fencing at Limmo Peninsula |  | Contr | SKC |  |  | 2019-02-06 | 2019-02-15 12:26 | 9 | 2019-01-23 14:36 | Architectural - Landscape Architectural | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | No benchmark surveys were undertaken for the fencing installation at Limmo.
| 03SR - Stations (RfL) | Cxxx-NCR-000809 | NCR | Stepney Green - Exposed Top Face of Structural Beam |  | Contr | SKC |  |  | 2019-06-01 | 2019-07-18 16:59 | 47 | 2019-03-05 10:39 | Structural Engineering - Steel Member | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | The tops of 4no beams located on B01 and B02 are exposed and have not been installed with 15mm of concrete as per the approved detail
| 03SR - Stations (RfL) | Cxxx-NCR-000810 | NCR | Louvre fabrication ITP has not been written specific to Limmo Peninsula |  | Contr | SKC |  |  | 2019-02-25 | 2019-02-22 08:30 | -3 | 2019-02-11 15:23 | Architectural - General | 1000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | Louvre fabrication ITP has not been written specific to Limmo Peninsula. The 'site wide' ITP refers to products only specific to other shafts. The louvre products used at Limmo Peninsula have there not been captured under an ITP fabrication record. MCR Cxxx-SKC-C-LRC-CR094-50410 is code 1. The products used at Limmo comply with the site specification (Cxxx-SKC-A-RSP-CR144_WS155-50001). __ (Louvre fabricator) have supplied check sheets which covers the same information as the check sheets that are within the approved site wide ITP. They have also supplied a certificate of conformity for the supplied louvres.
| 03SR - Stations (RfL) | Cxxx-NCR-000811 | NCR | Fisher Street - Manhole C1 Water Test |  | Contr | SKC |  |  | 2019-02-26 | 2019-02-20 07:53 | -6 | 2019-02-12 16:19 | Civil - Drainage | 1000 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | BS EN 1610:2015 outlines the requirements of water testing manholes in clause 13.3. The wetted internal surface of Manhole C1 had an allowable water loss of approximately 3.2L in 30mins, which is a drop in height of 2.2mm. When it was tested the actual drop was 5mm (a loss of approximately 7.1L) in 30mins.
| 03SR - Stations (RfL) | Cxxx-NCR-000812 | NCR | Fisher Street - Resin Floor Damage - B2 Lift Lobby Door Threshold |  | Contr | SKC |  |  | 2019-05-31 | 2019-07-05 09:06 | 35 | 2019-02-12 16:31 | Architectural - Flooring | 1500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The resin floor in the threshold of door number DB2.06 has been damaged. 08/04/2019 Update: The resin floor was damaged locally around the door threshold only. The door does not affect the floor in any other area.
| 03SR - Stations (RfL) | Cxxx-NCR-000813 | NCR | Replacement of riser grilles |  | Contr | SKC |  |  | 2019-03-29 | 2019-04-01 08:30 | 3 | 2019-02-13 09:39 | Architectural - General | 2000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Grilles were fabricated incorrectly, anticipating CMS to run through a void which had been purposefully made. Once CMS was installed, in some instances, this void was not needed. The grilles therefore had to be replaced with no void. The grilles which were installed incorrectly were as follows: - B4, Coms 1. (2 grilles in this room, the incorrect grille was the southern most grille). - B5, Coms 1. (2 grilles in this room, the incorrect grille was the southern most grille).
| 03SR - Stations (RfL) | Cxxx-NCR-000814 | NCR | Fisher Street - Resin Floor Damage - B2 LV SR 2 Door Threshold |  | Contr | SKC |  |  | 2019-05-31 | 2019-07-02 08:16 | 32 | 2019-02-13 10:02 | Architectural - Flooring | 1500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The resin floor in the threshold of door number DB2.03 has been damaged. 08/04/2019 Update: The resin floor was ground down (approx. 2-3mm) to allow the door threshold for door DB2.03 to be installed. The dimensions of the affected area are 2000mm x 250mm (approx.).
| 03SR - Stations (RfL) | Cxxx-NCR-000815 | NCR | ESS - Drainage manhole S11 changed to plastic and confirmation of dished channels |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2019-03-29 | 2019-03-05 08:56 | -24 | 2019-02-15 18:01 | Civil - Drainage | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | 1. MH S11 has been changed to a plastic preformed manhole due to its size. Cxxx were unable to source a 600mm diameter concrete ring, hence a plastic manhole has been used. The manhole was surrounded with 150mm of concrete and then topped with 3 courses of engineering bricks and a D400 600 x 600 cover. This change was made without it being formalised on eB. 2. On the change to the levels and alignment of the dished channel along GL H changed in FCD-001462 (WW RFI-1102 attached), CEG have asked for confirmation that: • It is acceptable to have the increased length of dished channel, now 25m • The flowrate in the channel will not cause it to overflow. • There is sufficient fall in the channel.
| 03SR - Stations (RfL) | Cxxx-NCR-000817 | NCR | STG - Firestopping of conduits accessible only from one side |  | Contr | SKC |  |  | 2019-06-20 | 2019-10-04 14:15 | 106 | 2019-03-06 09:22 | Fire - Compartmentation | 5000 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | At Stepney Green shaft, CMS for electrical and communications wiring has been installed using the following detail (shown in attachment "Detail.pptx"): - 25mm conduit passes through a 38mm core hole made in RC or blockwork. - Conduit enters a 100mm x 100mm (or similar) electrical box which is fixed to the wall by the method of bolting it to unistruts which are then fixed to the wall. This holds the box 40mm off the wall As a result, mastic can only be applied to the side of the wall without the adaptable box (mastic could be applied using a long nozzle, however depth/width of mastic cannot be guaranteed as it cannot be inspected).
| 03SR - Stations (RfL) | Cxxx-NCR-000818 | NCR | LPS - Welfare hot water and pressure pipework |  | Contr | SKC |  |  | 2019-06-24 | 2019-06-28 14:17 | 4 | 2019-04-25 10:09 | Mechanical - Hot & Cold Water Supplies | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During a CEG site visit to Limmo on 01/03/19 it was discovered that there were issues with the domestic hot water system in the welfare room: "The water heater and associated overflow and pressure systems have been moved from their intended location on the adjacent wall into the welfare cupboard below the sink. This installation is non-compliant with Building Regulations Part G due to the minimum spacing, pipe lengths and falls required with such a system."
| 03SR - Stations (RfL) | Cxxx-NCR-000819 | NCR | Stepney Green -Water Damage - CMS and Sockets in TVA B02 |  | Contr | SKC |  |  | 2019-08-19 | 2019-08-13 14:03 | -6 | 2019-05-17 15:58 | Electrical - General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | On level B02 of the TVA a section of trunking and 2no. socket outlets are located adjacent to the maintenance hatch. Due to ongoing lifting operations through the hatch there has been some water ingress causing the trunking to rust and the two socket outlets have been damaged. See attached mark-ups for elevation and plan views of the impacted equipment, also see photos of damage: IMG_2810 and IMG_2811.
| 03SR - Stations (RfL) | Cxxx-NCR-000820 | NCR | Garden Street Damaged Granite Kerbs |  | Contr | SKC |  |  | 2019-11-30 | 2019-11-29 12:00 | -1 | 2019-07-01 14:42 | Civil - Kerbs | 3000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following Cxxx-PMC-03071 the contractor notes damage to permanent works on the granite kerbs installed along Garden Street.
| 03SR - Stations (RfL) | Cxxx-NCR-000821 | NCR | STG Louvre 1 - fixings for surround steel |  | Contr | SKC |  |  | 2019-10-31 | 2019-11-14 15:23 | 14 | 2019-09-04 09:05 | Structural Engineering - Structural Engineering - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | F2 drawing Cxxx-SKC-A-DWG-CR094_WS108-50115 (developed from Cxxx-SKC-A-DDD-CR094_SH005_Z-00704) shows that Louvre surround steel is fixed with M16 __ HIT-V-F Anchors with 110mm minimum embedment. This has not been achieved in places (100mm embedment appears is the worst case).
| 03SR - Stations (RfL) | Cxxx-NCR-000822 | NCR | The Contractor has commenced Fire Alarm Enhancement works without accepted ITP |  | Crossrail | XRL |  |  | 2019-10-24 | 2019-10-29 07:49 | 5 | 2019-09-04 09:46 | Fire - Fire Systems & General | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | During a Surveillance on 'Fire Systems-Deliverable Records' a review found that there is no accepted ITP in place for the Fire Alarm enhancement work carried out by MECE.
| 03SR - Stations (RfL) | Cxxx-NCR-000823 | NCR | Fire Detection/Alarm installation commenced without accepted F2 Design |  | Crossrail | XRL |  |  | 2020-06-16 | 2020-06-16 14:50 | 0 | 2019-09-04 10:09 | Fire - Fire Systems & General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | During a surveillance on 'Fire Systems-Deliverable Records' it was found that the Contractor has carried out the installation of the Fire Detection/Alarm System at Limmo Peninsular Shaft without accepted F2 Design in place.
| 03SR - Stations (RfL) | Cxxx-NCR-000824 | NCR | Fire Detection/Alarm installation commenced without accepted F2 Design |  | Crossrail | XRL |  |  | 2020-03-31 | 2020-03-17 06:49 | -14 | 2019-09-04 10:20 | Fire - Fire Systems & General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | During a surveillance on 'Fire Systems-Deliverable Records' it was found that the Contractor has carried out the installation of the Fire Detection/Alarm System at Fisher Street Shaft without accepted F2 Design in place.
| 03SR - Stations (RfL) | Cxxx-NCR-000825 | NCR | Fire Detection/Alarm installation commenced without accepted F2 Design |  | Crossrail | XRL | ELS - Eleanor Street Shaft (Central) |  | 2020-08-20 | 2020-08-06 09:58 | -14 | 2019-09-04 10:30 | Fire - Fire Systems & General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | During a surveillance on 'Fire Systems-Deliverable Records' it was found that the Contractor has carried out the installation of the Fire Detection/Alarm System at Eleanor Street Shaft without accepted F2 Design in place.
| 03SR - Stations (RfL) | Cxxx-NCR-000826 | NCR | Fire Detection/Alarm installation commenced without accepted F2 Design |  | Crossrail | XRL |  |  | 2020-08-24 | 2020-08-24 09:19 | 0 | 2019-09-04 10:36 | Fire - Fire Systems & General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | During a surveillance on 'Fire Systems-Deliverable Records' it was found that the Contractor has carried out the installation of the Fire Detection/Alarm System at Stepney Green Shaft without accepted F2 Design in place.
| 03SR - Stations (RfL) | Cxxx-NCR-000829 | NCR | Stepney Green - ATX1 & ATX2 Floor Drainage/Pooling |  | Contr | SKC |  |  | 2020-02-29 | 2020-06-19 10:09 | 111 | 2019-10-16 10:08 | Architectural - Flooring | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | In ATX 1 & ATX 2 the concrete slab was poured as per drawing number Cxxx-JUL-S-DDA-CR094_SH005-01207, which does not show falls in the concrete, however, drawing number Cxxx-JUL-P-DDA-CR094_SH005-00531 shows falls in the concrete towards the gullies. As a result of not following the design gradients water pools in ATX 1 & ATX 2 during wet weather. See attached photos.
| 03SR - Stations (RfL) | Cxxx-NCR-000830 | NCR | Firestopping Checksheets |  | Contr | SKC |  |  | 2019-12-30 | 2019-11-13 15:15 | -47 | 2019-10-11 12:54 | Fire - Compartmentation | 1000 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The following two ITP’s collectively cover the installation of fire protection at Limmo peninsula Shaft: • Inspection and Test Plan – Limmo Peninsula Shaft – Installation of __ Compound (Cxxx-SKC-C-ITP-CR144_WS155-50012) • Inspection and Test Plan – Firestopping Installation to Blockwork joints and Wind posts at Limmo. (Cxxx-SKC-C-ITP-CR144_WS155-50011) Inspections have been carried out to ensure installation is as per the specification and parameters included on the ITPs, however, upon review have identified that incorrect and inconsistent checksheets have been used to record the installation. Additionally some checksheets are missing. Further review identified that the checksheets included on the above ITP’s were not adequate as they did not provide the correct signature boxes for the required parties. Additionally, the checksheets were provided and letter-headed by __ as at the time of producing the ITP, it was not foreseen that the installation would be divided between two certified installers. It would not be appropriate to use these checksheets for works completed by __.
| 03SR - Stations (RfL) | Cxxx-NCR-000832 | NCR | ESS - External Door Ramp Handrail |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2019-11-22 | 2019-11-29 11:30 | 7 | 2019-11-08 09:34 | Architectural - Balustrade | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Installation of hand rail on external door ramp at Eleanor street shaft does not comply with Part K of building regulations and BS8300: - Handrails does not project horizontally 300mm from the stair nosing or end of ramp - The mid-rail is not installed at 600mm height.
| 03SR - Stations (RfL) | Cxxx-NCR-000833 | NCR | Eleanor Street Landscaping Boundary Wall |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2020-01-31 | 2020-01-31 11:29 | 0 | 2019-11-08 11:38 | Structural Engineering - Concrete Member | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Exhaustive engineering checks not carried out prior to documentation being submitted for Client review. Further examination identified one batch of mortar cube test result below required compressive strength.
| 03SR - Stations (RfL) | Cxxx-NCR-000834 | NCR | Eleanor Street Landscaping Boundary Wall foundation |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2019-11-15 | 2019-11-25 07:33 | 10 | 2019-11-12 08:48 | Structural Engineering - Concrete Member | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Engineering Checks, further investigations on the cube results have identified some cubes below the specified strength.
| 03SR - Stations (RfL) | Cxxx-NCR-000836 | NCR | limmo Peninsula-External drainage Post installation CCTV Observations |  | Contr | SKC |  |  | 2020-01-31 | 2020-01-07 15:33 | -24 | 2019-11-14 16:14 | Civil - Drainage | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following Observations have been raised in the review of cctv videos for the external drainage at Limmo Peninsula 1-Drainage Run b/w S5B-S5C 150dia-Half Perforated PVC Pipe: Deformed pipe at 6.49m 2- Drainage Run b/w S5B-S5C 150dia-Half Perforated PVC Pipe: bump/Dent near the crown section of the pipe at 33.63m 3-Drainage Run b/w S5B-S5C 150dia-Half Perforated PVC Pipe: Incorrect Orientation of some pipes (slotted section not located in the crown) 4-Drainage Run b/w S5B-S5C 150dia-Half Perforated PVC Pipe: Confirmation that Geotextile membrane have not been damaged 5-Drainage Run b/w S13-S20 150dia Vitrified Clay Pipe: Belly in the Pipe/Slump in last section (approx.1.5m length) of pipe work leading to back drop and holding minimal water 6-Drainage Run b/w S13-S20 150dia Vitrified Clay Pipe: Misaligned Pipe Joint at 8.68m 7-Drainage Run b/w S1-S5 150dia Vitrified Clay Pipe: Debris in the pipes 8-Drainage Run b/w F2-F3 100dia PVC Pipe: Debris in the pipes 9-Missing backdrop caps in Manholes S5, S15, and S20
| 03SR - Stations (RfL) | Cxxx-NCR-000837 | NCR | Pegler Valves and fittings - MCR not approved |  | Contr | SKC |  |  | 2020-04-27 | 2020-05-20 11:39 | 23 | 2020-01-10 16:50 | Mechanical - Hot & Cold Water Supplies | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Lack or improper material identification and traceability | Completed |  | Subcontractor has installed Pegler Valves and Fittings on the cold water supply ahead of MCR approval, across Limmo, Eleanor Street, Fisher Street and Stepney Green Shafts, to meet programme requirements and third party interfaces.
| 03SR - Stations (RfL) | Cxxx-NCR-000838 | NCR | Access Panel - Incorrect colour |  | Contr | SKC |  |  | 2020-01-27 | 2020-01-14 07:47 | -13 | 2020-01-13 11:06 | Architectural - Finishes | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | have installaed a wall access panel within the CER room which is the wrong colour. The colour of the access panel is plain white instaled of light grey. The specification of the access panel is the same as per MRC Cxxx-SKC-C-LRC-CR144_WS115-50462, only incorrect colour.
| 03SR - Stations (RfL) | Cxxx-NCR-000839 | NCR | Limmo Peninsula Shaft - <20% spare capacity provided for Fire Alarm System Loop 2 (JW50.1305) |  | Contr | SKC |  |  | 2020-02-24 | 2020-03-27 14:45 | 32 | 2020-01-14 15:47 | Fire - Fire Systems & General | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | During review of the Limmo Peninsula Fire Alarm System a non-compliance with JW50.1305 was identified. Loop 2 of the Fire Alarm System at Limmo Peninsula Shaft does not allow for 20% spare capacity.
| 03SR - Stations (RfL) | Cxxx-NCR-000840 | NCR | FIS, LPS, ESS, STG non-compliance against JW50.1305 j. for high level Multi-sensor conduit labelling |  | Contr | SKC |  |  | 2020-02-14 | 2020-07-03 08:48 | 140 | 2020-01-21 14:37 | Fire - Fire Systems & General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Within the Cxxx Shafts the ceiling heights within the shaft prevent labels from being added to conduits immediately before and after high level multi sensors within Fisher Street, Limmo Peninsula, Eleanor Street and Stepney Green. The labels if installed will also be illegible from the ground. This is non compliant with the requirements in JW50.1305 part j.
| 03SR - Stations (RfL) | Cxxx-NCR-000842 | NCR | Stepney Green Shaft - GATIC - Watertightness |  | Contr | SKC |  |  | 2020-05-22 | 2020-08-10 21:13 | 80 | 2020-03-11 16:23 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following the assured installation (Cxxx-SKC-O4-LRC-CR094_WS108-50132) of the Tunnel Vent Hatch (GATIC) at Stepney Green Shaft, and subsequent removals and installations as necessary to facilitate works, water ingress has been observed from inspections underneath. NCR has been raised based on not meeting clause JL22.1211 part E of the Stepney Green Architectural Specification Cxxx-SKC-A-RSP-CR094_WS108-50001 which states; e) Watertight: A film of graphite grease between the contact faces of the units provides a gas and airtight seal, and a watertight joint under normal rainwater conditions. Update 22/04/2020 - Feedback on additional information from Sandy Birdi from CRL below: Is the Densotape / Overband appropriate for this use? The Denso Overbanding tape is A polymer modified bitumen strip for sealing over cracks or failed reinstatement joints on secondary roads. There is no “off the shelf” solution to solve this problem and we’re not able to seal the joints with mastic as this will restrict the removability of the lids. have liased with Denso on the suitability of this product and they are confident it will create a waterproof seal to the joints. The product is suitable for joints up to 5mm. The joints on the GATIC are <1mm. The product has also previously been successfully used in a similar situation at the Tower of London. How will the system be verified to show this it's working? The idea is to trial this system to determine if it is suitable. It’s suitability will be obvious as water will be evident below should it fail. Denso are confident that the product will last for more than 10 years. Does this just delay further water seeping? The purpose of the Tape is to prevent water seepage not delay it. The Tape should last as long as the Gatic covers are not lifted. How often does the product need to be replaced?” The tape will only need to be re-instated/replaced if/when the Gatic Covers are lifted. The TVS fans are replaced every 10 years and/or 10000 hours (whichever is the lesser)
| 03SR - Stations (RfL) | Cxxx-NCR-000843 | NCR | Mile End RAM Demonstration case |  | Contr | SKC |  |  | 2020-04-27 | 2020-03-10 06:56 | -48 | 2020-03-02 09:49 | Architectural - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | The full process of the Mile End RAM Specification and Demonstration Report has not been followed fully during installation/T&C as RAM data from the suppliers of components not made available to .
| 03SR - Stations (RfL) | Cxxx-NCR-000844 | NCR | Fisher, Limmo, Eleanor & Stepney RAM Specification and Demonstration Case |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2020-04-23 | 2020-04-22 08:24 | -1 | 2020-04-16 07:28 | Shafts - Shafts General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Further to NCR ref Cxxx-NCR-000843 raised at Mile End the full process of the RAM Specification and Demonstration Reports has not been followed fully during installation/T&C for Fisher Street, Eleanor Street, Limmo Peninsula and Stepney Green. The RAM data from the suppliers of components was not made available to , a majority of products used at these shafts was accepted firstly at Mile End and then extended to cover all other Cxxx shafts.
| 03SR - Stations (RfL) | Cxxx-NCR-000845 | NCR | Limmo - Level 6 Pump Removal Room - HT3 non compliant ladder rung spacing |  | Contr | SKC |  |  | 2020-07-22 | 2020-07-22 10:35 | 0 | 2020-03-10 08:52 | Architectural - Handrail | 3000 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | HT3 in the Pump Removal Room 6/780 was modified as per Cxxx-FCD-001605. As a result of this modification a section of the ladder has rungs spaced at 360mm apart from one another. BS 4211:2008 Section 5.4.2 specifies that ladder rungs "shall be uniformly spaced throughout at centres between 225 mm and 300mm".
| 03SR - Stations (RfL) | Cxxx-NCR-000846 | NCR | Stepney Green Shaft - Slip Testing Stairs - Durbar Plate |  | Contr | SKC |  |  | 2020-04-24 | 2020-05-27 12:00 | 33 | 2020-03-13 11:14 | Architectural - Finishes | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Independent slip testing was undertaken in the Stepney Green Shaft by RSK on 07/02/2020. The results have been documented in Cxxx-SKC-C-RGN-CR094_WS108-50035. High slip resistance was achieved in all but the following locations, on Durbar plate: Moderate slip resistance (PTV 33) was identified in one location using the Slider 96 test (B0 Intervention stair landing) Moderate slip resistance (PTV32 & 33) was identified in two locations using the Slider 55 test (B2 & B3 Intervention stair landings) Low slip resistance (PTV 24) was identified in one location using the Slider 55 test (B4 TVA Stair - Note test was only able to be tested in two directions on the top stair tread) A similar issue has been raised previously in: Cxxx-NCR-000659 (Stepney Green Shaft)
| 03SR - Stations (RfL) | Cxxx-NCR-000847 | NCR | LPS - Fire Main PAC Pneumatic Testing |  | Contr | SKC |  |  | 2020-05-05 | 2020-04-30 10:24 | -5 | 2020-03-19 10:45 | Fire - Suppression | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Subcontractor unable to produce calibration record for a 4 Bar Pressure Gauge used for Testing and Commissioning as a part as a part of the PAC deliverables for Fire Main (Cxxx-SKC-O4-LRC-CR144_WS155-50018.) The test involves a pneumatic pressurization of the Fire Main to 0.5 Bar, to prove that the system has no open ends before it is charged with water for a 2 hour 19 Bar hydrostatic test.
| 03SR - Stations (RfL) | Cxxx-NCR-000848 | NCR | Eleanor Street Shaft - Fire Alarm System - Lift Shaft Aspirating Unit does not have 72 hours battery backup |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2020-07-27 | 2020-06-23 07:57 | -34 | 2020-03-22 18:51 | Fire - Detection | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The Lift Shaft Aspirator batteries do not provide 72 hour battery backup as per the Eleanor Street - Electrical Services Specification Cxxx-SKC-E-RSP-CR094_WS110-50001 JW50.1308 Air Sampling Systems. Note: Pressurisation Air Intake Aspirator does not have the 72 hour battery backup requirement. A/782 Fan Room Aspirator batteries provide 72 hours of backup.
| 03SR - Stations (RfL) | Cxxx-NCR-000849 | NCR | ESS - Duraslab repair |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2020-10-30 | 2020-10-08 17:33 | -22 | 2020-05-06 14:42 | Civil - Civil Engineering General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Insufficient quantity of material to do the job | Completed |  | - Duraslab panels installed on site, have had surface damage and supplier advised replacement is required. - Type 75 duraslab panels (as per Cxxx-SKC-C-LRC-CR094-50337) are not presently available and supplier suggested that the best alternative are the Type 50.
| 03SR - Stations (RfL) | Cxxx-NCR-000850 | NCR | Incorrect Refrences in Section 4B of UPS PAC Fisher Street |  | Contr | SKC |  |  | 2020-06-09 | 2020-05-26 10:36 | -14 | 2020-05-26 07:52 | Electrical - Lighting | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The Fisher Street UPS PAC (Cxxx-SKC-E-CER-CR086_WS095-50012) incorrectly references an Eleanor Street IRN in section 4B of the package listing. This has been picked up after the PAC was accepted, during review of the Acceptance Certificate. In order to address this the Contractor proposes to live-update the PAC to address the errors, rather than issuing a new revision. The live update will save time in document control in what is a crucial time for AC acceptance, just prior to handover. This will also save having to update the UPS AC package listing which is currently under CEG and RfL review.
| 03SR - Stations (RfL) | Cxxx-NCR-000851 | NCR | Sleeves omitted on fire main where passing between shaft and trace |  | Contr | SKC |  |  | 2020-06-18 | 2020-06-09 09:50 | -9 | 2020-06-04 16:18 | Mechanical - Piping | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | With respect to four builders works opening where the fire main leaves Limmo shaft and enters the Eastbound and Westbound tunnels, the Contractor notes that Cxxx-SKC-O9-RSP-CR144_WS155-50001 Clause JS61.3301 n) States Pipe sleeves through fire barriers shall be provided. The Contractor notes that when installing the fire main in tandem with Cxxx, at the interface point (which is immediately to the trackside of the shaft wall) it was found that the alignment of the fire main in the tunnel and it’s connection to the GRE Ts which make the connection to the pipework within the shaft, meant that installing sleeves around the pipework compliantly was not possible. Refer to photo “Lim fire main tunnel side”. This shows that if a sleeve were installed, it would clash with the exposed threads of the bolts used to connect the flanges and would make replacement of pipework without damaging the firestopping seal impossible. As such, a sleeve has not been installed. Refer to photo “Lim fire main shaft side” which shows that the opening has been filled with hard firestopping compound, a surround of __ RWA45, faced with intumescent mastic. These seals are represented in Cxxx-SKC-E1-LRG-CR144_WS155-50003, __ Limmo Fire Protection Register as Nr0151, Nr0929, Nr0930 and Nr0931 and certified as noted by Cxxx-SKC-O4-CER-CR144_WS155-50003 “Limmo Peninsula Shaft - FIRAS Certificate of Conformity - __”. Also the risk of pipe movement damaging the fire stopping is considered to be very low because the pipes are fixed at the shaft/tunnel interface.
| 03SR - Stations (RfL) | Cxxx-NCR-000852 | NCR | Mile End Missing Fire Door Selector |  | Crossrail | XRL |  |  | 2020-09-15 | 2020-09-04 09:34 | -11 | 2020-06-05 17:30 | Architectural - Doors | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | During the Dilapidation Survey at Mile End (March 2020), it was noted that the double internal fire doors on the ground floor (Doors D00-18) do not have a door selector. were requested to raise this NCR in March.
| 03SR - Stations (RfL) | Cxxx-NCR-000853 | NCR | Limmo - Miscellaneous Metalwork |  | Contr | SKC |  |  | 2020-08-07 | 2020-08-06 07:45 | -1 | 2020-06-20 09:42 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | - UB 152*89*16, Steel Section Lintels to act as __ support Metalwork at SR LV1 and SR LV2, have been replaced with RHS 90*50*5, due to restriction to the door opening height for DB.23 and DB.25. Replacement has been done without previous approval by CRL. - Miscellaneous metalwork (Plenum Primary Steelwork - Walkable Gutter - Balustrade - Ladder, Louvre & Brickwork Support, PR Riser Grills, Lintels on Level 2) installation without previous approval of pre-construction records.
| 03SR - Stations (RfL) | Cxxx-NCR-000855 | NCR | Limmo Peninsula Shaft - Miscellaneous metalwork |  | Contr | SKC |  |  | 2020-07-15 | 2020-07-17 14:10 | 2 | 2020-07-01 15:31 | Architectural - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Cxxx-SKC-C-CER-CR144_WS155-5003 - Miscellaneous metalwork package has been submitted with associated ITP Deliverable handover records issued not having the formal Crossrail acceptance of fabrication and installation of a number of metalwork components. Inspection and Test Plan Cxxx-SKC-C-ITP-CR144_WS155-50020, Fabrication of Miscellaneous Metalwork, and Cxxx-SKC-C-ITP-CR144_WS155-50010, Installation of Miscellaneous Metalwork refers. Additionally, ITP Deliverables Handover record have missing and incorrect checksheet templates, which differ from the approved ITP checksheets. This includes the following installations: - Plenum Roof – Walkable Gutter, Louvre Support, Steel Framing and Brickwork Steel - Plenum Roof - Mechanical Riser Grills - Pressurized Riser Grills - Service Void Kickrail and handrail - __ wall support (Above door) - Steel Lintels Notwithstanding the above, these works have been installed in strict accordance with the specifications, drawings and relevant British Standards. The circumstantial evidence of the IRF’s listed below, indicate our purpose to invite Crossrail to witness and inspect the works, as have been recorded on our programme tracker. This procedural ‘Non Conformance’ Report addresses that Crossrail had not been afforded the opportunity to accept the fabrication and installation of the aforementioned. Consequently, the following IRFs have not been duly signed by a Crossrail PFE. • -Cxxx-IRF-928 – External Grillage, Cable trench covers, Grills and wall hatches 16/09/2017 • -Cxxx-IRF-976 – Installation to steel angles (External) 07/12/17 • -Cxxx-IRF-1041 – Pull out test to façade support angles 16/05/18 • -Cxxx-IRF-1050 – Louvre Support steel and walkable gutter steel 22/05/18 • -Cxxx-IRF-1164 – Inspection of complete __ wall (B1.33) and Ceilings (B6) 24/01/2019 • -Cxxx-IRF-1257- Inspection of Trench covers, hatches, void stiffeners, access panels, transformer room grillage and steel lintels 18/07/19 confirms that the works meet the required specification and have been installed as per the approved drawings, and has retrospectively signed the ITP Deliverable records in lieu of the recovery of the original documentation.
| 03SR - Stations (RfL) | Cxxx-NCR-000856 | NCR | Fireboarding Beam in Level 6 FF Lobby |  | Contr | SKC |  |  | 2020-07-17 | 2020-07-15 13:14 | -2 | 2020-07-01 17:12 | Fire - Compartmentation | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The firestopping subcontractor has installed __ L500 board around the beam using steel angles as per __ requirements. Cxxx-FCD-001502 mentions the use of stainless steel angles. The installation has been completed as per the documents referenced within the FCD and the use of galvanised steel angles.
| 03SR - Stations (RfL) | Cxxx-NCR-000857 | NCR | Stepney Green Shaft - Gas Suppression Multimeter calibration certificate |  | Contr | SKC |  |  | 2020-07-20 | 2020-07-29 13:11 | 9 | 2020-07-06 11:41 | Fire - Suppression | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | The calibration certificate for the Multimeter was not in date at time of completing the Loop Checks on the Gaseous Fire Suppression System at Stepney Green.
| 03SR - Stations (RfL) | Cxxx-NCR-000858 | NCR | Cxxx - NCR - Limmo LUX Levels in the plenum |  | Contr | SKC |  |  | 2020-07-22 | 2020-09-08 15:22 | 48 | 2020-07-08 08:03 | Electrical - Lighting | 500 |  | Testing and Commissioning | Repair | 4 (0.5-3k) | Complete | Verification Problems - Inspection points not adequate | Completed |  | Following LUX Level testing in the plenum area level A of Limmo, the average LUX levels for the area is 135 LUX. This is below the 150 LUX threshhold required for the area. Proposed that additional luminaires are installed in the area to increase the average LUX to over 150 LUX. Note the non-compliance is with LU 1-066 A3 spec for Plant Rooms.
| 03SR - Stations (RfL) | Cxxx-NCR-000859 | NCR | Limmo Peninsula Shaft - Hammer Test |  | Contr | SKC |  |  | 2020-09-01 | 2020-08-27 14:48 | -5 | 2020-07-17 04:51 | Architectural - Flooring | 3000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | An Insitu Crushing Resistance Soundness test was not carried out on the screed floor at Limmo Peninsula Shaft prior to the floor finish being applied, as per Architectural Specification; see below. This is also noted in section 3.2.6 of the Internal Floor Finishes ITP - Cxxx-SKC-C-ITP-CR144_WS155-50008, for a __ Drop Hammer test for compressive strength of screed 35N/mm2 Soundness Test Tolerance with a maximum penetration depth of 3mm. (LIM Floor Finishes package - Cxxx-SKC-A-CER-CR144_WS155-50008 refers)
| 03SR - Stations (RfL) | Cxxx-NCR-000863 | NCR | Live updating Page2 of ITP deliverables for Lighting PAC Cxxx-SKC-O4-LRC-CR094_WS110-50060 |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2020-08-12 | 2020-08-14 16:58 | 2 | 2020-07-29 12:27 | Electrical - Lighting | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | At the time of the ITP deliverable submission for Lighting and Lighting Control PAC Cxxx-SKC-O4-LRC-CR094_WS110-50060, there was a tying error on page 2 related to the LU standard Specification used at Eleanor Street. LU 1066 A5 was mentiond on the document instead of LU 1066 A3 standard that has been followed across Cxxx shafts. Page no 2 of the ITP has been live swapped to reflect the correct LU standard and updated on EB.
| 03SR - Stations (RfL) | Cxxx-NCR-000864 | NCR | UPS ITP Deliverables Cxxx-SKC-O4-LRC-CR094_WS110-50083 - amendment |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2020-08-28 | 2020-08-18 16:20 | -10 | 2020-07-29 12:58 | Electrical - Lighting | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | It has been identified that the __ Commissioning Report contains conflicting information in relation to UPS Comms and EML Battery Capacity Ah and revised document has been requested from __ to be provided.
| 03SR - Stations (RfL) | Cxxx-NCR-000865 | NCR | Damaged Vedafeu in Intervention and Escape Staircases |  | Contr | SKC |  |  | 2020-10-05 | 2020-10-07 09:02 | 2 | 2020-08-25 15:38 | Fire - Compartmentation | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Within the intervention and escape staircases, Vedafeu-C (Cxxx-SKC-C-LRC-CR094_WS108-50007) rope system has been installed to firestop gaps between RC joints. Over time the rope system has been 'picked' at and become damaged. The manufacturer was contacted and asked to review the state of a number of joints, it was suggested that they be replaced to ensure the integrity of the product. To reduce the risk of the product becoming damaged over time, an approved mastic (Cxxx-SKC-C-LRC-CR094-50300) will be applied on top for aesthetic purposes. The mastic will not impact on the performance of the rope system as per attached 'RE Vedafeu Rope repairs'.
| 03SR - Stations (RfL) | Cxxx-NCR-000866 | NCR | All shafts - Lighting - Single Points of Failure |  | Crossrail | XRL |  |  | 2021-01-28 | 2021-01-27 09:41 | -1 | 2020-09-02 07:50 | Electrical - Lighting | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In July 2020 the Project Manager was made aware of an potential issue with lighting circuitry throughout the shafts. In some cases whole areas within each shaft had been connected in such a way that should the single lighting circuit fail for any reason then this would result in those areas having no lighting available whatsoever. Since July these potential ‘single points of failure’ have been the subject of lengthy discussions with the Contractor. This NCR records why the Project Manager and the Employer’s technical directorate regard this as a non-conformance to the Works Information. This NCR covers Mile End, Eleanor Street, Fisher Street, Limmo Peninsula and Stepney Green shafts.
| 03SR - Stations (RfL) | Cxxx-NCR-000867 | NCR | Eleanor Street shaft - Lighting Column maintenance |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2020-02-26 | 2021-02-26 08:47 | 366 | 2020-11-19 12:51 | Electrical - Lighting | 10000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Procedure Problem - Other | Completed |  | Installation of 3 No. Abacus light duty, base hinged lighting columns at Eleanor Street shaft is such that lowering the columns for maintenance purposes does not enable the manufacturer's recommended use of the proprietary Spring Counterbalance apparatus ( model - RLS168) for this operation.
| 03SR - Stations (RfL) | Cxxx-NCR-000868 | NCR | Sitewide - Door replacements at ELS, FIS, LIM & STG |  | Contr | SKC |  |  | 2021-04-30 | 2021-04-27 09:47 | -3 | 2020-12-24 08:28 | Architectural - Doors | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | The Contractor is to anticipate possible sources of damage to works and take active measures to mitigate against such damage arising from warping, distortion and other conditions which could have adverse effects on materials, as per Architectural specification; clause JA.6300. Whilst every effort has been expended to protect and maintain the doors in "pristine condition until full practical completion", following routine, critical and statutory maintenance inspections, the following doors have been identified as being damaged beyond repair and require replacement. Note, instructed door replacements due to Maglock ironmongery changes. i.e. Limmo: DB6.01 and Stepney Green: DB4.02 and DB5.03. Eleanor Street: D01.01 (COMPLETE PWK-01202 refers) D01.11 (COMPLETE PWK-01202 refers) D00.08 (COMPLETE PWK-01202 refers) D00.12 (COMPLETE PWK-01202 refers) D00.19 (COMPLETE PWK-01202 refers) DB4.06 (COMPLETE PWK-01202 refers) Fisher Street: D00.07 (COMPLETE PWK-01237 refers) DB1.04 (COMPLETE PWK-01237 refers) DB1.05 (COMPLETE PWK-01237 refers) DB1.08 DB3.06 (COMPLETE PWK-01237 refers) Limmo Peninsula: D00.13 (COMPLETE PWK-01230 refers) DB1.01 (COMPLETE PWK-01230 refers) DB6.01 (Covered under Cxxx-PWK-01222 refers) DB6.15 (COMPLETED see attached) Stepney Green: D00.02 (COMPLETE PWK-01235 refers) D00.07 (COMPLETE PWK-01235 refers) D00.11 (Covered under Cxxx-PWK-01244) D00.19 (COMPLETE PWK-01235 refers) DB1.02 (Covered under Cxxx-PWK-01263) DB2.02 (COMPLETE PWK-01235 refers) DB2.04 (COMPLETE PWK-01235 refers) DB2.06 (COMPLETE PWK-01235 refers) DB2.19 (COMPLETE PWK-01235 refers) DB3.02 (COMPLETE PWK-01235 refers) DB3.04 (COMPLETE PWK-01235 refers) DB3.18 (COMPLETE PWK-01235 refers) DB3.19 (COMPLETE PWK-01235 refers) DB4.02 (COMPLETE PWK-01235 refers) DB5.01 (COMPLETE PWK-01235 refers) DB5.03 (COMPLETE PWK-01235 refers) DB5.09 (COMPLETE PWK-01235 refers) DB5.17 (COMPLETE PWK-01235 refers) DB5.20 (COMPLETE PWK-01235 refers)
| 03SR - Stations (RfL) | Cxxx-NCR-000869 | NCR | MES - Fan Acoustic Jackets installed without Approved MCR |  | Contr | SKC |  |  | 2021-06-30 | 2021-05-05 10:12 | -56 | 2021-01-15 16:00 | Mechanical - Heating Ventilation & Air Conditioning | 5000 |  | Documentation and Records | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Following D25 testing at Mile End, it was identified when in operation the general extract fans exceeded allowable noise limits and required sound attenuation (refer to Cxxx-SKC-T1-RGN-CR094_WS109-50106). A specialist subcontractor was engaged for acoustic fan jackets. These were then installed on the following fans at Mile End prior to the acceptance of the MCR: • General Extract Fan - EF01A • General Extract Fan - EF01B The MCR (CRL-MCR-005292) has subsequently been rejected by CRL/CEG as the product does not meet CRL/CEG's fire specifications. Note this issue has been identified elsewhere on Crossrail (Cxxx Farringdon).
| 03SR - Stations (RfL) | Cxxx-NCR-000870 | NCR | __ - Fan Acoustic Jackets installed without Approved MCR |  | Contr | SKC |  |  | 2021-06-30 | 2021-05-14 06:46 | -47 | 2021-01-15 15:27 | Mechanical - Heating Ventilation & Air Conditioning | 5000 |  | Documentation and Records | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Following D25 testing at Stepney Green, it was identified when in operation the pressurisation fans exceeded allowable noise limits and required sound attenuation (refer to Cxxx-SKC-T1-RGN-CR094_WS108-50008). A specialist subcontractor was engaged for acoustic fan jackets. These were then installed on the following fans at Stepney Green prior to the acceptance of the MCR: • Pressurisation Fan - PSF-01A • Pressurisation Fan - PSF-01B The MCR (CRL-MCR-005292) has subsequently been rejected by CRL/CEG as the product does not meet CRL/CEG's fire specifications. Note this issue has been identified elsewhere on Crossrail (Cxxx Farringdon).
| 03SR - Stations (RfL) | Cxxx-NCR-000871 | NCR | All shafts - Aspirating Smoke Detection - Nuisance Faults |  | Crossrail | XRL |  |  | 2021-06-18 | 2021-06-25 08:34 | 7 | 2021-03-03 13:58 | Fire - Detection | 500 |  | System Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | **THIS NCR RELATES TO ALL SHAFTS** As discussed in depth at daily I__ ‘Viz’ meetings in recent weeks it has become apparent that the Xtralis ICAM IAS-1 & IAS-2 aspirating smoke detectors (ASDs) installed to monitor for smoke in the lift shafts are generating nuisance fault signals. Upon investigation by the RfL maintenance team it appears that the Xtralis ICAM units are sensing the increased airflow whenever the shaft pressurisation fans are in use and raising this as a fault at the fire alarm panels, which in turn report to the RCC. During RfL’s occupancy of the shafts this issue has lead to numerous engineer call outs to identify the sources of the faults. See also the following communications: CRL-OBS-35081 Mile End CRL-OBS-35082 Fisher Street CRL-OBS-35083 Eleanor Street CRL-OBS-35084 LIMMO CRL-OBS-35085 Stepney Green Cxxx-PMI-01877 ******UPDATE 01/04/2021 N Lyons****** A bit more narrative to the issue is included below. have been sent very similar wording by email already but it needs to be recorded here. Background · The complete fire alarm and pressurisation systems were designed by Cxxx. Requirements such as pressure differentials and flow rates were known about from the beginning of the detailed design stages for each shaft. · To Crossrail’s knowledge there are no new and unavoidable external factors (e.g. train movements, TVS) at work that would cause the aspirating smoke detection systems to generate air flow faults. · The ICAM units are generating intermittent ‘high flow’ faults during normal operation and testing of the fire alarm and pressurisation systems. We’ve seen no evidence that the recent faults experienced by RfL are the result of unusual environmental conditions caused by operating the systems outside of their usual parameters. · After trying many adjustments to the systems over many months, during both ’s and RfL’s time as custodians of the shafts, it has become apparent that the ICAM units cannot be adjusted to give fault free running.
| 03SR - Stations (RfL) | Cxxx-NCR-000872 | NCR | Door Replacements |  | Contr | SKC |  |  | 2021-07-07 | 2021-07-06 09:37 | -1 | 2021-03-02 16:07 | Architectural - Doors | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | At the behest of the Client, the Contractort has carried out an intrusive survey of the doors at Mile End Shaft post RfLI handover/ takeover. The following doors have been identified with damages beyond repair. Replacement will be done under warranty. D00.01 D00.08 DB1.01 DB3.01 DB4.01 DB6.01
| 03SR - Stations (RfL) | Cxxx-NCR-000873 | NCR | G4 Barrel Bolt dust excluding socket omission |  | Contr | SKC |  |  | 2021-03-23 | 2021-03-23 14:47 | 0 | 2021-03-03 00:37 | Architectural - Doors | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | As per Ironmongery schedule, Cxxx-SKC-A-TSC-CR094_WS109-50002, the following 12No. doors have been designed to include a G4 barrel bolt dust excluding socket. D00.07 - FD120S door with threshold D00.10 - FD90S door with threshold D00.15 - FD120S door with threshold D00.16 - FD90S door with threshold D00.17 - FD90S door with threshold D00.19 - FD120S door with threshold D00.20 - FD120S door with threshold D00.23 - FD120S door with threshold D00.24 - FD90S door with threshold D00.27 - Louvre door includes proprietary Surelock McGill Slimline SL313 three point auto bolting dead-locking system; no floor sockets required D00.28 - Louvre door includes proprietary Surelock McGill Slimline SL313 three point auto bolting dead-locking system; no floor sockets required DB9.03 - FD120S door with threshold The manufacturer has advised that fitting the floor sockets where there is a threshold requirement would compromise the performance of the door, i.e Fire, Acoustic and Thermal properties. See attached email correspondence from __ __. In accordance with the Architectural specification, Cxxx-SKC-A-RSP-CR094_WS109-50001, clause JL20.1204 (b) - The doorset manufacturer shall ensure that the ironmongery does not compromise the certification of the works. Therefore, the dust excluding sockets have not been fitted and in there stead thresholds have been drilled through to receive the barrel bolt at required depth. However, the Contractor has not effectively communicated or adhered to design change management protocols as per agreed assurance processes, and raise this procedural NCR to note.
| 03SR - Stations (RfL) | Cxxx-NCR-000875 | NCR | VE3 Channels - incorrect falls |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2021-06-14 | 2021-07-08 15:58 | 24 | 2021-05-13 16:26 | Civil - Drainage | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A survey of the invert of the drainage channels in VE3 has shown that these do not fall consistently toward the outlet. See "ELS Drainage Survey and mark ups.pdf".
| 03SR - Stations (RfL) | Cxxx-NCR-000876 | NCR | VE3 recessed drainage channels |  | Contr | SKC | ELS - Eleanor Street Shaft (Central) |  | 2021-07-02 | 2021-07-08 15:59 | 6 | 2021-05-13 16:46 | Civil - Drainage | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | WRT the recessed drainage channels in the lower area of VE3, survey by engineer on 12/02/21 has shown that where concrete has been broken back, and a screed has been installed to create a finished surface, this screed is debonding from the substrate.
| 03SR - Stations (RfL) | Cxxx-NCR-000877 | NCR | Fisher Street - Access to Fire Main Header Tanks for Maintenance |  | Crossrail | XRL |  |  | 2023-03-31 |  | -53 | 2022-11-02 13:47 | Civil - Civil Engineering General | 500 |  | Design |  |  | Open |  | PROPOSE ACTION |  | As communicated to the Project Manager under CRL-NDF-00300, the Infrastructure Maintainer for these assets (RfL) identified that there are inadequate access arrangements to inspect and maintain the 2no. fire main header tanks in FIS Welfare room 1/350. A joint site inspection with RfL and CRL was carried out on 03/08/2022 and it was confirmed on that visit that corrective work is required to improve this situation. There are some photos attached from the visit. The specific concern is around safe access for routine maintenance and inspection given the size of the room, the drip tray footprint and various pipes and support structures meaning that MEWP access is impossible, and makes access to the top of the tanks difficult even from a ladder. Having looked through the A&M strategy and the relevant O&M manual this particular access issue does not appear to be discussed. As there seem to be some relatively simple alterations/additions that could be made to provide safer access this NCR is raised to track and agree a solution. To date the Contractor has invited their steelwork fabricator to site with a view to working up a simple proposal to improve access. Initial suggestions involve the installation of some relatively simple mesh walkway gratings, handrails as required, and possibly a retractable ladder. Note that Cxxx-SND-00001 has also been raised alongside this NCR. References: *Cxxx-SKC-K2-RGN-CR086_WS095-50001 7.0 Fisher Street Shaft - Maintenance and Access Strategy Report *Cxxx-SKC-K2-OMT06-CR086_SH003-50005 3.0 Operations and Maintenance Manual T5 - PFU/FU/Asset Maintenance Fire Suppression and Compartmentation System & Equipment Cabinets at Fisher Street Shaft - and associated 'T' documents.
| 03SR - Stations (RfL) | Cxxx-NCR-000076 | NCR | No access to PO/NR Conveyor tunnel under Paddington |  | Contr |  | PAD - Paddington Station (West) |  | 2012-04-25 | 2012-09-06 17:13 | 134 | 2012-04-11 | Surveying - Instrumentation and Monitoring | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | No access to PO/NR Conveyor tunnel under Paddington due to blockwork wall constructed at property boundary of PO building (see photo attached) and retail unit food chiller placed over access point at NR end in Lawn.
| 03SR - Stations (RfL) | Cxxx-NCR-000097 | NCR | Sussex Gardens Deep Datum |  | Contr |  | PAD - Paddington Station (West) |  | 2012-05-07 | 2012-06-01 08:56 | 25 | 2012-04-24 | Surveying - Instrumentation and Monitoring | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | The Sussex Gardens deep datum is not 50m from the TBM drive (an area of development), it is less than 15m from the drive as seen in attached image.
| 03SR - Stations (RfL) | Cxxx-NCR-000108 | NCR | Vibrating Wire Piezometers |  | Contr |  | PAD - Paddington Station (West) |  | 2012-05-04 | 2012-06-12 16:32 | 39 | 2012-04-26 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | Piezometers have been installed three in each borehole
| 03SR - Stations (RfL) | Cxxx-NCR-000119 | NCR | Incorrect positioning of bar mk 01 in slab locations |  | Contr |  | PAD - Paddington Station (West) |  | 2012-05-11 | 2012-05-23 11:10 | 12 | 2012-05-08 | Structural Engineering - Diaphragm Walls | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | bar mk 01 omitted or misplaced in various locations
| 03SR - Stations (RfL) | Cxxx-NCR-000125 | NCR | ATS accuracy 1" theodolites used |  | Contr |  | PAD - Paddington Station (West) |  | 2012-05-28 | 2012-06-07 08:48 | 10 | 2012-05-14 | Surveying - Instrumentation and Monitoring | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | have used __ TM30 1" and TCRA1201 for ATS. These are 1" of arc theodolites.
| 03SR - Stations (RfL) | Cxxx-NCR-000135 | NCR | Non-Compliance with ITP |  | Contr |  | PAD - Paddington Station (West) |  | 2012-05-23 | 2012-07-16 17:29 | 54 | 2012-05-16 | Structural Engineering - Diaphragm Walls | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Checks were not carried out by __ or on the cage prior to transporting to site
| 03SR - Stations (RfL) | Cxxx-NCR-000136 | NCR | Non- Compliance with ITP |  | Contr |  | PAD - Paddington Station (West) |  | 2012-05-23 | 2012-07-16 17:26 | 54 | 2012-05-16 | Structural Engineering - Diaphragm Walls | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Inspections and tests are not being undertaken prior to the cage being transported to site
| 03SR - Stations (RfL) | Cxxx-NCR-000141 | NCR | ATS Reference prisms |  | Contr |  | PAD - Paddington Station (West) |  | 2012-06-06 | 2012-08-20 19:30 | 75 | 2012-05-23 | Surveying - Instrumentation and Monitoring | 500 |  | System Defect | Rework |  | Complete |  | Completed |  | Due to the ATS being installed in NR tunnels there is no way to obtain reference to external prisms outside of the zone of influence of the main works.
| 03SR - Stations (RfL) | Cxxx-NCR-000149 | NCR | Insufficient readings from inclinometer A7 prior to Dwall Construction |  | Contr |  | PAD - Paddington Station (West) |  | 2012-06-08 | 2012-07-25 12:27 | 47 | 2012-05-24 | Civil - Geotechnical Engineering | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | inclinometer was installed the day before excavation commenced on the adjacent panel
| 03SR - Stations (RfL) | Cxxx-NCR-000152 | NCR | Panel S1: Reinforcement |  | Contr |  | PAD - Paddington Station (West) |  | 2012-07-10 | 2012-07-11 10:35 | 1 | 2012-06-01 | Structural Engineering - Diaphragm Walls | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | Constructability problems encountered during splicing operation to manually position and fix L-bar with couplers resulted in: 6no. Bars placed out of orientation, 2no Bars were cut and rejoined during splicing due to clashes with lifting band, 5no. couplers cut 500mm from bars to enable placement. Please refer to attached sketch. A high volume of steel in this localised area has lead to congestion and difficulty placing the loose L-bar couplers in the splice zone between the middle and top cages of S01 (South Wall).
| 03SR - Stations (RfL) | Cxxx-NCR-000153 | NCR | Panel S1: Top Link |  | Contr |  | PAD - Paddington Station (West) |  | 2012-07-10 | 2012-07-11 10:37 | 1 | 2012-06-01 | Structural Engineering - Diaphragm Walls | 500 |  | Workmanship | Reject |  | Complete |  | Completed |  | Head wall cage: The top link nearest the top lifting band was cut at four locations to enable access for trapping beams. Please refer to attached sketch. Top link was locally high in this area positioning it too close to the top lifting band, hence leaving insufficient space below the lifting band for correct positioning of the trapping beam.
| 03SR - Stations (RfL) | Cxxx-NCR-000154 | NCR | Panel S1: Sonic Tubes |  | Contr |  | PAD - Paddington Station (West) |  | 2012-06-15 | 2012-07-02 16:59 | 17 | 2012-06-01 | Structural Engineering - Diaphragm Walls | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | 2no. Sonic logging tubes incorrectly positioned on head wall cage. Please refer to attached sketch. The 2no. Sonic logging reservation tubes were initially omitted in error. Prior to cage placement the sonic logging reservation tubes were manually tied in to the panel cage.
| 03SR - Stations (RfL) | Cxxx-NCR-000155 | NCR | Panel W1: Reiforcement Tolerance |  | Contr |  | PAD - Paddington Station (West) |  | 2012-06-15 | 2012-07-02 17:03 | 17 | 2012-06-01 | Structural Engineering - Diaphragm Walls | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The main bars consisting of Bar Marks 12, 18, 16 and 11 were out of positional tolerance by up to 30mm (80mm from theoretical minus 50mm vertical position tolerance = 30mm). This is detailed in the cage dimension check sheet as part of the panel record. The effect was minimised by setting the cage at 20mm higher than the theoretical but still ensuring all other components were within the +/-50mm vertical tolerance.
| 03SR - Stations (RfL) | Cxxx-NCR-000156 | NCR | Panel W1: Deformed Links |  | Contr |  | PAD - Paddington Station (West) |  | 2012-07-10 | 2012-07-24 15:27 | 14 | 2012-06-01 | Structural Engineering - Diaphragm Walls | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Fibre strops attached to the reinforcement cage for pre-slinging purposes, were only choked around the shear link at the base of the cage, not around the main bar. This lead to deformation of the shear link when the cage was lifted. The deformed sections were cut out and replaced with a minimum of 300mm lap length onto the existing shear components as per the attached sketch.
| 03SR - Stations (RfL) | Cxxx-NCR-000157 | NCR | ITP-Fabrication Yard Test and Inspections |  | Contr |  | PAD - Paddington Station (West) |  | 2012-06-15 | 2012-07-02 13:48 | 17 | 2012-06-01 | Structural Engineering - Diaphragm Walls | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Inspections and tests were not undertaken prior to the cage being transported to site.
| 03SR - Stations (RfL) | Cxxx-NCR-000158 | NCR | BS 4449 Traceability |  | Contr |  | PAD - Paddington Station (West) |  | 2012-06-22 | 2012-10-31 17:09 | 131 | 2012-06-08 | Structural Engineering - Diaphragm Walls | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Records were not available to demonstrate that reinforcement steel materials were in accordance with the contract Part 2 of volume 2C of the works information as specified by KP10.3200 and SPERW clause B19.
| 03SR - Stations (RfL) | Cxxx-NCR-000160 | NCR | Clash in Borehole C7 |  | Contr |  | PAD - Paddington Station (West) |  | 2012-06-15 | 2012-07-25 15:34 | 40 | 2012-06-12 | Geotechnical Engineering - Geotechnical Engineering - General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Borehole Cxxx-lG-PE-07 converged with borehole Cxxx-lG-PE-01 during installation
| 03SR - Stations (RfL) | Cxxx-NCR-000161 | NCR | Non-Compliance with Temporary Works Design |  | Contr |  | PAD - Paddington Station (West) |  | 2012-06-26 | 2012-07-30 09:42 | 34 | 2012-06-12 | Structural Engineering - Diaphragm Walls | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Only 3Nr. hanging beams were used instead of the designed soultion of 4Nr. beams. The hanging steel bars are also used in the temporary works solution to retain the services corridor. The support of the diaphragm wall cages forms a designed solution and should not be changed unless a formal change control is implemented
| 03SR - Stations (RfL) | Cxxx-NCR-000168 | NCR | Panel W1 Toe Level |  | Contr |  | PAD - Paddington Station (West) |  | 2012-06-29 | 2012-07-06 09:35 | 7 | 2012-06-15 | Structural Engineering - Diaphragm Walls | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Panel W1 was escavated to the lowest toe level of 110.66, thus protruding into the soft tunnel eye section. The toe level was, for the permanent panel, brought up above the tunnel crown by packing up using a sand bag system.
| 03SR - Stations (RfL) | Cxxx-NCR-000171 | NCR | Incorrect Coupler used panel S1 |  | Contr |  | PAD - Paddington Station (West) |  | 2012-06-26 | 2012-07-30 11:48 | 34 | 2012-06-19 | Structural Engineering - Diaphragm Walls | 500 |  | Material | Rework |  | Complete |  | Completed |  | The couplers fitted at the fabrication yard were not transitional and non-positional transitional couplers that were available on site were used.
| 03SR - Stations (RfL) | Cxxx-NCR-000178 | NCR | Systems for sampling & testing Concrete |  | Contr |  | PAD - Paddington Station (West) |  | 2012-07-11 | 2012-07-24 15:25 | 13 | 2012-06-27 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | The stage that requires re-mixing of the fresh concrete sample using the remixing container and the square mouthed shovel before carrying out the flow table test on fresh concrete was omitted. CRL surveillance visit corrected this omission however concrete sampled & tested with this omission ( 2 loads) had been placed. The Contractor's system to demonstrate that no further omissions take place no available
| 03SR - Stations (RfL) | Cxxx-NCR-000189 | NCR | 3no Couplers Omitted - Panel W2 |  | Contr |  | PAD - Paddington Station (West) |  | 2012-07-16 | 2012-07-16 17:00 | 0 | 2012-07-02 | Structural Engineering - Diaphragm Walls | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | 3no loose 'L' couplers were omitted from the W2 reinforcement cage, as highlighted in the attached photograph and two sketches.
| 03SR - Stations (RfL) | Cxxx-NCR-000201 | NCR | S07: Break In Monolithic Concrete Pour |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-12-01 | 2014-08-29 10:49 | -94 | 2012-07-10 | Structural Engineering - Diaphragm Walls | 500 |  | Equipment Breakdown | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | During the concrete pour of panel S07 several brick size blocks of cured concrete were discharged from the back of the concrete wagon and into the tremie pipe. These proceeded to block the pipe and prevent the continuation of the pour. Unsuccessful efforts were made to unblock the pipe. However, as the tremie could not be unblocked in-situ, it had to be removed, hence breaking the monolithic nature of the concrete pour. The lumps of concrete were removed and the tremie unblocked. The tremie was then reassembled, sealed over the leading end and reinserted into the concrete before recommencement of the pour. This occurred at a depth of 21.8m from guidewall or 105.3mAOD
| 03SR - Stations (RfL) | Cxxx-NCR-000205 | NCR | Vibrating wire strain gauges- commisioning readings |  | Contr |  | PAD - Paddington Station (West) |  | 2012-08-17 | 2012-07-27 09:54 | -21 | 2012-07-12 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Planning | Rework |  | Complete |  | Completed |  | No readings were taken from strain gauges installed within panel S12 before the reinforcement cage was lowered into the panel shaft and prior to concreting.
| 03SR - Stations (RfL) | Cxxx-NCR-000206 | NCR | footway width |  | Contr |  | PAD - Paddington Station (West) |  | 2012-08-30 | 2012-10-06 13:14 | 37 | 2012-07-12 | Construction Health & Safety - Construction Health & Safety General | 500 |  | Design | Rework |  | Complete |  | Completed |  | The footway has been constrained at the east end by hoarding. This is approximately 1.75m generally and 1.1m at the pinch point.
| 03SR - Stations (RfL) | Cxxx-NCR-000207 | NCR | Implementation of temporary works design |  | Contr |  | PAD - Paddington Station (West) |  | 2012-08-03 | 2012-08-03 12:15 | 0 | 2012-07-12 | Structural Engineering - Diaphragm Walls | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | Temporary works design was implemented incorrectly and workmanship was poor.
| 03SR - Stations (RfL) | Cxxx-NCR-000217 | NCR | Panel S16: Out of Tolerance Bars |  | Contr |  | PAD - Paddington Station (West) |  | 2012-08-14 | 2012-08-02 14:28 | -12 | 2012-07-19 | Structural Engineering - Diaphragm Walls | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | In panel S16, the inner near face bars of the Part B middle cage (Cxxx-SKC-C-DWG-B071_WS077-50138) consisting of Bar Marks 19 and 18 were out of positional tolerance by up to 30mm (80 mm from theoretical minus 50mm vertical positional tolerance = 30mm). This is detailed in the cage dimension check sheet as part of the panel record. In summary bar marks 19 and 18 have been positioned 80mm higher than the design causing bar marks 9 and 10 of the top cage (Cxxx-SKC-C-DWG-B071_WS077-50139) to be 80mm higher than specified (30mm out of tolerance)
| 03SR - Stations (RfL) | Cxxx-NCR-000222 | NCR | Panel S05: Out Of Tolerance Bars |  | Contr |  | PAD - Paddington Station (West) |  | 2012-08-14 | 2012-08-02 14:22 | -12 | 2012-07-23 | Structural Engineering - Diaphragm Walls | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Outer far face bars of the top cage consisting of Bar Marks 11 and 44 were out of positional tolerance by up to 35mm (85mm from theoretical minus 50mm vertical positional tolerance=35mm). This is detailed in the cage dimension check sheet as part of the panel record. Inner face bars of top cage consisting of Bar Marks 02 were out of positional tolerance by up to 105mm (155mm from theoretical minus 50mm vertical position tolerance = 105mm). This is detailed in the cage dimension check sheet as part of the panel record.
| 03SR - Stations (RfL) | Cxxx-NCR-000225 | NCR | Diaphragm wall inclinometers |  | Contr |  | PAD - Paddington Station (West) |  | 2012-08-09 | 2012-08-24 12:40 | 15 | 2012-07-26 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | Eastbourne Terrace reduced dig excavation commenced with no diaphragm wall inclinometers being installed and baselined.
| 03SR - Stations (RfL) | Cxxx-NCR-000227 | NCR | Honey Combing in the MacMillan House Wall |  | Contr |  | PAD - Paddington Station (West) |  | 2012-08-13 | 2012-08-24 12:13 | 11 | 2012-07-30 | Structural Engineering - Concrete Member | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Honey combing to the construction joint at the bottom of the second lift of the MacMillan House RC Lining Wall as captured in the attached picture.
| 03SR - Stations (RfL) | Cxxx-NCR-000236 | NCR | Panel E1 – Sonic Tube Loss |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-02-18 | 2014-01-24 09:01 | -25 | 2012-08-07 | Structural Engineering - Diaphragm Walls | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | During the final stages installation of the cage into panel E1, one of the sonic logging tube extension pieces became dislodged as it was not secured sufficiently at the joint. Once loose it could not be relocated, onto the tube welded to the cage through the head of the bentonite panel, prior to the concrete pour and as such the remainder of the tube was backfilled with concrete. The position of this sonic tube is highlighted on the attached drawing. This prevents the sonic integrity testing being carried out as agreed in the sonic logging method statement.
| 03SR - Stations (RfL) | Cxxx-NCR-000237 | NCR | Panel E1 – Inclinometer Tube Loss |  | Contr |  | PAD - Paddington Station (West) |  | 2012-09-04 | 2012-10-15 14:40 | 41 | 2012-08-07 | Structural Engineering - Diaphragm Walls | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | During the final stages of concreting the extension piece of the inclinometer reservation tube became dislodged as it was not secured sufficiently at this joint. Once loose, it could not be relocated onto the tube welded to the cage and the remainder of the tube was backfilled with concrete. An inclinometer cannot now be installed into the panel.
| 03SR - Stations (RfL) | Cxxx-NCR-000242 | NCR | 33 Westbourne Terrace I&M installation |  | Contr |  | PAD - Paddington Station (West) |  | 2012-09-28 | 2012-10-15 14:35 | 17 | 2012-08-21 | Surveying - Instrumentation and Monitoring | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | Prisms installed as shown in attached document, 1 prism not installed due to location, 2 prisms are duplicates, 1 level point is a duplicate. No duplicates installed.
| 03SR - Stations (RfL) | Cxxx-NCR-000247 | NCR | Unsafe and unplanned excavation |  | Contr |  | PAD - Paddington Station (West) |  | 2012-09-28 | 2012-11-02 18:16 | 35 | 2012-08-27 | Construction Health & Safety - Construction Health & Safety General | 500 |  |  | Rework |  | Complete |  | Completed |  | During the night shift of 22/23 August excavation works were undertaken by tracked excavator to prepare the site to construct the west 'box' wall. A near vertical 'cut' was formed in one location and 60 degree batter adjacent. The stability of the haul road above was compromised. An unsafe condition was created for persons working at the toe of the batter and beneath the cut.
| 03SR - Stations (RfL) | Cxxx-NCR-000248 | NCR | NCR- Change in location from Panel S70-S71 |  | Contr |  | PAD - Paddington Station (West) |  | 2012-09-29 | 2012-09-04 16:59 | -25 | 2012-08-28 | Structural Engineering - Diaphragm Walls | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Install additional inclinometer tube at S71.
| 03SR - Stations (RfL) | Cxxx-NCR-000250 | NCR | Rebar at panel E2 exceeding the marked level |  | Contr |  | PAD - Paddington Station (West) |  | 2012-09-28 | 2012-10-06 13:40 | 8 | 2012-08-28 | Structural Engineering - Reinforcement | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | Crossrail intent drawaing (Cxxx-SWN-S-DDD-M171_Z-55545 Rev C01) states that BM22 to exetend into the top cage of panel E2 to a level of 111.300. Installed were BM20 to a level of 113.205 and BM21 to a level of BM 112.415, both exceeding the Crossrail requirements as detailed in the client drawing. No action has been taken to correct the NCR, __ continued to install the cages with the extra steel.
| 03SR - Stations (RfL) | Cxxx-NCR-000262 | NCR | Inclinometer tubes in panels N3 and N8 |  | Contr |  | PAD - Paddington Station (West) |  | 2012-09-10 | 2012-09-18 13:44 | 8 | 2012-09-03 | Surveying - Instrumentation and Monitoring | 500 |  | Planning | Rework |  | Complete |  | Completed |  | The re-bar cages to panels N3 and N7 were released from the fabrication yard without the inclinometer tubes installed.
| 03SR - Stations (RfL) | Cxxx-NCR-000264 | NCR | Blocked Sonic Logging tubes 1 |  | Contr |  | PAD - Paddington Station (West) |  | 2012-10-31 | 2012-12-06 16:56 | 36 | 2012-09-06 | Structural Engineering - Diaphragm Walls | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The following panels were observed to have blockages within the tubes: S5, S15, S17, S25, S27, S32, S59, S63, S63A, S63B, S69, E1 & E1B.
| 03SR - Stations (RfL) | Cxxx-NCR-000265 | NCR | 18 hour constraint |  | Contr |  | PAD - Paddington Station (West) |  | 2012-10-12 | 2012-11-02 18:21 | 21 | 2012-09-06 | Structural Engineering - Diaphragm Walls | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | For certain panels the 18 hour constraint has been exceeded.
| 03SR - Stations (RfL) | Cxxx-NCR-000267 | NCR | QV Installation Records / Inclinometers |  | Contr |  | PAD - Paddington Station (West) |  | 2012-10-31 | 2012-11-09 17:18 | 9 | 2012-09-06 | Surveying - Instrumentation and Monitoring | 500 |  |  | Rework |  | Complete |  | Completed |  | The records have not been submitted within the 1 month period.
| 03SR - Stations (RfL) | Cxxx-NCR-000268 | NCR | QV Installation Records / Extensometers |  | Contr |  | PAD - Paddington Station (West) |  | 2012-10-17 | 2012-11-09 17:20 | 23 | 2012-09-06 | Surveying - Instrumentation and Monitoring | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | The records were not submitted within the 1 month period.
| 03SR - Stations (RfL) | Cxxx-NCR-000269 | NCR | QV Installation Records / Piezometers |  | Contr |  | PAD - Paddington Station (West) |  | 2012-10-31 | 2012-11-09 17:22 | 9 | 2012-09-06 | Surveying - Instrumentation and Monitoring | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | The records were not submitted within the 1 month period.
| 03SR - Stations (RfL) | Cxxx-NCR-000270 | NCR | QV Installation Records / Strain Gauges |  | Contr |  | PAD - Paddington Station (West) |  | 2012-10-31 | 2012-11-09 17:24 | 9 | 2012-09-06 | Surveying - Instrumentation and Monitoring | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | The records were not submitted within 1 month.
| 03SR - Stations (RfL) | Cxxx-NCR-000271 | NCR | QV Installation Records / ATS + Prism Arrays |  | Contr |  | PAD - Paddington Station (West) |  | 2012-10-17 | 2012-10-25 17:44 | 8 | 2012-09-06 | Surveying - Instrumentation and Monitoring | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | The records were not submitted within the 1 month period.
| 03SR - Stations (RfL) | Cxxx-NCR-000272 | NCR | Mac Hse Basement Trim Formwork failure |  | Contr |  | PAD - Paddington Station (West) |  | 2012-10-18 | 2012-11-09 17:28 | 22 | 2012-09-07 | Construction Health & Safety - Construction Health & Safety General | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | During the night shift of 4/5 Sept. 2012 a section of formwork moved during a concrete pour resulting in a loss of concrete and substantial rework.
| 03SR - Stations (RfL) | Cxxx-NCR-000275 | NCR | Panel S71: Out of tolerance bars |  | Contr |  | PAD - Paddington Station (West) |  | 2012-10-05 | 2012-10-25 17:11 | 20 | 2012-09-07 | Structural Engineering - Diaphragm Walls | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | In Panel S71 the inner face bars of the middle cage (Cxxx-SKC-C-DWG-B071_WS077-50096), Bar Mark 13 was out of positional tolerance by up to 44mm (94mm from the theoretical minus 50mm vertical position = 44mm). This is detailed in the cage dimension checksheet as part of the panel record.
| 03SR - Stations (RfL) | Cxxx-NCR-000276 | NCR | Panel_N9: Missing Links |  | Contr |  | PAD - Paddington Station (West) |  | 2012-10-26 | 2012-10-15 12:49 | -11 | 2012-09-07 | Structural Engineering - Diaphragm Walls | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | One no. set of shear link was found missing in top section cage of N9 (Cxxx-SKC-C-DWG-B071_WS077-50295). This is detailed in the cage dimension checklist as a part of the panel record. See attached sketch. 8 no 'C' shaped shear links (BM03) were tied on site to the top cage at the design position of the missing link set. However the B20 outer links, 1 no. BM05, 1no. BM08, could not be replaced due to site constraints. The as built cage is missing 1 no. BM05 and 1 no BM08 at the location shown in the attached sketch.
| 03SR - Stations (RfL) | Cxxx-NCR-000277 | NCR | Panel_N74: Out of Tolerance Bars |  | Contr |  | PAD - Paddington Station (West) |  | 2012-10-26 | 2012-10-09 17:55 | -17 | 2012-09-07 | Structural Engineering - Diaphragm Walls | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | In panel N74 in the inner far face of the top cage (Cxxx-SKC-C-DWG-B071_WS077-50270), Bar Mark 02 were out of positional tolerance. The as built levels are 140mm higher than that specified. This is detailed in the cage dimension checklist as a part of the panel record. The as built vs specified levels are shown in the attached sketch.
| 03SR - Stations (RfL) | Cxxx-NCR-000285 | NCR | London St borehole groundwater monitoring |  | Contr |  | PAD - Paddington Station (West) |  | 2013-05-15 | 2013-05-15 14:16 | 0 | 2012-09-12 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Received record shown non compliance with the specified monitoring frequency.
| 03SR - Stations (RfL) | Cxxx-NCR-000286 | NCR | Grout sampling D-Wall inclinometer N4 |  | Contr |  | PAD - Paddington Station (West) |  | 2012-09-26 | 2012-10-25 17:48 | 29 | 2012-09-19 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | Grouting up of the incinometer casing within panel N4 (monitoring location reference Cxxx-ld-E2-04) was completed by __ Environmental Services without any specimen taken from the batches prepared.
| 03SR - Stations (RfL) | Cxxx-NCR-000298 | NCR | Panel S09 Sonic Logging |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-30 | 2013-05-03 18:02 | 3 | 2012-09-26 | Structural Engineering - Diaphragm Walls | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Increased transit times were reported between profiles 1 and 2 at the base of the panel.
| 03SR - Stations (RfL) | Cxxx-NCR-000299 | NCR | Panel S21 Sonic Logging |  | Contr |  | PAD - Paddington Station (West) |  | 2013-01-25 | 2012-12-06 17:16 | -50 | 2012-09-26 | Structural Engineering - Diaphragm Walls | 500 |  | Material | Rework |  | Complete |  | Completed |  | The sonic logging records for S21 do not include the element of panel S21 beneath level 87.0 m ATD.
| 03SR - Stations (RfL) | Cxxx-NCR-000300 | NCR | Panel S10 Sonic Logging |  | Contr |  | PAD - Paddington Station (West) |  | 2013-01-25 | 2012-12-06 17:14 | -50 | 2012-09-26 | Structural Engineering - Diaphragm Walls | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | For panel S10 there are no records provided for the element of the panel beneath 87.0m ATD.
| 03SR - Stations (RfL) | Cxxx-NCR-000301 | NCR | sonic tubes left open to the ingress of debris |  | Contr |  | PAD - Paddington Station (West) |  | 2012-10-31 | 2012-10-31 15:49 | 0 | 2012-09-28 | Structural Engineering - Diaphragm Walls | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Tubes are in some cases taped over and in others left open
| 03SR - Stations (RfL) | Cxxx-NCR-000302 | NCR | Panel N9 Concrete Pour 1 |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2014-12-31 | 2014-09-02 09:40 | -120 | 2012-09-28 | Civil - Geotechnical Engineering | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Whilst pouring the concrete for diaphragm wall panel N9 the time between batch and discharge of load 705765 was 3 hours and 20mins.
| 03SR - Stations (RfL) | Cxxx-NCR-000303 | NCR | Panel N9 concrete 2 |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2014-12-31 | 2014-09-02 09:41 | -120 | 2012-09-28 | Civil - Geotechnical Engineering | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | The pour record for Diaphragm wall panel N9 shows an elapsed time between the completion of load 705764 and 705765 of 2hrs and the elapsed time between the completion of load 705766 and 705767 of 1hr and 20mins.
| 03SR - Stations (RfL) | Cxxx-NCR-000304 | NCR | Panel S77 concrete pour |  | Contr |  | PAD - Paddington Station (West) |  | 2014-12-31 | 2012-12-11 17:28 | -750 | 2012-09-29 | Civil - Geotechnical Engineering | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Whilst pouring the concrete for diaphragm wall panel S77 the time between batch and discharge for the following loads was; 706047 - 2hrs 18mins. 694886 - 2hrs 53mins. 694887 - 2hrs 41mins. 694888 - 2hrs 44mins. 706048 - 2hrs 40mins.
| 03SR - Stations (RfL) | Cxxx-NCR-000306 | NCR | Panel N4 Link |  | Contr |  | PAD - Paddington Station (West) |  | 2012-11-06 | 2012-10-25 17:19 | -12 | 2012-10-02 | Structural Engineering - Diaphragm Walls | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Panel N04 bottom cage top lifting band was 0.195m lower than the theoretical. The first link was positioned 0.206m below the band to allow for the positioning of trapping beams meaning that the first link was out of position by 0.206m. No additional links were added. This is detailed in the cage dimension checklist as a part of the panel record. See attached sketch
| 03SR - Stations (RfL) | Cxxx-NCR-000307 | NCR | Panel S28 concrete pour |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2014-12-31 | 2014-07-15 09:01 | -169 | 2012-10-02 | Civil - Geotechnical Engineering | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the concrete pour of Diaphragm wall panel S28 there is a time exceedance of 1hr and 19mins between the discharge of load 702348 and the start of load 70234.
| 03SR - Stations (RfL) | Cxxx-NCR-000308 | NCR | Cage Bars Length Tolerance |  | Contr |  | PAD - Paddington Station (West) |  | 2012-11-06 | 2012-10-06 13:10 | -31 | 2012-10-02 | Structural Engineering - Diaphragm Walls | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | On Panel S13, as indicated on the dimensional check sheets, 3no bars were found to be overlength by more than the 25mm cutting tolerance.
| 03SR - Stations (RfL) | Cxxx-NCR-000309 | NCR | Panel S75 Level |  | Contr |  | PAD - Paddington Station (West) |  | 2014-12-31 | 2014-09-05 15:56 | -117 | 2012-10-03 | Structural Engineering - Diaphragm Walls | 2500 |  | Material | Rework | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | Panel S75 is constructed 277mm higher than the theoretical. The original as-built guide wall survey levels for S75 indicated that the average guide wall level was 125.195 and the cage was constructed based on this level. However the as-built survey undertaken after the panel was concreted indicates that the guide wall level for panel S75 is 125.472mm (average). See attached
| 03SR - Stations (RfL) | Cxxx-NCR-000313 | NCR | Panel S04 Tremmie Split |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-06-16 | 2014-07-25 10:23 | -326 | 2012-10-04 | Structural Engineering - Diaphragm Walls | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During pouring of Panel S04 at approximately 130m^3 the tremmie was spli and the embedment dropped below the specified 3m.
| 03SR - Stations (RfL) | Cxxx-NCR-000314 | NCR | Panel S12_Construction Time Limit |  | Contr |  | PAD - Paddington Station (West) |  | 2012-11-15 | 2012-11-08 14:29 | -7 | 2012-10-04 | Structural Engineering - Diaphragm Walls | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | During the construction of panel S12 the time from last passage of the grab to completion of the concreting operation exceeded 24 hours. The recorded duration from end of digging to end of concreting for this panel is 44hours.
| 03SR - Stations (RfL) | Cxxx-NCR-000315 | NCR | Panel S10_Construction Time Limit |  | Contr |  | PAD - Paddington Station (West) |  | 2012-11-15 | 2012-11-08 14:38 | -7 | 2012-10-04 | Structural Engineering - Diaphragm Walls | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | During the construction of panel S10 the time from last passage of the grab to completion of the concreting operation exceeded 24 hours. The recorded duration from end of digging to end of concreting for this panel is 35hours.
| 03SR - Stations (RfL) | Cxxx-NCR-000316 | NCR | Panel S03_Construction Time Limit |  | Contr |  | PAD - Paddington Station (West) |  | 2012-11-01 | 2012-11-02 18:02 | 1 | 2012-10-04 | Structural Engineering - Diaphragm Walls | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | During the construction of panel S03 the time from last passage of the grab to completion of the concreting operation exceeded 24 hours. The recorded duration from end of digging to end of concreting for this panel is 33hours.
| 03SR - Stations (RfL) | Cxxx-NCR-000320 | NCR | Magnetic extensometers not read |  | Contr |  | PAD - Paddington Station (West) |  | 2012-10-31 | 2012-10-25 18:17 | -6 | 2012-10-09 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Equipment Breakdown | Rework |  | Complete |  | Completed |  | Readings from the magnetic extensometers installed within the box (locations C7, C12 and C20) have not been obtained since 26.09.2102. Monitoring contractor DATUM informed that this was due to breakdown of the probe used. This situation would have been avoided if base readings were also taken by a second probe which should have been kept as a spare.
| 03SR - Stations (RfL) | Cxxx-NCR-000321 | NCR | Sonic Tubes Potential for Blockage |  | Contr |  | PAD - Paddington Station (West) |  | 2012-10-31 | 2012-10-29 14:26 | -2 | 2012-10-09 | Structural Engineering - Diaphragm Walls | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | Sonic tubes left open on Panel 59 allowing the ingress of debris. This has been raised as a generic NCR under PAD-CRL NCR-Cxxx-00301, discussed at NCR Preventative action meeting and EWN 161 raised but the problem still persists.
| 03SR - Stations (RfL) | Cxxx-NCR-000322 | NCR | Sonic tubes left open with potential for blockage to occur |  | Contr |  | PAD - Paddington Station (West) |  | 2012-10-31 | 2012-10-25 18:06 | -6 | 2012-10-09 | Structural Engineering - Diaphragm Walls | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | Sonic tubes left open on Panel 58 allowing the ingress of debris. This has been raised as a generic NCR under PAD-CRL NCR-Cxxx-00301, discussed at NCR Preventative action meeting and EWN 161 raised but the problem still persists.
| 03SR - Stations (RfL) | Cxxx-NCR-000323 | NCR | Sonic tubes left open with potential for blockage to occur S57 |  | Contr |  | PAD - Paddington Station (West) |  | 2012-10-31 | 2012-10-25 18:04 | -6 | 2012-10-09 | Structural Engineering - Diaphragm Walls | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | Sonic tubes left open on Panel 57 allowing the ingress of debris. This has been raised as a generic NCR under PAD-CRL NCR-Cxxx-00301, discussed at NCR Preventative action meeting and EWN 161 raised but the problem still persists.
| 03SR - Stations (RfL) | Cxxx-NCR-000324 | NCR | Sonic tubes left open with potential for blockage to occur S47 |  | Contr |  | PAD - Paddington Station (West) |  | 2012-10-31 | 2012-10-25 18:02 | -6 | 2012-10-09 | Structural Engineering - Diaphragm Walls | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | Sonic tubes left open on Panel 47 allowing the ingress of debris. This has been raised as a generic NCR under PAD-CRL NCR-Cxxx-00301, discussed at NCR Preventative action meeting and EWN 161 raised but the problem still persists.
| 03SR - Stations (RfL) | Cxxx-NCR-000325 | NCR | Sonic tubes left open with potential for blockage to occur S34 |  | Contr |  | PAD - Paddington Station (West) |  | 2012-10-31 | 2012-10-25 10:14 | -6 | 2012-10-09 | Structural Engineering - Diaphragm Walls | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | Sonic tubes left open on Panel S34 allowing the ingress of debris. This has been raised as a generic NCR under PAD-CRL NCR-Cxxx-00301, discussed at NCR Preventative action meeting and EWN 161 raised but the problem still persists.
| 03SR - Stations (RfL) | Cxxx-NCR-000326 | NCR | Sonic tubes left open with potential for blockage to occur S36 |  | Contr |  | PAD - Paddington Station (West) |  | 2012-10-31 | 2012-10-25 09:59 | -6 | 2012-10-09 | Structural Engineering - Diaphragm Walls | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | Sonic tubes left open on Panel S36 allowing the ingress of debris. This has been raised as a generic NCR under PAD-CRL NCR-Cxxx-00301, discussed at NCR Preventative action meeting and EWN 161 raised but the problem still persists.
| 03SR - Stations (RfL) | Cxxx-NCR-000327 | NCR | Sonic tubes left open with potential for blockage to occur S37 |  | Contr |  | PAD - Paddington Station (West) |  | 2012-10-31 | 2012-10-25 09:57 | -6 | 2012-10-09 | Structural Engineering - Diaphragm Walls | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | Sonic tubes left open on Panel 59 allowing the ingress of debris. This has been raised as a generic NCR under PAD-CRL NCR-Cxxx-00301, discussed at NCR Preventative action meeting and EWN 161 raised but the problem still persists.
| 03SR - Stations (RfL) | Cxxx-NCR-000328 | NCR | Sonic tubes left open with potential for blockage to occur S38 |  | Contr |  | PAD - Paddington Station (West) |  | 2012-10-31 | 2012-10-25 09:56 | -6 | 2012-10-09 | Structural Engineering - Diaphragm Walls | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | Sonic tubes left open on Panel S38 allowing the ingress of debris. This has been raised as a generic NCR under PAD-CRL NCR-Cxxx-00301, discussed at NCR Preventative action meeting and EWN 161 raised but the problem still persists.
| 03SR - Stations (RfL) | Cxxx-NCR-000329 | NCR | Sonic tubes left open with potential for blockage to occur E4 |  | Contr |  | PAD - Paddington Station (West) |  | 2012-10-31 | 2012-10-25 09:54 | -6 | 2012-10-09 | Structural Engineering - Diaphragm Walls | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | Sonic tubes left open on Panel E4 allowing the ingress of debris. This has been raised as a generic NCR under PAD-CRL NCR-Cxxx-00301, discussed at NCR Preventative action meeting and EWN 161 raised but the problem still persists.
| 03SR - Stations (RfL) | Cxxx-NCR-000330 | NCR | Inclinometer Reservation tubes left open with potential for blockage to occur E4 |  | Contr |  | PAD - Paddington Station (West) |  | 2012-10-31 | 2012-11-02 17:59 | 2 | 2012-10-09 | Structural Engineering - Diaphragm Walls | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | Top of tube left open with the optential for ingress of debris
| 03SR - Stations (RfL) | Cxxx-NCR-000331 | NCR | Panel S07 Concrete Pour |  | Contr |  | PAD - Paddington Station (West) |  | 2014-12-31 | 2014-09-02 09:46 | -120 | 2012-10-09 | Civil - Geotechnical Engineering | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | The pour record for Diaphragm wall panel S7 shows an elapsed time between the completion of load 681043 and 681045 of 1hr and 43mins.
| 03SR - Stations (RfL) | Cxxx-NCR-000335 | NCR | Panel N67- blockage within void former |  | Contr |  | PAD - Paddington Station (West) |  | 2012-11-30 | 2012-11-29 17:59 | -1 | 2012-10-12 | Structural Engineering - Diaphragm Walls | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | Top of void former was exposed resulting to a blockage which has postponed the scheduled installation of the inclinometer casing.
| 03SR - Stations (RfL) | Cxxx-NCR-000339 | NCR | Panel S46 - Tremie Embedment |  | Contr |  | PAD - Paddington Station (West) |  | 2014-12-31 | 2014-07-28 09:24 | -156 | 2012-10-16 | Structural Engineering - Diaphragm Walls | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During the concrete pour of panel S46 the tremie embedment was 1.6m. The concrete depth was 7.4m and the tremie was split from 12m to 9m. The first issue of the S46 panel record had an error in the tremie split plot and this has been corrected in the attached sheet. The panel record will be reissued.
| 03SR - Stations (RfL) | Cxxx-NCR-000340 | NCR | Panel S68 - Lost Cubes |  | Contr |  | PAD - Paddington Station (West) |  | 2012-11-30 | 2012-11-23 12:09 | -7 | 2012-10-16 | Structural Engineering - Diaphragm Walls | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Panel S68 - Cube samples lost during the curing process by __ prevented cube strength results being produced at 28 days. This was due to human error. __ investigation to follow. Cubes were found in time for 56 day testing and 56 day testing performed showed adequate strength across all three sets of cubes.
| 03SR - Stations (RfL) | Cxxx-NCR-000341 | NCR | Panel S27: 28 day rolling mean cube strength |  | Contr |  | PAD - Paddington Station (West) |  | 2012-11-30 | 2012-10-31 15:39 | -30 | 2012-10-16 | Structural Engineering - Diaphragm Walls | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Panel S27 marginally failed the rolling mean cube strength: 45.5mPa < 46mPa at 28 days
| 03SR - Stations (RfL) | Cxxx-NCR-000343 | NCR | Within 18-24hours - Exceeding 18 hour limit |  | Contr |  | PAD - Paddington Station (West) |  | 2012-11-30 | 2012-10-25 18:19 | -36 | 2012-10-18 | Structural Engineering - Diaphragm Walls | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | As noted on the attached table, for the following panels, the time limit of 18 hours from last pass of grab to completion of concreting was exceeded, but did not extend beyond 24 hours: W02 / S02 / S08 / S21 / S11 / S19 / S04/ S12 / S33 / S29 / S17 / S05 / S28 / S68 / S60 / S70 / S75 / N09 / N07 / N75 / N80 / N05 / N78 / N67 / N68 / S38 / S37 / S36
| 03SR - Stations (RfL) | Cxxx-NCR-000344 | NCR | Omission of sheet piling alongside service corridor |  | Contr |  | PAD - Paddington Station (West) |  | 2012-11-30 | 2012-12-10 13:41 | 10 | 2012-10-18 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | Sheet piles to the southern area of the site have been omitted.
| 03SR - Stations (RfL) | Cxxx-NCR-000346 | NCR | Panels S09 and S10: Water Addition |  | Contr |  | PAD - Paddington Station (West) |  | 2012-11-30 | 2012-12-03 18:13 | 3 | 2012-10-18 | Structural Engineering - Diaphragm Walls | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Water was added to the concrete for Panels S09 and S10. This was done in accordance with the Diaphragm Wall Method Statement - Part A1.11.6.4 Concreting.
| 03SR - Stations (RfL) | Cxxx-NCR-000349 | NCR | System wide failure of CSJV controlled ATS |  | Contr |  | PAD - Paddington Station (West) |  | 2012-11-02 | 2012-11-09 17:34 | 7 | 2012-10-19 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Rework |  | Complete |  | Completed |  | Due to a system wide computer hardware failure the ATS controlled by did not observe the 00:00 or 06:00 cycle for the Cxxx TBM monitoring at Paddingtion within the TBM ZOI.
| 03SR - Stations (RfL) | Cxxx-NCR-000353 | NCR | Panel S35_Links |  | Contr |  | PAD - Paddington Station (West) |  | 2012-11-30 | 2012-11-19 17:45 | -11 | 2012-10-22 | Structural Engineering - Diaphragm Walls | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | 2no link sets at the bottom of the bottom cage of Panel S35 where incorrectly positioned. This resulted in a gap in the links. An additional loose comb link set was installed at the required position.
| 03SR - Stations (RfL) | Cxxx-NCR-000354 | NCR | Panel S65_Concrete Testing |  | Contr |  | PAD - Paddington Station (West) |  | 2012-12-07 | 2012-11-28 17:28 | -9 | 2012-10-22 | Structural Engineering - Diaphragm Walls | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The concrete testing technician did not carry out the concrete test prior to discharge of the final cocrete load of Panel S65. When the technician was challenged by the Crossrail Field Engineer the discharge was paused and the load flow tested. The result was 430mm, outside the acceptable flow range. It was however noticed that equipment was not in the required condition prior to testing so the flow testing equipment was cleaned and the flow table wetted, and the test undertaken again. Upon repeat of the test the flow was 580mm and within the 530mm-660mm flow range. A result of 590mm was written on the concrete ticket prior to any testing.
| 03SR - Stations (RfL) | Cxxx-NCR-000358 | NCR | Panel W04 Concrete Pour |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2015-01-30 | 2014-12-19 09:59 | -42 | 2012-10-24 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The pour for Diaphragm Wall panel W04 shows an elapsed time between the completion of load 703122 and the start of load 703124 of 1hr and 28mins.
| 03SR - Stations (RfL) | Cxxx-NCR-000361 | NCR | Panel S31: Concrete Time Between Pours |  | Contr |  | PAD - Paddington Station (West) |  | 2012-11-30 | 2012-10-31 18:11 | -30 | 2012-10-25 | Structural Engineering - Diaphragm Walls | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Panels S31. Concrete ticket 60853 records completion of pour at 00:55. Concrete ticket 690854 records a start of pour of next load at 2:00. The time between the pours is 1:05 instead of the specified 1:00 hour
| 03SR - Stations (RfL) | Cxxx-NCR-000368 | NCR | Panel W01_Tremmie Embedment |  | Contr |  | PAD - Paddington Station (West) |  | 2012-12-01 | 2012-11-14 17:50 | -17 | 2012-11-01 | Structural Engineering - Diaphragm Walls | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | During the concrete pour for panel W01 the tremmie embedment extended past the maximum allowable of 9.0m. This occurred with the concrete at 7.45m below the guidewall (Thus at a level of 127.1-7.45=119.65mAOD). The embedment at this level was 10.0m. At no other instance was the tremmie embedment greater than 9.0m.
| 03SR - Stations (RfL) | Cxxx-NCR-000369 | NCR | Panel_S31: Tremmie Embedment |  | Contr |  | PAD - Paddington Station (West) |  | 2012-12-01 | 2012-11-12 16:44 | -19 | 2012-11-01 | Structural Engineering - Diaphragm Walls | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | During the concrete pour for panel S31 the tremie embedment was reduced to 2.8m, less than the minimum 3.0m agreed. This occurred with the concrete at 15.2m below the guidewall. At no other instance was the tremie embedment less than 3.0m.
| 03SR - Stations (RfL) | Cxxx-NCR-000370 | NCR | Panel_S59: Tremmie Embedment |  | Contr |  | PAD - Paddington Station (West) |  | 2012-11-05 | 2012-11-08 14:40 | 3 | 2012-11-01 | Structural Engineering - Diaphragm Walls | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | During the concrete pour for panel S59 the tremie embedment was reduced to 2.8m, less than the minimum 3.0m agreed. This occurred with the concrete at 18.2m below the guidewall. At no other instance was the tremie embedment less than 3.0m.
| 03SR - Stations (RfL) | Cxxx-NCR-000371 | NCR | Panel S43: Time to Completion of Concreting |  | Contr |  | PAD - Paddington Station (West) |  | 2012-12-21 | 2012-12-21 14:09 | 0 | 2012-11-01 | Structural Engineering - Diaphragm Walls | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The construction of panel S43 has passed the 120 hour (5 day) time limit for construction - commencement of excavation to completion of concreting. The actual time taken was 175hours. Panel excavation started at 09:30 24/10/2012, Last pass of grab happened at 01:00 31/10/2012 and the End of Concreting at 17:15 31/10/2012. Please note the duration between last pass of grab and end of concreting was 15hr 45mins (< 24hr). Reason this occured: Difficulties were experienced removing the stopend from the cast face of the adjacent panel. An intermittent problem with the grab instrumentation has also delayed the completion of the excavation.
| 03SR - Stations (RfL) | Cxxx-NCR-000372 | NCR | Panel S46: 28 day Cube Strength |  | Contr |  | PAD - Paddington Station (West) |  | 2012-12-20 | 2012-11-29 18:04 | -21 | 2012-11-01 | Structural Engineering - Diaphragm Walls | 500 |  |  | Rework |  | Complete |  | Completed |  | Please see attached. For panel S46 cast 29/09/2012, one set of cubes did not meet the PASS criteria (criterion 2) for 28 day results. One cube at 28 days from set S1205854 was 40.1N/mm2 and the other cube 40.8N/mm2, with the average for this set at 28 days being therefore 40.5N/mm2 < 41N/mm2 PASS criteria (45N/mm2 minus 4N/mm2). As a result, the criterion 1 rolling mean is also not a PASS, as it is 44.6N/mm2 < 46N/mm2 (45N/mm2 + 1N/mm2 for 4 sets).
| 03SR - Stations (RfL) | Cxxx-NCR-000374 | NCR | Panel N1_Missing Delivery Ticket |  | Contr |  | PAD - Paddington Station (West) |  | 2012-12-20 | 2012-11-19 18:04 | -31 | 2012-11-01 | Structural Engineering - Diaphragm Walls | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | For Panel N1 cast on 21/08/2012, 1no concrete delivery ticket was missing from __ and __'s system.
| 03SR - Stations (RfL) | Cxxx-NCR-000375 | NCR | Panel S71_Tremmie Embedment |  | Contr |  | PAD - Paddington Station (West) |  | 2012-12-20 | 2012-11-12 16:50 | -38 | 2012-11-01 | Structural Engineering - Diaphragm Walls | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | During the concrete pour for panel S71 the tremie embedment extended past the maximum allowable of 9.0m. This occurred with the concrete at 26.8m below the guidewall (Thus at a level of 127.1-26.8=100.3mAOD). The embedment at this level was 9.2m. At no other instance was the tremie embedment greater than 9.0m.
| 03SR - Stations (RfL) | Cxxx-NCR-000376 | NCR | Panel S31_Concreting Time |  | Contr |  | PAD - Paddington Station (West) |  | 2014-12-30 | 2012-12-11 16:53 | -749 | 2012-11-01 | Structural Engineering - Diaphragm Walls | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | During the concrete pour of panel S31, load 680853 exceeded the 2 hour limit from time of batching to completion of discharge. The load was batched at 23:44, started discharging at 00:50 and completed discharge at 01:55. The load was tested prior to discharge with a flow of 600mm. Utilising the flow retention information previously submitted it is anticipated that at the end of the discharge the concrete would still be within the 530-660mm range detailed on the ITP.
| 03SR - Stations (RfL) | Cxxx-NCR-000377 | NCR | Exceeding 24 Hour Limit |  | Contr |  | PAD - Paddington Station (West) |  | 2012-12-20 | 2013-01-14 17:22 | 25 | 2012-11-02 | Structural Engineering - Diaphragm Walls | 500 |  | Planning | Rework |  | Complete |  | Completed |  | Elapsed time between last pass of grab and end of concreting exceeded 24 hours on a number of panels. A list of these panels, including the actual elapsed time is attached. Affected panels are: S09, S10, S15, S03, S07, S16, S63, S77, S69, E01, S61, E02, S62, S74, N01, N02, N06, N81, N04 and N74. Please note, S15, S16, S62 are crank panels; S77, N1 and N81 are corner panels; due to their size and complexity, they demand longer durations compard to standard panels.
| 03SR - Stations (RfL) | Cxxx-NCR-000378 | NCR | Panel S62_Sonic Tube |  | Contr |  | PAD - Paddington Station (West) |  | 2012-12-20 | 2013-01-18 17:13 | 29 | 2012-11-02 | Structural Engineering - Diaphragm Walls | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | Sonic logging tube 1 in panel S62 part A and tube 4 in panel S62 part B (same tube) has a blockage approximately 300mm from the toe of the panel. S62 also has an anomaly issue but this will be dealt with in a separate NCR. This blockage was confirmed in site visit 7 and site visit 9.This panel is split into three parts, and so has eight no. sonic logging tubes. The reason for the blockage is unknown
| 03SR - Stations (RfL) | Cxxx-NCR-000379 | NCR | Concrete Cubes |  | Contr |  | PAD - Paddington Station (West) |  | 2012-12-20 | 2012-11-19 18:35 | -31 | 2012-11-02 | Structural Engineering - Diaphragm Walls | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Non conformance against site storage of cubes prior to transporting off site. Cubes (21-10-12) exceeded the 3 day limit of being struck from the mould. Cube moulds were not properly covered; and un-heated cabin used.
| 03SR - Stations (RfL) | Cxxx-NCR-000380 | NCR | Panel S77_Concrete Timings |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-12-30 | 2014-08-13 16:04 | -139 | 2012-11-02 | Structural Engineering - Diaphragm Walls | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The elapsed time between batching and start of pour has exceeded the time limit of 2hrs set in project spec KF11.3203c, per following list: 706047 - 2hrs 18mins. 694886 - 2hrs 53mins. 694887 - 2hrs 41mins. 694888 - 2hrs 44mins. 706048 - 2hrs 40mins.
| 03SR - Stations (RfL) | Cxxx-NCR-000381 | NCR | Panel_56: Reinforcement Out Of Tolerance |  | Contr |  | PAD - Paddington Station (West) |  | 2012-12-20 | 2012-11-29 18:09 | -21 | 2012-11-02 | Structural Engineering - Diaphragm Walls | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Panel S56: the inner near face bars (Bar marks: 73 and 63) were out of tolerance by 120mm as detailed in drawing number Cxxx-SKC-C-DWGB071_WS077-50109 (170mm theoretical difference minus 50mm tolerance = 120mm). This is detailed in the cage dimension check sheet as part of the submitted panel record. Please see attached.
| 03SR - Stations (RfL) | Cxxx-NCR-000383 | NCR | Temporary works for fire main |  | Contr |  | PAD - Paddington Station (West) |  | 2012-11-30 | 2013-02-18 12:35 | 80 | 2012-11-05 | Mechanical - Hot & Cold Water Supplies | 500 |  | Design | Rework |  | Complete |  | Completed |  | Temporary fire main has been installed along NR boundary. Repeated requests for the design details of this pressurised pipeline have gone unanswered. Temporary works design to be submitted
| 03SR - Stations (RfL) | Cxxx-NCR-000384 | NCR | Toe level on panel E4 200mm high on southern corner |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2014-12-31 | 2014-12-19 10:02 | -12 | 2012-11-05 | Structural Engineering - Diaphragm Walls | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Whilst the majority of the panel was constructed to the design toe level, the southern most corner was 200mm high. the Dwall contractor advised that to remove this section would result in overdig to the remainder of the panel and since the panel is located over the eastbound tunnel CRL PFE and agreed that this was the best course of action. confirmed that cage was installed in accordance with the design.
| 03SR - Stations (RfL) | Cxxx-NCR-000385 | NCR | Inclinometer reservation tube missing from panel S20 |  | Contr |  | PAD - Paddington Station (West) |  | 2012-12-07 | 2012-12-21 14:13 | 14 | 2012-11-05 | Structural Engineering - Diaphragm Walls | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | advise that an inclinometer cannot be installed within this panel.
| 03SR - Stations (RfL) | Cxxx-NCR-000388 | NCR | Panel N1: Tremmie Embedment |  | Contr |  | PAD - Paddington Station (West) |  | 2012-12-21 | 2012-11-19 18:10 | -32 | 2012-11-08 | Structural Engineering - Diaphragm Walls | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | When concreting panel N1, when cumulative concrete volume reached ~70m^3, the tremmie embedment (1 no. Tremmie only for this corner panel's deeper North Wall part) temporarily exceeded 9m; maximum embedment was 11.8m.
| 03SR - Stations (RfL) | Cxxx-NCR-000389 | NCR | Inclinometers / Borehole Grout Sampling |  | Contr |  | PAD - Paddington Station (West) |  | 2013-02-15 | 2013-01-25 10:23 | -21 | 2012-11-08 | Surveying - Instrumentation and Monitoring | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Samples were taken but not in accordance with the British Standard. This NCR applies to inclinometer references Cxxx-IG [CT-06, CS-02, A15-08, A8-03, A12-09, E24-09, E13-06, E10-09, E15-07, A7-02] & Cxxx-IGT [A1-02, E1-01].
| 03SR - Stations (RfL) | Cxxx-NCR-000390 | NCR | Inclinometers / Keyway Spiral Twisting |  | Contr |  | PAD - Paddington Station (West) |  | 2013-03-08 | 2013-03-08 17:28 | 0 | 2012-11-08 | Surveying - Instrumentation and Monitoring | 500 |  | Material | Rework |  | Complete |  | Completed |  | This NCR applies to inclinometer references Cxxx-IG [CT-06, CS-02, A15-08, A8-03, A12-09, E24-09, E13-06, E10-09, E15-07, A7-02] & Cxxx-IGT [A1-02, E1-01].
| 03SR - Stations (RfL) | Cxxx-NCR-000402 | NCR | Spring Street ATS System failure |  | Contr |  | PAD - Paddington Station (West) |  | 2012-12-21 | 2012-12-21 14:16 | 0 | 2012-11-16 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | A problem with the conversion software provided by Geomos resulted inthe data not being displayed on the webpage in a timely manner.
| 03SR - Stations (RfL) | Cxxx-NCR-000403 | NCR | Panel S37_Concrete Timings |  | Contr |  | PAD - Paddington Station (West) |  | 2012-11-30 | 2012-12-10 14:16 | 10 | 2012-11-16 | Structural Engineering - Diaphragm Walls | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Panel S37, concrete load 703980 (2hours and 56mins) exceeded the 2hour duration between batching and end of pour.
| 03SR - Stations (RfL) | Cxxx-NCR-000404 | NCR | Panel S47 |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2014-12-31 | 2014-07-18 16:25 | -166 | 2012-11-16 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Panel S47. Concrete ticket 705204 records completion of pour at 16.15. Concrete ticket 705215 records a start of pour of next load at 17.35. The time between the pours is 1:20 instead of the specified 1:00 hour
| 03SR - Stations (RfL) | Cxxx-NCR-000406 | NCR | Cube Strength_MacMillan House Wall |  | Contr |  | PAD - Paddington Station (West) |  | 2012-12-19 | 2012-12-21 14:18 | 2 | 2012-11-19 | Structural Engineering - Concrete Member | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | C40/50 __ concrete for pour 1 (4m3) of MacMillan house block E lining wall has not reached required compressive strength after 28 or 56 days. See attached; 1. Concrete test cube reports for 4, 7, 28, 28 & 56 days (series 62 A to E) 2. __ Report
| 03SR - Stations (RfL) | Cxxx-NCR-000408 | NCR | Compliance documentation for piling mat subbase |  | Contr |  | PAD - Paddington Station (West) |  | 2012-12-20 | 2013-02-14 17:17 | 56 | 2012-11-20 | Civil - Sub-base | 500 |  | Material | Rework |  | Complete |  | Completed |  | have not been able to demonstrate that the crushed material forming the subbase to the piling mat is in accordance with __ Report 470
| 03SR - Stations (RfL) | Cxxx-NCR-000409 | NCR | Anchor depth of Rod Extensometer - Chilworth Mews |  | Contr |  | PAD - Paddington Station (West) |  | 2013-02-28 | 2013-01-17 08:57 | -42 | 2012-11-20 | Surveying - Instrumentation and Monitoring | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The extensometer anchor points are at the incorrect levels
| 03SR - Stations (RfL) | Cxxx-NCR-000411 | NCR | Inclinometer bored hole verticality |  | Contr |  | PAD - Paddington Station (West) |  | 2013-02-28 | 2013-02-27 11:59 | -1 | 2012-11-22 | Surveying - Instrumentation and Monitoring | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | In the case of the following inclinometers the above requirement was not achieved: Cxxx-IG-E13-06 & Cxxx-IG-E15-07.
| 03SR - Stations (RfL) | Cxxx-NCR-000412 | NCR | Inclinometer Installation / Pre-Installation condition surveys |  | Contr |  | PAD - Paddington Station (West) |  | 2012-12-21 | 2013-01-18 09:05 | 28 | 2012-11-22 | Surveying - Instrumentation and Monitoring | 500 |  | Planning | Rework |  | Complete |  | Completed |  | The contractor did not produce this written record for the following inclinometers: Cxxx-IG- [CT-06, CS-02, A15-08, A8-03, A12-09, E24-09, E13-06, E10-09, E15-07, A7-02, CS-05]; Cxxx-IGT-[A1-02, E1-01]; Cxxx-IS-E6-01; Cxxx-ID-[A10-11, A4-07, A2-05, A5-25, A7-27, A8-32, B1-03, A9-36, A17-15, A23-19, A2-17]
| 03SR - Stations (RfL) | Cxxx-NCR-000413 | NCR | Inclinometers / spiral twisting 2 |  | Contr |  | PAD - Paddington Station (West) |  | 2013-01-25 | 2013-02-14 14:35 | 20 | 2012-11-22 | Surveying - Instrumentation and Monitoring | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | For the following inclinometers the requirement was not achieved: Cxxx-IG-CS-05, Cxxx-IS-E6-01, Cxxx-ID-[A10-11, A4-07, A2-05, A5-25, A7-27, A8-32, B1-03, A9-36, A17-15, A23-19, A2-17]
| 03SR - Stations (RfL) | Cxxx-NCR-000414 | NCR | Grout sampling for compressive strength testing |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-30 | 2013-03-26 15:48 | -35 | 2012-11-22 | Surveying - Instrumentation and Monitoring | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Samples were taken but not in accordance with the British Standard. This NCR applies to inclinometers Cxxx-IG-CS-05, Cxxx-IS-E6-01, Cxxx-ID-[A10-11, A4-07, A2-05, A5-25, A7-27, A8-32, B1-03, A9-36, A17-15, A23-19, A2-17]
| 03SR - Stations (RfL) | Cxxx-NCR-000415 | NCR | Vibrating Wire Piezometers on gridline C7 |  | Contr |  | PAD - Paddington Station (West) |  | 2013-02-28 | 2013-02-27 11:51 | -1 | 2012-11-23 | Surveying - Instrumentation and Monitoring | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | The piezometers do not appear to be reading accurately
| 03SR - Stations (RfL) | Cxxx-NCR-000416 | NCR | Extensometers gridlines C7 & C12 |  | Contr |  | PAD - Paddington Station (West) |  | 2013-05-10 | 2013-05-09 10:33 | -1 | 2012-11-23 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Rework |  | Complete |  | Completed |  | The extensometers at gridlines C7 and C12 are not functioning correctly or are blocked. These are required prior to excavation
| 03SR - Stations (RfL) | Cxxx-NCR-000417 | NCR | Panel S69_Sonic Logging Anomaly |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-30 | 2013-04-30 20:46 | 0 | 2012-11-23 | Structural Engineering - Diaphragm Walls | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Panel S69 was identified as having a blockage which prevented a full sonic logging test taking place (see separate NCR _264). By drilling out of this blockage using a mini-piling rig a full test was able to be performed. Upon re-test an anomaly was identified in S69 -Profile 3-4 shows an increase in transit time of 23.5% over a vertical extent of 200mm. Please see attached APPENDIX for full report.
| 03SR - Stations (RfL) | Cxxx-NCR-000418 | NCR | Panel_S27: Sonic Logging Anomaly |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-30 | 2013-05-01 00:26 | 1 | 2012-11-23 | Structural Engineering - Diaphragm Walls | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Panel S27 was identified as having a blockage which prevented a full sonic logging test taking place (see separate NCR _264). By drilling out of this blockage using a mini-piling rig a full test was able to be performed and NCR 031 applied to be closed out. Upon re-test an anomaly was identified in S27 -Profile 1-2 shows an increase in transit time of 20.4%, approximately 300mm from the base of the panel over a vertical extent of 500mm. Please see attached APPENDIX for full report.
| 03SR - Stations (RfL) | Cxxx-NCR-000419 | NCR | Panel S63A_Sonic Logging Anomaly |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-30 | 2013-05-01 00:23 | 1 | 2012-11-23 | Structural Engineering - Diaphragm Walls | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | Panel S63A was identified as having a blockage which prevented a full sonic logging test taking place (see separate NCR_264). By drilling out of this blockage using a mini-piling rig a full test was able to be performed. Upon re-test an anomaly was identified in S63A - Profile 2-3, 3-4 and 1-3 shows an increase in transit times at the base of the profiles, over a vertical extent of 400mm. Please see attached APPENDIX for full report.
| 03SR - Stations (RfL) | Cxxx-NCR-000420 | NCR | Panel S17_Sonic Logging Anomaly |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-30 | 2013-05-01 00:11 | 1 | 2012-11-23 | Structural Engineering - Diaphragm Walls | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Panel S17 was identified as having a blockage which prevented a full sonic logging test taking place (see separate NCR_264). Upon drilling out of this blockage using a mini-piling rig a full test was able to be performed. Upon re-test an anomaly was fully identified in S17 - Profiles 1-2, 3-4, 4-1 and 2-4 all show increases in transit times at the base of the panel, the largest increase being 64% on profile 1-2, over a vertical extent of approximately 700mm. As these increases are not repeated on the remaining profile the increases are likely to be the result of localised features in the vicinity of tubes 1 and 4. A further increase in transit time is shown on profile 3-4 at a depth of 90.8m AOD. As this increase is not present on the remaining profiles it can be considered the result of a localised feature with no significance in terms of panel integrity. All other areas showed sound and homogenous concrete throughout. Please see attached APPENDIX for full report.
| 03SR - Stations (RfL) | Cxxx-NCR-000421 | NCR | Panel N9_Sonic Logging Anomaly |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-12-30 | 2014-06-09 13:10 | -204 | 2012-11-25 | Structural Engineering - Diaphragm Walls | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | For panel N9 cast on 19/8/2012, it was sonic logged on 26/9/12, and profile 1-2 shows an increase in transit time of 22.2% at approximately 118mAD, over a vertical extent of 200mm. All other area tested show sound concrete throughout. Please see the attached report for the signals.
| 03SR - Stations (RfL) | Cxxx-NCR-000422 | NCR | Panel S02_Sonic Logging Anomaly |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-30 | 2013-04-30 23:52 | 0 | 2012-11-25 | Structural Engineering - Diaphragm Walls | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Panel S02- An anomaly was identified by __ during sonic logging works. Profile 2-3, 3-4, 4-1 & 2-4 all show increases in transit time at the base of the panel, the largest increase being 28% on profile 3-4, over a vertical extent of approximately 200mm. Please see attached APPENDIX for full report.
| 03SR - Stations (RfL) | Cxxx-NCR-000423 | NCR | Panel S04_Sonic Logging Anomaly |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-30 | 2013-04-30 23:45 | 0 | 2012-11-25 | Structural Engineering - Diaphragm Walls | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Panel S04- An anomaly was identified during sonic logging works by __. Profiles 1-2 & 2-4 show an increase in transit time at the base of the profiles. Please see attached APPENDIX for full report.
| 03SR - Stations (RfL) | Cxxx-NCR-000424 | NCR | Panel S14_Sonic Logging Anomaly |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-30 | 2013-04-30 23:40 | 0 | 2012-11-25 | Structural Engineering - Diaphragm Walls | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Panel S14- An anomaly was identified by __ during sonic logging works. Profiles 1-2, 4-1 & 1-3 show an increase in transit time at the base of the panel. Please see attached APPENDIX for full report.
| 03SR - Stations (RfL) | Cxxx-NCR-000425 | NCR | Panel S16_Sonic Logging Anomaly |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-30 | 2013-04-30 23:35 | 0 | 2012-11-25 | Structural Engineering - Diaphragm Walls | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Panel S16C- An anomaly was identified during sonic logging works by __. Profiles 2-3, 3-4, 4-1, 1-3 & 2-4 all show increases in transit times at the base of the panel, the largest increase being 136% on profile 3-4, over a vertical extent of 600mm. Please see attached APPENDIX for full report.
| 03SR - Stations (RfL) | Cxxx-NCR-000426 | NCR | Panel S29_Sonic Logging Anomaly |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-30 | 2013-04-30 23:30 | 0 | 2012-11-25 | Structural Engineering - Diaphragm Walls | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Panel S29- An anomaly was identified during sonic logging works by __. Profile 1-2 shows an increase in transit time of approximately 65% at the base of the profile, over a vertical extent of 400mm. Please see attached APPENDIX for full report.
| 03SR - Stations (RfL) | Cxxx-NCR-000427 | NCR | Panel S33_Sonic Logging Anomaly |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-30 | 2013-04-30 23:22 | 0 | 2012-11-25 | Structural Engineering - Diaphragm Walls | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Panel S33- An anomaly was identified by __ during sonic logging work. Profiles 2-3, 3-4 & 1-3 all show increases in transit time at the base of the panel, the largest increase being 93.5% on profile 3-4, over a vertical extent of approximately 400mm. Please see attached APPENDIX for full report.
| 03SR - Stations (RfL) | Cxxx-NCR-000428 | NCR | Panel S53_Sonic Logging Anomaly |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-30 | 2013-04-30 23:16 | 0 | 2012-11-25 | Structural Engineering - Diaphragm Walls | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Panel S53- An anomaly was identified during the sonic logging work by __. Profiles 1-2, 4-1 and 1-3 all show increases in transit times at the base of the panel, the largest increase being 37.5% on profile 1-2 over a vertical extent of approximately 300mm. Please see attached APPENDIX for full report.
| 03SR - Stations (RfL) | Cxxx-NCR-000429 | NCR | Panel S63C_Sonic Logging Anomaly |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-30 | 2013-04-30 23:11 | 0 | 2012-11-25 | Structural Engineering - Diaphragm Walls | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Panel S63C- An anomaly was identified during sonic logging works by __. Profile 1-2 shows an increase in transit time at the base of the profile over a vertical extent of 500mm. Please see attached APPENDIX for full report.
| 03SR - Stations (RfL) | Cxxx-NCR-000430 | NCR | Panel S74_Sonic Logging Anomaly |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-30 | 2013-04-30 23:06 | 0 | 2012-11-25 | Structural Engineering - Diaphragm Walls | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Panel S74- An anomaly was identified by __ during sonic logging works. Profile 1-2 shows an increase in transit time of 42% approximately 700mm from the base of the panel, over a vertical extent of 200mm. Please see attached APPENDIX for full report.
| 03SR - Stations (RfL) | Cxxx-NCR-000431 | NCR | Panel E02_Sonic Logging Anomaly |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-30 | 2013-04-30 23:01 | 0 | 2012-11-25 | Structural Engineering - Diaphragm Walls | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Panel E02- An anomaly was identified by __ during sonic logging works. Profile 3-4 show an increase in transit time of 37% approximately 1m from the base of the panel, over a vertical extent of 200mm. Please see attached APPENDIX for full report.
| 03SR - Stations (RfL) | Cxxx-NCR-000432 | NCR | Panel N2_Sonic Logging Anomaly |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-30 | 2013-04-30 22:56 | 0 | 2012-11-25 | Structural Engineering - Diaphragm Walls | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Panel N02- An anomaly was identified during sonic logging works by __. Profiles 1-2 & 3-4 show an increase in transit time at the base of the panel, the largest increase being 155% on profile 1-2, over a vertical extent of approximately 300mm. Please see attached APPENDIX for full report.
| 03SR - Stations (RfL) | Cxxx-NCR-000433 | NCR | Panel N4_Sonic Logging Anomaly |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-30 | 2013-04-30 22:51 | 0 | 2012-11-25 | Structural Engineering - Diaphragm Walls | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Panel N04- An anomaly was identified by __ during sonic logging works. Profile 1-2 shows an increase in transit time of 104% approximately 400mm from the base of the panel, over a vertical extent of 400mm. Please see attached APPENDIX for full report.
| 03SR - Stations (RfL) | Cxxx-NCR-000434 | NCR | Panel N5_Sonic Logging Anomaly |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-30 | 2013-04-30 22:44 | 0 | 2012-11-25 | Structural Engineering - Diaphragm Walls | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Panel N05- An anomaly was identified during sonic logging works by __. Profiles 1-2, 3-4, 4-1, 1-3 and 2-4 all show increases in transit times at the base of the panel, the largest increase being 75.4% on profile 3-4 over a vertical extent of approximately 300mm. As these increases are not present on the remaining profile, the increases are likely to be the result of localised features in the vicinity of tubes 1 and 4 and not considered to be of any significance in terms of panel integrity. Further increases in transit times are shown on profile 1-2 extending to 800mm from the base of the panel. As these are not repeated on the remaining profiles, can be considered localised in nature with no significance in terms of panel integrity. All other areas tested show sound and homogeneous concrete throughout. Please see attached APPENDIX for full report.
| 03SR - Stations (RfL) | Cxxx-NCR-000435 | NCR | Panel N71_Sonic Logging Anomaly |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-30 | 2013-04-30 22:38 | 0 | 2012-11-25 | Structural Engineering - Diaphragm Walls | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Panel N71- An anomaly was identified by __ during sonic logging works. Profile 3-4 shows an increase in transit time of 152.8% at the base of the profile over a vertical extent of 500mm. Please see attached APPENDIX for full report.
| 03SR - Stations (RfL) | Cxxx-NCR-000436 | NCR | Panel N79_Sonic Logging Anomaly |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-30 | 2013-04-30 22:33 | 0 | 2012-11-25 | Structural Engineering - Diaphragm Walls | 500 |  | Material | Rework |  | Complete |  | Completed |  | Panel N79- Profiles 1-2 & 3-4 show an increase in transit time at the base of the panel, the largest increase being 131.4% on profile 3-4, over a vertical extent of approximately 300mm. Please see attached APPENDIX for full report.
| 03SR - Stations (RfL) | Cxxx-NCR-000437 | NCR | Panel N18_Sonic Logging Anomaly |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-30 | 2013-04-30 22:28 | 0 | 2012-11-25 | Structural Engineering - Diaphragm Walls | 500 |  | Material | Rework |  | Complete |  | Completed |  | Anomaly identified on sonic logging testing by __ on site visit 12 on panel N18. Profile1-2 shows an increase in transit time of 100% at the base of the profile, over a vertical extent of 300mm. Please see attached APPENDIX for full report.
| 03SR - Stations (RfL) | Cxxx-NCR-000438 | NCR | Panel S43_Sonic Logging Anomaly |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-30 | 2013-04-30 22:14 | 0 | 2012-11-25 | Structural Engineering - Diaphragm Walls | 500 |  | Material | Rework |  | Complete |  | Completed |  | Anomaly identified on sonic logging testing by __ on site visit 12 on panel S43. Profile 1-2 shows an increase in transit time of 44.3% at approximately 87.5m AOD, over a vertical extent of 200mm. Please see attached APPENDIX for full report.
| 03SR - Stations (RfL) | Cxxx-NCR-000439 | NCR | Panel S56_Sonic Logging Anomaly |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-30 | 2013-04-30 22:21 | 0 | 2012-11-25 | Structural Engineering - Diaphragm Walls | 500 |  | Material | Rework |  | Complete |  | Completed |  | Anomaly identified on sonic logging testing by __ on site visit 12 on panel S56. Profiles 1-2 & 3-4 show an increase in transit time at a depth of 87.5m AOD, the largest increase being 25% on profile 3-4, over a vertical extent of approximately 400mm. Please see attached APPENDIX for full report.
| 03SR - Stations (RfL) | Cxxx-NCR-000440 | NCR | Panel S41_Sonic Logging Anomaly |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-30 | 2013-04-30 22:12 | 0 | 2012-11-25 | Structural Engineering - Diaphragm Walls | 500 |  | Material | Rework |  | Complete |  | Completed |  | Anomaly identified on sonic logging testing by __ on site visit 13 on 14th Nov on panel S41. Profiles 1-2 & 3-4 show an increase in transit time at the base of the panel, the largest increase being 95.3% on profile 1-2, over a vertical extent of approximately 200mm. Please see Appendix for the Report.
| 03SR - Stations (RfL) | Cxxx-NCR-000441 | NCR | 56 day Identity Testing |  | Contr |  | PAD - Paddington Station (West) |  | 2013-01-31 | 2012-12-16 10:23 | -46 | 2012-11-25 | Structural Engineering - Diaphragm Walls | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | On occasion, (See APPENDIX), the frequency for 56 day testing has reduced to below that in the ITP, with two sets of 56 day results having a greater concrete volume than 500m3 poured between them.
| 03SR - Stations (RfL) | Cxxx-NCR-000443 | NCR | Panel S35_Sonic Tube Blockage |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-11-01 | 2013-10-22 12:10 | -10 | 2012-11-25 | Structural Engineering - Diaphragm Walls | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Panel S35 was found to have a blockage in its sonic logging tube upon testing by __. S35 was flushed on the 19/10/12 and the flushing report shows that this blockage was identified. It was tested on the 30/10/12 in order to have data obtained for this panel in the 7-21 day test window. Only 3 full depth profiles were able to be obtained due to a blockage in tube 3 approximately 4.5m below top of tube level. All areas tested showed sound and homogenous concrete throughout. See APPENDIX for report.
| 03SR - Stations (RfL) | Cxxx-NCR-000444 | NCR | Panel S51: Cube Strength |  | Contr |  | PAD - Paddington Station (West) |  | 2013-01-31 | 2013-01-11 16:56 | -20 | 2012-11-25 | Structural Engineering - Diaphragm Walls | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Panel S51 - one set of cubes results (S1188955) had one cube at a strength of 37.1N/mm2 and one of 37.2N/mm2 at 28 days. The average for the pair of results was 37.2N/mm2 which is below the PASS criteria of 41N/mm2 for an individual result.
| 03SR - Stations (RfL) | Cxxx-NCR-000445 | NCR | Panel S57_Bentonite |  | Contr |  | PAD - Paddington Station (West) |  | 2013-01-31 | 2013-01-11 16:58 | -20 | 2012-11-25 | Structural Engineering - Diaphragm Walls | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Please see attached Appendix for the full set of bentonite testing data. In the second set of betonite test the marsh cone result was 53.8 seconds, which is above the 50 seconds limit for bentonite after airlift as stated in the accepted D Wall ITP rev6.
| 03SR - Stations (RfL) | Cxxx-NCR-000446 | NCR | Panel S30_Tremmie Embedment Exceeds 9m |  | Contr |  | PAD - Paddington Station (West) |  | 2013-01-31 | 2012-12-16 10:30 | -46 | 2012-11-25 | Structural Engineering - Diaphragm Walls | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Please see attached Appendix for the tremmie graph for panel S30. At 5 locations, as marked in the Appendix, the maximum tremmie embedment exceeded 9m limit. The reinforcement cage was installed to the correct level.
| 03SR - Stations (RfL) | Cxxx-NCR-000447 | NCR | Panel S64_Concrete Timing |  | Contr |  | PAD - Paddington Station (West) |  | 2013-01-31 | 2012-12-11 17:10 | -51 | 2012-11-25 | Structural Engineering - Diaphragm Walls | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | When concreting panel S64, the following 1 no. Loads of concrete exceeded the 2hr limit on duration between batching and end of pour. Reference Ticket 683796 (2hr 15min duration)
| 03SR - Stations (RfL) | Cxxx-NCR-000448 | NCR | Panel N13_Sonic Logging Anomaly |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-30 | 2013-04-30 22:05 | 0 | 2012-11-25 | Structural Engineering - Diaphragm Walls | 500 |  | Material | Rework |  | Complete |  | Completed |  | During sonic logging works by __, an anomaly was identified on panel N13: Profile 3-4 shows an increase in transit time of 74.2%, approximately 200mm from the base of the panel, over a vertical extent of 250mm. Please see attached APPENDIX for full report.
| 03SR - Stations (RfL) | Cxxx-NCR-000449 | NCR | Panel S49: Panel Construction Time |  | Contr |  | PAD - Paddington Station (West) |  | 2013-01-31 | 2013-01-09 15:35 | -22 | 2012-11-25 | Structural Engineering - Diaphragm Walls | 500 |  | Equipment Breakdown | Use As-Is |  | Complete |  | Completed |  | The construction of panel S49 has passed the 120 hour (5 day) time limit for construction - commencement of excavation to completion of concreting. The actual time taken was 138hours. Panel excavation started at 23:00 27/10/2012, Last pass of grab happened at 01:09 02/11/2012 and the End of Concreting at 16:45 02/11/2012. Please note the duration between last pass of grab and end of concreting was 15hr 36mins (< 24hr). Reason for this occurrence: the D-Wall rig experienced a breakdown due to a faulty cable and stood from 04:30 28-10-12 until 19:00 29-10-12. A total of 38.5 hrs were lost.
| 03SR - Stations (RfL) | Cxxx-NCR-000450 | NCR | Panel N05: Panel Construction Time |  | Contr |  | PAD - Paddington Station (West) |  | 2013-01-31 | 2013-01-09 15:23 | -22 | 2012-11-25 | Structural Engineering - Diaphragm Walls | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The construction of panel N05 has passed the 120 hour (5 day) time limit for construction - commencement of excavation to completion of concreting. The actual time taken was 147.5hours. Panel excavation started at 15:00 05/09/2012, Last pass of grab happened at 21:35 10/09/2012 and the End of Concreting at 18:15 11/09/2012. Please note the duration between last pass of grab and end of concreting was 20hr 40mins (< 24hr). Reason for this occurrence: Problems were encountered when removing the stop end which caused the delay. The stop end extraction took a total of 41hrs.
| 03SR - Stations (RfL) | Cxxx-NCR-000451 | NCR | Panel S67_Concrete Timings |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-12-31 | 2014-12-18 15:26 | -13 | 2012-11-25 | Structural Engineering - Diaphragm Walls | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Panel S67; the duration between batching and end of pour of 2 loads of concrete exceeded 2hours; Reference Ticket No: 705156 (2hr 43min); 705157 (3hr 21min).
| 03SR - Stations (RfL) | Cxxx-NCR-000452 | NCR | Panel E04_Concrete Timings |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-12-31 | 2014-07-17 09:28 | -167 | 2012-11-25 | Structural Engineering - Diaphragm Walls | 1500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | The first three loads of concrete for Panel E04, on 5th Oct, exceeded two hours from the addition of water to cement at batching plant to completion of pour. Concrete tickets 705216, 705217 & 705218 with actual batching to end of pour durations of 5hr 28mins, 5hr 8mins, 5hr 29mins respectively. Reason for occurrence: The concrete was provisionally booked for 19:30. It is believed the concrete was despatched without official confirmation before the panel could be made ready for concreting. __ have been made aware of the breakdown in procedure and concrete is not to be batched until confirmation is received from the site supervisor / shift manager.
| 03SR - Stations (RfL) | Cxxx-NCR-000453 | NCR | Panel W4_Sonic Tube Blockage |  | Contr |  | PAD - Paddington Station (West) |  | 2014-12-30 | 2014-02-14 13:57 | -319 | 2012-11-25 | Structural Engineering - Structural Engineering - General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | Panel W4 was cast on 8/9/12. It was due to be tested within the expected 7-21 day test window. This was not possible due to the top of the panel being backfilled and buried under the hall road. When tested on the 14/10/12, W4a was found to have a blockage in tube 1 approximately 700mm from the base of the toe and a blockage in tube 4 above cut off level. All areas tested below cut off level showed sound and homogenous concrete throughout. W4b - only 3 full depth profiles available due to a blockage in tube 1 at pile cut off level. All areas tested showed sound and homogenous concrete throughout. W4b tube 4 and W4b tube 1 are the same tubes. Therefore there are a total of 2no. blockages in this panel. See APPENDIX for sonic reports.
| 03SR - Stations (RfL) | Cxxx-NCR-000458 | NCR | Panel S67_Sonic Logging Anomaly |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-30 | 2013-04-30 21:57 | 0 | 2012-11-27 | Structural Engineering - Diaphragm Walls | 500 |  | Material | Rework |  | Complete |  | Completed |  | Panel S67- An anomaly was identified by __ during the sonic logging works. Profiles 1-2 and 3-4 show an increase in transit time at the base of the panel, the largest increase being 43.4% on profiles 1-2 over a vertical extent of approximately 200mm. Please see attached APPENDIX for full report.
| 03SR - Stations (RfL) | Cxxx-NCR-000461 | NCR | Instrumentation installed at C7 and C12 clash with EB TBM |  | Contr |  | PAD - Paddington Station (West) |  | 2013-03-28 | 2013-03-26 13:10 | -2 | 2012-11-29 | Surveying - Instrumentation and Monitoring | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | Plan position and verticality such that they will potentially clash with tunnel alignment
| 03SR - Stations (RfL) | Cxxx-NCR-000462 | NCR | Panel S25_Sonic Tube Blockage |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-11-01 | 2013-10-25 12:03 | -7 | 2012-11-29 | Structural Engineering - Diaphragm Walls | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Panel S25 - Only three full length sonic logging profiles were achieved due to a blockage in sonic logging tube 2, approximately 6.5m from the top of the tube level (earlier NCR: PAD-CRL-NCR-Cxxx-00264 refers). Please see attached APPENDIX for full report. S25 was first tested on the 10/7 and a blockage identified. This was drilled out. A re-test was planned on the 27/09 but the panel could not be tested due to access issues – type 1 backfilling had been put in place. When the panel was uncovered and access given for visits 8 and 9, one of tubes (Tube 4) that were exposed was heavily damaged and unable to be logged - See attached photos. It is currently not possible to log this panel with tube 4 in this condition.
| 03SR - Stations (RfL) | Cxxx-NCR-000463 | NCR | Panel S15_Sonic Tube Blockage |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-11-01 | 2013-10-22 12:21 | -10 | 2012-11-29 | Structural Engineering - Diaphragm Walls | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Panel S15 - Only three sonic logging profiles due to a blockage at the top of sonic logging tube 2. Of these profiles only 1 was to full depth due to a blockage in tube 3, approximately 0.5m from the base of the panel (previous NCR Pad-CRL-NCR-Cxxx-00264 refers). See APPENDIX.pdf. S15 was first tested on the 31/07 in visit 4. 15A passed and 15B required a retest due to signal issues. On retest on visit 5 there was a blockage identified at the top of tube 2, and a blockage at 0.5m from the base in tube 3. This was then drilled out. Further re-test was planned in visit 8 but was not possible due to access issues as a result of backfilling. When the panel was available in visit 9 , the exposed tubes were damaged and blockages found the following S15B tube conditions: Tube 1 was cut off at cast level heavily damaged not possible for testing, Tube 2 was blocked at 1.5m from top of tube, Tube 3 – blocked at 1.8m from top of tube. Tube 4 had no issues. Attached is original sonic logging report in APPENDIX 2 to full depth. The originally submitted APPENDIX contains the second retest where the original blockage was identified.
| 03SR - Stations (RfL) | Cxxx-NCR-000466 | NCR | Excavation Backfill |  | Contr |  | PAD - Paddington Station (West) |  | 2013-01-31 | 2012-12-16 11:55 | -46 | 2012-11-29 | Civil - Fill | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | The excavation to remove the conflicting section of egg sewer for Plunge Column P2 was backfilled using methods outside of the control of the methodology detailed in SNC-109 to WPP-166 CRL ref: Cxxx-SKC-C-CCN-B071_WS077-50110. The excavation was backfilled at night by an excavator driver without adequate engineering supervision. The backfilling was conducted during a period of heavy rainfall and once complete, soft spots were identified at surface level.
| 03SR - Stations (RfL) | Cxxx-NCR-000468 | NCR | Panel N22 Out Of Tolerance Bars |  | Contr |  | PAD - Paddington Station (West) |  | 2013-01-31 | 2013-01-29 13:14 | -2 | 2012-12-05 | Structural Engineering - Diaphragm Walls | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | In panel N22 the inner near face of middle cage (Cxxx-SKC-C-DWG-B071_WS077-50281) consisting of Bar Mark 03 were out of positional tolerance by up to 55mm (105mm from theoretical minus 50 mm vertical position tolerance = 55m) This is detailed in the cage dimension check sheet as a part of panel record and in the attached sketch.
| 03SR - Stations (RfL) | Cxxx-NCR-000469 | NCR | Panel S63: Panel Construction Time |  | Contr |  | PAD - Paddington Station (West) |  | 2013-02-28 | 2013-02-04 17:21 | -24 | 2012-12-05 | Structural Engineering - Diaphragm Walls | 500 |  | Planning | Rework |  | Complete |  | Completed |  | For panel S63, commencement of excavation of the panel was on the 25/07/2012 at 22:20, with the end of concrete pour for the panel at 22:45 on the 01/08/2012. The time between the start of excavation and end of concrete pour was therefore 168hours and 25minutes, in excess of the 120hours limit. Additionally the 24hr rule between the last pass of the grab and end of concrete pour was greater than 24hours (as raised separately in PAD-CRL-NCR-Cxxx-00377). Reason for this occurrence: This panel is a 3-bite larger cranked panel and as a result the time for excavation and cage installation/concrete pour is increased significantly.
| 03SR - Stations (RfL) | Cxxx-NCR-000471 | NCR | Panel S63_Tremmie Embedment Exceeds 9m |  | Contr |  | PAD - Paddington Station (West) |  | 2013-02-28 | 2013-01-09 14:54 | -50 | 2012-12-05 | Structural Engineering - Diaphragm Walls | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | During the concrete pour of panel S63, on two occasions the tremmie embedment exceeded 9.0m and was recorded at 9.4m. The tremmie graph is not strictly speaking accurate as the concrete was poured with 2 tremmies and the concrete level indicated is an average of the levels recorded at the 2 tremmies each after a load of concrete was discharged. Reason for occurrence: It is not known why the tremmie embedment exceeded 9.0m, however the tremmie would only be split after a load of concrete has been discharged into it, and in this time the concrete level would have risen twice as much as normal - approximately 4.0m. It could be that the tremmie could not be split (a 3.0m length removed) with the embedment at 5.9m or less as this would result in less than 3.0m embedment. Therefore a further two loads of concrete were required to be discharged before removing a 3.0m section.
| 03SR - Stations (RfL) | Cxxx-NCR-000479 | NCR | Grout sampling for compressive strength testing 2 |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-19 | 2013-03-26 15:50 | -24 | 2012-12-07 | Surveying - Instrumentation and Monitoring | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | Grout was sampled and moulded in a way that did not enable a standard compressive strength test to be undertaken.
| 03SR - Stations (RfL) | Cxxx-NCR-000480 | NCR | Grout sampling for compressive strength testing 2 |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-19 | 2013-03-21 18:06 | -29 | 2012-12-07 | Surveying - Instrumentation and Monitoring | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | Grout was sampled and moulded in a way that did not enable a standard compressive strength test to be undertaken. This condition applies to rod extensometers referenced Cxxx-RE [CS-03, CS-01, CS-04]; magnetic extensometers Cxxx-ME [C7-04,C12-05, C20-06]; piezometers Cxxx-PE [ C12-02,C7-01, C20-03, C12-08, C7-01A, C20-09].
| 03SR - Stations (RfL) | Cxxx-NCR-000481 | NCR | Instrumentation pre-installation survey |  | Contr |  | PAD - Paddington Station (West) |  | 2013-02-08 | 2013-01-09 14:45 | -30 | 2012-12-07 | Surveying - Instrumentation and Monitoring | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Photographic records were not provided for the following installations: Rod extensometers Cxxx-RE-[CT-07, CS-03, CS-01, CS-04]; Magnetic extensometers Cxxx-ME- [C7-04, C12-05, C20-06]; Piezometers Cxxx-PE-[C12-02, C7-01,C20-03, C12-08, C7-01A, C20-09].
| 03SR - Stations (RfL) | Cxxx-NCR-000486 | NCR | Contractors database |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2013-09-25 | 2013-10-01 11:56 | 6 | 2012-12-13 | Surveying - Instrumentation and Monitoring | 2000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | The database specification has not been submitted to the Project manager for acceptance and does not allow for the direct comparison of monitoring data, trigger values and construction progress records. Therefore the database does not accord with the requirements of the Works Information
| 03SR - Stations (RfL) | Cxxx-NCR-000487 | NCR | Damaged inclinometer tube E4-06 in panel N8 |  | Contr |  | PAD - Paddington Station (West) |  | 2013-05-21 | 2013-05-13 18:13 | -8 | 2012-12-14 | Surveying - Instrumentation and Monitoring | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | Top of the casing has been bent flat by the guide wall breakdown works.
| 03SR - Stations (RfL) | Cxxx-NCR-000488 | NCR | Inaccurate reading and presentation of Inclinometer data |  | Contr |  | PAD - Paddington Station (West) |  | 2013-01-31 | 2013-01-29 13:12 | -2 | 2012-12-16 | Surveying - Instrumentation and Monitoring | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | The data obtained from both in-ground and in-wall inclinometers is read and presented incorrectly. there is no apparent quality control on the data read from the instrumentation and adjustments are not being inmplemented as is normal practice. The extent of the problem is widespread and has included inclinometers showing no deflection when deflection is expected, to inclinometers showing significant deflection when no deflection is expected.
| 03SR - Stations (RfL) | Cxxx-NCR-000489 | NCR | Temporary works feet for pile cage support |  | Contr |  | PAD - Paddington Station (West) |  | 2012-12-21 | 2013-01-07 17:50 | 17 | 2012-12-16 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The feet have beeen fabricated at 130mmx130mm
| 03SR - Stations (RfL) | Cxxx-NCR-000490 | NCR | Temporary works handrail to south of site not in accordance with deign |  | Contr |  | PAD - Paddington Station (West) |  | 2013-01-14 | 2013-01-18 08:58 | 4 | 2012-12-16 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Reject |  | Complete |  | Completed |  | The first section of handrail was erected in accordance withthe design, but subsequent sections have been erected to an arrangement that has no design in place. this was notified to the temporary works co-ordinator on 10th Dec, inspection on 16th Dec shows that the arrangement of the handrail remains unchanged. This protects operatives from a fall approx 3m and the designed solution also protects those at low level from loose material, which the installed version does not.
| 03SR - Stations (RfL) | Cxxx-NCR-000492 | NCR | Panel S70_Concrete Timing |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-12-31 | 2014-08-13 16:05 | -140 | 2012-12-19 | Structural Engineering - Diaphragm Walls | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Panel S70, concrete ticket 706293, time between batch and end of pour is 3hr 35mins (>3hr); And the time between completion of pour of 706293 and the start of next load of ticket 696781 is 2hr 24mins.
| 03SR - Stations (RfL) | Cxxx-NCR-000493 | NCR | Multiple Panels_Concrete Timing |  | Contr |  | PAD - Paddington Station (West) |  | 2013-02-28 | 2013-01-11 17:02 | -48 | 2012-12-19 | Structural Engineering - Diaphragm Walls | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Panel S63, concrete ticket 704979, time between batch and end of pour is 2hr 41mins (>2hr, however <3hr); Panel E01, concrete ticket 696536, time between batch and end of pour is 2hr 51mins (>2hr, however <3hr); Panel S70, concrete ticket 696782, time between batch and end of pour is 2hr 12mins (>2hr, however <3hr); Panel S75, concrete ticket 705576, time between batch and end of pour is 2hr 8mins (>2hr, however <3hr); Panel S75, concrete ticket 705578, time between batch and end of pour is 2hr 7mins (>2hr, however <3hr); Panel S75, concrete ticket 714128, time between batch and end of pour is 2hr 47mins (>2hr, however <3hr); Panel S75, concrete ticket 705582, time between batch and end of pour is 2hr 7mins (>2hr, however <3hr); Panel S75, concrete ticket 714136, time between batch and end of pour is 2hr 25mins (>2hr, however <3hr);
| 03SR - Stations (RfL) | Cxxx-NCR-000494 | NCR | Panel S22_Bentonite Testing |  | Contr |  | PAD - Paddington Station (West) |  | 2013-02-28 | 2013-01-11 17:00 | -48 | 2012-12-19 | Structural Engineering - Diaphragm Walls | 500 |  |  | Rework |  | Complete |  | Completed |  | Please see attached Appendix 1; bentonite Mash Cone viscosity result is 56.8s > 50s limit.
| 03SR - Stations (RfL) | Cxxx-NCR-000495 | NCR | Panel N14_Sonic Logging Anomaly |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-12-30 | 2014-07-10 12:30 | -173 | 2012-12-19 | Structural Engineering - Diaphragm Walls | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Panel N14 - A sonic logging anomaly was identified by __ during the sonic logging testing - Profile 3-4 shows an increase in transit time of approximately 26% at a depth of 115.7m AOD over a vertical extent of 200mm. Please see attached APPENDIX for full report. Panel retested, please find the attached results
| 03SR - Stations (RfL) | Cxxx-NCR-000496 | NCR | Panel N35_Sonic Logging Anomaly |  | Contr |  | PAD - Paddington Station (West) |  | 2013-06-26 | 2013-05-24 10:22 | -33 | 2012-12-19 | Structural Engineering - Diaphragm Walls | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Panel N35 - A sonic logging anomaly was identified by __ during the sonic logging testing -Profile 3-4 shows an increase in transit time of approximately 65% at the toe of the panel over vertical extent of 300mm. Please see attached APPENDIX for full report. A detail report will be produced
| 03SR - Stations (RfL) | Cxxx-NCR-000497 | NCR | Panel N27_Sonic Tube Blockage |  | Contr |  | PAD - Paddington Station (West) |  | 2013-06-12 | 2013-05-24 10:11 | -19 | 2012-12-19 | Structural Engineering - Diaphragm Walls | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Panel N27 - a blockage was identified during sonic logging testing on panel N27 - Only 3 full depth profiles recorded due to a blockage, approximately 400mm from the base of tube 2. All areas tested show sound and homogeneous concrete throughout. See attached APPENDIX for report.
| 03SR - Stations (RfL) | Cxxx-NCR-000498 | NCR | Panel N34_Sonic Tube Blockage |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-04-01 | 2013-08-05 12:14 | -604 | 2012-12-19 | Structural Engineering - Diaphragm Walls | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Panel N34 - a blockage was identified during sonic logging testing on panel N34 -Only 3 full depth profiles recorded due to a blockage, approximately 400mm from the base of tube 3. All areas tested show sound and homogeneous concrete throughout. See attached APPENDIX for report.
| 03SR - Stations (RfL) | Cxxx-NCR-000503 | NCR | Failure to issue ATS data at prescribed frequency |  | Contr |  | PAD - Paddington Station (West) |  | 2013-02-28 | 2013-02-21 09:02 | -7 | 2012-12-20 | Surveying - Instrumentation and Monitoring | 500 |  | System Defect | Repair |  | Complete |  | Completed |  | The ATS system at Paddington has (as detailed in attached XLS sheet) not met the specification for deliverable data in a timely fashion due to ATS observation obstructions or failures and then subsequent prism array computation failures. Thus data from time of measurement to display/issue as only partially computed was not available fully within the specified epoch. These failures may be caused by metrological conditions, physical obstructions, communications outages or quality of geometry of measured data that cause the computation to fail.
| 03SR - Stations (RfL) | Cxxx-NCR-000507 | NCR | Panel N79 Concrete Discharge time |  | Contr |  | PAD - Paddington Station (West) |  | 2013-01-31 | 2013-01-29 14:01 | -2 | 2012-12-21 | Structural Engineering - Diaphragm Walls | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Ticket 703210 indicates a time lapse of 2hrs 09mins.
| 03SR - Stations (RfL) | Cxxx-NCR-000508 | NCR | Panel N76 Concrete Discharge Delay |  | Contr |  | PAD - Paddington Station (West) |  | 2013-01-31 | 2013-01-29 13:59 | -2 | 2012-12-21 | Structural Engineering - Diaphragm Walls | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Delivery ticket 727398 indicates a time lapse of 2hr 10mins.
| 03SR - Stations (RfL) | Cxxx-NCR-000509 | NCR | Panel N70 Concrete discharge delay |  | Contr |  | PAD - Paddington Station (West) |  | 2013-01-31 | 2013-01-29 13:10 | -2 | 2012-12-21 | Structural Engineering - Diaphragm Walls | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Delivery Ticket 703938 indicates a time lapse of 2hr 07mins.
| 03SR - Stations (RfL) | Cxxx-NCR-000510 | NCR | Panel N68 Concrete discharge delay |  | Contr |  | PAD - Paddington Station (West) |  | 2013-01-31 | 2013-01-29 13:09 | -2 | 2012-12-21 | Structural Engineering - Diaphragm Walls | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Delivery ticket 727105 2hr 01mins, Delivery ticket 703655 2hr 13mins, Delivery ticket 727108 2hr 11mins.
| 03SR - Stations (RfL) | Cxxx-NCR-000511 | NCR | Panel N71 Concrete discharge delay |  | Contr |  | PAD - Paddington Station (West) |  | 2013-01-31 | 2013-01-29 13:07 | -2 | 2012-12-21 | Structural Engineering - Diaphragm Walls | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Delivery ticket 727085 2hr 07mins Delivery ticket 727086 2hr 14mins, Delivery ticket 727087 2hr 18mins, Delivery ticket 727088 2hrv 44mins.
| 03SR - Stations (RfL) | Cxxx-NCR-000516 | NCR | Instrumentation data missing |  | Contr |  | PAD - Paddington Station (West) |  | 2013-02-21 | 2013-02-04 17:37 | -17 | 2013-01-09 | Civil - Geotechnical Engineering | 500 |  | Planning | Rework |  | Complete |  | Completed |  | From the last Monday (7th January 2013), the D-Wall activity was near the Block E MacMillan House, working on the panels N52 and N59, with no reading of these instruments during these two days.
| 03SR - Stations (RfL) | Cxxx-NCR-000517 | NCR | Plunge Column Pile Cage Feet |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-15 | 2013-04-02 10:06 | -13 | 2013-01-09 | Civil - Civil Engineering General | 500 |  | Design | Rework |  | Complete |  | Completed |  | Cage feet fabrication and installation not in accordance with temporary work design certificate Cxxx-SKC-C-ZFM-B071_WS077-50110
| 03SR - Stations (RfL) | Cxxx-NCR-000518 | NCR | P11 Cage Trapping Bracket |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-15 | 2013-04-08 18:05 | -7 | 2013-01-09 | Civil - Civil Engineering General | 500 |  | System Defect | Rework |  | Complete |  | Completed |  | Cage not trapped on 4no brackets as per Cxxx-SKC-C-ZFM-B071_WS077-50110
| 03SR - Stations (RfL) | Cxxx-NCR-000520 | NCR | MacMillan House Basement Wall_Concrete Timings |  | Contr |  | PAD - Paddington Station (West) |  | 2013-02-28 | 2013-02-14 15:00 | -14 | 2013-01-09 | Structural Engineering - Concrete Member | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Placement of concrete for the named pours exceeded two hours from batching to placement and compaction of concrete. (table attached shows durations for all concrete loads for MacMillan House lining wall)
| 03SR - Stations (RfL) | Cxxx-NCR-000521 | NCR | Temporary works loose links site tied within splice zone |  | Contr |  | PAD - Paddington Station (West) |  | 2013-05-23 | 2013-05-08 16:28 | -15 | 2013-01-10 | Civil - Civil Engineering General | 500 |  | Design | Rework |  | Complete |  | Completed |  | loose links of incorrect length
| 03SR - Stations (RfL) | Cxxx-NCR-000522 | NCR | Panel E04_Concrete Timings |  | Contr |  | PAD - Paddington Station (West) |  | 2013-02-28 | 2013-01-14 17:51 | -45 | 2013-01-14 | Structural Engineering - Diaphragm Walls | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Duration between load 705217 and 705218 was 1 hour 6mins, which exceeded 1 hour limit by 6mins.
| 03SR - Stations (RfL) | Cxxx-NCR-000523 | NCR | ATS failure. No data available |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-30 | 2013-02-25 09:40 | -64 | 2013-01-14 | Civil - Geotechnical Engineering | 500 |  | System Defect | Repair |  | Complete |  | Completed |  | Last night there was a failure with the Datum software and the data were not in the webpage for our reference. This information was not available for more than 12 hours. Cxxx didn't get this information either. They were concerned about the missing data and the TBM start-up.
| 03SR - Stations (RfL) | Cxxx-NCR-000524 | NCR | Plunge columns dropping following release of Cemloc |  | Contr |  | PAD - Paddington Station (West) |  | 2013-03-14 | 2013-03-15 13:34 | 1 | 2013-01-14 | Structural Engineering - Steel Member | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The embedded steel column dropped up to 14mm when the trmporary support structure was released suggesting that the concrete had not reached sufficient strength to support the self weight of the column
| 03SR - Stations (RfL) | Cxxx-NCR-000528 | NCR | Panel S62_Sonic Logging Anomaly |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-30 | 2013-04-30 21:49 | 0 | 2013-01-14 | Structural Engineering - Diaphragm Walls | 500 |  | Damaged | Rework |  | Complete |  | Completed |  | Panel S62B has been identified as having an anomaly by __ during sonic logging works. This panel also had a blockage but this is detailed in a separate NCR (see NCR_378). Parts S62C has passed whilst S62A also passes although does have a blockage shared with S62B. See appendices for detailed information of anomaly, contained in this NCR.
| 03SR - Stations (RfL) | Cxxx-NCR-000530 | NCR | Void Former blocked by bentonite |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-05 | 2013-03-13 13:26 | -23 | 2013-01-17 | Civil - Geotechnical Engineering | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | The installation was impossible to carry out because the void former was blocked by bentonite at the depth of 29 m from the top.
| 03SR - Stations (RfL) | Cxxx-NCR-000531 | NCR | Shear studs to plunge columns |  | Contr |  | PAD - Paddington Station (West) |  | 2013-03-31 | 2013-03-26 13:40 | -5 | 2013-01-18 | Structural Engineering - Steel Member | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | The shear studs on the upper columns have not been bend tested. The shear studs that have been bend tested have been bent towards the wrong end of the column On columns P8 and P13 the heads of the 100mm shear studs have been bent up to 70mm ie 70% of the length rather than the specified 25%
| 03SR - Stations (RfL) | Cxxx-NCR-000533 | NCR | Prisms more than maximum specified distance from ATS #2 |  | Contr |  | PAD - Paddington Station (West) |  | 2013-02-01 | 2013-02-13 13:18 | 12 | 2013-01-18 | Surveying - Instrumentation and Monitoring | 500 |  | Design | Rework |  | Complete |  | Completed |  | 3D geodetic prisms installed by Cxxx should have been installed to the specification as noted above. Of the approximate 300 prisms installed almost 13% are over 100m from the ATS, however only 3 No. are over 150m with none over 190m
| 03SR - Stations (RfL) | Cxxx-NCR-000536 | NCR | Tension Pile: Incorrect Concrete Mix |  | Contr |  | PAD - Paddington Station (West) |  | 2013-03-29 | 2013-03-05 10:25 | -24 | 2013-01-21 | Structural Engineering - Diaphragm Walls | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The first 4 loads of concrete placed in Pile No P1 were not the approved mix. The mix used was compliant with the specification but it was not the approved mix. The ticket was checked prior to placement for correct contract (the ticket was directed to __, had the correct strength, and noted that it was a pile mix not a D Wall mix).
| 03SR - Stations (RfL) | Cxxx-NCR-000537 | NCR | Tension Pile: Steel Cage Level |  | Contr |  | PAD - Paddington Station (West) |  | 2013-03-29 | 2013-03-05 10:28 | -24 | 2013-01-21 | Structural Engineering - Concrete Member | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | The pile cage feet were set to have the cage 100mm high which would have been within tolerance. However with the additional variance of the adjustment length on the specified couplers this added a further 100mm to the overall cage length which put the top of steel out of tolerance. The feet were not adjusted as the time taken to do this would of meant the construction time would of greatly exceeded the 12 hr limit.
| 03SR - Stations (RfL) | Cxxx-NCR-000538 | NCR | Tension Pile: Incorrect Steel Ring |  | Contr |  | PAD - Paddington Station (West) |  | 2013-03-29 | 2013-03-05 10:30 | -24 | 2013-01-21 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | The lowe cage section for Pile P7 was manufactured incorrectly with 20mm rings instead of 16mm rings
| 03SR - Stations (RfL) | Cxxx-NCR-000539 | NCR | Tension Pile: Verticality Tolerance |  | Contr |  | PAD - Paddington Station (West) |  | 2013-03-29 | 2013-03-05 10:33 | -24 | 2013-01-22 | Structural Engineering - Steel Member | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The measured verticality on Pile 7 was 1:125, therefore outside the specified 1:150.
| 03SR - Stations (RfL) | Cxxx-NCR-000540 | NCR | Tension Pile: Sonic Tube |  | Contr |  | PAD - Paddington Station (West) |  | 2013-03-29 | 2013-03-21 18:08 | -8 | 2013-01-22 | Surveying - Instrumentation and Monitoring | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | On Pile no 7 one sonic tube, on the upper and sacrificial cage would not meet to be joined. Background: It is unclear if this is a fabrication error, however the procedure is to make the cage in a signle piece and split for delivery, and the fabricators claim this was done on this cage as has been witnessed on previous cages. It may be possible that the upper section of the cage was struck by the 20t excavator the previous evening which could have caused distrotion of the tube.
| 03SR - Stations (RfL) | Cxxx-NCR-000542 | NCR | __ Block Hoarding |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-09-25 | 2013-09-25 17:52 | 0 | 2013-01-22 | Civil - Civil Engineering General | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The __-block hoarding East of GL 24 on the North site boundary is positioned in such a way that the NR fire-escape walkway is less than the contractually required 2.0m in width.
| 03SR - Stations (RfL) | Cxxx-NCR-000545 | NCR | Concrete Biscuit Mix |  | Contr |  | PAD - Paddington Station (West) |  | 2013-03-29 | 2013-02-15 11:00 | -42 | 2013-01-22 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  |  | Rework |  | Complete |  | Completed |  | The biscuit mix approved with the MCR was not the same as that installed on site. The mix proportions however are identical. Background: The concrete supplier did not appreciate that the change in the source of the material required a revised approval.
| 03SR - Stations (RfL) | Cxxx-NCR-000547 | NCR | Tension Pile: Incorrect Steel |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-01 | 2013-02-04 17:27 | -56 | 2013-01-22 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | The top cage of P9 has been fabricated with 1 No link missing. The top cage should have 41 No @ 150mm and 24 No @ 225mm, it has 41 No @ 150mm and 23 No @ 225mm.
| 03SR - Stations (RfL) | Cxxx-NCR-000548 | NCR | Tension Pile: Cage Steel Level |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-01 | 2013-03-05 10:35 | -27 | 2013-01-22 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | The steel level on P8 when installed was 217mm above pile COL and hence 67mm above allowable tolerance. Background:The pile cage feet were set to have the cage 100mm high which would have been within tolerance. However with the additional variance of the adjustment length on the specified couplers this added a further 100mm to the overall cage length which put the top of steel out of tolerance.
| 03SR - Stations (RfL) | Cxxx-NCR-000552 | NCR | Local Overbreak |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-01 | 2013-04-08 17:02 | 7 | 2013-01-23 | Structural Engineering - Diaphragm Walls | 500 |  | System Defect | Repair |  | Complete |  | Completed |  | Please see Appendix 1 for a list of the affected panels, the location of large local overbreak, and whether they are above or below base slab.
| 03SR - Stations (RfL) | Cxxx-NCR-000553 | NCR | Panel_N39: Blocked Sonic Tubes |  | Contr |  | PAD - Paddington Station (West) |  | 2013-05-15 | 2013-04-26 10:47 | -19 | 2013-01-23 | Structural Engineering - Diaphragm Walls | 500 |  | System Defect | Rework |  | Complete |  | Completed |  | During Sonic Logging works by __ on Panel N39 - carried out on site visit 17 on the 09/01/2013 - blockages were identified in some of the sonic logging tubes: Please see __s report: Only 1 full depth profile obtained due to blockages in tubes 2 & 3 at depths of approximately 28.5m & 26.5m below top of tube levels respectively. All areas tested show sound and homogeneous concrete throughout. It is believed that these blockages are not due to inadequate capping as they were all sufficiently capped before and after testing and over the Christmas break. It is possible that the flushing and water filling process may not have been properly followed just before the break for Christmas leaving some of these panels sonic sleeves dry which may have led to this.
| 03SR - Stations (RfL) | Cxxx-NCR-000554 | NCR | Panel_N38: Sonic Tube Blockage |  | Contr |  | PAD - Paddington Station (West) |  | 2013-05-16 | 2013-05-08 16:17 | -8 | 2013-01-23 | Structural Engineering - Diaphragm Walls | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | During Sonic Logging works by __ on Panel N38 - carried out on site visit 17 on the 09/01/2013 - a blockage was identified during testing in tube 3 - approximately 27.8-28m below top of tube level. This blockage was also identified after flushing by __ when tube 3 was depth checked with the use of a weighted tape. This blockage was identified by __ at 28.7m as on the flushing record. Unfortunately due to the blockage a 700mm length of rebar was lost as the tape snapped when the blockage was encountered. REV 1 - After assessment with minipiling rig operator, it was deemed not safe to drill the bottom 400mm of the panel to remove the blcokage for fear of drilling through the base of the panel. Hence the blockage cannot be drilled. INstead the panel was reflsuhed although a blockage remains. It is applied for this NCR to be closed out and panel accpeted as is as all other areas show sound concrete throughout
| 03SR - Stations (RfL) | Cxxx-NCR-000555 | NCR | Panel_N64: Sonic Tube Blockage |  | Contr |  | PAD - Paddington Station (West) |  | 2013-05-22 | 2013-05-08 16:20 | -14 | 2013-01-23 | Structural Engineering - Diaphragm Walls | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | During Sonic Logging works by __ on Panel N64 - carried out on site visit 17 - a blockage was identified in the sonic logging works as follows: Only 3 full depth profiles obtained due to a blockage in tube 3, approximately 31m below top of tube level. All areas tested show sound and homogeneous concrete throughout. This blockage was encountered by __ during their dip check also by a weighted tape - unfortunately a 'dummy probe' used to weight the tape was lost in the tube when the blockage was encountered. It is believed that these blockages are not due to inadequate capping as they were all sufficiently capped before and after testing and over the Christmas break. It is possible that the flushing and water filling process may not have been properly followed just before the break for Christmas leaving some of these panels sonic sleeves dry which may have led to this.
| 03SR - Stations (RfL) | Cxxx-NCR-000556 | NCR | Panel_S49: Water addition after cubes were taken |  | Contr |  | PAD - Paddington Station (West) |  | 2013-05-22 | 2013-05-13 18:27 | -9 | 2013-01-23 | Structural Engineering - Diaphragm Walls | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | 30 litres of water was added to a 7.7c/m load of conrete (727570) for Panel S49, and no cubes were taken by the concrete cube technician.
| 03SR - Stations (RfL) | Cxxx-NCR-000557 | NCR | Panel_N58: Concrete Timings |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-12-31 | 2014-03-27 14:15 | -279 | 2013-01-23 | Structural Engineering - Diaphragm Walls | 500 |  | System Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | ITP Rev 6 and the SPERW (2nd edition) specify the requirement for concrete casting level. 'If the cut-off level is greater than 1m below the top level of the guide walls, concrete shall be brought to 1m above the the cut off level specified, with a tolerance of +/- 150mm. An additional tolerance of of +150mm over the above tolerances shall be permitted for for each 1.0m of depth by which the cut off level is below the top of the guide wall, up to a maximum of 2 m. For panel N58 the last top up load of 3m was placed with a gap of 1 hour and 30 minutes between completion of the prior load and commencement of discharge. The permanent cut off level for this panel is 121.750 A.T.D. The guide wall level is 124.088, therefore the minimum casting level is 122.750 +/- 150mm. This level had already been surpassed with no issues after the placement of 161.7m of concrete to a level of approx 123.188. The , however, require the concrete level to be brought near the top level of the guide wall. This creates problems with the removal of the contaminated bentonite support fluid at this level creating a delay in placing the final top up load that was not required structurally or to comply with Crossrail specificaion or approved ITP
| 03SR - Stations (RfL) | Cxxx-NCR-000558 | NCR | Panel_N32: Sonic Anomaly |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-30 | 2013-04-30 17:40 | 0 | 2013-01-23 | Structural Engineering - Diaphragm Walls | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | For panel N32 - during sonic logging testing by __ - an increase in transit time was identified. - Profile 3-4 shows an increase of 33% approximately 600mm from the toe of the panel over a vertical extent of 150mm.
| 03SR - Stations (RfL) | Cxxx-NCR-000559 | NCR | Panel_N63: Concrete Timings |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-12-31 | 2014-07-04 14:28 | -180 | 2013-01-23 | Structural Engineering - Diaphragm Walls | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | For panel N63, there was more than an hour (1hr 16mins) between discharging of two loads (between load no 19 and 20, of Ticket no: 766519 and 766521). This represents 16mins additinoal time vs 1hr allowance.
| 03SR - Stations (RfL) | Cxxx-NCR-000560 | NCR | Cube Hut Temperature |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-01 | 2013-03-12 18:42 | -20 | 2013-01-23 | Structural Engineering - Diaphragm Walls | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | Please see Appendix 1 for details, during the 4 days listed the temperature of the cube hut fell below specification. This may have minor effect on early age cube strength - affecting test results only. One out of the two electric heater inside the cube hut went missing, apparently during Christmas period, this resulted in a drop in cube hut temperature at night (lowest measured min temperature of 12 degrees).
| 03SR - Stations (RfL) | Cxxx-NCR-000561 | NCR | Panel_N60: Exceedance of 120hour limit |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-01 | 2013-02-28 14:36 | -32 | 2013-01-23 | Structural Engineering - Diaphragm Walls | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | During excavation and construction of Panel N60, the construction time (from first excavation to final concrete) was 134hrs and 22 mins exceeding the allowed maximum of 120hrs. In detail, start of excavation of cut1 started 11/1/13 14:15 and continued to 14.9m depth (approx 109mAD) on 12/1/13 00:52; this followed by a long pause period until the excavation was resumed on 14/1/13 08:45, followed by last pass of grab on 16/1/13 11:00 and end of concrete pour on 17/1/13 03:40. Hence on the top 14.9m in cut1 was exposed to >120hr opening duration by 14.3hrs. __ were instructed by to alter their construction sequence due to a Bentonite leak on Panel N57 and N49. Excavation of N60 was executed earlier than planned under JV instruction (on 11/01/2013 @ 13:05) while the leak on N57 and N49 was addressed. Once the leak was addressed, excavation on N57 and N49 was resumed immediately, leaving N60 open longer than it would have under normal circumstances.
| 03SR - Stations (RfL) | Cxxx-NCR-000562 | NCR | Panel_N36: 24hour limit exceeded |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-01 | 2013-01-29 18:40 | -62 | 2013-01-23 | Structural Engineering - Diaphragm Walls | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | Time between last grab of spoil at base of the panel and final pouring of concrete exceeded the maximum allowed of 24hrs. The was panel was completed in 24hrs and 40mins. In detail: last pass of grab on 29/11/12 09:10, and after 23.5hrs on 30/11/12 08:40 top of concrete reached 3.5m below top of guide wall (approx 120.5mAD) - within the probing disturbance, madeground zone. After which two more loads of concrete was poured to bring the concrete level to 0.8m below top of guidewall, and the end of last pour at 30/11/12 09:50, at 24.6hr after last pass of grab.
| 03SR - Stations (RfL) | Cxxx-NCR-000563 | NCR | Panel_N53: Concrete Timings (1hour) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-12-31 | 2014-07-10 12:31 | -174 | 2013-01-24 | Structural Engineering - Diaphragm Walls | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | For panel N53, there was more than an hour (1hr 34mins) between discharging of two loads (between load no 20 and 21, of Ticket no: 766982 and 766983). This represents 38mins additinoal time vs 1hr allowance. A set of 4no. cubes were taken on each load. The concrete from this load was placed between 5.6m - 2.6m from guide wall level. This occured due to problems with the site pumps used to send bentonite back to the bentointe farm from the panel.
| 03SR - Stations (RfL) | Cxxx-NCR-000564 | NCR | Panel_N53: Concrete Timing (3hours) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-12-31 | 2014-07-10 12:32 | -174 | 2013-01-24 | Structural Engineering - Diaphragm Walls | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | When concreting panel N53, 1 Load of concrete exceeded the 3hr limit on duration between batching and end of pour. It is Ticket 766985 (3hr 37min duration). The concrete from this load was placed between 1.3m - 0.2m from guide wall level, above permanent cut off level.
| 03SR - Stations (RfL) | Cxxx-NCR-000565 | NCR | Panel_N09: Concrete Timings |  | Contr |  | PAD - Paddington Station (West) |  | 2013-02-28 | 2013-01-28 16:59 | -31 | 2013-01-24 | Structural Engineering - Diaphragm Walls | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Panel N09 - Concrete load 7015741 had a delay of 2 hours 6 minutes between batch time and start of discharge. This is outside of the Project Specification KF11.3221 d). This exceeds the 2hour limit by only 6mins. A delay was experienced on site, and although the Shift Supervisor informed the concrete plant but the above load had already been batched and dispatched to site.
| 03SR - Stations (RfL) | Cxxx-NCR-000566 | NCR | Panel_N14: Concrete Timings |  | Contr |  | PAD - Paddington Station (West) |  | 2013-02-28 | 2013-01-28 16:57 | -31 | 2013-01-24 | Structural Engineering - Diaphragm Walls | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | During the concrete pour for panel N14 cast 15/11/12 running into 16/11/12, two no. loads - ticket numbers 730210 and 730211 - exceeded the 2hr limit between batch time and end of pour time. The first instance - 730210 was batched at 00:17 on the 16/11/2012 and was finished being poured into the panel at 02:25 on the 16/11/2012 - a time frame of 2hrs and 8mins, 8 mins in exceedance of the 2hr limit. The second instance - 730211 was batched at 01:03 on the 16/11/2012 and finished its pour at 03:16 on the 16/11/2012 - a time lag of 2hrs and 13mins. This is 13mins exceedance of the 2hr limit.
| 03SR - Stations (RfL) | Cxxx-NCR-000567 | NCR | Panel N12: Concrete Timings |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-04-04 | 2014-01-10 09:59 | -449 | 2013-01-24 | Structural Engineering - Diaphragm Walls | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | When concreting panel N12, the 21st concrete load (Ticket No. 727872) was completed at 02:57 and the 22nd load (Ticket No. 727823) commenced at 04:04. This has exceeded the specified time limit of one hour.
| 03SR - Stations (RfL) | Cxxx-NCR-000568 | NCR | Panel_N53: Exceedance of 120hours |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-02 | 2013-02-28 14:39 | -33 | 2013-01-24 | Structural Engineering - Diaphragm Walls | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | For panel N53, the total construction time was 154hr 24mins > 120hr limit. The excavation started at 16/01/13 12:30; the last pass of grab at 22/01/13 07:30 and the end of concrete pour at 22/01/13 22:54, please note the duration between last pass of grab and end of concreting was 15hr 24min < 24hr limit. The panel was completed as quickly as possible and the 24hr rule was observed. The total construction duration exceeded 120hrs because the site activities stood down during the weekend of 19th and 20th Jan due to unavailible muck away affected by severe snow conditions.
| 03SR - Stations (RfL) | Cxxx-NCR-000576 | NCR | P10 lower plunge column shear stud welding |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-01 | 2013-04-03 10:07 | 2 | 2013-01-30 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | 23 out of 120 shear studs on lower column P10 do not show a full 360 degree collar of weld
| 03SR - Stations (RfL) | Cxxx-NCR-000577 | NCR | Lower plunge column shear stud welding |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-30 | 2013-04-26 11:26 | -4 | 2013-01-30 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Column for P15 was inspected on site and found to have approximately 15 of 120 shear studs not meeting the requirement. Currently awaiting report from Steel Fabricator on condition of columns yet to be delivered
| 03SR - Stations (RfL) | Cxxx-NCR-000585 | NCR | Inadequate loose link lap length |  | Contr |  | PAD - Paddington Station (West) |  | 2013-05-15 | 2013-05-08 16:07 | -7 | 2013-02-04 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Loose links supplied from __ for Piles 4 & 14 are 2300mm length and do not provide adequate lap length
| 03SR - Stations (RfL) | Cxxx-NCR-000586 | NCR | Blocked sonic logging tube P11 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-06-17 | 2013-10-27 16:38 | -233 | 2013-02-04 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | ! no. sonic logging tube in P11 is blocked at 47m
| 03SR - Stations (RfL) | Cxxx-NCR-000591 | NCR | Plunge Column P5 marked north on both faces |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-12 | 2013-04-08 17:59 | -4 | 2013-02-05 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | P5 upper column marked north on both faces
| 03SR - Stations (RfL) | Cxxx-NCR-000592 | NCR | P15 - Duration from boring below cut off to completion of concreting |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-08 | 2013-04-02 09:30 | -6 | 2013-02-07 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Due to high winds preventing the use of cranes for caging up, the time from boring below cut off level to completion of concreting was 36 hours and 35 minutes (ref Cem-Skan-018)
| 03SR - Stations (RfL) | Cxxx-NCR-000593 | NCR | Tremmie trapping bars |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-08 | 2013-02-07 09:50 | -60 | 2013-02-07 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Design | Rework |  | Complete |  | Completed |  | No temporary works design in place for the arrangement used for trapping off the tremmie pipe. (Ref Cem-Skan-019)
| 03SR - Stations (RfL) | Cxxx-NCR-000594 | NCR | P27 reinforcement cage low |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-12-30 | 2014-12-12 17:01 | -18 | 2013-02-07 | Geotechnical Engineering - Concrete - Bored Pile | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | P27 cage is 110mm below design level (ref Cem-Skan-021)
| 03SR - Stations (RfL) | Cxxx-NCR-000595 | NCR | P9 NE sonic tube blocked |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-08 | 2013-04-04 13:01 | -4 | 2013-02-07 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | NE sonic tube on P9 is blocked at 49m by a broken piece of cap. (ref Cem-Skan-021)
| 03SR - Stations (RfL) | Cxxx-NCR-000596 | NCR | P27 sonic tube couplings |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-08 | 2013-04-07 14:40 | -1 | 2013-02-07 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Upper sonic tubes provided without a union coupling. (Ref Cem-Skan-023)
| 03SR - Stations (RfL) | Cxxx-NCR-000597 | NCR | P16 damaged spacers |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-08 | 2013-04-07 14:53 | -1 | 2013-02-07 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | Spacers on P16 were damaged during offloading. (Ref Cem-Skan-024)
| 03SR - Stations (RfL) | Cxxx-NCR-000598 | NCR | P16 time from boring below cut off level to completion of concreting |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-08 | 2013-03-12 18:37 | -27 | 2013-02-07 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | For P16, time from boring below cut off level to completion of concreting was 12 hours 20 minutes (ref Cem-Skan-025)
| 03SR - Stations (RfL) | Cxxx-NCR-000599 | NCR | P16 sonic tube top hat arrangement |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-08 | 2013-04-07 14:56 | -1 | 2013-02-07 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Top hats on sacrificial cage for P16 did not allow sufficent movement to install the cage. (Ref Cem-Skan-026)
| 03SR - Stations (RfL) | Cxxx-NCR-000600 | NCR | Column for P36 cut short |  | Contr |  | PAD - Paddington Station (West) |  | 2013-05-22 | 2013-05-13 18:23 | -9 | 2013-02-07 | Structural Engineering - Steel Member | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Flange plates cut 160mm short. Web cut to correct length. (Ref CB-001)
| 03SR - Stations (RfL) | Cxxx-NCR-000601 | NCR | P21 shear stud welding |  | Contr |  | PAD - Paddington Station (West) |  | 2013-05-22 | 2013-04-26 12:18 | -26 | 2013-02-07 | Structural Engineering - Steel Member | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | A NUMBER OF 100 X 25MM STUDS WERE FOUND TO HAVE INSUFFICIENT WELD/ PENTRATION ON THE WELD COLLARS (ref CB-002)
| 03SR - Stations (RfL) | Cxxx-NCR-000602 | NCR | P15 lower column shear stud welding |  | Contr |  | PAD - Paddington Station (West) |  | 2013-05-22 | 2013-05-08 16:04 | -14 | 2013-02-07 | Structural Engineering - Steel Member | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | 79 100 X 25MM STUDS WERE FOUND TO HAVE INSUFFIENT WELD/ PENETRATION AROUND THE WELD COLLAR (ref CB-003)
| 03SR - Stations (RfL) | Cxxx-NCR-000603 | NCR | Shear stud welding - P42, P47, P50, P51 |  | Contr |  | PAD - Paddington Station (West) |  | 2013-05-22 | 2013-05-08 16:03 | -14 | 2013-02-07 | Structural Engineering - Steel Member | 500 |  |  | Repair |  | Complete |  | Completed |  | THE FOLLOWING COLUMNS HAD INSUFFICIENT WELD/PENETRATION AROUND THE WELD COLLARS P51 - 6 STUDS, P42 -13 STUDS,P47 - 12 STUDS, P50 - 19 STUDS. (ref CB-004)
| 03SR - Stations (RfL) | Cxxx-NCR-000604 | NCR | Shear stud welding - P49, P17, P31, P27 |  | Contr |  | PAD - Paddington Station (West) |  | 2013-05-22 | 2013-05-08 16:01 | -14 | 2013-02-07 | Structural Engineering - Steel Member | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | THE FOLLOWING COLUMNS HAD INSUFFICIENT WELD/ PENETRATION AROUND 100 X 25MM STUD COLLARS P49 -27 STUDS, P17 -8 STUDS,P31 -13 STUDS,P27 -21 STUDS (ref CB-005)
| 03SR - Stations (RfL) | Cxxx-NCR-000605 | NCR | Shear stud welding P28, P38, P7, P23 |  | Contr |  | PAD - Paddington Station (West) |  | 2013-05-22 | 2013-05-08 15:59 | -14 | 2013-02-07 | Structural Engineering - Steel Member | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | THE FOLLOWING COLUMNS HAVE INSUFFICIENT WELD/ PENETRATION ON THE 100X25MM STUDS. P28 -6 STUDS,P38 -7 STUDS,P7 -9 STUDS,P23 -18 STUDS (ref - CB-006)
| 03SR - Stations (RfL) | Cxxx-NCR-000606 | NCR | Shear stud welding P30, P45, P33, P24 |  | Contr |  | PAD - Paddington Station (West) |  | 2013-05-22 | 2013-05-21 18:29 | -1 | 2013-02-07 | Structural Engineering - Steel Member | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | THE FOLLOWING COLUMNS HAVE INSUFFICIENT WELD/PENTRATION ON THE 100X25MM STUDS, P30 -14 STUDS, P45 -5 STUDS, P33 -8 STUDS, P24 -2 STUDS (ref CB-007)
| 03SR - Stations (RfL) | Cxxx-NCR-000607 | NCR | Spray paint on reinforcement cage for P22 |  | Contr |  | PAD - Paddington Station (West) |  | 2013-05-01 | 2013-04-29 16:19 | -2 | 2013-02-07 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Paint on one bar within the cage (ref Cem-Skan-027)
| 03SR - Stations (RfL) | Cxxx-NCR-000619 | NCR | In-ground instruments damage & blockages |  | Contr |  | PAD - Paddington Station (West) |  | 2013-06-15 | 2013-06-11 17:40 | -4 | 2013-02-11 | Geotechnical Engineering - Geotechnical Engineering - General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | The following in-ground instruments were not being monitored or does not provide consistent data due to damage & blockages from construction activities. Blocked Inclinometers: A5-25, A7-27, A8-32, A9-36 - Last 0.5m blocked A12-09 - Last 1m blocked E15-07 & A1-02 - Filled with bentonite (approximately 20m) A12-09 - Last 1m blocked Blocked Extensometer: C20-06 - Last 1m blocked Damaged inclinometers: C24-21 - Broken casing E4-06 - Damaged Peizometer C20-09 cable severed
| 03SR - Stations (RfL) | Cxxx-NCR-000620 | NCR | P17 - damaged spacers |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-12 | 2013-04-08 16:49 | -4 | 2013-02-11 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | Spacers on P17 damaged during offloading
| 03SR - Stations (RfL) | Cxxx-NCR-000622 | NCR | ATS data not available for review due to Cyber Attack on Geomos System |  | Contr |  | PAD - Paddington Station (West) |  | 2013-03-08 | 2013-03-08 13:12 | 0 | 2013-02-12 | Surveying - Instrumentation and Monitoring | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | Due to cyber attack (on 08/02/2013 evening) in the Geomos system, the ATS data is not uploaded in the website for review. All cycles has been observed and are being restored at present.
| 03SR - Stations (RfL) | Cxxx-NCR-000629 | NCR | P23 - Spray paint on reinforcement bar |  | Contr |  | PAD - Paddington Station (West) |  | 2013-10-05 | 2013-06-17 18:20 | -110 | 2013-02-13 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | 1 main bar in P23 sprayed full length - spray used to show orientation of cage for rejoining. (REF CEM-SKAN-029)
| 03SR - Stations (RfL) | Cxxx-NCR-000636 | NCR | Blockage of sonic tubes in P15,P17 and P21 |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-20 | 2013-04-19 14:32 | -1 | 2013-02-21 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | All four sonic tubes in P15 are blocked at a depth of 6m, tubes 1 and 2 in P17 are blocked at 6m and all four tubes in P21 are blocked at 9m. It is believed that the tubes have detached at joints (sections are in 3m lengths) during the extraction of the temporary casing due to the granite backfill gripping the tubes. (ref Cem-Skan-031)
| 03SR - Stations (RfL) | Cxxx-NCR-000637 | NCR | Spray paint on reinforcement cages for piles P18 and P29 |  | Contr |  | PAD - Paddington Station (West) |  | 2013-05-30 | 2013-05-10 09:07 | -20 | 2013-02-20 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | The top links on each of the reinforcement cages was sprayed with paint. Paint has been scoured with wire brush (ref Cem-Skan-032)
| 03SR - Stations (RfL) | Cxxx-NCR-000638 | NCR | P18 reinforcement cage low |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-20 | 2013-04-08 16:36 | -12 | 2013-02-20 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | P18 cage is 330mm below design level (ref Cem-Skan-033)
| 03SR - Stations (RfL) | Cxxx-NCR-000639 | NCR | Panel N32 verticality |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-01 | 2013-04-08 16:33 | 7 | 2013-02-21 | Structural Engineering - Diaphragm Walls | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | For panel N32, at 107.2mAD (16.8m bGW; tunnel centre line) allowed deviatin of 16800/200=84mm; Measured deviation is approximately 98mm > 84mm by 15mm. Panel kicking outwards from the excavation, on impact on internal space, and TBM passed without reported clash issue. Please see attached Appendix for rig print out
| 03SR - Stations (RfL) | Cxxx-NCR-000640 | NCR | Panel N52 Cube testing regime |  | Contr |  | PAD - Paddington Station (West) |  | 2015-04-04 | 2013-04-02 10:17 | -732 | 2013-02-21 | Structural Engineering - Diaphragm Walls | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | Necessity to test at 14 days - but although the 28 day compliance has been sacrificed for this set, 2 cubes remain to be tested at 56 days for the set. This will prove adequate strength for the set, and also allow compliance of the 56 day test regime (which is spread across numerous panels) to be obeyed.
| 03SR - Stations (RfL) | Cxxx-NCR-000641 | NCR | Sonic logging testing N63 |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-30 | 2013-04-30 21:11 | 0 | 2013-02-21 | Structural Engineering - Diaphragm Walls | 500 |  |  | Rework |  | Complete |  | Completed |  | For panel N63, see appendix for data, profile 1-2 shows an increase in transit time of 27.9% at approx 1m above toe, over a vertical extent of 200mm. Profile 3- 4 shows an increase in transit time of 18.8% at approx 120mAD over a vertical extent of 250mm. These increases are not repeated on other profiles and are considered as localised features with no significance in terms of panel integrity. All other areas tested show sound and homogeneous concrete throughout
| 03SR - Stations (RfL) | Cxxx-NCR-000642 | NCR | Excedence of 1 hour time period between concrete loads on P29 |  | Contr |  | PAD - Paddington Station (West) |  | 2013-05-30 | 2013-05-13 18:11 | -17 | 2013-02-21 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | On pile P29 the time between the third and fourth concrete loads exceded 1 hour. The third load completed discharge at 14:32 and the fourth load began discharge at 16:30. There was a period of 1 hour and 58 mins between loads. This was due to a plant breakdown at the normal batching plant which required the concrete to come from other back up plants (ref Cem-Scan-034)
| 03SR - Stations (RfL) | Cxxx-NCR-000649 | NCR | Sonic logging blockage at N59 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-01-04 | 2013-09-13 17:20 | -113 | 2013-02-25 | Structural Engineering - Diaphragm Walls | 1000 |  |  | Rework | 4 (0.5-3k) | Complete |  | Completed |  | For panel N59, sonic logging tube 3 was blocked at approx 21.5m depth from top of guide wall. All alreas tested show sound and homogeneous concrete throughout. See appendix for data
| 03SR - Stations (RfL) | Cxxx-NCR-000651 | NCR | Sonic Logging blockage at N53 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-12-15 | 2015-11-23 10:27 | -22 | 2013-02-25 | Structural Engineering - Diaphragm Walls | 2500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | For Panel N53, profile 3-4 shows an increase in transit time of approx 40% at depth / level approximal to 120mAD over a vertical extent of 800mm. The sonic logging contractor's assessment points towards localized feature. All other area tested show sound and homogeneous concrete throughout. The anomaly is located at approximately 1m below panel COL
| 03SR - Stations (RfL) | Cxxx-NCR-000654 | NCR | D-wall over break at N58 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-12-23 | 2014-12-16 14:46 | -7 | 2013-02-25 | Structural Engineering - Diaphragm Walls | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | We investigated the following main possible causes: 1) batching error: the autographic records of all loads were obtained from __, and they confirm the volume poured is as expected [records in Appendix 1]. 2) physical overdigging: N58 is a 1-cut starter panel, hence the panel cut can not exceed the size of the jaw, which was measured daily and confirmed immediately after the event to be as expected 2.8m x 1.22m. 3) human error in records: the concrete pour record was independently checked for possible error; all records are checked to be consistent and accurate. Excluding these possibilities, the remaining probable root cause is unforseen ground conditions, which 3. How and why did this occur. Issued to: Name of person raising this NC: Y Zhao Date NC raised: 15/01/2013 Hence approximately 50m^3 more concrete were poured into N58 than expacted. Please note, the panel record for N58 is being transmitted to JV via Aconex in due course. The cumulative total overbreak for panel N58 is 30.3%, and this overbreak is distributed more or less evenly over the entire depth of the panel, and may represent significant enlargement of as built cross section of concrete (e.g. the as built panel size is comparable to a 2.8 x 1.6m, compared to the design size of 2.8 x 1.2m). N/A Q2.17 Other (please specify below) Audit No : 1a. Complete the sections below 1b. Complete all of the blue drop down boxes below. Project or Department Name : NCR-149 Q1.6 Unforeseen / Ground Conditions Major Project DIAPHRAGM WALLING Project No : 271155 Date: 15/01/2013 N C Report No: MANAGEMENT SYSTEM NON CONFORMANCE REPORT On a project where a product or service Quality NC has occurred the Project Engineer shall complete as much of this form as possible. The Project Quality NC Schedule shall be maintained up to date and both documents shall be forwarded to the BS Administrator immediately following each month end. During an audit, sections 1a, 1b and 2 shall be completed by the auditor and then it shall be submitted to the QA Manager with the audit report. The recipient of an NC Report raised at an audit, shall fully complete this form and return it to the QA Manager Cat 2 Cause Cat 1 Cause Technique Document No : MON :002 Appendix 1 Rev : 10.1 Date : Feb 2012 Page 1 of 1 Name of person agreeing closure Date agreed contibuted to the unexpected ground collapse that gave rise to the 30% overbreak; the passage of the TBM may have contributary effects. We recommand N58 to be surveyed and the ground condition adjacent N58 to be closely studied upon bulk dig, to gather evidence towards this possible root cause. This occurance may point to similar unforseen ground condition related local high overbreaks, we are in the process of compiling a seperate generic NCR/EWR for that purpose.
| 03SR - Stations (RfL) | Cxxx-NCR-000655 | NCR | Sonic logging blocked tubes at N47 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-07-21 | 2014-06-20 10:59 | -31 | 2013-02-25 | Structural Engineering - Diaphragm Walls | 500 |  |  | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | For panel N47, tube 3 blocked at the top. As a result only 3 full profiles were tested; and path 1-4 and 2-4 indicated significant damping in a 2.5m zone immediately below panel COL. All other areas tested show sound and homogeneous concrete throughout. See Appendix for test report
| 03SR - Stations (RfL) | Cxxx-NCR-000656 | NCR | D-wall panel construction exceeding over 120 hours |  | Contr |  | PAD - Paddington Station (West) |  | 2015-01-04 | 2013-05-08 15:54 | -606 | 2013-02-26 | Structural Engineering - Diaphragm Walls | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | For panel N53, the total construction time was 154hr 24mins > 120hr limit. The excavation started at 16/01/13 12:30; the last pass of grab at 22/01/13 07:30 and the end of concrete pour at 22/01/13 22:54, please note the duration between last pass of grab and end of concreting was 15hr 24min < 24hr limit. The total construction duration exceeded 120hrs because the site activities stood down during the weekend of 19th and 20th Jan due to unavailible muck away affected by severe snow conditions
| 03SR - Stations (RfL) | Cxxx-NCR-000657 | NCR | Panel construction exceeding 120 hours : N56 |  | Contr |  | PAD - Paddington Station (West) |  | 2015-01-04 | 2013-04-30 15:27 | -614 | 2013-02-26 | Structural Engineering - Diaphragm Walls | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | For panel N56, the total construction time was 159hr 05mins > 120hr limit. The excavation started at 23/01/13 17:00, the last pass of grab at 28/01/13 10:30 and the end of concrete pour at 29/01/13 08:05, please note the duration between last pass of grab and end of concreting was 22hr 25min < 24hr limit The total construction duration exceeded 120hrs because insufficient muck away, stopping us from caging up and concreting by Friday afteroon, ahead of the weekend shut down.
| 03SR - Stations (RfL) | Cxxx-NCR-000658 | NCR | N56: D-wall panel plan constructed 112mm outwards |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-06-24 | 2014-05-30 10:32 | -25 | 2013-02-26 | Structural Engineering - Diaphragm Walls | 500 |  |  | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | For Panel N56, the panel plan position measured at tunnel centre line deviated by +112mm from design position (outwards, away from the box); this exceeds the 99mm as allowed by verticality tolerance. As the deviation is towards the outside of the box, it does not encroach upon the main box internal space; the out of tolerance is 13mm which may be considered less significant. We recommand the panel accepted as is with no remedial measures being necessary. The rig operator actively adjusted grab control to minimise the deviation. He as able to limit the out of tolernace to 13mm
| 03SR - Stations (RfL) | Cxxx-NCR-000659 | NCR | N56: Sonic logging results |  | Contr |  | PAD - Paddington Station (West) |  | 2015-01-04 | 2013-05-08 15:45 | -606 | 2013-02-26 | Structural Engineering - Diaphragm Walls | 500 |  |  | Rework |  | Complete |  | Completed |  | During sonic logging testing of diaphragm wall panel N56 tested on visit 11th - 13th February 12, the following result was produced: 'Profiles 1-2 & 3-4 show increases in transit time of 53.4% at the toe of the panel, most significantly on profile 1-2 over a vertical extent of 800mm. As this increase is not repeated to a similar extent on the remaining profiles, it can be considered the result of localised features with no significance in terms of panel integrity. All other areas showed sound and homogenous concrete throughout'.
| 03SR - Stations (RfL) | Cxxx-NCR-000662 | NCR | N57: Concrete pour exceeding 1 hour limit |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-04-08 | 2014-03-27 14:18 | -12 | 2013-02-26 | Structural Engineering - Diaphragm Walls | 500 |  |  | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | For panel N57, the duration between end of pour of concrete ticket 766732 and the start of pour of 766742 is 1hr and 16mins > 1hr limit. All other loads comply with both 1hr and 3hr rule. Load 766742 is placed between 121.6mAD and 122.3mAD which is immedately at or mostly above panel COL of 121.650mAD. We recommand the panel to be accepted as is, and no further investigation necessary, based on the short exceedence and the fact the offending load will be broken out. The offending load was part of 2 last loads topping up the concrete to within the guide wall; site congestion issued delayed placement by 16 minutes
| 03SR - Stations (RfL) | Cxxx-NCR-000663 | NCR | D-wall panel S01: Sonic tubes cast at lower level |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-02-18 | 2015-02-04 10:03 | -14 | 2013-02-26 | Structural Engineering - Diaphragm Walls | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | For panel S01, the sonic tubes were left cast in below top of concrete, with the intention to carry out sonic testing after D Wall panel break down. This meant the testing could not be carried out within 21 days after concreting. Narrative: Project specification KP10, section 2202 f) i), requires that "Wall panels: sonic logging of each panel shall be undertaken after the wall has been trimmed". In the same document section 2202 b) it states "integrity testing shall be carried out between 7 days and 21 days after piles have been cast". Cross Rail has taken the view that the above KP10 section 2202 b) also applies to Diaphragm Wall. As such for S01, it exceeded the 21 day limit, hence the raising of this NCR. This NCR is raised at Cross Rail request to expediate panel record close out only.
| 03SR - Stations (RfL) | Cxxx-NCR-000664 | NCR | W01: Sonic logging tubes casted below top of concrete |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-07-17 | 2015-06-18 09:46 | -29 | 2013-02-26 | Structural Engineering - Diaphragm Walls | 2500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | For panel W01, the sonic tubes were left cast in below top of concrete, with the intention to carry out sonic testing after D Wall panel break down. This meant the testing could not be carried out within 21 days after concreting. Narrative: Project specification KP10, section 2202 f) i), requires that "Wall panels: sonic logging of each panel shall be undertaken after the wall has been trimmed". In the same document section 2202 b) it states "integrity testing shall be carried out between 7 days and 21 days after piles have been cast". Cross Rail has taken the view that the above KP10 section 2202 b) also applies to Diaphragm Wall. As such for S01, it exceeded the 21 day limit, hence the raising of this NCR. Th.
| 03SR - Stations (RfL) | Cxxx-NCR-000665 | NCR | D-wall panel W2: sonic logging tubes casted below concrete level |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-07-30 | 2013-07-30 13:46 | 0 | 2013-02-26 | Structural Engineering - Diaphragm Walls | 500 |  |  | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | For panel W02, the sonic tubes were left cast in below top of concrete, with the intention to carry out sonic testing after D Wall panel break down. This meant the testing could not be carried out within 21 days after concreting. Narrative: Project specification KP10, section 2202 f) i), requires that "Wall panels: sonic logging of each panel shall be undertaken after the wall has been trimmed". In the same document section 2202 b) it states "integrity testing shall be carried out between 7 days and 21 days after piles have been cast". Cross Rail has taken the view that the above KP10 section 2202 b) also applies to Diaphragm Wall. As such for S01, it exceeded the 21 day limit, hence the raising the NCR
| 03SR - Stations (RfL) | Cxxx-NCR-000666 | NCR | Collapse New Boreholes in Gridline 1 |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-05 | 2013-03-27 17:47 | -9 | 2013-02-26 | Civil - Geotechnical Engineering | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | The boreholes were drilled during the 9th and 10th of February, and they have been opened during all this time (more than 2 weeks now) without doing the installation after being drilled. The boreholes have collapsed and there is a blockage for two of them at 45m depth, and the other one at 56m depth. The installations were not carried out because the instruments were not on site at that time.
| 03SR - Stations (RfL) | Cxxx-NCR-000668 | NCR | Dwall panel W2: Over break recorded during the construction of panel |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-03-11 | 2015-03-16 16:19 | 5 | 2013-02-27 | Structural Engineering - Diaphragm Walls | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Panel W02, recorded -2.5% cumulative total overbreak. And -7.5% cumulative overbreak below base level of guidewall, as reported in W02 Panel Record. Please see section 3 for a narrative. We recommand the panel accepted as is, pending the sonic logging reports [currently test planned after breaking down, in week commencing 11st March 2013]W02 was an intermediate panel, with both joints formed by stop end process, therefore the integrity of the joint can not be affected. Panel was constructed with 1m norminal (thickness) size grab, which garantees the thickness of panel, hence cover to cage; this was confirmed by the fact the 1m cage was installed without reportable issue. The root cause of the underbreak is not known, but is considered minor.
| 03SR - Stations (RfL) | Cxxx-NCR-000669 | NCR | D-wall over break of panels |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-09-01 | 2014-08-29 10:51 | -3 | 2013-02-27 | Structural Engineering - Diaphragm Walls | 5000 |  | Workmanship | Rework | 3 (3-6k) | Complete | Supervision - Insufficient supervision | Completed |  | The local overbreak region is confined to short vertical extents, much less than the size of the grab; this precludes the possibility of off-line digging by the grab. The remaining most probable cause is local unforseen ground condition, one possible scenario may be pockets of material significantly more disturbed than expected London Clay encountered leading to local cavity manifesting as overbreak We recommand during bulk dig, the surrounding ground condition to be closely observed and studied to investigate local ground conditions at the affected zones
| 03SR - Stations (RfL) | Cxxx-NCR-000670 | NCR | Concrete Mix D-Wall |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2013-07-16 | 2013-07-04 14:05 | -12 | 2013-02-27 | Civil - Civil Engineering General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete |  | Completed |  | In early January __ noticed that the 7 day cube results were showing lower than usual results. As a result a decision was made to increase the cement content of approved D-Wall Mix DW_2 by 5%. This increases the cement content to 513Kg which is still within specification, however prior approval was not sought from the PM. This effects panels N53, N61, N56, N47, N62, N46, N55, N54 only.
| 03SR - Stations (RfL) | Cxxx-NCR-000672 | NCR | N61: Increase in transit time during sonic logging testing |  | Contr |  | PAD - Paddington Station (West) |  | 2014-01-04 | 2013-05-08 15:56 | -241 | 2013-02-27 | Structural Engineering - Diaphragm Walls | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | Panel N61, during sonic logging, profile 3-4 (short path) shows an increase in transit time of 35.6% at approx 0.7m above cage toe for an vertical extent of 300mm. As this increase is not repeated on the remaining profiles, it can be considered the result of a localised feature with no significance in terms of panel integrity. All other areas tested show sound and homogeneous concrete throughout
| 03SR - Stations (RfL) | Cxxx-NCR-000675 | NCR | Craven Road __ Main Permanent Connection |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-30 | 2013-04-29 16:24 | -1 | 2013-02-28 | Utilities Engineering - Water | 500 |  | Material | Rework |  | Complete |  | Completed |  | A 90 degree red ductile iron fitting has been installed at the __ permanent main connection at Craven Road as shown in -Cxxx-U-MDA-00002. This fitting does not have WRAS accreditation and is strictly for use with sewage and waste (non potable) water only and not suitable for use in drinking water pipework. As a result we will not be opening up this connection to the local network and the fitting will have to be replaced and pipework re-chlorinated prior to the future connection being brought into service.
| 03SR - Stations (RfL) | Cxxx-NCR-000677 | NCR | Maintenance of the Temporary Works |  | Contr |  | PAD - Paddington Station (West) |  | 2013-05-24 | 2013-05-08 15:42 | -16 | 2013-03-04 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Objective evidence was not made available to demonstrate implementation of the above requirement with respect to the plunge column temporary works.
| 03SR - Stations (RfL) | Cxxx-NCR-000678 | NCR | Concrete curing records |  | Contr |  | PAD - Paddington Station (West) |  | 2013-05-25 | 2013-05-21 18:31 | -4 | 2013-03-04 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Concrete site curing records for compressive samples not made available
| 03SR - Stations (RfL) | Cxxx-NCR-000679 | NCR | Calibration records |  | Contr |  | PAD - Paddington Station (West) |  | 2013-05-15 | 2013-05-08 15:30 | -7 | 2013-03-04 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Calibration records for laser plumb, pilling rig and torque wrenches not made available
| 03SR - Stations (RfL) | Cxxx-NCR-000680 | NCR | ITP interventions |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-30 | 2013-04-25 18:10 | -5 | 2013-03-04 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | The inspection and test plan Cxxx-SHC-C-ITP-B071_WS077-50017 rev 2 show a number of inspection activities as N/A for the Contractor.
| 03SR - Stations (RfL) | Cxxx-NCR-000687 | NCR | Concrete cube storage for Plunge column |  | Contr |  | PAD - Paddington Station (West) |  | 2013-05-03 | 2013-05-03 16:41 | 0 | 2013-03-04 | Structural Engineering - Diaphragm Walls | 500 |  |  | Rework |  | Complete |  | Completed |  | As per BS EN 12390-2 section 5.5.1, concrete cubes were not stored in designated cube storage area and under certain temperature
| 03SR - Stations (RfL) | Cxxx-NCR-000688 | NCR | D-wall panel N54: Sonic logging anomolies |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-05-25 | 2016-04-21 11:00 | -34 | 2013-03-04 | Structural Engineering - Diaphragm Walls | 5000 |  | Workmanship | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | For panel N54, on sonic testing anomalies were found at high level. Please see appendix for details In brief, paths 1-2, 3-4, show increase of transit times between approximately 115 and 117.3mAD. They are considered the result of localised features with no significance in terms of panel integrity. All other areas tested show sound and homogeneous concrete throughout
| 03SR - Stations (RfL) | Cxxx-NCR-000689 | NCR | Dwall panel N55: Increase transit time in sonic logging testing |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-03-31 | 2015-05-08 11:49 | 38 | 2013-03-04 | Structural Engineering - Diaphragm Walls | 5000 |  | Workmanship | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During sonic logging testing of diaphragm wall panel N55 tested on visit 11th - 13th February 12, the following result was produced: 'Profiles 3-4 & 4-1 show increases in transit time at a depth of approximately 117.2m AOD. The largest increase is 34.8% on profiles 3-4 over a vertical extent of 700mm. As these increases are not featured or repeated on remaining profiles, they can be considered the result of a localised featurewith no significance in terms of panel integrity. All other areas showed sound and homogenous concrete throughout'.
| 03SR - Stations (RfL) | Cxxx-NCR-000690 | NCR | Dwall panel N62 exceeding 120 hours of construction |  | Contr |  | PAD - Paddington Station (West) |  | 2013-05-14 | 2013-05-10 08:55 | -4 | 2013-03-04 | Structural Engineering - Diaphragm Walls | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | THe total construction duration exceeded 120h because the site activities stood down during the weenkends (26th- 27th January and 2nd-3rd February). When it started rig was stood due to concerns aboout N61 concrete curing time. The shank broke so, it was necessary nearly a shift to repair it. Moreover, it's a closer panel so, the time to remove stopends was considerable, as well as, the problems to change clutches (it was an important use of time changing them
| 03SR - Stations (RfL) | Cxxx-NCR-000691 | NCR | Dwall panel E3- Increase in transit time during sonic logging testing |  | Contr |  | PAD - Paddington Station (West) |  | 2015-01-01 | 2013-05-08 15:23 | -603 | 2013-03-04 | Structural Engineering - Diaphragm Walls | 500 |  |  | Rework |  | Complete |  | Completed |  | The concreting could not be started earlier than planned due to supply issues, impacted by the difficulty of stop end extraction. This meant the pre-booked concreting slot with the supplier was lost, as the concreting time had to be delayed
| 03SR - Stations (RfL) | Cxxx-NCR-000692 | NCR | Dwall panel N46: Last pass of grab and end of concreting exceeded the 24hr limit |  | Contr |  | PAD - Paddington Station (West) |  | 2013-05-14 | 2013-05-10 08:37 | -4 | 2013-03-04 | Structural Engineering - Diaphragm Walls | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | For Panel N46, the duration between last pass of grab and end of concreting exceeded the 24hr limit by 2hr and 37mins. At 24hr after the last pass of grab, concrete has risen to 111mAD [ticket 764999, end pour of this load at 1/2/13 19:07, concrete rose to 13m below top of guide. The concreting could not be started earlier than planned due to supply issues, impacted by the difficulty of stop end extraction. This meant the pre-booked concreting slot with the supplier was lost, as the concreting time had to be delayed
| 03SR - Stations (RfL) | Cxxx-NCR-000693 | NCR | D-wall Panel N55: Increase in transit time |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-30 | 2013-04-30 21:21 | 0 | 2013-03-06 | Structural Engineering - Diaphragm Walls | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | During first round of testing high level sonic anomaly was found (Rev0 for this NCR), to further study of the anomaly, an additional testing was carried out in visit 22 by offset-probes. The conclusion is:"Test were repeated by offsetting emitter and reciever by 0.6m in both directions. Profiles 3-4 shows an increase in transit time of between 16.7 and 20.9% at a depth of approximately 117.4 AOD, over a vertical extent of 800mm. As this increase in not repeated on the remaining profiles, it can be considered the result of a localised featured with no significance in terms of panel integrity. All other areas tested show sound and homogeneous concrete troughout." Please, see the attached appendix for test results. An additional probe testing is completed and no more testing are planned.
| 03SR - Stations (RfL) | Cxxx-NCR-000694 | NCR | D-wall Panel N56: Increase in tanrsmital signals at panel toe |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-30 | 2013-04-30 20:59 | 0 | 2013-03-06 | Structural Engineering - Diaphragm Walls | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | During first round of testing at toe level sonic anomaly was found in Rev0 of this NCR, to further study an additional testing was carried out in visit 22 by offset probes. The conclusion is: "Test were repeated by offsetting emiter and receiver by 0.6m in both direcions. Profile 1-2 and 3-4 show an increase time between 46.8- 50.6% (for profile 1-2) and 33.7% (for profile 3-4) at the toe of the panel, over a vertical extent of between 0.5 and 0.8m. As this increase is not repeated on the remaining profiles, they can be conisedered the result of a localised feature with no significance in terms of panel integrity. All other areas tested show sound and homogeneous concrete throughout
| 03SR - Stations (RfL) | Cxxx-NCR-000695 | NCR | Plunge column P47: Defective shear studs |  | Contr |  | PAD - Paddington Station (West) |  | 2015-01-04 | 2013-04-26 12:24 | -618 | 2013-03-08 | Structural Engineering - Steel Member | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | Plunge column P47: 10XNumber Defective shear studs, not having sufficent weld colar around the studs i.e. less than 7mm
| 03SR - Stations (RfL) | Cxxx-NCR-000696 | NCR | Plunge column P41: Defective shear studs |  | Contr |  | PAD - Paddington Station (West) |  | 2015-01-04 | 2013-04-15 17:47 | -629 | 2013-03-08 | Structural Engineering - Steel Member | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | Plunge column P47: 3XNumber Defective shear studs, not having sufficent weld colar around the studs i.e. less than 7mm
| 03SR - Stations (RfL) | Cxxx-NCR-000699 | NCR | Plunge column P42: Defective shear studs |  | Contr |  | PAD - Paddington Station (West) |  | 2013-06-10 | 2013-05-21 18:26 | -20 | 2013-03-08 | Structural Engineering - Steel Member | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | Plunge column P42: 1XNumber Defective shear studs, not having sufficent weld colar around the studs i.e. less than 7mm. 4XNo one one side, 7xNo other side
| 03SR - Stations (RfL) | Cxxx-NCR-000716 | NCR | Plunge column P42: Defective shear studs |  | Contr |  | PAD - Paddington Station (West) |  | 2013-08-08 | 2013-07-30 13:50 | -9 | 2013-03-13 | Structural Engineering - Steel Member | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Plunge column P42: 15XNumber Defective shear studs, not having sufficent and complete weld colar (360) around the studs
| 03SR - Stations (RfL) | Cxxx-NCR-000720 | NCR | Plunge column N48: Defective shear studs |  | Contr |  | PAD - Paddington Station (West) |  | 2013-05-26 | 2013-05-31 16:17 | 5 | 2013-03-14 | Structural Engineering - Steel Member | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | P-48 10xNo defective shear studs with incomplete or undercut weld collars
| 03SR - Stations (RfL) | Cxxx-NCR-000722 | NCR | Plunge column: P35 Defective weld collars |  | Contr |  | PAD - Paddington Station (West) |  | 2013-06-18 | 2013-06-20 08:58 | 2 | 2013-03-14 | Structural Engineering - Steel Member | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | 5xNo defective weld collars with incomplete 360 ring.
| 03SR - Stations (RfL) | Cxxx-NCR-000745 | NCR | Concrete cubes kept beyond 3 days |  | Contr |  | PAD - Paddington Station (West) |  | 2013-06-04 | 2013-05-17 16:01 | -18 | 2013-03-18 | Structural Engineering - Structural Engineering - General | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | Concrete cubes kept beyond 3 days without getting struck from cube mould.
| 03SR - Stations (RfL) | Cxxx-NCR-000751 | NCR | Grouting of sonic tubes prior to testing |  | Contr |  | PAD - Paddington Station (West) |  | 2013-03-27 | 2013-04-02 09:39 | 6 | 2013-03-20 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The sonic logging tubes were grouted prior to testing therefore preventing testing
| 03SR - Stations (RfL) | Cxxx-NCR-000755 | NCR | Inclinometer Probe 1 damaged |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-30 | 2013-04-29 16:56 | -1 | 2013-03-22 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | Inclinometer Probe 1 was damaged on 21/03/2013. At present Probe 2 is being used to cover the SRG requirements. had planned the procurement of a backup probe which was brought to site on Monday and is currently being baselined. Until this probe is prepared for deployment, it may not be possible to fulfill all of the weekly monitoring requirements.
| 03SR - Stations (RfL) | Cxxx-NCR-000756 | NCR | Installation Piezometer C7-11 |  | Contr |  | PAD - Paddington Station (West) |  | 2013-05-03 | 2013-05-03 16:32 | 0 | 2013-03-22 | Civil - Geotechnical Engineering | 500 |  |  | Rework |  | Complete |  | Completed |  | During the installation of the C7-11 Piezometer, the bottom casing string broke off and the bottom piece of casing (3m long) was left on the borehole unrecoverable and at unknown depth. The implication for the unknown depth is important due to the lack of knowledge about the casing localization. This piece of the casing can affect the functionality of the instrument .
| 03SR - Stations (RfL) | Cxxx-NCR-000770 | NCR | Piezometers within the station box are not read as per Cxxx requirements |  | Contr |  | PAD - Paddington Station (West) |  | 2013-05-22 | 2013-05-17 16:05 | -5 | 2013-03-27 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Planning | Rework |  | Complete |  | Completed |  | There are 6 piezometer boreholes within the station box and each boreholes have 3 piezometer sensors installed at different depth (See attached sketch for locations). At present is reading the piezometers manually on a weekly basis.
| 03SR - Stations (RfL) | Cxxx-NCR-000771 | NCR | Piezometer borehole C20-03: Cables damaged due to construction activities |  | Contr |  | PAD - Paddington Station (West) |  | 2013-06-20 | 2013-06-17 18:13 | -3 | 2013-03-27 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | This borehole (C20-03) is located in gridline 20 and there are 3 piezometer sensors installed at different depths. These sensors are read at ground level via cables connected to them and the cables are labelled & protected at the ground level to avoid any damages. These instrument were not accessible for the past 1 month due to on going construction activities. However, I&M was liaising with construction team to get access. Access was provided on Monday (25/03/2013) and we realised that the sensor cables at the ground level were severed and the labels missing making it unreadable.
| 03SR - Stations (RfL) | Cxxx-NCR-000772 | NCR | Piezometer borehole C20-09: Cables damaged due to construction activities |  | Contr |  | PAD - Paddington Station (West) |  | 2013-05-29 | 2013-05-21 18:24 | -8 | 2013-03-27 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | This borehole (C20-09) is located in gridline 20 and there are 3 piezometer sensors installed at different depths. These sensors are read at ground level via cables connected to them and the cables are labelled & protected at the ground level to avoid any damages. These instruments were not accessible for the past 1 month due to on going construction activities. However, I&M was liaising with construction team to get access. Access was provided on Monday (25/03/2013) and we realised that the sensor cables at the ground level were severed and the labels missing making it unreadable.
| 03SR - Stations (RfL) | Cxxx-NCR-000777 | NCR | Water found on top of concrete P47,P49,P51 |  | Contr |  | PAD - Paddington Station (West) |  | 2013-07-18 | 2013-06-11 17:38 | -37 | 2013-04-02 | Civil - Civil Engineering General | 500 |  | Material | Rework |  | Complete |  | Completed |  | Water found on top of concrete- most likely cause concrete bleed: P49: 200mm P47 (21.1m top of concrete at placement, 21.9 top of concrete following day): 800mm P51 (20.4 top of concrete at placement, 20.8 top of concrete following day): 400mm
| 03SR - Stations (RfL) | Cxxx-NCR-000781 | NCR | Head beams fabricated without approved material. |  | Contr |  | PAD - Paddington Station (West) |  | 2013-05-20 | 2013-05-17 15:57 | -3 | 2013-04-03 | Structural Engineering - Steel Member | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | Beader beams (B14, B60, B3, B5, B6) between GL1- GL9 fabricated and erected on site without MCR approval
| 03SR - Stations (RfL) | Cxxx-NCR-000803 | NCR | P36 Plunge column: Defective weldable anchors (strain guage anchors) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-07-25 | 2013-07-25 12:27 | 0 | 2013-04-05 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete |  | Completed |  | Installation record for plunge column P36, flagged up misallignment in weldable anchors at the central locationof the south face of the plunge column for sensor EG-360002.
| 03SR - Stations (RfL) | Cxxx-NCR-000804 | NCR | Strain Gauges North D-Wall |  | Contr |  | PAD - Paddington Station (West) |  | 2013-06-20 | 2013-06-17 18:10 | -3 | 2013-04-05 | Civil - Geotechnical Engineering | 500 |  |  | Repair |  | Complete |  | Completed |  | Not only the Strain gauges cables within panel N24 have been cut, the Strain Gauges within Panels N12, N16 and N20 have been affected and cut without Crossrail approval. The minimum length of 100mm has not been achieved for some of the cables and there is not marks on them causing almost impossible the cables splice prior to the roof slab pour.
| 03SR - Stations (RfL) | Cxxx-NCR-000805 | NCR | Damaged Inclinometers: E6-01, E9-37, E10-10, C24-21, B24-22 |  | Contr |  | PAD - Paddington Station (West) |  | 2013-06-26 | 2013-06-17 18:14 | -9 | 2013-04-05 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Damaged to Inclinometers: E6-01, E9-37, E10-10, C24-21, B24-22
| 03SR - Stations (RfL) | Cxxx-NCR-000806 | NCR | Unable to report monitoring data from exisiting inclinometers |  | Contr |  | PAD - Paddington Station (West) |  | 2013-06-26 | 2013-06-17 18:11 | -9 | 2013-04-05 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Unable to report monitoring data from exisiting inclinometers: E2-04, E4-06, E10-01, E13-06, E15-07, A1-02, B1-03, C1-02, D1-01
| 03SR - Stations (RfL) | Cxxx-NCR-000807 | NCR | KTP Instrumentation |  | Contr |  | PAD - Paddington Station (West) |  | 2013-05-08 | 2013-05-08 16:37 | 0 | 2013-04-05 | Civil - Geotechnical Engineering | 500 |  |  | Repair |  | Complete |  | Completed |  | The instruments that were attached to a holding before, they were found lying on the ground covered by concreted and clay without any protection. There is a high risk of damage for these instruments.
| 03SR - Stations (RfL) | Cxxx-NCR-000808 | NCR | Damage instruments PE C20-09, PE C20-03 & ME C20-06 |  | Contr |  | PAD - Paddington Station (West) |  | 2013-06-19 | 2013-06-17 18:07 | -2 | 2013-04-05 | Civil - Geotechnical Engineering | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | was informed by CRL that these instruments cables were not protected on 05.03.2013. The actions were not taken and the instruments were reported to be damaged the 26th March.
| 03SR - Stations (RfL) | Cxxx-NCR-000809 | NCR | GL1-GL9: Inadequate rebar cover for D-wall panels |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-03-12 | 2014-08-20 10:39 | -204 | 2013-04-08 | Structural Engineering - Diaphragm Walls | 5000 |  | Workmanship | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | GL1-GL9: Inadequate rebar cover for D-wall panels
| 03SR - Stations (RfL) | Cxxx-NCR-000810 | NCR | GL1-GL9: Loose concrete at D-wall panel joints |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-04-04 | 2014-01-29 08:33 | -65 | 2013-04-08 | Structural Engineering - Diaphragm Walls | 2500 |  |  | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | GL1-GL9: From panels N1 to N25, certain joints between the panels have not got the right concrete bonding
| 03SR - Stations (RfL) | Cxxx-NCR-000820 | NCR | Damage to Prism PR000512 |  | Contr |  | PAD - Paddington Station (West) |  | 2013-04-22 | 2013-04-18 12:43 | -4 | 2013-04-10 | Surveying - Geotechnical Surveys | 500 |  | Damaged | Use As-Is |  | Complete |  | Completed |  | The prism was damaged and showed a 20mm movement. The prism has since stabilised
| 03SR - Stations (RfL) | Cxxx-NCR-000822 | NCR | Concrete cast level |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-06-16 | 2015-04-16 13:20 | -61 | 2013-04-10 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Pile P02 was cast 203mm above cut off level Pile P07 was cast 465mm above cut off level
| 03SR - Stations (RfL) | Cxxx-NCR-000823 | NCR | B6: Header beam bolts not erected to the right size |  | Contr |  | PAD - Paddington Station (West) |  | 2013-05-21 | 2013-05-13 18:20 | -8 | 2013-04-11 | Structural Engineering - Steel Member | 500 |  |  | Rework |  | Complete |  | Completed |  | Header beam B6: Bolts are misalligned/drilled short of required size as per attached sketch.
| 03SR - Stations (RfL) | Cxxx-NCR-000824 | NCR | Damage to existing sonic tubes during excavation works |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-08-18 | 2013-08-09 15:03 | -9 | 2013-04-11 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  |  | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Damage to existing sonic tubes during the bulk excavation works below the ground level
| 03SR - Stations (RfL) | Cxxx-NCR-000825 | NCR | Plunge column P36, P51, P41: Unapproved back fill |  | Contr |  | PAD - Paddington Station (West) |  | 2013-05-28 | 2013-05-17 15:47 | -11 | 2013-04-11 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Unapprovedf __ 20mm single size gravel was used as follows: P36 8m3 below biscuit 32m3 above biscuit / P41 8m3 used to complete backfill / P47 40m3 used above biscuit / P51 40m3 used above biscuit. This all occured due to supply problem og Granite from supplier
| 03SR - Stations (RfL) | Cxxx-NCR-000826 | NCR | P41: No electrical testing |  | Contr |  | PAD - Paddington Station (West) |  | 2013-06-20 | 2013-06-21 17:54 | 1 | 2013-04-11 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | P41 was to be checked for electrical continuity, however it was not tested as the cage went in and as the cage was for P43 it was not tested in the factory either.
| 03SR - Stations (RfL) | Cxxx-NCR-000827 | NCR | P50: Unapproved backfill used for top 6m |  | Contr |  | PAD - Paddington Station (West) |  | 2013-06-25 | 2013-05-21 17:55 | -35 | 2013-04-11 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | On pile P50 the the top 6m of bore has been backfilled with clay spoil and not the Granite sand and gravel.This was due to (suppliers) are unable to supply any Granite to complete the backfill due to delivery problems. In order to release the casing for the next pile the last 6m of bore was backfilled with clay, the last 3m of column is set in clay and no sonic tubes are fitted to this pile. The remainder of backfill was as per spec with granite and biscuit
| 03SR - Stations (RfL) | Cxxx-NCR-000828 | NCR | P38:Out of Vertical tolerance |  | Contr |  | PAD - Paddington Station (West) |  | 2013-05-20 | 2013-05-13 18:02 | -7 | 2013-04-11 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | P38 was measured with a verticality of 1:143 which is less than the specified 1:150
| 03SR - Stations (RfL) | Cxxx-NCR-000829 | NCR | P42:Plunge column above design level |  | Contr |  | PAD - Paddington Station (West) |  | 2013-05-26 | 2013-05-31 15:57 | 5 | 2013-04-11 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | P42 final steel level 180mm above design level = 30mm out of tolerance
| 03SR - Stations (RfL) | Cxxx-NCR-000830 | NCR | Plunge column P16: Sonic logging anomly at bored pile |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-02-10 | 2015-02-10 14:41 | 0 | 2013-04-11 | Geotechnical Engineering - Concrete - Bored Pile | 2500 |  |  | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | There is a signal loss of 1m section below cut off level on all profiles.
| 03SR - Stations (RfL) | Cxxx-NCR-000831 | NCR | Plunge column P29: Concrete exceeding one hour |  | Contr |  | PAD - Paddington Station (West) |  | 2013-06-20 | 2013-05-14 09:02 | -37 | 2013-04-11 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  |  | Rework |  | Complete |  | Completed |  | On pile P29 the time between the 3rd and 4th load exceeded 1 hr. The 3rd load finished at 14:32 and the 4th load started at 16:30 giving a period of 1 hr 58 minutes between loads.
| 03SR - Stations (RfL) | Cxxx-NCR-000841 | NCR | Plunge column P6: Out of tolerance by 1mm |  | Contr |  | PAD - Paddington Station (West) |  | 2013-06-03 | 2013-05-15 09:35 | -19 | 2013-04-12 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | P6:Plunge column P6, out of positional tolerance by 1mm.
| 03SR - Stations (RfL) | Cxxx-NCR-000842 | NCR | P2:Plunge column out of tolerance by 2mm |  | Contr |  | PAD - Paddington Station (West) |  | 2013-06-25 | 2013-05-21 17:51 | -35 | 2013-04-12 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | P2: Plunge column out of positional tolerance by 2mm
| 03SR - Stations (RfL) | Cxxx-NCR-000846 | NCR | Plunge column P7: Sonic tubes grouted prior to testing |  | Contr |  | PAD - Paddington Station (West) |  | 2013-05-29 | 2013-05-15 09:33 | -14 | 2013-04-17 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | Plunge column P7: Sonic tubes grouted prior to testing
| 03SR - Stations (RfL) | Cxxx-NCR-000847 | NCR | Plunge column P8: Sonic tubes grouted prior to testing |  | Contr |  | PAD - Paddington Station (West) |  | 2013-06-28 | 2013-06-17 17:57 | -11 | 2013-04-17 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | Plunge column P8: Sonic tubes grouted prior to testing
| 03SR - Stations (RfL) | Cxxx-NCR-000848 | NCR | Plunge column P15:Only grouted upto 6m |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-03-12 | 2015-03-16 16:19 | 4 | 2013-04-17 | Geotechnical Engineering - Concrete - Bored Pile | 2500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Plunge column P15:Only grouted upto 6m, as a result of existing tubes snapped
| 03SR - Stations (RfL) | Cxxx-NCR-000849 | NCR | Plunge column:Follower removed without final survey |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-07-29 | 2013-07-12 10:26 | -17 | 2013-04-17 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  |  | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Plunge columns P24, P29:Follower removed without final survey
| 03SR - Stations (RfL) | Cxxx-NCR-000850 | NCR | Plunge column P35: Construction time exceeding 12 hours |  | Contr |  | PAD - Paddington Station (West) |  | 2013-07-17 | 2013-06-17 17:54 | -30 | 2013-04-17 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | Plunge column P35: Construction time exceeding 12 hours, actual time: 15 hours, 50.
| 03SR - Stations (RfL) | Cxxx-NCR-000851 | NCR | Plunge column P32: Electrical testing not done |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-08-11 | 2013-08-09 15:02 | -2 | 2013-04-17 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  |  | Rework | 4 (0.5-3k) | Complete |  | Completed |  | Plunge column P32: Electrical testing not done at express yard, testing was only done on site, it happened casue actual P32 cage was used in P35
| 03SR - Stations (RfL) | Cxxx-NCR-000853 | NCR | Plunge column P36: Fabricated short in length |  | Contr |  | PAD - Paddington Station (West) |  | 2013-07-25 | 2013-05-23 12:23 | -63 | 2013-04-17 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | P36 was fabricated short in length at the yard
| 03SR - Stations (RfL) | Cxxx-NCR-000855 | NCR | D-wall panel N1: Rebar cage 150m high in level |  | Contr |  | PAD - Paddington Station (West) |  | 2013-05-31 | 2013-05-14 09:42 | -17 | 2013-04-18 | Structural Engineering - Diaphragm Walls | 500 |  |  | Rework |  | Complete |  | Completed |  | D-wall panel N1: Rebar cage 150m high in level, existing lifting band clashing with capping beam steel
| 03SR - Stations (RfL) | Cxxx-NCR-000856 | NCR | D-wall panel W3/W4: Damage to exisiting water bar |  | Contr |  | PAD - Paddington Station (West) |  | 2013-05-15 | 2013-04-30 12:24 | -15 | 2013-04-18 | Structural Engineering - Diaphragm Walls | 500 |  |  | Repair |  | Complete |  | Completed |  | D-wall panel W3/W4: Damage to exisiting water bar
| 03SR - Stations (RfL) | Cxxx-NCR-000857 | NCR | Dwall panel N5: Start bars damaged during D-wall break down |  | Contr |  | PAD - Paddington Station (West) |  | 2013-06-11 | 2013-06-11 17:21 | 0 | 2013-04-18 | Structural Engineering - Diaphragm Walls | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Dwall panel N5: Start bars damaged and bent during D-wall break down
| 03SR - Stations (RfL) | Cxxx-NCR-000858 | NCR | Panel N75: Back linning wall hit whilst doing the D-wall break down trial |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-08-11 | 2013-08-09 15:09 | -2 | 2013-04-18 | Structural Engineering - Diaphragm Walls | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete |  | Completed |  | Panel N75: Back linning wall hit whilst doing the D-wall break down trial for break down. The coring hit at 1mm of the wall face
| 03SR - Stations (RfL) | Cxxx-NCR-000859 | NCR | GL9-GL11: Repair to damaged existing D-wall, North side |  | Contr |  | PAD - Paddington Station (West) |  | 2013-05-13 | 2013-04-30 12:32 | -13 | 2013-04-18 | Structural Engineering - Diaphragm Walls | 500 |  |  | Repair |  | Complete |  | Completed |  | Between gridline GL9-GL11: Damage to existing D-wall recorded. Attached drawing shows details for damaged area
| 03SR - Stations (RfL) | Cxxx-NCR-000878 | NCR | DN_15: Reinforcement Issues at the D-Wall/Capping Beam Connection Interface |  | Contr |  | PAD - Paddington Station (West) |  | 2013-05-08 | 2013-05-08 12:16 | 0 | 2013-04-24 | Structural Engineering - Concrete Member | 500 |  | Damaged | Use As-Is |  | Complete |  | Completed |  | Following discussions with the CRL/Cxxx team as captured in RFI (ref PAD-CRL-RFI-Cxxx-00860). We require that the following are formally confirmed as acceptable in order to progress with casting DN15 and to provide the supply chain with the relevant NCR reference for the reinforcement as-built drawings. 1) 2no Diaphragm Wall Starter Bars Damaged By Coring – Panel N3 There are 2No. FF vertical bars that have been damaged by core cutting in Panel N3 during the D-Wall breakdown operations. Please confirm that these can be left as is (noting that we are unable to source M__ coupler certification for 50mm diameter bars) Please refer to attached Image_1 2) 7no Diaphragm Wall Starter Bars Bent – Panels N1, W3, W4 The following D-wall starter bars have been bent during break-down works and will foul the capping beam reinforcement (see photo’s attached in Image_2); Panel W3 – 1 x Near Face (NF) Panel W4 – 2 x NF and 1 x Far Face (FF) Panel N1 – 2 x NF and 1 x FF Where they will clash with the capping beam link and / or lacers, it is being proposed that the NF bars are cut directly below the bent section. For the FF bars it is proposed that they are left as is and the capping beam reinforcement locally adjusted to accommodate the. Please confirm this is acceptable. Please note that as this issue is likely to occur in other slabs it would be adventitious if an in principle solution could be reached for this type of problem 3) Starter Bars 230mm High – Panel N1 Panel N1 reinforcement cage has been installed approx 230mm too high and as such the near-face vertical starter bars (19No) are extending into the cover zone. These will also clash with the top mat of the capping beam. Please confirm that trimming these bars by max 150mm to bring them below the line of the reinforcement cage. Note - The far-face bars (19No) are also high requiring the RC detailing to be adjusted to suit the higher level for coupling. 4) Exposed Diaphragm Wall Shear Links – Panel N1 As a result of the reinforcement cage in Panel N1 being high the top layer of shear links is exposed as shown in the attached Image_3. As a result of this the shear links clash with the reinforcement as shown on the attached marked up drawing Cxxx-SKC-C-DWG-B071-WS077-50506. Please confirm it is acceptable to cut the exposed shear links. 5) Exposed Diaphragm Wall Shear Links – Panel N9 The top layer of shear links is partly exposed at the concrete surface of the D-Wall cut-off level. These shear links interfere with the capping beam waterproofing at cut-off level and could act as a water path through the capping beam Please confirm it is acceptable to cut these links.
| 03SR - Stations (RfL) | Cxxx-NCR-000879 | NCR | D-wall break down: GL19-GL24 |  | Contr |  | PAD - Paddington Station (West) |  | 2013-06-26 | 2013-06-17 17:49 | -9 | 2013-04-25 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | From gridline GL19 to GL24, North D-wall broke down 140mm below designed cutt off level (121.750).
| 03SR - Stations (RfL) | Cxxx-NCR-000895 | NCR | Plunge column P2: Possibility of modulus concrete at cut off level |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-02-17 | 2015-02-16 09:27 | -1 | 2013-04-30 | Geotechnical Engineering - Concrete - Bored Pile | 1500 |  |  | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Plunge column P2: The sonic logging report presents concrete as sound & homogenous, the actual graphical presentation shows possibility of modulus concrete at cut off level
| 03SR - Stations (RfL) | Cxxx-NCR-000896 | NCR | P51 damaged and blocked sonic tubes |  | Contr |  | PAD - Paddington Station (West) |  | 2013-05-31 | 2013-05-14 09:05 | -17 | 2013-04-30 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | All tubes bent and damaged during excavation, tube 3 also blocked at approx 73mATD
| 03SR - Stations (RfL) | Cxxx-NCR-000900 | NCR | Plunge column P6 |  | Contr |  | PAD - Paddington Station (West) |  | 2013-05-31 | 2013-05-23 13:02 | -8 | 2013-05-01 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | Please note: this NCR is to be read in conjuction with 537. NCR 537 did not mention clearly the pile no, in pile no P6 , the pile cage feet were set to have the cage 100mm high which would have been within tolerance. However with the additional variance of the adjustment length on the specified couplers this added a further 100mm to the overall cage length which put the top of steel out of tolerance. The feet were not adjusted as the time taken to do this would of meant the construction time would of greatly exceeded the 12 hr limit.
| 03SR - Stations (RfL) | Cxxx-NCR-000901 | NCR | Spray Paint on Roof Slab Binding |  | Contr | JUL | PAD - Paddington Station (West) |  | 2013-10-24 | 2013-10-10 12:43 | -14 | 2013-05-01 | Structural Engineering - Structural Engineering - General | 500 |  | System Defect | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Binding and Reinforcement Sprayed with paint to during installation of strain gauges in DN16
| 03SR - Stations (RfL) | Cxxx-NCR-000902 | NCR | Spray Paint on Roof Slab Blinding - Section DN15 |  | Contr |  | PAD - Paddington Station (West) |  | 2013-06-06 | 2013-05-23 12:29 | -14 | 2013-05-02 | Structural Engineering - Structural Engineering - General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Blinding and reinforcement Sprayed with paint to during installation of strain gauges in DN15 roof slab section
| 03SR - Stations (RfL) | Cxxx-NCR-000909 | NCR | N81: D wall break down cut off level low at North east head wall |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-07-03 | 2013-07-01 14:13 | -2 | 2013-05-08 | Structural Engineering - Reinforcement | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete |  | Completed |  | 3XNo coring holes drilled at a level (121.950), 100mmm below the actual cut off level (122.050), during the D-wall break down
| 03SR - Stations (RfL) | Cxxx-NCR-000910 | NCR | N10/N11 hydrophillic strip not installaed to construction issue drawing |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-09-26 | 2013-09-10 16:42 | -16 | 2013-05-09 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete |  | Completed |  | The hydrophillic strip and it was fixed south of the dumbell rather than north, as specified, due to site constraints from diaphram wall breakdown
| 03SR - Stations (RfL) | Cxxx-NCR-000920 | NCR | Byrnes Cube Storage for Roof Slab |  | Contr |  | PAD - Paddington Station (West) |  | 2013-06-02 | 2013-05-21 17:23 | -12 | 2013-05-13 | Structural Engineering - Concrete Member | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Byrnes have been removing their concrete cubes to the testing lab when they are still fresh at the end of the concrete pour. The journey by van would induce vibration into the cubes that does not comply with BS EN 12390-2:2009. They have done this for cubes for DN15 & DN16.
| 03SR - Stations (RfL) | Cxxx-NCR-000924 | NCR | Damaged rebar during D-wall break down |  | Contr |  | PAD - Paddington Station (West) |  | 2013-06-07 | 2013-06-07 17:36 | 0 | 2013-05-17 | Structural Engineering - Diaphragm Walls | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | 5xNo starter bars damaged during D-wall break down. Please refer to the attached file for the summary location and dimension
| 03SR - Stations (RfL) | Cxxx-NCR-000938 | NCR | Unapproved curing membrane DN15-17 |  | Contr |  | PAD - Paddington Station (West) |  | 2013-06-21 | 2013-06-21 17:56 | 0 | 2013-05-21 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Adocure is the approved curing membrane product. This was not used for the top of pours DN15, 16, 17. SURE CURE (data sheet attached) was used. (It was commented that a Greenlease container was found on site. This is not an approved material. Byrnes insists that this i snot theirs and they have not used this product).
| 03SR - Stations (RfL) | Cxxx-NCR-000939 | NCR | Plunge column P2: Signal lost 900mm below cut off level |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-12-31 | 2014-06-11 12:20 | -203 | 2013-05-23 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | There is a signal loss in the 900mm section of casted bored pile under cut off level. Please see the atttached sonic logging report
| 03SR - Stations (RfL) | Cxxx-NCR-000940 | NCR | Concrete line hold down bolts DN15 & DN16 |  | Contr |  | PAD - Paddington Station (West) |  | 2013-06-23 | 2013-06-20 08:42 | -3 | 2013-05-23 | Structural Engineering - Concrete Member | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | 2 No. 16mm diameter divvy dag bars were post drill and fixed at approximate 5m centres along DN15 & 16. These were used to hold down Byrnes concrete line for the pour of DN17. Byrnes have been rebriefed that permission must be obtained prior to casting any materials in.
| 03SR - Stations (RfL) | Cxxx-NCR-000941 | NCR | Plunge column: P6 blockage recorded during sonic logging testing |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-08-12 | 2013-07-30 17:52 | -13 | 2013-05-23 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Sonic logging tests results show blockages at Plunge column P6. Sonic logging tests results show blockages at Plunge column P6. Only one tube is clear to full depth. Rest of the 3 blocked gone past 55m depth. Piling records attached
| 03SR - Stations (RfL) | Cxxx-NCR-000944 | NCR | Damage to Magnetic Extensometer C20-06 |  | Contr | JUL | PAD - Paddington Station (West) |  | 2013-07-31 | 2013-07-30 08:44 | -1 | 2013-05-29 | Geotechnical Engineering - Geotechnical Monitoring | 5000 |  | Damaged | Rework | 3 (3-6k) | Complete |  | Completed |  | Instrument was damaged and will need Jet-washing to clear the base sensors. Currently 5no out of 7no sensors can be read
| 03SR - Stations (RfL) | Cxxx-NCR-000955 | NCR | Vertical rate concrete placing in roof slab |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-07-23 | 2013-07-25 12:39 | 2 | 2013-05-30 | Civil - Structural Engineering | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The vertical rate in the roof slab pours has been monitored and is less than 2m/hour
| 03SR - Stations (RfL) | Cxxx-NCR-000958 | NCR | DN28: __ apllied wrong way |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-12-31 | 2014-10-03 09:44 | -89 | 2013-05-31 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | A small section of __ 300R which is adhered to D Wallwith Bituthene LM along GL24 has been laid reversed with the active side not in contact with the slab pour concrete.
| 03SR - Stations (RfL) | Cxxx-NCR-000960 | NCR | Pre-condition photos for inclinometers installation |  | Contr |  | PAD - Paddington Station (West) |  | 2013-07-01 | 2013-07-01 10:54 | 0 | 2013-06-03 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete |  | Completed |  | Photographic records were not provided for the following inclinometers installation: Cxxx-IG-CS-05 Cxxx-IG-E6-01 Cxxx-ID-A10-11 Cxxx-ID-A4-07 Cxxx-ID-A2-05 Cxxx-ID-A7-27 Cxxx-ID-A8-32 Cxxx-ID-B1-03 Cxxx-ID-A9-36 Cxxx-ID-A5-25 Cxxx-ID-A17-15 Cxxx-ID-A23-19 Cxxx-ID-A2-17 The above instruments were installed between June & October 2012. Most of them were installed on August 2012.
| 03SR - Stations (RfL) | Cxxx-NCR-000962 | NCR | D-wall Panel N44/N45 joint: Wrong orientation of installed water bar |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-06-12 | 2015-06-21 11:37 | 9 | 2013-06-03 | Structural Engineering - Diaphragm Walls | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Water bar at D-wall panel joints N44/N45, wrong orientation and direction
| 03SR - Stations (RfL) | Cxxx-NCR-000966 | NCR | Unsound concrete in D-wall panels in south roof slab connection |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-07-25 | 2013-07-18 12:39 | -7 | 2013-06-07 | Civil - Structural Engineering | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | As the coupler box outs have been exposed in the south D-wall for DS8, there is evidense of concrete in localised areas without agregate or containing sand. It is probable that this will occur in numerous locations along the south D-wall Further details to follow.
| 03SR - Stations (RfL) | Cxxx-NCR-000967 | NCR | Damage to plunge column plate dowels |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-08-30 | 2013-08-29 13:42 | -1 | 2013-06-10 | Civil - Civil Engineering General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | 1no 150mm dowel bar bent at circa 35degrees from vertical.
| 03SR - Stations (RfL) | Cxxx-NCR-000969 | NCR | D-wall Panels N58, N59, N60: Loose concrete at front/back face & presence of bentonite |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-07-25 | 2013-07-25 15:45 | 0 | 2013-06-10 | Structural Engineering - Diaphragm Walls | 2500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete |  | Completed |  | During the break down of North D-wall panels, Panels N58, N59, N60 have good got loose concrete and sand at front and back face. This will affect DN24, DN25 concrete pours for capping beams
| 03SR - Stations (RfL) | Cxxx-NCR-000970 | NCR | Verticality check of Magnetic Extensometer boreholes |  | Contr | JUL | PAD - Paddington Station (West) |  | 2013-09-01 | 2013-08-08 14:24 | -24 | 2013-06-11 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | When the boreholes were excavated no testing was carried out to prove that it was within the specification provdied
| 03SR - Stations (RfL) | Cxxx-NCR-000972 | NCR | Cover in chamfer area of spine beams |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-07-24 | 2013-07-22 12:30 | -2 | 2013-06-11 | Structural Engineering - Structural Engineering - General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | The nominal cover on the precast spine beam drawings is noted as 25mm. This has not been achieved in areas at the ends of the panels where the panels are joined together with grout. The cover in this zone has been 12mm. This has occured in panels: • 1 No. S002 (Cast 06/06/13) • 1No. SS003 (Cast 10/06/13) • 3 No. S004 (Cast 10/06/13, 6/6/13, 7/6/13)
| 03SR - Stations (RfL) | Cxxx-NCR-000977 | NCR | Pre condition survey for installation of Tell Tale Crack Meters and Vibrating Wire Tilt Sensors |  | Contr | JUL | PAD - Paddington Station (West) |  | 2013-07-10 | 2013-07-07 12:26 | -3 | 2013-06-12 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete |  | Completed |  | No photographic evidence is provided.
| 03SR - Stations (RfL) | Cxxx-NCR-000978 | NCR | Verticality of Rod Extensometer |  | Contr | JUL | PAD - Paddington Station (West) |  | 2013-07-25 | 2013-07-18 14:24 | -7 | 2013-06-18 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Verticality Check was not completed on installation.
| 03SR - Stations (RfL) | Cxxx-NCR-000981 | NCR | D-wall panels S2, S3, S4: Presence of Sand & loose concrete at Box outs |  | Contr |  | PAD - Paddington Station (West) |  | 2013-07-24 | 2013-07-25 15:49 | 1 | 2013-06-13 | Structural Engineering - Diaphragm Walls | 500 |  |  | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the exposure of box outs at D-wall panels S2, S3 & S4, there are imminent signs for presence of sand and loose concrete. As a result of it there is visibility of sonic tubes as well.
| 03SR - Stations (RfL) | Cxxx-NCR-000985 | NCR | Plunge Column P18 Dimensions out of tolerance |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-08-12 | 2013-07-30 17:52 | -13 | 2013-06-14 | Structural Engineering - Structural Engineering - General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Upon inspection after delivery to site of column P18. The dimensions at the bottom of the North side (Outside of Flange West to Outside of Flange East) measured 8mm. Which does not conform to the specification. The attached sketch shows a visual interpretation of the non conformance.
| 03SR - Stations (RfL) | Cxxx-NCR-000989 | NCR | Precast Mix_10mm Aggregate |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-07-14 | 2013-07-07 12:12 | -7 | 2013-06-16 | Structural Engineering - Concrete Member | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete |  | Completed |  | The precast concrete mix (referenced as “mix 14”) currently being used for the precast soffit panels contains 10mm aggregate in place of the 20mm aggregate noted in the accepted precast mix design previously proposed. The decision to make this alteration to the concrete mix was taken by / in response to the concerns raised regarding the use of a 20mm aggregate mix in elements that have a nominal 25mm cover (minimum 21mm). In the absence of a trial mix, and a sufficient time frame to obtain one, written confirmation from __ has been obtained to confirm that since the design is primarily designed for early strength development, the change in aggregate size will have no detrimental effect to the characteristic strength of the concrete. It is noted that the precast soffit panels do not act as part of the structure. Please refer to attached __ confirmation and draft MCR and confirm that this is acceptable for the spine beam precast elements.
| 03SR - Stations (RfL) | Cxxx-NCR-000993 | NCR | Cxxx inclinometer blockage |  | Contr | JUL | PAD - Paddington Station (West) |  | 2013-09-13 | 2013-09-13 14:00 | 0 | 2013-06-18 | Geotechnical Engineering - Ground Investigation | 1500 |  | Damaged | Rework | 4 (0.5-3k) | Complete |  | Completed |  | Cxxx inclinometer (Cxxx-IM300001) located outside East head wall was identified to be blocked at 3m depth. It is suspected that the blockage could have occurred due to Manhole 5 works which was at close proximity. The instrument was isolated and protected from the surface during the Manhole 5 works.
| 03SR - Stations (RfL) | Cxxx-NCR-000999 | NCR | DN28 Non-compliant surface concrete |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-09-27 | 2013-09-24 16:34 | -3 | 2013-06-20 | Structural Engineering - Structural Engineering - General | 3000 |  | Design | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | There is a localised area where the concrete has a very high density of blow holes
| 03SR - Stations (RfL) | Cxxx-NCR-001001 | NCR | Concrete cube strength DN16 |  | Contr |  | PAD - Paddington Station (West) |  | 2014-01-30 | 2014-01-23 14:22 | -7 | 2013-06-20 | Structural Engineering - Structural Engineering - General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | C40/50 Roof Concrete Cube failure for Roof Slab DN16 Please see cube results sheet for cube series 210 B, C
| 03SR - Stations (RfL) | Cxxx-NCR-001005 | NCR | Damaged couplers DS02 & DS08 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-07-21 | 2013-07-25 19:09 | 4 | 2013-06-21 | Structural Engineering - Diaphragm Walls | 10000 |  | Damaged | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Upon exposing the coupler box outs, it has been a number of couplers that can not be repaired in the panels on the attached sketch.
| 03SR - Stations (RfL) | Cxxx-NCR-001006 | NCR | Grout test for rod extensometers |  | Contr | JUL | PAD - Paddington Station (West) |  | 2013-09-26 | 2013-09-11 14:22 | -15 | 2013-06-21 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete |  | Completed |  | No grout test was carried out since the samples taken were not appropriate/suitable for any test.
| 03SR - Stations (RfL) | Cxxx-NCR-001007 | NCR | Out of Level Tolerance couplers_S9,S10,S16 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-08-16 | 2013-07-30 18:02 | -17 | 2013-06-22 | Structural Engineering - Diaphragm Walls | 2500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The couplers in the diaphragm wall at panels S9 and S10 are high. On panel S9 the couplers are 100mm – 120mm from the top of slab On panel S10 the couplers are 125mm -140mm from the top of slab In both of the above cases the couplers clash with the T2 layer of reinforcement as shown on the attached sketch. On panel S16 the bottom row of couplers are out of tolerance. The centre of the coupler is 105mm from the bottom of the slab. This clashes directly with the B2 layer of reinforcement.
| 03SR - Stations (RfL) | Cxxx-NCR-001009 | NCR | DN27_4no Missing Starters |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-07-01 | 2013-07-01 16:49 | 0 | 2013-06-22 | Structural Engineering - Reinforcement | 500 |  | Design | Rework | 4 (0.5-3k) | Complete |  | Completed |  | 4no 16 diameter wall starters in DN27 have not been included, as highlighted in the attached. We’re proposing to drill and fix to an embedment of 400mm using __ HY150 Max resin.
| 03SR - Stations (RfL) | Cxxx-NCR-001017 | NCR | Panel S3_Screw bar cannot be engaged. |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-07-24 | 2013-07-25 12:48 | 1 | 2013-06-25 | Structural Engineering - Reinforcement | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The attached markup highlights a coupler on panel S3 that cannot be engaged due to the coupler being cast at an angle within the diaphragm wall resulting in the coupler facing downwards. As the coupler is facing downwards we cannot engage the screw bar as it clashes with the bottom mat.
| 03SR - Stations (RfL) | Cxxx-NCR-001021 | NCR | Strain gauge sensor exposed, Panel S16 |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2013-07-29 | 2013-07-30 12:59 | 1 | 2013-07-03 17:17 | Civil - Geotechnical Engineering | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete |  | Completed |  | One of the embedded Strain gauges on the panel S16 was exposed during the concrete repairs on this panel.
| 03SR - Stations (RfL) | Cxxx-NCR-001022 | NCR | Pre-condition survey photos for installed Vibrating Wire Crack Sensors |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-08-22 | 2013-08-09 13:33 | -13 | 2013-07-05 12:57 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete |  | Completed |  | Pre-condition survey photos were not taken prior to installation of Vibrating Wire Crack Sensors
| 03SR - Stations (RfL) | Cxxx-NCR-001024 | NCR | Inclinometer B1-03 [damage] |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-08-30 | 2013-07-30 17:54 | -31 | 2013-07-08 14:23 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The void former was not extended above the top of the roof slab and as a consequence the void former was filled and burried with concrete. The current status is that the inclinometer is out of action.
| 03SR - Stations (RfL) | Cxxx-NCR-001025 | NCR | Piezometer C7-10 Grout Test |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-08-31 | 2013-08-09 09:55 | -22 | 2013-07-08 14:38 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete |  | Completed |  | No tests for compressive strength have been undertaken. This is not in accordance with the accepted ITP.
| 03SR - Stations (RfL) | Cxxx-NCR-001026 | NCR | Magnetic extensometer C7-12 Grout test |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-09-26 | 2013-09-11 14:27 | -15 | 2013-07-08 14:47 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete |  | Completed |  | The grout used to fill around the instrument was not tested for compressive strength. This is not in accordance with the accepted ITP.
| 03SR - Stations (RfL) | Cxxx-NCR-001027 | NCR | Inclinometer Grout testing |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-09-26 | 2013-09-06 17:10 | -20 | 2013-07-08 14:58 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete |  | Completed |  | Compressive strength testing has not been undertaken for the following inclinometers: E2-04, D1-01, C1-02, E4-06, A13-13, E21-16, E23-18, D24-20, C24-21, E5-24, E7-26, E8-30, E8-33, E10-10 & B24-22. This testing is included in the accepted ITP.
| 03SR - Stations (RfL) | Cxxx-NCR-001028 | NCR | Inclinometer Pack 3 Spiral surveys |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-08-31 | 2013-08-23 14:57 | -8 | 2013-07-08 15:08 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Material | Rework | 4 (0.5-3k) | Complete |  | Completed |  | For the following inclinometers the casing groove spiral survey indicated partial non-compliances: E2-04, D1-01, C1-02, E4-06, A13-13, E21-16, E23-18, D24-20, C24-21, E5-24, E7-26, E8-30, E8-33, E10-10, B24-22, E9-67, E13-11, E13-12 & E17-14. Maximum acceptable value is 0.75 degrees/metre.
| 03SR - Stations (RfL) | Cxxx-NCR-001029 | NCR | Inclinometer Pack 3 Pre-condition photographs |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-08-31 | 2013-08-09 09:41 | -22 | 2013-07-08 15:25 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete |  | Completed |  | For the following inclinometers the pre-condition photographs were not taken: E2-04, D1-01, C1-02, E4-06, A13-13, E21-16, E23-18, D24-20, C24-21, E5-24, E7-26, E8-30, E8-33, E10-10, B24-22, E9-57, E13-11, E13-12 & E17-14.
| 03SR - Stations (RfL) | Cxxx-NCR-001031 | NCR | Plunge Columns in P47 and P50 Swapped |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-08-14 | 2013-07-26 09:14 | -19 | 2013-07-09 16:31 | Structural Engineering - Steel Member | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | During the installation process of Plunge columns in the tension piles, Columns for P47 and P50 were swapped. Note: These columns are of the same type.
| 03SR - Stations (RfL) | Cxxx-NCR-001033 | NCR | Shrinkage cracks within __-L-42 gridline 1-2 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-09-16 | 2013-08-09 09:44 | -38 | 2013-07-09 17:15 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | some Post concrete shinkage cracks cracks have appeared within the vertical face of __-L-42
| 03SR - Stations (RfL) | Cxxx-NCR-001034 | NCR | __-L-42 (GL 2) Concrete finish to kicker not to specification |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-11-28 | 2013-11-14 15:57 | -14 | 2013-07-10 08:58 | Civil - Civil Engineering General | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | On striking the Kicker formwork, some sections of the kicker was not within the specification and had some 'pin holes' visible.
| 03SR - Stations (RfL) | Cxxx-NCR-001035 | NCR | __-T-23 (GL 6) starter bars excessively bent to allow walkway access |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-11-30 | 2014-08-13 15:10 | -109 | 2013-07-10 09:11 | Civil - Civil Engineering General | 1000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Starter bars excessively bent excessively to allow walkway access accross the roof slab
| 03SR - Stations (RfL) | Cxxx-NCR-001037 | NCR | Adding water to DS02 concrete |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-12-18 | 2013-12-16 14:41 | -2 | 2013-07-10 15:55 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | A single load of concrete in pour DS02 narrowly failed its slump test. The __ materials expert happened to be on site at the time of the occurance and confirmed the quantity of water to be added to the wagon such that it met the water:cement ratio meets the design. They did not inform and hence did not follow the approved procedure
| 03SR - Stations (RfL) | Cxxx-NCR-001038 | NCR | DS08 delayed retarding characteristics |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-09-20 | 2013-09-15 10:22 | -5 | 2013-07-10 16:37 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | DS08 pour was finished at approximately 18.30 08/07/13 and at 09.00 on 09/07/13 it appeared to still be slightly compressible. Throughout the day the concrete hardened and the surface was finished using a power float in line with the previous pours.
| 03SR - Stations (RfL) | Cxxx-NCR-001040 | NCR | D-Wall Panel S70 joint to S71 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-09-11 | 2013-09-05 14:46 | -6 | 2013-07-13 12:57 | Structural Engineering - Diaphragm Walls | 3500 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | During the exposure of box outs at D-wall panels S70 and S71, a certain amount of sand intrusion into the box out was found. this was removed and traced back towards the joint of S70 and S71 at which point the removal stopped as it was nearing the the location of the waterbar.
| 03SR - Stations (RfL) | Cxxx-NCR-001041 | NCR | DS03 infill no formal sign off of DDCD |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-08-23 | 2013-08-09 13:34 | -14 | 2013-07-18 11:02 | Civil - Structural Engineering | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete |  | Completed |  | A pour was started on DS03 including the GL8-9 infill base for the grab. The site team fixed the steel to the C01 drawing, but DDCD for the infill element of the pour was not formally signed off by Cxxx prior to the pour commencing. Email confirmation was received by the designers of acceptability of C01 drawings prior to concrete reaching the infill end of the pour. The DS03 main slab DDCD was all signed off prior to pouring.
| 03SR - Stations (RfL) | Cxxx-NCR-001044 | NCR | __ walls-Starter bars bent excessively |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-12-26 | 2013-11-28 19:34 | -28 | 2013-07-19 16:09 | Civil - Civil Engineering General | 1500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The starter bars on wall __-T-15,__-T-23,__-T-02 and __-T-03 starter bars have been bent excessively to allow site access as shown on attached sketch.
| 03SR - Stations (RfL) | Cxxx-NCR-001045 | NCR | Wall __-L-38 / 43; kicker pour cast without lacers bar reinforcment (GL12-13) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-09-18 | 2013-09-17 17:34 | -1 | 2013-07-19 16:44 | Civil - Civil Engineering General | 1000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Walls __-L-38 / 43 kicker pours were cast without lacers bar reinforcment
| 03SR - Stations (RfL) | Cxxx-NCR-001046 | NCR | Couplers in Precast – DS4 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-07-29 | 2013-07-30 12:54 | 1 | 2013-07-22 13:50 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete |  | Completed |  | One coupler can’t be exposed in the precast soffit S-002 at gridline 10 – 6m.
| 03SR - Stations (RfL) | Cxxx-NCR-001047 | NCR | Starter bar in bottom mat Between DS9 - 10 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-07-30 | 2013-07-30 18:04 | 0 | 2013-07-22 14:09 | Structural Engineering - Reinforcement | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The starter bar between PF 52 & 53 (BM 12 B25) from DS9 lap length is 600mm instead of 1150mm
| 03SR - Stations (RfL) | Cxxx-NCR-001048 | NCR | Damage to plunge column plate dowels |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-09-09 | 2013-09-05 13:48 | -4 | 2013-07-23 09:08 | Civil - Civil Engineering General | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 3no 150mm 25mm dia welded shear dowel bars bent during excavation works for roof slab formation.
| 03SR - Stations (RfL) | Cxxx-NCR-001049 | NCR | Plunge column plate dowel repair without approved procedure in place |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-08-30 | 2013-08-23 16:13 | -7 | 2013-07-23 10:16 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete |  | Completed |  | Remedial works carried out to damaged shear stud on plunge column capping plate at GL 8(+5.8)/C without required documents in place. Remedial works were accelerated to mitigate delay. No approved procedure in place
| 03SR - Stations (RfL) | Cxxx-NCR-001050 | NCR | Vesicular concrete in roof slab pour DN28 |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2016-02-29 | 2016-02-27 16:25 | -2 | 2013-07-23 12:39 | Structural Engineering - Concrete Member | 2500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Following technical meetings with , Byrnes Bros and __ we are advised that the concrete used in DN28 has suffered a reaction between the high GGBS content and high doseage of Glenium sky 569 superplasticiser. this has resulted in vesicular concrete within the pour. The extent of this has not yet been established, however it is clearly visible on cores taken and at the surface.
| 03SR - Stations (RfL) | Cxxx-NCR-001051 | NCR | Column kickers – DS8 & 9 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-09-16 | 2013-09-11 13:52 | -5 | 2013-07-23 15:04 | Structural Engineering - Reinforcement | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | refer to drawing Cxxx-SWN-S-DDA-M171_2-01564 rev C05 The kickers, for the columns on DS8 & 9 were cast without the links right links.
| 03SR - Stations (RfL) | Cxxx-NCR-001052 | NCR | Concrete Roof Slab DN 15 TOC levels |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-10-15 | 2016-08-24 07:22 | -52 | 2013-07-23 18:51 | Structural Engineering - Structural Engineering - General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Finished concrete levels in DN 15 are out of tolerance to NSCS for Basic slab finish (+/- 12mm) at highlighted location on attached drawing.
| 03SR - Stations (RfL) | Cxxx-NCR-001053 | NCR | Commencing work without required permit to load in place for South D-Wall Removal Stage 1 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-10-22 | 2013-10-21 15:18 | -1 | 2013-07-24 08:43 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | on the 23/07/2013, work was started without a required permit to load in place. A Permit to Load was required before any wire saw works could be started on the South Diaphraghm walls, the works started and was stopped after one cut. The permit to load has since been issued to allow works to continue as per the agreed method.
| 03SR - Stations (RfL) | Cxxx-NCR-001054 | NCR | Coupler Top mat Between DS3 - 4 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-07-28 | 2013-08-07 11:45 | 10 | 2013-07-24 10:40 | Structural Engineering - Reinforcement | 750 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A coupler between PF 40 & 29 beams from DS3 is missing
| 03SR - Stations (RfL) | Cxxx-NCR-001055 | NCR | Damaged shear dowel on plunge column plate |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-08-30 | 2013-08-29 13:41 | -1 | 2013-07-24 12:56 | Civil - Civil Engineering General | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete |  | Completed |  | 1no 300mm shear dowel bent by an excavator during ground work on a B38-I plate on GL 10(+6.110m)/C.
| 03SR - Stations (RfL) | Cxxx-NCR-001056 | NCR | __-L-38;Columns kickers on DS8 and DS9 cast with incorrect reinforcement |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-09-18 | 2013-09-20 08:27 | 2 | 2013-07-24 16:43 | Civil - Civil Engineering General | 1000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __-L-38;2 columns on the west side of DS8 and the 2 columns on DS9 were cast with the incorrect reinforcement detail
| 03SR - Stations (RfL) | Cxxx-NCR-001057 | NCR | Signatures missing from Pile record hold point check sheets (General). |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-09-01 | 2013-07-30 09:58 | -33 | 2013-07-25 12:55 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete |  | Completed |  | Upon review of pile records it has been noted that signatures were missing from Section 16 (hold point check sheet). These items have been reviewed by and have been initialled retrospectively based on evidence from site records. This NCR refers to the following Items: P43 – Item 39 – Checking cross hole sonic reservation tubes prior to capping and concreting. P43 – Item 51 – Plunge column bolted connections P49 – Item 39 – Checking cross hole sonic reservation tubes prior to capping and concreting. P49 – Item 57B – Concrete for biscuit P49 – Item 58 – Pile Bore Backfill P51 – Item 39 – Checking cross hole sonic reservation tubes prior to capping and concreting. P51 – Item 56 – Release of Cemloc. Note: P51 was constructed on a Saturday, column locked in the Cemloc at 19:00. Work did not commence until 08:00 on the Monday (>36 hours). P51 – Item 57B – Concrete for biscuit P51 – Item 58 – Pile Bore Backfill
| 03SR - Stations (RfL) | Cxxx-NCR-001058 | NCR | Signature missing from Pile record hold point check sheets (P46 Plunge Column Bolted Connection). |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-12-01 | 2014-12-03 15:40 | 2 | 2013-07-25 13:14 | Structural Engineering - Bolted Connections | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Not Defined | Completed |  | Upon review of pile records for P46 it has been noted that a signature is not available for Section 16 (hold point check sheet), item 51 – Plunge Column Bolted Connection. This item has been reviewed by and although an engineer was on site to witness this, no signature has been provided. Please note that out of 49 columns installed this is the only one where a signature is unable to be justified for this item.
| 03SR - Stations (RfL) | Cxxx-NCR-001059 | NCR | Signatures missing from Pile record hold point check sheets (P49 and P51 Concrete Biscuit levels). |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-04-30 | 2014-04-29 16:39 | -1 | 2013-07-25 13:19 | Structural Engineering - Structural Engineering - General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Upon review of pile records for P49 and P51 it has been noted that a signature is not available for Section 16 (hold point check sheet), item 5A – Concrete Biscuit level. This item has been reviewed by and although an engineer was on site to witness this, no signature has been provided. Please note that having reviewed the site records, the correct volume of concrete was added to the pile. This NCR will be taken into consideration when excavation commences.
| 03SR - Stations (RfL) | Cxxx-NCR-001060 | NCR | Junction of __-L-40 and __-T-13;starter bars bent at 90 degrees |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-09-18 | 2013-09-17 16:30 | -1 | 2013-07-25 17:12 | Civil - Civil Engineering General | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | At the Junction of __-L-40 and __-T-13 4 number starter bars bent at 90 degrees
| 03SR - Stations (RfL) | Cxxx-NCR-001061 | NCR | Piezometer Sensors |  | Contr | JUL | PAD - Paddington Station (West) |  | 2014-01-21 | 2014-01-21 14:51 | 0 | 2013-08-08 17:22 | Geotechnical Engineering - Geotechnical Monitoring | 2500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | The following 5 No piezometers were installed at the required depth but with a range that will not be able to record hydrostatic pressure and may not record a change in pressure until the ground water pressure falls below the range of the installed piezometer. Borehole C7-10 @ 81m ATD Borehole C12-02 @ 82.4 & 66.4m ATD Borehole C20-03 @ 82.4 & 66.4m ATD There is no specified piezometer ranges in the specification.
| 03SR - Stations (RfL) | Cxxx-NCR-001062 | NCR | Header Beam B4 and B9 camber |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-08-31 | 2013-08-22 09:55 | -9 | 2013-07-25 18:24 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Header Beam B4 (L=4475mm) and B9 (L=5325mm) are both curved with a deviation of 9mm from the horizontal. The allowable deviation in accordance with NSSS 5th edition 7.4.9 is for a maximum 6mm, meaning both B4 and B9 are curved to be 3mm out of tolerance.
| 03SR - Stations (RfL) | Cxxx-NCR-001063 | NCR | 20Ø half round drip rebate ommited from DN15 |  | Contr | MMD | PAD - Paddington Station (West) |  | 2015-02-24 | 2015-02-20 08:41 | -4 | 2013-07-26 13:11 | Structural Engineering - Structural Engineering - General | 2500 |  | Material | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Omission of the 20Ø mm half round cast-in drip rebate in __ slab DN15. ref to drawing: Cxxx-SWN-S-DDD-M171_Z-05550 rev C03
| 03SR - Stations (RfL) | Cxxx-NCR-001064 | NCR | D-Wall Cage Starter Bars Position DN16 |  | Contr | MMD | PAD - Paddington Station (West) |  | 2013-11-06 | 2013-10-25 17:25 | -12 | 2013-07-26 15:52 | Structural Engineering - Reinforcement | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The D-wall starter bar and vertical lapping portion of the slab T1 L-bar is, in some localised areas, greater than 50mm (or 4x bar diameter whichever is smaller) across the length of the capping beam in DN16.
| 03SR - Stations (RfL) | Cxxx-NCR-001065 | NCR | DN19 soffit blinding level; localised area out of tolerance |  | Contr | MMD | PAD - Paddington Station (West) |  | 2013-09-10 | 2013-09-06 17:12 | -4 | 2013-07-26 15:54 | Structural Engineering - Structural Engineering - General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete |  | Completed |  | The concrete blinding for the soffit of DN19 slab has localised areas that are out of tolerance – see survey attached.
| 03SR - Stations (RfL) | Cxxx-NCR-001066 | NCR | Operatives not following ITP re repairs to concrete at DN17 |  | Contr | MMD | PAD - Paddington Station (West) |  | 2016-07-31 | 2016-06-30 08:10 | -31 | 2013-07-26 15:55 | Structural Engineering - Structural Engineering - General | 2500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Cxxx-SKC-C-ITP-B071_WS077-50009 (ITP) Operatives not following ITP procedure (section 49) with regard to repairs to concrete at the Departure Road Level slab DN17. An area of finished works (slab side wall in the opening on gridline D/8) was mistakenly scabbled and then repaired immediately. This was not flagged up to __F’s QA engineers and subsequently not offered up to / CRL for inspection.
| 03SR - Stations (RfL) | Cxxx-NCR-001067 | NCR | Use of Unapproved Curing Agent and Release on Slabs DN15 - 17 |  | Contr | MMD | PAD - Paddington Station (West) |  | 2013-10-09 | 2013-09-15 10:26 | -24 | 2013-07-26 15:58 | Structural Engineering - Reinforcement | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Use of an unapproved curing agent (Surecure S) on the __ slabs DN15 to DN17. Possible incompatibility with future waterproofing products.
| 03SR - Stations (RfL) | Cxxx-NCR-001068 | NCR | Roof Slab DN17 – side couplers |  | Contr | MMD | PAD - Paddington Station (West) |  | 2013-09-04 | 2013-09-03 14:18 | -1 | 2013-07-26 15:59 | Structural Engineering - Reinforcement | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | refer to Cxxx-SWN-S-DDA-M171_2-01562 rev C05 Cxxx-SKC-C-DWG-B071_WS077-50524 rev C01 There are 4no B25 BM-51 couplers missed out from pour DN17, grid line D/8, see mark-up attached.
| 03SR - Stations (RfL) | Cxxx-NCR-001069 | NCR | Concrete Delivery DN 15 |  | Contr | MMD | PAD - Paddington Station (West) |  | 2013-09-09 | 2013-08-30 08:40 | -10 | 2013-07-26 14:59 | Structural Engineering - Structural Engineering - General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete |  | Completed |  | Concrete Deliveries, Batches 800458 to 800464,were delivered 70mins apart exceeding the 60 min maximum specified in KF11.3204 h)
| 03SR - Stations (RfL) | Cxxx-NCR-001070 | NCR | Concrete Delivery DN 15 |  | Contr | MMD | PAD - Paddington Station (West) |  | 2013-08-23 | 2013-08-23 17:48 | 0 | 2013-07-26 15:03 | Structural Engineering - Structural Engineering - General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete |  | Completed |  | Concrete Delivery Batch 800458 was slumped at 200mm, to comply with S5 specification it should be 220mm minimum
| 03SR - Stations (RfL) | Cxxx-NCR-001072 | NCR | Blinding Concrete DN 16 |  | Contr | MMD | PAD - Paddington Station (West) |  | 2013-08-23 | 2013-08-23 17:51 | 0 | 2013-07-26 16:06 | Structural Engineering - Structural Engineering - General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete |  | Completed |  | Blinding concrete levels in DN 16 are out of tolerance (+/-5mm) as highlighted location on attached drawing.
| 03SR - Stations (RfL) | Cxxx-NCR-001073 | NCR | Concrete Delivery DN 16 |  | Contr | MMD | PAD - Paddington Station (West) |  | 2013-08-23 | 2013-08-19 09:51 | -4 | 2013-07-26 16:09 | Structural Engineering - Structural Engineering - General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Concrete Delivery Batch 807176 was slumped at 200mm, to comply with S5 specification it should be 220mm minimum
| 03SR - Stations (RfL) | Cxxx-NCR-001074 | NCR | Concrete Delivery DN 16, Batches 807218 to 807224 to 807230 |  | Contr | MMD | PAD - Paddington Station (West) |  | 2013-09-09 | 2013-08-30 08:42 | -10 | 2013-07-26 16:13 | Structural Engineering - Reinforcement | 500 |  | Material | Rework | 4 (0.5-3k) | Complete |  | Completed |  | Concrete Deliveries, Batches 807218 to 807224 to 807230,were delivered 70mins and 85 mins apart respectively exceeding the 60 min maximum specified in KF11.3204 h)
| 03SR - Stations (RfL) | Cxxx-NCR-001075 | NCR | Concrete Roof Slab DN 16 TOC |  | Contr | MMD | PAD - Paddington Station (West) |  | 2015-09-01 | 2015-06-25 09:35 | -68 | 2013-07-26 16:18 | Structural Engineering - Structural Engineering - General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Finished concrete levels in DN 16 are out of tolerance to NSCS for Basic slab finish (+/- 12mm) at highlighted locations on attached drawing.
| 03SR - Stations (RfL) | Cxxx-NCR-001076 | NCR | Blinding Concrete DN 17 |  | Contr | MMD | PAD - Paddington Station (West) |  | 2013-08-30 | 2013-08-29 17:59 | -1 | 2013-07-26 16:21 | Structural Engineering - Structural Engineering - General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete |  | Completed |  | Blinding concrete levels in DN 17 are out of tolerance (+/-5mm) as highlighted location on attached drawing.
| 03SR - Stations (RfL) | Cxxx-NCR-001077 | NCR | Concrete Roof Slab DN 17 TOC |  | Contr | MMD | PAD - Paddington Station (West) |  | 2013-09-24 | 2013-09-20 09:50 | -4 | 2013-07-26 16:25 | Structural Engineering - Structural Engineering - General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Finished concrete levels in DN 17 are out of tolerance to NSCS for Basic slab finish (+/- 12mm) at highlighted locations on attached drawing.
| 03SR - Stations (RfL) | Cxxx-NCR-001078 | NCR | Blinding Concrete DN 18 and 19 TOC |  | Contr | MMD | PAD - Paddington Station (West) |  | 2013-08-23 | 2013-08-23 17:52 | 0 | 2013-07-26 16:30 | Structural Engineering - Structural Engineering - General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete |  | Completed |  | Blinding concrete levels in DN 18 & 19 are out of tolerance (+/-5mm) as highlighted location on attached drawing.
| 03SR - Stations (RfL) | Cxxx-NCR-001079 | NCR | DN17 Wall Starter Bars |  | Contr | MMD | PAD - Paddington Station (West) |  | 2013-08-30 | 2013-08-30 11:59 | 0 | 2013-07-26 16:46 | Structural Engineering - Reinforcement | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | DRAWING REFERENCE: Cxxx-SKC-C-DWG-B071_WS077-50524 rev C01 Deviation from the approved construction ‘Wall Starter Bar RC Detail’ drawing (as referenced above) for DN17 without a formal FCD number or RFI response being received.
| 03SR - Stations (RfL) | Cxxx-NCR-001080 | NCR | DS 5 – 7 no B25 CP missed out |  | Contr | MMD | PAD - Paddington Station (West) |  | 2013-08-12 | 2013-08-09 14:57 | -3 | 2013-07-29 11:43 | Structural Engineering - Reinforcement | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | DRAWING REFERENCE: Cxxx-SKC-C-DWG-B071_WS077-51560 7 CP B25 – 66 side bars were missed from pour DS5.
| 03SR - Stations (RfL) | Cxxx-NCR-001081 | NCR | DS 4 and 5 - Shear rails missing |  | Contr | MMD | PAD - Paddington Station (West) |  | 2013-08-28 | 2013-08-23 17:54 | -5 | 2013-07-29 11:51 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 67 no shear studs missing from pour DS4 10 no shear studs missing from pour DS5, see as-built attached.
| 03SR - Stations (RfL) | Cxxx-NCR-001082 | NCR | Wall kicker – DS8 & 9 (wall __-L-38 and __-L-43) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-11-13 | 2013-09-15 10:33 | -59 | 2013-08-01 08:30 | Civil - Civil Engineering General | 1500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The kickers, for wall __-L-38 (from 100 high on the south side and 280mm on the north side)& L43 (145mm high) on pour DS8 (grid line 12-13), were cast without lacers.
| 03SR - Stations (RfL) | Cxxx-NCR-001083 | NCR | IPI installation in E1-01 |  | Contr | JUL | PAD - Paddington Station (West) |  | 2013-08-22 | 2013-08-23 17:55 | 1 | 2013-08-01 13:32 | Civil - Geotechnical Engineering | 1000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete |  | Completed |  | Uni-axial IPI sensors was installed in the ground inclinometer as opposed to bi-axial sensors. The variation was identified while reviewing the data.
| 03SR - Stations (RfL) | Cxxx-NCR-001084 | NCR | Surveying rod extensometer head level |  | Contr | JUL | PAD - Paddington Station (West) |  | 2013-09-30 | 2013-10-02 12:34 | 2 | 2013-08-02 09:42 | Civil - Geotechnical Engineering | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | The head of the rod extensometers should be surveyed to identify the surface movement and consider that in interpretation (Cxxx-OVE-Z4-RSP-CR001-00007, KX10.3216 refers) This has not been carried out.
| 03SR - Stations (RfL) | Cxxx-NCR-001085 | NCR | DS08 slab - Void around reinforcement |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2013-08-30 | 2013-08-28 09:03 | -2 | 2013-08-01 14:12 | Structural Engineering - Concrete Member | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete |  | Completed |  | Poor concrete and voids around reinforcement identified followed striking of shutter and scabbling of construction joint between __ slab DS08 and DS07. See attached photos for reference.
| 03SR - Stations (RfL) | Cxxx-NCR-001086 | NCR | Blocked inclinometers |  | Contr | JUL | PAD - Paddington Station (West) |  | 2013-09-06 | 2013-08-24 13:24 | -13 | 2013-08-05 15:52 | Civil - Geotechnical Engineering | 1500 |  | System Defect | Rework | 4 (0.5-3k) | Complete |  | Completed |  | Inclinometers should be monitored as per I&M plans. The following inclinometers are filled with debris. E5-24, E7-26 & E8-33.
| 03SR - Stations (RfL) | Cxxx-NCR-001087 | NCR | Kicker DN28: T-40, T-27 and L-46 walls |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2013-09-27 | 2013-09-15 10:39 | -12 | 2013-08-06 12:14 | Civil - Civil Engineering General | 1500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The wall kicker at DN28, walls T-40, T-27 and L-46 walls presents a poor workmanship: grout loss and inadequate vibration that cause poor concrete finish.
| 03SR - Stations (RfL) | Cxxx-NCR-001088 | NCR | Incorrect capping plate fitted to P23 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-09-05 | 2013-09-02 12:08 | -3 | 2013-08-06 17:48 | Civil - Civil Engineering General | 1000 |  | Material | Rework | 4 (0.5-3k) | Complete |  | Completed |  | Due to a B38-I capping plate (300mm shear dowels) being unavailable for installation, a B38 plate (150mm dowels) was used to enable blinding works to progress.
| 03SR - Stations (RfL) | Cxxx-NCR-001089 | NCR | Monitoring the inclinometers in north D-wall |  | Contr | JUL | PAD - Paddington Station (West) |  | 2013-08-29 | 2013-08-27 13:29 | -2 | 2013-08-06 18:08 | Civil - Geotechnical Engineering | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete |  | Completed |  | Inclinometers within the 20m zone of monitoring should be read daily. The following north D-Wall inclinometers were not read due to safe access issue in the haul road: E4-06, E5-24, E7-26, E8-30 & E8-33.
| 03SR - Stations (RfL) | Cxxx-NCR-001090 | NCR | Plunge column P44 strain gauges |  | Contr | JUL | PAD - Paddington Station (West) |  | 2013-08-30 | 2013-08-27 11:03 | -3 | 2013-08-09 10:07 | Civil - Geotechnical Engineering | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete |  | Completed |  | The Plunge Column 44 strain gauge cables were not recovered prior to roof slab blinding. These strain gauges are additional to Cxxx requirements and were installed to include redundancy. All Cxxx plunge column strain gauge cables have been exposed.
| 03SR - Stations (RfL) | Cxxx-NCR-001091 | NCR | Coupler Top mat Between DS6 -7 |  | Contr | MMD | PAD - Paddington Station (West) |  | 2013-09-27 | 2013-09-26 17:54 | -1 | 2013-08-12 11:23 | Structural Engineering - Reinforcement | 750 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 1 CP B25 wasn’t cast in DS6 for DS7, PF-96 B/12 T2, see sketch attached
| 03SR - Stations (RfL) | Cxxx-NCR-001093 | NCR | Concrete Roof slab DN27 TOC |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-06-01 | 2015-06-17 17:18 | -350 | 2013-08-13 16:07 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | There are a number of levels on the asbuilt that show top of roof slab in DN27 are higher than NSCS allows.
| 03SR - Stations (RfL) | Cxxx-NCR-001094 | NCR | Concrete Roof Slab DN 28 TOC |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-07-31 | 2016-05-24 15:45 | -68 | 2013-08-13 16:16 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Finished concrete levels in DN 28 are out of tolerance to NSCS for Basic slab finish. Out of tollerance in both too high in some locations and too low in others.
| 03SR - Stations (RfL) | Cxxx-NCR-001095 | NCR | E15-07 inclinometer blocked and unrecoverable |  | Contr | JUL | PAD - Paddington Station (West) |  | 2014-02-12 | 2014-02-12 09:23 | 0 | 2013-08-15 17:03 | Civil - Geotechnical Engineering | 10000 |  | Damaged | Rework | 2 (6-60k) | Complete | Material/Preservation Problems - Other | Completed |  | E15-07 inclinometer blocked and damaged and could not be recovered by jetwashing.
| 03SR - Stations (RfL) | Cxxx-NCR-001096 | NCR | Unapproved 10mm roof slab mix DS07 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-10-31 | 2013-10-04 16:40 | -27 | 2013-08-16 14:52 | Civil - Civil Engineering General | 500 |  | System Defect | Rework | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | The approved reinforcement design for DS07 had extremely heavily congested reinforcement. Concern was raised and the Contractor set up risk reductions meetings held to ensure buildability of the slab. The designer permitted reinforcement to be omitted in localised areas to alleviate the congestion, allow steel to be fixed and help concrete flow. This suggestion was acted upon and some of the permitted steel omitted. However, the congestion issue was still heavily prevalent in a much larger area of the slab than the permitted areas of omission and a decision was made by the Contractor to try and get a 10mm aggregate mix approved to help with concrete flow. The 10mm mix was the corresponding of the existing 20mm mix and reviewed and signed off by the subcontractors expert and the Contractors Engineering Manager. Attached is the approved 20mm mix and the corresponding 10mm mix MCR. Due to the uncertain nature of the extent of reinforcement congestion until the steel was fixed, the application for the new 10mm mix was 14.00 the day before the pour. CRL advised the only authorised people to sign off MCRs were on holiday. A decision was made by the Contractor to proceed with the 10mm mix for the following reasons: 1. The risk of rejection of the 10mm mix was assessed to be relatively low because all previous 10mm mixes, which have corresponding accepted 20mm mixes, have been accepted (including the same mixes with more and less admixture). 2. The risk of quality issues with using the accepted 20mm mix was assessed to be greater than using the 10mm mix. There were 7 No. loads of 10mm mix used in the heavily congested areas of DS07
| 03SR - Stations (RfL) | Cxxx-NCR-001097 | NCR | Minimum I&M weekly requirements |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2013-10-01 | 2013-09-27 14:34 | -4 | 2013-08-16 16:48 | Civil - Geotechnical Engineering | 500 |  | System Defect | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | As per the CTC on 08.08.2013,where it was agreed that the weekly readings for the total number of Cxxx inclinometers within the box will be presented once per week. This information was not presented as agreed, the requirement was not achieved. The information has been missed, weekly, since beginning of the week 12.08.13 until last week13.09.2013 (total of 5 weeks) 12-16.08.2013
| 03SR - Stations (RfL) | Cxxx-NCR-001098 | NCR | Damage to Plunge column P38 strain gauge cables |  | Contr | JUL | PAD - Paddington Station (West) |  | 2013-09-02 | 2013-09-02 14:50 | 0 | 2013-08-19 12:04 | Civil - Geotechnical Engineering | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete |  | Completed |  | I&M instruments should be guarded from damage due to construction activities. The plunge column 38 strain gauge cables were damaged due to construction activity on 14/08/2013 even though the cables were protected as agreed with construction team.
| 03SR - Stations (RfL) | Cxxx-NCR-001099 | NCR | Piezometer C7-10 damaged during bulk excavation |  | Contr | JUL | PAD - Paddington Station (West) |  | 2013-09-27 | 2013-09-05 15:48 | -22 | 2013-08-19 12:12 | Civil - Geotechnical Engineering | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete |  | Completed |  | Piezometer C7-10 borehole cables were damaged/severed during bulk excavation below roof slab on 16/08/2013 night shift. The excavation was not suppose to go beyond gridline C in the south.
| 03SR - Stations (RfL) | Cxxx-NCR-001100 | NCR | Blocked inclinometer C1-02 |  | Contr | JUL | PAD - Paddington Station (West) |  | 2013-09-17 | 2013-09-05 16:03 | -12 | 2013-08-20 09:14 | Civil - Geotechnical Engineering | 1000 |  | System Defect | Rework | 4 (0.5-3k) | Complete |  | Completed |  | Unable to monitor Inclinometer C1-02 in the west head wall as it is blocked and requires jetwashing. The planned jetwashing (on 18/08/2013) did not happen as it was cancelled.
| 03SR - Stations (RfL) | Cxxx-NCR-001101 | NCR | Installation Records, Roof Slab Strain gauges |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2013-09-12 | 2013-09-11 14:44 | -1 | 2013-08-20 14:01 | Civil - Geotechnical Engineering | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete |  | Completed |  | According with the Cxxx Specification Cxxx-SWN-S-RSP-B071-00014, KX10.2109, the installation records and measurement records shall be provided by the Contractor to the Project Manager within 24 hours of the installation or reading respectively. The installations records for the Strain gauges on the DS1, DN15, DS2, DN16,DS3,DS9,DN28 and DS14 Roof Slabs were not submitted 24 hours after the installation. The instrument references are: * Cxxx-G-D3-R-01- DN15 * Cxxx-G-B3-R-02- DS1 *Cxxx-G-D7-R-07 - DN16 * Cxxx-G-B7-R-08 -DS2 * Cxxx-G-B7-R-09 - DS3 * Cxxx-G-B13-R-14 – DS09 * Cxxx-G- D22-R-25 – DN28 * Cxxx-G-B22-R-26 – DS14
| 03SR - Stations (RfL) | Cxxx-NCR-001102 | NCR | DS10 - Ticket 804016 missing time |  | Contr | MMD | PAD - Paddington Station (West) |  | 2013-09-19 | 2013-09-20 08:25 | 1 | 2013-08-20 18:13 | Structural Engineering - Structural Engineering - General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During concrete pour for Roof Slab DS10, operative missed to record the time of discharge for ticket 804016.
| 03SR - Stations (RfL) | Cxxx-NCR-001103 | NCR | North D-wall starter bars damage N31-N60 |  | Contr | MMD | PAD - Paddington Station (West) |  | 2013-09-26 | 2013-09-23 17:08 | -3 | 2013-08-21 15:47 | Structural Engineering - Diaphragm Walls | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During break down of the North D-wall the panels N31-N60 starter bars were damage by rock drill. Far face: 5No starter bars (see attached pictures) with up to 4mm damage in cross section area. Panel N36 – 2nd bar B40, 300mm above cut off level refer to drawing: Cxxx-SWN-S-DDD-M171_Z-55543 Panel N36 – 12th bar B40, 350mm above cut off level refer to drawing: Cxxx-SWN-S-DDD-M171_Z-55543 Panel N39 – 8th bar B40, 400mm above cut off level refer to drawing: Cxxx-SWN-S-DDD-M171_Z-55543 Panel N45 – 9th bar B40, 300mm above cut off level refer to drawing: Cxxx-SWN-S-DDD-M171_Z-55543 Panel N46 – 2nd bar B50, 450mm above cut off level refer to drawing: Cxxx-SWN-S-DDD-M171_Z-55548 Near face: 40mm starter bars with minor damage of ribs on the surface of rebar with no visible damage to the cross section. (see typical minor damage picture) see sketches attached with note core drill (note this should be rock drill) on the near face.
| 03SR - Stations (RfL) | Cxxx-NCR-001104 | NCR | __ L 39 - Cast in Bolts without Signed MCR |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-09-05 | 2013-08-24 13:25 | -12 | 2013-08-22 11:14 | Civil - Civil Engineering General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete |  | Completed |  | __ L 39 GL2-4 walls concreted with casting bolts without relevant MCR sign off.
| 03SR - Stations (RfL) | Cxxx-NCR-001105 | NCR | Shear dowels (7no) on header beam B1 GL17/C damaged by excavator |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-09-21 | 2013-08-29 18:06 | -23 | 2013-08-22 14:35 | Civil - Civil Engineering General | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete |  | Completed |  | During backfilling operation, excavator tracked over the tenporarily burried beam postion and subsequestly bent 7no 150mm shear dowels.
| 03SR - Stations (RfL) | Cxxx-NCR-001106 | NCR | DS11 - position T1 and T3 |  | Contr | MMD | PAD - Paddington Station (West) |  | 2013-09-21 | 2013-10-04 17:27 | 13 | 2013-08-22 17:28 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Refer to drawing: Cxxx-SKC-C-DWG-B071_WS077-50552 rev C01 In NE corner, the top reinforcement BM24 - centres of layers T1 and T3 are located 110mm and 190mm respectively below top soffit. In discussion with designer Cxxx was mentioned the structural capacity of section will be reduced (crack width) and would need to be reassessed.
| 03SR - Stations (RfL) | Cxxx-NCR-001107 | NCR | Qaulity assurance - no qaulity plan in place for CES |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-11-19 | 2013-11-24 11:03 | 5 | 2013-08-23 16:44 | Civil - Geotechnical Engineering | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The sub contractor __ Enviromental Services, have not put into place an approved quality plan as required by Works Information, Volume 2B, Part 20.
| 03SR - Stations (RfL) | Cxxx-NCR-001108 | NCR | Qaulity assurance - no qaulity plan in place for Datum Monitoring services |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-11-19 | 2013-11-24 11:20 | 5 | 2013-08-23 16:52 | Civil - Geotechnical Engineering | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The sub contractor Datum Monitoring Services, have not put into place an approved quality plan as required by Works Information, Volume 2B, Part 20.
| 03SR - Stations (RfL) | Cxxx-NCR-001109 | NCR | DS11 - 10No B40 CP missing at T4 |  | Contr | MMD | PAD - Paddington Station (West) |  | 2013-09-22 | 2013-10-04 17:24 | 12 | 2013-08-23 18:46 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Refer to drawing: Cxxx-SKC-C-DWG-B071_WS077-50557 mark up 10No missing couplers in T4 layer - 150mm c/c. see sketch
| 03SR - Stations (RfL) | Cxxx-NCR-001110 | NCR | Piezometer C7-11 damaged during bulk excavation |  | Contr | JUL | PAD - Paddington Station (West) |  | 2013-09-10 | 2013-09-05 15:53 | -5 | 2013-08-27 09:38 | Civil - Geotechnical Engineering | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete |  | Completed |  | Piezometer C7-11 is not monitored as per I&M requirement since the sensor cables (3no.) were severed/damaged due to construction activities below the roof slab level.
| 03SR - Stations (RfL) | Cxxx-NCR-001111 | NCR | Magnetic Extensometer C7-12 damaged during bulk excavation |  | Contr | JUL | PAD - Paddington Station (West) |  | 2013-11-20 | 2013-10-18 14:26 | -33 | 2013-08-27 09:44 | Civil - Geotechnical Engineering | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The Magnetic Extensometer C7-12 is not monitored as per I&M requirement since it was damaged during bulk excavation on 23/08/2013.
| 03SR - Stations (RfL) | Cxxx-NCR-001113 | NCR | DN20 and DN21 - cages misalignment GL 10 to 12 |  | Contr | MMD | PAD - Paddington Station (West) |  | 2014-10-31 | 2014-08-20 10:40 | -72 | 2013-08-30 17:48 | Structural Engineering - Structural Engineering - General | 5000 |  | Workmanship | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | GL10 - GL12/E, North D-wall reinforcement cages were installed twisted with unknown cover below roof slab level.
| 03SR - Stations (RfL) | Cxxx-NCR-001114 | NCR | Damage to Soffit of DN15 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-07-31 | 2014-07-22 09:53 | -9 | 2013-09-03 13:13 | Structural Engineering - Concrete Member | 10000 |  | Damaged | Rework | 2 (6-60k) | Complete | Management Problem - Inadequate supervision | Completed |  | During the process of excavating the main box, accidental damage was caused to the concrete finish on the soffit of DN15. This was caused by a breaker/pecker which was being used to remove the blinding from the soffit of the slab. Note that upon inspection from dig level, no reinforcement has been exposed. A photo has been attached to this NCR.
| 03SR - Stations (RfL) | Cxxx-NCR-001115 | NCR | Damage to Soffit of DN16 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-09-30 | 2014-07-22 10:04 | -70 | 2013-09-03 13:39 | Structural Engineering - Concrete Member | 1500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During the process of excavating the main box, accidental damage was caused to the concrete finish on the soffit of DN16. This was caused by a breaker/pecker which was being used to remove the blinding from the soffit of the slab. Note that upon inspection from dig level, no reinforcement has been exposed.
| 03SR - Stations (RfL) | Cxxx-NCR-001116 | NCR | Damage to Soffit of DS01 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-09-30 | 2014-07-22 10:05 | -70 | 2013-09-03 13:48 | Structural Engineering - Concrete Member | 2000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During the process of excavating the main box, accidental damage was caused to the concrete finish on the soffit of DS01. This was caused by a breaker/pecker which was being used to remove the blinding from the soffit of the slab. Note that upon inspection from dig level, no reinforcement has been exposed.
| 03SR - Stations (RfL) | Cxxx-NCR-001117 | NCR | Damage to Soffit of DS02 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-09-30 | 2014-06-17 11:59 | -105 | 2013-09-03 13:51 | Structural Engineering - Concrete Member | 2000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | During the process of excavating the main box, accidental damage was caused to the concrete finish on the soffit of DS02. This was caused by a breaker/pecker which was being used to remove the blinding from the soffit of the slab. Note that upon inspection from dig level, no reinforcement has been exposed.
| 03SR - Stations (RfL) | Cxxx-NCR-001118 | NCR | Damaged Shear Stud on P1 during bulk excavation |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-09-30 | 2013-09-26 17:58 | -4 | 2013-09-03 14:48 | Structural Engineering - Steel Member | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 2 No Shear Studs Damaged at North Face of Plunge Column No 1 at Intermediate Level During Main box Excavation Works. See attached photograph for detail.
| 03SR - Stations (RfL) | Cxxx-NCR-001119 | NCR | Inclinometer - Daily monitoring |  | Contr | JUL | PAD - Paddington Station (West) |  | 2013-10-07 | 2013-10-01 14:37 | -6 | 2013-09-09 15:26 | Civil - Geotechnical Engineering | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | Not all inclinometers within 20m zone of excavation is monitored on 08/09/2013 due to damage to Geokon probe communication unit. Two main inclinometer probe comms units are damaged; one each on Saturday (07/09/13) & Sunday (08/09/13). On Sunday the comms unit failed after covering the daily north inclinometers and south inclinometers are not monitored. The third probe was already utilized for spare parts.
| 03SR - Stations (RfL) | Cxxx-NCR-001120 | NCR | N56 roof slab level substandard concrete |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-10-10 | 2013-10-03 13:55 | -7 | 2013-09-10 17:28 | Civil - Civil Engineering General | 2500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Panel N56 contains concrete that has presence of bentonite, sand and lack of presence of aggregate. This has been discovered during the diaphragm wall breakdown activity. The attached photo shows the breaking part complete.
| 03SR - Stations (RfL) | Cxxx-NCR-001122 | NCR | __-L-36 Panel 70 (column 66) poor concrete finish |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-10-15 | 2013-10-04 17:36 | -11 | 2013-09-13 11:45 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Concrete finish to the north face of panel 70 (column 66) not to specification. Clear visible vertical line where concrete looks of not to have settled against the shutter. See attached photo
| 03SR - Stations (RfL) | Cxxx-NCR-001125 | NCR | D-Wall Pannel N1 (North Face) - Coupler level too high |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-10-15 | 2013-10-14 12:51 | -1 | 2013-09-13 15:37 | Structural Engineering - Diaphragm Walls | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Level of couplers in the north face of D-wall pannel N1 is too high out of tollerance, as per the conditions setout in DDCD Cxxx-SKC-07-XCS-B071¬_WS077-50382.
| 03SR - Stations (RfL) | Cxxx-NCR-001126 | NCR | D-Wall Pannel W1 - Couplers too high |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-10-15 | 2013-10-14 12:58 | -1 | 2013-09-13 15:50 | Structural Engineering - Diaphragm Walls | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Level of bottom row of couplers, in left and center section of box out, in the D-wall pannel W1 is too low and out of tollerance, as per the conditions setout in DDCD Cxxx-SKC-07-XCS-B071¬_WS077-50382.
| 03SR - Stations (RfL) | Cxxx-NCR-001127 | NCR | D-Wall Pannel W1 - 1No. Coupler Damaged |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-10-15 | 2013-10-18 14:45 | 3 | 2013-09-13 16:05 | Structural Engineering - Diaphragm Walls | 750 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 1No. coupler, second form left on top row, from top row in D-wall pannel W1 is damaged and cannot be used.
| 03SR - Stations (RfL) | Cxxx-NCR-001128 | NCR | High Spots in Blinding for Intermediate Slab |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-10-22 | 2013-10-22 12:26 | 0 | 2013-09-13 16:12 | Structural Engineering - Formwork | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | High spots identified within blinding for intermediate slab.
| 03SR - Stations (RfL) | Cxxx-NCR-001129 | NCR | DN22/DN23 couplers not found |  | Contr | MMD | PAD - Paddington Station (West) |  | 2013-10-16 | 2013-11-06 09:38 | 21 | 2013-09-16 12:13 | Structural Engineering - Reinforcement | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 1No BM 07 coupler wasn't found in DN22/DN23 construction joint. See sketch.
| 03SR - Stations (RfL) | Cxxx-NCR-001130 | NCR | __-L-40; pull out bars |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-09-30 | 2013-10-10 13:25 | 10 | 2013-09-16 15:49 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | __-L-40 pull out bars are B16 and not B20 as detailed in the design intent
| 03SR - Stations (RfL) | Cxxx-NCR-001131 | NCR | DS01 – wall starters |  | Contr | MMD | PAD - Paddington Station (West) |  | 2013-10-17 | 2013-10-25 17:23 | 8 | 2013-09-17 09:16 | Structural Engineering - Reinforcement | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Refer to drawing: Cxxx-SKC-C-DWG-B071_WS077-50626- mark up.pdf There are 28no B12 BM-160 starter bars missed out from pour DS01, grid line B/4, see mark-up attached.
| 03SR - Stations (RfL) | Cxxx-NCR-001132 | NCR | __-L-38 Panel 60 (column 64) poor concrete finish |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-12-13 | 2013-10-18 14:46 | -56 | 2013-10-14 16:31 | Civil - Civil Engineering General | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Concrete finish of panel 60 (column 64) not to specification. Concrete on the wall appears to have settled against the shutter. See attached photo.
| 03SR - Stations (RfL) | Cxxx-NCR-001133 | NCR | __-L-38 Panel 56 (column 56) poor concrete finish |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-12-13 | 2013-10-25 12:09 | -49 | 2013-10-14 16:32 | Civil - Civil Engineering General | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Concrete finish to the south face of panel 56 (column 56) not to specification. Concrete on the columns appears to have settled against the shutter, evidence of honeycombing . See attached photo.
| 03SR - Stations (RfL) | Cxxx-NCR-001134 | NCR | DS12 slab non-compliant unformed surface finish |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2013-11-27 | 2013-11-24 11:13 | -3 | 2013-09-19 09:23 | Civil - Civil Engineering General | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | __ level slab DS12 top surface does not comply with project specified unformed plain finish (KF11.1309).
| 03SR - Stations (RfL) | Cxxx-NCR-001135 | NCR | DN23 DN24 non-compliant surface finish |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2016-10-25 | 2016-09-28 10:40 | -27 | 2013-09-19 09:40 | Civil - Civil Engineering General | 2500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | DN23 DN24 slab vertical surface do not comply with project specified plain formed surface finish. (KF11.3227).
| 03SR - Stations (RfL) | Cxxx-NCR-001136 | NCR | DN21 non-compliant surface finish |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2016-10-25 | 2016-09-28 10:39 | -27 | 2013-09-19 09:43 | Civil - Civil Engineering General | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | DN21 slab vertical surface do not comply with project specified plain formed surface finish. (KF11.3227).
| 03SR - Stations (RfL) | Cxxx-NCR-001142 | NCR | DS02 low cube results |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-02-11 | 2014-01-29 08:44 | -13 | 2013-09-23 18:28 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Low 28 day cube results in DS02 are less than 50N/mm2 Attachments to be uploaded once results confirmed
| 03SR - Stations (RfL) | Cxxx-NCR-001143 | NCR | DS09 low cube result |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-01-21 | 2014-01-07 11:18 | -14 | 2013-09-23 18:30 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Low 28 day cube results in DS09 are less than 50N/mm2 Attachments to be uploaded once results confirmed
| 03SR - Stations (RfL) | Cxxx-NCR-001144 | NCR | DS03 low cube result |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-02-11 | 2014-02-07 08:57 | -4 | 2013-09-23 18:32 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Low 28 day cube results in DS03 are less than 50N/mm2 Attachments to be uploaded once results confirmed
| 03SR - Stations (RfL) | Cxxx-NCR-001146 | NCR | DS04-05 low cube result |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-02-28 | 2014-02-28 10:29 | 0 | 2013-09-23 18:44 | Civil - Civil Engineering General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Low 28 day cube results in DS04-05 are less than 50N/mm2 Attachments to be uploaded once results confirmed
| 03SR - Stations (RfL) | Cxxx-NCR-001147 | NCR | DS10 Low cube strength |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-01-21 | 2014-01-07 11:38 | -14 | 2013-09-23 18:53 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The concrete cube results in DS10 are lower that 50N/mm2. Attachments to be uploaded once data verified.
| 03SR - Stations (RfL) | Cxxx-NCR-001148 | NCR | DS11 low cube strength |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-01-21 | 2014-01-07 14:39 | -14 | 2013-09-23 19:01 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The concrete cube results in DS11 are lower that 50N/mm2. Attachments to be uploaded once data verified.
| 03SR - Stations (RfL) | Cxxx-NCR-001149 | NCR | DS07 low cube result |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-01-21 | 2014-01-07 14:42 | -14 | 2013-09-23 19:04 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The concrete cube results in DS07 are lower that 50N/mm2. Attachments to be uploaded once data verified.
| 03SR - Stations (RfL) | Cxxx-NCR-001150 | NCR | DS06 low cube strength |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-01-21 | 2014-01-08 10:47 | -13 | 2013-09-23 19:11 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The concrete cube results in DS06 are lower that 50N/mm2. Attachments to be uploaded once data verified.
| 03SR - Stations (RfL) | Cxxx-NCR-001151 | NCR | __-L-43 GL11;north face of kicker finish |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-10-08 | 2013-10-04 08:51 | -4 | 2013-09-24 12:43 | Civil - Civil Engineering General | 1000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __-L-43 GL11;north face of kicker. During pouring the kicker the kicker moved north slightly resulting in the line of the wall being out of tolerance
| 03SR - Stations (RfL) | Cxxx-NCR-001152 | NCR | Wall cast without signed concrete MCR in place |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-10-30 | 2013-10-23 15:54 | -7 | 2013-09-25 16:00 | Civil - Civil Engineering General | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | some above roof slab walls were cast without signed concrete mix MCR in place
| 03SR - Stations (RfL) | Cxxx-NCR-001153 | NCR | Out of tolerance box outs within IL-1 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-10-29 | 2013-10-25 17:07 | -4 | 2013-09-27 11:29 | Structural Engineering - Formwork | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 3No. box outs are out of the allowable tollerance within the IL-1 slab. The locations and dimensions of thes box outs are shown in the attached survey drawings.
| 03SR - Stations (RfL) | Cxxx-NCR-001154 | NCR | Possible damage to water proofing due to vehilce movement |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-10-30 | 2013-10-15 09:19 | -15 | 2013-09-30 18:04 | Structural Engineering - Surface Treatment | 1500 |  | System Defect | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Due to site logistical constraints, the water proofing contractor had to track his working vehicle on top of existing/already laid water proofing working from GL4 to GL1.
| 03SR - Stations (RfL) | Cxxx-NCR-001155 | NCR | 40 Eastbourne Terrace PLP removal |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-10-15 | 2013-10-08 17:23 | -7 | 2013-10-01 14:05 | Surveying - Instrumentation and Monitoring | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | A PLP was installed to the front facade of 40 Eastbourne terrace by Cxxx, the location where this PLP was installed has now been re-moddeled by the asset owner. This included removing the stone flooring into which the PLP was installed and replacing it with a new surface. The asset owner has denied permission for the PLP to be re-instated into this area, there are no other suitable surfaces in the are for re-installation that the assest owner will allow.
| 03SR - Stations (RfL) | Cxxx-NCR-001156 | NCR | DS5-6 - Compressive cube test failed at 56 day |  | Contr | MMD | PAD - Paddington Station (West) |  | 2014-01-21 | 2014-01-08 10:13 | -13 | 2013-10-01 18:10 | Structural Engineering - Structural Engineering - General | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Concrete compressive cube test for 353D sample failed at 56 days in roof slab sections DS5-6. See attached concrete cube test record.
| 03SR - Stations (RfL) | Cxxx-NCR-001157 | NCR | __-L-44 GL 22;Poor Concrete Finish to southern face of wall L44 2nd Panel from East |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-12-17 | 2013-11-28 19:36 | -19 | 2013-10-02 09:32 | Civil - Civil Engineering General | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | __-L-44 GL 22;Poor Concrete Finish to southern face of wall L44 2nd Panel from East. Please see attached photos for clarity
| 03SR - Stations (RfL) | Cxxx-NCR-001158 | NCR | N64- Water bar cut & repaired at cut off level |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-11-18 | 2014-11-21 09:04 | 3 | 2013-10-02 12:53 | Structural Engineering - Diaphragm Walls | 1000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Water bar was cut and repaired at cut off level.
| 03SR - Stations (RfL) | Cxxx-NCR-001159 | NCR | __-L-43; GL 12.5-GL13 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-11-29 | 2013-11-28 19:38 | -1 | 2013-10-02 15:09 | Civil - Base Course | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | On completion of wall pour, a 30mm bed of water had risen to the top of the wall pour and was sitting on top of the newly poured concrete.
| 03SR - Stations (RfL) | Cxxx-NCR-001161 | NCR | Damage to Strain Guage DN26 (Grid Line 17) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-11-15 | 2013-10-11 14:16 | -35 | 2013-10-03 09:54 | Civil - Structural Engineering | 750 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | __ drove a mobile crane over the cables of DN26 stretching & severing the cables. Severed cables (still in the cable troughing protection) where then thrown into the nearest mole hole. If these cables have stretched under the concrete we will not be able to recover these instruments.
| 03SR - Stations (RfL) | Cxxx-NCR-001162 | NCR | Concrete Test Cube Report Wall __ 38 (Column 62) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-01-28 | 2014-01-29 08:50 | 1 | 2013-10-14 16:18 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Concrete Test Cube Report indicates that concrete cubes taken for Wall __ 38 (Column 62) did not reach 50N/mm2 after 28 days. Please see full Concrete Test Cube Report attached.
| 03SR - Stations (RfL) | Cxxx-NCR-001163 | NCR | Restricted access to Magnetic Extensometer C20-06 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-10-31 | 2013-10-30 17:20 | -1 | 2013-10-03 11:22 | Civil - Geotechnical Engineering | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | __ are installing a temporary platform above magnetic extensometer C20-06 (Grid Line 20) - See attached photograph. Once installed this will restrict access and prevent instrument reading.
| 03SR - Stations (RfL) | Cxxx-NCR-001164 | NCR | Damage to IPI 21-16 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-10-31 | 2013-10-18 14:52 | -13 | 2013-10-03 11:39 | Civil - Geotechnical Engineering | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The cable has been severed and thrown over the wall behind the install. The manhole has been covered with concrete spillage from the slope. (See attached damage report).
| 03SR - Stations (RfL) | Cxxx-NCR-001165 | NCR | IPI E2‐04 covered by north haul road approach ramp |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-11-22 | 2013-11-01 14:25 | -21 | 2013-10-23 15:34 | Civil - Structural Engineering | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During resurfacing the west entrance slope on the north haul road have concreted over the IPI E2‐04 (manhole & all). As a result we can no longer access this instrument
| 03SR - Stations (RfL) | Cxxx-NCR-001166 | NCR | Inclusion of whinch points in IL-1 Slab pour |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-06-06 | 2014-06-09 08:41 | 3 | 2013-10-04 10:04 | Structural Engineering - Inserts | 1500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Winch point not installed in slab IL-1.
| 03SR - Stations (RfL) | Cxxx-NCR-001167 | NCR | DN20 - cube tests at 28 days |  | Contr | MMD | PAD - Paddington Station (West) |  | 2014-01-21 | 2014-01-08 10:52 | -13 | 2013-10-04 17:19 | Structural Engineering - Structural Engineering - General | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Concrete Cube test samples 419b and 419C for Roof slab section DN20 failed at 28 days. See attached test report.
| 03SR - Stations (RfL) | Cxxx-NCR-001168 | NCR | Paxton Canopy Column Inclination |  | Contr | JUL | PAD - Paddington Station (West) |  | 2013-11-05 | 2013-11-07 11:43 | 2 | 2013-10-08 17:00 | Geotechnical Engineering - Settlement | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Paxton Canopy column inclination is not being reported as per Cxxx I&M Plan
| 03SR - Stations (RfL) | Cxxx-NCR-001170 | NCR | DN20 and DN21 - Concrete Cube Strength |  | Contr | MMD | PAD - Paddington Station (West) |  | 2014-01-21 | 2014-01-08 10:54 | -13 | 2013-10-09 09:48 | Structural Engineering - Structural Engineering - General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Concrete cube test for Roof Slab sections DN20 and DN21 failed at 28days - sample 430C. See attached report.
| 03SR - Stations (RfL) | Cxxx-NCR-001171 | NCR | __-L-44 - Concrete Finish (GL20-21.5) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-11-19 | 2013-10-25 11:58 | -25 | 2013-10-14 16:25 | Civil - Civil Engineering General | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Concrete finish to the south face of Panel 80 (GL20-21.5) not to specification. Clear visible vertical line where concrete looks to not have settled against the shutter. See attached photo.
| 03SR - Stations (RfL) | Cxxx-NCR-001172 | NCR | __-L-44 - Concrete Mix (GL20-21.5) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-12-10 | 2013-12-02 12:23 | -8 | 2013-10-14 16:28 | Civil - Civil Engineering General | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Evidence of concrete bleeding found in the pour of __-L-44 (GL20-21.5) , water appears to have risen to the surface - see photo.
| 03SR - Stations (RfL) | Cxxx-NCR-001173 | NCR | __-L38 Concrete Finish (Panel 71@ GL11.5 ) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-11-19 | 2013-10-16 13:24 | -34 | 2013-10-14 16:28 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Concrete finish to the north face of Panel 71 (GL11.5) not to specification. Clear visible vertical line where concrete looks to not have settled against the shutter. See attached RFI with photo.
| 03SR - Stations (RfL) | Cxxx-NCR-001174 | NCR | Damage to Soffit of DN17 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-07-31 | 2014-07-22 10:06 | -9 | 2013-10-11 13:37 | Structural Engineering - Concrete Member | 2500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During the process of excavating the main box, accidental damage was caused to the concrete finish on the soffit of DN17. This was caused by a breaker/pecker which was being used to remove the blinding from the soffit of the slab. Note that upon inspection from dig level, no reinforcement has been exposed.
| 03SR - Stations (RfL) | Cxxx-NCR-001175 | NCR | Damage to Soffit of DS03 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-07-31 | 2014-07-22 10:07 | -9 | 2013-10-11 14:08 | Structural Engineering - Concrete Member | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During the process of excavating the main box, accidental damage was caused to the concrete finish on the soffit of DS03. This was caused by a breaker/pecker which was being used to remove the blinding from the soffit of the slab. Note that upon inspection from dig level, no reinforcement has been exposed.
| 03SR - Stations (RfL) | Cxxx-NCR-001176 | NCR | Damage to Soffit of DN18 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-07-31 | 2014-07-22 10:08 | -9 | 2013-10-11 14:23 | Structural Engineering - Concrete Member | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During the process of excavating the main box, accidental damage was caused to the concrete finish on the soffit of DN18. This was caused by a breaker/pecker which was being used to remove the blinding from the soffit of the slab. Note that upon inspection from dig level, no reinforcement has been exposed.
| 03SR - Stations (RfL) | Cxxx-NCR-001177 | NCR | Damage to Soffit of DS04 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-07-31 | 2014-07-22 10:09 | -9 | 2013-10-11 14:37 | Structural Engineering - Concrete Member | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During the process of excavating the main box, accidental damage was caused to the concrete finish on the soffit of DS04. This was caused by a breaker/pecker which was being used to remove the blinding from the soffit of the slab. Note that upon inspection from dig level, no reinforcement has been exposed.
| 03SR - Stations (RfL) | Cxxx-NCR-001178 | NCR | Damage to Soffit of DN19 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-07-31 | 2014-07-22 10:10 | -9 | 2013-10-11 14:41 | Structural Engineering - Concrete Member | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Details During the process of excavating the main box, accidental damage was caused to the concrete finish on the soffit of DN19. This was caused by a breaker/pecker which was being used to remove the blinding from the soffit of the slab. Note that upon inspection from dig level, no reinforcement has been exposed.
| 03SR - Stations (RfL) | Cxxx-NCR-001179 | NCR | Damage to Soffit of DS05 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-07-31 | 2014-07-22 10:10 | -9 | 2013-10-11 14:47 | Structural Engineering - Concrete Member | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During the process of excavating the main box, accidental damage was caused to the concrete finish on the soffit of DS05. This was caused by a breaker/pecker which was being used to remove the blinding from the soffit of the slab. Note that upon inspection from dig level, no reinforcement has been exposed.
| 03SR - Stations (RfL) | Cxxx-NCR-001180 | NCR | Damage to Soffit of DS06 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-07-31 | 2014-07-22 10:11 | -9 | 2013-10-11 14:51 | Structural Engineering - Concrete Member | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During the process of excavating the main box, accidental damage was caused to the concrete finish on the soffit of DS06. This was caused by a breaker/pecker which was being used to remove the blinding from the soffit of the slab. Note that upon inspection from dig level, no reinforcement has been exposed.
| 03SR - Stations (RfL) | Cxxx-NCR-001181 | NCR | Precast Props encasement construction joint |  | Contr | MMD | PAD - Paddington Station (West) |  | 2014-10-21 | 2014-10-10 14:48 | -11 | 2013-10-13 15:15 | Structural Engineering - Structural Engineering - General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The preparation of the construction joint for grout encasement was not adequate (scabling etc.).
| 03SR - Stations (RfL) | Cxxx-NCR-001182 | NCR | No line of sight to installed prism Cxxx-RP300030 in Osborne Tunnel |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-11-19 | 2013-11-01 08:32 | -18 | 2013-10-15 17:37 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Following the handover of Cxxx ATS as detailed in document Cxxx--C4-RGN-CRT00_ST005-50507 it became apparent that prism Cxxx-RP-300030 was unable to be seen by the installed ATS and the line of sight to the entire zone where this sensor is installed cannot be viewed by any of the installed ATS in the Osborne Tunnel. This prism is missing from the data in the handover document meaning that the obstruction to the line of sight was most likley there at time of handover or existed post commissioning of the system. The lines of sight from ATS33 can be seen in attached images ATS33-1.jpg and ATS33-2.jpg. Form these it can be seen that a large pipe has been installed obstructing the field of view from the ATS. Additionally attached plan Osborne Tunnel - Prism Cxxx-RP300030 - Obstructed Line of Sight_Rev1.pdf shows the area
| 03SR - Stations (RfL) | Cxxx-NCR-001183 | NCR | Damaged to E8-33 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-11-15 | 2013-10-18 14:54 | -28 | 2013-10-16 08:10 | Surveying - Instrumentation and Monitoring | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Whilst the sweeper was cleaning the haul road the barrier in front of the new IPI install at grid line 9 was removed & the sweeper struck the IPI top wheel assembly bending it over. This must have been struck with some force because it lifted the whole IPI assembly out of the inclo tube.
| 03SR - Stations (RfL) | Cxxx-NCR-001184 | NCR | __-L-43 - GL9.5 approx (Part of Panel 61) poor concrete finish |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-11-13 | 2013-10-25 12:00 | -19 | 2013-10-16 18:10 | Civil - Civil Engineering General | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Concrete finish to the south face of Panel 61 (GL9.5 approx) not to specification. Concrete looks to not have settled against the shutter. See attached RFI with photo.
| 03SR - Stations (RfL) | Cxxx-NCR-001185 | NCR | __-L-43 - GL9 approx (Panel 61) poor concrete finish |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-11-13 | 2013-10-25 12:01 | -19 | 2013-10-16 13:35 | Civil - Civil Engineering General | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Concrete finish to the south face of Panel 61 (GL9.5 approx) not to specification. Concrete looks to not have settled against the shutter. See attached RFI with photo
| 03SR - Stations (RfL) | Cxxx-NCR-001189 | NCR | DS12: Water proofing possible error in test results |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-12-10 | 2013-12-06 16:35 | -4 | 2013-10-17 16:45 | Civil - Structural Engineering | 1000 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | DS12 results show 0.6N/mm, ITP presents 0.7N/mm. Clarification required
| 03SR - Stations (RfL) | Cxxx-NCR-001190 | NCR | Cxxx inclinometer blockage |  | Contr | JUL | PAD - Paddington Station (West) |  | 2013-12-20 | 2013-12-22 19:40 | 2 | 2013-12-06 12:09 | Civil - Geotechnical Engineering | 1500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Cxxx inclinometer blocked and probe unable to reach full depth
| 03SR - Stations (RfL) | Cxxx-NCR-001191 | NCR | MH8 Missing Plastic Sheeting |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-11-01 | 2013-11-08 16:43 | 7 | 2013-10-18 17:50 | Civil - Drainage | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | No plastic sheeting membrane was installed in the base of the excavation prior to the blinding layer being poured for MH8.
| 03SR - Stations (RfL) | Cxxx-NCR-001192 | NCR | Breaking out of western upstand for excavation gantry 2 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-07-31 | 2016-07-29 12:39 | -2 | 2013-10-21 10:29 | Structural Engineering - Bolted Connections | 1500 |  | Design | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The western upstand for Excavation Gantry No.2 had a small section broken out for the tie beam to be bolted to the roof slab.
| 03SR - Stations (RfL) | Cxxx-NCR-001193 | NCR | C1-02 Restricted access and blockage |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-11-21 | 2013-10-22 12:49 | -30 | 2013-10-22 10:04 | Surveying - Instrumentation and Monitoring | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | C1-02 has not been read since 18th August or converted to an IPI due to restricted access and blockage at interface with capping beam and DWall
| 03SR - Stations (RfL) | Cxxx-NCR-001194 | NCR | C12 - Piezometers - damaged |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-12-17 | 2013-12-13 11:48 | -4 | 2013-10-22 10:12 | Surveying - Instrumentation and Monitoring | 750 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | __ severed the cables on the C12 piezo's whilst excavating in the bulk dig on Friday 11th October
| 03SR - Stations (RfL) | Cxxx-NCR-001195 | NCR | Cxxx-XM-300001 – Inclinometer blocked |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-11-21 | 2013-11-07 14:03 | -14 | 2013-10-22 14:20 | Surveying - Instrumentation and Monitoring | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Upon inspection of Cxxx-XM-300001 – Inclinometer it was found to be blocked at 17m below ground level.
| 03SR - Stations (RfL) | Cxxx-NCR-001196 | NCR | DS06 Concrete |  | Contr | MMD | PAD - Paddington Station (West) |  | 2014-01-21 | 2014-01-08 10:57 | -13 | 2013-10-23 08:56 | Structural Engineering - Structural Engineering - General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | 2 No Concrete Cubes Failed to Reach 50N/mm2 @ 28 days and 1 No Cube Failed to reach 50N/mm2 @ 56 days
| 03SR - Stations (RfL) | Cxxx-NCR-001197 | NCR | DS07 Concrete |  | Contr | MMD | PAD - Paddington Station (West) |  | 2014-01-21 | 2014-01-07 14:04 | -14 | 2013-10-23 08:59 | Structural Engineering - Structural Engineering - General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | 3 No Concrete Cube sets failed to Reach 50N/mm2 @ 28 days All sets subsequently reached 50N/mm2 @ 56 days
| 03SR - Stations (RfL) | Cxxx-NCR-001198 | NCR | DS10 Concrete |  | Contr | MMD | PAD - Paddington Station (West) |  | 2014-01-21 | 2014-01-08 10:59 | -13 | 2013-10-23 09:02 | Structural Engineering - Structural Engineering - General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | 2 No Concrete Cube sets failed to Reach 50N/mm2 @ 28 days
| 03SR - Stations (RfL) | Cxxx-NCR-001199 | NCR | Installation of precast wall prop |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-01-24 | 2014-01-24 09:57 | 0 | 2013-10-23 09:27 | Civil - Civil Engineering General | 500 |  | System Defect | Rework | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | Precast wall props installed prior to design certificate was approved by CRL
| 03SR - Stations (RfL) | Cxxx-NCR-001200 | NCR | DS11 Concrete |  | Contr | MMD | PAD - Paddington Station (West) |  | 2014-01-21 | 2014-01-08 11:09 | -13 | 2013-10-23 09:06 | Structural Engineering - Structural Engineering - General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | 2 No Concrete Cube sets failed to Reach 50N/mm2 @ 28 days All sets subsequently reached 50N/mm2 @ 56 days
| 03SR - Stations (RfL) | Cxxx-NCR-001201 | NCR | DS12 Concrete |  | Contr | MMD | PAD - Paddington Station (West) |  | 2014-02-11 | 2014-02-23 15:17 | 12 | 2013-10-23 09:09 | Structural Engineering - Structural Engineering - General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | 5 No Concrete Cube sets failed to Reach 50N/mm2 @ 28 days 56 days awaited.
| 03SR - Stations (RfL) | Cxxx-NCR-001202 | NCR | DS13 Concrete |  | Contr | MMD | PAD - Paddington Station (West) |  | 2014-01-21 | 2014-01-08 11:11 | -13 | 2013-10-23 09:13 | Structural Engineering - Structural Engineering - General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | 1 No Concrete Cube sets failed to Reach 50N/mm2 @ 28 days This set subsequently reached 50N/mm2 @ 56 days
| 03SR - Stations (RfL) | Cxxx-NCR-001204 | NCR | __-L-44; concrete cube failed to reached strength at 28 days |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-12-13 | 2013-12-13 11:52 | 0 | 2013-10-30 12:29 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Concrete compliance cubes crushed at 28 days did not reached required strength, please see attached concrete test cube report.
| 03SR - Stations (RfL) | Cxxx-NCR-001205 | NCR | Holes in existing water proofing at North wall between GL1-GL16 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-11-14 | 2013-11-13 15:20 | -1 | 2013-10-31 11:49 | Civil - Structural Engineering | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During the slab pours for North extrension, Byrnes carpenters inserted their formwork divi bars through completed and tested water proofing
| 03SR - Stations (RfL) | Cxxx-NCR-001206 | NCR | Screeding levels high at localised section of GL22 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-11-14 | 2013-11-14 13:32 | 0 | 2013-10-31 12:04 | Civil - Structural Engineering | 2000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Screeding levels at localised area is 60mm higher than approved design, thus affecting construction of Manhole MH10.
| 03SR - Stations (RfL) | Cxxx-NCR-001207 | NCR | Exposed rebar in D-Wall pannel N35 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-04-30 | 2014-04-29 16:45 | -1 | 2013-10-31 15:05 | Structural Engineering - Diaphragm Walls | 5000 |  | Workmanship | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Exposed rebar is present in D-Wall pannel N35, below the capping beam level. See attached photograph.
| 03SR - Stations (RfL) | Cxxx-NCR-001209 | NCR | Verticality of D-Wall pannel W4 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-05-14 | 2014-04-25 16:43 | -19 | 2013-10-31 15:47 | Structural Engineering - Diaphragm Walls | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The verticality of D-wall pannel W4 appears to be out of tollerance.
| 03SR - Stations (RfL) | Cxxx-NCR-001210 | NCR | In-ground Inclinometer B24-22 - Damaged |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-12-20 | 2013-12-22 19:50 | 2 | 2013-10-31 16:07 | Geotechnical Engineering - Geotechnical Monitoring | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | B24-22 has been damaged during the backfilling operation. This has occurred after protective measure were in place (see attached). A machine struck the top of the instrument on 28th October
| 03SR - Stations (RfL) | Cxxx-NCR-001211 | NCR | Damage to existing water proofing at GL22 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-11-15 | 2013-11-14 14:03 | -1 | 2013-11-01 13:02 | Civil - Structural Engineering | 1500 |  | Design | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During the break out of higher screeding at GL22 (Manhole 10) location water proofing was damaged.
| 03SR - Stations (RfL) | Cxxx-NCR-001212 | NCR | Excavator damage to __-T-19 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-11-18 | 2013-11-14 14:05 | -4 | 2013-11-04 08:59 | Civil - Civil Engineering General | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | __ excavator next to the mole hole at GL 8.5 has damaged the corner of wall __-T-19
| 03SR - Stations (RfL) | Cxxx-NCR-001213 | NCR | __-L-44 (GL19) Panel 80 - Concrete Finish |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-01-28 | 2014-01-29 09:29 | 1 | 2013-11-04 09:58 | Civil - Civil Engineering General | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | __-L-44 (GL19) Panel 80 - Concrete Finish. See photo attached.
| 03SR - Stations (RfL) | Cxxx-NCR-001214 | NCR | __-L-38 North Face (GL8-15) - Making Good |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-11-28 | 2013-11-29 15:53 | 1 | 2013-11-05 08:20 | Civil - Civil Engineering General | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | __-L-38 North Face (GL8-15) - Making Good to damaged wall - please see photo attached.
| 03SR - Stations (RfL) | Cxxx-NCR-001215 | NCR | Down water pipes in IL-1 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-08-06 | 2014-07-23 15:27 | -14 | 2013-11-06 14:41 | Structural Engineering - Inserts | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The down water pipes in IL1 were installed as cast iron pipes. The Cxxx specification Cxxx-SWN-M-RSP-B071-00001 Rev08, cl JR12.1407 specifies stainless steel pipes. There is currently a lack of clarity as to whether cast iron pipes were accepted in some form prior to the pour. This NCR is raised to record the issue and allow a thorough investigation to be undertaken.
| 03SR - Stations (RfL) | Cxxx-NCR-001216 | NCR | Untidy water proofing between GL1-GL8 slab section |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-11-26 | 2013-11-29 15:45 | 3 | 2013-11-12 07:27 | Civil - Structural Engineering | 1000 |  | Planning | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Untidy water proofing at slab section between GL1-GL8, as people started to walk on top of finished product without getting _laser approval.
| 03SR - Stations (RfL) | Cxxx-NCR-001217 | NCR | Damage to NGG 355 P.E Main |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-11-26 | 2013-11-29 10:41 | 3 | 2013-11-12 17:20 | Utilities Engineering - Gas | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 2 pipe lengths of the new 355 P.E gas main currently being laid by have been scraped by the excavator carrying out backfilling operations.
| 03SR - Stations (RfL) | Cxxx-NCR-001218 | NCR | Precast Prop grout strength 2 |  | Contr | MMD | PAD - Paddington Station (West) |  | 2014-09-23 | 2014-09-05 15:44 | -18 | 2013-11-13 18:35 | Structural Engineering - Structural Engineering - General | 2500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The precast prop grout failed 28 days test see attached result. The listing of the test results to folllow.
| 03SR - Stations (RfL) | Cxxx-NCR-001219 | NCR | DN20 Low Cube Results |  | Contr | MMD | PAD - Paddington Station (West) |  | 2014-01-21 | 2014-01-08 10:05 | -13 | 2013-11-13 18:53 | Structural Engineering - Structural Engineering - General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Low 28 day cube results in DN20 are less than 50N/mm2 See attachments results.
| 03SR - Stations (RfL) | Cxxx-NCR-001220 | NCR | DN21 Low Cube Results |  | Contr | MMD | PAD - Paddington Station (West) |  | 2014-01-21 | 2014-01-08 17:17 | -13 | 2013-11-13 18:55 | Structural Engineering - Structural Engineering - General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Low 28 day cube results in DN21 are less than 50N/mm2. See attachments results.
| 03SR - Stations (RfL) | Cxxx-NCR-001221 | NCR | DN23 and DN24 Low Cube Results |  | Contr | MMD | PAD - Paddington Station (West) |  | 2014-03-18 | 2014-02-26 09:06 | -20 | 2013-11-13 18:59 | Structural Engineering - Structural Engineering - General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Low 28 day cube results in DN23 and DN24 are less than 50N/mm2. See attachments results.
| 03SR - Stations (RfL) | Cxxx-NCR-001222 | NCR | DN26 Low Cube Results |  | Contr | MMD | PAD - Paddington Station (West) |  | 2014-03-18 | 2014-02-26 09:09 | -20 | 2013-11-13 19:02 | Structural Engineering - Structural Engineering - General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Low 28 day cube results in DN26 are less than 50N/mm2. See attachments results.
| 03SR - Stations (RfL) | Cxxx-NCR-001223 | NCR | NR Lawn Area - Reporting against Cxxx trigger levels |  | Contr | JUL | PAD - Paddington Station (West) |  | 2013-12-10 | 2013-11-24 11:40 | -16 | 2013-11-14 15:17 | Civil - Geotechnical Engineering | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | is not reporting against Cxxx trigger levels in the NR Lawn area for: 1. Vertical differential displacement between columns A and B or C and D 2. Vertical differential displacement between the Lawn and adjacent structures 3. Horizontal differential between columns A and B or C and D
| 03SR - Stations (RfL) | Cxxx-NCR-001224 | NCR | South D Wall Strain Guages S12 & S16 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-12-14 | 2013-11-29 16:13 | -15 | 2013-11-14 19:34 | Surveying - Instrumentation and Monitoring | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | DWall Strain Gauges within panels S12 & S16 were disconnected late on 9th November to facilitate DWall panel breakdown and reduce risk of damage to the strain gauges. This was to be a temporary disconnection and a permanent relocation and reconnection carried out on 11th November. Due to continued DWall breakdown works and inability to locate a suitable permanent and safe relocation, the strain gauges remained disconnected.
| 03SR - Stations (RfL) | Cxxx-NCR-001226 | NCR | C01 trimmed to 100mm of final formation level |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-12-03 | 2013-12-05 13:38 | 2 | 2013-11-19 08:09 | Civil - Excavation | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Regarding Cxxx-FCD-001193: On Friday evening 15/11/13 were verbally informed that it was acceptable to CRL field team & Cxxx to dig to 100mm above finished formation level for concourse works (and not have to blind within 24 hours). were informed that this would sent over formally on PTR in 15 minutes time. The PTR confirmation did not arrive. Subsequently C01 area was trimmed to within 100mm of final formation level over the weekend works. The permit to dig now has been renewed to go back to trimming 300mm within formation level until a PTR response is received.
| 03SR - Stations (RfL) | Cxxx-NCR-001227 | NCR | Damage to C7-12 Magnetic Extensometer |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-12-19 | 2013-12-13 12:05 | -6 | 2013-11-19 10:53 | Geotechnical Engineering - Geotechnical Monitoring | 750 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Sometime during the temperary prop install the Magnetic extensometer C7-12 has been smashed leaving it just above ground level.
| 03SR - Stations (RfL) | Cxxx-NCR-001228 | NCR | DS 04 and 05 Roof Slab Concrete Slump |  | Contr | MMD | PAD - Paddington Station (West) |  | 2014-02-11 | 2014-02-12 10:01 | 1 | 2013-11-19 15:58 | Structural Engineering - Structural Engineering - General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Concrete delivered as S5 slump out of tolerance with S4 slump stated on delivery ticket.
| 03SR - Stations (RfL) | Cxxx-NCR-001229 | NCR | DS08 Roof Slab levels TOC |  | Contr | MMD | PAD - Paddington Station (West) |  | 2014-01-28 | 2014-01-24 09:43 | -4 | 2013-11-19 16:07 | Structural Engineering - Structural Engineering - General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Isolated out of tolerance finished concrete levels at southern limit of slab in six locations
| 03SR - Stations (RfL) | Cxxx-NCR-001230 | NCR | Panel S5 out of verticality tolerance |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-07-31 | 2014-07-25 11:27 | -6 | 2013-11-20 12:53 | Structural Engineering - Diaphragm Walls | 2500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The verticallity of panel S5 may not met the specification requirement of 1 in 200
| 03SR - Stations (RfL) | Cxxx-NCR-001231 | NCR | N17 panel out of verticality tolerance |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-09-30 | 2014-08-29 10:55 | -32 | 2013-11-20 12:59 | Structural Engineering - Diaphragm Walls | 2500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Panel N17 may not have achieved the required verticality of 1 in 200
| 03SR - Stations (RfL) | Cxxx-NCR-001232 | NCR | Capping Plate GL 11 (– 6.110m) / C (Retrospective) |  | Contr | MMD | PAD - Paddington Station (West) |  | 2014-01-29 | 2014-01-14 11:25 | -15 | 2013-11-20 18:05 | Civil - Civil Engineering General | 1500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Shear Stud bent to plunge column capping plate at GL 11 (-6.110m) / C during final trim to reduce level to formation of roof slab.
| 03SR - Stations (RfL) | Cxxx-NCR-001233 | NCR | Installation of track monitoring prisms from Cxxx-FCD-001171 (NR Track prisms 9m spacing) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-12-20 | 2013-12-19 15:05 | -1 | 2013-11-21 16:07 | Surveying - Instrumentation and Monitoring | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Further to Cxxx-FCD-001171 (NR Track prisms 9m spacing) the proposed design for the layout and installation of the monitoring sensors was designed. However during installation it became clear that in using the existing ATS that have been installed not every prism could be installed due to obstructed lines of sight. At approximately between 160m to 180m from the buffer stop along the track well between platforms 3/4, due to the curvature of the track alignment and the obstruction the platform edge, rail position and station structure cause several prisms in the new plan shown on drawing -Cxxx-G-XSK-00224. Platform nib prisms: Cxxx-RP930002, Cxxx-RP930003, Cxxx-RP930004. Track prisms: Cxxx-RP931016.
| 03SR - Stations (RfL) | Cxxx-NCR-001234 | NCR | Chilworth Street compound ATS obstructions |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-12-05 | 2013-12-06 14:52 | 1 | 2013-11-21 17:00 | Surveying - Instrumentation and Monitoring | 500 |  | System Defect | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Due to the installation of the second tier of cabins in Cxxx's Chilworth Street compound the line of sight to the existing prisms on the western facade of 30 Eastbourne Terrace along Chilworth Street can no longer be observed. This affects prisms: CxxxRP120902, CxxxRP120909, CxxxRP120917 However CxxxRP120917 will be re-directed to a alternate ATS, the other prisms though cannot be seen from any other location.
| 03SR - Stations (RfL) | Cxxx-NCR-001235 | NCR | Cxxx extensometer (4no.) |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2013-12-17 | 2014-01-10 13:31 | 24 | 2013-11-22 16:38 | Geotechnical Engineering - Geotechnical Engineering - General | 2500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | As per Cxxx-PMI-00171 issued on 23.07.2013, Cxxx CRL instructed to take over 4no. manually read rod extensometers None of the extensometers (4 no.) have been read during this time. These instrument are covered by the haul road concrete and need to be exposed. This issue was communicated to CRL on 5.11.13. is responsible to survey, repair and maintenance these instruments as per the PMI
| 03SR - Stations (RfL) | Cxxx-NCR-001237 | NCR | Dwaill monitoring not in accordance with I&M Plan |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2013-12-17 | 2013-12-19 12:09 | 2 | 2013-11-26 09:17 | Surveying - Instrumentation and Monitoring | 500 |  | System Defect | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The Employers requirement for Dwall instrumentation was for inclinometers and the monitoring was required to compare movements against trigger levels based on predicted deflections. proposed the use of strain gauges in the Dwalls, which was accepted by the Employer's designer, however to monitor against the predicted deflections need to interpret the data into equivalent movement. It has come to light that the strain gauges are not being monitored against trigger levels in the I&M plan at the required frequency and RFI 1376 has been raised By stating that the method is unusual for this type of monitoring and cannot give full quality results. At the same time requesting details of how to monitor these instruments.
| 03SR - Stations (RfL) | Cxxx-NCR-001238 | NCR | IL-1 Failed Cube Result |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-04-29 | 2014-04-29 17:40 | 0 | 2013-11-28 07:25 | Structural Engineering - Concrete Member | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | 1 No Concrete Cube set failed to reach 28 day strength (set No 479).
| 03SR - Stations (RfL) | Cxxx-NCR-001239 | NCR | IL-1 high spots in finished concrete |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-02-26 | 2014-02-28 10:56 | 2 | 2013-11-28 07:33 | Structural Engineering - Finishes | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Finished concrete out of tolerance in isolated areas (+11mm - +15mm)
| 03SR - Stations (RfL) | Cxxx-NCR-001240 | NCR | Non-cementitious material W1 concourse |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-12-24 | 2013-12-13 14:18 | -11 | 2013-11-28 14:53 | Civil - Structural Engineering | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | When carrying out drilling for drill and fixing remedials of D-wall couplers that are out of level tollerance in W1, non-cementitious material was found after a certain depth.
| 03SR - Stations (RfL) | Cxxx-NCR-001241 | NCR | CT-07 Rod Extensometer |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2014-02-04 | 2014-02-05 12:23 | 1 | 2013-11-28 17:22 | Civil - Geotechnical Engineering | 1500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | CT-07 rod extensometer has not being read as per the I&M plan, this instrument is in place for the __ assets monitoring. has reported a broken antenna.
| 03SR - Stations (RfL) | Cxxx-NCR-001242 | NCR | D-Wall Overbreak, S1 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-07-31 | 2014-07-31 12:14 | 0 | 2013-11-29 13:33 | Structural Engineering - Diaphragm Walls | 1500 |  | Material | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Not Defined | Completed |  | Large overbreak present in D-Wall panel S1 at 118-121ATD. Overbreak is aprox 2.5mx3m and petruding 900mm.
| 03SR - Stations (RfL) | Cxxx-NCR-001243 | NCR | DN 23 and 24 TOC levels |  | Contr | MMD | PAD - Paddington Station (West) |  | 2015-12-23 | 2015-12-10 10:58 | -13 | 2013-11-29 16:11 | Structural Engineering - Structural Engineering - General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Slab finished level out of tolerance in one location (+12mm)
| 03SR - Stations (RfL) | Cxxx-NCR-001244 | NCR | Non-cementitious material panel S1 concourse |  | Contr | MMD | PAD - Paddington Station (West) |  | 2013-12-29 | 2013-12-19 14:37 | -10 | 2013-11-29 17:16 | Structural Engineering - Diaphragm Walls | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | There are several cavities in D-Wall panel S1B that are full of non cementitious debris, the majority of it being clay. This is preventing pouring the Concourse Slab 1.
| 03SR - Stations (RfL) | Cxxx-NCR-001245 | NCR | Non-cementitious material W4 concourse |  | Contr | MMD | PAD - Paddington Station (West) |  | 2013-12-29 | 2013-12-19 14:39 | -10 | 2013-11-29 17:19 | Structural Engineering - Diaphragm Walls | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | There are several cavities at either side of D-Wall panel W4 that are full non cementitious debris, the majority of it being clay. This is preventing pouring the Concourse Slab 1.
| 03SR - Stations (RfL) | Cxxx-NCR-001246 | NCR | Temporary Works Design for Heras Panel |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-02-18 | 2014-02-10 13:01 | -8 | 2013-11-29 17:26 | Civil - Civil Engineering General | 500 |  | System Defect | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Heras fencing has been installed on the site without any temporary works design checks.
| 03SR - Stations (RfL) | Cxxx-NCR-001247 | NCR | Non-cementitious material panel N1 concourse |  | Contr | MMD | PAD - Paddington Station (West) |  | 2013-12-29 | 2013-12-19 14:48 | -10 | 2013-11-29 17:25 | Structural Engineering - Diaphragm Walls | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | There are several cavities in D-Wall panel N1B that are full non cementitious debris, the majority of it being clay. This is preventing pouring the Concourse Slab 1.
| 03SR - Stations (RfL) | Cxxx-NCR-001248 | NCR | C1 - No couplers are visible in the Diaphragm Wall in panel N4 |  | Contr | MMD | PAD - Paddington Station (West) |  | 2013-12-29 | 2013-12-19 14:52 | -10 | 2013-11-29 17:32 | Structural Engineering - Diaphragm Walls | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The box out covering the couplers at concourse level has been removed and no couplers are visible. This is preventing pouring the Concourse Slab 1.
| 03SR - Stations (RfL) | Cxxx-NCR-001249 | NCR | Materials Compliance Record [MCR] not submitted for concrete embedded strain gauges |  | Contr | SKC | PAD - Paddington Station (West) |  | 2013-12-30 | 2013-12-19 14:59 | -11 | 2013-11-30 11:36 | Surveying - Instrumentation and Monitoring | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | During the production of CES and DATUM's Quality Plans its was noted that an MCR has not been issued for the Concrete Embedded Strain Gauges. PAD-CRL RFI-Cxxx-00717 was raised requesting approval to use GeoKon 4200 series SG and this was accepted (see attached with request and agreement highlighted).
| 03SR - Stations (RfL) | Cxxx-NCR-001250 | NCR | Use of materials without compliance record |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-01-21 | 2014-01-17 08:30 | -4 | 2013-12-02 14:34 | Civil - Civil Engineering General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | Materials where used on site prior to obtaining approval through the use a Material compliance records. The materials used where, __ GP and __ HB.
| 03SR - Stations (RfL) | Cxxx-NCR-001251 | NCR | C20 Magnet extensometer |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-01-01 | 2013-12-22 20:01 | -10 | 2013-12-02 15:42 | Surveying - Instrumentation and Monitoring | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | C20 access has been restricted with a temporary deck. Access hatch too small to read instrument.
| 03SR - Stations (RfL) | Cxxx-NCR-001252 | NCR | Obstruction to retaining wall & footpath sensors adjacent 40 Eastbourne Terrace |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-03-11 | 2014-02-12 10:35 | -27 | 2013-12-04 10:17 | Surveying - Instrumentation and Monitoring | 500 |  | System Defect | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Due to relocation of a pedestrian walkway and the on/off access ramp the 3D geodetic prisms installed on the retaining wall to the lightwell to 40 Eastbourne terrace and the PLP's on the footpath in the area of the on/off access ramp will no longer be accessable. Prisms: Cxxx-RP000442, Cxxx-RP000443 & Cxxx-RP000444 PLP's: Cxxx-LP910048 & Cxxx-LP910049
| 03SR - Stations (RfL) | Cxxx-NCR-001253 | NCR | Subcontractor competency records for __ Precast Plant |  | Contr | MMD | PAD - Paddington Station (West) |  | 2014-02-18 | 2014-02-18 12:55 | 0 | 2013-12-04 17:48 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Competency records were not in place during CRL visit in __ Precast Plant for labour carrying the slump test and concrete cubes.
| 03SR - Stations (RfL) | Cxxx-NCR-001254 | NCR | Procedure of precast concrete below 5deg |  | Contr | MMD | PAD - Paddington Station (West) |  | 2014-02-18 | 2014-02-07 12:25 | -11 | 2013-12-04 17:54 | Structural Engineering - Structural Engineering - General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Procedure of concrete placing below 5deg in writing was not in place at __ Precast Plan during CRL visit 3/12/2013.
| 03SR - Stations (RfL) | Cxxx-NCR-001255 | NCR | Non-cementitious material in joint panel W1 and W2 concourse |  | Contr | MMD | PAD - Paddington Station (West) |  | 2014-01-03 | 2013-12-19 14:55 | -15 | 2013-12-04 18:36 | Structural Engineering - Diaphragm Walls | 1500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Please refer to Cxxx-NCR-001040 (NCR for S70 at roof slab level): During the snagging required for the concourse slab construction non-cementitious material (clay) has been dug from between the panel joint of W1 & W2. This digging out has penetrated through 1m behind the concrete face position. No vertical dumbbell waterbar has been visible.
| 03SR - Stations (RfL) | Cxxx-NCR-001256 | NCR | Header beam weld failure at P2 |  | Contr | MMD | PAD - Paddington Station (West) |  | 2014-04-29 | 2014-03-28 10:11 | -32 | 2013-12-06 16:14 | Structural Engineering - Welding | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Weld was completed at the west side of the first connection plate at P2. Weld failed the ultrasonic test.
| 03SR - Stations (RfL) | Cxxx-NCR-001258 | NCR | Lack of rebar on South D-wall at S10, S16 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-12-24 | 2015-11-27 16:18 | -27 | 2013-12-09 11:47 | Civil - Structural Engineering | 1500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the current exposure of South D-wall, it has been found that southern face of certain panels (S10, S16) has not got required rebar cover. Survey report attached
| 03SR - Stations (RfL) | Cxxx-NCR-001259 | NCR | DS 13 Roof Slab TOC |  | Contr | MMD | PAD - Paddington Station (West) |  | 2014-01-21 | 2014-01-29 09:39 | 8 | 2013-12-09 17:30 | Structural Engineering - Structural Engineering - General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Finished concrete level out of tolerance in one isolated location (+11mm, 1mm above tolerance)
| 03SR - Stations (RfL) | Cxxx-NCR-001260 | NCR | DN 20 Concrete Delivery Times |  | Contr | MMD | PAD - Paddington Station (West) |  | 2014-01-28 | 2014-01-29 10:12 | 1 | 2013-12-09 17:38 | Civil - Civil Engineering General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Supervision - Not Defined | Completed |  | 1 Hour 45 Minutes between loads, Delivery Ticket Nos 354224 & 354234
| 03SR - Stations (RfL) | Cxxx-NCR-001261 | NCR | Design concrete mix for coffers Concourse Slab |  | Contr | MMD | PAD - Paddington Station (West) |  | 2014-01-09 | 2014-01-10 13:46 | 1 | 2013-12-10 17:02 | Materials - Approval | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | NCR regarding the use of concrete mix in precast panels in concourse and intermediate slab. MCR Cxxx-SKC-O-TSC-B071_WS077-50108 was signed off with Code 2. The list of incorporated changes is attached in document Cxxx-SKC-O-XCS-B071_WS077-50056.
| 03SR - Stations (RfL) | Cxxx-NCR-001262 | NCR | Load Monitoring Cell in P15 not functioning correctly |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-01-14 | 2014-01-08 17:00 | -6 | 2013-12-13 11:52 | Surveying - Instrumentation and Monitoring | 1000 |  | Equipment Breakdown | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Load Monitoring Cell in P15 is not functioning correctly. The requirement is for all Props up to P16 to be monitored and then alternate props from here onwards.
| 03SR - Stations (RfL) | Cxxx-NCR-001263 | NCR | chase details for water proofing at South D-wall location |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-02-28 | 2014-03-07 10:31 | 7 | 2013-12-15 19:01 | Civil - Structural Engineering | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | At South D-wall panels S10, S15, there are 2xNo temporary rebar, which are not aligned straight. As a result of this the chase details for water proofing approved as per RFI1275, cannot be at back face, instead it goes in front
| 03SR - Stations (RfL) | Cxxx-NCR-001264 | NCR | Incomplete grouting of sonic logging tubes - Dwalls |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2014-07-15 | 2014-07-14 09:08 | -1 | 2013-12-17 09:56 | Civil - Civil Engineering General | 1500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | It has come to the attention of the supervisor that the sonic logging tubes in the Dwall panels have not been fully grouted. This should be evident from your grouting records. It appears that incomplete grouting was carried out at completion of Dwalls due to blockages and again on breakdown of the walls.
| 03SR - Stations (RfL) | Cxxx-NCR-001265 | NCR | Failed Cube Result, 482 D |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-03-18 | 2014-01-14 11:29 | -63 | 2013-12-18 12:39 | Structural Engineering - Concrete Member | 500 |  | Material | Reject | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Concrete cube 482 D, failed its 58 day cube results.
| 03SR - Stations (RfL) | Cxxx-NCR-001266 | NCR | IL1 Failed Cube Result, 480 B and C |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-05-13 | 2014-05-09 17:25 | -4 | 2013-12-19 06:52 | Structural Engineering - Concrete Member | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Cube set 480 (shown in pink in the attached) failed to reach its 28 day strength. With 480B reaching 50.1 N/mm^2, and 480C reaching 50.9N/mm^2.
| 03SR - Stations (RfL) | Cxxx-NCR-001267 | NCR | Panel N1A at concouse level - water leak |  | Contr | MMD | PAD - Paddington Station (West) |  | 2014-01-18 | 2014-01-29 10:05 | 11 | 2013-12-19 15:54 | Structural Engineering - Diaphragm Walls | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | The water leak was discovered at panel N1A at concourse level around top coupler.
| 03SR - Stations (RfL) | Cxxx-NCR-001268 | NCR | C1 - 2No B40 couplers not engaged |  | Contr | MMD | PAD - Paddington Station (West) |  | 2014-01-18 | 2014-01-14 11:30 | -4 | 2013-12-19 16:06 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | In panel N1B were not possible to engagged 2No B40 bar mark E02 couplers. Refer to drawing: Cxxx-SKC-C-DWG-B071_WS077-50517
| 03SR - Stations (RfL) | Cxxx-NCR-001269 | NCR | C1 - Concourse Slab Pour 1 |  | Contr | MMD | PAD - Paddington Station (West) |  | 2014-08-12 | 2014-08-08 15:35 | -4 | 2013-12-19 16:58 | Structural Engineering - Structural Engineering - General | 2500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 13 No loads of concrete were poured over 2 Hrs after batching.
| 03SR - Stations (RfL) | Cxxx-NCR-001272 | NCR | Use of flame torch to dry concrete surface for water proofing |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-02-27 | 2015-02-02 09:04 | -25 | 2013-12-22 21:18 | Civil - Structural Engineering | 0 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | _laser are using Naked flame torch to dry concrete surface before applying primer.
| 03SR - Stations (RfL) | Cxxx-NCR-001273 | NCR | Setting out error for gullies between CH25-CH90 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-09-09 | 2014-09-04 11:56 | -5 | 2014-01-02 10:08 | Civil - Civil Engineering General | 3500 |  | Workmanship | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | 3XNo draiange gullies (Reference RG) are 150mm out of position due to setting out error
| 03SR - Stations (RfL) | Cxxx-NCR-001274 | NCR | C2 - Dwall N9 couplers |  | Contr | MMD | PAD - Paddington Station (West) |  | 2014-02-06 | 2014-02-02 09:17 | -4 | 2014-01-07 12:13 | Structural Engineering - Reinforcement | 2500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Please be aware that the couplers on N9 panel are too high, clashing with the T2 mat. Please see attached survey of the couplers in the panels next to N9. It is not an option to drop T2 mat as it would clash with the couplers in N7 panel.
| 03SR - Stations (RfL) | Cxxx-NCR-001275 | NCR | Rejection of gasmain between GL1-GL16 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-02-12 | 2014-02-14 09:37 | 2 | 2014-01-07 16:48 | Civil - Structural Engineering | 5000 |  | Workmanship | Rework | 3 (3-6k) | Complete | Supervision - Insufficient supervision | Completed |  | As per National Grid's site visit and inspection for existing gasmain laid as part of E__ works, rejection for existing line has been implemented by NG due to physical damage at certain locations.
| 03SR - Stations (RfL) | Cxxx-NCR-001276 | NCR | E__ kerbs casted at 20mm higher than desgined level |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-02-12 | 2014-02-12 17:36 | 0 | 2014-01-07 16:56 | Civil - Structural Engineering | 5000 |  | Workmanship | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | At CH35 (Infront of No 2 Building) existing granite kerbs were casted at 20mm higher than designed level. The total affected length was 40m
| 03SR - Stations (RfL) | Cxxx-NCR-001277 | NCR | Damage to existing water proofing at GL18 high level slabs |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-12-31 | 2017-02-17 14:41 | 48 | 2014-01-07 17:10 | Civil - Structural Engineering | 5000 |  | Damaged | Rework | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | Water proofing at GL18, high level slabs were damaged by third parties. After the application material was placed on certain section. The over all dimension of affected section is 3mx4m.
| 03SR - Stations (RfL) | Cxxx-NCR-001278 | NCR | Possible cold joint within D-wall panel N9 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-08-19 | 2014-08-20 10:42 | 1 | 2014-01-08 06:47 | Structural Engineering - Diaphragm Walls | 1500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A possible cold joint is present in pannel N9, at level 117ATD.
| 03SR - Stations (RfL) | Cxxx-NCR-001279 | NCR | Exposed rebar and clay inclusions in D-Wall N23 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-01-29 | 2015-01-28 11:26 | -1 | 2014-01-08 06:58 | Structural Engineering - Diaphragm Walls | 2500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | A number of clay inclusion pockets are present in panel N23, in some cases exposing rebar.
| 03SR - Stations (RfL) | Cxxx-NCR-001280 | NCR | Caly/Bentonite inclusion in D-Wall panel N24/N25 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-05-06 | 2014-05-08 15:28 | 2 | 2014-01-08 07:14 | Structural Engineering - Diaphragm Walls | 2500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A large clay/bentonite inclusion was found inbetween pannels N24/N25. Inclusion has been chased back untill hard concrete has been found, aprox 500x400mm and 500mm deep.
| 03SR - Stations (RfL) | Cxxx-NCR-001281 | NCR | Boxout materials distributed throughout D-Wall Pannel S29 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-01-30 | 2014-08-29 11:04 | -154 | 2014-01-08 07:33 | Structural Engineering - Diaphragm Walls | 2500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The ply and foam from the intermediate slab coupler boxout is distributed throughout panel S29. The depth that obstructions go into panel is unknown.
| 03SR - Stations (RfL) | Cxxx-NCR-001282 | NCR | C2 - Water leak repair works panel N6 |  | Contr | MMD | PAD - Paddington Station (West) |  | 2014-02-07 | 2014-02-02 09:20 | -5 | 2014-01-08 15:44 | Structural Engineering - Diaphragm Walls | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Water leak appeared when box out exposed at panel N6 see attached photo.
| 03SR - Stations (RfL) | Cxxx-NCR-001283 | NCR | C2 - Water leak repair works panel S5 |  | Contr | MMD | PAD - Paddington Station (West) |  | 2014-02-07 | 2014-02-02 09:23 | -5 | 2014-01-08 15:56 | Structural Engineering - Diaphragm Walls | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Water leak appeared when box out exposed at panel N5.
| 03SR - Stations (RfL) | Cxxx-NCR-001284 | NCR | C2 - Water leak repair works joint S5/S6 |  | Contr | MMD | PAD - Paddington Station (West) |  | 2014-02-07 | 2014-02-02 09:28 | -5 | 2014-01-08 15:59 | Structural Engineering - Diaphragm Walls | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Water leak appeared when box out exposed at joint S5/S6 see attached photo.
| 03SR - Stations (RfL) | Cxxx-NCR-001285 | NCR | Paddington Stn [Lawn Terrace] Escalator tilt sensor reading programme |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-03-18 | 2014-02-13 15:05 | -33 | 2014-01-09 09:32 | Surveying - Instrumentation and Monitoring | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | Planned reading date Monday 6th January missed.
| 03SR - Stations (RfL) | Cxxx-NCR-001286 | NCR | C12-08 Piezo's damaged |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-02-18 | 2014-02-18 09:10 | 0 | 2014-01-09 10:05 | Geotechnical Engineering - Geotechnical Monitoring | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Piezo's C12‐08 stopped reporting on the 19/12/2013. The cables have been severed and lost again in the dig. It looks as if they have been severed by the excavator whilst being tracked up & down the dig. Also due to the location of the instruments being in an exclusion zone and the Christmas break (shutdown) we have not been able to access them until now.
| 03SR - Stations (RfL) | Cxxx-NCR-001287 | NCR | West retaining wall; materials installed prior relevant MCR's being accepted |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-02-11 | 2014-02-12 10:58 | 1 | 2014-01-09 10:44 | Civil - Civil Engineering General | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Various materials were installed within the west retaining wall backfilling operations prior to MCR's being accepted. Theses include; 100mm Diameter Perforated Pipe-Cxxx-SKC-O-TSC-B071_WS077-50311 No Fines Concrete- Cxxx-SKC-O-TSC-B071_WS077-50312 Transitional drainage Coupler-Cxxx-SKC-O-TSC-B071_WS077-50313 Cast Iron T-Piece - Cxxx-SKC-O-TSC-B071_WS077-50314 6N Backfill-Cxxx-SKC-O-TSC-B071_WS077-50261
| 03SR - Stations (RfL) | Cxxx-NCR-001288 | NCR | Magnetic Extensometer C12-13 - Unable to read [covered with spoil] |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-01-23 | 2014-01-16 13:26 | -7 | 2014-01-09 13:19 | Geotechnical Engineering - Geotechnical Monitoring | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Magnetic Extensometer C12-13 - Unable to read [covered with spoil]
| 03SR - Stations (RfL) | Cxxx-NCR-001289 | NCR | Testing of drainage along Eastbourne Terrace |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2014-02-25 | 2014-02-28 10:54 | 3 | 2014-01-12 12:52 | Civil - Drainage | 2500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | carried out air testing to the newly installed drainage for the Eastbourne Terrace Works(Manhole 7-10 main drain pipe and gully lines ) This is due to be done before placing the concrete for the carriageway to confirm that none of the pipework has been damaged as a result of backfilling works. The air test failed with no clear explanation of why a failure occured and the extent of the failure. This has the potential to delay the opening of Eastbourne Terrace and add further costs due to re-working and/or repair.
| 03SR - Stations (RfL) | Cxxx-NCR-001290 | NCR | Fracture in Gully Tail SG8 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-02-11 | 2014-02-20 12:16 | 9 | 2014-01-13 15:47 | Civil - Drainage | 1500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Personnel Error - Not Defined | Completed |  | During the CCTV survey of the drainage run a blockage was found in the drainage run from gully SG8 to the main pipe. The operatives dug down to expose the blockage. A fracture was observed on one of the pipe sections leading to the main drainage run.
| 03SR - Stations (RfL) | Cxxx-NCR-001291 | NCR | Fracture in Gully Tail SG 21 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-09-29 | 2018-11-26 14:48 | 58 | 2014-01-13 15:53 | Civil - Drainage | 2500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the CCTV survey of the drainage run and the gullies a fracture was found in the gully pipe of gully SG21
| 03SR - Stations (RfL) | Cxxx-NCR-001292 | NCR | Concourse Pour CL1 - fresh concrete placed against concrete over one hour after initial placement |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2014-10-07 | 2014-09-19 16:24 | -18 | 2014-01-14 13:18 | Structural Engineering - Concrete Member | 2500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the initial pour of the concourse slab, concrete was placed in layers across the pour. Subsequent layers were placed in excess of one hour after the initial placement. Cxxx-SCM-0016 covers this and requests details to provide assurance that a cold joint hasn't formed. This assurance should attached to this NCR to allow closure
| 03SR - Stations (RfL) | Cxxx-NCR-001293 | NCR | West retaining wall; North face of wall- steel pins for shutters left flush with face of concrete |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-03-25 | 2014-03-25 10:46 | 0 | 2014-01-15 17:05 | Civil - Civil Engineering General | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | North face of wall- steel pins to hold shutters for the no fines concrete pour left flush with face of concrete. See attached photo for clarity
| 03SR - Stations (RfL) | Cxxx-NCR-001294 | NCR | Cracking of Eastbourne Terrace Concrete Road Slab |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-03-07 | 2014-03-07 16:00 | 0 | 2014-01-16 01:37 | Civil - Roadworks Joints | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Following the first concrete pour for the road slab of Eastbourne Terrace, certain dowel bars which were to be installed at the line of the concrete joint between pours were installed prematurely, which has led to crack formation on a section along the joint.
| 03SR - Stations (RfL) | Cxxx-NCR-001296 | NCR | Eastbourne Terrace Concrete Road Slab Thickness |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-02-25 | 2014-03-07 12:20 | 10 | 2014-01-16 02:01 | Civil - Streets & Highways | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | The slab thickness at the eastern end of the Eastbourne Terrace concrete road slab poured on Saturday 11th January, has not been constructed in accordance to the design requirement and varies between 250-300mm
| 03SR - Stations (RfL) | Cxxx-NCR-001297 | NCR | PCC Spine Beam Soffit |  | Contr | MMD | PAD - Paddington Station (West) |  | 2014-02-15 | 2014-02-18 15:54 | 3 | 2014-01-16 12:35 | Structural Engineering - Pre-cast | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | PCC Panels Installed on 29.07.13 Cubes taken for grout to these units were mislaid and as a result not crushed.
| 03SR - Stations (RfL) | Cxxx-NCR-001298 | NCR | Non Installation of Duct Route for I&M installation |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-02-18 | 2014-02-19 12:13 | 1 | 2014-01-16 19:27 | Civil - Streets & Highways | 1500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Prior to the first concrete pour for the Eastbourne Terrace road slab a duct crossing for the cable for the I&M installation Cxxx-ID-A4-07 across the road was not installed.
| 03SR - Stations (RfL) | Cxxx-NCR-001299 | NCR | Damage to pre-cast unit in roofslab during excavation |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-07-31 | 2016-05-26 13:54 | -66 | 2014-01-17 12:47 | Structural Engineering - Pre-cast | 5000 |  | Damaged | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Unfortunately we appear to have damaged one of the spine beam precast panels within the lightwell area (see photos attached). The damage is approx. 70mm x 70mm x 15mm deep and is located approx. 500mm west of plunge column 29 (GL13).
| 03SR - Stations (RfL) | Cxxx-NCR-001300 | NCR | Damage to strain gauge cables in plunge column 34, 35, 36, 37, 38 & 44 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-02-20 | 2014-02-02 09:26 | -18 | 2014-01-21 08:17 | Surveying - Instrumentation and Monitoring | 1500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Sometime on 14/01/2014 (Friday afternoon) the cables for the strain gauges on the column were severed by the excavators in the dig. (see attached damage report)
| 03SR - Stations (RfL) | Cxxx-NCR-001301 | NCR | Damage to C20-06 Magnetic Extensometer |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-04-29 | 2014-04-25 13:57 | -4 | 2014-01-21 08:28 | Surveying - Instrumentation and Monitoring | 1500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During the bulk excavation on the evening of the 13/01/2014 __ broke the tubing of the mag exto . Access required to expose instrument and assess if the tubing has been blocked. (see attached damage report).
| 03SR - Stations (RfL) | Cxxx-NCR-001302 | NCR | DN26 - Soffit of Roof Slab 1 |  | Contr | MMD | PAD - Paddington Station (West) |  | 2015-01-30 | 2014-09-02 09:48 | -150 | 2014-01-21 11:32 | Structural Engineering - Surface Treatment | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Area of deep blinding on DN26 is adhered to soffit of roof slab which will cause scarring to the concrete soffit on removal. (East of GL 16 at D-wall)
| 03SR - Stations (RfL) | Cxxx-NCR-001303 | NCR | DN26 – Soffit of Roof Slab 2 |  | Contr | MMD | PAD - Paddington Station (West) |  | 2014-07-31 | 2014-07-25 11:28 | -6 | 2014-01-21 11:44 | Structural Engineering - Surface Treatment | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Area of Soffit east of GL16 mid DN26 slab (area of approximately 3 - 4 m2) appears open textured.
| 03SR - Stations (RfL) | Cxxx-NCR-001305 | NCR | Failure to display ATS data from PM 22nd to AM 23rd January 2014 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-02-23 | 2014-02-28 13:01 | 5 | 2014-01-24 11:35 | Surveying - Instrumentation and Monitoring | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Database code changes used for the website 3d data display caused a prolonged downtime. This proved more complex than DATUM initially thought.
| 03SR - Stations (RfL) | Cxxx-NCR-001306 | NCR | 10/30 Eastbourne Terrace, retaining wall prisms no longer obserable |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-02-07 | 2014-02-05 13:21 | -2 | 2014-01-24 12:56 | Surveying - Instrumentation and Monitoring | 0 |  | Damaged | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Not Defined | Completed |  | Due to the 3rd party construction works to 20 Eastbourne Terrace ATS08 mounted on the facade will have to be removed. This ATS is the only sensor capable of observing prisms installed to the retaining walls of 10 & 30 Eastbourne Terrace. Prisms not observable are: Cxxx-RP000413 Cxxx-RP000414 Cxxx-RP000415
| 03SR - Stations (RfL) | Cxxx-NCR-001307 | NCR | Green trigger breaches Block D & A (ATS height) and PLP Block D - Not reported |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-02-25 | 2014-02-13 15:09 | -12 | 2014-01-27 18:31 | Surveying - Instrumentation and Monitoring | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | Green trigger breaches Block D & A (ATS height) and PLP's Block D - Not reported in required timeframe
| 03SR - Stations (RfL) | Cxxx-NCR-001308 | NCR | No ITP in place for lighting column baseplates and holding down arrangements |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2014-03-18 | 2014-03-21 16:57 | 3 | 2014-01-29 09:15 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Lighting column baseplates and holding down arrangements are being constructed on site without an ITP in place
| 03SR - Stations (RfL) | Cxxx-NCR-001309 | NCR | Material Compliance Records for Eastbourne Terrace Lighting Columns |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-03-31 | 2014-03-28 13:16 | -3 | 2014-01-29 18:56 | Civil - Street Furniture | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Works on the Eastbourne Terrace lighting columns have been progressed without MCRs in place for the following materials: - Structural concrete - Steel reinforcement - 355 grade 70mm steel plate - M20 threaded bar and nuts - M27 threaded bar - __ HIT-HY-200A - Bituminous paint - Weber 5 star grout Note that the above have been approved by Cxxx's designer prior to inclusion in the works, but the MCR process has not been followed as detailed in the works information.
| 03SR - Stations (RfL) | Cxxx-NCR-001310 | NCR | Buried __ Valve |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-08-20 | 2014-08-06 16:00 | -14 | 2014-01-29 19:26 | Utilities Engineering - Water | 2500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The valve for the new Thames water connection outside number 20 Eastbourne Terrace was buried during the concrete pour for the Eastbourne Terrace road slab.
| 03SR - Stations (RfL) | Cxxx-NCR-001311 | NCR | Early Removal of Frost Blankets over E__ road slab |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-02-18 | 2014-02-18 13:32 | 0 | 2014-01-29 19:39 | Civil - Streets & Highways | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Following the third pour for the Eastbourne Terrace concrete slab on 19/01/2014 frost blankets were placed over poured area. On 20/01/2014 the frost blankets were removed prior to the required 54 hour period.
| 03SR - Stations (RfL) | Cxxx-NCR-001312 | NCR | C2 - Segregation during the concrete pour |  | Contr | MMD | PAD - Paddington Station (West) |  | 2014-05-31 | 2014-05-30 11:09 | -1 | 2014-01-30 09:04 | Structural Engineering - Concrete Member | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | During concrete pour of concourse slab C2 on the 25/01/2014 the aggregate segregation of the concrete mix occurred when discharging from the transportation pipe. More information will follow.
| 03SR - Stations (RfL) | Cxxx-NCR-001313 | NCR | C2 - Plastic settlement of fresh concrete |  | Contr | MMD | PAD - Paddington Station (West) |  | 2014-10-31 | 2014-10-13 09:09 | -18 | 2014-01-30 09:11 | Structural Engineering - Concrete Member | 2500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | During concrete pour of concourse slab C2 on the 25/01/2014 the plastic settlement of the fresh concrete mix occurred when discharging from the transportation pipe. More information will follow.
| 03SR - Stations (RfL) | Cxxx-NCR-001314 | NCR | C2 - Chalky top surface - possible delaminating of top surface |  | Contr | MMD | PAD - Paddington Station (West) |  | 2014-10-31 | 2014-10-29 15:19 | -2 | 2014-01-30 09:18 | Structural Engineering - Concrete Member | 80000 |  | Material | Rework | 1 (>60k) | Complete | Material/Preservation Problems - Other | Completed |  | After concrete pour of concourse slab C2 on the 25/01/2014 the top surface was found chalky/powdery with possibility of delaminating. More information will follow.
| 03SR - Stations (RfL) | Cxxx-NCR-001315 | NCR | C2 - Waterlines on shutter faces |  | Contr | MMD | PAD - Paddington Station (West) |  | 2014-09-30 | 2014-10-01 16:16 | 1 | 2014-01-30 09:30 | Structural Engineering - Concrete Member | 1500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | After concrete pour of concourse slab C2 on the 25/01/2014 the waterlines were found on the shutter faces. See attached photos.
| 03SR - Stations (RfL) | Cxxx-NCR-001316 | NCR | Water leakage throiugh dwall panels N13 to N14 |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2014-03-01 | 2014-02-06 14:07 | -23 | 2014-01-30 14:56 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Water is leaking through the dwall panels between N13 and N14
| 03SR - Stations (RfL) | Cxxx-NCR-001317 | NCR | Water Ingress within IL-16 S77 South |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-08-26 | 2014-06-03 16:55 | -84 | 2014-01-31 08:18 | Structural Engineering - Diaphragm Walls | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Water ingressing through D-Wall panel S77 South within IL-16 footprint.
| 03SR - Stations (RfL) | Cxxx-NCR-001318 | NCR | Il-16 Water Ingress S77 East |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-08-26 | 2014-06-03 16:56 | -84 | 2014-01-31 08:34 | Structural Engineering - Diaphragm Walls | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Water ingress on panel S77 East within IL-16 footprint
| 03SR - Stations (RfL) | Cxxx-NCR-001319 | NCR | Il-16 Water Ingress E1 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-08-26 | 2014-06-03 16:57 | -84 | 2014-01-31 08:40 | Structural Engineering - Diaphragm Walls | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Water ingress on panel S77 East within IL-16 footprint
| 03SR - Stations (RfL) | Cxxx-NCR-001320 | NCR | Il-16 Water Ingress N81 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-08-26 | 2014-07-25 09:57 | -32 | 2014-01-31 08:46 | Structural Engineering - Diaphragm Walls | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Water ingress on panel N81 within IL-16 footprint
| 03SR - Stations (RfL) | Cxxx-NCR-001321 | NCR | Non-cementitious material joint S16/S17 at concourse |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-02-20 | 2014-02-23 15:21 | 3 | 2014-02-06 14:12 | Structural Engineering - Diaphragm Walls | 2500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the D-wall snagging required for the concourse slab construction non-cementitious material (clay) has been found in the joint between panels S16 and S17 (see photo). This is in the area of the joint (not the panel cage) and seems to continue past the water bar ( 500mm deep).
| 03SR - Stations (RfL) | Cxxx-NCR-001322 | NCR | Precast Panels at GL 9 + 2.15m |  | Contr | MMD | PAD - Paddington Station (West) |  | 2014-04-29 | 2014-03-28 10:13 | -32 | 2014-02-07 15:30 | Structural Engineering - Structural Engineering - General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Outside face of upstand surveyed (See attached) is indicated as between 10mm – 14mm beyond design position, up to 4mm out of tolerance.
| 03SR - Stations (RfL) | Cxxx-NCR-001323 | NCR | Commencing work without MCR's |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2014-02-25 | 2014-02-26 08:58 | 1 | 2014-02-11 11:29 | Civil - Roadworks Formation | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | __ and white lining activities have taken place on Eastbourne Terrace without Crossrail receiving an MCR for the materials. In a recent meeting Westminster City Council approved the use of the materials that have been placed, however they are not what is stated in the specification, drawings or the schedule 3 submitted to WCC in August 2013. are currently discussing this issue with the designer with regards to a change of the specification, drawings etc.
| 03SR - Stations (RfL) | Cxxx-NCR-001324 | NCR | West liner wall-Void between 'D' wall panels W4/N1 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-03-14 | 2014-03-07 13:33 | -7 | 2014-02-12 10:35 | Civil - Civil Engineering General | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | 1.5m above concourse slab level between panels W4/N1 the is a small void approximately 300mm x 300mm x 250mm deep. Please see attached notification of defect FYI
| 03SR - Stations (RfL) | Cxxx-NCR-001325 | NCR | Waling escalator beam clash with N35 |  | Contr | MMD | PAD - Paddington Station (West) |  | 2014-03-14 | 2014-03-07 13:45 | -7 | 2014-02-12 14:27 | Structural Engineering - Structural Engineering - General | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The sketch showing the waling beam clashing with the d-wall rebar cage due N35 panel is out of position. The distance is approximately 20mm however we would need more space to get concrete around and vibrate this area.
| 03SR - Stations (RfL) | Cxxx-NCR-001326 | NCR | D-Wall Panel N23 and Cavity Drain Pipe Clash |  | Contr | MMD | PAD - Paddington Station (West) |  | 2014-09-30 | 2014-08-29 10:58 | -32 | 2014-02-12 16:16 | Structural Engineering - Structural Engineering - General | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | N23 extends too far to the south by 200-250mm. This results in the cavity that runs parallel with the diaphragm wall being 50mm wide at this location. A 75mm stainless steel pipe is detailed within the cavity. The current d-wall position prevents this. The distance between the design centreline of the pipe and the coupler box-out face is 54mm. Attached as built survey - 156-216mm further to the south.
| 03SR - Stations (RfL) | Cxxx-NCR-001327 | NCR | Possible concrete movement with pockers |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-04-29 | 2014-04-03 15:04 | -26 | 2014-02-12 17:43 | Structural Engineering - Concrete Member | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Within the concrete pour of IL-16 there may have been possible movement of concrete with the use of vibrating pockers.
| 03SR - Stations (RfL) | Cxxx-NCR-001328 | NCR | DATUM Logger Box 1 - Power disconnection |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-02-27 | 2014-02-18 09:14 | -9 | 2014-02-13 16:18 | Surveying - Instrumentation and Monitoring | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Power supply to DATUM logger box 1 located on hoarding opposite Cleveland Terrace was disconnected by __ on instruction from Construction team (Name to be confirmed). DATUM were not informed of this disconnection which occurred on Tuesday 11th February and instrumentation continued reporting under battery power. Battery power ran out on Thursday 13th February and failure to report was identified. __ are currently re-connecting the power.
| 03SR - Stations (RfL) | Cxxx-NCR-001329 | NCR | C3 - PC Coffer GL D – 6 to 7 |  | Contr | MMD | PAD - Paddington Station (West) |  | 2014-05-13 | 2014-05-12 11:26 | -1 | 2014-02-13 17:22 | Structural Engineering - Concrete Member | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Damaged coupler(H12) discovered in coffer.
| 03SR - Stations (RfL) | Cxxx-NCR-001330 | NCR | No Temporary works design in place for site gates |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2014-03-18 | 2014-03-19 10:33 | 1 | 2014-02-14 14:47 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The site gates have been erected on Eastbourne Terrace without any temporary works design in place for the arrangement and size of gates erected on site.
| 03SR - Stations (RfL) | Cxxx-NCR-001331 | NCR | DS11 Slump Range |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-03-25 | 2014-03-27 11:21 | 2 | 2014-02-17 15:02 | Structural Engineering - Structural Engineering - General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | Concrete delivery tickets show slump range to be S4, slump tests carried out reveal that 26 out of 37 loads delivered recorded slumps within the S5 range. The concrete mix design was adapted to accommodate a reduction in the PCE plasticiser, to reduce potential frothing, the resultant mix was designated S4 but was always considered S4/S5 by the mix designers, this was discussed prior to use and not considered a factor as long as the constraints of the specification were adhered to.
| 03SR - Stations (RfL) | Cxxx-NCR-001332 | NCR | Piezo's C12-14 Damaged |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-03-20 | 2014-03-21 07:12 | 1 | 2014-02-18 08:51 | Geotechnical Engineering - Geotechnical Monitoring | 1500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Sometime after the Friday shift on the 14/02/2014 __ have severed the cables to the Piezo's C12-14 again. This damage was found after they cleared the ruble they had stored over the install on Monday 17/02/2014
| 03SR - Stations (RfL) | Cxxx-NCR-001333 | NCR | Drill in bars for IL-16 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-04-29 | 2014-02-24 17:42 | -64 | 2014-02-18 14:18 | Structural Engineering - Diaphragm Walls | 2500 |  | Design | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | 38 No. D-Wall couplers could not be used within the footprint of IL-16: N79 - 6 Couplers N80 - 1 Coupler S77 South - 11 Couplers S75 - 18 Couplers These couplers could not be used because they were either damaged or too low so that they would clash with the bottom mat.
| 03SR - Stations (RfL) | Cxxx-NCR-001334 | NCR | Concourse Slab C 03 temperature |  | Contr | MMD | PAD - Paddington Station (West) |  | 2014-05-06 | 2014-04-29 16:54 | -7 | 2014-02-18 16:32 | Structural Engineering - Structural Engineering - General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Core temperature for C03 slab exceeded 60°C reaching a maximum 64.8°C. REF:- KF11.1307 Update 1/4/2014 However it is considered that the storage of shuttering material on the top surface of the slab, acted as an insulator and so increased the core temperature.
| 03SR - Stations (RfL) | Cxxx-NCR-001335 | NCR | Failure to raise manual inclinometer readings to daily following Amber trigger alert |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-03-05 | 2014-03-04 12:52 | -1 | 2014-02-19 12:58 | Surveying - Instrumentation and Monitoring | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Amber trigger alert breached on internal prop 9 on 13th February and discuss at CTC on same date. Failure to record monitoring frequency increase in manual monitoring inclinometers in vicinity of prop 9 during CTC on Thursday 13th February.
| 03SR - Stations (RfL) | Cxxx-NCR-001336 | NCR | Misaligned Gullies in Eastbourne Terrace Drainage |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-11-11 | 2014-10-29 15:35 | -13 | 2014-02-19 16:37 | Civil - Drainage | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | The requirement for the road gullies according to drawing Cxxx-SKC-D-DDD-M171_1-0546 is that they are positioned with the internal edge of the gully 25-75mm off the edge of the kerb into the road. 8 gullies do not comply with this as their internal edge is on average 35mm behind the kerb alignment. These are gullies SG12-16 and SG18-20.
| 03SR - Stations (RfL) | Cxxx-NCR-001338 | NCR | CL-T-10;start bars out of postion |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-03-25 | 2014-03-26 08:29 | 1 | 2014-02-20 12:29 | Civil - Civil Engineering General | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | There are 3 B12 starter bar cast out of position for CL-T-10 / Slab C01 Grid line 3/B. Drill & fix 8 B12 4EF depth 450mm 150 C/c, __ 200 resin
| 03SR - Stations (RfL) | Cxxx-NCR-001339 | NCR | Concourse Level area 4 and 5 Construction Joint |  | Contr | MMD | PAD - Paddington Station (West) |  | 2014-03-23 | 2014-03-21 17:01 | -2 | 2014-02-21 12:45 | Structural Engineering - Structural Engineering - General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 1 No of B25 side couplers could not be found on C04 and C05 construction joint on grid line A.
| 03SR - Stations (RfL) | Cxxx-NCR-001340 | NCR | No Temporary Works Design for Site Gates on Praed Street and Bishops Bridge Road |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-03-24 | 2014-03-21 07:14 | -3 | 2014-02-24 16:17 | Civil - Civil Engineering General | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Gates erected on Praed Street and Bishops Bridge Road have no Temporary Works Design in place
| 03SR - Stations (RfL) | Cxxx-NCR-001341 | NCR | C5 - water leak panels N21, N22 |  | Contr | MMD | PAD - Paddington Station (West) |  | 2014-03-27 | 2014-03-21 16:59 | -6 | 2014-02-25 09:35 | Structural Engineering - Diaphragm Walls | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The following diaphragm wall panels in pour C5 were inspected to have water lightly running through them, prior to slab pour: N21 - damp joint with N20 N22 - bottom couplers Please see attached records.
| 03SR - Stations (RfL) | Cxxx-NCR-001342 | NCR | C6 - water leak panels N27, N29, N30, N31 |  | Contr | MMD | PAD - Paddington Station (West) |  | 2014-03-27 | 2014-03-26 08:37 | -1 | 2014-02-25 09:41 | Structural Engineering - Diaphragm Walls | 3000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The following diaphragm wall panels in pour C6 were inspected to have water lightly running through them, prior to slab pour: N27 - bottom couplers N29 - right side N30 - damp bottom left N31 - damp bottom couplers Please see attached records.
| 03SR - Stations (RfL) | Cxxx-NCR-001343 | NCR | C7 - water leak panels N32, N33 |  | Contr | MMD | PAD - Paddington Station (West) |  | 2014-03-27 | 2014-03-23 11:01 | -4 | 2014-02-25 13:01 | Structural Engineering - Diaphragm Walls | 2500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | NCR: The following diaphragm wall panels in pour C7 were inspected to have water lightly running through them, prior to slab pour: N32 - damp bottom couplers N33 - damp bottom couplers
| 03SR - Stations (RfL) | Cxxx-NCR-001345 | NCR | C4 - Top surface settlement Concourse Slab C 04 |  | Contr | MMD | PAD - Paddington Station (West) |  | 2014-06-13 | 2014-06-19 14:24 | 6 | 2014-02-27 18:02 | Structural Engineering - Concrete Member | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Small area showing plastic settlement at centre of slab at gridlines D – E/ 7 – 8 where the concrete surface has settled approximately 5mm.
| 03SR - Stations (RfL) | Cxxx-NCR-001346 | NCR | Plunge Column 11B |  | Contr | MMD | PAD - Paddington Station (West) |  | 2014-04-29 | 2014-04-02 14:29 | -27 | 2014-02-26 11:48 | Structural Engineering - Structural Engineering - General | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | 1 No Shear Stud Damaged during installation/excavation on Plunge Column 11B
| 03SR - Stations (RfL) | Cxxx-NCR-001347 | NCR | C5 - 3No B40 Bottom Couplers not engagged in S23 |  | Contr | MMD | PAD - Paddington Station (West) |  | 2014-03-28 | 2014-03-27 18:22 | -1 | 2014-02-26 16:55 | Structural Engineering - Reinforcement | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 3No B40 Bottom Couplers were not engagged in S23 panel due to the angle.
| 03SR - Stations (RfL) | Cxxx-NCR-001348 | NCR | Cracking to channel block at gully face |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-03-17 | 2015-03-19 12:02 | 2 | 2014-03-31 10:56 | Civil - Kerbs | 2500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Cracking to west face of channel blocks at gully SG10, SG25 & SG27 & east face of SG28.
| 03SR - Stations (RfL) | Cxxx-NCR-001349 | NCR | C5 - 1No Bottom Couplers omitted in S21 |  | Contr | MMD | PAD - Paddington Station (West) |  | 2014-03-28 | 2014-03-07 15:47 | -21 | 2014-02-26 17:04 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 1No B40 Bottom Coupler was omitted in S21 panel due to clash with cavity drainage.
| 03SR - Stations (RfL) | Cxxx-NCR-001350 | NCR | C5 - 1No Bottom Couplers in S22 |  | Contr | MMD | PAD - Paddington Station (West) |  | 2014-03-28 | 2014-03-07 15:49 | -21 | 2014-02-26 17:07 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 1No B40 Bottom Coupler was not fully fixed in S22 panel due to an angle.
| 03SR - Stations (RfL) | Cxxx-NCR-001352 | NCR | Concourse Level;'D' wall couplers in N1 clashing with west liner wall starter bars |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-04-25 | 2014-04-04 16:33 | -21 | 2014-02-27 15:06 | Civil - Civil Engineering General | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Concourse Level;'D' wall couplers in N1 clashing with west liner wall starter bars.
| 03SR - Stations (RfL) | Cxxx-NCR-001353 | NCR | MH6-MH7 Airtest |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-03-10 | 2015-03-11 15:09 | 1 | 2014-02-27 17:43 | Civil - Drainage | 2000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The air test of the drainage run between Manhole 6 and Manhole 7 has failed
| 03SR - Stations (RfL) | Cxxx-NCR-001355 | NCR | Couplers between D-wall panel S1/W1 and the West liner wall at Concourse Level |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-04-29 | 2014-03-31 09:14 | -29 | 2014-03-03 17:21 | Civil - Civil Engineering General | 1500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | 3 couplers from panel S1 to the southern end of the west liner wall and 1 coupler to W1 were damaged during construction
| 03SR - Stations (RfL) | Cxxx-NCR-001356 | NCR | C6 - PC Coffer GL D – 10 (P-65) |  | Contr | MMD | PAD - Paddington Station (West) |  | 2014-05-13 | 2014-05-09 16:53 | -4 | 2014-03-03 17:18 | Structural Engineering - Reinforcement | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Missing coupler(H12) in coffer CS -01 yard pour ref: P-65
| 03SR - Stations (RfL) | Cxxx-NCR-001358 | NCR | Header Beams Delivered with Bent Shear Dowels (Studs) |  | Contr | MMD | PAD - Paddington Station (West) |  | 2014-04-30 | 2014-04-15 16:48 | -15 | 2014-03-10 09:57 | Structural Engineering - Structural Engineering - General | 1500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Header beams B46 and B96 which are to be installed at gridline 3 Intermediate level have been delivered to with the shear studs at the top face of the beam bent. Attached is a photograph showing the bent studs while the beam is on the delivery wagon. Attachment: Photograph of B46 and B96
| 03SR - Stations (RfL) | Cxxx-NCR-001360 | NCR | C3 - Upstand around 700 X 700mm void GL D-E/6-7 |  | Contr | MMD | PAD - Paddington Station (West) |  | 2014-04-29 | 2014-04-07 10:50 | -22 | 2014-03-10 11:29 | Structural Engineering - Reinforcement | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Attached SI-659 alters the size of the Concourse Slab opening at GLE- 2m /GL7- 3.1m. Please advise what size and where the upstand is required around this opening. Attachments: SI-659 Cxxx-SWN-C-XSK-B071-50073 Trimming detail for 700SQ opening in concourse slab GL7.pdf OHLE Builders work holes_16012014092848.pdf Ref for Cxxx-RFI-001589 for attachments.
| 03SR - Stations (RfL) | Cxxx-NCR-001361 | NCR | Water ingress S54/S55 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-04-10 | 2015-03-27 09:08 | -14 | 2014-03-12 08:49 | Structural Engineering - Diaphragm Walls | 2500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Water ingress observed through the joint of S54/S55.
| 03SR - Stations (RfL) | Cxxx-NCR-001362 | NCR | Water ingress S55/S56 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-04-10 | 2015-03-27 09:09 | -14 | 2014-03-12 08:51 | Structural Engineering - Diaphragm Walls | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Water ingress observed through the joint of S55/S56.
| 03SR - Stations (RfL) | Cxxx-NCR-001363 | NCR | WATER INGRESS S56/S57 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-04-10 | 2015-03-27 09:10 | -14 | 2014-03-12 08:50 | Structural Engineering - Diaphragm Walls | 2500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Water ingress observed through the joint of S56/S57.
| 03SR - Stations (RfL) | Cxxx-NCR-001364 | NCR | Exposed Rebar N39 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-02-17 | 2016-02-05 15:31 | -12 | 2014-03-12 12:55 | Structural Engineering - Diaphragm Walls | 2500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Exposed rebar, including the links, can be seen in D-Wall panel N35.
| 03SR - Stations (RfL) | Cxxx-NCR-001365 | NCR | Exposed Rebar N47 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-12-15 | 2015-11-23 10:47 | -22 | 2014-03-12 12:54 | Structural Engineering - Diaphragm Walls | 15000 |  | Workmanship | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | Exposed rebar, including the links, can be seen in D-Wall panel N35.
| 03SR - Stations (RfL) | Cxxx-NCR-001366 | NCR | Exposed Rebar N41 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-03-15 | 2016-02-23 12:39 | -21 | 2014-03-12 13:02 | Structural Engineering - Diaphragm Walls | 2500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The skid spacers are exposed on panel N41 which is likely to indicate that the minimum cover requirements for the D-Wall reinforcement have not been met.
| 03SR - Stations (RfL) | Cxxx-NCR-001368 | NCR | I&M, Manual Levels not taken at CTC frequency: Praed Street Feb2014 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-03-26 | 2014-03-21 07:25 | -5 | 2014-03-12 20:59 | Surveying - Instrumentation and Monitoring | 1000 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Manual readings of the I&M leveling points with ID's Cxxx-LP106168, Cxxx-LP106169, Cxxx-LP106170a & Cxxx-LP106171a were not taken at the frequency set by the CTC between 04/02/2014 and 06/03/2014.
| 03SR - Stations (RfL) | Cxxx-NCR-001369 | NCR | Water Ingress - N4 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-06-11 | 2014-06-04 08:58 | -7 | 2014-03-13 08:32 | Structural Engineering - Diaphragm Walls | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | A large damp patch exceeding 1m^2 is present within the boxout of panel N4. 115-118 ATD.
| 03SR - Stations (RfL) | Cxxx-NCR-001370 | NCR | Missing CBR Tests to Type 1 - Eastbourne Terrace ch340-390 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-07-16 | 2014-07-21 08:57 | 5 | 2014-03-18 18:12 | Civil - Roadworks Formation | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Due to a communication error on site, no CBR tests were carried out on type 1 sub-base to the Eastbourne Terrace carriageway between chainages 340-390.
| 03SR - Stations (RfL) | Cxxx-NCR-001373 | NCR | I&M, Manual Levels not taken at CTC frequency: Adjacent 2 Eastborne Terrace Sept 2013 > Mar 2014 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-04-29 | 2014-04-08 10:59 | -21 | 2014-03-20 11:34 | Surveying - Instrumentation and Monitoring | 500 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Interfacing problems | Completed |  | Manual readings of the I&M leveling points with ID's Cxxx-LP800001a, Cxxx-LP800002, Cxxx-LP800003, Cxxx-LP800004, Cxxx-LP800005, Cxxx-LP800006, Cxxx-LP800007 & Cxxx-LP800008 were not taken at the frequency set by the CTC between 24/09/2013 and 06/03/2014.
| 03SR - Stations (RfL) | Cxxx-NCR-001374 | NCR | C08 Pre-cast CS-02 Starter Bars |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-04-19 | 2014-03-25 16:09 | -25 | 2014-03-20 18:16 | Civil - Structural Engineering | 1500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | BM 03A - B20 bars are clashing with the slab edge.
| 03SR - Stations (RfL) | Cxxx-NCR-001375 | NCR | CL-L-47; wall cast with without correct steel to connect walls CL-T-03 and CL-T-120 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-04-29 | 2014-03-28 16:17 | -32 | 2014-03-24 17:47 | Civil - Civil Engineering General | 1000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | CL-L-47; wall cast with without correct steel to connect walls CL-T-03 and CL-T-120. BM 25 and BM50 missing from the attached drawing
| 03SR - Stations (RfL) | Cxxx-NCR-001376 | NCR | Plunge columns not reported in accordance with specification (kN and trigger levels not shown) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-04-29 | 2014-04-25 16:04 | -4 | 2014-03-25 01:11 | Surveying - Instrumentation and Monitoring | 2500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | Plunge columns not reported in accordance with specification (kN and trigger levels not shown)
| 03SR - Stations (RfL) | Cxxx-NCR-001377 | NCR | __-L_40;Pull out bars missed from wall __ T-40 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-04-30 | 2014-04-17 16:09 | -13 | 2014-03-25 11:02 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 4 B12 bars missed from wall T-40 to connect to slab ES 13 Attachment: Cxxx-SKC-C-DWG-B071_WS077-51574
| 03SR - Stations (RfL) | Cxxx-NCR-001378 | NCR | __ Utilities Quality Plan |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-04-30 | 2014-05-02 11:28 | 2 | 2014-03-25 11:11 | Civil - Drainage | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | s specialist subcontractor for utilities works on site have carried out works without an approved Quality Plan in place.
| 03SR - Stations (RfL) | Cxxx-NCR-001379 | NCR | FS-31A Precast Unit |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-11-15 | 2017-09-23 07:50 | -53 | 2014-03-28 17:31 | Civil - Civil Engineering General | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A fixing on the precast panel FS-31A is missing - see attached for details.
| 03SR - Stations (RfL) | Cxxx-NCR-001380 | NCR | Missing Fixing In Precast unit (C08) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-11-15 | 2017-10-07 10:26 | -39 | 2014-06-30 | Civil - Civil Engineering General | 1000 |  | Damaged | Reject | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | One of the fixings to a precast panel in C08 is missing – See attached Sketch
| 03SR - Stations (RfL) | Cxxx-NCR-001381 | NCR | N9 - Coupler Level |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-04-30 | 2014-04-08 11:11 | -22 | 2014-03-31 17:06 | Structural Engineering - Diaphragm Walls | 2500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Within panel N9, at intermediate level, the entire top row of couplers range from 880-920mm from bottom of slab to centre of coupler. The design level is 820mm, and at current this will not allow top mat to fit within the cover zone.
| 03SR - Stations (RfL) | Cxxx-NCR-001382 | NCR | __ Yard - precast panels - defects 1-30 |  | Contr | MMD | PAD - Paddington Station (West) |  | 2014-06-30 | 2014-06-09 08:31 | -21 | 2014-04-01 15:57 | Structural Engineering - Concrete Member | 25000 |  | Damaged | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Attached 30 No Internally Raised NCRs produced at __ Yard during production of precast concrete units for inclusion in works at Cxxx Paddington Crossrail. Faults are various and detailed on individual reports (attached) NCRs forwarded for information.
| 03SR - Stations (RfL) | Cxxx-NCR-001383 | NCR | C03 Blinding and Slab level |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-05-20 | 2014-04-29 16:25 | -21 | 2014-04-03 16:45 | Civil - Structural Engineering | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | C03 TOC out of tolerance due to heave
| 03SR - Stations (RfL) | Cxxx-NCR-001384 | NCR | IL2-Surface crack |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-08-20 | 2014-07-15 09:07 | -36 | 2014-04-03 14:00 | Civil - Civil Engineering General | 1500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | After pouring IL2, suface cracks apperered at the north side of the slab, at approximately GL 3/E
| 03SR - Stations (RfL) | Cxxx-NCR-001385 | NCR | CL-L-34-starter bars in wrong postion |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-04-30 | 2014-04-29 17:00 | -1 | 2014-04-03 14:19 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Some of the starter bars within CL-L-34 were cast in the incorrect postion. B12 bars at 150c/c will need to be drilled and fixed to a depth of 250mm with hilti hit 200. Please see attached sketch for clarity
| 03SR - Stations (RfL) | Cxxx-NCR-001389 | NCR | Compliance Requirements for Competence Management |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-05-15 | 2014-05-12 13:32 | -3 | 2014-04-04 15:53 | Surveying - Instrumentation and Monitoring | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Refer to Surveillence Log Cxxx-SKC-O4-LLG-B071_WS077-50002. Surveillence Report 50040 - Compliance requirements for competence assessments have not been satisfied to date.
| 03SR - Stations (RfL) | Cxxx-NCR-001391 | NCR | Plunge Column 34: Damaged Strain Gauge |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-05-13 | 2014-05-15 17:10 | 2 | 2014-04-07 16:33 | Surveying - Instrumentation and Monitoring | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A strain gauge on PC34 has stopped transmitting readings. It is likely that this is a sign that the strain gauge has been damaged. At this stage it is not possible to access the transfer box to make an assessment of the damage.
| 03SR - Stations (RfL) | Cxxx-NCR-001392 | NCR | N17 Joint - Clay Inclusion |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-05-04 | 2014-04-10 09:36 | -24 | 2014-04-09 08:26 | Structural Engineering - Diaphragm Walls | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A large clay inclusion was found within the joint of N16 and N17. This inclusion extended back to the waterbar.
| 03SR - Stations (RfL) | Cxxx-NCR-001393 | NCR | IL 2;Staircase-missing starter bars |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-06-27 | 2014-06-25 11:27 | -2 | 2014-04-11 07:48 | Civil - Civil Engineering General | 1500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | bars haven't been detailed in the IL 02 reinforcement drawing refer to Cxxx-SKC-C-DWG-B071_WS077-51715 for the staircase on GL 4-5/B
| 03SR - Stations (RfL) | Cxxx-NCR-001394 | NCR | C09 top cover |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-07-11 | 2014-07-03 13:47 | -8 | 2014-04-11 17:35 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Prior to pouring C09 it was discovered that a 10m long 1m wide section would not have enough cover in a localized area to the top of slab. This was calculated to have 25-40mm cover along C08 & C09 construction joint. Please find attached cover survey. We propose to pour concrete 25mm high in this section.
| 03SR - Stations (RfL) | Cxxx-NCR-001395 | NCR | C09 Reinforcement bend bars |  | Contr | MMD | PAD - Paddington Station (West) |  | 2014-05-11 | 2014-04-17 10:19 | -24 | 2014-04-11 17:45 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | Bend some bars(12 no) without the use of steel bender machine. The size of the bending rebar have been 16 mm .Further details to follow. Area: Around escalator pit(Grid lines 13-5m/D + 2m )
| 03SR - Stations (RfL) | Cxxx-NCR-001396 | NCR | IL3 -shrinkage cracks |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-07-31 | 2014-07-17 09:32 | -14 | 2014-04-16 09:07 | Civil - Civil Engineering General | 1500 |  | Material | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | IL3; On the north side of the construction opening within IL3 some shrinkage crack have appeared on the top of IL3. Please see attached photo
| 03SR - Stations (RfL) | Cxxx-NCR-001397 | NCR | CL-T-escalator support wall starter bars |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-05-21 | 2014-05-30 16:35 | 9 | 2014-04-23 18:22 | Civil - Civil Engineering General | 1500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | approximately 16no. escalator support wall starter bars bent at GL11/D-E have been excessively bent to accommodate pedestrian access
| 03SR - Stations (RfL) | Cxxx-NCR-001398 | NCR | I&M: Discrepencies in Report and Record Submission Timescales for Inclinometer Instruments |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-05-13 | 2014-05-02 11:31 | -11 | 2014-04-25 12:12 | Surveying - Instrumentation and Monitoring | 1000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | Following the installation of inclinometers A27-27 and E7-26, submission of installation records and installation report was not undertaken in line with the timescales required in the Contract. Dates of submission are listed below: A27-27: Installed - 09/08/12 Record submitted - 02/01/13 Report submitted - 24/05/13 E7-26 Installed - 30/11/12 Record submitted - 02/01/13 Report submitted - 05/07/13 Installation records are required within 24 hours of installation. Installation reports are required within 30 days of installation. Moving forward, are to appoint a suitably qualified package manager to oversee the preparation and issue of installation documentation.
| 03SR - Stations (RfL) | Cxxx-NCR-001399 | NCR | I&M: Reading of inclinometers within 20m zone of influence |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-05-16 | 2014-05-02 11:33 | -14 | 2014-04-25 12:26 | Surveying - Instrumentation and Monitoring | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | All inclinometers (within the 20m zone of influence from the Mole Hole) are required t be read daily during excavation operations in accordance with Cxxx-SWN-C2-DDA-M171_Z-01518 Rev C05. In the SRG meeting on 07/08/13, 4 of 6 required inclinometers were read on the South Wall and 2 of 7 of the required inclinometers were read on the South Wall. It should be noted that of the inclinometer readings that were read, none showed breach of the trigger levels.
| 03SR - Stations (RfL) | Cxxx-NCR-001400 | NCR | IL-SSL level around tempoary openings |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-05-26 | 2014-05-23 14:21 | -3 | 2014-04-25 14:04 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Around the temporary opening splays (see attached sketch) in IL5 the SSL level is proposed to be increased by a maximum of 20mm (worst case scenario) due to the future coupler connections heads sitting on top of one another and fixed U bars scheduled rather than chairs bent to suit SSL .
| 03SR - Stations (RfL) | Cxxx-NCR-001401 | NCR | IL5-missing earthing boxout |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-05-30 | 2014-05-29 09:57 | -1 | 2014-04-28 16:03 | Civil - Civil Engineering General | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | Earthing boxout required in IL5 as per drawing Cxxx-SWN-E-DDA-M171_Z-31520
| 03SR - Stations (RfL) | Cxxx-NCR-001402 | NCR | IL level;west liner wall |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-05-22 | 2014-05-23 15:01 | 1 | 2014-04-28 16:44 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The positions of the couplers in the Departures Road Slab that connect to the verts in the west liner wall are too far east resulting in 25mm cover to the screw bars.
| 03SR - Stations (RfL) | Cxxx-NCR-001403 | NCR | C7 Piezometers Not Reading |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-05-28 | 2014-05-27 16:23 | -1 | 2014-04-29 09:58 | Surveying - Instrumentation and Monitoring | 1500 |  | Equipment Breakdown | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | C7 piezometers have stopped transmitting readings. Inspections of the piezometers are to be undertaken (access permitting) on Tuesday 29th April to determine any required actions to get the piezometers transmitting once more.
| 03SR - Stations (RfL) | Cxxx-NCR-001404 | NCR | CT06 IPI Battery Requiring Replacement |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-05-27 | 2014-05-16 15:58 | -11 | 2014-04-29 10:09 | Surveying - Instrumentation and Monitoring | 1500 |  | Equipment Breakdown | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The battery on IPI CT06 has flatlined, with the IPI therefore no longer transmitting readings. The IPI is located in Cleveland Terrace, with a road closure required in order to gain access to undertake battery replacement.
| 03SR - Stations (RfL) | Cxxx-NCR-001405 | NCR | IL-lightwell beam fabrication error |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-05-30 | 2014-05-23 10:27 | -7 | 2014-04-30 15:48 | Civil - Civil Engineering General | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | On inspection of lightwell beams received it was noted that a web stiffener was missing from a 12215mm beam. Please see attached photo from clarity
| 03SR - Stations (RfL) | Cxxx-NCR-001406 | NCR | Concrete Embedded Strain Gauges: Concourse Slab |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-09-30 | 2014-09-10 08:45 | -20 | 2014-04-30 17:10 | Surveying - Instrumentation and Monitoring | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Concrete embedded strain gauges on GL3, GL7 and GL13, in the concourse have not been installed in the correct position as specified in Cxxx-RFI-001373 and Cxxx-RFI-001422. The incorrect locations are as listed below: Cxxx-G-B3-C-31 (GL3 South) - Approximately 4.0m too far from South Wall Cxxx-G-D3-C-32 (GL3 North) - Generally correct Cxxx-G-D7-C-37 (GL7 North) - Generally correct Cxxx-G-B7-C-38 (GL7 South) - Approximately 4.0m too far from South Wall Cxxx-G-D13-C-43 (GL13 North) - Approximately 4.0m too close to North Wall Cxxx-G-D13-C-43 (GL13 South) - Approximately 2.0m too far from South Wall The reasons for the strain gauges being installed away from the recommended locations are as below: 1. The requirement to avoid coffered areas as specified in Cxxx-RFI-001373/001422 2. The requirement to avoid zones of lapping bars as specified in Cxxx-RFI-001373/001422 3. The increased amount of reinforcement being installed in the slab, thereby increasing the extents of the lapping zones 4. The original design intent to have strain gauges located in identical locations each slab going down inside the box An RFI should have been raised at the moment it became apparent that it was not possible to install the strain gauges in the specified location. However, waiting for this to be answered would have held up the concrete pour and would have had programme implications for the project.
| 03SR - Stations (RfL) | Cxxx-NCR-001407 | NCR | Large Clay Inclusion in E4/N80 Joint |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-07-15 | 2015-06-25 09:37 | -20 | 2014-04-30 17:47 | Structural Engineering - Diaphragm Walls | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A large clay inclusion is present in the joint of D-Wall pannels E4/N80 at the concourse boxout level.
| 03SR - Stations (RfL) | Cxxx-NCR-001408 | NCR | E1 Clay Inclusion |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-07-29 | 2014-07-21 14:14 | -8 | 2014-04-30 17:52 | Structural Engineering - Diaphragm Walls | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A large clay inclusion is present in D-Wall panel E1 in the concourse boxout.
| 03SR - Stations (RfL) | Cxxx-NCR-001409 | NCR | C15 Dwall Panel N77 Concourse Level Grid Line 22/E |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-05-29 | 2014-05-29 11:19 | 0 | 2014-05-08 13:52 | Structural Engineering - Reinforcement | 2000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | 7 bottom couplers cast high level from GL22- 500mm (insteead GL22 + 500mm). Attachment: Cxxx-NOD-0031
| 03SR - Stations (RfL) | Cxxx-NCR-001410 | NCR | C13 D-Wall Joint N66 N67 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-10-10 | 2014-08-29 11:06 | -42 | 2014-05-12 17:14 | Structural Engineering - Diaphragm Walls | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Clay inclusion in D-wall joint between panels N66 and N67.
| 03SR - Stations (RfL) | Cxxx-NCR-001411 | NCR | Monitoring of Escalators in Paddington Station |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-06-27 | 2014-06-23 09:57 | -4 | 2014-05-09 18:06 | Surveying - Instrumentation and Monitoring | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Failure to take monitoring readings of the NR escalators at agreed scheduled intervals.
| 03SR - Stations (RfL) | Cxxx-NCR-001412 | NCR | C11 Pre-Cast W-03A, W03B Damage |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-05-26 | 2014-05-19 12:06 | -7 | 2014-05-12 12:16 | Civil - Civil Engineering General | 2000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Damage to the corner of vertical Pre-Cast panels on C11, W-03A and W-03B, which could result in delay.
| 03SR - Stations (RfL) | Cxxx-NCR-001413 | NCR | C12 Pre-Cast Panel US-01A Damage |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-04-30 | 2014-10-02 15:24 | -210 | 2014-05-12 12:24 | Civil - Civil Engineering General | 2000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Pre-Cast panel US-01A in pour area C12, next to escalator pit damaged. The upstand has been cut.
| 03SR - Stations (RfL) | Cxxx-NCR-001414 | NCR | C05 TOC out of tolerance due to heave |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-06-09 | 2014-07-21 08:58 | 42 | 2014-05-12 14:54 | Civil - Structural Engineering | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | C05 TOC out of tolerance due to heave
| 03SR - Stations (RfL) | Cxxx-NCR-001415 | NCR | Sand/Bentonite Inclusion N66 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-08-11 | 2014-07-28 09:26 | -14 | 2014-05-13 10:58 | Structural Engineering - Diaphragm Walls | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 3No. possible Sand/Bentonite inclusions are visible on the surface of panel N66.
| 03SR - Stations (RfL) | Cxxx-NCR-001416 | NCR | Sand/Bentonite Inclusion N63 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-05-11 | 2015-05-08 14:14 | -3 | 2014-05-13 11:03 | Structural Engineering - Diaphragm Walls | 2500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A possible Sand/Bentonite inclusion is visible on the surface of panel N63.
| 03SR - Stations (RfL) | Cxxx-NCR-001417 | NCR | C12 Panels N60 - N62 reinforcement cages out of tolerance |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-06-30 | 2014-06-20 12:07 | -10 | 2014-05-13 17:05 | Structural Engineering - Diaphragm Walls | 1500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | D-Wall Panel N62 (also N60 and N61) reinforcement cage is out of tolerance and is twisted within the panel. A survey was undertaken (attached) to show the concourse level couplers to be up to 319mm from intended position. Concern over the potential for the reinforcement to be exposed on the back face with no cover.
| 03SR - Stations (RfL) | Cxxx-NCR-001418 | NCR | IL6 Concrete Pour- Non approved MCR |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-08-27 | 2014-07-25 11:30 | -33 | 2014-05-14 15:27 | Structural Engineering - Concrete Member | 1500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | RC 40/50 INT 10mm Concrete mix for the Intermediate Slab 10mm gravel was replaced 10mm Limestone for 35m3 on IL6
| 03SR - Stations (RfL) | Cxxx-NCR-001419 | NCR | IL6 Slump Site Record Observation |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-07-13 | 2014-06-12 14:31 | -31 | 2014-05-14 15:56 | Structural Engineering - Concrete Member | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Crossrail Field Engineer observed a slump test - ticket No 829618 - out of tolerance 270-280mm for S4 slump that was placed into IL6.
| 03SR - Stations (RfL) | Cxxx-NCR-001420 | NCR | IL6 Concrete Waiting Time |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-10-31 | 2014-10-10 14:52 | -21 | 2014-05-14 16:13 | Structural Engineering - Concrete Member | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Exceedance of 1hr 25min between placing ticket No 829628-451073 and ticket 829620-829628.
| 03SR - Stations (RfL) | Cxxx-NCR-001421 | NCR | IL6 Concrete Quality |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-07-13 | 2014-06-12 15:54 | -31 | 2014-05-14 16:24 | Structural Engineering - Concrete Member | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | There were signs of segregation of concrete within the IL06 slab. After an hour of placing the concrete water appeared visable on the surface due to settlement occuring.
| 03SR - Stations (RfL) | Cxxx-NCR-001423 | NCR | Repaired precast panel US-01A in c12 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-03-10 | 2014-12-03 09:50 | -97 | 2014-05-15 14:07 | Structural Engineering - Pre-cast | 1500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Precast panel US-01A in C12 was damged during blinding works. A small chip was broken off the corner of the panel. The panel was removed and returned to __ __ precast yard to enable a repair to be undertaken in controlled conditions.
| 03SR - Stations (RfL) | Cxxx-NCR-001424 | NCR | IL4-28 day cubes failed to reach strength |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-06-30 | 2014-07-02 12:22 | 2 | 2014-05-16 10:05 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Cube strength for IL4 slab failed at 28 days (877B, 877C) please see attached
| 03SR - Stations (RfL) | Cxxx-NCR-001425 | NCR | IL-T-22; water added to concrete without batching plants consent |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-10-21 | 2014-10-05 09:24 | -16 | 2014-05-20 16:24 | Civil - Civil Engineering General | 1000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | On pouring IL-T-22, it was observed that 20L of water was added to the onsite concrete without consent of the tarmac batching plant or without following the agreed procedure for adding water stated in Cxxx-SKC-C-STP-B071_WS077-50008
| 03SR - Stations (RfL) | Cxxx-NCR-001426 | NCR | Damage to Strain Gauges on PC36 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-06-20 | 2014-05-30 11:24 | -21 | 2014-05-23 09:11 | Surveying - Instrumentation and Monitoring | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | On 20th May 2014, it was noted that the cables for 3No. strain gauges on the south side of PC36 had been cut. The strain gauges in question are SG-D, SG-E and SG-F. It will not be possible to take readings from the strain gauges in question until they have been reconnected. At present it is not possible to access the plunge columns in order to re-connect the cables. Under the current programme of works, it will not be possible to access the strain gauges for repairs until the concourse slab has been cast in that area (C12/C13). C12 is due to be cast 29/5. C13 is due to be cast 7/6. If the strain gauges are to be repaired prior to the concrete being cast, it will be necessary to erect temporary scaffolding for access, which may have programme implications. Damage reports are attached to this NCR.
| 03SR - Stations (RfL) | Cxxx-NCR-001427 | NCR | Damage to Strain Gauges on PC38 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-06-20 | 2014-06-04 11:11 | -16 | 2014-05-23 09:16 | Surveying - Instrumentation and Monitoring | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | On 19th May 2014, it was noted that the cables for 3No. strain gauges on the south side of PC38 had been cut. The strain gauges in question are SG-D, SG-E and SG-F. It will not be possible to take readings from the strain gauges in question until they have been reconnected. At present it is not possible to access the plunge columns in order to re-connect the cables. Under the current programme of works, it will not be possible to access the strain gauges for repairs until the concourse slab has been cast in that area (C12/C13). C12 is due to be cast 29/5. C13 is due to be cast 7/6. If the strain gauges are to be repaired prior to the concrete being cast, it will be necessary to erect temporary scaffolding for access, which may have programme implications. Damage reports are attached to this NCR.
| 03SR - Stations (RfL) | Cxxx-NCR-001428 | NCR | Header beam Installation, Concourse and Intermediate slab |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-08-12 | 2014-08-15 12:51 | 3 | 2014-05-27 16:08 | Structural Engineering - Welding | 1500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Non-conformities flagged in Surveillance Report 50155.
| 03SR - Stations (RfL) | Cxxx-NCR-001429 | NCR | West liner wall finish; Intermediate level, IL1, Gridline 1/A-E |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-06-26 | 2014-06-10 14:06 | -16 | 2014-05-28 08:33 | Structural Engineering - Concrete Member | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Concrete finish affected by water track marks caused by concrete “bleed” on the west liner wall from intermediate level to Departure level.
| 03SR - Stations (RfL) | Cxxx-NCR-001430 | NCR | Bent starter bars Wall T-11; Intermediate level, IL3, Gridline 5/E Wall T-11 kicker |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-06-26 | 2014-06-10 14:15 | -16 | 2014-05-28 08:38 | Structural Engineering - Reinforcement | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | 7 B12 starter bars were bent to allow access for the walk way, bars have been bent back and kicker has been poured.
| 03SR - Stations (RfL) | Cxxx-NCR-001432 | NCR | IL8 D-Wall couplers |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-06-17 | 2014-06-12 15:56 | -5 | 2014-06-03 09:17 | Structural Engineering - Reinforcement | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | listed below are dwall couplers that were damaged and required replacing Panel S38, S37, S33 Please find pictures attached
| 03SR - Stations (RfL) | Cxxx-NCR-001433 | NCR | IL8 concrete placement time exceeded and one load placed with high slump |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-11-28 | 2014-10-09 13:18 | -50 | 2014-06-03 11:25 | Structural Engineering - Concrete Member | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | 1 hr placement time was exceeded after rejection of four sequential load due to high slump and one load with ticket number 396096 with a recorded slump of 270 was used in the pour. Placement time recorded between end of discharge on ticket No.396089 to ticket No. 396096 was 1hr 5mins.
| 03SR - Stations (RfL) | Cxxx-NCR-001434 | NCR | Strain gauges on plunge columns: Incorrect baseline frequency at installation |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-07-22 | 2014-07-25 09:35 | 3 | 2014-06-03 12:05 | Surveying - Instrumentation and Monitoring | 5000 |  | System Defect | Rework | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | At the time of installation of strain gauges on PC34, PC35, PC36 and PC38, the commissioning readings (the HZ readings) taken were at the bottom end of the operating range specified by the manufacturer of 450-1250Hz. Consequently, a number of strain gauges have dropped out of range and been set to faulty. For the faulty gauges, the commissioning reading and the date set to faulty is summarised below: PC34 A: Commissioning reading 527.3Hz Set to faulty 05/03/14. Set to ok 24/04/14. PC34 B: Commissioning reading 467.2Hz. Set to faulty 05/03/14. PC34E: Commissioning reading 644.3Hz. Set to faulty 24/04/14. Note that this strain gauge has been set to faulty due to suspected damage, not due to the readings dropping out of range. PC35 A: Commissioning reading 611.3Hz. Set to faulty 05/03/14. PC35 B: Commissioning reading 530.0Hz. Set to faulty 05/03/14. PC35 C: Commissioning reading 511.6Hz. Set to faulty 05/03/14. PC36 A: Commissioning reading 696.7Hz. Set to faulty 20/12/13. PC36 B: Commissioning reading 591.1Hz. Set to faulty 20/12/13. PC38 D: Commissioning reading 504.1Hz. Set to faulty 08/02/14. PC38 E: Commissioning reading 486.3Hz. Set to faulty 08/02/14. PC38 F: Commissioning reading 568.6Hz. Set to faulty 08/02/14. Additional strain gauges have now been installed on the plunge columns listed above. Attached to this NCR is a powerpoint presentation detailing the damaged strain gauges. Also attached is the original installation report.
| 03SR - Stations (RfL) | Cxxx-NCR-001435 | NCR | IL8 1 B25 BM20 coupler |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-06-27 | 2014-06-12 15:57 | -15 | 2014-06-04 17:23 | Structural Engineering - Reinforcement | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Intermediate Level, IL 8- 9 construction joint Grid line 12/A-B 1 B25 BM20 coupler can not be located after concrete placed to IL 8
| 03SR - Stations (RfL) | Cxxx-NCR-001436 | NCR | IL9 Damaged D-Wall Couplers |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-06-27 | 2014-06-10 14:16 | -17 | 2014-06-05 17:17 | Structural Engineering - Reinforcement | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Replaced damaged couplers in Dwall Panels Panels: S40 2 Top Couplers was drilled and fixed S42 3 Top Couplers was drilled and fixed Please find attached pictures & miscellaneous works approval.
| 03SR - Stations (RfL) | Cxxx-NCR-001437 | NCR | C16 Top coupler (panel N81) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-07-09 | 2014-06-26 10:47 | -13 | 2014-06-09 09:40 | Structural Engineering - Diaphragm Walls | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 2No top couplers cannot be fully engaged on panel N81 at concourse level due to being installed at wrong angle. (1No - 40mm gap and 1No - 7mm gap). Please note that this issue was revealed after all of the couplers on the east wall (top and bottom), all bottom couplers on the north wall had been installed and all U-bars and side bars had been fixed. Due to safety constrain we are unable to drill inside the already fixed cage and drilling above will result in bars being too high and not having minimum cover. Originally, as per SI regarding cavity pipe, 1 No coupler was omitted for the cavity pipe and there is a 1No drilling on top to replace it. As agreed with __ we have moved the cavity pipe approx. 300mm from design position hence enabling the use of the coupler.
| 03SR - Stations (RfL) | Cxxx-NCR-001438 | NCR | IL Header Beams/Plates. WPQR Discain 20. Use of welding gas bottles with 20% Co2 mix |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-08-22 | 2014-08-14 12:39 | -8 | 2014-06-10 17:28 | Structural Engineering - Steel Member | 1500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Welding procedure WPQR Discain 20 states use of gas for welding with a 7% Co2 mix. Gas used for all welding to Header Beams/Plates has a 20% Co2 mix
| 03SR - Stations (RfL) | Cxxx-NCR-001439 | NCR | Header Beams/Plates Concourse and Intermediate Level |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-06-24 | 2014-06-13 16:41 | -11 | 2014-06-10 17:33 | Civil - Civil Engineering General | 1000 |  | Equipment Breakdown | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | 3 out of 4 welding rectifiers being used by Discain did not have calibration stickers fixed to the equipment during CRL site visit of 28/05/14 and certification records for the equipment was not available at site.
| 03SR - Stations (RfL) | Cxxx-NCR-001441 | NCR | IL10 Damaged D-Wall Couplers |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-06-30 | 2014-06-19 14:27 | -11 | 2014-06-12 17:37 | Structural Engineering - Reinforcement | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Two top mat d-wall couplers were drilled and fixed due to damaged threads
| 03SR - Stations (RfL) | Cxxx-NCR-001443 | NCR | C04 TOC out of tolerance due to heave |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-07-11 | 2014-06-26 16:57 | -15 | 2014-06-12 18:38 | Civil - Structural Engineering | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The clay heave encountered after the blinding has been placed has resulted in rise of the blinding level of approx. 20mm (see attached survey).
| 03SR - Stations (RfL) | Cxxx-NCR-001444 | NCR | CL-Columns starters bars on C2-N&C2-S have been bent |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-10-31 | 2014-09-27 12:17 | -34 | 2014-06-13 11:07 | Civil - Civil Engineering General | 2500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Columns starters on C2-N and C2-S have been bent at a 75 degree angle to accommodate shutters for adjacent wall
| 03SR - Stations (RfL) | Cxxx-NCR-001445 | NCR | C8 reduced cover to top slab |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-06-30 | 2014-06-25 10:11 | -5 | 2014-06-16 18:11 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | This NCR has been raised to separate Cxxx-NCR-001394 for a specific response to C8. All attachments are in Cxxx-NCR-001394. See cover survey attached - min cover is 29mm. Referring to KF11 Table 04 the concrete exposure class for internal slabs is XC1; XD0; XF0 According to BS 8500-1 2006 Table A.5 minimum cover is 15mm+deltaC Please note the T1 reinforcement is B25 bars and concourse slab mix suit to Table A.7 expectation. It is proposed to leave as is, because the durability and strength requirements are satisfied in this location.
| 03SR - Stations (RfL) | Cxxx-NCR-001446 | NCR | IL 10-concrete pour without signed accepted MCR in place |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-08-15 | 2014-08-05 09:26 | -10 | 2014-06-18 08:49 | Materials - Approval | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | IL 10 was poured using MCR; Cxxx-SKC-O-TSC-B071_WS077-50359 prior to being accepted by CRL.
| 03SR - Stations (RfL) | Cxxx-NCR-001447 | NCR | Tension columns-couplers cast with roof slab out of tolerance |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-05-08 | 2015-04-07 10:21 | -31 | 2014-06-19 12:43 | Civil - Base Course | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | Some couplers from the departure level slab to the tension columns are in the cover zone. See below options for proposals assuming that the main load is on the fraissy bars not on the column reinforcement. It is proposed to Omit couplers which are in the cover zone, extra anchorage (2 number 25mm dia) placed into the 50mm tubes for grouting. Reinforcement remains the same in the column - juggle bars can be used between couplers in use; anchorage bars and column verticals. Please see attached sketch for clarity
| 03SR - Stations (RfL) | Cxxx-NCR-001448 | NCR | C12 Slab – Bent Starter bars to L-48 and L-124 walls |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-07-17 | 2014-06-26 10:53 | -21 | 2014-06-19 16:51 | Civil - Civil Engineering General | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | A number of starter bars to L-48 and L-124 walls were bent at time of the C-12 pour to enable access routes across the slab Attachment: photograph: 100614 FE 036 photograph: 100614 FE 037
| 03SR - Stations (RfL) | Cxxx-NCR-001449 | NCR | Cracking to C13 Slab |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-09-30 | 2014-09-27 12:19 | -3 | 2014-06-20 17:59 | Structural Engineering - Concrete Member | 1000 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Shrinkage cracking between GL A-B with minor local pockets between GL B-D.
| 03SR - Stations (RfL) | Cxxx-NCR-001450 | NCR | CL2 slab-Zone 2 core strengths |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-08-22 | 2014-08-20 09:45 | -2 | 2014-06-26 13:35 | Civil - Civil Engineering General | 50000 |  | Material | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | CL2 slab; zone 2;Cores taken with zone failed compressive strength when crushed.
| 03SR - Stations (RfL) | Cxxx-NCR-001452 | NCR | Lack of concrete cover to rear of Dwall Panel N47 |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2016-02-29 | 2016-01-29 14:00 | -31 | 2014-07-02 10:48 | Structural Engineering - Diaphragm Walls | 15000 |  | Incorrect Installation | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | When chasing out defective concrete from Panel N47, it was discovered that the rear face reinforcement had little or no concrete cover.
| 03SR - Stations (RfL) | Cxxx-NCR-001453 | NCR | Scabbling back Dwall Panels no Inspection requests rasied |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2015-10-15 | 2015-10-12 14:54 | -3 | 2014-07-03 15:02 | Structural Engineering - Diaphragm Walls | 2500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | The face of many of the Dwall panels has been scabbled back without giving the PM's team the opprotunity to inspect, there is no specific WPP in place to indicate how depth control was achieved, nor an ITP requiring a test to prove the remaining cover. This is in contravention of part 20 of the works information. This has occurred on south side panels 29, 30, 31, 38, 39, 43, 44, 45, 49, 50, 51, 52, 53, 54, 55, 56, 58, 62, 64, 65, 66, 67, 68, 69, 70, 75, 77, and north side panels N42, 43, 50, 51, 55, 56, 57, 58, 59, 60, 76, 78, 79, 80, 81 and east end panels E1, E2, E3 7 E4
| 03SR - Stations (RfL) | Cxxx-NCR-001455 | NCR | ITP |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2014-09-01 | 2014-08-14 10:45 | -18 | 2014-07-07 10:27 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | During a CRL planned surveillance it was found the ITP Cxxx-SKC-C-ITP-B071_WS077-50009 rev 08 found that setting out had not been referenced as an activity or procedure.
| 03SR - Stations (RfL) | Cxxx-NCR-001456 | NCR | Commencement of works without approvals |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-08-12 | 2014-08-05 13:41 | -7 | 2014-07-07 18:27 | Structural Engineering - Steel Member | 2500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | With regards to the steel gantry being erected at moling hole 3 location ,gridlines 13 & 14. the following items listed are non conformance's - Fabrication of the steel structure commenced without an approved ITP being in place, Weld Procedure Specification and a weld procedure qualification record. However the correct grade of steel was used, S355JR in accordance with the spec.
| 03SR - Stations (RfL) | Cxxx-NCR-001457 | NCR | D-Wall N-56 Sandy inclusion |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-02-03 | 2015-01-29 10:59 | -5 | 2014-07-10 10:54 | Structural Engineering - Diaphragm Walls | 2500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Sandy inclusion on the surface on D-Wall panel N56 at a level 118.750mATD
| 03SR - Stations (RfL) | Cxxx-NCR-001458 | NCR | Non-Approved Mix Designs – C40/50 Roof |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-10-28 | 2014-10-09 12:40 | -19 | 2014-07-10 11:18 | Civil - Civil Engineering General | 1000 |  | Planning | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Departures Roof Slab Pours: DS1-DS14, DN15-DN28: Works proceeded without approved MCR’s for the following three mix designs using 10mm aggregate: Mix Design Certificate: 1005134001 Mix Design Certificate: 1005171673 Mix Design Certificate: 1005190599
| 03SR - Stations (RfL) | Cxxx-NCR-001459 | NCR | D-Wall N-57 Sandy inclusion |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-04-28 | 2015-04-28 15:33 | 0 | 2014-07-11 12:01 | Structural Engineering - Diaphragm Walls | 5000 |  | Material | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | Sandy inclusion on the surface on D-Wall panel N57 at a level 118.750mATD
| 03SR - Stations (RfL) | Cxxx-NCR-001460 | NCR | D-Wall N-65 Sandy inclusion |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-07-08 | 2015-07-02 13:47 | -6 | 2014-07-11 13:19 | Structural Engineering - Diaphragm Walls | 2500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Sandy inclusion on the surface on D-Wall panel N65 at a level 119.500 mATD
| 03SR - Stations (RfL) | Cxxx-NCR-001461 | NCR | Sandy inclusion D-Wall panel S-49 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-08-12 | 2014-08-13 16:02 | 1 | 2014-07-14 16:53 | Structural Engineering - Diaphragm Walls | 2500 |  | Material | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Sandy inclusion on the surface on D-Wall panel S-49 at a level 120.550 mATD
| 03SR - Stations (RfL) | Cxxx-NCR-001463 | NCR | Heathrow __ tunnel, Unreported trigger breaches |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2014-09-09 | 2014-08-05 13:43 | -35 | 2014-07-15 19:10 | Civil - Geotechnical Engineering | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Constractor fails to report trigger breaches on Heathrow __ Tunnel as per Cxxx Specification (Cxxx-OVE-C2-XWI-B071_WS077-00001) and Contractor I&M Plan. Green trigger has been breached in the last few months and the data is showing nearly amber trigger level at the moment. (Levelling data)
| 03SR - Stations (RfL) | Cxxx-NCR-001464 | NCR | IL12 - D-Wall Panel Low Level Couplers |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-07-30 | 2014-07-22 09:47 | -8 | 2014-07-16 09:46 | Structural Engineering - Reinforcement | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | In IL12 - D-wall Panels S58 and S60, 24no Bottom Couplers are too low.
| 03SR - Stations (RfL) | Cxxx-NCR-001465 | NCR | IL12-concrete placing time |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-10-31 | 2014-08-06 09:28 | -86 | 2014-07-21 11:19 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | IL12 concrete placing time exceeded 1 hour limit
| 03SR - Stations (RfL) | Cxxx-NCR-001466 | NCR | Damage to Roof Soffit GL 1 - 9 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-06-02 | 2015-05-15 11:52 | -18 | 2014-07-21 15:10 | Structural Engineering - Concrete Member | 10000 |  | Damaged | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | During the process of excavating the main box, accidental damage was caused to the concrete finish on the soffit of Roof Slab between Grid Lines 1 to 9.
| 03SR - Stations (RfL) | Cxxx-NCR-001467 | NCR | Damage to Roof Soffit GL 9 - 15 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-10-23 | 2015-09-11 15:37 | -42 | 2014-07-21 15:15 | Structural Engineering - Concrete Member | 10000 |  | Damaged | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | During the process of excavating the main box, accidental damage was caused to the concrete finish on the soffit of Roof Slab between Grid Lines 9 to 15.
| 03SR - Stations (RfL) | Cxxx-NCR-001468 | NCR | Damage to Roof Soffit GL 15 - 24 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-10-09 | 2015-09-11 15:38 | -28 | 2014-07-21 15:17 | Structural Engineering - Concrete Member | 10000 |  | Damaged | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | During the process of excavating the main box, accidental damage was caused to the concrete finish on the soffit of Roof Slab between Grid Lines 15 - 24.
| 03SR - Stations (RfL) | Cxxx-NCR-001469 | NCR | IL12 - D-wall Panel Couplers Panels N58-N61 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-08-04 | 2014-07-23 09:36 | -12 | 2014-07-21 17:18 | Structural Engineering - Reinforcement | 2500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | In IL12 - D-wall panels couplers had to be replaced (Drill and Fix) in panels N58 to N61 on North D-wall. Therefore, 10no Bottom Couplers in Panel N58, 14no Bottom Couplers in Panel N59, 14no Bottom Couplers in Panel N60 and 14no Bottom Couplers in Panel N61 need to bee raised.
| 03SR - Stations (RfL) | Cxxx-NCR-001470 | NCR | IL5 - Surface crack |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-08-20 | 2014-08-06 09:35 | -14 | 2014-07-22 15:59 | Civil - Civil Engineering General | 1500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | In IL5, surface cracks are visible on the south side of the slab, approximately around GL9/A.
| 03SR - Stations (RfL) | Cxxx-NCR-001471 | NCR | IL7 - Visible Surface Crack |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-08-20 | 2014-08-20 09:43 | 0 | 2014-07-22 16:06 | Civil - Civil Engineering General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There are crack visible on the surface of of IL7, The cracks surveyed are visible along Grid Line 10.5 and by the two newly installed gullies to the south of the slab, short of Grid Line 11/A. The cracks have been surveyed on the 22nd and the 28th of May 2014 and no apparent change in width has been noticed.
| 03SR - Stations (RfL) | Cxxx-NCR-001472 | NCR | Levelling data on UCIMS |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2015-06-24 | 2015-06-24 14:25 | 0 | 2014-07-28 15:29 | Civil - Geotechnical Engineering | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate resources | Completed |  | According with the Specification for Control of Ground Movement Cxxx-OVE-C2-XWI-B071_wS077-00001 (1.1.2.11) all the monitoring data obtained by the Contractor shall be incorporated into the UCIMS with the minimum of delay and in any event within 12 hours of the time of reading. A meeting was organised Cxxx (CRL/) and Cxxx to find out the issues with the UCIMS system on the 10.06.2014, where was required to send all the levelling data to Cxxx to be uploaded to UCIMS. The Contractor has failed to send the levelling data, data still not available on UCIMS.
| 03SR - Stations (RfL) | Cxxx-NCR-001474 | NCR | Contractor design programme submision of changes |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2014-11-17 | 2014-11-13 10:28 | -4 | 2014-08-05 11:54 | Mechanical - Mechanical Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The Contractor could not demonstrate the requirement to submit changes to the programme within the specified timescale as required by of WIv2B part 7.5.1 and part 14.1 with respect to the Surveillance of 25June 2014 and the sampled of PMI 269 issued 20th February 2014.
| 03SR - Stations (RfL) | Cxxx-NCR-001475 | NCR | Design Statement acceptance |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2014-11-17 | 2014-11-13 10:29 | -4 | 2014-08-05 13:03 | Mechanical - Mechanical Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | WIv2B part 7.7.3 requires “The Contractor does not start design work until the Contractor’s design statement has been accepted by the Project Manager.” Design Statement Cxxx-SKC-S-RGN-B071_WS077-50001 rev 4.0 titled “Departures Road Canopy” has a decal code 2 (Not accepted –revise and resubmit. Works may proceed subject to incorporating of changes indicated) since 11/02/2013. No design statements were in place for the mini gate design work referenced programme P03 2014-2015 dated 16th June 14.
| 03SR - Stations (RfL) | Cxxx-NCR-001476 | NCR | Maintaining interface control documents |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2014-11-10 | 2014-11-13 10:30 | 3 | 2014-08-05 13:13 | Mechanical - Mechanical Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | WIv2B part 7.7.7.2 requies “maintaining interface control documents (ICD) that provide a definitive reference for the progress status, design input requirements and design solution in respect of a particular interface, as agreed between the interfacing parties”, ICD presented during survaillance QS405-10 of 25th June 2014were for interface between Cxxx and Cxxx communication control systems and Cxxx non traction power systems. The ICDs were detailed and appeared satisfactory with the exception that they documented actions up to December 2013 only.
| 03SR - Stations (RfL) | Cxxx-NCR-001477 | NCR | Design administration procedures |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2014-11-17 | 2014-11-13 10:31 | -4 | 2014-08-05 13:27 | Mechanical - Mechanical Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | WIv2B part 20.4 requires That the Contract Quality Plan shall be supported by comprehensive QSPs including administration of design & design control. The procedures were not avaialbe for survaillance QS405-10 undertaken on 25th June 2014.
| 03SR - Stations (RfL) | Cxxx-NCR-001478 | NCR | Non conformances from Surveillance Cxxx-SKC-O-RGN-B071_WS077-50192 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-08-29 | 2014-08-29 12:26 | 0 | 2014-08-06 12:33 | Civil - Roadworks Formation | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | Surveillance Cxxx-SKC-O-RGN-B071_WS077-50192 identified 3no non-conformance on E__ road construction, as detailed in the attached report. These were: - Rev 2 of Urban Realm ITP not signed code 1 prior to commencement of works. - No record on Aconex or document number assigned to readiness review. - Paving check sheet not available at time of surveillance.
| 03SR - Stations (RfL) | Cxxx-NCR-001479 | NCR | Coffer Panel 88 - Unacceptable finish as identified in CRL surveillance dated 9th July 14. |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2014-12-23 | 2014-12-01 16:58 | -22 | 2014-08-06 13:33 | Civil - Civil Engineering General | 5000 |  | Manufacturing Defect | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | During the Cxxx Crossrail Surveillance dated 9th July 2014 the pre-cast coffer panels on the intermediate level next to plunge column 18, which require a special surface finish, were reviewed as placed. It was highlighted during the surveillance that Coffer Panel 88 showed a significant darker discolouration in comparison to the other panels. A post surveillance request was made to review the inspection check sheet and authorisation for the release of Coffer Panel 88 to site which was provided and signed off by the sub-contractor for release to site. Additionally QA.36 form for Panel 88 was provided. __ Crossrail Lead Architect was contacted during the surveillance to discuss the discoloration of Coffer Panel 88 and its acceptance against the benchmark colour and requirements set out in JE80 and KF11. It was confirmed post surveillance on 23rd July 2014 following a visit to site by the Lead Architect (17th July 2014) that Coffer Panel 88 was of darker visual appearance with more aggregate visible than surrounding Coffer Panels and as such was not acceptable in its current condition. Additionally during the site visit by the Lead Architect further points were highlighted regarding marks on several Coffer edges and panels showing sealant/ grout leakages which appear in the corners. These were also deemed not acceptable. This NCR has been raised to ensure appropriate remedial measures are proposed to achieve an acceptable visual appearance of Coffer Panel 88.
| 03SR - Stations (RfL) | Cxxx-NCR-001480 | NCR | Slump/ flow records do not identify the person responsible for testing as required by BS EN 12350-1 and ISO 17025 |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2014-10-22 | 2014-08-29 11:02 | -54 | 2014-08-06 13:39 | Civil - Civil Engineering General | 1000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Following the Cxxx Crossrail Surveillance dated 9th July 2014 a post surveillance a request was made to review the most recent concrete pour slump/ flow test reports. On post surveillance review it was identified that the slump/ flow report being used by the Contractor does not identify the person responsible for undertaking the sampling and testing. BS EN 12350-1:2009 Testing Fresh Concrete Part 1 Sampling states “Each sample shall be accompanied by a report from the person responsible for taking the sample. The report shall include: f) declaration by the person technically responsible for the sampling that it was carried out in accordance with this document”. Additionally ISO 17025:2005 General Requirements for the Competence of Testing and Calibration Laboratories clause 5.7.3 states “The laboratory shall have procedures for recording relevant data and operations relating to sampling that forms part of the testing ... These records shall include the sampling procedure used, the identification of the sampler …”. The competence of the person undertaking the testing could not be identified in line with the Holiday testing training records.
| 03SR - Stations (RfL) | Cxxx-NCR-001481 | NCR | Intermediate Slab IL10, IL11,IL12-Missing grout cubes |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-09-04 | 2014-08-20 09:37 | -15 | 2014-08-07 13:59 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Purpose of grouting has been verified to increase designed cover to some units due to slenderness and not for strength. Propose that the grouting cube strength analysis attached undertaken on the precast grouting done to date is accepted in lieu of the individual cube results. Required concrete strength for PC units is 50N/mm2. 28 day average for precast grout cubes is 98N/mm2
| 03SR - Stations (RfL) | Cxxx-NCR-001482 | NCR | C02 Precast Panel FS-47 cut coupler bar |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-09-05 | 2014-08-28 11:18 | -8 | 2014-08-08 13:47 | Structural Engineering - Pre-cast | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During coring works in Concourse Slab C02 (Zone 2 grout vein) a 12mm diameter coupler bar was accidentially cut. This bar is one of 5 coupler bars holding precast panel FS-47 in place and was cut at the top by 35mm (maximum 50mm). Please see attached sketches.
| 03SR - Stations (RfL) | Cxxx-NCR-001483 | NCR | D-Wall repairs Section I1 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-01-27 | 2015-01-09 16:02 | -18 | 2014-08-12 17:24 | Structural Engineering - Diaphragm Walls | 5000 |  | Material | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | This NCR covers D-Wall defects in Section I1 (See attached) This is Panels N1-N26 from intermediate floor level to Underside of roof level. A full snagging list will be developed following and CR inspection Inclused in this will be issued raised in the following NCRs Cxxx-NCR-000809 - Cover meter survey Grid lines 1-9 Cxxx-NCR-001231 - N17 Verticality
| 03SR - Stations (RfL) | Cxxx-NCR-001484 | NCR | IL16 High Slump Concrete |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-10-31 | 2014-10-03 12:04 | -28 | 2014-08-21 08:25 | Structural Engineering - Concrete Member | 1500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | 7 No slump observations recorded with 250 slump which is greater than 240 allowed with S4 mix. Please find attached concrete delivery records stating the batch ticket no# for reference.
| 03SR - Stations (RfL) | Cxxx-NCR-001485 | NCR | D-Wall repairs Section I2 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-01-27 | 2015-01-09 16:05 | -18 | 2014-08-18 10:33 | Structural Engineering - Diaphragm Walls | 10000 |  | Material | Rework | 2 (6-60k) | Complete | Material/Preservation Problems - Other | Completed |  | This NCR covers D-Wall defects in Section I2 (See attached) This is Panels S1-S25 from intermediate floor level to Underside of roof level. A full snagging list will be developed following and CR inspection
| 03SR - Stations (RfL) | Cxxx-NCR-001486 | NCR | D-Wall repairs Section I3 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-04-30 | 2015-04-13 15:29 | -17 | 2014-08-18 10:39 | Structural Engineering - Diaphragm Walls | 10000 |  | Material | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | This is Panels N27-N54 from intermediate floor level to Underside of roof level. A full snagging list will be developed following and CR inspection Inclused in this will be issued raised in the following NCRs Cxxx-NCR-0001113 - DN20 and DN21 - cages misalignment GL 10 to 12 (Cover surveys required)
| 03SR - Stations (RfL) | Cxxx-NCR-001487 | NCR | D-Wall repairs Section I4 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-01-27 | 2015-01-09 16:08 | -18 | 2014-08-18 10:58 | Structural Engineering - Diaphragm Walls | 10000 |  | Material | Rework | 2 (6-60k) | Complete | Material/Preservation Problems - Other | Completed |  | This NCR covers D-Wall defects in Section I1 (See attached) This is Panels S26-S51 from intermediate floor level to Underside of roof level. A full snagging list will be developed following and CR inspection Inclused in this will be issued raised in the following NCRs Cxxx-NCR-001281 - Boxout materials distributed throughout D-Wall Pannel S29
| 03SR - Stations (RfL) | Cxxx-NCR-001488 | NCR | D-Wall repairs Section I5 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-10-09 | 2015-10-02 09:50 | -7 | 2014-08-18 11:19 | Structural Engineering - Diaphragm Walls | 10000 |  | Material | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | This NCR covers D-Wall defects in Section I5 (See attached) This is Panels N55-N81 from intermediate floor level to Underside of roof level. A full snagging list will be developed following and CR inspection
| 03SR - Stations (RfL) | Cxxx-NCR-001489 | NCR | D-Wall repairs Section I6 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-01-27 | 2015-01-09 16:10 | -18 | 2014-08-18 11:22 | Structural Engineering - Diaphragm Walls | 10000 |  | Material | Rework | 2 (6-60k) | Complete | Material/Preservation Problems - Other | Completed |  | This NCR covers D-Wall defects in Section I1 (See attached) This is Panels S52-S77 from intermediate floor level to Underside of roof level. A full snagging list will be developed following and CR inspection
| 03SR - Stations (RfL) | Cxxx-NCR-001490 | NCR | D-Wall repairs Section C1 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-09-04 | 2015-08-26 15:48 | -9 | 2014-08-18 12:07 | Structural Engineering - Diaphragm Walls | 10000 |  | Material | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | This NCR covers D-Wall defects in Section C1 (See attached) This is Panels N1-N26 from concourse floor level to intermediate soffit level. A full snagging list will be developed following and CR inspection Inclused in this will be issued raised in the following NCRs Cxxx-NCR-001231 - N17 Verticality Cxxx-NCR-001326 - D-Wall Panel N23 and Cavity Drain Pipe Clash
| 03SR - Stations (RfL) | Cxxx-NCR-001491 | NCR | D-Wall repairs Section C2 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-09-04 | 2015-08-26 15:51 | -9 | 2014-08-18 12:13 | Structural Engineering - Diaphragm Walls | 10000 |  | Material | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | This NCR covers D-Wall defects in Section C1 (See attached) This is Panels S1-S25 from concourse floor level to intermediate soffit level. A full snagging list will be developed following and CR inspection
| 03SR - Stations (RfL) | Cxxx-NCR-001493 | NCR | D-Wall repairs Section C3 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-04-24 | 2015-04-13 15:31 | -11 | 2014-08-18 12:24 | Structural Engineering - Diaphragm Walls | 10000 |  | Material | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | This NCR covers D-Wall defects in Section C1 (See attached) This is Panels N27-N54 from concourse floor level to intermediate soffit level. A full snagging list will be developed following and CR inspection
| 03SR - Stations (RfL) | Cxxx-NCR-001494 | NCR | D-Wall repairs Section C5 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-11-19 | 2015-11-12 12:00 | -7 | 2014-08-18 13:06 | Structural Engineering - Diaphragm Walls | 10000 |  | Material | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | This NCR covers D-Wall defects in Section I1 (See attached) This is Panels N55-N81 from intermediate floor level to Underside of roof level. A full snagging list will be developed following and CR inspection Inclused in this will be issued raised in the following NCRs Cxxx-NCR-001410 - C13 D-Wall Joint N66 N67
| 03SR - Stations (RfL) | Cxxx-NCR-001495 | NCR | D-Wall repairs Section C4 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-09-04 | 2015-08-26 16:03 | -9 | 2014-08-18 12:57 | Structural Engineering - Diaphragm Walls | 10000 |  | Material | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | This NCR covers D-Wall defects in Section I1 (See attached) This is Panels N1-N26 from intermediate floor level to Underside of roof level. A full snagging list will be developed following and CR inspection Inclused in this will be issued raised in the following NCRs Cxxx-NCR-001281 - Boxout materials distributed throughout D-Wall Pannel S29
| 03SR - Stations (RfL) | Cxxx-NCR-001496 | NCR | D-Wall repairs Section C6 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-09-04 | 2015-08-26 16:12 | -9 | 2014-08-18 13:08 | Structural Engineering - Diaphragm Walls | 10000 |  | Material | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | This NCR covers D-Wall defects in Section I1 (See attached) This is Panels N1-N26 from intermediate floor level to Underside of roof level. A full snagging list will be developed following and CR inspection
| 03SR - Stations (RfL) | Cxxx-NCR-001499 | NCR | Minor damage to tarmac topping on Eastbourne Terrace (GL13-14) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-09-17 | 2014-09-10 14:33 | -7 | 2014-08-20 17:16 | Civil - Civil Engineering General | 2500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Around 20:00 on 11/08/14, whilst the CAT 349 with Koccurek attachment was tracking up onto the grillage at MH3, the tracks of the machine moved the plywood which had been laid to protect the tarmac. This resulted in direct contact of the machine with the ground, causing minor damage to the tarmac topping of the road. A photograph of the resulting damage is attached. To prevent a reoccurance, any operative involved in a repeat of this operation or a similar task will be more attentive to the potential danger of damage. A briefing on this issue will be given to the operatives involved.
| 03SR - Stations (RfL) | Cxxx-NCR-001500 | NCR | IL16 Cover to cavity drainage pipes |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-09-30 | 2014-08-27 12:24 | -34 | 2014-08-19 18:20 | Civil - Drainage | 1500 |  | Material | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | It was not possible to achieve the correct minimum cover around to cavity drainage down pipes due to clashes with the D-wall starter bars.
| 03SR - Stations (RfL) | Cxxx-NCR-001501 | NCR | E__ Road base construction |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-09-30 | 2020-03-19 11:41 | 536 | 2014-08-19 18:17 | Civil - Roadworks Joints | 10000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | NCR The connection of the newly installed 335mm gas main to the existing gas main at Praed street required an excavation which was to be reinstated as per Cxxx-SKC-D-DDD-M171_Z-04480. Due to the strength of the concrete that was used for the road base on Eastbourne terrace, a saw cut was required for the excavations. The saw cut method left a ‘clean cut’ in the existing concrete, which in turn allowed for a much neater installation of the 600mm dowel bars as per Cxxx-SKC-D-DDD-M171_Z-04480 prior to road base reinstatement. However at the location of the Praed Street gas connection, the cover to existing buried services was known to be less than standard depths. Therefore it was decided by /__ Utilities not to use a saw cut method in the interest if minimising risk of a service strike. Consequently during the connection of the 335mm gas main to the existing gas main at Praed street, the saw cut method was not used, with the effect that the concrete finish was not smooth.
| 03SR - Stations (RfL) | Cxxx-NCR-001502 | NCR | PC13 Damaged Strain Gauge |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-09-30 | 2014-08-28 11:24 | -33 | 2014-08-19 18:10 | Surveying - Geotechnical Surveys | 1000 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | On 19/8/14 it was noted the strain gauge B on PC13 was damaged. It is believed that this occurred when during construction the batteries were knocked loose, creating a short circuit which led to a power surge, which it is believed has damaged the vibrating wire the measures strain. This is to be verified with a time domain reflexometer (TDR) being used to test the wire. This was the last remaining gauge working on the web of this plunge column. As agreed with Cxxx, strain in the plunge column is now to be monitored using a combination of diagonal flange gauges, C and F. This plot has already been set up on the Contractor's Database and is being monitored ongoing.
| 03SR - Stations (RfL) | Cxxx-NCR-001503 | NCR | E__ - Dowel Bar installation |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-09-30 | 2020-06-05 14:29 | 614 | 2014-08-19 18:25 | Civil - Roadworks Joints | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Dowel Bars have not be installed as per Cxxx-SKC-D-DDD-M171_Z-04480 in trench excavations which are 1000mm or less in width during the reinstatement of Eastbourne Terrace carriageway concrete roadbase.
| 03SR - Stations (RfL) | Cxxx-NCR-001504 | NCR | Pre-installation condition survey of columns in 20 Eastbourne Terrace |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-09-24 | 2014-08-27 17:37 | -28 | 2014-08-20 09:02 | Surveying - Instrumentation and Monitoring | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | As specified in KX10.2107 of Cxxx-OVE-Z4-RSP-CR001-00007, the contractor is required to make a pre-installation condition survey, comprising of written and photographic records, recording the pre-installation conditions at the locations of all monitoring equipment prior to installation. This was not done for the installation of anchor points for tape extensometers in the basement of 20 Eastbourne Terrace. The reason why this was not done was a lack of awareness of this requirement in the specification. However, the works in question are considered low impact, and it can be seen from the post installation photos that no damage has been caused to the columns during the installation.
| 03SR - Stations (RfL) | Cxxx-NCR-001505 | NCR | NCRs Captured in Surveillance Cxxx-SKC-O-RGN-B071_WS077-50205 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-09-17 | 2014-09-08 08:59 | -9 | 2014-08-20 12:14 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Surveillance Cxxx-SKC-O-RGN-B071_WS077-50205 recorded the following NCR: - Drawings for lighting columns not approved prior to activity start. At time of surveillance these drawings were at revision P05. Drawing reference Cxxx-SKC-S-DDD-M171_1-06100
| 03SR - Stations (RfL) | Cxxx-NCR-001507 | NCR | IL11 & IL12 - Slab Level Adjustment (__F-487-NCR-158) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-11-17 | 2014-10-20 15:44 | -28 | 2014-08-21 13:58 | Civil - Civil Engineering General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Intermediate Slab I11 and I12, With reference to __F-487-RFI-948 a 12mm rider bar was placed in the T2 layer to ease reinforcement congestion in the top zone which has resulted in slab levels being raised between +0mm and +15mm to maintain cover. See attached surveys.
| 03SR - Stations (RfL) | Cxxx-NCR-001508 | NCR | C06 Concourse Slab – 2hr Batching time exceeded |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-09-25 | 2014-08-27 12:17 | -29 | 2014-08-21 15:22 | Structural Engineering - Concrete Member | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | 2hr time for batching to placement (see Cxxx-FCD-001483) exceeded for one load. Ticket number 331706 with delivery ticket showing 2hr 35 mins from batching to end of placement. Delivery for 331706 was out of sequence with other deliveries.
| 03SR - Stations (RfL) | Cxxx-NCR-001509 | NCR | Concourse Level; East Liner Wall Couplers |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-09-26 | 2014-08-29 11:01 | -28 | 2014-08-22 11:58 | Structural Engineering - Reinforcement | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Previous Construction - Interfacing issues | Completed |  | The positions of the couplers in Dwall Panel S77 on the Concourse level that connect to the verts in the west liner wall are too far west beyond the correct position.
| 03SR - Stations (RfL) | Cxxx-NCR-001510 | NCR | 2 hour placing period concourse mix |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-09-09 | 2014-08-27 17:43 | -13 | 2014-08-26 12:22 | Structural Engineering - Concrete Member | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Cxxx-FCD-001235 justifies the extension for placing fresh concrete from 1 hour to 2 hours for the concourse C40/50 F 80% mix cert 1005277589A. However after Concourse Slab Pour Area 2 the mix was changed to C40/50 F 80% mix cert 1005277589 (Note no “A”) for the remainder of the concourse slab. This NCR is to capture the fact that occassionally concrete loads for the concourse slab exceeded the agreed 1 hour between loads (but less than 2 hours) without an approved FCD in place for the new mix.
| 03SR - Stations (RfL) | Cxxx-NCR-001511 | NCR | D-Wall repairs Section B1 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-03-18 | 2016-03-14 12:25 | -4 | 2014-08-26 14:23 | Structural Engineering - Diaphragm Walls | 10000 |  | Material | Rework | 2 (6-60k) | Complete | Material/Preservation Problems - Other | Completed |  | This NCR covers D-Wall defects in Section B1 (See attached) This is Panels N1-N26 from platform level to the underside of concourse level. A full snagging list will be developed following and CR inspection This NCR will close out all items covered by the following current NCRs NCR-000302 - N09, 106.995mATD (3hrs 20mins between batching and placing) NCR-000303 - N09, 106.995mATD (Elapsed time between loads, 2hrs and 1hr20 between concrete placing)
| 03SR - Stations (RfL) | Cxxx-NCR-001512 | NCR | D-Wall repairs Section B2 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-10-04 | 2015-08-11 15:06 | -54 | 2014-08-26 14:28 | Structural Engineering - Diaphragm Walls | 10000 |  | Material | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | This NCR covers D-Wall defects in Section B2 (See attached) This is Panels S1-S25 from platform level to the underside of concourse level. A full snagging list will be developed following and CR inspection This NCR will close out all items covered by the following current NCRs NCR-000201 - S07: Break In Monolithic Concrete Pour NCR-000331 - Panel S07 Concrete Pour (Visual inspection required)
| 03SR - Stations (RfL) | Cxxx-NCR-001513 | NCR | D-Wall repairs Section B3 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-03-18 | 2016-04-19 16:42 | 32 | 2014-08-26 14:31 | Structural Engineering - Diaphragm Walls | 10000 |  | Material | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | This NCR covers D-Wall defects in Section B3 (See attached) This is Panels N26-N54 from platform level to the underside of concourse level. A full snagging list will be developed following and CR inspection
| 03SR - Stations (RfL) | Cxxx-NCR-001514 | NCR | D-Wall repairs Section B4 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-11-30 | 2015-11-23 14:02 | -7 | 2014-08-26 14:32 | Structural Engineering - Diaphragm Walls | 10000 |  | Material | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | This NCR covers D-Wall defects in Section B4 (See attached) This is Panels S26-N51 from platform level to the underside of concourse level. A full snagging list will be developed following and CR inspection
| 03SR - Stations (RfL) | Cxxx-NCR-001515 | NCR | D-Wall repairs Section B5 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-03-18 | 2016-03-14 11:43 | -4 | 2014-08-26 14:37 | Structural Engineering - Diaphragm Walls | 10000 |  | Material | Rework | 2 (6-60k) | Complete | Material/Preservation Problems - Other | Completed |  | This NCR covers D-Wall defects in Section B5 (See attached) This is Panels N55-N81 from platform level to the underside of concourse level. A full snagging list will be developed following and CR inspection This NCR will close out all items covered by the following current NCRs NCR-000309 - Panel S75 Level (coupler level at base slab)
| 03SR - Stations (RfL) | Cxxx-NCR-001516 | NCR | D-Wall repairs Section B6 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-10-04 | 2015-08-28 11:12 | -37 | 2014-08-26 14:39 | Structural Engineering - Diaphragm Walls | 10000 |  | Material | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | This NCR covers D-Wall defects in Section B6 (See attached) This is Panels S52-S77 from platform level to the underside of concourse level. A full snagging list will be developed following and CR inspection
| 03SR - Stations (RfL) | Cxxx-NCR-001517 | NCR | __ - Damaged Wall Starter Bars – __ – L41 (__F-487-NCR-160) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-03-25 | 2016-02-26 14:32 | -28 | 2014-08-27 09:50 | Structural Engineering - Reinforcement | 2500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Departures Road Level – Wall __ L-41 at GL9 Wall starter bars adjacent to the haul road at GL 9 have been damaged by placement of skips next to the Mole Hole being used for removal of muck away from the excavation below Concourse. Bars are B16 on north side and B12 on south side. Please note area will be used for skip loading until excavation finished on site so NCR can’t be closed until then. Please see attachments: Cxxx-SWN-S-DDA-M171_2-01563_NCR-160_1 Cxxx-SWN-S-DDA-M171_1-01663_NCR-160_2
| 03SR - Stations (RfL) | Cxxx-NCR-001518 | NCR | Alternative binder spec used for trench reinstatement surfacing |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-10-10 | 2014-10-10 15:36 | 0 | 2014-08-27 13:32 | Civil - Wearing Course | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Other | Completed |  | The earliest date and time that the surfacing subcontractor __ could provide resources to lay the base and wearing course for trench reinstatement was Fri 22 Aug after 1800 hrs. At this time, the batching plants that usually supply the binder material previously used (and approved by MCR) were closed and would not be able to remain open for the back shift due to the forthcoming bank holiday weekend. __ proposed an alternative binder material on Thurs 21 Aug to for approval, attached to this MCR. The alternative binder material was used in place of the one approved on MCR Cxxx-SKC-O-TSC-B071_WS077-50283
| 03SR - Stations (RfL) | Cxxx-NCR-001519 | NCR | __ – Damage to Precast Spine Beam Units (__F-487-NCR-163) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-04-30 | 2016-04-28 09:09 | -2 | 2014-08-28 16:50 | Civil - Civil Engineering General | 10000 |  | Damaged | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | in Departures Road Level – Spine Beam G/L 9.5-14.5. RCP of Intermediate Level. Various chipped and accidental damage to spine beam precast units as identified on attached mark up for locations together with photographs.
| 03SR - Stations (RfL) | Cxxx-NCR-001520 | NCR | Tape Extensometers in 20 Eastbourne Terrace |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-09-12 | 2014-09-01 09:06 | -11 | 2014-08-29 13:38 | Surveying - Geotechnical Surveys | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | For the eye bolts used for the installation of tape extensometers in the basement of 20 Eastbourne Terrace, outlined in MCR Cxxx-SKC-0-TSC-B071_WS077, the relevant specification requires that stainless steel bolts be used. However, for the installation, durable steel bolts have been used. The relevant specification is Cxxx-OVE-Z4-RSP-CR001-00007, section KX10.3217. However, the bolts are contained within a non-aggressive environment, with a required useful life of approximately 18 months to 2 years. It is considered that there is no issue with regards to the durability of the bolts. Photos of the installation are attached for reference.
| 03SR - Stations (RfL) | Cxxx-NCR-001521 | NCR | Bent shear rails C2 Zone 7 repair |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-09-30 | 2014-09-09 15:17 | -21 | 2014-09-02 15:37 | Structural Engineering - Concrete Member | 2500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | While breaking out concrete as part of C2-Zone repair a number of shear rails have been slightly bent. Please see attached mark up and photos showing amount of damaged shear rails. Due to the number and small degree of bending that has occured propose to leave as is.
| 03SR - Stations (RfL) | Cxxx-NCR-001522 | NCR | Concourse Slab C13 – 2hr batching time exceeded |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-09-30 | 2014-09-08 09:13 | -22 | 2014-09-02 15:40 | Structural Engineering - Concrete Member | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | 2hr time for batching to placement exceeded for 8 loads for ticket numbers 467432,477533,477535,477536,477537,477539,477541,477542. Times exceed by range of 1min to 35mins (477542)
| 03SR - Stations (RfL) | Cxxx-NCR-001523 | NCR | Damaged to Precast Units: Dig below Concourse Level (__F-NCR-164) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-06-30 | 2016-06-02 10:01 | -28 | 2014-09-02 16:41 | Civil - Civil Engineering General | 30000 |  | Damaged | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | RCP of Base Slab. Precast Units of Concourse Level Soffit at G/12.5 1. Photo D1: Dowel bars from Concourse slab stop end penetrated through underside of coffer CS-02 and panel US-02B 2. Photo D2: Grout spill at joint between units US-01 at GL 13 3. Photo D3 : Large chip to edge of unit type US-01 at G/L 12.5 4. Photo D4: Minor damage to face of panel type FS30-D at GL 13 Please see attached documents for clarification.
| 03SR - Stations (RfL) | Cxxx-NCR-001524 | NCR | T-33 -IL Tension Wall T-33 As-built survey out of tolerance |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-09-24 | 2014-09-15 13:46 | -9 | 2014-09-04 11:41 | Civil - Civil Engineering General | 2500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Location: Intermediate Level GL 14.5 C-E As-built survey shows a number of locations where the permitted deviation (10mm) for verticality and curvature have been exceeded. See attached.
| 03SR - Stations (RfL) | Cxxx-NCR-001525 | NCR | Damaged B16 Couplers in West Liner Wall |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-09-30 | 2014-09-15 13:44 | -15 | 2014-09-04 11:35 | Structural Engineering - Reinforcement | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Intermediate level, IL1, Gridline 1/A-D There are 6 B16 couplers damaged in the Dwall behind the west liner wall, panel W1 -W3.
| 03SR - Stations (RfL) | Cxxx-NCR-001526 | NCR | Damage to C20 series piezometers |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-10-10 | 2014-10-10 15:19 | 0 | 2014-09-05 15:57 | Surveying - Instrumentation and Monitoring | 1500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During excavation to 104.5m west of MH3, the cables running from the C12 series piezometers were severed. At this stage, it is not possible to repair the cables, as they have are still buried and need to be recovered. The recovery has been arranged at the SOS for week commencing 8th September. The recovery works will involve the survey team locating the known position of the cables, with the cables being dug out and repaired. The damage report has been attached to this NCR, along with data plots showing when the instrument went offline.
| 03SR - Stations (RfL) | Cxxx-NCR-001527 | NCR | C12 Magnetic Extensometer Damage |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-12-09 | 2014-11-25 16:02 | -14 | 2014-09-17 12:11 | Surveying - Instrumentation and Monitoring | 2500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Sometime during the excavation of the ground inbetween the tunnels between GL11 and GL12, the tube for the C12 magnet extensometer appears to have been smashed and the top of the tube blocked with clay. A more detailed assessment will be made once access is granted for inspection. The instruments have not been read since February 2014, when they were buried as part of the concourse slab construction. The instruments have only been recovered following the excavation below concourse. In order for the instruments to become operational again, the tubes will need to be jet washed to remove any blockages. The best case scenario is that the tube is only blocked at the top, in which case the blocked tube will be cut off and the instrument reinstated. Worst case is that the tube will have to be cut down. As with C12 piezometers, any recovery/repair works are dependent on access. At present, it is not possible to enter the box to undertake any repairs, due to the progression of the excavation works and tunnel ring removal in that area. The attached plots show the time the instrument was last read.
| 03SR - Stations (RfL) | Cxxx-NCR-001528 | NCR | C20 Piezometers Stopped Reading |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-10-10 | 2014-09-27 12:21 | -13 | 2014-09-05 16:15 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Not Defined | Completed |  | On 5th September 2014, it was noted that the C20 series piezometers have stopped transmitting readings. It is thought, from review of the data plots, that the transmitter has either lost power or signal. The transmitter is located in an exclusion zone as it is within the formwork of IL15. Once the formwork has been struck, the transmitter can be accessed to make an assessment of the damage. the current data plots are attached showing when the instrument went offline.
| 03SR - Stations (RfL) | Cxxx-NCR-001529 | NCR | PC35 Daamged transmitter |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-09-19 | 2014-09-08 09:00 | -11 | 2014-09-05 16:23 | Surveying - Instrumentation and Monitoring | 1500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The transmitter on PC35 was damaged on 22/8/14. It appears that the transmitter was knocked over which smashed the aerial and battery box. As a result of this damage, no data was received from 22/8/14 until 5/9/14, when the replacement transmitter went online. Damage reports are attached to this NCr, as is a data plot from 5/9/14 showing that the gauge is now back online.
| 03SR - Stations (RfL) | Cxxx-NCR-001530 | NCR | Slab strain gauges no longer transmitting readings |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-09-30 | 2014-09-18 09:54 | -12 | 2014-09-05 16:36 | Surveying - Instrumentation and Monitoring | 1000 |  | Equipment Breakdown | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The strain gauges listed below have stopped reading on the dates noted: DN28-B: 1st September 2014 DS14-B: 29th September 2014 CS15-T: 5th September 2014 CS15-B: 5th September 2014 It is not currently known what the cause of the breakdown is. This is to be investigated by Datum week commencing 8th September.
| 03SR - Stations (RfL) | Cxxx-NCR-001531 | NCR | C09 surface cracks |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-10-06 | 2014-09-15 13:48 | -21 | 2014-09-08 16:38 | Structural Engineering - Concrete Member | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Surface cracks appeared on C09 slab. The crack width is less than 0.3mm, with the exception of one location which is approximately 0.5mm in a 100mm long section (See attached Photo).
| 03SR - Stations (RfL) | Cxxx-NCR-001532 | NCR | Concourse Slab – Damaged Cavity Drainage Inserts |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-03-06 | 2014-11-25 13:46 | -101 | 2014-09-09 09:00 | Civil - Drainage | 5000 |  | Damaged | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Three number cavity drain inserts at GL 8 North , GL 9 South , and GL 15 South have been damaged during concreting operations.
| 03SR - Stations (RfL) | Cxxx-NCR-001533 | NCR | Column C3-N Cutting Starter Bars |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-11-07 | 2014-10-24 13:39 | -14 | 2014-09-09 15:04 | Structural Engineering - Reinforcement | 2500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Concourse level C02 GL: 3/C-D Three number B20 starter bars were cut to access the area within the footprint of the column that needed to be broken out. Bars were cut 150mm from surface of concrete. This was carried out before adequate approvals were in place.
| 03SR - Stations (RfL) | Cxxx-NCR-001534 | NCR | C09 Concourse Slab - Precast Unit US-02a |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-04-30 | 2016-04-11 16:27 | -19 | 2014-09-09 15:43 | Structural Engineering - Pre-cast | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Damage to corner of US-02A panel as shown in attached photos and sketches.
| 03SR - Stations (RfL) | Cxxx-NCR-001535 | NCR | Concourse Slab C15 – 2hr batching time exceeded |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-09-24 | 2014-09-15 09:56 | -9 | 2014-09-10 08:39 | Structural Engineering - Concrete Member | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 2hr time for batching to placement exceeded for 6 loads for ticket numbers 369016,369019,669042,507350,507353, and 369048. Times exceed by range of 3min to 25mins (507353)
| 03SR - Stations (RfL) | Cxxx-NCR-001536 | NCR | __ Yard - precast panels - defects 31 - 36 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-09-24 | 2014-09-23 09:11 | -1 | 2014-09-10 10:57 | Structural Engineering - Pre-cast | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Attached 6 No Internally Raised NCRs produced at __ Yard during production of precast concrete units for inclusion in works at Cxxx Paddington Crossrail.
| 03SR - Stations (RfL) | Cxxx-NCR-001537 | NCR | CS-03 Rod Extensometer |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-09-30 | 2014-09-27 12:23 | -3 | 2014-09-10 14:07 | Surveying - Instrumentation and Monitoring | 1000 |  | Equipment Breakdown | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Rod extensometer CS-03 stopped transmitting readings on 26th August 2014. The cause of this is flooding and general wear and tear on the transmitter. A replacement transmitter has been ordered and is to be installed 11th September. The data plot showing when the instrument went down is attached for information.
| 03SR - Stations (RfL) | Cxxx-NCR-001538 | NCR | C2 North Strain Gauge Damage |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-10-14 | 2014-09-18 10:29 | -26 | 2014-09-10 14:22 | Surveying - Instrumentation and Monitoring | 1500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During C2 remedial works, the strain gauges on the North side of the box were damaged as detailed below: Top gauge: the strain gauge itself has been destroyed by impact from the concrete breaking. This cannot be recovered. Bottom gauge: the cables have been severed in two places. It has been repaired by soldering a new piece of cables between the two breaks. Damage reports are attached to this NCR, along with a data plot showing that CN-02B has now been recovered.
| 03SR - Stations (RfL) | Cxxx-NCR-001539 | NCR | IL 15 Concrete Batching Times (__F-487-NCR-171) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-10-15 | 2014-10-10 16:34 | -5 | 2014-09-10 16:45 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Intermediate Slab IL 15, 2hr time for batching to placement slightly exceeded for 5 loads for ticket numbers 512551,512554,536765,536722 and 536774. Times exceed by range of 1min to 10mins (536774) Please see attached concrete delivery record for clarification.
| 03SR - Stations (RfL) | Cxxx-NCR-001542 | NCR | IL-8 Slab Level Adjustment (__F-487-NCR-170) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-09-29 | 2014-09-25 09:49 | -4 | 2014-09-15 09:21 | Civil - Civil Engineering General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | With reference to __F-487-RFI-948 a 12mm rider bar was placed in the T2 layer to ease reinforcement congestion in the top zone which has resulted in slab levels being raised between +0mm and +18mm to maintain cover. See attached survey.
| 03SR - Stations (RfL) | Cxxx-NCR-001543 | NCR | C08 Lift Pit Wall Top Lacers |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-10-13 | 2014-10-10 16:40 | -3 | 2014-09-15 17:11 | Structural Engineering - Concrete Member | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The lift pit dividing wall in Concourse Slab C08 was poured with incorrect reinforcement detailing. Due to recesses in the wall (as shown in the attached sketch) the vertical reinforcement varies in height resulting in the top lacer bar not being placed in the knuckle of the reinforcement over the full width of the wall. The error was noticed shortly before the wall was poured however the pour went ahead as the concrete arrived earlier than expected before the error had been communicated to the site team.
| 03SR - Stations (RfL) | Cxxx-NCR-001544 | NCR | DN 25 __ Repair |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-09-14 | 2016-07-29 12:57 | -47 | 2014-09-15 16:56 | Structural Engineering - Surface Treatment | 1500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The shutter had been removed too quickly for the Prepufe membrane. Along the length of the pour the __ had not adhered for approximately the top 300mm of the concrete. Please find attached __ QA sheet.
| 03SR - Stations (RfL) | Cxxx-NCR-001545 | NCR | S62b Clay inclusion |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-01-27 | 2015-01-28 11:32 | 1 | 2014-09-17 11:55 | Structural Engineering - Diaphragm Walls | 4000 |  | Material | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | While cleaning was underway on diaphragm wall S62b a clay inclusion was found under the roof soffit. See attached diagram showing extends of clay inclusion. please advise on any constraints required with this repair. especially in regards to excavation below concourse.
| 03SR - Stations (RfL) | Cxxx-NCR-001546 | NCR | C2N Strain Gauge Damage |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-10-31 | 2014-10-02 11:34 | -29 | 2014-09-17 17:44 | Surveying - Instrumentation and Monitoring | 1500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the breakout of C2 concrete, as part of the ongoing C2 remedial works, there was damage to the strain gauge. It was noted on 8/9/14 that the cables running to C2N-B were severed. This was repaired by cutting out the damaged cable and soldering a new length of cable in place. Also, on 8/9/14, it was noted that that the top gauge has been destroyed by the impact of the breaking. This gauge cannot be recovered/repaired. This instrument is to be set to faulty on the Contractor's Database. Damage report EDR 59 relating to the above breakages is attached to this NCR for reference. Subsequent to the repair on CN-02B cables, the cables were damaged again on 15/9. These cables have now been repaired. A damage report will be submitted to accompany this NCR when it is received. The data plot showing that Cn-02B is now reporting again is attaché for reference.
| 03SR - Stations (RfL) | Cxxx-NCR-001547 | NCR | No MCR in place for the lift shaft holding down bolts |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2015-09-24 | 2015-09-02 16:37 | -22 | 2014-09-18 10:34 | Civil - Structural Engineering | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Inspection carried out on 8th September 2014 attended by __ and __ identified that bolts cast in to the concourse slab around the location of the unpaid lift have been installed without an MCR in place
| 03SR - Stations (RfL) | Cxxx-NCR-001548 | NCR | C01 Cold joint durability |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-01-13 | 2015-12-04 13:54 | -40 | 2014-09-19 13:45 | Structural Engineering - Concrete Member | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The joint identified in Slab C01 is approximately 420mm below the top of concrete level so is approximately in the middle of the slab. For this reason water ingress to the reinforcement is not possible from above or below but only from the side face. This face is an internal surface with no horizontally driven water and as such water ingress is not expected to be an issue. In addition it was found from the core samples this joint has good bond between layers. It is therefore our opinion that no additional waterproofing is required.
| 03SR - Stations (RfL) | Cxxx-NCR-001549 | NCR | Pile Fab ITP not accepted before fabrication started |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-10-16 | 2014-10-10 15:25 | -6 | 2014-09-19 14:55 | Structural Engineering - Reinforcement | 1000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Pre-fabrication of the pile cages for the Bakerloo Line Link has commencd before an Inspection and Test Plan (ITP) has been accepted by Crossrail.
| 03SR - Stations (RfL) | Cxxx-NCR-001550 | NCR | PC19 Damage to strain gauges |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-11-26 | 2014-11-25 16:04 | -1 | 2014-09-24 09:25 | Surveying - Instrumentation and Monitoring | 1000 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the breaking of the blinding beneath the concourse slab in the vicinity of PC19, two of the strain gauges on the plunge columns have been damaged beyond repair. The gauges that have been damaged are gauges D and A. Previously gauges E/F were set to faulty on 5th March 2014. The remaining working gauges on PC19 are gauges B and C. Gauge B is the gauge that is currently used to monitor load, with corrections applied for harmonic effects. This will continue to be the case as the excavation progresses. Damage reports and data plots showing when the gauges were damaged (between 19/20 September) are attached for information.
| 03SR - Stations (RfL) | Cxxx-NCR-001551 | NCR | BLL Pile 90 Open Bore Duration |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-10-24 | 2014-10-24 13:38 | 0 | 2014-09-26 07:31 | Structural Engineering - Concrete Member | 1500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Pile 90 has not been constructed in line with Clause KP11.1205 (v) which states that 'for piles founded in London Clay, the time period between commencement of excavation in the London Clay and the completion of placement of concrete shall not exceed 12hrs. The reinforcement cage has already been installed but concrete was not installed within the 12hr period.
| 03SR - Stations (RfL) | Cxxx-NCR-001552 | NCR | BLL Incorrect Pile Depth (Pile 90) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-10-24 | 2014-10-17 16:42 | -7 | 2014-09-26 14:49 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Further to Cxxx-NCR-001551 (Open Bore Time) Pile 90, bored on 25/09/2014 was not excavated to the minimum bore depth. This depth inadequacy was not established until 26/09/2014.
| 03SR - Stations (RfL) | Cxxx-NCR-001553 | NCR | Wall L-34 (Pour 4)- Curing Agent not applied |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-11-28 | 2014-10-10 16:36 | -49 | 2014-09-29 18:01 | Structural Engineering - Surface Treatment | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Curing agent not applied to wall CL-L-34 (GL 11 1-B) in accordance to Cxxx Civils & Structural Specifications KF11.3207 (Document No: Cxxx-SWN-S-RSP-B071-00005).
| 03SR - Stations (RfL) | Cxxx-NCR-001554 | NCR | IL 8; Permit to unload constriaints |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-11-28 | 2014-11-27 10:26 | -1 | 2014-09-29 20:24 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Discrepancy noted on permit to unload process. Cubes ref 984 B/C/D failed to reach design strength and permit to unload was signed off by . The striking constraints detailed in (Cxxx-RFI-001669) was not followed. 'Cxxx would have no objection to a proposal which ensured a minimum 6m of full strength slab remains supported when striking Intermediate slab pours'. Please find attached IL08 permit to unload documentation for clarity.
| 03SR - Stations (RfL) | Cxxx-NCR-001555 | NCR | Damage to concourse slab soffit level due to blinding removal |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2015-12-15 | 2015-12-16 16:56 | 1 | 2014-09-30 16:59 | Civil - Excavation | 5000 |  | Damaged | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | during the removal of blindng at the concourse soffit level, impact damage has occurred to the to the soffit. A mitigation action was implemented when the sam eproblem occurred at roof slab soffit, but this has not follwed down to concourse level
| 03SR - Stations (RfL) | Cxxx-NCR-001556 | NCR | Paint on pile cages - Bakerloo line link |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2014-11-04 | 2014-10-13 09:04 | -22 | 2014-09-30 17:14 | Geotechnical Engineering - Concrete - Bored Pile | 1500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Lifting bands have been painted at the fabrication yard to identify the lift positions. However, the band is located at a link position and so forms part of the reinforcement cage as required by the design intent. Painted rebar is strictly prohibited due to the unkown bond performance
| 03SR - Stations (RfL) | Cxxx-NCR-001557 | NCR | No IRF form for 22/09 - 26/09 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-10-29 | 2014-10-15 10:25 | -14 | 2014-10-01 07:58 | Structural Engineering - Concrete Member | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | No IRF form was raised for the Bakerloo Line Link Piling works between 22/09 - 26/09.
| 03SR - Stations (RfL) | Cxxx-NCR-001558 | NCR | Concrete placed after 2 hours from batching |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-11-14 | 2014-11-03 16:53 | -11 | 2014-10-01 08:05 | Structural Engineering - Concrete Member | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Concrete used for Piles 114 and 106 on 30/09/2014 was outside of the 2hr specification (KF12.3221 (b)). The concrete was batched at 3:19pm with concrete discharging at 4:50pm and finished at 5:55pm.
| 03SR - Stations (RfL) | Cxxx-NCR-001559 | NCR | No IRF form for 29/09 - 03/10 |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2014-10-15 | 2014-10-15 10:24 | 0 | 2014-10-01 10:17 | Structural Engineering - Structural Engineering - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | No IRF form has been raised for the Bakerloo Line Link Piling works between 29/09 - 03/10 as per Works Information requirement
| 03SR - Stations (RfL) | Cxxx-NCR-001560 | NCR | Paint remover used on steel cage lifting bands |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-01-31 | 2015-01-29 15:33 | -2 | 2014-10-01 11:08 | Structural Engineering - Reinforcement | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | Steel cages from Hy-Ten for use in the Bakerloo Line Link piles were supplied with paint over the entire outer surface of the lifting bands. Nitromors paint & varnish remover was used to remove the paint from the lifting bands and was not washed off after use. The lifting bands also act as structural links as part of the permanent works.
| 03SR - Stations (RfL) | Cxxx-NCR-001561 | NCR | IL12 – Box-out position out of tolerance (__F-487-NCR-174) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-12-02 | 2014-10-21 12:18 | -42 | 2014-10-01 11:23 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Intermediate Slab IL12 GL16 North box out at GL16 cast out of tolerance too far North by 14-24mm. (Permitted deviation 10mm) Please see attached As-buit drawing for details.
| 03SR - Stations (RfL) | Cxxx-NCR-001562 | NCR | BLL Pile 122 bore open greater than 12 hours |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-11-12 | 2014-10-24 13:35 | -19 | 2014-10-02 10:04 | Structural Engineering - Concrete Member | 1500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | As part of the Bakerloo Line Link piling works pile 122 was bored on 01/10/2014. The pile was not completed within the 12 hours required in the specification. The pile was backfilled on 01/10/0/2014.
| 03SR - Stations (RfL) | Cxxx-NCR-001563 | NCR | BLL Pile 51 bore open greater than 12 hours |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-10-30 | 2014-10-24 13:33 | -6 | 2014-10-02 10:08 | Structural Engineering - Concrete Member | 1500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | As part of the Bakerloo Line Link piling works pile 51 was bored on 01/10/2014. The pile was not completed within the 12 hours required in the specification. The pile was backfilled on 01/10/0/2014.
| 03SR - Stations (RfL) | Cxxx-NCR-001564 | NCR | BLL Pile 110 bore open greater than 12 hours |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-11-12 | 2014-10-24 13:24 | -19 | 2014-10-02 10:13 | Structural Engineering - Concrete Member | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | As part of the Bakerloo Line Link piling works pile 110 was partially bored on 01/10/2014. The pile was not completed within the 12 hours required in the specification. The pile was backfilled on 02/10/2014.
| 03SR - Stations (RfL) | Cxxx-NCR-001565 | NCR | BLL Pile 59 bore open greater than 12 hours |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-11-12 | 2014-10-25 08:55 | -18 | 2014-10-02 10:18 | Structural Engineering - Concrete Member | 1500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | As part of the Bakerloo Line Link piling works pile 59 was partially bored on 01/10/2014. The pile was not completed within the 12 hours required in the specification. The pile was backfilled on 02/10/2014.
| 03SR - Stations (RfL) | Cxxx-NCR-001566 | NCR | Flow test outside of specification requirements |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-02-27 | 2015-02-27 16:13 | 0 | 2014-10-02 14:54 | Structural Engineering - Concrete Member | 1000 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The concrete delivered from the second wagons for the piles of the Bakerloo Line Link poured on 20/09/2014 gave a flow test result of 660mm which outside the limits of BS EN 206:2013. This concrete was included in piles 98 & 55.
| 03SR - Stations (RfL) | Cxxx-NCR-001567 | NCR | C09 Concourse Slab – Water Addition to load without additional cube set taken |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-10-16 | 2014-10-03 12:05 | -13 | 2014-10-02 15:52 | Structural Engineering - Concrete Member | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Concrete mix RC40/50F . Mix ref 219 Ticket No. 450466 had 50l water added to load. It appears that an additional cube set was not taken from the concrete delivery record.
| 03SR - Stations (RfL) | Cxxx-NCR-001568 | NCR | No MCR in place for Intermediate Level Lightwell Encast Beam |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-12-02 | 2014-11-14 16:42 | -18 | 2014-10-03 12:02 | Structural Engineering - Steel Member | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The Intermediate Level Lightwell steel I beam (GL 9- 15) has been installed without an approved MCR in place.
| 03SR - Stations (RfL) | Cxxx-NCR-001569 | NCR | 20 Eastbourne Terrace: Damaged anchor points for tape extensometers |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-10-30 | 2014-10-29 15:38 | -1 | 2014-10-07 17:57 | Surveying - Instrumentation and Monitoring | 1500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Anchor points have been installed in the basement of 20 Eastbourne Terrace to enable tape extensometers to be utilised to monitor movement of the columns relative to each other, as the excavation of the Paddington Box progresses. The anchor points have not been read since 28th July 2014, due to difficulties obtaining access to the basement due to the presence of asbestos and interfacing with demolition works. When Datum attended the site to take readings on 7th October 2014, it was found that the anchor points had been cut off using a welding torch, during the demolition works. If the monitoring is still required, the anchor points will have to be reinstalled, and re-baselined. A damage report will be attached to this NCR once it has been prepared.
| 03SR - Stations (RfL) | Cxxx-NCR-001571 | NCR | IL L53 & L18 – Concrete Placement time exceeded (__F-NCR-176) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-12-07 | 2014-10-15 15:28 | -53 | 2014-10-08 08:45 | Civil - Civil Engineering General | 2500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | on Intermediate Level, Walls L53/L18, Time between batching loads (1hr 50 and 1hr 40) at batching plant far in excess of required rate to meet 1m per hour rate of rise for these non-structural walls. 2hr limit from batching to discharge exceeded by 15mins for ticket No. 370153 and 14mins for ticket No. 370158. 1hr limit for time between discharges exceeded by 5mins for ticket Nos. 370139 and 370158. Batching plant advised of issue after first delivery time exceeded.
| 03SR - Stations (RfL) | Cxxx-NCR-001572 | NCR | Damaged Starter Bars For C21-N & C22-N Columns |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-11-19 | 2014-11-19 17:33 | 0 | 2014-10-08 10:09 | Structural Engineering - Reinforcement | 1500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | 1) 1 Starter bar has been slightly bent in column C21-N during installation of the intermediate level decking. Propose to leave bar as it is and post fix an extra bar, 600mm depth using hilti 500. 2) 1 starter bar has been cut in column C22-N for unknown reasons. Propose to replace it with post fixed bar, 750mm depth using hilti 500. See photos attached.
| 03SR - Stations (RfL) | Cxxx-NCR-001573 | NCR | IL L53– Concrete Placement time exceeded (__F-NCR-178) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-12-10 | 2014-10-15 15:29 | -56 | 2014-10-09 12:19 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Intermediate Walls L53GL18-18.5 (4/10/12) and GL21-22 (6/10/14) Pour date 4/10/14. 2hr limit from batching to discharge exceeded by 5 mins for ticket No. 370395. 1hr limit for time between discharges exceeded by 20mins for ticket Nos. 370386 and 370395. Pour date 06/10/14. 2hr limit from batching to discharge exceeded by 5 mins for ticket No. 370386.
| 03SR - Stations (RfL) | Cxxx-NCR-001574 | NCR | BLL Pile cages - detail at corners of square links |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-11-06 | 2014-10-14 16:13 | -23 | 2014-10-09 15:44 | Structural Engineering - Reinforcement | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Drawing No. Cxxx-SKC-S-DWG-B071_WS077-50182 gives the reinforcement layout for the piles in the Bakerloo Line Link. At the top of the cage the main reinforcement transitions from a circular layout to a square layout and has a pair of B16 links. The original intention was to have the main B40 vertical bars of the reinforcing cages positioned in the corners of these square links. Following a visit to the reinforcement suppliers yard before the piling works had commenced it became evident that a number of the cages did not have the vertical B40 bars in the corner of the square shaped links. The fabricator was subsequently instructed to retrofit the cages with packers inbetween the main vertical B40 bars and the corners of the square links. A number of the cages that arrived on site for inclusion in the permanent works did not contain acceptable packing arrangements where required. The affected cages from deliveries 1 - 5 are: 12, 13, 14, 15, 16, 18, 19, 22, 23, 24, 25, 26, 27, 29, 31, 32, 34, 35, 46, 47, 48, 49, 50, 51, 52, 53, 54.
| 03SR - Stations (RfL) | Cxxx-NCR-001575 | NCR | Use of Lifting Bands with no accepted TW design |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-11-06 | 2014-10-29 15:42 | -8 | 2014-10-09 16:03 | Structural Engineering - Reinforcement | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Following a review of the construction process of the first few piles of the Bakerloo Line Link the cage fabricator was instructed to amend the location of the lifting bands on the sections of reinforcing cage to reduce the risk of striking the precase coffers on the soffit of the concourse slab. A number of the cages that had not been delivered to site had already been fabricated and therefore additional lifting bands were retrofitted to these cages. Inspection of the retrofitted cages upon arrival identified that the new lifting bands had not been constructed in accordance with the fabricator's Weld Procedure Specification (WPS) or the accepted Temporary Works design for the lifting bands (see attached photograph). The piling contractor was therefore instructed to use the original lifting bands to lift (and trap) these cages. The piling contractor was observed lifting the cage 14 into pile 112 (08/10/2014) and cage 13 into pile 28 (09/10/2014) by the incorrect lifting bands.
| 03SR - Stations (RfL) | Cxxx-NCR-001576 | NCR | Cage sections not fitting together |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-11-06 | 2014-10-13 09:05 | -24 | 2014-10-09 16:23 | Structural Engineering - Reinforcement | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | During installation of cage 19 into pile 122 of the Baqkerloo Line Link piling works it was observed that one of the couplers in the bottom-middle splice of the reinforcing cage could not be engaged on both sections of the cage simultaneously (see attached photo). One of the bars was positioned incorrectly or was too short.
| 03SR - Stations (RfL) | Cxxx-NCR-001577 | NCR | Coffer struck and damaged during Bakerloo Line Link Piling Works |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-05-30 | 2016-05-26 14:15 | -4 | 2014-10-16 11:52 | Structural Engineering - Concrete Member | 1500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The precast coffer panel directly to the east of GL13 and between GLD & GLE was struck and damaged by one of the 5t crawler cranes assisting with the Bakerloo Line Link piling works on 13/10/2014. See attached mark-up and photographs.
| 03SR - Stations (RfL) | Cxxx-NCR-001578 | NCR | BLL Pile Concrete time from batching to placement exceeded 2 hours |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-11-14 | 2014-11-05 08:41 | -9 | 2014-10-17 16:22 | Structural Engineering - Concrete Member | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The concrete used for Piles 130, 134, 138, 28, 86, 82 and 78 was outside 2hr limit for batching to placement as stated within the specification (KF12.3221 (b)). Summary of non-confirmances below: Pile 130 load 2 batched 16:05, placed at 18:12, pile completed at 18:12 (time of batch for first load 15:51). Pile 134 load 1 batched 16:05, placed at 18:20, pile completed at 18:20 Pile 138 load 1 batched 16:05, placed at 18:24, pile completed at 18:33 Pile 138 load 2 batched 16:32, placed at 18:33, pile completed at 18:33 Pile 028 load 1 batched 16:32, placed at 18:42, pile completed at 18:42 Pile 086 load 1 batched 16:32, placed at 18:50, pile completed at 18:59 Pile 082 load 1 batched 17:05, placed at 19:06, pile completed at 19:06 Pile 078 load 1 batched 17:05, placed at 19:09, pile completed at 19:25 In all instances the time taken from the batching of the first concrete in to the pile to completion of the pile did not exceed 3hours (se attached concrete record).
| 03SR - Stations (RfL) | Cxxx-NCR-001579 | NCR | BLL cage detail at corner of square links |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-11-12 | 2014-10-16 14:27 | -27 | 2014-10-15 11:16 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Drawing No. Cxxx-SKC-S-DWG-B071_WS077-50182 gives the reinforcement layout for the piles in the Bakerloo Line Link. At the top of the cage the main reinforcement transitions from a circular layout to a square layout and has a pair of B16 links. The original intention was to have the main B40 vertical bars of the reinforcing cages positioned in the corners of these square links. Following a visit to the reinforcement suppliers yard before the piling works had commenced it became evident that a number of the cages did not have the vertical B40 bars in the corner of the square shaped links. The fabricator was subsequently instructed to retrofit the cages with packers inbetween the main vertical B40 bars and the corners of the square links. A number of the cages that arrived on site for inclusion in the permanent works did not contain acceptable packing arrangements where required. The affected cages from deliveries 6 - 8 are: 62 - 70, 37 - 45, 55 - 61 & 71 - 72.
| 03SR - Stations (RfL) | Cxxx-NCR-001580 | NCR | Concourse Slab Strain Gauge break down |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-10-30 | 2014-10-24 13:21 | -6 | 2014-10-16 13:04 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | On 12/10/14, concourse slab strain gauge CN-13Bb stopped transmitting readings. Subsequent investigation revealed that the connection to the transmitter was working fine, and it is infact the gauge itself that has broken down. As the gauge is embedded in concrete it is not possible to identify specifically what has caused the gauge to break down. It is not possible to recover the gauge, without breaking out the concrete and fitting a new gauge. The data plot showing the point where the gauge went offline is attached for reference. There is no damage report for this gauge, as it has broken down, rather than being damaged.
| 03SR - Stations (RfL) | Cxxx-NCR-001581 | NCR | BLL Concrete batching to placement time exceeded 2hrs 06/10/2014 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-11-14 | 2014-11-05 08:42 | -9 | 2014-10-17 16:37 | Structural Engineering - Concrete Member | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | On 06/10/2014 concrete used for some of the piles completed was placed after the requirement of 2hours after batching as required in specification (KF12.3221 (b)). A summary of the affected piles is given below: Pile 094 load 1 batched @ 17:12, placed @ 19:15, pile completed @ 19:50 Pile 094 load 2 batched @ 17:31, placed @ 19:35, pile completed @ 19:50 Pile 122 load 1 batched @ 17:31, placed @ 19:45, pile completed @ 19:45 Pile 118 load 1 batched @ 17:31, placed @ 19:50, pile completed @ 20:02 At no point did the time between batching of the first concrete load into any pile and completion of the concreting of any pile exceed 3 hours (see attached concrete record).
| 03SR - Stations (RfL) | Cxxx-NCR-001582 | NCR | C7 Piezometer Damage |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-11-19 | 2014-11-24 08:25 | 5 | 2014-10-19 09:43 | Surveying - Instrumentation and Monitoring | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | During excavation below concourse level, on 9th October 2014 the cables connecting the C7 piezometers and their transmitter were severed by the excavation plant. The instrument is located in an exclusion zone, therefore as of the time of writing it has not been possible to gain access to either inspect the instrument or undertake any repairs. The damage was reported and recorded on the SRG minutes when it occurred. The damage report and data plots showing when the instrument went offline are attached for reference. It is proposed to recover this instrument ASAP and take manual readings until the excavation is complete.
| 03SR - Stations (RfL) | Cxxx-NCR-001583 | NCR | C20-03 piezometer breakdown |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-12-31 | 2014-12-03 15:39 | -28 | 2014-10-19 09:42 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | On 14th October 2014, piezometer C20-03 sensor A (the bottom sensor at 66.1m ATD) stopped transmitting data. It is thought that this is due to the instrument itself breaking down. It is not an issue with the transmitter as this would have cause the other two sensors to stop transmitting data also. It is not possible to recover or repair this instrument. No damage report has been submitted as the instrument has not been damaged, it has broken down. The data plots showing when the instrument went offline are attached for reference.
| 03SR - Stations (RfL) | Cxxx-NCR-001584 | NCR | CN-13 Strain Gauges |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-11-27 | 2014-11-25 16:08 | -2 | 2014-10-19 09:53 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | On 12/10/14, it was noted that strain gauge CN-13B had gone offline and stopped transmitting data. Subsequent investigation has identified that the issue behind this is that the gauge itself has stopped working. It should be noted that as a concrete embedded gauge it is located in an aggressive environment, and it is to be expected that some of the concrete embedded gauges will be lost over time. The only way to "recover" the instrument would be to breakout the concrete in the area and fit a new gauge. After the instrument initially went offline, there is some unstable data reported for the instrument, between 16/10 and 18/10, as shown on the attached plot. This is caused by the transmitter still looking for data, as the gauge had not been set to faulty at this stage. The gauge CN-13B has now been set to faulty, and no more data will appear for it. It appears that Datum have also set CN13T to faulty at the same time, in error. This is a manual error and this will be corrected on Monday 20/10. It is possible that the gauge has gone down, and this is to be investigated, however it would be a remarkable coincidence if this was the case as both gauges have "gone off" at the exact same time.
| 03SR - Stations (RfL) | Cxxx-NCR-001585 | NCR | Clay inclusion S29, S28 at base slab level |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-05-05 | 2015-05-12 08:05 | 7 | 2014-10-20 16:47 | Structural Engineering - Diaphragm Walls | 15000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Material/Preservation Problems - Other | Completed |  | A significant clay inclusion was found at the bottom of the boxouts at base slab level in panels S28 and S29. S28 - two localised areas; S29 the full width of the panel (see photos) Both panels the clay inclusion extends around the vertical bars and below the blinding.
| 03SR - Stations (RfL) | Cxxx-NCR-001586 | NCR | IL11 - High concret flow test results |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-12-24 | 2014-12-03 14:57 | -21 | 2014-10-20 14:33 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | In IL11 slab concrete pour, a number of flow tests exceeded the allowable tolerance. In the Cxxx Civil and Structural Specifications KF11, In-Situ Concrete for buildings, Section KF11.2207, paragraph B) state that the permitted ranges of workability of fresh concrete shall be in accordance with BS EN 206 Table 3. The concrete mix design for IL11 (MCR: Cxxx-SKC-O-TSC-B071_WS077-50359 rev2.0) stated a target flow of 550mm. The conformity criteria for target values of consistency is specified in Table 11 of BS EN 206. Which, allow a tolerance of Plus/Minus 30mm. Thus, the flow range is 520 to 580mm. However, the mix design MCR disclose the allowable tolerance for a target flow as 490 to 620mm (550mm -60 +70) in accordance with BS 8500-1:2006. As a result, the flow test of a number of loads carried out on site exceeded the allowable tolerance of a target flow concrete mix by up to 40mm. (Please see attached concrete record)
| 03SR - Stations (RfL) | Cxxx-NCR-001587 | NCR | IL11 - Concrete Slump/flow |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-12-24 | 2014-12-11 09:18 | -13 | 2014-10-20 15:08 | Civil - Civil Engineering General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Concrete delivery tickets state concrete has a consistency target of 210mm slump in accordance with C40/50 300 10mm Mix design, MCR (Cxxx-SKC-O-TSC-B071_WS077-50359 Rev 1.0). However, Concrete was flow tested to 550mm target flow, in accordance to C40/50 300 10mm Mix design MCR (Cxxx-SKC-O-TSC-B071_WS077-50359 Rev 2.0).
| 03SR - Stations (RfL) | Cxxx-NCR-001588 | NCR | Light column base plate weld |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-04-06 | 2015-03-17 11:59 | -20 | 2014-10-21 11:37 | Civil - Structural Engineering | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | As per Cxxx-SKC-C-ITP-B071_WS077-50074 (REV1.0) item 3.1 - Steel base plate fabrication states 10% MPI on fillet welds. This was not completed during the fabrication of the base plates installed.
| 03SR - Stations (RfL) | Cxxx-NCR-001589 | NCR | Balustrade Bolts Out of Tolerance on GL 15 (Concourse Slab C11) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-12-16 | 2014-11-24 12:28 | -22 | 2014-10-21 13:28 | Architectural - Balustrade | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Several of the Balustrade cast in fixings on Concourse Level along GL 15 have been installed out of tolerance (See attached survey). This is due to the density of reinforcement in the area resulting in some fixings being installed marginly away from their design position.
| 03SR - Stations (RfL) | Cxxx-NCR-001590 | NCR | PC pile P16 - Lack of good quality concrete above COL |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-02-02 | 2015-02-02 09:15 | 0 | 2014-10-21 19:26 | Structural Engineering - Concrete Member | 5000 |  | Material | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | PC pile P16 has been exposed to 200mm above COL. Within the region exposed there does not apear to be sound concrete.
| 03SR - Stations (RfL) | Cxxx-NCR-001591 | NCR | IL12 - High concret flow test results |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-01-20 | 2014-12-01 09:48 | -50 | 2014-10-22 13:01 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Not Defined | Completed |  | In IL12 slab concrete pour, a number of flow tests exceeded the allowable tolerance. In the Cxxx Civil and Structural Specifications KF11, In-Situ Concrete for buildings, Section KF11.2207, paragraph B) state that the permitted ranges of workability of fresh concrete shall be in accordance with BS EN 206 Table 3. The concrete mix design for IL12 (MCR: Cxxx-SKC-O-TSC-B071_WS077-50359 rev2.0) stated a target flow of 550mm. The conformity criteria for target values of consistency is specified in Table 11 of BS EN 206. Which, allow a tolerance of Plus/Minus 30mm. Thus, the flow range is 520 to 580mm. However, the mix design MCR disclose the allowable tolerance for a target flow as 490 to 620mm (550mm -60 +70) in accordance with BS 8500-1:2006. As a result, the flow test of a number of loads carried out on site exceeded the allowable tolerance of a target flow concrete mix by up to 40mm. (Please see attached concrete record)
| 03SR - Stations (RfL) | Cxxx-NCR-001592 | NCR | Intermediate Walls L53 and L18 – Water addition procedure not followed (__F-NCR-179) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-02-13 | 2015-02-02 13:43 | -11 | 2014-10-22 16:39 | Civil - Civil Engineering General | 2500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Water addition procedure not followed for : 1. notifications and approvals prior to water addition 2. Slump recorded at arrival time on site but not re-recorded for loads with water addition. 3. Unable to verify water addition quantity in in-line with water addition procedure 4. Addional set of 4 cubes not taken for loads with water added L53 GL 19-20 (30/09/14) . Ticket No. 370153 : 90l water added L18 GL 16.5-17 (30/09/14) Ticket No. 370153 : 90l water added L53 GL 18-18.5 (4/10/12) Ticket No. 370386 : 30l water added (Cube set 1212) Ticket No 370395 : 20l water added L53 GL 21-22 (6/10/14) Ticket No.370426: 50l water added
| 03SR - Stations (RfL) | Cxxx-NCR-001593 | NCR | C20-03 piezometer lost |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-11-26 | 2014-11-14 16:43 | -12 | 2014-10-22 18:04 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | On 14/10/14, all there sensors in piezometer C20-03 went offline due to a loss in signal. Sensors B&C immediately recovered, whereas sensor A (the deepest sensor) has not yet returned (1 week later). Sensor A is the deepest sensor, located at 66.1mATD. will continue to monitor however it appears that the instrument itself has gone offline and will not be recovered. A data plot is attached showing the date at which the instrument went offline.
| 03SR - Stations (RfL) | Cxxx-NCR-001594 | NCR | PC35 Strain Gauge C |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-11-05 | 2014-10-29 17:28 | -7 | 2014-10-22 18:14 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | At the SRG on Friday 17th October, it was observed that there was an unexplained load fluctuation of PC35, combination C/F. A review of gauges (by taking manual readings) was instigated, and it was found that PC35 gauge C was operating at the very bottom of its Hz range, occasionally dropping out of range, thereby not providing reliable data. PC35 C has now been set to faulty on the Contractor's Database. Remaining working strain gauge combinations on this PC are G/H and E, which are used to compare against triggers. Gauge F is reviewed as a standalone gauge to monitor changes in strain, to supplement the remaining load combinations. Attached to this NCR are data plots showing the unstable load data (PC35CF 171014) and strain plots showing gauge C to be unstable.
| 03SR - Stations (RfL) | Cxxx-NCR-001595 | NCR | CN-13 Strain Gauges |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-11-26 | 2014-10-30 10:02 | -27 | 2014-10-22 18:20 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | At the SRG on 15/10/14, it was observed that strain gauge CN-13B was displaying unstable data. This data was not mirrored by the top gauge. A subsequent review, taking manual readings, revealed that CN-13B was operating at the bottom of its range, and CN-13T was actually not reading at all. It can be seen on closer inspection that CN-13T is flat lining, thereby indicating that there is no data being returned. Both gauges have now been set to faulty. It is not known specifically what has happened to the gauges, as they are embedded in concrete and therefore cannot be accessed. Similarly, it will not be possible to recover/replace the gauges without breaking out the concrete around them. Attached is the data plot showing when both gauges went off line.
| 03SR - Stations (RfL) | Cxxx-NCR-001596 | NCR | Clay Inclusions above tunnels |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-07-17 | 2015-06-25 09:39 | -22 | 2014-10-28 10:35 | Structural Engineering - Diaphragm Walls | 5000 |  | Material | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A significant quantity of concrete has been found beneath the toe of D-Wall panels W4 and N1. In addition to this clay inclusions have been found in the base of the panel, in cases exposing the toe of the rebar cage. (see attached photographs).
| 03SR - Stations (RfL) | Cxxx-NCR-001597 | NCR | Inconsistent Concrete Consistence at Plunge Column/Tension Pile Cut Off Level - P19 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-02-17 | 2015-02-02 09:18 | -15 | 2014-10-24 13:24 | Civil - Structural Engineering | 1250000 |  | Material | Rework | 1 (>60k) | Complete | Material/Preservation Problems - Other | Completed |  | During breakdown to cut-off level on plunge column/tension piles 19-21, the material encountered is inconsistent - particularly in the centre of the pile. An initial visual inspection would suggest there is an area of the pile with no aggregate present which appears to continue below the pile cut-off level. A sample was brought back for further visual inspection on 23/10/14.
| 03SR - Stations (RfL) | Cxxx-NCR-001598 | NCR | PC36 strain gauge broken down |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-11-10 | 2014-11-03 16:56 | -7 | 2014-10-27 15:10 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In the SRG meeting on 24/10, it was observed that the load plots for PC36 on combination A/C/D/F (flanges) was showing an unusual reading, hinting that one of the gauges had gone down. This was identified as being gauge C from the attached strain plot, which was verified by taking manual readings. The load plot is also attached for information. Datum have been asked to set gauge C to faulty to remove it from the calculation. The remaining gauges on the flanges A/D/F is not a valid combination (following the methodology agreed with Cxxx). Therefore this combination is to be removed from the database, and replaced with A/D. Gauge F will be used as a standalone gauge to verify increase in load by comparison with strain plots. G/H combination (the additional gauges) is also still working on this plunge column.
| 03SR - Stations (RfL) | Cxxx-NCR-001599 | NCR | Concourse Slab C1 Soffit Damage |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-04-30 | 2016-04-11 16:36 | -19 | 2014-10-29 10:01 | Civil - Civil Engineering General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A section of concrete approx. 500mm long has been broken off the underside of the soffit to C1 GL D/2-3 at the Tunnel Ventilation Fan Opening during removal of the blinding for the excavation works below concourse slab.
| 03SR - Stations (RfL) | Cxxx-NCR-001600 | NCR | BLL cage detail at corner of square links |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-11-26 | 2014-10-30 17:13 | -27 | 2014-10-29 10:51 | Structural Engineering - Reinforcement | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Drawing No. Cxxx-SKC-S-DWG-B071_WS077-50182 gives the reinforcement layout for the piles in the Bakerloo Line Link. At the top of the cage the main reinforcement transitions from a circular layout to a square layout and has a pair of B16 links. The original intention was to have the main B40 vertical bars of the reinforcing cages positioned in the corners of these square links. Following a visit to the reinforcement suppliers yard before the piling works had commenced it became evident that a number of the cages did not have the vertical B40 bars in the corner of the square shaped links. The fabricator was subsequently instructed to retrofit the cages with packers inbetween the main vertical B40 bars and the corners of the square links. A number of the cages that arrived on site for inclusion in the permanent works did not contain acceptable packing arrangements where required. The affected cages from deliveries 9 - 18 are: 19, 73 - 143
| 03SR - Stations (RfL) | Cxxx-NCR-001601 | NCR | Concrete batching to placement time exceeding 3 hours |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-11-27 | 2014-10-30 17:14 | -28 | 2014-10-30 09:03 | Structural Engineering - Concrete Member | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | On 24/10/2014 the first load of concrete poured in to pile 23 exceeded the 2 hour batching to placement time as stated in specification KF12.3221 (b) and the extended 3 hour batching to placement time covered by Cxxx-FCD-482 for this concrete mix. The concrete was batched at 08:54 but the pour for this pile did not commence until 11:50 and was completed at 12:06.
| 03SR - Stations (RfL) | Cxxx-NCR-001602 | NCR | C12 piezometer damage |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-01-23 | 2014-12-22 16:57 | -32 | 2014-10-30 13:36 | Surveying - Instrumentation and Monitoring | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On 29/10/14, during breaking of the Bakerloo Line Link piling mat, the cables for piezometers C12-02 and C12-14 were severed. C12-08 was severed during the excavation below concourse and has not to date been recovered. At this stage the piezometers are still located within an exclusion zone so it is not possible to access the instruments to make a more accurate assessment of the damage. The piezometers were last read on 27/10/14. It is currently proposed to cast the blinding over the instruments on 3/4 November, at which point the instrument will be decommissioned in any case. While efforts will be made to recover the instrument, where possible, it is considered that there is limited value in delaying the blinding to achieve this. In the event that the instruments cannot be recovered, the readings taken on 27/10 will be used as the final readings. The data plots showing when the instruments went offline are attached for reference. Note the instruments have been read manually of late so there is no "dropping off the chart" effect.
| 03SR - Stations (RfL) | Cxxx-NCR-001603 | NCR | Inconsistent Concrete Consistence at Plunge Column/Tension Pile Cut Off Level - P17-18 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-01-30 | 2015-01-30 15:26 | 0 | 2014-10-30 18:23 | Civil - Civil Engineering General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Further to NCR-001597, during breakdown to cut-off level on plunge column/tension piles 17-18, the material encountered is inconsistent - particularly in the centre of the pile. An initial visual inspection would suggest there is an area of the pile with no aggregate present which appears to continue below the pile cut-off level. Coring of these piles to ascertain the extent of the inconsitent material is ongoing as per the response to NCR-001597 and subsequent discussions.
| 03SR - Stations (RfL) | Cxxx-NCR-001604 | NCR | BLL Concrete batching to placement time exceeded 2hrs 14/10/2014 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-11-28 | 2014-11-05 08:54 | -23 | 2014-10-31 08:15 | Structural Engineering - Concrete Member | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | On 14/10/2014 concrete used for some of the piles completed was placed after the requirement of 2hours after batching as required in specification (KF12.3221 (b)). A summary of the affected piles is given below: Pile 042 load 1 batched @ 17:09, placed @ 19:12, pile completed @ 19:12 Pile 038 load 1 batched @ 17:09, placed @ 19:17, pile completed @ 19:27 Pile 024 load 2 batched @ 18:01, placed @ 20:10, pile completed @ 20:10 (load 1 batched at 17:37) At no point did the time between batching of the first concrete load into any pile and completion of the concreting of any pile exceed 3 hours (see attached concrete record).
| 03SR - Stations (RfL) | Cxxx-NCR-001605 | NCR | C20 piezometers damaged |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-11-17 | 2014-11-14 16:44 | -3 | 2014-11-03 09:25 | Surveying - Instrumentation and Monitoring | 1500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | On 30/31 October, during excavation East of MH4, the signal was lost to piezometers C20-03 and C20-09. It is most likely that these were severed by excavation plant. This will be confirmed upon further investigation and submission of the damage report. The pressures had begun to drop when the signal was lost, which is further indication that excavation was progressing in the area when the piezometers went off. The surveyors are marking out the positions of the piezometers today (3/11) with a view to recovering the instruments. Data plots are attached with details of when the instrument went offline.
| 03SR - Stations (RfL) | Cxxx-NCR-001606 | NCR | BLL Concrete batching to placement time exceeded 2hrs 18/10/2014 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-12-01 | 2014-11-05 08:58 | -26 | 2014-11-03 18:14 | Structural Engineering - Concrete Member | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | On 14/10/2014 concrete used for one of the piles completed was placed after the requirement of 2 hours after batching as required in specification (KF12.3221 (b)). A summary of the affected piles is given below: Pile 26, Pour 1, batched @ 12:17, pour complete @ 14:58 Pile 26, Pour 2, batched @ 12:50, pour complete @ 15:15, pile complete @ 15:15 At no point did the time between batching of the first concrete load into any pile and completion of the concreting of any pile exceed 3 hours (see attached concrete record).
| 03SR - Stations (RfL) | Cxxx-NCR-001607 | NCR | BLL Concrete batching to placement time exceeded 2hrs 22 & 24/10/2014 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-12-01 | 2014-11-05 09:04 | -26 | 2014-11-03 18:04 | Structural Engineering - Concrete Member | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The concrete used for some of the piles completed was placed after the requirement of 2hours after batching as required in specification (KF12.3221 (b)). A summary of the affected piles is given below: Date 22/10/2014, Pile 54, Pour 1, Batched @ 18:02, Pour complete @ 20:25, Pile complete @ 20:25 Date 24/10/2014, Pile 6, Pour 2, Batched @ 08:54, Pour complete @ 11:40, Pile complete @ 11:40 (Pour 1 batched @ 08:45). At no point did the time between batching of the first concrete load into any pile and completion of the concreting of any pile exceed 3 hours (see attached concrete records).
| 03SR - Stations (RfL) | Cxxx-NCR-001608 | NCR | Inconsistent Concrete Consistence at Plunge Column/Tension Pile Cut Off Level - P10 & P22 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-01-30 | 2015-01-30 15:33 | 0 | 2014-11-11 17:31 | Civil - Civil Engineering General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Further to NCR-001597 & NCR-1603, during breakdown to cut-off level on plunge column/tension piles 10 & 22, the material encountered is inconsistent - particularly in the centre of the pile. An initial visual inspection would suggest there is an area of the pile with no aggregate present which appears to continue below the pile cut-off level. Coring of these piles to ascertain the extent of the inconsitent material is ongoing as per the response to NCR-001597 and subsequent discussions.
| 03SR - Stations (RfL) | Cxxx-NCR-001609 | NCR | Damage to Precast Units – Dig below Concourse Slab |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-06-30 | 2016-05-26 14:03 | -35 | 2014-11-14 09:23 | Civil - Civil Engineering General | 30000 |  | Damaged | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | P1: GL 6 North: Small Chip P2: GL15 South: Small Chip P3: GL18.5 South: Small Chip P4: GL 18-18.5 South: Small Chip P5: GL 18-18.5 South: Small Chip P6: GL 18 South: Large chip and gouge
| 03SR - Stations (RfL) | Cxxx-NCR-001610 | NCR | Inconsistent Concrete Consistence at Plunge Column/Tension Pile Cut Off Level - P6, P12 & P31 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-01-30 | 2015-01-30 15:35 | 0 | 2014-11-14 15:14 | Civil - Civil Engineering General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Further to NCR-001597, NCR-001603 & NCR-001608, during breakdown to cut-off level on plunge column/tension piles 6, 12 & 31, the material encountered is inconsistent. An initial visual inspection would suggest there is an area of the pile with no aggregate present which appears to continue below the pile cut-off level. Coring of these piles to ascertain the extent of the inconsitent material is ongoing as per the response to NCR-001597 and subsequent discussions.
| 03SR - Stations (RfL) | Cxxx-NCR-001611 | NCR | Inconsistent Concrete Consistence at Plunge Column/Tension Pile Cut Off Level - P9 & P35 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-01-30 | 2015-01-30 15:38 | 0 | 2014-11-18 08:51 | Civil - Civil Engineering General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Further to NCR-001597, NCR-001603, NCR-001608 & NCR-001610, during breakdown to cut-off level on plunge column/tension piles 9 & 35, the material encountered is inconsistent. An initial visual inspection would suggest there is an area of the pile with no aggregate present which appears to continue below the pile cut-off level. Coring of these piles to ascertain the extent of the inconsitent material is ongoing as per the response to NCR-001597 and subsequent discussions.
| 03SR - Stations (RfL) | Cxxx-NCR-001612 | NCR | Traceability of BLL pile reinforcement |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-03-31 | 2015-03-31 15:57 | 0 | 2014-11-24 09:36 | Materials - General | 1500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Other | Completed |  | following surveillance report Cxxx-SKC-O-RGN-B071_WS077-50235 it has been identified that full traceability of the steel reinforcement of the BLL piles can not be ascertained due to a small number of exit check sheets and delivery note reference numbers not fully corresponding. Given that the majority of reference numbers are fully corresponding it would suggest that this is an administration error. The contractor is investigating the issue with the supplier and will propose a solution in due course.
| 03SR - Stations (RfL) | Cxxx-NCR-001614 | NCR | Inconsistent Concrete Consistence at Plunge Column/Tension Pile Cut Off Level - P38 & P42 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-01-30 | 2015-01-30 15:41 | 0 | 2014-11-24 12:37 | Civil - Civil Engineering General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Further to NCR-001597, NCR-001603, NCR-001608, NCR-001610 & NCR-001611, during breakdown to cut-off level on plunge column/tension piles 38 & 42, the material encountered is inconsistent. An initial visual inspection would suggest there is an area of the pile with no aggregate present which appears to continue below the pile cut-off level. Coring of these piles to ascertain the extent of the inconsitent material is ongoing as per the response to NCR-001597 and subsequent discussions.
| 03SR - Stations (RfL) | Cxxx-NCR-001615 | NCR | N55-N56 joint – non compliant concrete, intermediate/roof slab level |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-05-30 | 2015-05-26 13:53 | -4 | 2014-11-24 14:08 | Structural Engineering - Diaphragm Walls | 5000 |  | Material | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | Non compliant material has been identified on the joint of N55-N56. This defect is below a previous repair recorded from roof slab level in Cxxx-NCR-001120. Please see attached PDF for further information and photos.
| 03SR - Stations (RfL) | Cxxx-NCR-001616 | NCR | Damaged couplers. BLL piles during concrete break down |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2015-03-03 | 2015-03-06 16:31 | 3 | 2014-11-25 15:55 | Civil - Civil Engineering General | 5000 |  | Damaged | Rework | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | During the BLL piles concrete breakdown, several couplers have been damaged. Piles 62, 63, 71, 85, 103, 108 and 119 have been identified with damaged/bent couplers. As per Clause KF 12.3236, "No item of reinforcement shall be bent, or otherwise disturbed, after any part of it is embedded in concrete." This is just a sample of piles and the concrete breaking activity is not completed yet. The Contractor will need to carry out further investigation.
| 03SR - Stations (RfL) | Cxxx-NCR-001617 | NCR | N78 Intermediate level - Horizontal sand inclusion |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-02-03 | 2015-01-29 11:02 | -5 | 2014-11-24 14:33 | Structural Engineering - Diaphragm Walls | 5000 |  | Material | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | A horizontal sand inclusion has been identified on the intermediate level of panel N78. From an initial investigation the inclusion does not extend more than 50mm behind near face rebar. Please see attached PDF for further information.
| 03SR - Stations (RfL) | Cxxx-NCR-001618 | NCR | Damage to reinforcement bars in BLL Pile P6 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-03-03 | 2015-03-06 16:32 | 3 | 2014-11-24 16:16 | Structural Engineering - Reinforcement | 1500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Since installing the Bakerloo link pile P6 the projecting reinforcement bars have been damaged by way of bending (Please see attached photographs).
| 03SR - Stations (RfL) | Cxxx-NCR-001619 | NCR | N78 – Out of position rebar cage |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-01-14 | 2015-12-18 15:57 | -27 | 2014-11-24 18:08 | Structural Engineering - Diaphragm Walls | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Along the right hand side of panel N78 the link bars of the rebar cage are touching the adjacent panel N79. This was found whilst investigating sand inclusions along the right side edge which were part of the diaphragm wall snags. There is also a horizontal sand inclusion which has been covered in a separate NCR, Cxxx-NCR-001617. Please see attached PDF for further information and photos
| 03SR - Stations (RfL) | Cxxx-NCR-001620 | NCR | Out of tolerance Dwall at sub-platform level |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2015-07-30 | 2015-07-09 11:26 | -21 | 2014-11-26 15:20 | Structural Engineering - Diaphragm Walls | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Followed the completion of the excavation work below concourse level, it was noted that the location and verticality of several numbers of Dwall appeared to be out of tolerance. This could have significant impact on the subsequent activities, other Crossrail Contracts (eg system wide), and railway alignment / operation. An EWN was previously raised to highlight the potential out of tolerance Dwall panels at the sub-platform level. (EWN-00981).
| 03SR - Stations (RfL) | Cxxx-NCR-001622 | NCR | Inconsistent Concrete Consistence at Plunge Column/Tension Pile Cut Off Level - P14, P15 & P16 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-01-26 | 2015-01-30 15:45 | 4 | 2014-11-27 10:33 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Further to NCR-001597, NCR-001603, NCR-001608, NCR-001610, NCR-001611 & NCR-001614, during breakdown to cut-off level on plunge column/tension piles 14, 15 & 16, the material encountered is inconsistent. An initial visual inspection would suggest there is an area of the pile with no aggregate present which appears to continue below the pile cut-off level. Coring of these piles to ascertain the extent of the inconsitent material is ongoing as per the response to NCR-001597 and subsequent discussions.
| 03SR - Stations (RfL) | Cxxx-NCR-001623 | NCR | Out of tolerance Diaphragm wall S5 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-11-05 | 2015-11-04 17:16 | -1 | 2014-11-28 16:00 | Structural Engineering - Diaphragm Walls | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Survey and inspection of diaphragm wall S5 has shown the wall to be out of tolerance from concourse to intermediate. Please see attached alignment and cover survey. Over one section the minimun cavity wall distance of 125mm cannot be achieved without reducing the diaphragm wall cover to below 50mm. The diaphragm wall protrudes 17.5mm into the 125mm cavity area within a 1mx1m section of the panel.
| 03SR - Stations (RfL) | Cxxx-NCR-001624 | NCR | Exposed couplers in Diaphragm wall at District and circle line. |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-05-05 | 2015-04-01 09:23 | -34 | 2014-11-28 16:55 | Structural Engineering - Diaphragm Walls | 3500 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | On grid line 24 at intermediate level the diaphragm lining wall has been omitted to allow for a possible future district and circle line link. (Cxxx-SWN-S-DDA-M171_3-01570) Diaphragm walls panels N81 and E4 have been installed with liner wall connection couplers and these are currently exposed. (see attached photos) The lining wall intent drawing (Cxxx-SWN-S-DDD-M171_Z-55560) shows a continous liner wall over this area of the diaphragm wall.
| 03SR - Stations (RfL) | Cxxx-NCR-001625 | NCR | Intermediate Slab – Fibres in Cavity Drainage Infill concrete (NCR-186) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-01-17 | 2015-01-13 08:25 | -4 | 2014-11-28 15:44 | Civil - Civil Engineering General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | Intermediate Slab - Cavity Drainage Channel GL A/1-7 Fibres were found in the mix which were not expected. Ordered RC40/50 101 (line ref 101). Ticket number C538972. See photos attached
| 03SR - Stations (RfL) | Cxxx-NCR-001626 | NCR | Out of tolerance Diaphragm wall S19 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-11-26 | 2015-11-17 11:44 | -9 | 2014-11-28 16:15 | Structural Engineering - Diaphragm Walls | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Survey and inspection of diaphragm wall S19 has shown the wall to be out of tolerance over an area from concourse to intermediate. Please see attached alignment and cover survey. Over one section the minimun cavity wall distance of 125mm cannot be achieved without resulting in the diaphragm wall cover being compromised. Low cover areas over the panel will once remediated result at worst case the cavity channel being reduced from 125mm to 105mm. over a section of the panel between concourse and intermediate levels
| 03SR - Stations (RfL) | Cxxx-NCR-001627 | NCR | Out of tolerance Diaphragm wall N17 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-11-26 | 2015-11-12 12:31 | -14 | 2014-11-28 16:23 | Structural Engineering - Diaphragm Walls | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Survey and inspection of diaphragm wall S5 has shown the wall to be out of tolerance over a section of the panel between concourse to intermediate. Please see attached alignment and cover survey. Over one section the minimun cavity wall distance of 125mm cannot be achieved without reducing the diaphragm wall cover to below 50mm. The cavity zone will be at worst case reduced from 125mm to 105mm over a secton of the RHS of the panel.
| 03SR - Stations (RfL) | Cxxx-NCR-001628 | NCR | Ballustrade Bolts Out of Tolerance GL 12 Concourse Level |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-12-29 | 2014-12-04 09:42 | -25 | 2014-12-01 10:29 | Architectural - Balustrade | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Several of the Balustrade cast in bolts on Concourse Level around the lift pit on GL 12 have been installed out of tolerance (See attached survey). This is due to the density of reinforcement in the area resulting in some fixings being installed marginly away from their design position.
| 03SR - Stations (RfL) | Cxxx-NCR-001629 | NCR | Sonic Logging Tubes within Tension Piles W/O grout at Base Slab Level in P17, P18, P21 & P22. |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-03-31 | 2015-03-10 14:40 | -21 | 2014-12-01 17:11 | Structural Engineering - Concrete Member | 2500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | At Base Slab Level there are 4No. Tension Piles which have Sonic Logging Tubes without grout in them at this level. P22 has 3No. Sonic Logging Tubes without grout, the north, south and west tubes. P21 has 4No. Sonic Logging Tubes without grout. P18 has 4No. Sonic Logging Tubes without grout. P17 has 3No. Sonic Logging Tubes without grout, the north, south and west tubes.
| 03SR - Stations (RfL) | Cxxx-NCR-001630 | NCR | Concrete on Couplers of Tension Pile Reinforcement P15 P16, P17, P19, P20, P22, P23 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-04-22 | 2015-04-18 13:03 | -4 | 2014-12-01 17:10 | Structural Engineering - Reinforcement | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Some of the couplers at Base Slab Level have concrete on them to an extent which may affect the ability of the couplers to be threaded. This is due to either gaps in the debonding foam, damage to protective cap, of lack of the measures to prevent concrete reaching the couplers during concreting of the Tension Piles. Details as below: P15 3No. Couplers P16 1No. Coupler P17 4No. Couplers P19 4No. Couplers P20 5No. Couplers P22 6No. Couplers P23 4No. Couplers
| 03SR - Stations (RfL) | Cxxx-NCR-001632 | NCR | Bakerloo Line Link: Damage to inclinometer tubes |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-03-27 | 2015-03-18 17:05 | -9 | 2014-12-02 15:30 | Surveying - Instrumentation and Monitoring | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During the breakdown of contiguous piles around the Bakerloo Line Link box, inclinometer tubes cast into the piles were damaged by concrete breaking plant. Whereas with previous inclinometers it has been possible to cut down the tube and install an artificial joint to the new piece of tube, owing to the type of tube that has been installed in this case, it is only possible to install the a new section at a joint. The tubes come in 3.0m lengths, and the nearest joint is approximately 2m below blinding level. The reason why another section of tube is required to be attached is to take the instrument above the level of the capping beam, which is yet to be cast. It is proposed to cut down the tubes as they are, and attached the new tube using a coupler from a different inclinometer system. This will hinge on the ability to line up the grooves on the inside of the tubes, into which the IPIs will slide. Note that this methodology is not guaranteed to work, and it will not be possible to evaluate whether the approach has been successful until the IPI is installed. There is a lead time of 6 weeks on the IPIs, hence the long close out time requested for this NCR. In the meantime, it is proposed to read the instruments using a manual inclinometer in the short term, until construction of the capping beam makes this impractical. Photos of the damaged tube are attached for reference.
| 03SR - Stations (RfL) | Cxxx-NCR-001633 | NCR | Roof Level – Bent starter bars ETL- T-24 (__F-NCR-187) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-04-02 | 2014-12-15 14:30 | -108 | 2014-12-03 09:09 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 8 N0. B12 starter bars (4 each face at 150crs.) to the south end of wall T-24 have been bent erecting the north side shutter to wall L-44. (please see attached photo)
| 03SR - Stations (RfL) | Cxxx-NCR-001634 | NCR | Missed reporting of amber alert for construction control |  | Contr | SKC | PAD - Paddington Station (West) |  | 2014-12-18 | 2014-12-22 16:52 | 4 | 2014-12-04 14:03 | Surveying - Instrumentation and Monitoring | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | As specified in Section 7.2 of Cxxx-OVE-C2-RGN-B071-50013 (I&M Plan for non-rail assets), amber construction alerts are provided to apportion the total movement from CRL works i.e. the amber triggers, to different construction activities. The purpose of the alert is to verify the appropriateness of construction controls in place, and upon breach should prompt a review of data at the SRG. For station box excavation, the amber construction alert was breached some time ago for 10/20/30/40 Eastbourne Terrace, and not reported to the SRG. The amber construction alert for these assets is 15mm. In practice, the monitoring data is reviewed daily at the SRG regardless of whether the amber construction alert is breached. However, while the actions prompted by the breach have been implemented, the non-reporting of the breach (of the amber construction alert) is a non-conformance.
| 03SR - Stations (RfL) | Cxxx-NCR-001635 | NCR | Intermediate Walls L27 and T34– Concrete Placement time exceeded (NCR-188) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-01-10 | 2014-12-19 16:47 | -22 | 2014-12-05 09:42 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Intermediate Walls L27(GL 22-23), T-34(GL 16/D-E) Pour date 09/10/14. Concrete delivery record shows 2hr limit from batching to discharge exceeded by for 1 loads. Ticket number 372102 by 15min,
| 03SR - Stations (RfL) | Cxxx-NCR-001636 | NCR | D'wall panel N60, Intermediate level - Exposed rebar from removal of loose material |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-04-04 | 2015-04-02 13:44 | -2 | 2014-12-08 13:16 | Structural Engineering - Diaphragm Walls | 2500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Along the right hand side of panel N60 loose material has been removed from the surface, exposing the rebar cage. Please see attached PDF for photographs.
| 03SR - Stations (RfL) | Cxxx-NCR-001637 | NCR | Intermediate Walls L27/T116/L53– Concrete Placement times exceeded (NCR-183) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-01-06 | 2014-12-19 16:49 | -18 | 2014-12-08 17:43 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Intermediate Walls L27/T116/L53, Pour date 23/10/14. Concrete delivery record shows 2hr limit from batching to discharge exceeded by for 3 loads. Ticket number 370690 by 1min, Ticket 370696 by 18 mins and Ticket number 370723 by 12 mins. 1hr limit for fresh concrete in touch with fresh concrete exceeded by 30mins between Ticket numbers 370696 and 370723.
| 03SR - Stations (RfL) | Cxxx-NCR-001638 | NCR | Inconsistent Concrete Consistence at Plunge Column/Tension Pile Cut Off Level - P11, P13, P33 & P46 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-02-07 | 2015-02-02 09:29 | -5 | 2014-12-09 09:20 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Further to NCR-001597, NCR-001603, NCR-001608, NCR-001610, NCR-001611, NCR-001614 & NCR-001622 during breakdown to cut-off level on plunge column/tension piles 11, 13, 33 & 46 the material encountered is inconsistent. An initial visual inspection would suggest there is an area of the pile with no aggregate present which appears to continue below the pile cut-off level. Coring of these piles to ascertain the extent of the inconsitent material is ongoing as per the response to NCR-001597 and subsequent discussions.
| 03SR - Stations (RfL) | Cxxx-NCR-001639 | NCR | No Quattro 10/20 shingle in place prior to works |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-04-03 | 2015-03-19 16:10 | -15 | 2014-12-09 09:40 | Civil - Drainage | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | No MCR in place for quattro 10/20 shingle prior to drainage works commencing
| 03SR - Stations (RfL) | Cxxx-NCR-001640 | NCR | No MCR in place for Quattro 6F2 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-04-03 | 2015-03-19 16:13 | -15 | 2014-12-09 09:45 | Civil - Drainage | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | No MCR was in place for Quattro 6F2 prior to drainage works commencing.
| 03SR - Stations (RfL) | Cxxx-NCR-001641 | NCR | No __ Concrete MCR in place |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-04-03 | 2015-03-19 16:17 | -15 | 2014-12-09 09:52 | Civil - Drainage | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | No __ - GEN3 and C32-40 AEA MCR in place prior to drainage works.
| 03SR - Stations (RfL) | Cxxx-NCR-001642 | NCR | No MCR in place for Quattro ST2, CBM3 and C32-40 AEA |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-04-03 | 2015-03-25 11:07 | -9 | 2014-12-09 10:35 | Civil - Drainage | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | No MCR in place for Quattro ST2, CBM3 and C32-40 AEA
| 03SR - Stations (RfL) | Cxxx-NCR-001643 | NCR | Concourse Slab – C08 Unpaid Lift Shaft Cast-in Items |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-02-03 | 2015-01-29 11:36 | -5 | 2014-12-09 15:28 | Structural Engineering - Bolted Connections | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | For the Unpaid Lift Cast in bolts on concourse level GL12: 1) 24 No. Stainless Steel Anchor Plates installed 100x100x16mm in lieu of 100x100x20mm as specified by the original design drawings. See photos attached. 2) Material specification was changed last minute to ’All bolts to be grade 8.8 with S355 anchor plates’. Insufficient time to procure revised material specification so pour proceeded with original materials.
| 03SR - Stations (RfL) | Cxxx-NCR-001644 | NCR | E__ slab GL 14 cracks |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-01-20 | 2016-11-25 15:52 | -56 | 2014-12-11 12:13 | Civil - Civil Engineering General | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | On a site inspection there were some visible cracks to the soffit of the E__ slab at GL 14, please see attached for clarity of location
| 03SR - Stations (RfL) | Cxxx-NCR-001645 | NCR | BLL 600dia Pile 1 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-10-29 | 2015-10-06 14:53 | -23 | 2015-05-18 18:19 | Structural Engineering - Reinforcement | 1500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | P1 has honeycombing present on the exposed surface, but is predominantly present between approximately 101.000mATD and 101.300mATD. Due to on-going excavation in the area, visual inspection was limited. Additional clay is to be removed.
| 03SR - Stations (RfL) | Cxxx-NCR-001646 | NCR | Sonic Logging Tubes within Tension Piles W/O grout at Base Slab Level in P41 & P43. |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-04-15 | 2015-04-07 11:03 | -8 | 2014-12-16 12:40 | Structural Engineering - Concrete Member | 1500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Further to Cxxx-NCR-001629 2No. more Tension Piles with Sonic Logging Tubes without grout have been exposed at base slab level. These are P41, the west tube and P43, the west tube.
| 03SR - Stations (RfL) | Cxxx-NCR-001647 | NCR | Eastbourne Terrace – Wall ETL-L-40 – Pull out bar not installed (__F-NCR-190) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-01-30 | 2015-01-08 11:25 | -22 | 2014-12-16 17:16 | Civil - Civil Engineering General | 1500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Eastbourne Terrace – Wall ETL-L-40 GL5 Pull out bar 300/10 detailed on drawing Cxxx-SKC-C-DWG-B071_WS077-50572 has not been installed.
| 03SR - Stations (RfL) | Cxxx-NCR-001648 | NCR | Inconsistent Concrete Consistence at Plunge Column/Tension Pile Cut Off Level - P41 & P34 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-02-15 | 2015-02-02 09:32 | -13 | 2014-12-17 07:41 | Civil - Civil Engineering General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Further to NCR-001597, NCR-001603, NCR-001608, NCR-001610, NCR-001611, NCR-001614, NCR-001622 & NCR-001638 during breakdown to cut-off level on plunge column/tension piles 11, 13, 33 & 46 the material encountered is inconsistent. An initial visual inspection would suggest there is an area of the pile with no aggregate present which appears to continue below the pile cut-off level. Coring of these piles to ascertain the extent of the inconsitent material is ongoing as per the response to NCR-001597 and subsequent discussions.
| 03SR - Stations (RfL) | Cxxx-NCR-001650 | NCR | No approved __ ducting MCR prior to construction |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-02-15 | 2015-02-11 16:39 | -4 | 2014-12-17 16:17 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | No approved __ ducting MCR prior to construction of Light columns on EBT.
| 03SR - Stations (RfL) | Cxxx-NCR-001651 | NCR | Concourse Walls T-27/L50 return/L35 return– Concrete Placement time exceeded (NCR-191) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-01-21 | 2014-12-19 16:51 | -33 | 2014-12-17 18:15 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | GL 23/D-E:Concourse Walls T-27/L50 return/L35 return Pour date 14/11/14. Concrete delivery record shows 2hr limit from batching to discharge exceeded by for ticket number 589219 by 14min. 1hr limit for fresh concrete in touch with fresh concrete exceeded by for 50mins between ticket numbers 589186 and 589201, 5mins between ticket numbers 589201 and 589209, and 45mins between ticket numbers 589209 and 589219.
| 03SR - Stations (RfL) | Cxxx-NCR-001652 | NCR | Calibration of manual inclinometer probes |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-01-21 | 2014-12-22 14:49 | -30 | 2014-12-18 14:13 | Surveying - Instrumentation and Monitoring | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | In surveillance report Cxxx--SKC-O-RGN-B071_WS077-50222, it was noted (Item 1.1.2) that the CES Instrument Register was showing that 2No. inclinometer probes were overdue calibration, with an NCR to be raised. It is thought that this referred to the __ probes which were off hired in March 2013. The probes currently in use are next due for calibration on the dates noted below: PR1302036: November 24, 2015 PR1302035: May 2, 2015 PR1306851: August 11, 2015. Note that probes are required to be calibrated once every 12 months. Attached are calibration certificates currently in use. Note that for PR1302035 and PR1302036, the calibration dates are written in American date format, i.e. MM-DD-YYYY.
| 03SR - Stations (RfL) | Cxxx-NCR-001653 | NCR | Roof Level Slab Area 2 and Concourse upstands : Concrete Placement time exceeded (NCR-192) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-02-02 | 2015-01-30 15:06 | -3 | 2014-12-19 09:07 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Improper resource allocation | Completed |  | Roof Level Slab Area 2 GL 19-20/D & Concourse upstands 20-22/A-B and 16-17/A-B Pour date 18/11/14. Concrete delivery record shows 2hr limit from batching to discharge exceeded by for ticket numbers 589363 by 17mins and 589367 for 1hr 28mins.
| 03SR - Stations (RfL) | Cxxx-NCR-001654 | NCR | Plunge Column defective strain gauge |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-01-29 | 2015-01-23 09:32 | -6 | 2015-01-05 10:45 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Over the Christmas shut down plunge column strain gauges 34a and 36d were noted to be giving anomalous readings. Further investigation has revealed that the gauges have dropped out of their operating frequency. Consequently the gauges can not be relied upon to provide reliable data. Gauges are to be set to faulty and load calculations amended on the Contractors data base. Data plots of the anomalous readings are attached for information.
| 03SR - Stations (RfL) | Cxxx-NCR-001655 | NCR | Plunge Column PC34 defective strain gauge |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-02-18 | 2015-01-22 16:02 | -27 | 2015-01-06 17:32 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Over the Christmas shut down plunge column strain gauge 34A noted to be giving anomalous readings. Further investigation has revealed that the gauge dropped out of operating frequency. Consequently the gauge can not be relied upon to provide reliable data. Gauge PC34A has been set to faulty and load calculations amended on the Contractors data base. The remaining gauges on the flanges C/D/F is not a valid combination (following the methodology agreed with Cxxx). Therefore this combination is to be removed from the database, and replaced with C/F. Data plots of the anomalous readings are attached for information.
| 03SR - Stations (RfL) | Cxxx-NCR-001656 | NCR | South East Tunnel - Crack in tunnel segment |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-12-22 | 2015-12-15 10:23 | -7 | 2015-01-12 12:46 | Tunnelling - Tunnelling General | 1500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | A small crack has been identified in a tunnel segment in the SE tunnel. The crack is located in a segment that we have saw cut, and extends from a grout hole on the cut line to the joint. See attached photographs and sketch showing the location of the crack.
| 03SR - Stations (RfL) | Cxxx-NCR-001657 | NCR | S48, S49 & S52 Clay Inclusions @ 102.560mATD |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-07-17 | 2015-06-23 11:21 | -24 | 2015-01-14 16:30 | Structural Engineering - Diaphragm Walls | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Clay inclusions have been found at 102.560mATD on panels S48-49 and S52, on all panels the inclusion goes around the vertical reinforcement, and below the blinding (See photos).
| 03SR - Stations (RfL) | Cxxx-NCR-001658 | NCR | Commencement of Procurement / fabrication of Escalators without accepted Quality Plan |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-03-12 | 2015-03-12 17:08 | 0 | 2015-01-16 16:27 | Mechanical - Escalators | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | The contractor has commenced manufacturing of component parts for Cxxx Escalators without; o Gate 3 Design Assurance signed off and subsequent instruction to proceed from o Code 1 Quality Plan and Manufacture ITP’s, contra the requirement of WI. Vol. 2B Part 20.2 o Planned QA/QC interventions with in attendance ie. the requirement of galvanised trusses?
| 03SR - Stations (RfL) | Cxxx-NCR-001659 | NCR | Sensor fault with IPI A12-09 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-02-09 | 2015-02-04 14:58 | -5 | 2015-01-19 13:03 | Surveying - Instrumentation and Monitoring | 1000 |  | Equipment Breakdown | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Monitoring results for In-place Inclinometer A12-09 have displayed a fault with one of the sensors. No results have been recorded for the inclinometer from 18/01/2015. This fault was previously observed between 26/12/2014 and 11/01/2015 with a temporary period of good monitoring results received until the latest fault on the 18/01/2015. IPI A12-09 is an in-ground inclinometer, located within Chilworth Street and between two D-wall IPI instruments at A10-11 and A13-13. The purpose of the inclinometer was to monitor ground displacements during the construction of the D-wall and is now superseded by the two D-wall inclinometers. Displacement within the IPI has shown negligible movement +/-1mm since the excavation to base slab level. See attached IPI trend plot and extract of IPI location.
| 03SR - Stations (RfL) | Cxxx-NCR-001660 | NCR | Cavity Drain Infill works – SI 930 – 100mm concrete infill |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-03-20 | 2015-03-18 17:08 | -2 | 2015-01-19 17:46 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Main Box – Intermediate Level GL24/D-E SCC concrete from the tension columns was used as the 100mm stage 1 concrete infill in the above location.(RC40/50 Agillia (MCR50031) in lieu of RC40/50INT).
| 03SR - Stations (RfL) | Cxxx-NCR-001661 | NCR | S08 Sub-Platform D-Wall Couplers out of tolerance |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-02-17 | 2015-02-19 14:15 | 2 | 2015-01-20 12:18 | Structural Engineering - Diaphragm Walls | 2500 |  | Design | Rework | 4 (0.5-3k) | Complete | Previous Construction - Problems based on previous construction errors | Completed |  | When preparing the Sub-Platform D-Wall couplers some panels were found to be out of tolerance (+ -50mm). Where low couplers were found clashes with the bottom reinforcement will occur. These bars will need to be redrilled. Furthermore due to difference in D-Wall and base slab tolerances some in-tolerance couplers will still clash with the bottom mat of reinforcement. For this reason any coupler 150mm or less from the top of blinding level (see attachment) needs to be redrilled. This NCR covers Pour S08 with the following Panels affected: S38 - 4 No. Couplers 56mm to 64mm low (D-Wall out of tolerance) 2No. bars redrilled (See attached record sheet) S40 - 7 No. Couplers 29mm to 39mm low (D-Wall in tolerance but clash still likely) 5No. bars redrilled (See attached record sheet)
| 03SR - Stations (RfL) | Cxxx-NCR-001663 | NCR | Missed Red Trigger (FALSE ALARM) for LU03 Retaining Wall CH110 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-02-06 | 2015-02-10 14:38 | 4 | 2015-01-23 13:07 | Surveying - Instrumentation and Monitoring | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | On Tuesday 20th January 2015 a red trigger breach (Cxxx-GR117173) was observed for the inclination of the LU03 eastern retaining wall at Ch110. The red trigger was first breached on 12/11/2014 as a one off spike with increasing more frequent red trigger breaches throughout November. From the 4th December 2014 the red trigger was permanently breached until the observation on 20/01/2015. See attached inclination graph. The inclination measurement Cxxx-GR117173 measures the differential movement between ATS prisms Cxxx-RP211071 and Cxxx-RP211073. The two prisms are fixed the LU03 retaining wall, vertically aligned with a vertical separation of 5.92m. The Red trigger is set at an inclination change of 0.45mm/m or change in slope of 1:2240. Monitoring of the individual prism movement was undertaken at frequent weekly intervals by Johnny Falder (previous Monitoring Manager). The plots for horizontal movement perpendicular and parallel to the LU track show negligible movement (+/- 2mm) and less than 20% of the green trigger value set at 13mm (see attached graphs). As negligible movement was observed across the individual prisms, a check of the relative movement was carried out by Cxxx. This manual check identified a calculation error within the presentation of the inclination on the Datum database. A review was carried out by and agreed with Cxxx. The result of this manual check found that the actual inclination change was only 0.18mm/m. This is well within the 0.29mm/mm green trigger value set out by Cxxx and LU. For this reason the red trigger breach has now been classed as a false alarm.
| 03SR - Stations (RfL) | Cxxx-NCR-001664 | NCR | S71 - Out of tolerance D' wall |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-02-25 | 2015-02-25 16:42 | 0 | 2015-01-26 15:13 | Structural Engineering - Diaphragm Walls | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Previous Construction - Interfacing issues | Completed |  | Diaphragm wall panel S71 is out of tolerance. This has reduced the cavity width to the liner wall below the 125mm tolerance.
| 03SR - Stations (RfL) | Cxxx-NCR-001665 | NCR | Sub-Platform S02 - Out of Tolerance Blinding |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-05-15 | 2015-04-15 10:07 | -30 | 2015-01-26 17:32 | Structural Engineering - Concrete Member | 2500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | GL 4.5/A-D Pour date 29/10/14 An area of localized heave has been identified on the sub-platform blinding in the S02 slab. The area identified was cast on the 29/10/14 and is up to +34mm high (tolerance +/-19mm). The adjacent area cast on 21/1/15 has been set 5-10mm low. See survey attached.
| 03SR - Stations (RfL) | Cxxx-NCR-001666 | NCR | BLL Piles P9 and P48 - Concrete Cube Strength taken on 12/10/2014 Batch ticket number 509323 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-02-12 | 2015-02-16 09:32 | 4 | 2015-01-29 11:05 | Civil - Civil Engineering General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Cubes taken on 12/10/2014 from the concrete load with ticket number 509323 have failed to reach 45N/mm2 at 28 days. The compression strength results from the two cubes crushed at 28 days were 44.7MPa and 43.0MPa. The concrete from this load was used in piles P9 & P48.
| 03SR - Stations (RfL) | Cxxx-NCR-001667 | NCR | Base slab S7: Inconsistent Concrete at Plunge Column/Tension Piles P21, P22, P23 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-03-31 | 2015-03-25 18:00 | -6 | 2015-01-29 12:34 | Civil - Civil Engineering General | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | During breakdown to cut-off level on plunge column/tension piles P21, P22, P23, the material encountered is inconsistent - particularly in the centre of the pile. An initial visual inspection would suggest there is an area of the pile with no aggregate present which appears to continue below the pile cut-off level. Please note this NCR supersedes NCR-001608. Please confirm Cxxx have no objection to these piles being incorporated into the permanent works.
| 03SR - Stations (RfL) | Cxxx-NCR-001668 | NCR | Base slab S6: Inconsistent Concrete at Plunge Column/Tension Piles P18, P19, P20 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-04-22 | 2015-04-18 11:49 | -4 | 2015-01-29 12:43 | Civil - Civil Engineering General | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | During breakdown to cut-off level on plunge column/tension piles P18, P19, P20 the material encountered is inconsistent - particularly in the centre of the pile. An initial visual inspection would suggest there is an area of the pile with no aggregate present which appears to continue below the pile cut-off level. Please note this NCR supersedes NCR-001597 and NCR-001603. Please confirm Cxxx have no objection to these piles being incorporated into the permanent works.
| 03SR - Stations (RfL) | Cxxx-NCR-001669 | NCR | Base slab S5: Inconsistent Concrete at Plunge Column/Tension Piles P15, P16, P17 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-05-24 | 2015-04-29 13:15 | -25 | 2015-01-29 12:51 | Civil - Civil Engineering General | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | During breakdown to cut-off level on plunge column/tension piles P21, P22, P23, the material encountered is inconsistent - particularly in the centre of the pile. An initial visual inspection would suggest there is an area of the pile with no aggregate present which appears to continue below the pile cut-off level. Please note this NCR supersedes NCR-001622, 1603 and NCR-001590. Please confirm Cxxx have no objection to these piles being incorporated into the permanent works.
| 03SR - Stations (RfL) | Cxxx-NCR-001670 | NCR | Base slab S4: Inconsistent Concrete at Plunge Column/Tension Piles P12, P13, P14 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-06-26 | 2015-06-17 17:19 | -9 | 2015-01-29 13:06 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During breakdown to cut-off level on plunge column/tension piles P12, P13, P14 the material encountered is inconsistent - particularly in the centre of the pile. An initial visual inspection would suggest there is an area of the pile with no aggregate present which appears to continue below the pile cut-off level. Please note this NCR supersedes NCR-001610, NCR-001622 and NCR-1638.
| 03SR - Stations (RfL) | Cxxx-NCR-001672 | NCR | Base slab S3: Inconsistent Concrete at Plunge Column/Tension Piles P9, P10, P11 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-05-27 | 2015-05-27 14:21 | 0 | 2015-01-29 13:18 | Civil - Civil Engineering General | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | During breakdown to cut-off level on plunge column/tension piles P9, P10, P11 the material encountered is inconsistent - particularly in the centre of the pile. An initial visual inspection would suggest there is an area of the pile with no aggregate present which appears to continue below the pile cut-off level. Please note this NCR supersedes NCR-001608, NCR-001611 and NCR-001638.
| 03SR - Stations (RfL) | Cxxx-NCR-001673 | NCR | Concrete protection to waterproofing does not comply with the specification |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2017-03-11 | 2017-01-25 11:53 | -45 | 2015-01-29 15:18 | Civil - Streets & Highways | 10000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Material/Preservation Problems - Other | Completed |  | The Waterproofing to the E__ slabs should have a 100mm fibre reinforced concrete protection layer applied, as per specification CR-STD-303 (3.4.5), material Compliance record Cxxx-SKC-O-TSC-B071_WS077-50194 and associated concession. During the construction of Eastbourne Terrace it was suspected that an area of the E__ slabs had been protected with concrete that was not Fibre Reinforced/non compliant. A Supervisors Instruction was raised to investigate another suspected defect in the same area and the were asked to take a core of the concrete used and to test to determine if the protective concrete was in fact fibre reinforced. Report Cxxx-SKC-O4-RGN-B071_WS077-50031 was received by Crossrail on the 29th/1st/2015, page 5 confirms that the concrete used is non compliant and not fibre reinforced.
| 03SR - Stations (RfL) | Cxxx-NCR-001674 | NCR | Base slab S2: Inconsistent Concrete at Plunge Column/Tension Piles P4, P5, P6 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-06-05 | 2015-05-29 16:52 | -7 | 2015-01-29 17:17 | Civil - Civil Engineering General | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | During breakdown to cut-off level on plunge column/tension piles P6 the material encountered is inconsistent - particularly in the centre of the pile. An initial visual inspection would suggest there is an area of the pile with no aggregate present which appears to continue below the pile cut-off level. Please note this NCR supersedes NCR-001610. Please confirm Cxxx have no objection to these piles being incorporated into the permanent works. 29/01/15 Piles P4 and P5 are still to be broken to cut off level. 29/04/15 Following pile breakdown to DCOL: P4 - breaking not required P5 - inconsistent material identified; breaking required
| 03SR - Stations (RfL) | Cxxx-NCR-001675 | NCR | Base slab S10: Inconsistent Concrete at Plunge Column/Tension Piles P31, P32 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-05-01 | 2015-04-18 12:08 | -13 | 2015-01-29 17:42 | Civil - Civil Engineering General | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | During breakdown to cut-off level on plunge column/tension piles P31, P32 the material encountered is inconsistent - particularly in the centre of the pile. An initial visual inspection would suggest there is an area of the pile with no aggregate present which appears to continue below the pile cut-off level. Please note this NCR supersedes NCR-001610. Please confirm Cxxx have no objection to these piles being incorporated into the permanent works.
| 03SR - Stations (RfL) | Cxxx-NCR-001676 | NCR | Base slab S11: Inconsistent Concrete at Plunge Column/Tension Piles P33, P34, P35 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-06-01 | 2015-04-29 10:44 | -33 | 2015-01-29 17:52 | Civil - Civil Engineering General | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | During breakdown to cut-off level on plunge column/tension piles P33, P34, P35 the material encountered is inconsistent - particularly in the centre of the pile. An initial visual inspection would suggest there is an area of the pile with no aggregate present which appears to continue below the pile cut-off level. Please note this NCR supersedes NCR-001611, NCR-001638 and NCR-001648 Please confirm Cxxx have no objection to these piles being incorporated into the permanent works.
| 03SR - Stations (RfL) | Cxxx-NCR-001677 | NCR | Base slab S12: Inconsistent Concrete at Plunge Column/Tension Piles P36, P37, P38 and P39 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-06-17 | 2015-05-15 08:52 | -33 | 2015-01-29 17:57 | Civil - Civil Engineering General | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | During breakdown to cut-off level on plunge column/tension piles P36, P37, P38 and P39 the material encountered is inconsistent - particularly in the centre of the pile. An initial visual inspection would suggest there is an area of the pile with no aggregate present which appears to continue below the pile cut-off level. Please note this NCR supersedes NCR-001614. Please confirm Cxxx have no objection to these piles being incorporated into the permanent works.
| 03SR - Stations (RfL) | Cxxx-NCR-001678 | NCR | Base slab S13: Inconsistent Concrete at Plunge Column/Tension Piles P40, P41, P42, P43 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-06-16 | 2015-06-16 13:52 | 0 | 2015-01-29 18:01 | Civil - Civil Engineering General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | During breakdown to cut-off level on plunge column/tension piles P40, P41, P42, P43 the material encountered is inconsistent - particularly in the centre of the pile. An initial visual inspection would suggest there is an area of the pile with no aggregate present which appears to continue below the pile cut-off level. Please note this NCR supersedes NCR-001648 and NCR-001614.
| 03SR - Stations (RfL) | Cxxx-NCR-001679 | NCR | Base slab S14: Inconsistent Concrete at Plunge Column/Tension Piles P46, P47, P48 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-06-30 | 2015-06-16 14:04 | -14 | 2015-01-29 18:08 | Civil - Civil Engineering General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During breakdown to cut-off level on plunge column/tension piles P46 the material encountered is inconsistent - particularly in the centre of the pile. An initial visual inspection would suggest there is an area of the pile with no aggregate present which appears to continue below the pile cut-off level. Please note this NCR supersedes NCR-001638. 29/01/15 Piles P47 and P48 are still to be broken down 19/05/15 P47 material identified as mortar; Sandy rich material found in core P47E (NCR-1750); P48 no grout found, large clay pockets at 450mm (NCR-1746)
| 03SR - Stations (RfL) | Cxxx-NCR-001680 | NCR | S08 Bakerloo Link Piles |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-02-20 | 2015-02-16 10:54 | -4 | 2015-02-04 09:08 | Structural Engineering - Reinforcement | 2500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Please refer NCR-1616 Some of the Bakerloo Link piles have bent reinforcement bars. propose the following: P70 One East-West 32mm bar has a minor bend. The bend radii has been checked and is greater than the minumim of r=112mm for 32mm bars. The bend faces away from the BLL slab edge and will not clash with the shutter. propose to leave the bent bar as is. P85 One North-South 32mm bar has a large bend. propose to cut this bar below the bend and attach an M__ coupler. P103. There are two minor bends on 40mm corner bars. The bend radii has been checked and is greater than the minumim of r=140mm for 40mm bars. Both bends face away from the BLL slab edge and will not clash with the shutter. propose to leave the bent bars as is. P107 One East-West 32mm bar has a minor bend. The bend radii has been checked and is greater than the minumim of r=112mm for 32mm bars. The bend faces away from the BLL slab edge and will not clash with the shutter. propose to leave the bent bar as is. P108 There are 3 minor bends on 40mm corner bars. The bend radii has been checked and is greater than the mininum on all bars (as above) 2 bars are facing away from the BLL slab edge and propose to leave as is. 1 bar has been identified to be facing the BLL slab edge and may clash with the slab edge. propse to cut this bar below the bend and attach a M__ coupler to enable an embedment bar to be attached. This will require 20-30mm lowering of the concrete to enable concrete below the coupler.
| 03SR - Stations (RfL) | Cxxx-NCR-001681 | NCR | Sub-platform slab - waterproofing details BLL box |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2015-04-01 | 2015-02-21 12:28 | -39 | 2015-02-04 11:29 | Civil - Structural Engineering | 2500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Waterprrofing to the sub-basement slab at the location of the BLL box is not installed as the __ detail accepted under DDCD on drawing D12086/21 Rev A. The __ between the piles has been omitted and bituthene LM only applied for the south side of pour S8
| 03SR - Stations (RfL) | Cxxx-NCR-001683 | NCR | S09 Bakerloo link piles |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-03-30 | 2015-03-24 16:14 | -6 | 2015-02-06 14:21 | Structural Engineering - Concrete Member | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Please refer NCR-1616 Some of the Bakerloo Link piles have bent reinforcement bars. propose the following: P04 Two 32mm bars have minor bends. The bend radii has been checked and is greater than the minumim of r=112mm for 32mm bars. The bends faces away from the BLL slab edge and will not clash with the shutter. propose to leave the bent bars as is. P41, P42,P43 One bar has a minor bend on each pile The bend radii has been checked and is greater than the minumim of r=112mm for 32mm, r=140mm for 40mm bars. The bend faces away from the BLL slab edge and will not clash with the shutter. propose to leave the bent bar as is. P51 2 40mm bars have bad bends. propse to cut these bars below the bends and attach a M__ coupler to enable an embedment bar to be attached. This has been raised as part of Cxxx-RFI-002410 P51 2 40mm bars have bends. 1 bend requires replacing and 1 can be left as is as the bend radius is less than r=40m for 40mm bars. propse to cut 1 bars below the bend and attach a M__ coupler to enable the embedment bar to be attached This has been raised as part of Cxxx-RFI-002410 the current Remedial tracker had been attached for refrence.
| 03SR - Stations (RfL) | Cxxx-NCR-001684 | NCR | Damage to plunge column pile P32 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-03-13 | 2015-03-13 16:52 | 0 | 2015-02-09 16:45 | Civil - Civil Engineering General | 1500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | During the preparation of the pile head of P32 concrete from the cover zone of the pile has been broken above COL and the cover to the reinforcement reduced. See photo attached.
| 03SR - Stations (RfL) | Cxxx-NCR-001685 | NCR | Missing delivery ticket for BLL cage |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-02-23 | 2015-02-21 12:31 | -2 | 2015-02-09 17:14 | Human Factors - Human Factors General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The delivery ticket for the second reinforcement cage delivery on 13/10/2104 is missing. The delivery ticket was not received by the Site Supervisor. The missing delivery ticket was first noticed when compiling the Report on Reinforcement Steel Traceability (Cxxx-SKC-O-SKC-RGN-B071_WS077- 50239).
| 03SR - Stations (RfL) | Cxxx-NCR-001687 | NCR | BLL Piling - Reinforcing steel cage out of tolerance. |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-03-18 | 2015-03-16 15:07 | -2 | 2015-02-11 13:20 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The top of steel level in pile P109 was 102.978mATD. This is 57mm below the design top of steel level of 103.035mATD and 7mm outside of the allowable -50mm tolerance specified in ICE SPERW 2nd Edition.
| 03SR - Stations (RfL) | Cxxx-NCR-001688 | NCR | I&M omitted from Critical activity readiness review Schedule |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-03-31 | 2015-03-16 15:15 | -15 | 2015-02-11 15:16 | Surveying - Instrumentation and Monitoring | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | NCR raised in respect of Surveillance Report 50206/1.4 for omission of I&M from Critical Activities and Readiness Review Schedule
| 03SR - Stations (RfL) | Cxxx-NCR-001689 | NCR | __ soffit visible cracks and water ingress (GL1-9/C-E) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-04-30 | 2015-04-09 11:19 | -21 | 2015-02-13 11:26 | Civil - Civil Engineering General | 2500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Following the risk reduction meeting held on the 11th of February 2015 to discuss the Water ingress on intermediate level, the below points have been highlighted and discussed; On intermediate level GL1-9 /C-E Visible lines of cracks in __ soffit, with evidence of leeching. The permanent waterproofing system (spray applied and membrane) are not applied on the __ slab between GL1-9/C-E, and will not be applied until 2016. The area is currently being used as a haul route.
| 03SR - Stations (RfL) | Cxxx-NCR-001690 | NCR | __ soffit visible cracks and water ingress (GL14.5-16/C-E) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-04-30 | 2015-04-09 11:21 | -21 | 2015-02-13 11:31 | Civil - Civil Engineering General | 2500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Following the risk reduction meeting held on the 11th of February 2015 to discuss the Water ingress on intermediate level, the below points have been highlighted and discussed; On intermediate level GL14.5-16 /C-E Visible lines of cracks in __ soffit, with evidence of leeching. The permanent waterproofing system (spray applied and membrane) are not applied on the __ slab between and will not be applied until 2016. The area is currently being used as a haul route.
| 03SR - Stations (RfL) | Cxxx-NCR-001691 | NCR | D-wall panel N2 and INT upstand water patches and visible leeching |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-04-14 | 2015-02-26 14:18 | -47 | 2015-02-13 11:57 | Civil - Civil Engineering General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Previous Construction - Problems based on previous construction errors | Completed |  | Following the risk reduction meeting held on the 11th of February 2015 to discuss the Water ingress on intermediate level, the below points have been highlighted and discussed; D-wall Panel N2: Noticeable damp patches below previously repaired area. Leeching Through Upstand: Leeching through the upstand's vertical construction joint is visible.
| 03SR - Stations (RfL) | Cxxx-NCR-001692 | NCR | S08 - Repairs to D-Wall Box Outs |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-04-03 | 2015-04-02 13:45 | -1 | 2015-02-12 15:20 | Structural Engineering - Diaphragm Walls | 2500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | This NCR is raised to track any significant remedials to the D-Wall Boxouts for Slab S08 Sub-Platform Level including Panels S36 - S41 and N37 - N43. Attached are the Miscellaneous works sheets and Notification of Defects use to track the remedials. In Summary: S36 - Void on bottom right approx 600mm wide 150mm High broken out and grouted S37 - No large remedials S38 - Void 300mm wide 100mm High Dry packed S39 - Minor voids dry packed S40 - No large remedials S41 - No large remedials N37 - No large remedials N38 - No large remedials N39 - No large remedials N40 - Small voids dry packed N41 - No large remedials N42 - Small voids dry packed N43 - No large remedials
| 03SR - Stations (RfL) | Cxxx-NCR-001693 | NCR | Survey Equipment out of Calibration |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-04-06 | 2015-04-07 13:36 | 1 | 2015-02-13 09:58 | Surveying - Surveying General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Surveillance showed CAT + Genny calibration was out of date according to Surveying team instrument register
| 03SR - Stations (RfL) | Cxxx-NCR-001695 | NCR | Base slab S1: Inconsistent Concrete at Plunge Column/Tension Piles P1, P2, P3 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-05-27 | 2015-05-14 13:28 | -13 | 2015-02-16 07:32 | Civil - Civil Engineering General | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | During breakdown to cut-off level on plunge column/tension piles P2, P3 the material encountered is inconsistent - particularly in the centre of the pile. An initial visual inspection would suggest there is an area of the pile with no aggregate present which appears to continue below the pile cut-off level. Please not P1 is still to be broken. Please note this NCR supersedes NCR-000895. Please confirm Cxxx have no objection to these piles being incorporated into the permanent works. 29/04/15 Following completion of pile breakdown to DCOL: P1: material at DCOL consistent, no additional breaking required
| 03SR - Stations (RfL) | Cxxx-NCR-001697 | NCR | S08 - Unapproved Materials under HV Trench Shutters |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-04-30 | 2016-04-15 13:56 | -15 | 2015-02-19 16:46 | Structural Engineering - Concrete Member | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Unapproved shims secured with tie wire used to hold the void former spacers to the HV trench.
| 03SR - Stations (RfL) | Cxxx-NCR-001698 | NCR | Concrete line not following TWDCC |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-03-18 | 2015-03-02 15:15 | -16 | 2015-02-18 14:15 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The concrete pump line along the sub-platform blinding has been ued without a correct permit to load being in place.
| 03SR - Stations (RfL) | Cxxx-NCR-001699 | NCR | Damaged Cast in Ø76 Drainage Spigots on IL 15 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-04-16 | 2015-04-15 12:58 | -1 | 2015-02-19 11:03 | Civil - Civil Engineering General | 2500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The 3No. cast in Ø76 stainless steel spigots cast into the Intermediate Slab (IL 15) as per drawing Cxxx-SKC-M-DDA-M171_3-83221 have been damaged during the blinding removal as part of the excavation stage. The 150mm protruding detail below the interemdiate slab as shown on the left hand side of drawing Cxxx-SKC-M-DDA-M171_3-83221 is the section of the spigots which are damaged / crushed. See photos attached in pdf 'Damaged Cast in Ø76 Drainage Spigots on IL 15'.
| 03SR - Stations (RfL) | Cxxx-NCR-001700 | NCR | Water Leakage through Diaphragm Walls at Base Slab |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2016-04-20 | 2016-04-01 07:58 | -19 | 2015-02-19 14:14 | Structural Engineering - Diaphragm Walls | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | During an inspection of dwall joints carried out on 13th February 2015 it was noted that the following joints had water running from them; S1 to S2, S14 to S15, S25, S51 to S52, S55 to S56, S56 to S57, S63 to S64. This was only a sample of the panels and it is expected that once all are available for inspection, there will be more panels out of specification.
| 03SR - Stations (RfL) | Cxxx-NCR-001701 | NCR | D-Wall Panel W3 - out of tolerance GL1/C |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-04-21 | 2015-04-10 09:41 | -11 | 2015-02-20 13:34 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The verticality of D-wall panel W3 (GL1/C) between Sub-platform level and concourse level appears to be out of tolerance. A survey has been carried out to determine the position of the D-wall panel W3 between Sub-platform and concourse level. From the survey results, the maximum deviation from the design position is 0.210m into the box, mainly along GL C. The allowable tolerance as per KP10 Piling and Embedment Retaining walls specification document, Clause KP10.3214 is 1 in 200 plumb and 25mm positional. Accordingly, the maximum allowable tolerance is 125mm, yet the tolerance is exceeded by a maximum of 85mm (along GL C).This deviation will have an impact on the lining wall width in the affected area (please see attached survey) . A cover meter survey has been carried out in order to determine the reinforcement cover in the panel and if there is any potential to scabble back to bring the wall back to within tolerance. However, following a scan survey of the panel and cover meter survey the panel cannot be scabbled as this will reduce the reinforcement cover in the D-wall panel (please see attached Cover meter survey and Scan survey (-Cxxx-C-XSK-00471). The liner wall has only one line of near face reinforcement. The second line of couplers in the concourse level soffit are not required and therefore redundant (please see attached photos). The liner wall at GL C will have to be reduced in width by 100 to 190mm. please see attached documents for clarification.
| 03SR - Stations (RfL) | Cxxx-NCR-001702 | NCR | Cavity Drainage Concrete Infill D-wall panels N1 to N3 Concourse level |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-05-29 | 2015-04-22 09:50 | -37 | 2015-02-20 17:33 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | on concourse level D-wall panels N1 to N3 __F poured the concrete infill for the cavity drianage before signing off the D-wall panels. The NCR is raised agianst the procedure as the D-walls must be inspedcted and signed off before any drainage work is carried out.
| 03SR - Stations (RfL) | Cxxx-NCR-001704 | NCR | Fixings for Blockwork Ties to structural concrete |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-03-23 | 2015-03-23 09:36 | 0 | 2015-02-23 17:37 | Architectural - Brickworks/Blockworks | 1500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Fixings to connect stainless steel ties in the blockwork to the concrete wall was installed without approved MCR in place on Intermediate level slab, between grid lines E5 to E10.
| 03SR - Stations (RfL) | Cxxx-NCR-001705 | NCR | P16 pile rebuild potential low cover to rebar |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2015-04-08 | 2015-04-07 13:43 | -1 | 2015-02-25 10:09 | Geotechnical Engineering - Concrete - Bored Pile | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The reinstated tension pile P16 over the weekend of 21-22 Feb has a distorted geometry. This affected the nominal cover cover (75mm) of some of the pile reinforcement. Ref: Cxxx-SWN-S-DDL-M171_Z-00501
| 03SR - Stations (RfL) | Cxxx-NCR-001706 | NCR | No IRF issued prior BLL piles remedial pour S09 (P51, P52 and P6) |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2015-04-22 | 2015-03-16 15:21 | -37 | 2015-02-27 15:34 | Structural Engineering - Concrete Member | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | No IRF issued to Crossrail to inspect the remedial works prior pour for piles 51, 52 and 6. Contractor to advise how the piles will be certified.
| 03SR - Stations (RfL) | Cxxx-NCR-001708 | NCR | Incorrect Pile Cage Levels |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-09-05 | 2015-09-04 17:12 | -1 | 2015-02-26 16:42 | Civil - Civil Engineering General | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | After installation of the 1800mm Diameter tension pile cages they were incorrectly as-builted (see attached __ documentation for further detail). This led to a number of NCR's been raised that aren’t required. It also led to a number of pile cages been incorrectly recorded as being within the required tolerance when in reality they are not. P06 (NCR-000537) and P42 (NCR-000828) are within the required tolerance when they were originally recorded as not P04, P05, P09, P10, P21 and P23 are out of tolerance when they were originally recorded as not. See attached documentation that shows level detail for the 28No piles that were available at the time of the recent survey after this error was discovered.
| 03SR - Stations (RfL) | Cxxx-NCR-001709 | NCR | S08 Nth. No MCR in place for Metal shims |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-06-01 | 2015-05-19 11:32 | -13 | 2015-03-02 10:18 | Structural Engineering - Formwork | 5000 |  | Documentation and Records | Rework | 3 (3-6k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Metal shims have been used to support the HV trench in Sub-Platform pour S08 Nth without an MCR in place.
| 03SR - Stations (RfL) | Cxxx-NCR-001710 | NCR | Potential cold joint, BLL Pile 114 |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2015-06-30 | 2015-06-24 16:52 | -6 | 2015-03-02 13:55 | Geotechnical Engineering - Concrete - Bored Pile | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During the revision of 1.25.1 package, a note made by the Sub-Contractor was found in the Hold Point form, which states: "Cage initially too low when placed in bore and hung from casing. Concrete poured below lifting band and left for 2 hours before chains removed and top section poured. Cage did not sunk". The 2 hours between concrete pours within the same bored pile increase the risk of cold joint. Could the Contractor describe how the integrity of the pile will be tested? It is known this is not the only case when the cage was hung. Can the Contractor please clarify if there are any other piles with the same issue (time gap in the concrete pour for the piles)?
| 03SR - Stations (RfL) | Cxxx-NCR-001711 | NCR | S09 - Repairs to D-Wall Box Outs |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-04-03 | 2015-04-02 13:46 | -1 | 2015-03-03 14:43 | Structural Engineering - Diaphragm Walls | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | This NCR is raised to track any significant remedials to the D-Wall Boxouts for Slab S09 Sub-Platform Level including Panels S42 - S47 and N44 - N48. Attached are the Notification of Defects used to track the remedials. In Summary: S42 - 2 small voids at bottom of panel dry packed, one small void at top right grouted S43 - One small void at top left grouted S44 - No large remedials S45 - No large remedials S46 - 2 small voids at bottom of panel dry packed S47 - Large Void at top of Panel Grouted (See Cxxx-RFI-002288) N44 - No large remedials N45 - No large remedials (See also Cxxx-RFI-002398) N46 - No large remedials N47 - No large remedials N48 - No large remedials
| 03SR - Stations (RfL) | Cxxx-NCR-001712 | NCR | S6 Blinding Levels out of Tolerance |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-04-14 | 2015-04-02 13:57 | -12 | 2015-03-02 18:52 | Civil - Civil Engineering General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Since pouring the S6 blinding on the 17/10/14 heave has occurred. Areas around Plunge column PC18, PC19 and PC20 are up to +32mm high.
| 03SR - Stations (RfL) | Cxxx-NCR-001713 | NCR | Intermediate Level Soffit remedials (GL13-15/A) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-05-15 | 2015-04-13 15:36 | -32 | 2015-03-16 15:07 | Civil - Civil Engineering General | 2500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Previous Construction - Interfacing issues | Completed |  | Intermediate Level Soffit GL13-15/A During the construction of the intermediate level slab and due to steel congestion some areas in the soffit were not cleaned properly, thus affecting the concrete finish of the soffit. As a result inclusions and pockets of loose material can be seen. please see attached document for clarification.
| 03SR - Stations (RfL) | Cxxx-NCR-001714 | NCR | intermediate level soffit remedials (GL 10-11/A) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-05-15 | 2015-04-13 15:40 | -32 | 2015-03-16 15:10 | Civil - Civil Engineering General | 2500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Previous Construction - Interfacing issues | Completed |  | Intermediate Level Soffit GL10-11/A During the construction of the intermediate level slab and due to steel congestion some areas in the soffit were not cleaned properly, thus affecting the concrete finish of the soffit. As a result inclusions and pockets of loose material can be seen. please see attached document for clarification.
| 03SR - Stations (RfL) | Cxxx-NCR-001715 | NCR | Damaged 1800mm Diameter Pile Heads |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-04-08 | 2015-04-07 13:47 | -1 | 2015-03-03 09:32 | Civil - Civil Engineering General | 1500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Pile 33 has been damaged during the break down process (See attached photographs) and will need repairing prior to waterproofing. The chip is approximately 300mm long by up to 70mm deep.
| 03SR - Stations (RfL) | Cxxx-NCR-001716 | NCR | Bakerloo piles Sub-platform pour S07 and S10 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-05-03 | 2015-04-01 17:11 | -32 | 2015-03-04 08:18 | Structural Engineering - Concrete Member | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During breakdown of the Bakerloo piles there has been a number of small damages occurred to the various piles. This NCR covers piles within Sub platform pour S07 and S10 Please see attached tracker showing remedial solutions used.
| 03SR - Stations (RfL) | Cxxx-NCR-001718 | NCR | S09 - BLL Pile 51 Link |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-05-13 | 2015-05-26 15:00 | 13 | 2015-03-10 11:44 | Structural Engineering - Reinforcement | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Difficulties occurred while fixing a link in the Bakerloo Line Link Pile 51 around M__ couplers. As a result of the varying size between M__ couplers and the non coupled bars a small gap was left between the link and bar in one corner (See attached photo).
| 03SR - Stations (RfL) | Cxxx-NCR-001719 | NCR | S09 water ingress N44-N45 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-05-06 | 2015-03-23 13:15 | -44 | 2015-03-09 10:36 | Structural Engineering - Diaphragm Walls | 1500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Water ingress has been noticed coming through Diaphragm wall panels N44 and N45 on sub platform level.
| 03SR - Stations (RfL) | Cxxx-NCR-001720 | NCR | Damaged shear studs on pile 15 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-04-29 | 2015-05-01 11:11 | 2 | 2015-03-10 09:02 | Civil - Civil Engineering General | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 2 no shear studs on the north web and 3 no shear studs on the south web of plunge column 15 have been damaged during break out operations in preparation for pile reinstatement.
| 03SR - Stations (RfL) | Cxxx-NCR-001721 | NCR | DDCD Drawings not in use at start of works |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-03-24 | 2015-03-23 09:20 | -1 | 2015-03-10 13:59 | Architectural - Brickworks/Blockworks | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | At construction start on site on 12/02/15, the latest typical detail dwgs (Cxxx-SKC-A-DDD-M171_84156 , and 84152) was not issued for construction to the subcontractor
| 03SR - Stations (RfL) | Cxxx-NCR-001723 | NCR | Benchmark Panel of Blockwork not agreed |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-03-24 | 2015-03-23 09:21 | -1 | 2015-03-10 16:42 | Architectural - Brickworks/Blockworks | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The specification states that the first 10m2 of constructed wall should be offered up to the client for acceptance as a benchmark. Benchmark panel has not yet been offered up for inspection.
| 03SR - Stations (RfL) | Cxxx-NCR-001724 | NCR | Thermometer used for temperature checks is not a calibrated model |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-03-31 | 2015-04-07 14:55 | 7 | 2015-03-10 17:00 | Architectural - Brickworks/Blockworks | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The 2no. thermometers used by the blockwork subcontractor do not have a calibration number, therefore cannot guarantee that they measure the correct temperature. No blocks shall be laid when air temp is at or below 3degrees.
| 03SR - Stations (RfL) | Cxxx-NCR-001725 | NCR | Vertical joint of blockwork exceeds 20mm at quoin intermediate level south perimeter wall GL 7/8 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-03-24 | 2015-04-07 09:40 | 14 | 2015-03-10 17:51 | Architectural - Brickworks/Blockworks | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Reference to the perimeter wall blockwork at Intermediate level, south wall between GL 7-8 The vertical joint of the at the corner/quoin, where the wall changes direction along the perimeter Dwall, the vertical mortar joint exceeds 20mm.
| 03SR - Stations (RfL) | Cxxx-NCR-001727 | NCR | Pile P15 bleed channels |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-04-09 | 2015-04-01 09:56 | -8 | 2015-03-11 15:53 | Civil - Civil Engineering General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Further to NCR-1669, following pile investigation and agreed pile breakdown works (1150mm below DCOL determined from 2No cores) significant bleed features were found at various locations on the pile head. Localised breaking was done at one of the areas to the maximum permitted breakdown depth provided by the designer (1350mm) in order to remove the sandy material. The remaining locations have been broken approx. 50-100mm. The material found at all three areas with additional breaking has been classed as weak sandy mortar.
| 03SR - Stations (RfL) | Cxxx-NCR-001728 | NCR | N1 - Base Slab Couplers Out of Tolerance |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-10-30 | 2015-10-01 10:38 | -29 | 2015-03-13 09:41 | Structural Engineering - Diaphragm Walls | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The top row of couplers in this panel compromise the cover of the poured slab. The levels from the top of the couplers are 104.336mATD – 104.320mATD. The finished slab level is 104.310mATD. They will protrude out of the slab by 20-26mm.
| 03SR - Stations (RfL) | Cxxx-NCR-001729 | NCR | S1 - Clay inclusion in D-wall at Subplatform level |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-05-12 | 2015-05-08 14:56 | -4 | 2015-03-13 10:37 | Structural Engineering - Diaphragm Walls | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | There are 2 large clay inclusions in panel S1, at sub-platform level. See attached photographs. 1. Above box-out level a clay inclusion extends around the liner wall box-out approximately 500mm wide by 600mm high. 2. Below blinding level there is clay inclusion approximately 500mm high by 500mm deep into the panel. across the full width of the panel.
| 03SR - Stations (RfL) | Cxxx-NCR-001730 | NCR | N17 Clay Inclusions Below Blinding @ 102.560mATD |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-07-03 | 2015-07-02 13:44 | -1 | 2015-03-13 14:37 | Structural Engineering - Diaphragm Walls | 2500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Clay is running into the panel S17 below blinding level (See attachment for dimensions).
| 03SR - Stations (RfL) | Cxxx-NCR-001731 | NCR | Sub-Platform Slab S8 North: HV trench concrete finish |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-09-24 | 2015-09-24 10:13 | 0 | 2015-03-18 15:58 | Structural Engineering - Finishes | 2100 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Blowholes/craters to surface finish not to required standard for plain finish for formed surface.
| 03SR - Stations (RfL) | Cxxx-NCR-001732 | NCR | Sub-Platform Slab S8 South: 1 hr concrete placement limit exceeded for fresh concrete in touch with fresh concrete. |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-04-01 | 2015-03-23 13:20 | -9 | 2015-03-18 16:06 | Structural Engineering - Concrete Member | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | 1 hr concrete placement limit exceeded for fresh concrete in touch with fresh concrete between ticket numbers 627601 and 627618. Specification Clause KF11.3204(h). Placement time exceeded by 15mins. No problems were observed at the time of the pour with achieving homogenous concrete.
| 03SR - Stations (RfL) | Cxxx-NCR-001733 | NCR | Sub-Platform Slab S8 South: HV trench levels |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-06-30 | 2016-05-19 16:18 | -42 | 2015-03-18 16:24 | Structural Engineering - Concrete Member | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | HV trench formwork lifted during pour to either side of GL12 predominantly to the south side of the trench. Max +51mm. See attached survey. Levels of the 50x50 rebate vary up to +17mm on the north side of the trench and +40mm on the south side of the trench.
| 03SR - Stations (RfL) | Cxxx-NCR-001734 | NCR | S07 - D-Wall Couplers out of tolerance |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-04-02 | 2015-04-07 09:24 | 5 | 2015-03-19 12:14 | Structural Engineering - Diaphragm Walls | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | When preparing the Sub-Platform D-Wall couplers some panels were found to be out of tolerance (+ -50mm). Where low couplers were found to clash with the bottom reinforcement these bars will need to be re-drilled. Furthermore due to difference in D-Wall and base slab tolerances some in-tolerance couplers will still clash with the bottom mat of reinforcement. For this reason any coupler 150mm or less from the top of blinding level (see attachment) needs to be re-drilled. This NCR covers Pour S07 with the following Panels affected: S33 - 2 no. couplers 37-46mm low, (D-Wall in tolerance but clash still likely) S33 - 2 No. Couplers 53-60mm low (D-Wall out of tolerance) S34 - 4 no. couplers 41-47mm low, (D-Wall in tolerance but clash still likely)
| 03SR - Stations (RfL) | Cxxx-NCR-001735 | NCR | Sub-Platform Slab S8 South: HV trench concrete finish |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-09-24 | 2015-09-24 10:14 | 0 | 2015-03-18 16:38 | Structural Engineering - Finishes | 2100 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Blowholes/craters to surface finish not to required standard for plain finish for formed surface.
| 03SR - Stations (RfL) | Cxxx-NCR-001736 | NCR | Sub-Platform Slab S8 South: Serviseal Waterstop Junction Type FT |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-07-15 | 2015-05-26 15:03 | -50 | 2015-03-18 16:57 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | 2 strips of __ Mastic were not applied at the end of the Serviseal AT240 within the S8 pour. Shown on __ Drawing 13 but not shown on __ Drawing 18
| 03SR - Stations (RfL) | Cxxx-NCR-001738 | NCR | S09 North - Sub-platform level - Damaged coupler N45 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-04-06 | 2015-03-23 13:16 | -14 | 2015-03-23 07:18 | Structural Engineering - Reinforcement | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In Pour 9 North, D-wall panel N45 has 1 No damaged coupler.
| 03SR - Stations (RfL) | Cxxx-NCR-001739 | NCR | visible leeching cracks in East Liner wall Concourse level |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-05-19 | 2015-04-02 13:58 | -47 | 2015-03-20 14:06 | Civil - Civil Engineering General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | on Concourse level, GL24/E-D. a number of visible cracks in the easter liner wall show signs of leeching.
| 03SR - Stations (RfL) | Cxxx-NCR-001740 | NCR | Damage to Piezometer C7-11 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-04-10 | 2015-04-02 12:10 | -8 | 2015-03-20 16:08 | Surveying - Instrumentation and Monitoring | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | As a result of blinding break out around Plunge column 05, the cables for Vibrating Wire Piezometer (VWP) C7-11 were damaged on 16th March 2015 (See attached image). Monitoring of the two VWP tips at 78m and 94m ATD have not been read following the damage to date.
| 03SR - Stations (RfL) | Cxxx-NCR-001741 | NCR | Out of tolerance diaphragm wall panels below concourse |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-08-03 | 2019-08-08 15:58 | 370 | 2015-03-23 08:37 | Structural Engineering - Diaphragm Walls | 5600 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | It has been surveyed that below concourse a number of Diaphragm walls are outside of the construction tolerance. The tolerance for at sub-platform (not including overbreak and additional overbreak) is calculated to be 139mm at sub-platform level The attached extract from survey shows measurements of the panels that are past this tolerance. Previous NCRS on this topic do not include accurate information outlining the defect.
| 03SR - Stations (RfL) | Cxxx-NCR-001742 | NCR | S09 North - D-wall Couplers out of tolerance |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-04-13 | 2015-04-09 11:23 | -4 | 2015-03-23 08:22 | Structural Engineering - Reinforcement | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | When preparing the Sub-Platform D-Wall couplers some panels were found to be out of tolerance (+ -50mm). Where low couplers were found to clash with the bottom reinforcement these bars will need to be re-drilled. Furthermore due to difference in D-Wall and base slab tolerances some in-tolerance couplers will still clash with the bottom mat of reinforcement. For this reason any coupler 150mm or less from the top of blinding level (see attachment) needs to be re-drilled. This NCR covers Pour S09 North with the following Panel affected: N45 - 5 couplers 43-48mm low (D-wall in tolerance but clash still likely)
| 03SR - Stations (RfL) | Cxxx-NCR-001743 | NCR | 28 day cube strength cubes 1343B and 1343C (__F-NCR-195) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-04-12 | 2015-03-27 09:17 | -16 | 2015-03-23 14:28 | Civil - Civil Engineering General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Roof Level slab G/L 5, Up-stand wall ETL-L20 GL D/19-20, Intermediate Level up-stand GL23/D-E Pour date 13/01/15. 28 day cube strengths failed to reach 50N/mm2. Cube 1343B 46.4 N/mm2 Cube 1343C 47.8N/mm2
| 03SR - Stations (RfL) | Cxxx-NCR-001744 | NCR | S07 Blinding Heave |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-05-22 | 2015-03-27 09:19 | -56 | 2015-03-23 17:52 | Civil - Civil Engineering General | 1500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | following the extended duration the S07 blinding was sitting for it was noticed that heave occurred over an area around the Plunge column P 22 excavation. This heave was identified during a pre works survey. Attachment "S07 Blinding Level Survey 15.11.15.pdf" shows the survey carried out on the blinding following pouring showing all areas within tolerance. Page 1 of attachment "NCR 200 S7 heave surveys.pdf " shows a survey carried out around the plunge column following completion of column works. attachment "__F-NCR-200 rev1 Blinding survey 2015_02_23.pdf" shows the survey following scabbling to remove all high areas.
| 03SR - Stations (RfL) | Cxxx-NCR-001745 | NCR | Diaphragm wall - Water ingress |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-04-30 | 2016-04-18 16:00 | -12 | 2015-03-24 17:56 | Structural Engineering - Diaphragm Walls | 15000 |  | Documentation and Records | Rework | 2 (6-60k) | Complete | Design Problem - Other | Completed |  | Having reviewed the data collected from the site measurements of water ingress through the Diaphragm wall it has become apparent that the water ingress in some cases is greater than that set out in SPERW and under KP10.1301 part b. i.e there is running water coming through the joints as the trial pits are filling up. However under KP10.1301 part a) it specifies that; water leakage through the diaphragm wall panels are acceptable if not exceeding 0.4 litre/m2 per day and leakage through the joints not to exceed an additional 6 litres/m of joint per day. With the above in mind it can be seen that the water ingress we have seen is a non-conformance in accordance with one part of the specification but not in accordance with another part, after risk Reduction meeting held 17/03/15 all agreed that base slab works should continue and that remedial measures could be assessed and carried out afterwards.
| 03SR - Stations (RfL) | Cxxx-NCR-001746 | NCR | PC48 clay inclusions below COL |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2015-04-29 | 2015-04-29 13:13 | 0 | 2015-03-25 09:59 | Structural Engineering - Concrete Member | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Three cores (N, E & W) have been taken of PC48. Two of the cores (north and west) show large clay inclusions at 0.13m below COL (West) and 0.46m below COL (North) as per __ core inspections. The clay pockets will need to be removed.
| 03SR - Stations (RfL) | Cxxx-NCR-001747 | NCR | No CE certification for structural steel windposts |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2016-01-26 | 2015-11-27 11:27 | -60 | 2015-03-26 10:01 | Architectural - Brickworks/Blockworks | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Windposts installed on the Intermediate and Concourse level will not be CE certified. It was previously discussed and communicated that the supplier is in the process of being audited in order to CE certify their products, a CE certifcate has been issued for their products on the 18th March. Crossrail have since been made aware that the CE certifcate will not be valid for any windposts supplied and installed prior to this date.
| 03SR - Stations (RfL) | Cxxx-NCR-001748 | NCR | S14 blinding levels |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-04-11 | 2015-04-01 11:01 | -10 | 2015-03-28 14:47 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Please see attached S14 blinding survey. A localized pocket of blinding to the south side of S14 is low -16mm to -27mm.
| 03SR - Stations (RfL) | Cxxx-NCR-001749 | NCR | Damaged shear studs on pile 10 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-07-29 | 2015-07-23 14:49 | -6 | 2015-03-30 10:25 | Civil - Structural Engineering | 1500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 1 no shear stud on the north web and 3 no shear studs on south web of Plunge column 10 have been damaged during break out operations in preparation for pile reinstatement.
| 03SR - Stations (RfL) | Cxxx-NCR-001750 | NCR | P47 sand rich material |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-06-08 | 2015-05-14 17:38 | -25 | 2015-03-30 17:40 | Civil - Civil Engineering General | 1500 |  | Material | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Following the cores inspection of pile P47, the presence of friable sand rich material was noted. This patch is at ~1.6m depth. It should be noted that the material is localised to a ~185x80mm patch and is surrounded by apparently robust mortar. This material is found only one of the cores - P47E. (See photo logs attached)
| 03SR - Stations (RfL) | Cxxx-NCR-001751 | NCR | S05 sub-platform blinding levels |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-04-13 | 2015-04-13 15:47 | 0 | 2015-03-30 17:40 | Structural Engineering - Concrete Member | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please see attached survey of S05 blinding. Page 1 is the current heights. page 2 is the initial asbuilt survey. Some area of the blinding appear to have heaved after pouring.
| 03SR - Stations (RfL) | Cxxx-NCR-001752 | NCR | Lifting Band High on P41 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-06-17 | 2015-05-29 10:41 | -19 | 2015-03-31 18:38 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The lifting band on P41 is approximately 25mm above design level, and projects into the area for bottom mat reinforcement of the base slab. Note that although P41 is shown on the earthing design, the cage was not continuity tested prior to installation as recorded in NCR-826. The earthing pile was switched to P47 as this was continuity tested.
| 03SR - Stations (RfL) | Cxxx-NCR-001753 | NCR | BLL - Piling - Concrete Placement into P23 exceeding time allowance. |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-05-07 | 2015-04-18 13:08 | -19 | 2015-04-01 10:18 | Structural Engineering - Concrete Member | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | This NCR has been raised to clarify the contents of NCR-1601. P58 was reference in previous NCR and contained concrete that exceeded the 2 hour time limit between batching and placement, but was within the revised time limit of 3 hours (FCD-1582). P23 contained concrete that exceeded the 3 hour time limit by 12 mins. (Load 510859 batched at 08:54 and finished placement at 12:06). There were no cubes taken from this load of concrete.
| 03SR - Stations (RfL) | Cxxx-NCR-001754 | NCR | Int Level Tension Column No.6 Verticality out of tolerance (__F-NCR-207) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-05-21 | 2015-05-08 15:10 | -13 | 2015-04-01 17:51 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Intermediate Level –Tension Column No. 6 . East of GL11 Column No. 6 is out of tolerance for verticality (NSCS specification 10.5.2 (allowable 10mm)). Actual to south side of column 12mm Please see attached As-built.
| 03SR - Stations (RfL) | Cxxx-NCR-001755 | NCR | Bent B50 Bar on Tension Pile P40 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-06-09 | 2015-06-12 10:52 | 3 | 2015-04-01 20:02 | Civil - Civil Engineering General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On tension pile P40, a B50 bar has been bent above the pile design COL. Note that the pile has been broken down a further 1600mm from design COL to remove grout.
| 03SR - Stations (RfL) | Cxxx-NCR-001756 | NCR | Damaged Shear Studs On Pile 5 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-06-16 | 2015-05-14 13:28 | -33 | 2015-04-14 14:12 | Civil - Civil Engineering General | 1500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 2 no shear studs (1 North, 1 South) were damaged during pile breakdown operations on pile 5 prior to pile reinstatement.
| 03SR - Stations (RfL) | Cxxx-NCR-001757 | NCR | S06 - Damaged __ Coupler PC 18 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-04-21 | 2015-04-22 10:03 | 1 | 2015-04-07 13:52 | Structural Engineering - Reinforcement | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The thread of 1no. __ coupler, attached to Plunge Column 18, is damaged. As the pile cage is low, the couplers are cast into the pile concrete. It was not possible to unscrew from the pile rebar and replace. A 107mm diameter core, 100mm deep from top of pile level, has been drilled around the 80mm coupler to allow it to be unscrewed from the pile reinforcement and replaced. It is proposed to back fill the 15mm void around the new coupler with Five star grout. See attached photo of replaced coupler with void to be filled. Please confirm this is an acceptable repair.
| 03SR - Stations (RfL) | Cxxx-NCR-001758 | NCR | S9 - Concrete finish - HV trench & sloping BLL adit |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-09-24 | 2015-09-24 10:18 | 0 | 2015-04-09 14:17 | Structural Engineering - Structural Engineering - General | 2500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | There are blowholes/craters on the surface finish that is not up to the required standard for plain finish formed surface.
| 03SR - Stations (RfL) | Cxxx-NCR-001760 | NCR | S12 Blinding levels |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-04-23 | 2015-04-16 14:43 | -7 | 2015-04-09 16:51 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | See attached P37 and P38 Coupler and blinding surveys. Please note that the blinding surrounding these piles is up to 30mm low in some localised areas.
| 03SR - Stations (RfL) | Cxxx-NCR-001761 | NCR | Diaphragm wall repairs Lightwell area |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-03-31 | 2016-03-14 14:29 | -17 | 2015-04-10 13:09 | Structural Engineering - Diaphragm Walls | 20000 |  | Workmanship | Rework | 2 (6-60k) | Complete | Material/Preservation Problems - Other | Completed |  | This NCR covers defects in diaphragm wall S27-S54 from concourse TOC to capping beam. These defects were previously covered by Cxxx-NCR-001486 and Cxxx-NCR-1493. Due to the works being carried out in one lift(Lightwell area) the NCRs have been incorporated. A full snag sheet will be created by and agreed with CRL field engineer. following this works will be implemented to repair each defect. An IRF will be issued for each panel once works are complete.
| 03SR - Stations (RfL) | Cxxx-NCR-001762 | NCR | Bent Starter Bars on Pile 16 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-05-07 | 2015-04-20 17:41 | -17 | 2015-04-14 11:16 | Civil - Civil Engineering General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | There are three bent B40 starter bars on Pile 16 that have been bent above cut off level 102.635.
| 03SR - Stations (RfL) | Cxxx-NCR-001763 | NCR | Damaged shear studs on pile 2 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-06-16 | 2015-06-15 18:12 | -1 | 2015-04-14 14:31 | Civil - Civil Engineering General | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | 10 no shear studs (6 North, 4 South) were damaged on plunge column 2 during pile breakdown operations prior to pile reinstatement.
| 03SR - Stations (RfL) | Cxxx-NCR-001764 | NCR | S06 - D Wall couplers re-drilled |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-05-28 | 2015-05-08 16:27 | -20 | 2015-04-14 15:19 | Structural Engineering - Reinforcement | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | When preparing the Sub-Platform D-Wall couplers some panels were found to be out of tolerance (+ -50mm). Where low couplers were found to clash with the bottom reinforcement these bars will need to be re-drilled. Furthermore due to difference in D-Wall and base slab tolerances some in-tolerance couplers will still clash with the bottom mat of reinforcement. For this reason any coupler 150mm or less from the top of blinding level (see attachment) needs to be re-drilled. This NCR covers Pour S06 with the following Panels affected: S25 - 5 no. couplers 22-50mm low re drilled (Not out of tolerance but likely to clash) S25 - 1 no. couplers 51mm low re drilled (Out of tolerance) S26 - 6no. couplers 45-50mm low re drilled (Not out of tolerance but likely to clash) S26 - 6no. couplers 50-55mm low re drilled (Out of tolerance) S27 - 3no. couplers 43-50mm low re drilled (Not out of tolerance but likely to clash) S27 - 2no. couplers 50-55mm low re drilled (Out of tolerance) All unused drilled holes have been filled with a resin injected piece of 40mm rebar. See attached photo.
| 03SR - Stations (RfL) | Cxxx-NCR-001765 | NCR | Blockwork Lintel Bearing |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-06-16 | 2015-06-15 15:42 | -1 | 2015-04-14 17:44 | Architectural - Brickworks/Blockworks | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | With reference to the lintels above the access hatch locations on the perimeter block work wall, the specification calls for the bearing blocks supporting the edge either side of the lintels to be full blocks. Some of the lintels installed on the intermediate level are not supported by full 440mm blocks.
| 03SR - Stations (RfL) | Cxxx-NCR-001766 | NCR | Cavity Drainage Installation of 50mm Stainless Steel Spigot (IL16) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-05-13 | 2015-05-11 17:32 | -2 | 2015-04-15 11:16 | Civil - Drainage | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | This NCR is raised based on the Proposed Answer to close out Cxxx-NCR-001699. Due to constraints on site with the methodology to carry out the remedial repair to the 3No. damaged Cast-In Spigots on IL16, the red line drawing attached details the different repair procedure that was carried out instead by the subcontractor to address Cxxx-NCR-001699. This red line drawing (Sketch in Relation to -RFI-000629 - Red Line Drawing) should be read in conjunction with -RRI-000703 which has been issued to __ for comment. In reference to the red line drawing, the epoxy resin used is called __ __ EP and is approved through MCR (Cxxx-SKC-O-TSC-B071_WS077-50150) and the fire grout used is called __ CP 611A and this is also approved through MCR (Cxxx-SKC-O-TSC-B071_WS077-50265). The screed installed for the cavity drainage and benching is approved through MCR (Cxxx-SKC-O-TSC-B071_WS077-50399).
| 03SR - Stations (RfL) | Cxxx-NCR-001767 | NCR | Damage on pile 14 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-04-29 | 2015-04-24 11:56 | -5 | 2015-04-15 16:36 | Civil - Civil Engineering General | 2500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | During the preparation of the pile head on P14, concrete from the cover zone of the pile has been broken above COL and the cover to the reinforcement reduced. See photo attached.
| 03SR - Stations (RfL) | Cxxx-NCR-001768 | NCR | Damage to P13 and P14 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-06-24 | 2015-06-05 13:30 | -19 | 2015-05-18 12:04 | Civil - Civil Engineering General | 1500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the preparation of the pile head on P13 and P14 concrete from the cover zone of the pile has been broken above COL and the cover to the reinforcement reduced. See photos attached.
| 03SR - Stations (RfL) | Cxxx-NCR-001769 | NCR | Sub-Platform West Sump: Inconsistent Concrete at Plunge Column/Tension Piles P07 and P08 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-09-15 | 2015-09-10 09:21 | -5 | 2015-04-15 17:48 | Civil - Civil Engineering General | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Piles P07 and P08 have been cored from above cut-off level, and the material encountered is inconsistent. A visual inspection of the cores would suggest there is an area of the pile with no aggregate present which appears to continue below the pile cut-off level. will proceed with investigation and reinstatement of the pile as proposed in Cxxx-SKC-S-RGN-B071_WS077-50030, then attach a supplementary pile record pack to this NCR containing test data relevant to these piles.
| 03SR - Stations (RfL) | Cxxx-NCR-001770 | NCR | Damaged Precast Panel GL11-C |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-01-04 | 2016-01-04 14:59 | 0 | 2015-04-17 17:19 | Civil - Civil Engineering General | 2500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Concourse Level Soffit GL11/C Column 1. Damaged Precast Panel (please see attached photo)
| 03SR - Stations (RfL) | Cxxx-NCR-001771 | NCR | Damaged Shear Studs on pile 46 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-06-16 | 2015-05-14 13:41 | -33 | 2015-04-20 12:22 | Civil - Civil Engineering General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 4 no Shear studs on Pile 46 (all on the north web) have been damaged during pile breakdown operations.
| 03SR - Stations (RfL) | Cxxx-NCR-001772 | NCR | Intermediate Level – Downpipe out of tolerance |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-07-31 | 2016-05-27 13:44 | -65 | 2015-04-20 16:11 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Intermediate Level A11 – GL11 South D-wall. Downpipe has been cast in 225mm out of position. The Downpipe should be 3605mm East of Gridline 11, the as built position of the downpipe is 3380mm east of GL11.
| 03SR - Stations (RfL) | Cxxx-NCR-001773 | NCR | Concourse Level – Downpipe out of tolerance Gridline 8 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-10-24 | 2016-10-10 15:30 | -14 | 2015-04-20 16:17 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Concourse Level A8 – Downpipe should be 1000mm East of Gridline 8. The as built position is 110mm West of Gridline 8.
| 03SR - Stations (RfL) | Cxxx-NCR-001774 | NCR | S10 - BLL pile starters - use of 2No M__ Couplers |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-05-04 | 2015-04-27 16:45 | -7 | 2015-04-20 16:41 | Structural Engineering - Reinforcement | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Drawing Cxxx-SKC-C-DWG-B071_WS077-52060 Rev. C01 2No. piles starter bars hy-ten couplers are damaged.
| 03SR - Stations (RfL) | Cxxx-NCR-001775 | NCR | S10 North and South: HV trench concrete finish |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-09-24 | 2015-09-24 13:16 | 0 | 2015-04-20 17:07 | Civil - Civil Engineering General | 2500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | In S10, there are blowholes/craters to the surface finish that is not upto the required standard for plain finish for formed surfaces
| 03SR - Stations (RfL) | Cxxx-NCR-001776 | NCR | Blockwork intumescnet mastic applied in gaps greater than 30mm |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-05-30 | 2016-05-13 08:47 | -17 | 2015-04-21 16:58 | Architectural - Brickworks/Blockworks | 1000 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The approved MCR for the intumescent sealant used in the block work (Refer to Cxxx-SKC-O-TSC-B071_WS077-50422) states that the maximum joint gap for application is 30mm. The design vertical gap at the wind post location is 30mm minimum. The horizontal gap at the head of the wall is 35mm. Therefore any areas where the gap is greater than 30mm, the mastic may not meet the required fire rating as recommended by the manufacturer.
| 03SR - Stations (RfL) | Cxxx-NCR-001777 | NCR | S11 - Drilled D-wall and Dummy Resined bars into D-wall |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-05-07 | 2015-05-08 15:22 | 1 | 2015-04-23 07:36 | Structural Engineering - Reinforcement | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | S58 D-wall couplers have been surveyed and noted that they are too low, hence have been redrilled. In D-wall the panel is in tolerance but likely to clash with the U-bars and bottom mat, so 6 additional bars have been drilled
| 03SR - Stations (RfL) | Cxxx-NCR-001779 | NCR | S11 - Angled couplers N57 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-05-28 | 2015-05-26 15:14 | -2 | 2015-04-23 15:53 | Structural Engineering - Reinforcement | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | In D-wall panel N57, during installation, it was noted that the couplers in the D-wall are at an angle facing upwards.
| 03SR - Stations (RfL) | Cxxx-NCR-001780 | NCR | Bleed channels on pile 48 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-06-24 | 2015-05-21 14:40 | -34 | 2015-04-23 08:41 | Civil - Civil Engineering General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On Pile 48 there is significant honeycombing in a bleed channel on the south face of the pile (photos attached). The nature of this material is very porous and friable. This material has been partially broken out to a depth of 900mm below cut-off. The defect appeared to be getting smaller with depth but continued deeper.
| 03SR - Stations (RfL) | Cxxx-NCR-001781 | NCR | S06 Missing couplers T4 layer BM131 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-05-20 | 2015-05-19 09:52 | -1 | 2015-04-23 10:00 | Structural Engineering - Reinforcement | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 3No.16mm couplers to BM131 to S6 top mat layer T4 are missing on West stop end on GL C. See attachment
| 03SR - Stations (RfL) | Cxxx-NCR-001782 | NCR | Eathing bands on pile1 and pile 51 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-06-09 | 2015-05-15 09:39 | -25 | 2015-04-23 11:29 | Civil - Structural Engineering | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Due to them clashing with the base slab bottom Mat reinforcement the lifting bands on piles 1 and 51 have been removed. Both these bands are specified as earthing electrodes in the Cxxx Earthing Design.
| 03SR - Stations (RfL) | Cxxx-NCR-001783 | NCR | Pile Cores Repair Concrete - Low 7 Day Cube Results |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-08-27 | 2015-07-01 15:22 | -57 | 2015-04-23 17:39 | Civil - Civil Engineering General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | On 25/03/2015 core holes in tension piles P46 - P51 were filled with 5 Star Repair Concrete through the use of a 4-10 colloidal mixer and pump. Six cubes were taken from the batch of repair concrete that was placed in the cores P51-East & P51-South. Cubes were crushed at 7 and 28 days and achieved compressive strength results at 28 days 19.0N/mm2 & 18.6N/mm2 (see attached cube results). These results are lower than the required (45N/mm2) and lower than what we have experienced with this mix in the past. The two spare cubes will be crushed at 56 days and the results provided as soon as they are available to us. This was the first batch mixed on this day. The sample given to the concrete technician may have contained residual water that was in the lines from the core flushing process. An inspection of these cores was carried out the following day by __ Engineers and the repair concrete appeared to have gained a comparable strength to other batches used on site.
| 03SR - Stations (RfL) | Cxxx-NCR-001784 | NCR | Records and Documentation |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2015-06-16 | 2015-05-28 11:59 | -19 | 2015-04-24 12:05 | Architectural - Masonary | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A review of the ITP Cxxx-SKC-C-ITP-B071_WS077-50071 rev 3.0 found that the Contractor had not been following the accepted ITP; check item 12 hold point; “installation of blockwork-check quality of workmanship”, check item 13 hold point: “installation of lintel”, check item 14 witness point;” installation of bed joint reinforcement”, check item 15 hold point; “installation of access hatches” and check item 16 hold point;” installation of PFC corofil and mastic”, The Contractor was unable to supply any evidence that the above intervention hold point checks have been carried as per the accepted ITP. It is also noted that there is no check for the installation of the damp proof membrane on the ITP.
| 03SR - Stations (RfL) | Cxxx-NCR-001785 | NCR | Materials Testing |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2015-06-16 | 2015-05-28 12:07 | -19 | 2015-04-24 12:10 | Architectural - Masonary | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | On request the Contractor was unable to provide compressive strength test results for the mortar in use for the installation of blockwork that started on the 15th February 2015.
| 03SR - Stations (RfL) | Cxxx-NCR-001786 | NCR | Records and Documentation |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2015-06-16 | 2015-05-28 11:56 | -19 | 2015-04-24 12:16 | Architectural - Masonary | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | On request the Contractor was unable to supply any check sheets for the installation of blockwork for the intermediate level of the Paddington Station box,
| 03SR - Stations (RfL) | Cxxx-NCR-001787 | NCR | S05 - Re-drilled D' wall couplers |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-05-08 | 2015-05-08 15:23 | 0 | 2015-04-24 14:01 | Structural Engineering - Reinforcement | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | When preparing the Sub-Platform D-Wall couplers some panels were found to be out of tolerance (+ -50mm). Where low couplers were found to clash with the bottom reinforcement these bars will need to be re-drilled. Furthermore due to difference in D-Wall and base slab tolerances some in-tolerance couplers will still clash with the bottom mat of reinforcement. For this reason any coupler 150mm or less from the top of blinding level (see attachment) needs to be re-drilled. This NCR covers Pour S05 with the following Panels affected: S19 (in S05) – 1 no. coupler 36mm low, re drilled (Not out of tolerance but likely to clash). S22 – 10 no. couplers 41-50mm low, re drilled (Not out of tolerance but likely to clash). S22 – 2 no. couplers 50-51mm low, re drilled (Out of tolerance) S23 – 12 no. couplers 61-81mm low, re drilled (Out of tolerance) S24 – 09 no. couplers 44-49mm low, re drilled (Not out of tolerance but likely to clash). All unused drilled holes have been filled with a resin injected piece of 40mm rebar.
| 03SR - Stations (RfL) | Cxxx-NCR-001788 | NCR | Damage to Shear studs on pile 16 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-06-08 | 2015-05-09 09:19 | -30 | 2015-04-27 11:41 | Civil - Civil Engineering General | 1500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | During Pile breakout operations on Pile 16, 12 no shear studs that were exposed at the bottom of the plunge column were found to have been damaged.
| 03SR - Stations (RfL) | Cxxx-NCR-001789 | NCR | Blockwork Lintel Bearing |  | Contr | COS | PAD - Paddington Station (West) |  | 2015-06-16 | 2015-06-15 15:40 | -1 | 2015-04-27 13:46 | Architectural - Brickworks/Blockworks | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | With reference to the lintels above the access hatch locations on the perimeter blockwork wall, the specification calls for the bearing blocks supporting the edge either side of the lintels to be full blocks. Some of the lintels installed on the Concourse level are not supported by full 440mm blocks.
| 03SR - Stations (RfL) | Cxxx-NCR-001790 | NCR | S6 HV trench concrete finish |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-09-24 | 2015-09-24 10:15 | 0 | 2015-04-28 08:48 | Civil - Civil Engineering General | 2100 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | In S06, there are blowholes/craters to the surface finish that is not upto the required standard for plain finish for formed surfaces
| 03SR - Stations (RfL) | Cxxx-NCR-001791 | NCR | P01 High couplers |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-06-28 | 2015-06-12 10:37 | -16 | 2015-04-29 13:30 | Structural Engineering - Reinforcement | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | It has been identified that plunge column pile reinforcing starter bars haves been cast high. – See attached Pile cage level survey. The worst case pile starter bar is 511mm higher than design. This additional height has resulted in the current detail of connecting a ‘L’ to gain the termination length impossible. This is due to fabrication constraints during the bending and threading of the ‘L’ bar. A bar cannot be bent and threaded with a short enough leg to enable to bar to be below the top mat reinforcing.
| 03SR - Stations (RfL) | Cxxx-NCR-001792 | NCR | S11 - Water Addition |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-06-30 | 2015-06-09 09:34 | -21 | 2015-05-01 08:46 | Structural Engineering - Reinforcement | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Procedure for adding water stipulates rate of addition should not exceed 1 in 20 loads. Document ref:Cxxx-SKC-C-STP-B071_WS077-50008 On pour S11 on 27/04/2015 20No. loads had water added out of a total of 86 loads which is 1 in 4 loads.
| 03SR - Stations (RfL) | Cxxx-NCR-001793 | NCR | S11 HV trench concrete finish |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-09-24 | 2015-09-24 13:16 | 0 | 2015-05-01 08:59 | Civil - Civil Engineering General | 5000 |  | Workmanship | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In S11, there are blowholes/craters to the surface finish that is not upto the required standard for plain finish for formed surfaces
| 03SR - Stations (RfL) | Cxxx-NCR-001794 | NCR | Design Co-Ordination & Integration between Elliptical Columns, Precast Slab Soffit, and Insitu Slab |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-07-31 | 2015-07-29 09:53 | -2 | 2015-05-05 14:11 | Civil - Civil Engineering General | 5000 |  | Design | Use As-Is | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | Following the Early Warning Risk Reduction Meeting held on Monday 27th April 2015 in response to EWN 1198, raise the following NCR: • Potential Insufficient insitu concrete cover to elliptical column reinforcement where the column connects to the slab soffit. This issue has become apparent following the uncovering of the slab couplers previously installed which form the connection between the slab and the column reinforcement, where there is encroachment of the precast soffit into the column reinforcement cover zone above the shadow gap. The couplers and precast are installed in line with the precast design DDCD Cxxx-SKC-O7-XCS-B071_WS077-50388, However the exact detail cannot be determined from the general arrangement drawings as there is no section through this area. From the initial surveys taken the minimum insitu concrete cover range between 5 and 46mm to the primary reinforcement. RFI reference Cxxx-RFI-002564
| 03SR - Stations (RfL) | Cxxx-NCR-001795 | NCR | BLL - Pile Defect |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-06-25 | 2015-06-17 17:20 | -8 | 2015-05-05 15:21 | Civil - Civil Engineering General | 5000 |  | Material | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After excavation down the side of the pile wall, a defect in P38 has been found. Currently under investigation.
| 03SR - Stations (RfL) | Cxxx-NCR-001796 | NCR | Grouting of magnetic extensometers beneath base slab |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-06-24 | 2015-06-18 09:27 | -6 | 2015-05-06 11:08 | Surveying - Instrumentation and Monitoring | 500 |  | Incomplete Works | Reject | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Three magnetic extensometers (ME) located beneath the base slab blinding level were not fully grouted with the potential for air voids to be left within the permanent works. The instruments were installed prior to the TBM tunnels for the purpose of measuring base heave during tunnelling and bulk excavation. During each excavation phase the instruments were damaged beyond repair with attempts made to recover the instruments at various stages in the project. Several NCR’s (Cxxx-NCR-000944, 001111, 001288, 001301, 001527) were issued at the time with a final FCD (Cxxx-FCD-001551) formed to replace the ME monitoring with heave monitoring of the base slab. ME-C12-13 (GL12) has since been lost beneath Base Slab S07 with no action taken to locate and clear the instrument for grouting. ME-C7-12 (GL02) and ME-C20-06 (GL22) were both uncovered over 15th/16th April 2015 with clay blockage observed within both instruments. Attempts were made to jet wash the blockage with a maximum of two meters cleared before the instruments pipes were grouted on 17th April 2015. See ‘Grouting Extensometer tubes’ attachment.
| 03SR - Stations (RfL) | Cxxx-NCR-001797 | NCR | S15 D-wall clay inclusion |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-07-12 | 2015-05-15 11:55 | -58 | 2015-05-13 09:57 | Civil - Civil Engineering General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Clay is running into D-wall panel S15 below blinding level. See attached photos which shows the affected areas.
| 03SR - Stations (RfL) | Cxxx-NCR-001798 | NCR | S16 D-wall Clay inclusion |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-07-12 | 2015-05-15 11:55 | -58 | 2015-05-13 10:03 | Civil - Civil Engineering General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Clay is running into the panel S16 below blinding level (See attached photos which shows area affected marked).
| 03SR - Stations (RfL) | Cxxx-NCR-001799 | NCR | S12 - Drilled and resined bars in D-wall |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-07-07 | 2015-05-15 11:57 | -53 | 2015-05-08 13:10 | Civil - Civil Engineering General | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In pour area 12, the D-wall panels couplers and blinding levels have been surveyed. It has been noted that some of the couplers are out of tolerance (+/- 50mm). Some D-wall panel couplers are within tolerance but have been assessed and deemed likely to clash with U-bars. The out of Tolerance D-walls are S60, S62 west, N62. While the D-wall panels that have couplers that are likely to clash are : S58 and N60.
| 03SR - Stations (RfL) | Cxxx-NCR-001800 | NCR | 12 Windposts installed with incorrect tie slots - Concourse Level Perimeter Blockwork |  | Contr | COS | PAD - Paddington Station (West) |  | 2015-05-21 | 2015-05-21 16:29 | 0 | 2015-05-07 13:16 | Architectural - Brickworks/Blockworks | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | 12 windposts have been installed on the Concourse Level (3 between E8-9, 3 between A15.5-17, 6 between E18-22) from the most recent delivery (Fri 01/05/15). These windposts have the slots (for the windpost ties) out of position. The slots should be 45mm from the front face of the windpost - which allows for the tie to sit in the centre of the blockwork. The slots on the 12 windposts are are further back from the front face, this leaves the tie to be at the very back of the block (110mm from the front face of the block). The windposts are being removed and reworked.
| 03SR - Stations (RfL) | Cxxx-NCR-001801 | NCR | S74 D-wall remedials |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-07-07 | 2015-05-21 16:28 | -47 | 2015-05-08 10:25 | Civil - Civil Engineering General | 2000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | At the base of the D-wall, there is a large clay inclusion. In addition there is also exposed rebars across the D-wall panel. This results in not being able to have a path along the D-wall to install the hydrophilic strip and the reinjector tube
| 03SR - Stations (RfL) | Cxxx-NCR-001802 | NCR | Weld procedure and competence records not made for the earthing welds as requested during a planned surveillance. |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2015-06-16 | 2015-06-15 17:57 | -1 | 2015-05-08 09:02 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | A planned surveillance was carried out on 17th April 2015 which looked pile connections to the continuous horizontal earth bar in base slab section S11. During the site visit it was detailed by both the Contractor and representatives that the welding to date had been undertaken and visually inspected by . A request was made for the documented welding procedure which was agreed to be provided by the Contractor forming part of the exit note sign off. Following multiple further requests no weld procedure was provided by the Contractor covering non structural welding. Material and Workmanship Specification In-Situ Concrete for Buildings, Cxxx – Paddington Station Main Works KF11, Cxxx-SWN-S-RSP-B071-00005 Rev 6 states under section KF11.3237 a) “…the welding procedure established by successful test welds shall be maintained and no departure from this procedure shall be permitted” and b) “Following the establishment of a satisfactory welding procedure, each welder to be employed on the Works shall carry out welder performance qualifications tests on reinforcing bars of the same metal and size as those on the Works”. Furthermore, BS EN ISO 17660-2:2006 Welding – Welding of Reinforcing Steel Part 2: Non Load-Bearing Welded Joints states under section 9.2 Welder and Operator Qualifications “The welders shall receive training on the welding of non load-bearing joints, and shall demonstrate that they are capable of producing acceptable joints” and section 10 Welding Procedure Specification (WPS) “Welding procedures shall be prepared in accordance with ISO 15609-1 or ISO 15609-5, as appropriate. However the WPS shall be supplemented with the additional essential parameters in Clause 11.” As no weld procedure or qualification records were provided by the Contractor following multiple requests, the competence of the welder and organisation could not be verified. If the welding has not been undertaken correctly, the welded joints could potentially fail whilst pouring and vibrating the concrete; additionally the long term durability and integrity of the welded joints for the earthing connections could be compromised; as such this NCR was raised.
| 03SR - Stations (RfL) | Cxxx-NCR-001803 | NCR | Damaged waterproofing (PREPRUFE) BLL Box |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2015-11-20 | 2015-11-02 14:26 | -18 | 2015-05-11 13:51 | Structural Engineering - Concrete Member | 5000 |  | Damaged | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Several areas of the __ sheets have been damaged during the BLL excavation, repair work will be required. Please note there are some areas where the repair will be difficult due to high damage between base slab and pile cut off level. Contractor to identify areas where __ is damaged and provide proposal for the repair.
| 03SR - Stations (RfL) | Cxxx-NCR-001804 | NCR | Base slab S15: Inconsistent Concrete at Plunge Column/Tension Piles P49, P50, P51 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-05-27 | 2015-05-21 14:47 | -6 | 2015-05-12 11:34 | Civil - Civil Engineering General | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During breakdown to cut-off level on plunge column/tension piles P49, P50, P51, the material encountered is inconsistent - particularly in the centre of the pile. An initial visual inspection would suggest there is an area of the pile with no aggregate present which appears to continue below the pile cut-off level.
| 03SR - Stations (RfL) | Cxxx-NCR-001805 | NCR | Sub-platform, Links around additional plunge coulmn shear studs |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-09-08 | 2015-06-05 11:50 | -95 | 2015-05-11 17:33 | Structural Engineering - Reinforcement | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Please see Cxxx-SWN-S-DDD-M171_7-05002 Cxxx-SWN-S-DDD-M171_7-05002 calls shear links to be added around plunge columns that have additional shear studs welded within the sub-platform slab. These links have not been incorporated sub-platform slabs poured to date. A breakdown of the plunge columns with additional shear studs is below. P01 – 30 shear studs required as per drawing C03, No shear studs welded and no shear links put around pile P10 – 20 shear studs required as per drawing C02, 26 welded on, Shear links to be installed. (4 studs damaged during excavation) P11 – 20 shear studs required as per drawing C02, 20 welded on, Shear links to be installed. P13 – 30 shear studs required as per drawing C03, 30 to be welded on, Shear links to be installed. P16 – 30 shear studs required as per drawing C02, 52 welded on, Shear links not installed. P17 – 20 shear studs required as per drawing C02, 28 welded on, Shear links not installed. P19 – 20 shear studs required as per drawing C02, 40 welded on, Shear links not installed. P22 – 20 shear studs required as per drawing C02, 20 welded on, Shear links not installed. P31 – 20 shear studs required as per drawing C02, 40 welded on, Shear links not installed. P32 – 20 shear studs required as per drawing C02, 20 welded on, Shear links not installed. P34 – 20 shear studs required as per drawing C02, 10 more added on drawing C03, 40 welded on, Shear links not installed. P35 – 20 shear studs required as per drawing C02, 10 more added on drawing C03, 36 welded on, Shear links not installed. P36 – 30 shear studs required as per drawing C03, 28 welded on, Shear links not installed. P38 – 20 shear studs required as per drawing C02, 0 welded on P39 – 20 shear studs required as per drawing C03, 0 welded on P41 – 50 shear studs required as per drawing C03, 50 to be welded on, Shear links to be installed. P51 – 20 shear studs required as per drawing C02, 0 welded on Note C03 and C04 drawings have not been issued yet, It is s knowledge these will be issued under RIR70 and RIR 71 respectively. changes on C04 are within the Bakerloo box and not taken into account in this NCR Please note - On plunge columns P16, P18, P22, P21, P34 and P36 4 No links have been installed on each pile as part of the elliptical column reinforcing.
| 03SR - Stations (RfL) | Cxxx-NCR-001806 | NCR | BLL 600dia Piles Defect - P24 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-08-20 | 2015-08-19 17:28 | -1 | 2015-05-18 18:33 | Structural Engineering - Concrete Member | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Further to Cxxx-NCR-001795, BLL 600dia P24, has some defective material, which bears a resemblance to P38, though to a lesser extent. As agreed during joint site inspection (CRL, URS, , __) on 08/05/2015, a small area has been broken out back to the reinforcement to assess the extent of this defective material.
| 03SR - Stations (RfL) | Cxxx-NCR-001807 | NCR | S07 - HV trench concrete finish |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-09-24 | 2015-09-24 13:16 | 0 | 2015-05-14 08:35 | Structural Engineering - Reinforcement | 2500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In S07, there are blowholes/craters to the surface finish that is not upto the required standard for plain finish for formed surfaces.
| 03SR - Stations (RfL) | Cxxx-NCR-001808 | NCR | Non conformance Architectural concrete finish, soffit BLL Box adit |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2015-09-18 | 2015-09-17 16:31 | -1 | 2015-05-14 11:02 | Architectural - Finishes | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As per drawing Cxxx-SWN-A-DDA-M171_7-31332, the finish of the BLL adit is "exposed concrete" which requires architectural finish. Cxxx-SWN-A-RSP-B071-00001 (Architectural Specification) JE80.1202 requires a "dense, even-coloured, blemish-free surface". After the BLL Box excavation completion it was found a decolouration in the concrete surface and misalignment of the shutters which does not comply with the requirements. Please find pictures attached.
| 03SR - Stations (RfL) | Cxxx-NCR-001809 | NCR | Walls T21 Starter bars |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-03-01 | 2016-02-27 11:31 | -3 | 2015-05-18 17:08 | Civil - Civil Engineering General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | With reference to RFI 001648 due to formation of temporary opening in wall T-21 for access bars have been cut/bent as follows: 1. 16No. (8 EF) 12mm kwickerstrip bars already pulled out have been cut. 2. 20No. (10EF) 12mm vertical wall starter bars bent
| 03SR - Stations (RfL) | Cxxx-NCR-001810 | NCR | Damage to P40 Pile head |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-06-30 | 2015-06-05 16:40 | -25 | 2015-05-18 17:05 | Civil - Civil Engineering General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the preparation of the pile head of P40 concrete from the cover zone of the pile has been broken above COL and the cover to the reinforcement reduced. See photo attached.
| 03SR - Stations (RfL) | Cxxx-NCR-001811 | NCR | BLL 600dia Pile 30 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-07-30 | 2015-07-23 11:34 | -7 | 2015-05-18 18:36 | Structural Engineering - Concrete Member | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | P30 was completed on the same day as P38 and shows some micro-cracking to the surface. However the extent of this appears to be very limited and is not believed to affect the pile below the surface or around the reinforcement. An area of the pile has been broken out (approx 5mm deep) around the micro-cracking. The cracks are no longer visible at this depth and sound concrete material is present.
| 03SR - Stations (RfL) | Cxxx-NCR-001812 | NCR | BLL 600dia Pile 42 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-08-24 | 2015-08-19 17:31 | -5 | 2015-05-18 18:40 | Structural Engineering - Concrete Member | 2000 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Further to Cxxx-NCR-001795, BLL 600dia P42, has some defective material, which bears a resemblance to P38, though to a lesser extent. As agreed during joint site inspection (CRL, URS, , __) on 08/05/2015, a small area has been broken out back to the reinforcement to assess the extent of this defective material. Additional inspection on 21/5/2015 showed additional defective material and honeycombing to the pile at approx. 102.360.
| 03SR - Stations (RfL) | Cxxx-NCR-001813 | NCR | BLL 600dia Pile 53 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-08-31 | 2015-08-19 17:33 | -12 | 2015-05-18 18:42 | Structural Engineering - Concrete Member | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | BLL P53 has a small area of honeycombing present from approximately 102.000mATD to COL. A joint site inspection between CRL, URS, & __ established that this was minor. The cover to the reinforcement has not been compromised and the surface material is not loose.
| 03SR - Stations (RfL) | Cxxx-NCR-001814 | NCR | BLL 600dia Pile 66 & 67 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-10-05 | 2015-06-29 14:28 | -98 | 2015-05-18 18:46 | Structural Engineering - Concrete Member | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | An area of BLL Piles P67 & P68 at approximately 100.100mATD shows some honeycombing. This honeycombing does not appear very severe, but may require patching, as discussed during joint site inspection on 08/05/2015. This material currently has limited access due to waler beam location, but it was agreed that this repair could be done at any point prior to completion of the lining wall in this area and does not affect the progress of the excavation or removal of waler beams and props.
| 03SR - Stations (RfL) | Cxxx-NCR-001815 | NCR | BLL 600dia Pile 96 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-10-07 | 2015-10-06 17:11 | -1 | 2015-05-18 18:47 | Structural Engineering - Concrete Member | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | An area of honeycombing is present on BLL Pile 96 from approximately 100.500mATD to 101.000mATD. This honeycombing was not deemed severe during the joint site inspection (08/05/2015.) However it was agreed that a cover survey would be carried out in order to establish whether the cover on this pile had been compromised, but it is not anticipated that this will be the case. No reinforcement is visible from the surface and material at the surface is not loose.
| 03SR - Stations (RfL) | Cxxx-NCR-001816 | NCR | BLL 600dia Pile 100 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-09-30 | 2015-09-16 15:45 | -14 | 2015-05-18 18:49 | Structural Engineering - Concrete Member | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | BLL P100 shows a horizontal ‘crack/line’ present at approximately 102.000mATD. This has the potential to be a cold joint. As agreed at joint site inspection (08/05/2015) a small area is to be broken-out to establish any presence of a cold joint.
| 03SR - Stations (RfL) | Cxxx-NCR-001817 | NCR | BLL 600dia Pile 112 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-09-25 | 2015-09-21 10:27 | -4 | 2015-05-18 18:53 | Structural Engineering - Concrete Member | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | P112 has an angular ‘line/crack’ present at approximately 102.000mATD. Due to the angle of this line and the use of self-compacting concrete in the construction of the piles, it is not believed to be a cold joint. However due to the close proximity of the installed angle bracket, safe investigatory breaking in the area is difficult at this time.
| 03SR - Stations (RfL) | Cxxx-NCR-001818 | NCR | BLL 600dia Pile 125 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-10-09 | 2015-10-06 17:11 | -3 | 2015-05-18 18:55 | Structural Engineering - Concrete Member | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Honeycombing is present on BLL 600dia Pile at approximately 101.000mATD. The cover to the reinforcement has not been compromised and the surface material present on this pile is not loose.
| 03SR - Stations (RfL) | Cxxx-NCR-001819 | NCR | BLL 600dia Pile 130 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-07-10 | 2015-07-08 14:43 | -2 | 2015-05-18 18:57 | Structural Engineering - Concrete Member | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There is some minor honeycombing present in the locations of the spacers on P130 at approximately 102.200mATD. This is present at this level only and limited in extent. Areas above the propping have been broken out and small voids have been discovered around the reinforcement and temporary works have been installed to allow for additional breaking. Inspection of piles below temporary propping has shown additional defective material on P130. This defect extends on the surface from 98.350mATD to 99.350mATD. There is also diagonal cracking present across the pile 99.150mATD and 98.450mATD.
| 03SR - Stations (RfL) | Cxxx-NCR-001820 | NCR | Damaged Concrete to Vertical Faces of BLL Excavation |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-08-20 | 2016-08-11 08:13 | -9 | 2015-05-18 19:07 | Civil - Civil Engineering General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Damaged edges to concrete to corner on GL D/13 and east wall GL B-D
| 03SR - Stations (RfL) | Cxxx-NCR-001821 | NCR | C7 Escalator Pit moved by 110mm |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-06-19 | 2015-05-21 16:30 | -29 | 2015-05-20 15:18 | Civil - Civil Engineering General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | With reference to previous NCR Cxxx-NCR-001325, regarding the escalator pit and the clash between the D-wall rebar cage and waling escalator beam. The NCR mentioned above stated that the escalator pit edge was to be moved by 70mm towards south due to the clash between the Waling beam and the D-wall panel N35. however, in order to satisfy Cxxx requirements of providing the minimum cover to the reinforcement in the slab as well as the cover to the D-wall reinforcement, the edge of the escalator pit had to be moved south by an additional 40mm. Therefore the escalator pit edge has been moved south by a total of 110mm, providing an escalator pit width of 965mm. This has been communicated back to the designers and __ the manufacturer, and the response was that the width is sufficient for the escalators and the minimum width required is 935mm (please see attached correspondence).
| 03SR - Stations (RfL) | Cxxx-NCR-001822 | NCR | S02 - Out of tolerance D wall couplers |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-06-23 | 2015-06-04 09:26 | -19 | 2015-05-26 10:32 | Structural Engineering - Reinforcement | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | When preparing the Sub-Platform D-Wall couplers some panels were found to be out of tolerance (+ -50mm). Where low couplers were found to clash with the bottom reinforcement these bars will need to be re-drilled. Furthermore due to difference in D-Wall and base slab tolerances some in-tolerance couplers will still clash with the bottom mat of reinforcement. For this reason any coupler 150mm or less from the top of blinding level (see attachment) needs to be re-drilled. This NCR covers Pour S02 with the following Panels affected: Panel S7 - The bottom row of 14no couplers are out of tolerance or are likely to clash, see below for details. S7 - 10 No. Couplers 50-75mm low (D-Wall out of tolerance) S7 - 4 no. couplers 47-50mm low, (D-Wall in tolerance but clash still likely) 12no couplers have been redrilled, 6 each side of the panel. A clash did occur and all 12 holes where used. Panel N8 - The bottom row of 14no couplers are out of tolerance, see below for details. N8 - 14 No. Couplers 58-70mm low (D-Wall out of tolerance) 12no couplers have been redrilled, 6 each side of the panel. A clash did not occur, the original bottom row of 14 couplers where used and resin injected dumpy bars used to fill the drilled holes. See DDCD, Cxxx-SKC-O7-XCS-B071_WS077-50382 for agreed comments.
| 03SR - Stations (RfL) | Cxxx-NCR-001823 | NCR | Decommissioning of IPI A12-09 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-07-29 | 2015-07-17 17:28 | -12 | 2015-05-26 11:26 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | In-place inclinometer IPI A12-09 stopped sending ground data following a permanent system error on 12th May 2015 (see attached plots). An investigation has been carried out by both the on-site monitoring engineers and database managers with both groups advising that the only remaining fix would be to remove the installation, thereby effectively decommissioning the installation due to the lengthy baseline period (six weeks). The IPI has previously suffered from technical glitches with four probes below 104.33m ATD switched off to eliminate bad data on 20/01/2015. The recent error is considered more significant as no probes are responding and only the signature ping of the transmitted is received by the monitoring database. The site maintenance engineers have move the transmitter inside the service chamber which previously has brought the instrument back on-line. However, after two attempts this method is no longer proving successful. Email communications with Datum are attached for additional information. The instrument is a ground IPI located between two D-wall IPI’s A10-11 and A13-13. Combining the previous reduction to the instrument length with the bottom four sensors set to faulty, casting of the adjacent base slab S08 ( 25th Feb 2015), and current excavation limited to the BLL below 102.56m, future ground data from this installation is considered non-beneficial to the project.
| 03SR - Stations (RfL) | Cxxx-NCR-001824 | NCR | S15 - North & South HV Trench Finish |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-09-24 | 2015-09-24 13:16 | 0 | 2015-05-28 08:37 | Structural Engineering - Finishes | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | S15 HV trench - Blowholes/craters to surface finish not to required standard for plain finish for formed surface.
| 03SR - Stations (RfL) | Cxxx-NCR-001825 | NCR | S12 - North HV Trench As built Levels |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-06-30 | 2016-05-13 08:13 | -48 | 2015-05-28 08:51 | Structural Engineering - Formwork | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | S12 North HV trench - 1) A localised area of the North HV trench as built level is low, up to -24mm. See as-built survey dated 18/05/15 attached. Cover has been achieved in the north west section of the HV trench. 2) Further to this, there are other areas of the HV trench with an as built level below -10mm of the design levels.
| 03SR - Stations (RfL) | Cxxx-NCR-001826 | NCR | S01 - North & South HV trench finish |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-09-24 | 2015-09-24 13:27 | 0 | 2015-05-28 09:05 | Structural Engineering - Finishes | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | S01, North & South HV trench finish - Blowholes/craters to surface finish not to required standard for plain finish for formed surface.
| 03SR - Stations (RfL) | Cxxx-NCR-001827 | NCR | S12 - North & South HV trench concrete finish |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-09-24 | 2015-09-24 13:27 | 0 | 2015-05-28 09:11 | Structural Engineering - Finishes | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | S12, North & South HV trench concrete finish - Blowholes/craters to surface finish not to required standard for plain finish for formed surface.
| 03SR - Stations (RfL) | Cxxx-NCR-001828 | NCR | S35 Initial Repair |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-09-01 | 2015-08-20 15:03 | -12 | 2015-05-28 15:55 | Structural Engineering - Diaphragm Walls | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | 4 repairs are proposed by with reference to NCR 1514, for the Diaphragm wall panel S35 at sub-platform. Repair 1: propose to remove timber stake embedded in wall and break out loose material covering a maximum area of 1300x500mm. This will involve removing loose material around the timber stake. do not expect the repair to go any deeper than 250mm from the surface of the panel. Repair 2: propose to break out loose material covering a maximum area of 1500x500mm. This will involve removing loose material at the soffit of the panel. do not expect the repair to go any deeper than 250mm from the surface of the panel. Repair 3: propose to break loose material covering a maximum area of 1300x500mm. This will involve removing loose material at panel surface. do not expect the repair to go any deeper than 200mm from the surface of the panel. Repair 4: propose to scabble loose material covering a maximum area of 2000x500mm. This will involve removing loose material on the panel surface. do not expect the repair to go any deeper than 250mm from the surface of the panel. Please advise any constraints.
| 03SR - Stations (RfL) | Cxxx-NCR-001829 | NCR | P50 Sandy material |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-06-15 | 2015-06-12 16:07 | -3 | 2015-06-01 10:47 | Civil - Civil Engineering General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On Pile 50 there is significant honeycombing in a bleed channel on the western face of the pile. The nature of this material is very porous and friable.
| 03SR - Stations (RfL) | Cxxx-NCR-001830 | NCR | Pile 47 sandy material |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-06-15 | 2015-06-03 16:19 | -12 | 2015-06-01 10:41 | Civil - Civil Engineering General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Upon inspection of Pile 47 it was found that there were localised areas of sandy and friable material making up the edges of the pile head on the north and eastern faces.
| 03SR - Stations (RfL) | Cxxx-NCR-001831 | NCR | P42 Sandy material |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-06-15 | 2015-06-03 17:25 | -12 | 2015-06-01 11:38 | Civil - Civil Engineering General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Upon final inspection of pile 42 COL it was discovered that there is a localised area of sandy and fraiable material on the north face of the pile.
| 03SR - Stations (RfL) | Cxxx-NCR-001832 | NCR | P43 sandy material |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-06-15 | 2015-06-05 13:02 | -10 | 2015-06-01 11:53 | Civil - Civil Engineering General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | upon inspection of Pile 43 COL it was discovered that were large areas of sandy friable material on the North and South edges of the pile. (Photos attached)
| 03SR - Stations (RfL) | Cxxx-NCR-001833 | NCR | P46 Sandy material |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-06-15 | 2015-06-03 16:26 | -12 | 2015-06-01 12:06 | Civil - Civil Engineering General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After breaking down P46 to 700mm below design COL as per NCR-001679 a small area of honeycombing in a bleed channel on the eastern face of the pile was discovered.
| 03SR - Stations (RfL) | Cxxx-NCR-001834 | NCR | Non acceptable repairs in BLL pile 24, 100, 112 and 125 |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2015-10-15 | 2015-10-13 13:56 | -2 | 2015-06-01 13:13 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Local break out was required in Pile 24, 100, 112 and 125 as per NCRs: Cxxx-NCR-001806, Cxxx-NCR-001816, Cxxx-NCR-001817 and Cxxx-NCR-001818. Grouting of the "square break outs" has not been carried out adequately and there is a hole between grout and concrete pile (some areas with main reinforcement exposed) which has been dry packed. The Construction joint has not been prepared and dry packing does not provide the assurance of getting the concrete around the reinforcement.
| 03SR - Stations (RfL) | Cxxx-NCR-001835 | NCR | No TW Certificate during P42 remedial works |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2015-06-29 | 2015-06-18 10:10 | -11 | 2015-06-01 13:19 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Non conformance material was found at the top of the pile (Cxxx-NCR-001812). As per previous NCR response, the removal of the defective material was required. To carry out the remedial works, the area needs to be supported below the repair area in order to prevent the movement of the pile during repair works. (ULS load 300 kN). The Contractor has failed to raise the TW before the beginning of the breaking activities and the remedial works have started without Temporary Works Design in place
| 03SR - Stations (RfL) | Cxxx-NCR-001836 | NCR | __ Wall __-L-101 : Wall cut for plant access for Mole Holes (__F-NCR-230) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-11-21 | 2015-11-09 16:06 | -12 | 2015-06-01 14:00 | Civil - Civil Engineering General | 2500 |  | Planning | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Wall __-L-101 was cut after construction due to plant access requirements to the mole holes. Reinforcement is flush with the cut line. Due to mobilization of crawler cranes and demobilization of TC1 and TC2 walls and slabs at __ and E__ levels are to be completed by 17/06/2015.
| 03SR - Stations (RfL) | Cxxx-NCR-001837 | NCR | DPC layer not installed flush with the face of block wall |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-07-25 | 2016-05-21 09:38 | -65 | 2015-06-01 15:11 | Architectural - Brickworks/Blockworks | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | For the perimeter block work wall on the Intermediate and Concourse levels, the DPC layer should be installed on the RC upstand flush up against the line of the face of the wall. There are some instances where the DPC has been installed not exactly flush, and recessed back 10mm in some places.
| 03SR - Stations (RfL) | Cxxx-NCR-001838 | NCR | S59 Initial repairs |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-08-29 | 2015-08-21 11:23 | -8 | 2015-06-02 11:31 | Structural Engineering - Diaphragm Walls | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | 4 repairs are proposed to with reference to NCR 1516, for the Diaphragm wall panel S59 at sub-platform. Repair 1 – propose to remove loose concrete with folds along concrete reinforcement to a maximum area of 900x1000mm. do not expect the repair to go any deeper than 250mm from the surface of the panel. Repair 2 – Repeat same method as above for same size area. Repair 3 – propose to remove loose material and check for voids along area to a maximum area to be 400x400mm. do not expect the repair to go any deeper than 250mm from the surface of the panel. Repair 4 – propose to remove material across full width of panel to break around already exposed reinforcement to a maximum area of 2600x3000mm. do not expect the repair to go any deeper than 250mm from the surface of the panel. Repair 5 – Repeat same method as above for same size area. Dimensions offset (o/s) from soffit of panel added to diagram as instructed. Please advise any constraints as per the attached diagram.
| 03SR - Stations (RfL) | Cxxx-NCR-001839 | NCR | S14 - Out of tolerance D Wall couplers |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-06-16 | 2015-06-15 11:12 | -1 | 2015-06-02 10:19 | Structural Engineering - Reinforcement | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | When preparing the Sub-Platform D-Wall couplers some panels were found to be out of tolerance (+ -50mm). Where low couplers were found to clash with the bottom reinforcement these bars will need to be re-drilled. Furthermore due to difference in D-Wall and base slab tolerances some in-tolerance couplers will still clash with the bottom mat of reinforcement. For this reason any coupler 150mm or less from the top of blinding level (see attachment) needs to be re-drilled. This NCR covers Pour S14 with the following Panels affected: Panel N75 - The bottom row of 10no couplers are out of tolerance, see below for details. N75 - 10 No. Couplers 50-53mm low (D-Wall out of tolerance) 8no. couplers have been redrilled, 6 each side of the panel. A clash did occur and all 8 holes where used. See DDCD, Cxxx-SKC-O7-XCS-B071_WS077-50382 for agreed comments.
| 03SR - Stations (RfL) | Cxxx-NCR-001840 | NCR | BLL - P48 Pile - Damage to links during remedial Works |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-08-24 | 2015-08-20 11:27 | -4 | 2015-06-02 12:05 | Civil - Civil Engineering General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During remedial works to P48 (ref NCR - 1812), the pile links have been damaged/bent. The damaged area is a cluster of 4no. links approx 400mm down from the underside of the slab above. The top link is bent in by approx 11mm, second by 7mm, 3rd by 5mm and the last by approx 3mm.
| 03SR - Stations (RfL) | Cxxx-NCR-001841 | NCR | Damage to PC34 and PC36 strain gauges |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-06-23 | 2015-06-24 14:30 | 1 | 2015-06-02 17:06 | Surveying - Instrumentation and Monitoring | 1500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | As a result of works to erect elliptical column steel around PC34 and 36, removed strain gauge combination G-H from the web of both plunge columns. The gauges were removed between the late afternoon of 01/06/2015 and morning of 02/06/2015.
| 03SR - Stations (RfL) | Cxxx-NCR-001842 | NCR | S05 - North & South HV trench concrete finish |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-09-24 | 2015-09-24 13:27 | 0 | 2015-06-02 17:50 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Blowholes/craters to surface finish not to required standard for plain finish for formed surface. Propose to repair finish defects to both base and sides of trench with Flexcrete Monolevel 844SP. __F to issue MCR for approval.
| 03SR - Stations (RfL) | Cxxx-NCR-001843 | NCR | S02 - North & South HV trench concrete finish |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-09-24 | 2015-09-24 13:32 | 0 | 2015-06-02 17:56 | Structural Engineering - Finishes | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Blowholes/craters to surface finish not to required standard for plain finish for formed surface. Propose to repair finish defects to both base and sides of trench with Flexcrete Monolevel 844SP. __F to issue MCR for approval.
| 03SR - Stations (RfL) | Cxxx-NCR-001844 | NCR | S05 - Incorrect use of spacers to HV trench |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-04-30 | 2016-04-12 16:28 | -18 | 2015-06-03 08:53 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Unapproved shims secured with tie wire used to the void former spacers to the HV trench. It was used in one location on the northern HV cable trench on the southwest corner 2m in from the S4/S5 construction joint. It was used to support the corner HV soffit formwork, as the lost cone system that’s supports the formwork was located too far from the edge causing it to dip and this point... The carpenters on the trench have recently arrived on site and were unaware of constraints of using unapproved materials in permanents works. Plastic shims were also installed on the HV sides were removed before the pour starts, has been located at the bottom was missed. There was no plastic shim’s as this was installed by a different, experienced chippy team.
| 03SR - Stations (RfL) | Cxxx-NCR-001845 | NCR | BLL - Pile 102 - Spacer protruding from pile |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-08-24 | 2015-08-20 10:30 | -4 | 2015-06-03 09:35 | Civil - Civil Engineering General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Pile 102 has a part of a spacer bar protruding from the pile surface approx 400mm down from soffit level.
| 03SR - Stations (RfL) | Cxxx-NCR-001850 | NCR | S03 - D-wall couplers not installed |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-08-08 | 2015-06-12 10:44 | -57 | 2015-06-09 15:35 | Structural Engineering - Diaphragm Walls | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | With reference to Cxxx-SKC-O7-XCS-B071_WS077-50382, it is permitted to miss 2 D-wall couplers per row. In Slab 3, the following D-wall couplers have been omitted. N11 due to clash with the D-wall 1 Top coupler 1 Middle coupler 1 bottom coupler N15 - damaged coupler 1 Top couplers
| 03SR - Stations (RfL) | Cxxx-NCR-001851 | NCR | Concrete defect west headwall (D-Wall panels: S1,W1,W4 and N1) |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2015-09-30 | 2015-09-21 10:29 | -9 | 2015-06-10 10:37 | Structural Engineering - Diaphragm Walls | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Several defects (clay inclusions and exposed reinforcement) have been found at the bottom of the D-Wall panels S1, W1, W4 and N1
| 03SR - Stations (RfL) | Cxxx-NCR-001852 | NCR | Concrete defect east headwall (D-Wall panels: S77,E1,E4 and N81) |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2015-10-28 | 2015-10-09 16:54 | -19 | 2015-06-10 10:40 | Structural Engineering - Diaphragm Walls | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Several defects (clay inclusions and exposed reinforcement) have been found at the bottom of the D-Wall panels S77, E1, E4 and N81
| 03SR - Stations (RfL) | Cxxx-NCR-001854 | NCR | S06 - PC20 box out |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-08-15 | 2016-07-26 13:16 | -20 | 2015-06-12 17:22 | Structural Engineering - Finishes | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Exposed reinforcement in undercut pocket at the perimeter of the temporary box-out for the plunge column removal. See attached photos.
| 03SR - Stations (RfL) | Cxxx-NCR-001856 | NCR | BLL - P106 Pile Defect |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-07-31 | 2015-07-01 16:08 | -30 | 2015-06-15 11:20 | Civil - Civil Engineering General | 1500 |  | Material | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Defective/honeycombed concrete has been found in P106.
| 03SR - Stations (RfL) | Cxxx-NCR-001857 | NCR | BLL - P69 Pile Defect |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-07-31 | 2015-07-01 16:12 | -30 | 2015-06-15 11:22 | Civil - Civil Engineering General | 1500 |  | Material | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Defective/Honeycombed concrete has been found in an area of P69.
| 03SR - Stations (RfL) | Cxxx-NCR-001858 | NCR | S13 - Out of tolerance D Wall couplers |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-06-29 | 2015-06-16 14:42 | -13 | 2015-06-15 12:03 | Structural Engineering - Reinforcement | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | When preparing the Sub-Platform D-Wall couplers some panels were found to be out of tolerance (+ -50mm). Where low couplers were found to clash with the bottom reinforcement these bars will need to be re-drilled. Furthermore due to difference in D-Wall and base slab tolerances some in-tolerance couplers will still clash with the bottom mat of reinforcement. For this reason any coupler 150mm or less from the top of blinding level (see attachment) needs to be re-drilled. This NCR covers Pour S13 with the following Panels affected: Panel S62 East - The bottom row of 8no couplers are out of tolerance, see below for details. S62 - 8 No. Couplers 90-98mm low (D-Wall out of tolerance) 7no. couplers have been redrilled, a clash did occur and all 8 holes were used. 7no. were redrilled as per DDCD, Cxxx-SKC-O7-XCS-B071_WS077-50382 .
| 03SR - Stations (RfL) | Cxxx-NCR-001859 | NCR | Elliptical Columns - Column C9 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-08-19 | 2015-08-06 13:04 | -13 | 2015-06-15 16:57 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Elliptical Columns Column C9 – Sub-platform to Concourse 3no B40 BM03 concourse soffit starter bars clash with the column links and compromise the main reinforcement cover. propose to omit the clashing bars in order to maintain cover. Please see attached Mark up drawing for clarification. A survey has been carried out on elliptical column C9 main reinforcement which show that the cover has been maintained apart from localised areas, however these areas will be dealt with on site to rectify by prior to installation of shutters and concrete pour. Please see attached survey for clarity.
| 03SR - Stations (RfL) | Cxxx-NCR-001860 | NCR | __ Slabs ES4, ES10, EN17, ES11 – Bent Bars |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-12-18 | 2015-12-15 13:58 | -3 | 2015-06-15 18:17 | Civil - Civil Engineering General | 2500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | ES4 GL B/8, ES10 & EN17 Stopend E of GL 16, ES11 GL B/16-17 Starter bars have been bent due to construction plant access requirements to the mole holes. Due to the demobilisation of TC1 and TC2 and the mobilisation of crawler cranes, __ and E__ walls and slabs are required to be completed.
| 03SR - Stations (RfL) | Cxxx-NCR-001861 | NCR | BLL Base Slab 2: inconsistent concrete in plunge column/tension piles P24, P25, P26 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-08-28 | 2015-08-26 12:49 | -2 | 2015-06-16 12:23 | Civil - Civil Engineering General | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Piles P24, P25 and P26 have been cored from above cut-off level, and the material encountered is inconsistent. A visual inspection of the cores would suggest there is an area of the pile with no aggregate present which appears to continue below the pile cut-off level. will proceed with investigation and reinstatement of the pile as proposed in Cxxx-SKC-S-RGN-B071_WS077-50030, then attach a supplementary pile record pack to this NCR containing test data relevant to these piles.
| 03SR - Stations (RfL) | Cxxx-NCR-001862 | NCR | BLL Base Slab 1: inconsistent concrete in plunge column/tension piles P27, P28, P29, P30 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-08-11 | 2015-08-07 11:55 | -4 | 2015-06-16 12:27 | Civil - Civil Engineering General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Piles P27, P28, P29 and P30 have been cored from above cut-off level, and the material encountered is inconsistent. A visual inspection of the cores would suggest there is an area of the pile with no aggregate present which appears to continue below the pile cut-off level. will proceed with investigation and reinstatement of the pile as proposed in Cxxx-SKC-S-RGN-B071_WS077-50030, then attach a supplementary pile record pack to this NCR containing test data relevant to these piles.
| 03SR - Stations (RfL) | Cxxx-NCR-001863 | NCR | East sump: inconsistent concrete in plunge column/tension piles P44, P45 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-09-24 | 2015-09-15 15:25 | -9 | 2015-06-16 12:32 | Civil - Civil Engineering General | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Piles P44 and P45 have been cored from above cut-off level, and the material encountered is inconsistent. A visual inspection of the cores would suggest there is an area of the pile with no aggregate present which appears to continue below the pile cut-off level. will proceed with investigation and reinstatement of the pile as proposed in Cxxx-SKC-S-RGN-B071_WS077-50030, then attach a supplementary pile record pack to this NCR containing test data relevant to these piles.
| 03SR - Stations (RfL) | Cxxx-NCR-001864 | NCR | Elliptical columns - Sub-platform to Concourse - C15 reinforcement |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-07-07 | 2015-07-06 09:38 | -1 | 2015-06-17 13:27 | Civil - Structural Engineering | 1500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Elliptical column GL15 - between Sub-platform and Concourse soffit. issue no 1: Due to steel congestion in the base slab and pile starter bars 1no BM02 B25 elliptical columns clash. 1no BM02 B25 starter bar has 40mm cover to the down pipe recess box before link is fixed. Proposal: To leave straight bar unengaged for the 600mm above slab level. The B20mm link would be fixed to the next main starter bar (please see sketch). The B25 bar can then be pulled back in to achieve cover. Issue no 2: Due to steel congestion in the concourse slab 1no BM03 B40 starter bar clash with column links and encroach cover zone. propose to omit clashing bar. Please see attached sketch for clarification
| 03SR - Stations (RfL) | Cxxx-NCR-001865 | NCR | S03- North and South: HV trench concrete finish |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-09-24 | 2015-09-24 13:32 | 0 | 2015-06-18 08:25 | Civil - Civil Engineering General | 2500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Blowholes/craters to surface finish not to required standard for plain finish for formed surface.
| 03SR - Stations (RfL) | Cxxx-NCR-001866 | NCR | __ Wall __-L-106 and __-T-84: Missing couplers and bent starter bars in DN17 slab |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-11-13 | 2015-11-11 15:53 | -2 | 2015-06-18 13:04 | Civil - Civil Engineering General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | 4 bent starter bars on corner of __-L-84 and DRl-L-106 and unable to locate 6 No.couplers in DN17 slab. Please see attached photos
| 03SR - Stations (RfL) | Cxxx-NCR-001867 | NCR | S04 - Dummy Bars and resined in bars |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-08-18 | 2015-06-25 13:19 | -54 | 2015-06-19 16:15 | Structural Engineering - Reinforcement | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please refer to drawing Cxxx-SKC-O7-XCS-B071_WS077-50382 that states that 2 couplers per row of 14 are permitted to be omitted In addition D-wall S 16, D-wall couplers are upto 81mm too low. Additionally in D-wall S19, a clash between the couplers and U-bars was likely. Holes have been drilled in to allow appropriate length bars to be resined in. S15 (partly in S03) - 5 couplers per row. Top – 1 coupler engaged, 2 drilled and resined in Middle – 2 couplers engaged, 2 drilled and resined in Bottom – 2 couplers engaged, 1 drilled and resined in S 16 west Top – 8 top couplers resined in Middle – 7 dummy bars resined in, 7 couplers engaged Bottom – 8 couplers engaged S16 east Top – 14 couplers engaged Middle – 12 drilled and resined in bars Bottom – 14 couplers engaged S19 Top – 12 couplers engaged Middle – 11 bars drilled and resined in Bottom – 12 couplers engaged N18 (10 couplers per row) Top – 9 couplers engaged Middle – 10 couplers engaged Bottom – 10 couplers engaged N21 – Bars clashing with S05 Construction joint Top – 14 top couplers engaged Middle – 13 couplers engaged Bottom – 13 couplers engaged
| 03SR - Stations (RfL) | Cxxx-NCR-001868 | NCR | N56 Initial repair |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-10-10 | 2015-10-01 09:39 | -9 | 2015-06-19 00:01 | Structural Engineering - Diaphragm Walls | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | 3 repairs are proposed by with reference to NCR 1515, for the Diaphragm wall panel N56 at sub-platform level, 104.310m AOD. Repair 1: propose to remove loose aggregate material to cover an area of 1.6x0.5m. Repair 2: propose to remove loose aggregate material to cover an area of 1.6x0.5m. Repair 3: propose to remove loose aggregate material to cover an area of 1.6x0.5m. do not expect the repair to go any deeper than 250mm from the surface of the panel. Please see attached diagram and advice any constraints.
| 03SR - Stations (RfL) | Cxxx-NCR-001869 | NCR | __ Wall __-T-49 : Missing starters in DS3 slab |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-10-31 | 2015-10-08 14:29 | -23 | 2015-06-19 18:31 | Civil - Civil Engineering General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | No starters detailed for the nib to the south of the doorway abutting wall __-L-31 please see attached
| 03SR - Stations (RfL) | Cxxx-NCR-001870 | NCR | BLL - P55 Defective Concrete |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-08-19 | 2015-08-12 14:11 | -7 | 2015-06-22 16:39 | Civil - Civil Engineering General | 1500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | A small section of honeycombing was found on P55. Propose to scabble the affected area and determine the extent of the defect. Defective concrete appears to be within the outer 20mm of concrete only Honeycombing was found to extend across an area approx. 400mm square, but defect continued around the side of the pile and could not be completely removed. Defective concrete appears to be within the outer 20mm of concrete only and no defects were found beyond this. A cover meter survey has been carried out and is attached. Minimum cover to main bars was found to be 58mm. See response below from __ regarding the issue of the reduced cover: BLL P55 – Reduced Nominal Cover Tension Pile Durability Durable concrete requires an appropriate combination of concrete quality and cover to reinforcement. The Crossrail requirements in this respect are set out in Section 3.8.4 of the Civil Engineering Design Standards (CEDS), Document CR-STD-303-3. The project specific requirements of the design are set out in Section KF11 of the Specification (Cxxx-SWN-S-RSP-B0710-00005 Rev 6.0) and Drg. No. Cxxx-SWN-S-DDL-M171_Z-00505 Rev C01. There is no distinction between Diaphragm Walling and Piling exposure classes for concrete made in KF11 although they have very different exposure conditions with the piles only exposed to the London clay. These ground conditions and pile locations essentially exclude any significant risk of carbonation or chloride attack and hence the carbonation class (XC3) and chloride class (XD2) of the concrete specified for the diaphragm walls is considered to be irrelevant for these piles. Cover to Reinforcement In the case of high yield steel, with no additional protection, the minimum cover (Cmin) to reinforcement is determined as the maximum of: • Cmin,b: Cover required to ensure full bond • Cmin,dur: Cover due to environmental conditions The nominal cover to the reinforcement (Cnom) is defined as Cmin + Δc and is specified as 75mm total in Drg. No. Cxxx-SWN-S-DDL-M171_Z-00505 Rev C01. BS EN 8500-1:2006; A3 notes that “The recommended values for minimum cover for durability have been chosen to give a low risk of the reinforcement becoming excessively corroded and requiring significant repairs before the end of the intended working life (design service life), on the assumptions that the designer has chosen a practical allowance for deviation, Δc, to add to the minimum value and that the level of workmanship on site is adequate to achieve the minimum cover.” The Crossrail CEDS Document (CR-STD-303-3: Table 3.8-g) requires that Δc should be 50mm for concrete cast against the ground in diaphragm walls and piles. Cover for Bond (BS EN 1992-1-1:2004; Table 4.2) The minimum cover for bond to individual bars is equal to the specific bar diameter. BLL pile P55 has a link diameter of 12mm (with the exception of a 16mm bunched double link located approximately 175mm below CoL) and maximum main vertical bar size of 40mm alternating with 32mm main bars. For bond purposes in the affected area 12mm cover to the links is adequate but the cover to the 40mm main steel needs to be 40mm (giving minimum cover to cage of 28mm, allowing for 12mm links) and 32mm to the 32mm main steel (similarly a minimum of 20mm, allowing for the 12mm link). Hence Cmin,b=28mm
| 03SR - Stations (RfL) | Cxxx-NCR-001871 | NCR | S72 Initial Repairs |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-09-30 | 2015-09-07 12:44 | -23 | 2015-06-24 12:56 | Structural Engineering - Diaphragm Walls | 2500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | propose the initial repairs to panel S72: Repair 1 – propose to remove sandy material from panel. Ensure a good blend of aggregate and cement is exposed. Maximum area to be 0.5mx1.2m. Repairs 2 – propose the same work method as above with maximum area to be 0.5mx1.4m. Repairs 3 – propose to remove sandy material and expose voids from reinforcement. Maximum area to be 0.5mx1.7m. Repairs will be to a maximum depth of 300mm. Please advise additional constraints.
| 03SR - Stations (RfL) | Cxxx-NCR-001872 | NCR | S74 Initial Repairs |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-08-31 | 2015-08-28 15:01 | -3 | 2015-06-24 13:00 | Structural Engineering - Diaphragm Walls | 2500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | propose the following repairs for panel S74: Repair 1 – propose to expose extent of voids in panel that show rebar. Ensure a good blend of aggregate and cement is exposed. Maximum area to be 0.840mx1.5m. Repairs 2 – propose the same work method as above with maximum area to be 0.840mx1.5m. Repairs 3 – propose the same work method in repair 1 above with maximum area to be 0.840mx1.5m. Repairs 4 – propose the same work method as above with maximum area to be 0.840mx1.5m. Repair 5 – propose to remove sandy material within in panel. Ensure good blend of aggregate and cement is exposed. Maximum area to be 0.8mx0.8m. Repairs will be to a maximum depth of 300mm. Please advise additional constraints.
| 03SR - Stations (RfL) | Cxxx-NCR-001873 | NCR | S13 - North and South: HV trench concrete finish |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-09-24 | 2015-09-24 13:32 | 0 | 2015-06-23 14:51 | Civil - Civil Engineering General | 2500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Blowholes/craters to surface finish not to required standard for plain finish for formed surface.
| 03SR - Stations (RfL) | Cxxx-NCR-001874 | NCR | ATS data loss 18th to 19th June 2015 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-07-14 | 2015-07-13 12:50 | -1 | 2015-06-23 15:42 | Surveying - Instrumentation and Monitoring | 500 |  | Software | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Following recent technical glitches with the I&M database, no ATS survey information was saved for a 36 hour period from 04:00hrs on Thursday 18th June to 16:00hrs on Friday 19th June. This extended period was compounded by the fact that the ATS equipment was reporting good accuracy and the morning I&M inspection on Thursday was up to date, therefore the error was not identified until Friday morning.
| 03SR - Stations (RfL) | Cxxx-NCR-001875 | NCR | Cavity Drainage Installation of 50mm Stainless Steel Spigot (IL1) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-08-20 | 2015-07-08 13:39 | -43 | 2015-06-24 11:04 | Civil - Drainage | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | This NCR is raised based on the close out of Cxxx-NCR-001215. The remedial repair as agreed in Cxxx-FCD-001355 states that the cast iron pipes installed in IL1 to act as down water pipes are not to the Cxxx specification Cxxx-SWN-M-RSP-B071-00001 Rev08, and the solution was to use as is and leave the cast iron pipes installed. As part of this and in order to allow connection of the later downpipe section, it was Implemented by __ on 14/02/2014 2:27 PM under the Work Task Notes on Cxxx-NCR-001215 to use sketch '140213 __ - IL1 NCR' produced by __ (attached). This sketch is captured in Detail B on drawing Cxxx-SKC-P-DDA-M171_4-41110. The work was carried out, but due to constraints on site the methodology to carry out the remedial repair to the 4No. damaged Cast-In Spigots on IL1 was changed. The red line drawing (Sketch in Relation to -RFI-000629 - Red Line Drawing) attached to Cxxx-NCR-001766 details the different repair procedure that was carried out instead by the subcontractor. The same repair method was used on IL 15 and IL1. In reference to the red line drawing, the epoxy resin used is called __ __ EP and is approved through MCR (Cxxx-SKC-O-TSC-B071_WS077-50150) and the fire grout used is called __ CP 611A and this is also approved through MCR (Cxxx-SKC-O-TSC-B071_WS077-50265). The screed installed for the cavity drainage and benching is approved through MCR (Cxxx-SKC-O-TSC-B071_WS077-50399). The tracker (Tracker Rev 5 - Cavity Wall Drainage (__ - 12.03.15)) attached identifies the Cast-In spigots this NCR refers to - DP05, DP06, DP07 & DP08.
| 03SR - Stations (RfL) | Cxxx-NCR-001876 | NCR | S14 - North and South: HV Trench Concrete Finish |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-09-24 | 2015-09-24 13:39 | 0 | 2015-06-24 13:20 | Civil - Civil Engineering General | 2500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Blowholes/craters to surface finish not to required standard for plain finish for formed surface.
| 03SR - Stations (RfL) | Cxxx-NCR-001877 | NCR | S04 - North and South: HV trench concrete finish |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-09-24 | 2015-09-24 13:40 | 0 | 2015-06-24 15:01 | Civil - Civil Engineering General | 2500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Blowholes/craters to surface finish not to required standard for plain finish for formed surface.
| 03SR - Stations (RfL) | Cxxx-NCR-001878 | NCR | Topflow Architectural SCC Mix- Water addition procedure and ITP |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-11-06 | 2015-10-21 16:18 | -16 | 2015-06-24 18:33 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Verification Problems - Inspection points not adequate | Completed |  | Sub-Platform : Columns C5N and C5S 1st lift and C16 1st lift Water added to ticket number 725758 and water and superplasticizer added to ticket number 725748 all under the direction of __ technician to ensure compliant consistency for SF2 class concrete. This is contrary to current documentation for the elliptical columns: ITP for elliptical columns Cxxx-SKC-C-ITP-B071_WS077-50091 rev 1 ITP item 43 states no water addition for SCC concrete Procedure for adding water to concrete Cxxx-SKC-C-STP-B071_WS077-5008 rev 1. Water addition procedure does not cover SCC concrete. Additional cube sets taken for both loads where on site additions occurred
| 03SR - Stations (RfL) | Cxxx-NCR-001879 | NCR | P24 Lifting Band - Band Level High |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-07-23 | 2015-07-01 16:53 | -22 | 2015-06-25 11:55 | Structural Engineering - Concrete Member | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Upon breakdown to COL of P24 it was discovered that the lifting band was up to 70mm above deign COL, 97.895mATD at its highest point. It was cut out to avoid any clashes with base slab reinforcement to be fixed in the area. This pile is not a designated earthing pile.
| 03SR - Stations (RfL) | Cxxx-NCR-001880 | NCR | S07 - Low cover to clamps in S07 North |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-08-13 | 2015-07-14 10:02 | -30 | 2015-06-25 14:08 | Structural Engineering - Structural Engineering - General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | 16 No. Bulldog clamps were used in the North side of S7 pour to secure the sides of the HV trench. The location was determined as it was connected to the D’ Wall dowel bars for added strength. These were attached to the T1 layer and have resulted in very localized reduction of cover in 8 locations. See attached survey (__F-NCR-245_survey.pdf ). Survey readings are taken to the highest point of the clamps which were fitted with the bolts running horizontally. The bolts are all steel galvanized. See attached Photo of clamps before pouring. surveyed the easting, northings and levels of each bolt prior to the pour. (S07 Bolt survey.pdf ) This data has been overlaid onto as built slab level survey to identify if low cover to the bolts had occurred. (__F-NCR-245_survey.pdf )
| 03SR - Stations (RfL) | Cxxx-NCR-001882 | NCR | Column C7 south - missing coupler (base slab) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-07-29 | 2015-07-28 16:41 | -1 | 2015-06-29 16:25 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Column C7 South. It would appear that the corner coupler was not installed in the soffit of the concourse slab for the sub platform column. See attached drawing Qty =1 Size B20
| 03SR - Stations (RfL) | Cxxx-NCR-001884 | NCR | Departures Road Level Wall __-L-105 : Missing coupler in DN17 slab |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-09-27 | 2015-09-24 15:31 | -3 | 2015-06-29 17:48 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Missing B16 coupler in DN-17 for __-L-105 wall starter. See attached photo
| 03SR - Stations (RfL) | Cxxx-NCR-001885 | NCR | Self compacting concrete on-site training (slump/flow) not carried out by a UKAS accredited laboratory |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2015-09-28 | 2015-09-09 09:45 | -19 | 2015-07-02 13:58 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Training Deficiency - Insufficient practice or hands -on experience | Completed |  | During a planned Crossrail surveillance dated 12th June 15 it was noted that on-site self compacting concrete testing was being undertaken by __ personnel, as accepted under RFI 00839. It was detailed during the visit that the personnel undertaking the testing had been trained by UKAS accredited laboratory __ Limited. On review of __ Limited’s UKAS schedule of accreditation (no. 0478) it was noted that the organisation is not UKAS accredited to undertake slump-flow testing, therefore the training provided to site personnel had not been undertaken by UKAS trained personnel.
| 03SR - Stations (RfL) | Cxxx-NCR-001886 | NCR | Fresh fibre testing not being undertaken on site as required by specification KF11.2208 |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2015-12-31 | 2015-12-10 11:04 | -21 | 2015-07-02 14:02 | Civil - Civil Engineering General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient surveillance of subcontractors | Completed |  | During a planned Crossrail surveillance dated 12th June 15, a review of the Contractors on-site testing activities was undertaken in accordance with the requirements set out within In-Situ concrete specification KF11. Materials and Workmanship Specification In-Situ Concrete KF11 clause 2208 states “The polypropylene fibre content of the concrete shall be tested by collecting the fibres from a sample of 10 litres of fresh concrete” and “The testing and sampling rate during continuous production shall be 1 test/ week”. A request was made for evidence of compliance to the aforementioned clause through fresh fibre test records, or documented acceptance of a relaxation from the specification through an accepted RFI or FCD. Following the request it was detailed by the Contractor that the test was not being undertaken for the column construction by either the supplier (__) or , and that no accepted relaxation currently existed within the eB system. To ensure appropriate corrective actions are implemented this NCR was raised.
| 03SR - Stations (RfL) | Cxxx-NCR-001887 | NCR | P30 External Bleed Channel |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-07-29 | 2015-07-14 08:52 | -15 | 2015-07-02 17:37 | Structural Engineering - Concrete Member | 1500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Excavation around P30 has showed 2No. external bleed channels on the North West of the pile. This has been broken locally, down to the level of blinding within the localised excavation. The defective material does not extend to the steel reinforcement, but appears to stop around 20mm from the links. The blinding has been removed locally to see the extent of the defect below this level. This shows that the defect, though continues below this level, is not of a greater extent at the lower level.
| 03SR - Stations (RfL) | Cxxx-NCR-001888 | NCR | ATS Data loss due to GEOMOS issues |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-08-11 | 2015-08-04 17:44 | -7 | 2015-07-02 16:47 | Surveying - Instrumentation and Monitoring | 500 |  | Software | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | On 26th June 2015, one of the two Geomos servers (GEO2) used to store and process ATS data reached its storage limit. The software does not give any notification that the storage limit has been breached, or warnings that the limit is being reached. Therefore it is only possible to observe that the storage limit has been breached by observing that data is not being processed. The storage limit was reached on a Friday night (26/6) and could not be rectified until the following Monday. Data was archived to free up some storage, and data began processing again from 30th June. the attached graph on shows the period of outage in the period 26/6 to 30/6. It should be noted that noted this only affected prisms outside of the NR station. Prisms inside the station are processed on GEO1 server.
| 03SR - Stations (RfL) | Cxxx-NCR-001889 | NCR | BLL - __ - L-104 Damaged Couplers in DN26 slab |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-12-18 | 2015-10-27 11:39 | -52 | 2015-07-03 07:47 | Civil - Civil Engineering General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 2 No. B16 couplers in DN26 slab are damaged . Starter bars for Wall __-L-104. Couplers detailed on Drg Cxxx-SKC-C-DWG-B071_WS077-50562
| 03SR - Stations (RfL) | Cxxx-NCR-001890 | NCR | BLL - __ - Cabinet Recess Walls - 2no. missing couplers in DN26 slab |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-11-13 | 2015-11-04 14:10 | -9 | 2015-07-03 07:50 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 2 No. missing B16 coupler in DN-26 for cabinet recess wall starters. Starters detailed on Cxxx-FCD-001154
| 03SR - Stations (RfL) | Cxxx-NCR-001891 | NCR | Sonic Logging Tubes within Tension Piles W/O grout at BLL slab level P28 |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2015-07-31 | 2015-07-27 14:56 | -4 | 2015-07-03 14:44 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | 4 number sonic logging tube within pile P28 were found to be without grout, identified during pile surface material inspection.
| 03SR - Stations (RfL) | Cxxx-NCR-001892 | NCR | West Liner Wall - Base Slab - Damaged & Clashing couplers |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-11-13 | 2015-10-30 11:45 | -14 | 2015-07-07 09:41 | Civil - Civil Engineering General | 1500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | 1. B20 Bar mark 28 cast in couplers, 8No at the present survey are damaged and unable to thread. propose to drill and fix (using __ Hit 500) new 20mm L-bars with a minimum 650mm embedment. 2. a number of B20 BM28 L bars clash with one another and construction joints. propose to thread a straight bar and drill and fix a new L-bar using hilti Hit 500 (minimum Lap length to be maintained) please see attached sketch and photos for clarity.
| 03SR - Stations (RfL) | Cxxx-NCR-001893 | NCR | West Liner Wall - Base Slab - North Section |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-12-18 | 2015-11-25 10:51 | -23 | 2015-07-07 13:57 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | 1. North D/wall cast in couplers are out of tolerance 25No. NF1 have 0mm cover & 10No. have approx. 30mm cover 2. Due to constrains of the D/wall cast in couplers FF1 are cast too far inside the wall, the threaded FF1 lacer bar to West liner wall BM 19/ BM13/ BM10/ BM 16/ will require to be fixed on the inside, as shown on sketch.
| 03SR - Stations (RfL) | Cxxx-NCR-001894 | NCR | East Liner wall - Base slab - damaged & clashing couplers |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-11-30 | 2015-11-27 16:21 | -3 | 2015-07-07 14:32 | Civil - Civil Engineering General | 1500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | 1. on East liner wall following a survey of the threaded female couplers cast in the D-wall, its found that 9 number cast in couplers are damaged and need to be replaced (BM28). propose to drill and fix (using __ hit 500) new 20mm L-bar with a minimum embedment of 650mm. 2. 9no BM28 B20 L-bars clash with construction joints, propose to cut bob and splice the straight bar with a drilled and fixed (using __ Hit 500) B20 L-bar, minimum lap length will be maintained.
| 03SR - Stations (RfL) | Cxxx-NCR-001895 | NCR | East Liner wall - base slab - BM05 vertical bars |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-11-13 | 2015-10-30 11:52 | -14 | 2015-07-07 15:02 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | East Liner wall GL24/D, 3 no BM05 vertical bars cannot be engaged. couplers are cast out of tolerance. propose engage the two extra couplers cast in the soffit slab and lap with base slab starters. drill and fix 2no B25mm starter bars to lap with the unengaged B32 vertical bar.
| 03SR - Stations (RfL) | Cxxx-NCR-001896 | NCR | East Liner wall - Base Slab - Lacer couplers out of tolerance |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-12-01 | 2015-11-27 16:29 | -4 | 2015-07-07 15:16 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | East Liner wall, South and north D-wall, couplers are cast in out of tolerance. Due to constrains of the D/wall cast in couplers, FF1 cast in too far inside the wall, the threaded FF1 lacer bar to East liner wall BM 19/ BM13/ BM10/ BM 16/ will require to be fixed on the inside, as shown on sketch.
| 03SR - Stations (RfL) | Cxxx-NCR-001897 | NCR | East liner wall - Base slab - Out of tolerance couplers |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-12-10 | 2015-12-10 11:06 | 0 | 2015-07-07 15:28 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | 1. North D/wall cast in couplers are out of tolerance 16No. NF1 have 0mm cover & 13No. have approx. 30mm cover 2. 12no couplers cast in concourse soffit lack cover. 3no north section above tunnel eye and 9no on south section above tunnel eye.
| 03SR - Stations (RfL) | Cxxx-NCR-001898 | NCR | P26 Honeycombed Area |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-08-31 | 2015-08-20 14:14 | -11 | 2015-07-08 10:44 | Structural Engineering - Concrete Member | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | An area on the West of P26 had honeycombing to the area just inside the steel reinforcement cage. The material in this area has some loose coarse aggregate and sand within it. A 350 X 320mm area was broken at the surface level of 96.500mATD. This defect has been followed down and the area reduces in size going lower. At the Limit B breakout (an exclusion zone has been put in place with loading materials removed to facilitate this prior to breaking past limit A) the broken out area is approx. 70mm X 160mm and still has some material with looser aggregate and higher concentrations of sand.
| 03SR - Stations (RfL) | Cxxx-NCR-001899 | NCR | Elliptical Column Flared Head Cover |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-10-16 | 2015-10-08 11:39 | -8 | 2015-07-09 08:38 | Civil - Civil Engineering General | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | __ flared head columns Grid Line 10 to 14 Issue 1. It has been found that some of the starter bars and couplers do not meet the cover requirement as per the specification. On Departure road level soffit level there is no cover to six couplers north and south faces of the flared head C10 to C14. It would appear that the 50mm shadow gap was not allowed for. Issue 2. It was found that a number of threaded bars in the __ soffit clash with the Plunge column steel plate corner. the clash prevents the couplers from fully engaging the bar. please see attached photos.
| 03SR - Stations (RfL) | Cxxx-NCR-001900 | NCR | Concrete pour Concourse level C5 N&S, C4 N |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2015-08-10 | 2015-07-28 14:42 | -13 | 2015-07-13 17:11 | Structural Engineering - Concrete Member | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Concrete pours were planned for Monday 13th July on columns at concourse level on grid lines C4 and C5. No Inspection Request Forms were issued to CRL to witness the appropriate intervention points. This is in contravention of the Works Information, and may be a contributory factor in the observations made on site that the wrong concrete was to be placed in the shutters.
| 03SR - Stations (RfL) | Cxxx-NCR-001901 | NCR | S03 - Earthing Pit connection details |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-10-20 | 2015-09-28 10:39 | -22 | 2015-07-14 15:44 | Structural Engineering - Formwork | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | The boxout for the earthing pit connection were installed as 250mm x 250mm x 150mm and not as detailed as 300mm x 300mm x 150mm
| 03SR - Stations (RfL) | Cxxx-NCR-001902 | NCR | Damp Proof Course Damaged in low-level cavity infill sections |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-06-30 | 2016-05-13 09:48 | -48 | 2015-07-15 16:57 | Architectural - Brickworks/Blockworks | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | In some areas the Damp Proof Course (DPC) which sits on top of the concrete upstand within the block work wall has shown signs of damage in the openings where blocks have been left out intentionally so the cavity can be cleaned prior to closing. The damage to the DPC looks to be holes where it has had some sort of abrasion. This is particularly on the Concourse level west end north side, however there are other areas as well.
| 03SR - Stations (RfL) | Cxxx-NCR-001903 | NCR | Intermediate level - C2N Structural Column Cover |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-09-24 | 2015-09-24 14:59 | 0 | 2015-07-15 18:35 | Structural Engineering - Reinforcement | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | C2N- structural column on intermediate level a number of couplers on the south and east face of the column are cast out of position, therefore compromise the required 50mm concrete cover to main reinforcement. Please see attached sketch for clarification.
| 03SR - Stations (RfL) | Cxxx-NCR-001904 | NCR | Sub-platform Column C23-S damage to slab connection coupler |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-09-30 | 2015-09-24 14:13 | -6 | 2015-07-17 17:06 | Civil - Structural Engineering | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | One of the corner couplers at the base connection of column reference Sub-platform C23-S has been damaged during the steel-fixing installation, and as a result can no longer be used for coupling a threaded B20 bar. This is likely as a result of the coupler itself being out of tolerance and in an attempt to pull the B20 Bar inward to maintain correct concrete cover, the coupler has cracked and no longer able to be used. In addition to this, the bottom 2 levels of B16 U-bar stringer was each replaced by 3no. B10 U-bar stringers to deal with the reduced cover. This was approved as a solution on another column elsewhere, however approval/confirmation is also required for this column if this is to be used.
| 03SR - Stations (RfL) | Cxxx-NCR-001905 | NCR | S13 - 28 day cube strengths |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-09-30 | 2015-09-14 16:54 | -16 | 2015-07-17 17:11 | Structural Engineering - Structural Engineering - General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | With reference to the attached conformity table for S13 cube results: 1. 1 individual 28day cube result (cube 1822) achieved 40.9N/mm2 which is less than 41N/mm2 (f ck -4) 2. For cubes 1817-1822 the mean of 6 results =46.4 N/mm2 which is less than 47N/mm2 (f ck +2)
| 03SR - Stations (RfL) | Cxxx-NCR-001906 | NCR | Precast Unit FS-47 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-08-28 | 2015-08-07 11:57 | -21 | 2015-07-22 08:36 | Structural Engineering - Pre-cast | 1500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper storage of material | Completed |  | Precast unit ref. FS-47 (cast at __ 17-07-2015) was inspected during unloading at undercroft and 2 No. chipped edges identified. Damage was not identified during post pour inspection at __ and it is expected that the damage has occurred during loading / unloading between locations. Units were stacked on timber bights with ‘bubbled’ pads during transport although it has since been established that the protection measures employed for earlier precast works were enhanced with rubber ‘D’ bands and white neoprene sheet over timber bights.
| 03SR - Stations (RfL) | Cxxx-NCR-001907 | NCR | Eliptical column C11 - Concourse base couplers surveyed to be out of position resulting in reduced cover |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-10-16 | 2015-10-08 11:17 | -8 | 2015-07-27 18:01 | Civil - Structural Engineering | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please refer to the attached survey of the couplers at the base of elliptical column C11 at concourse level, and the amount of concrete cover achievable for each vertical bar. Due to some of the couplers position, there are some sections along the north face which will achieve less than 40mm of cover if the 20mm outer lacer rebar is installed as per the design. The subcontractor has therefore suggested replacing each of 20mm diameter outer lacer rebar with 4no. 10mm diameter rebar (see attached photo). Also, for the worst case survey reference rebar 'no.29' the 4no. 10mm lacers have been installed on the inside face because even with the 10mm lacers it would only achieve 30mm of cover. Note that this is only for the bottom four rows of lacers, as the vertical bars can be cranked into within tolerance above the bottom four rows.
| 03SR - Stations (RfL) | Cxxx-NCR-001908 | NCR | Concourse A6-7 Blockwork Wall Vertical Joint Cracking |  | Contr | COS | PAD - Paddington Station (West) |  | 2016-05-30 | 2016-05-13 11:10 | -17 | 2015-07-29 16:17 | Architectural - Brickworks/Blockworks | 1000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Vertical cracking from the soffit of Concourse level at the joints of the "dogleg" of the South wall (A6-7) has been observed. On the Western joint, the crack extends a short distance from the soffit - whereas the Eastern joint extends to eye level. Other sections with similar joints have been inspected and no other instances of cracking have been observed.
| 03SR - Stations (RfL) | Cxxx-NCR-001909 | NCR | S03 – Starter bars for Wall SPL-L-06 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-03-30 | 2016-03-29 14:04 | -1 | 2015-07-31 07:46 | Structural Engineering - Structural Engineering - General | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Slab S03 wall, column starters reinforcement drawing Cxxx-SKC-C-DWG-B071_WS077-51803 C01 has Ferbox scheduled at 210mm for wall SPL-L-06 for a 300mm wall. This has been installed. GA drawing Cxxx-SWN-S-DDA-M171_6-01522 rev 09 (current at time of slab construction) and latest rev 10 shows a 200mm wide wall.
| 03SR - Stations (RfL) | Cxxx-NCR-001910 | NCR | Eliptical Column CL13 (4th lift Concourse Level) base couplers out of position |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-10-24 | 2015-10-21 10:49 | -3 | 2015-07-30 15:49 | Civil - Structural Engineering | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Please refer to the attached survey of the couplers at the base of elliptical column C13 at concourse level, and the amount of concrete cover achievable for each vertical bar. Survey Coupler reference 'no.11' shows only 52mm from the outside face of the concrete column to the vertical rebar, so when the horizontal lacers are installed there will be less than 50mm of cover in this location. note that the bar can be cranked inwards so this only affects the bottom row of lacers.
| 03SR - Stations (RfL) | Cxxx-NCR-001911 | NCR | Eliptical Column CL14 (4th lift Concourse Level) base couplers out of position |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-09-26 | 2015-09-25 15:45 | -1 | 2015-07-31 16:48 | Civil - Structural Engineering | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Please refer to the attached survey of the couplers at the base of elliptical column C14 at concourse level, and the amount of concrete cover achievable for each vertical bar. Survey Coupler reference 'no.1' , 'no.7-9' , 'no.19-32' shows less than a 50mm concrete cover when the 20mm links will be installed. note that the bars can be cranked inwards and this affects the bottom 5 rows of lacers.
| 03SR - Stations (RfL) | Cxxx-NCR-001912 | NCR | Unaproved plastic shims used in the Bakerloo base slab S01 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-08-21 | 2015-08-20 11:50 | -1 | 2015-07-31 09:39 | Civil - Civil Engineering General | 1000 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Unapproved shims secured with tie wire were used to support the four corners of shuttering used to form the lift pit in S01 __l slab.
| 03SR - Stations (RfL) | Cxxx-NCR-001913 | NCR | Lack of cover to C15 and C16 elliptical column |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2015-08-28 | 2015-08-19 17:48 | -9 | 2015-07-31 15:25 | Structural Engineering - Concrete Member | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Further to EWN-1198, PMC-2041 and NCR-1899, it was identified onsite that female couplers cast in intermediate slab for elliptical column C15 and C16 did not achieve the minimum cover required. The affected area of low cover is the section between 117.150-117.310 (within the depth of PC panel).
| 03SR - Stations (RfL) | Cxxx-NCR-001914 | NCR | Elliptical Column C16, concourse level - Cover issue |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-10-17 | 2015-10-08 11:22 | -9 | 2015-08-01 17:49 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Concourse Level: Elliptical Column : GL C/16 Drawing Cxxx-SWN-S-DDD-M171_4-01548 C03 Cxxx-SKC-C-DWG-B071_WS077-51689 Rev. C03; Elliptical column C16 Elliptical column does not meet the required cover of minimum 50mm as detailing drawings and Cxxx acceptance of min. 40mm. Due to congestion of steel in slabs the coupled starter bars had to be moved to suit encasing the starter bars out of position.
| 03SR - Stations (RfL) | Cxxx-NCR-001915 | NCR | chipped chamfers on Elliptical Columns |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-08-20 | 2016-07-16 11:45 | -35 | 2015-08-03 18:09 | Civil - Base Course | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | On striking the top lift of C11 and C16 (below concourse), the chamfer has chipped away
| 03SR - Stations (RfL) | Cxxx-NCR-001916 | NCR | Intermediate Level – Columns C2-N&S, C3-N&Sand C22-N&S (NCR-259) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-10-23 | 2015-10-08 13:32 | -15 | 2015-08-04 09:33 | Structural Engineering - Reinforcement | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Drawing Number: Cxxx-SKC-C-DWG-B071_WS077-51764 Rev. C01. In columns C2-N&S, C3-N&S and C22-N&S, the coupler/starter bars were cast out of position due to congestion of steel within the slab. therefore, the links have been replaced to gain sufficient minimum cover to the column reinforcement in these areas. This has been agreed with CRL and the solutions have been implemented.
| 03SR - Stations (RfL) | Cxxx-NCR-001917 | NCR | Concourse Level: Elliptical Column C15 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-10-10 | 2015-10-05 14:29 | -5 | 2015-08-04 10:18 | Structural Engineering - Reinforcement | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Drawing Cxxx-SWN-S-DDD-M171_4-01548 C03 Cxxx-SKC-C-DWG-B071_WS077-51689 Rev. C03; Elliptical column C15 Due to steel congestion in concourse slab, starter bars are cast out of position. 1. One starter bar encroach the elliptical column cover zone, thus 40mm minimum cover to the links cannot be achieved. 2. Double hook 28No. B16 BM 16 cut and lapped due to vertical bars cast out of position.
| 03SR - Stations (RfL) | Cxxx-NCR-001918 | NCR | Intermediate level column – C22-S, Bars drilled for nib (NCR-263) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-10-03 | 2015-09-29 15:36 | -4 | 2015-08-04 11:06 | Structural Engineering - Reinforcement | 1500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The nib for the doorway on column C22-S at intermediate level was not cast due to Nib details being absent from the steel detail drawing.
| 03SR - Stations (RfL) | Cxxx-NCR-001919 | NCR | Intermediate level – Square Column - C22N, Drilled Bar (NCR-264) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-10-31 | 2015-10-30 11:27 | -1 | 2015-08-04 11:33 | Structural Engineering - Reinforcement | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | C22-N square column at the intermediate level has 1No starter bar missing in the soffit.
| 03SR - Stations (RfL) | Cxxx-NCR-001920 | NCR | Concourse Level – Poor Finish to walls CL-L-35 and CL-L-37 (NCR-266) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-10-17 | 2015-10-08 11:41 | -9 | 2015-08-04 12:12 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Excess of surface blow holes and water scour not acceptable for Plain Finish (Spec cl KF11.1308) Refer attached photographs and location plan for details.
| 03SR - Stations (RfL) | Cxxx-NCR-001921 | NCR | SPL T-04 starter bars |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-10-10 | 2015-10-08 13:48 | -2 | 2015-08-04 12:20 | Structural Engineering - Reinforcement | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | With reference to RFI Cxxx-RFI-002740 Structural Wall T-04 GL8 The structural wall (T-04) base slab starter bars have been cast in as B16 BM111 as per RC detail (drawing number Cxxx-SKC-C-DWG-B071_WS077-51814 C02). However, Cxxx's intent shows the starter bars for the structural wall as B25 (Drawing Number Cxxx-SWN-S-DDD-M171_Z-57720 C03).
| 03SR - Stations (RfL) | Cxxx-NCR-001922 | NCR | Self Compacting Concrete Mix 285 (MCR 50031) – 2hr Placement Time exceeded (NCR-267) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-10-03 | 2015-09-28 11:20 | -5 | 2015-08-04 12:45 | Structural Engineering - Structural Engineering - General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Specification Clause KF11.3221. - 2hr time limit from batching to end of placement exceeded. Details of the pours relating to this are as follows. 1) Date:17/07/2015 ¦ Ticket No.813092 ¦ Location: C2 N&S 2nd lift (CL) and C22N&S 1st Lift (CL) ¦ 2hr 38mins from batching to end placement 2) Date:21/07/2015 ¦ Ticket No.813269 ¦ Location: C4 N&S C5N&S (IL) ¦ 2hr 13mins from batching to end placement
| 03SR - Stations (RfL) | Cxxx-NCR-001923 | NCR | SPL T-05 starter Bars |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-10-03 | 2015-09-25 11:41 | -8 | 2015-08-04 17:15 | Structural Engineering - Reinforcement | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Issue 1. Due to the clash with the plunge column the structural Wall T-05 starter bars at SPL are cast out of position. Therefore, the wall lack cover on west side as the starter bars were shifted west, while starter bars on east side have excess cover. Also, the line of the structural wall is flush with the plunge column, thus will have an implication on the plunge column removal, as T-05 is required to be fully constructed before the column can be taken out. Issue 2. The north and south end of the wall, are detailed as ferboxes with B12 starter bars.
| 03SR - Stations (RfL) | Cxxx-NCR-001924 | NCR | Self Compacting Concrete Mix 444 (MCR 50477) – 2hr Placement Time exceeded (NCR-286) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-10-03 | 2015-09-28 11:20 | -5 | 2015-08-04 13:41 | Structural Engineering - Structural Engineering - General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Specification Clause KF11.3221. - 2hr time limit from batching to end of placement exceeded. Details of the pours relating to this are as follows. 1) Date:17/07/2015 , Ticket No.813130 , Location: C20 N&S 3rd lift (SPL) , 2hr 13mins from batching to end placement 2)Date:24/07/2015 , Ticket No.812080 , Location: C22 N&S 3rd lift (SPL) , 2hr 27mins from batching to end placement 3)Date:27/07/2015 , Ticket No.812173 , Location: C23 N&S 2nd lift (SPL) , 2hr 33mins from batching to end placement
| 03SR - Stations (RfL) | Cxxx-NCR-001925 | NCR | Self Compacting Concrete Mix 295( MCR 50487) – 2hr Placement Time exceeded (NCR-269) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-10-03 | 2015-09-28 11:20 | -5 | 2015-08-04 13:46 | Structural Engineering - Structural Engineering - General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Specification Clause KF11.3221. - 2hr time limit from batching to end of placement exceeded. Details of the pours relating to this are as follows. 1) Date:27/07/2015 , Ticket No.812206 , Location: C22 N&S 2nd lift (CL) , 3hr 6mins from batching to end placement
| 03SR - Stations (RfL) | Cxxx-NCR-001926 | NCR | Concourse Level: Slab infill, Mole hole 1 at GL 4-5 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-09-04 | 2015-09-04 10:31 | 0 | 2015-08-05 13:46 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Various reinforcement clashes have been discovered in Concourse opening at GL4-5. These issues have been discussed at RRM (07/08/2015) and Pre-Pour meeting (13/08/2015) attended by __F, , CRL & Cxxx. Attached are the issues, as discussed in the Pre-Pour meeting, with the agreed proposals. Please confirm acceptability of proposals.
| 03SR - Stations (RfL) | Cxxx-NCR-001927 | NCR | C02 Slab Surface |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-02-12 | 2016-02-05 15:37 | -7 | 2015-08-05 13:53 | Civil - Civil Engineering General | 2500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Further to Cxxx-NCR-001314 some areas of C02 slab surface identified in the area of GL4-5, may require further investigation. This will occur after the completion of the slab infill works.
| 03SR - Stations (RfL) | Cxxx-NCR-001928 | NCR | Concourse Level – Columns C23-N&S and C2-S (NCR-271) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-11-24 | 2015-11-12 16:02 | -12 | 2015-08-05 14:50 | Structural Engineering - Reinforcement | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Refer Drawing Number: Cxxx-SKC-C-DWG-B071_WS077-51689 Rev. C03. In columns C23-N&S,C2-S, the coupler/starter bars were cast out of position due to congestion of steel within the slab. therefore, some of the links have been replaced to gain sufficient minimum cover to the column reinforcement in these areas. This has been agreed with CRL and the solutions have been implemented.
| 03SR - Stations (RfL) | Cxxx-NCR-001929 | NCR | Concourse Level: Elliptical Column : GL C/9 (NCR-273) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-10-10 | 2015-10-08 11:22 | -2 | 2015-08-06 16:34 | Structural Engineering - Reinforcement | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Refer to the following drawings: Cxxx-SWN-S-DDD-M171_4-01548 C03 Cxxx-SKC-C-DWG-B071_WS077-51689 Rev. C03; Elliptical column C9 at Concourse Level: 1No. B40 starter bar projecting 100mm from Concourse slab has insufficient cover. Due to congestion of steel the bar was cast out of position. Please see attached survey for detail.
| 03SR - Stations (RfL) | Cxxx-NCR-001930 | NCR | Concourse and intermediate level, GL 18/D (NCR-275) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-10-16 | 2015-10-08 13:50 | -8 | 2015-08-07 09:11 | Structural Engineering - Reinforcement | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Refer to location at GL 18/D, on both Concourse slab and intermediate slab levels: 2no. B12 starter bars are missing for nib adjacent to square column C18N on concourse level 2no. B12 starter bars are missing for nib adjacent to square column C18N on intermediate level Refer attached diagram to clarify location.
| 03SR - Stations (RfL) | Cxxx-NCR-001931 | NCR | Concourse Level - GL 7/B (NCR-277) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-10-16 | 2015-10-08 14:33 | -8 | 2015-08-07 16:56 | Structural Engineering - Reinforcement | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 1No. soffit Coupler bar misalignment with vertical bar in column C7-N – the correct number of bars was cast in the column C7-N however due to congestion of steel in Intermediate Level the 1No. Coupler was cast less than 150mm spacing requirements, the spacing between the vertical and the closest soffit starter bar was 100mm. There are also 2x missing vertical bars above the nib for wall CL-T-16
| 03SR - Stations (RfL) | Cxxx-NCR-001932 | NCR | BLL - Shotcrete Mix - No Trial |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-10-30 | 2016-10-24 07:49 | -6 | 2015-08-10 11:37 | Civil - Civil Engineering General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | Specification KF12, notes that trial mixes should be carried out where the addition of an admixture is present. Although the mix design for the sprayed concrete was accepted, no trial panel was carried out.
| 03SR - Stations (RfL) | Cxxx-NCR-001933 | NCR | Uncompacted Pile Arisings Left in West Sump |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-09-07 | 2015-09-04 17:13 | -3 | 2015-08-10 16:15 | Civil - Fill | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Prior to mass concrete backfill surrounding the west sump piles (P07, P08), uncompacted material was not removed from the sump. Note that this covers a localised area to the North of the sump.
| 03SR - Stations (RfL) | Cxxx-NCR-001934 | NCR | Damaged to elliptical column C14 SPL-CL |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-02-28 | 2019-02-06 16:52 | 343 | 2015-08-10 16:35 | Structural Engineering - Concrete Member | 3500 |  | Damaged | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | This NCR is raised to record the damages to the elliptical column concrete (architectural feature) as a result of shutter striking. The architectural feature cracked during striking process and will require an agreed remedial action in order to achieve specified architectural finishes.
| 03SR - Stations (RfL) | Cxxx-NCR-001935 | NCR | Walls in S03 & S06 - Walls SPL-T-54, SPL-T-153 ,SPL-T-154 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-03-23 | 2016-02-11 15:59 | -41 | 2015-08-11 10:37 | Structural Engineering - Structural Engineering - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | SPL-T-54 • Drawings 01523 and 04569 show a 255mm thick wall, however the ferbox used as shown on drawing 51814 is 110mm wide with 45mm cover - so for a 200mm wall. • Drawing 04569 shows 4 openings, however drawings 51814 (C02 rev - 19/5/2015)does not show any openings, 04569 C01 rev issued on 21/11/2014 and C02 which alters the size of the openings, but maintains 4 openings was issued on 12/6/2015. • This wall is located in S04 which was poured on 22/6/2015. SPL-T-153 • Drawing 04569 shows 4 openings, however drawings 52005 (C03 rev - 27/02/2015)does not show any openings, 04569 C01 rev issued on 21/11/2014 and C02 which alters the size of the openings, but maintains 4 openings was issued on 12/6/2015. • This wall is located in S06 which was poured on 17/4/2015. SPL-T-154 • Drawings 01523 and 04569 show a 255mm thick wall, however the ferbox used as shown on drawing 52005 is for a 200mm wall. • Drawing 04569 shows 4 openings, however drawings 52005 (C03 rev - 27/02/2015)does not show any openings, 04569 C01 rev issued on 21/11/2014 and C02 which alters the size of the openings, but maintains 4 openings was issued on 12/6/2015. • This wall is located in S06 which was poured on 17/4/2015.
| 03SR - Stations (RfL) | Cxxx-NCR-001936 | NCR | Tower crane [TC1] removal without NR WPP 323 sign-off |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-10-30 | 2015-10-06 17:29 | -24 | 2015-08-12 10:25 | Civil - Construction Health & Safety | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The removal of tower crane TC1 was recorded under WPP 323 [Cxxx-SKC-O1-GMS-B071_WS077-50282] and utilised the reverse methodology in the NR approved WPP 219 [Cxxx-SKC-O1-GMS-B071_WS077-50169]. This was discussed with NR who had no objection but required a review of the lift plan showing slew restrictions before formal approval. Due to NR annual leave constraints and no alternative point of contact, efforts were made to seek approval from NR. In discussion with CRL it was then proposed that the Cxxx [NR accredited CRE/CEM] would undertake an independent review and approve/comment as required.
| 03SR - Stations (RfL) | Cxxx-NCR-001938 | NCR | BLL - P25 Defective Material |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-09-17 | 2015-09-08 16:00 | -9 | 2015-08-12 12:42 | Civil - Civil Engineering General | 1500 |  | Material | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Cxxx-RFI-002725 permitted break-down on P25 to a level that exposed and undermined 30No. shear studs. Inspection after this break-down by Cxxx inspection showed an area in-between the flanges of the south side of the plunge column which contained pockets of material deemed to be loose/friable sandy material. As a result of this inspection and discussions between CRL, Cxxx & (13/07/2015) the pile was re-instated (14/07/2015) using high early strength ‘Top Rock’ mix up to a level which surrounded the exposed shear studs. This enabled 27No. total additional shear studs to be welded, both on the web and in the flanges of the plunge column below DCOL. The pile has then been reinstated from this level to DCOL using standard pile mix (21/07/2015.) Cxxx-RFI-002759 has also been raised to clarify this issue. Additional shear studs have been requested.
| 03SR - Stations (RfL) | Cxxx-NCR-001940 | NCR | Intermediate Level - Elliptical Column C9 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-10-13 | 2015-09-28 11:25 | -15 | 2015-08-14 18:01 | Structural Engineering - Reinforcement | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Intermediate Level: Elliptical Column : GL C/09 Drawing Numbers: Cxxx-SWN-S-DDA-M171_3-01568 Rev C04 Cxxx-SKC-C-DWG-B071_WS077-51764 Rev C01 On elliptical column C9 west face starter bars on intermediate level do not have sufficient cover, while east face starter bars have excess cover, please see attached pictures. __ soffit, 3no threaded couplers clash with the plunge column steel plate and therefore cannot be engaged.
| 03SR - Stations (RfL) | Cxxx-NCR-001942 | NCR | BLL Water Ingress |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-06-30 | 2016-05-27 10:46 | -34 | 2015-08-17 17:58 | Civil - Civil Engineering General | 2500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Water penetration has been identified at the construction joint between sub-platform level slabs, at the edge of the BLL box. See attached photo. The potential water path is illustrated in the attached “water path .pdf”. This is not in line with the requirements as set out in KW10.1301 part a. “All areas within the Station Box (except for the track side areas) and all areas within the __ (NR) connection shall achieve Grade 3 waterproofing protection of BS 8102:2009 Table 2. Grade 3 waterproofing protection requires performance level to be dry environment that is free from seepage or damp patches.” However the waterstop has been installed in the diaphragm walls and base slab in line with the manufacturers accepted detail drawings (and installation guidelines), and KW10.1110 parts a and c, “Waterstop (or waterbars) will be provided at all construction joints in the structure where water ingress is possible. The recommended waterstops types are: a) Between adjacent Diaphragm wall panels - Waterbars shall be rubber/ PVC dumbbell type with central reinjectable grout tube. …… c) Base slabs and cast-in-situ perimenter or lining walls - Waterbars shall be either rubber or PVC rear-guard or re-injectable type “ The water ingress that has currently been observed and measured as part of Cxxx-NCR-001745 is within with the allowable amounts of water penetration through the Diaphragm wall as set out in KP10.1301 B4.4.7 Water retention part a a) “In addition to SPERW, clause B8.4.7, diaphragm walls shall be free from running or dripping water after the inside face has been exposed. Beads of water (provided these are single spots and do not run) and areas of dampness not exceeding 1.0m² will be accepted without remedial work. The leakage through diaphragm wall panels shall not exceed 0.4 litre/ m² per day and the leakage through joints between adjacent panels shall not exceed an additional six litres/ m of joint per day.” These two parts of the specification contradict one another.
| 03SR - Stations (RfL) | Cxxx-NCR-001943 | NCR | Concourse Opening Infill GL20-21 Low Cover over Precast Unit SC-01A |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-10-16 | 2015-08-20 16:13 | -57 | 2015-08-17 17:56 | Structural Engineering - Pre-cast | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 3No. BM25 (B32) couplers on B1 of Concourse Level bottom mat at opening GL20-21, have been cast such that bars coupled into them have low cover to the eastern and western SC-01A units. The top of the precast unit has been scabbled, but this still only leaves a minimum of 10mm cover to 3No. of the BM64 bars, which tie in to BM25 couplers. Low cover is present for approx. the south 1000mm of the unit. Proposal is to remove the unit to allow cover to the BM64 bars. Additional bars required to replace the units will be as detailed on the attached.
| 03SR - Stations (RfL) | Cxxx-NCR-001944 | NCR | S15 - Sub-Platform Concrete Mix 444 (MCR 50388,50389) – 3hr Placement Time exceeded |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-09-17 | 2015-08-19 09:52 | -29 | 2015-08-18 12:11 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | On 25/5/2015 - S15 was poured. Ticket number 713886 of 323 mix had a placement time of 3hours 11minutes. Specification Clause KF11.3221. 2hr time limit from batching to end of placement. This was extended to 3hrs for the sub-platform mix. (__F-RFI-1070, Cxxx-RFI-002219)
| 03SR - Stations (RfL) | Cxxx-NCR-001945 | NCR | Concourse Level: Elliptical Column : GL C/9 (NCR-292) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-10-17 | 2015-09-29 15:38 | -18 | 2015-08-18 16:22 | Structural Engineering - Reinforcement | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Drawing Cxxx-SWN-S-DDD-M171_4-01548 C03 Cxxx-SKC-C-DWG-B071_WS077-51689 Rev. C03; 5No. B32 starter bar BM 18 projecting from soffit of Intermediate Level (C9) have been cast away from their design position. Insitu cast location differences as follows: 1No. bar = 155mm away / 185mm away / 245mm away / 185mm away / 145mm away (refer attached marked up drawing for details – not to scale). Additionally, the minimum cover requirements of 40mm are compromised in one area at the bottom South west side at CL (see mark up) where the starter bars are cast out of position due to congestion of steel within the slab. The 4No. bottom links of B20 would only achieve a cover of 35mm.
| 03SR - Stations (RfL) | Cxxx-NCR-001946 | NCR | Platform Edge Screen Couplers Omitted from Concourse Soffit GL3 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-05-03 | 2016-04-11 07:48 | -22 | 2015-08-20 11:45 | Civil - Civil Engineering General | 2500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | With respect to the PES structure, in the north west corner of the box where the type 4 smoke duct is due to be installed. A set of 6No couplers have been omitted from the concourse level slab at the western group of couplers as marked up on the attached drawing. This consequence of this means the PES steel bay in this location can only be fixed into the soffit on the eastern side of the bay. Please see attached mark-up drawings and photos for further clarification.
| 03SR - Stations (RfL) | Cxxx-NCR-001947 | NCR | Concourse Opening Infill GL20-21 Reinforcement |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-09-16 | 2015-09-09 09:55 | -7 | 2015-08-19 18:25 | Structural Engineering - Reinforcement | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Concourse Level Opening Infill GL20-21 had alterations to reinforcement fixing as listed in Cxxx-RFI-002832 & Cxxx-RFI-002835. Of these, those which constitute NCRs are listed here and those which are FCDs are referred to in Cxxx-FCD-001849. These issues have all been agreed between CRL, Cxxx, & __L at Pre-Pour meeting (19/08/2015.) Attached is the Cxxx response to these issues. 1. In the B2 layer on the east face, 1No. B32 BM48s have been cast too close to 1No. B16 BM83s. Further to Cxxx-NCR-001726, (similar issue to GL4-5) the proposal is to omit the 1No. B16 BM82, which couple into BM83, but to fix the bars up against the construction joint. Please note this was originally thought to be 3No. bars, but during fixing only 1No. could not be engaged. 2. North – East corner, Bottom Mat: 4No. BM77(a-d) B2 of which 2No. bars are cast on top of B1 B32 BM76 and bars will not be able to be threaded onto both due to the clash between couplers. Area has been broken back to allow the bars to split and to thread the both couplers. All couplers have been able to be engaged. 3. North – West corner bottom: 4No. BM40 (a-d) (from drawing no. 51700) B2 layer, 3No. of which are cast on top of B1 B32 BM76 and will unable to thread both bars due to a clash between couplers. Area has been broken back to allow the bars to split and to thread the both couplers. All couplers have been able to be engaged. 4. North-West corner Top: 4B25 BM 65 (from drawing no. 51701) are cast just under the T1 BM 108/109 (from drawing no. 51701) and due to this clash of couplers both bars cannot be threaded. Area has been broken back to allow the bars to split and to thread the both couplers. All couplers have been able to be engaged.
| 03SR - Stations (RfL) | Cxxx-NCR-001948 | NCR | Discolouration of concrete material used at C9 3rd lift |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-08-25 | 2016-08-11 08:49 | -14 | 2015-08-20 11:16 | Structural Engineering - Finishes | 10000 |  | Material | Rework | 2 (6-60k) | Complete | Material/Preservation Problems - Other | Completed |  | Elliptical Column G/L 9: The 3rd lift concrete pour of Elliptical column C9 at the underside of concourse slab soffit has resulted a poor surface finish. The non-conformities are as follows: 1) Surface not conforming to architectural finish spec. – refer attached photos 2) Discolouration – refer attached photo’s comparing the colour difference between lift 2 & 3.
| 03SR - Stations (RfL) | Cxxx-NCR-001949 | NCR | Bonding requirement for Blockwork |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-05-30 | 2016-05-13 09:43 | -17 | 2015-08-20 14:53 | Architectural - Brickworks/Blockworks | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Surveillance Cxxx-SKC-O-RGN-B071_WS077-50153 on Blockwork ITP Validation highlighted the requirement of JF10.3204 for 'intersections, external corners and internal corners ... to be fully bonded except where indicated otherwise.' However, surveillance observed changes in direction along the south wall having a straight vertical joint, that was not shown on __ drawings. Further investigation may be required into the specification requirements for bonded blocks.
| 03SR - Stations (RfL) | Cxxx-NCR-001950 | NCR | Elliptical Column GL C/10 insufficient cover at CL (NCR-294) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-10-19 | 2015-10-14 16:16 | -5 | 2015-08-20 16:45 | Structural Engineering - Reinforcement | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Drawings Cxxx-SWN-S-DDD-M171_4-01547 C04; Cxxx-SWN-S-DDD-M171_4-01548 C03 Cxxx-SKC-C-DWG-B071_WS077-51690 Rev. C02; Issue 1: Elliptical column C10 rebar does not meet the absolute minimum cover of 40mm as required by the spec. Issue 2: Areas of excessive cover were picked up during survey also. Please refer to attached diagram for further details including survey information.
| 03SR - Stations (RfL) | Cxxx-NCR-001952 | NCR | SPL Elliptical Column C9, Damage to Joint between lift 2 & 3 (NCR-296) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-06-30 | 2016-05-10 15:22 | -51 | 2015-08-20 18:01 | Structural Engineering - Joints | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | At the joint between 2nd and 3rd concrete lift of Elliptical column C9, there are several small voids and cracking at various locations around the perimeter of the column. Refer attached photos showing the extent of these defects. Note these defects are within the cladding zone.
| 03SR - Stations (RfL) | Cxxx-NCR-001953 | NCR | C13 elliptical column - missing coupler in __ soffit |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-10-20 | 2015-10-08 11:18 | -12 | 2015-08-21 09:49 | Structural Engineering - Reinforcement | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Drawing Numbers reference: Cxxx-SKC-C-DWG-B071_WS077-51690 Cxxx-SWN-S-DDA-M171_4-01548 1No. coupler in the soffit at __ for elliptical column C13 is missing which would be used to connect to BM10.
| 03SR - Stations (RfL) | Cxxx-NCR-001954 | NCR | Elliptical column C15 Intermediate Level (NCR-288-R2) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-10-19 | 2015-10-19 13:36 | 0 | 2015-08-20 19:07 | Structural Engineering - Reinforcement | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Drawing Numbers: Cxxx-SKC-C-DWG-B071_WS077-51764 Rev C01 Cxxx-SWN-S-DDA-M171_3-01569 Rev C05 Issue 1: 3No. starter bars at concourse level for elliptical column C15 have insufficient cover in the drainage recess area (refer attached diagram for clarification and dimension details). Issue 2: There are 3No.couplers at the IL soffit which are clashing with top plate of the plunge column by approx.. 35mm
| 03SR - Stations (RfL) | Cxxx-NCR-001955 | NCR | Precast units pour P184 cast 15-07-2015 low strength at 28 days |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-10-20 | 2015-10-13 14:08 | -7 | 2015-08-21 11:02 | Structural Engineering - Pre-cast | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Compressive strength test results relating to precast units cast on 15-08-2015 (pour reference P184) were below specified strength at 28 days; see attached test certificate A920_17082015 28 day cube results. 2No. cubes were tested at 28 days yielding results 48.0N/mm² and 53.0N/mm² (and so test result from this load is 50.5N/mm² in accordance with EN 206:2013 appendix B). Units cast on that date were as follows: - 2 No.: US-01 - 1 No.: W-01A - 2 No.: FS-47 - 4 No.: SC-01A These units are for filling temporary openings in the concourse slab and have been installed to GL4-5 and GL20-21. In-situ slab to GL:4-5 was cast on 14-08-2015, slab to GL:20-21 poured 20-08-2015. Feedback from the precast designer is as follows: “__ uses C50/60 for all components for uniformity and to allow early release from the mould, therefore the design conditions are not generally critical for concrete strength. I note that the lowest value was 48 N/mm2 at 28 days; therefore the grade should be downgraded to C35/45 [for the purposes of the calculation]. I checked the durability requirements and these are relatively low at XC1 exposure class, therefore durability still fine. In relation to strength I reran the calculations, strength was fine but there was a marginal estimated deflection excess in the flat panels (FS47) of 13.2mm compared to an allowable of 12mm. The deflection I have estimated is in the precast unit only and caused by the temporary condition. Once the props are struck then the full permanent section is working and governs deflection. I reran the calculation and deflection due to temporary condition was 12.7mm for C40/50. This is only 0.7mm greater than originally estimated” Unit W-01A has not been delivered to site and will be disposed of.
| 03SR - Stations (RfL) | Cxxx-NCR-001956 | NCR | T-05 Starter bar cover issue on Concourse Level (NCR-289) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-06-30 | 2016-05-13 13:18 | -48 | 2015-08-24 08:23 | Structural Engineering - Reinforcement | 1500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Drawing Numbers: Cxxx-SKC-C-DWG-B071_WS077-51698 Refer to the attached diagram detailing the existing cover issues to the starter bars at T-05. The survey data reveals we will not achieve minimum specified cover in various locations here.
| 03SR - Stations (RfL) | Cxxx-NCR-001957 | NCR | T-04 Starter bar cover issue on Concourse Level (NCR-291) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-10-23 | 2015-10-08 13:46 | -15 | 2015-08-24 08:32 | Structural Engineering - Reinforcement | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Drawing Number: Cxxx-SKC-C-DWG-B071_WS077-51698 Refer to the attached "Concourse Level T-04 survey to main bar_REV01.pdf" diagram for details. Issue 1: No longer an issue after reviewing more accurate survey data. Issue 2: The North and South faces of the wall have insufficient cover at the soffit. Kicker is already poured which has insufficient cover on the North face. Issue 3: The U-Bars for the upstand within the wall have been cast too high, with the design as it currently stands the bars will be protruding out of the TOC. Issue 4: 1No. Bar in the soffit at the south face is cast outside of the wall position. Issue 5: Various starter bars have been cast more than 50mm away from the vertical bar design position.
| 03SR - Stations (RfL) | Cxxx-NCR-001958 | NCR | T-04 Starter bar cover issue on Intermediate Level (NCR-293) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-10-23 | 2015-10-08 13:47 | -15 | 2015-08-24 08:41 | Structural Engineering - Reinforcement | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Drawing Number: Cxxx-SKC-C-DWG-B071_WS077-51767 The starter bars cast into the slab at Intermediate Level provide insufficient cover on the west face if rebar is installed as per the drawing details. Please refer attached sketch for clarification and please note these measurements are taken from the wall face to main vertical bar. understand that the wall thickness cannot be increased on this face.
| 03SR - Stations (RfL) | Cxxx-NCR-001959 | NCR | Elliptical Column C9; insufficient cover at concourse level (NCR-298) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-10-23 | 2015-10-21 10:54 | -2 | 2015-08-24 18:23 | Structural Engineering - Reinforcement | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Drawing Cxxx-SWN-S-DDD-M171_4-01548 C03 Cxxx-SKC-C-DWG-B071_WS077-51689 Rev. C03; Elliptical column C9: 1. Insufficient cover to starter bars at concourse slab level on South side of elliptical column. 2. Insufficient cover to soffit starter bars above concourse level, min. 30mm to B20 link. 3. Double hooks BM 12 & BM 13 & BM 16 require cut/lap for constructability purposes to allow engaging the vertical bars. BM14.
| 03SR - Stations (RfL) | Cxxx-NCR-001960 | NCR | SPL: T-04 soffit couplers missing and/or cast out of position (NCR-299) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-10-23 | 2015-10-19 13:50 | -4 | 2015-08-24 18:40 | Structural Engineering - Reinforcement | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Drawing Number: Cxxx-SKC-C-DWG-B071_WS077-52070 Various couplers (B20) for the connection from the SPL wall T-04 to the concourse level slab have been cast out of place and 2No. are missing. Refer attached marked up drawing detailing these non-conformities.
| 03SR - Stations (RfL) | Cxxx-NCR-001961 | NCR | C9: IL-__ soffit couplers missing |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-10-25 | 2015-10-13 09:21 | -12 | 2015-08-26 17:59 | Structural Engineering - Reinforcement | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Refer Drawing: Cxxx-SKC-C-DWG-B071_WS077-51764 Rev C01 2No. couplers for B32 bars are missing from the soffit at __ slab (BM 18). Refer attached "C9 IL-__ Soffit Couplers.pdf" detailing the measurements surveyed between each coupler as built in the soffit. It is assumed that the missing 2No. couplers would be within the widest intervals between adjacent bars shown on the survey (so missing from the intervals marked ‘270’ and ‘230’). Note*** Disregard the pink highlighted areas - this is not related to NCR-1961.
| 03SR - Stations (RfL) | Cxxx-NCR-001962 | NCR | Elliptical Column C16: __ soffit coupler clashes with plunge column plate |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-10-31 | 2015-10-19 13:38 | -12 | 2015-09-01 17:20 | Structural Engineering - Reinforcement | 1500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Refer elliptical column C16: 1No. coupler at __ soffit is cast on a slight angle such that a threaded bar cannot be engaged due to clashing with the corner of the plate of the plunge column.
| 03SR - Stations (RfL) | Cxxx-NCR-001963 | NCR | Wall Opening incorrect size at CL-T-04 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-10-31 | 2015-09-29 14:01 | -32 | 2015-09-01 18:37 | Structural Engineering - Structural Engineering - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Drawings referenced: Cxxx-SWN-S-DDB-M171_Z-04570 Cxxx-SWN-S-DDB-M171_Z-04580 Cxxx-SWN-S-DDC-M171_Z-04560 Cxxx-SWN-S-DDD-M171_4-01510 Cxxx-SKC-C-DWG-B071_WS077-51698 Cxxx-SWN-S-DDD-M171_3-01567 C06 Cxxx-SWN-S-DDD-M171_3-01568 C04 Issue: The opening in the wall at CL-T-04 is suppose to be 1200mm high as shown in the most recent drawing Z-04560 C09. However, the actual height of the opening will be 1280mm high. This is due to discrepancies between drawings and revisions to dimensions which seem to have occurred post construction. Intermediate GA drawing 3-01567 C06 & 3-01568 C04 shows a 100mm step in soffit. The drawing elevation Z-04560 shows 180mm step required in order for opening being flush to soffit. Intermediate slab was poured on 15th April 2014 and elevation drawing Z-04580 C02 was used for this detail. Refer attached elevation drawings Z-04560 C09 (latest rev) vs. Z-04560 C06 (latest rev at time of pour) illustrating the change in dimension detail post pour. Please see attached elevation drawing, rebar and GA’s drawings for more clarity.
| 03SR - Stations (RfL) | Cxxx-NCR-001964 | NCR | Damaged concourse slab soffit GL 14-15/A-B |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2016-02-16 | 2016-02-04 15:52 | -12 | 2015-09-02 09:24 | Structural Engineering - Concrete Member | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Concouse slab soffit damaged with reinforcement exposed. Located at concourse infill slab GL14-15/A-B.
| 03SR - Stations (RfL) | Cxxx-NCR-001965 | NCR | PL-T-05: Missing couplers in soffit (concourse slab) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-11-02 | 2015-10-19 14:00 | -14 | 2015-09-03 09:53 | Structural Engineering - Reinforcement | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Drawing Number: Cxxx-SKC-C-DWG-B071_WS077-52074 6No. Couplers missing from Soffit (i.e. within concourse slab) for connection to structural wall T-05 at Platform Level. Location of missing couplers are; 3No. from the Northern most face of the wall and 3No. from the Southern most face of the wall.
| 03SR - Stations (RfL) | Cxxx-NCR-001966 | NCR | Upstand Detail at IL-T-04 Intermediate Level (__F-302) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-11-06 | 2015-10-08 14:37 | -29 | 2015-09-07 10:19 | Structural Engineering - Reinforcement | 1500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Drawing Reference Numbers: Cxxx-SWN-S-DDC-M171_Z-04560 Rev. C05/C09 Cxxx-SKC-C-DWG-B071_WS077-51719 Cxxx-SKC-C-DWG-B071_WS077-51723 The U-Bars underneath the opening in wall T-04 on Intermediate have been cast at the wrong height. This is due to a revision of the drawing detail post construction. The U-bars are cast 100mm too high. Refer attached drawings for further details.
| 03SR - Stations (RfL) | Cxxx-NCR-001967 | NCR | Concourse Soffit Coupler for PES/Precast Smoke Ducts Out of Tolerance |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-04-18 | 2016-04-11 17:08 | -7 | 2015-09-07 11:49 | Civil - Civil Engineering General | 50000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | Whilst a full survey is ongoing, it would appear that some couplers cast into the concourse slab soffit for the platform edge screen and precast smoke ducts are out of tolerance. As a result, it is likely that the platform edge screen and precast smoke ducts as designed will not fit the couplers. This NCR will be updated once a full survey is completed. See attached survey results for PES & Smoke Duct Fixings.
| 03SR - Stations (RfL) | Cxxx-NCR-001968 | NCR | P7 Reinstatement Concrete over 2hr Limit |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-11-07 | 2015-09-10 09:19 | -58 | 2015-09-08 13:12 | Structural Engineering - Structural Engineering - General | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Concrete load 813916 (ticket attached) was batched at 14:11 and upon arrival on site gave a flow test result of 610mm (target F5). Discharge into P8 re-form commenced at 16:00 and was completed at 16:20, more than two hours since the concrete had been batched. Cxxx-RFI-000395 and Cxxx-FCD-000482 permit concreting in piling operations to occur up to three hours from batching using this concrete mix. An additional flow test was carried out, giving a result of 570mm between the concreting of P8 & P7. Concreting then commenced into P7 re-form at 16:40 and was completed at 17:00, 11 minutes inside the three hour limit given by Cxxx-FCD-000482.
| 03SR - Stations (RfL) | Cxxx-NCR-001969 | NCR | C15 at Intermediate Level: Drain recess clash with reinforcment detail at column head |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-11-07 | 2015-10-21 10:55 | -17 | 2015-09-08 18:05 | Structural Engineering - Reinforcement | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Drawing Numbers: Cxxx-SKC-C-DWG-B071_WS077-51764 Rev C01 Cxxx-SWN-S-DDA-M171_3-01569 Rev C05 Cxxx-SWN-S-DDD-M171_Z-01510 Cxxx-SKC-C-DWG-B071_WS077-51557 Intermediate level C15 elliptical column: Intent drawing (dwg no. 51557) does not incorporate detail of the drainage channel that runs from IL to the underside of the flare at column head, see note elevation drawing Z-01510. Please refer to R&R detailing drawing no. 51764 & intent drawing no. 51557 for additional information.
| 03SR - Stations (RfL) | Cxxx-NCR-001970 | NCR | T-05 Issues at Intermediate level - __ |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-10-30 | 2016-09-13 08:23 | -47 | 2015-09-09 13:39 | Structural Engineering - Reinforcement | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Issue 1. A Number of couplers in the soffit at __ are cast out of position due to steel congestion in the slab above, this will result in minimum cover being compromised. Said couplers are located at the West face of the wall T-05. Note* In the worst case here the cover is measured to be 10mm to the vertical bars. Refer to “IL-T-05 __ Soffit and IL base slab survey_cover to rebar” for details. Issue 2. Opening at __ slab is cast 100mm in IL 500mm wall, as shown on GA 2-01530 (refer attached). Box out designed to sit on IL-T-05. As a result, 4No. couplers are cast in behind the box ~120mm away from face of wall. For exact dimensions refer to sketch “IL-T-05 __ Soffit and IL base slab survey_cover to rebar”. The offset distance (horizontal displacement) between said __ soffit starter bars & IL slab starter bars is approximately 60mm. Issue 3. Couplers missing/not detailed from soffit at __. North side; 6No. in total missing South Side; 14No. in total missing. South end coupler detail was not shown on drawing No.50559
| 03SR - Stations (RfL) | Cxxx-NCR-001971 | NCR | No offsite ITP produced for windposts at start of works |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-04-29 | 2016-04-29 12:57 | 0 | 2015-09-10 16:34 | Architectural - Brickworks/Blockworks | 5000 |  | Documentation and Records | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Refer to "NCR1" in surveillance report reference: Cxxx-SKC-O-RGN-B071_W077-50256 There was no off-site ITP produced for the first batch of 59 windposts, which were fabricated prior to the manufacturer (Stainless Steel Fixings Ltd (SSF td)) gaining CE certification.
| 03SR - Stations (RfL) | Cxxx-NCR-001972 | NCR | N__ testing requirements |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-05-30 | 2016-05-13 08:19 | -17 | 2015-09-11 17:01 | Architectural - Brickworks/Blockworks | 5000 |  | Documentation and Records | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Reference to " NCR3" in surveillance report Cxxx-SKC-O-RGN-B071_WS077-50256 and item 1.2.1 in surveillance report Cxxx-SKC-O-RGN-B071_WS077-50243. Regarding the windposts that were installed on-site prior to CE certification (18 March 2015), for the N__ reports submitted as part of the works order and package listing, the records do not meet all of the suggested requirements of BS EN ISO 17638:2009 Cl5.14
| 03SR - Stations (RfL) | Cxxx-NCR-001973 | NCR | HV Trench finish |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-11-09 | 2015-09-24 13:40 | -46 | 2015-09-10 19:26 | Structural Engineering - Concrete Member | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | This NCR will supersede the following NCRs NCR-1731, 1735, 1755, 1790, 1793, 1807, 1824, 1826, 1827, 1842, 1843, 1844, 1865, 1873, 1876, 1877. These NCRs relate to the finish in the HV trench built into the sub-platform slab. A number of defects have been identified in the concrete finish of the HV trench through the sub-platform slab, Following a benchmark inspection between CRL, and __L the following was raised. 1. Blowholes/craters in the Trench base. 2. Delamination of side walls. 3. Chipping to 50mmx50mm rebate.
| 03SR - Stations (RfL) | Cxxx-NCR-001974 | NCR | Concrete Damage - __ header Beams removal |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-11-30 | 2016-09-22 14:38 | -69 | 2015-09-12 16:22 | Civil - Civil Engineering General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Location: Header Beams for PC47/48 & 49/50 on GL21 & 22 __ slab soffit. The header beams fixed to the underside of the __ slab had to be removed as part of the plunge column removal operation. The 2no Header beams 47/48 & 49/50 failed to release from slab under self weight. Therefore, a jacking operation had to be carried out to release both header beams and remove. As a result, damage to the concrete in two locations has been caused. please see attached photos for clarification.
| 03SR - Stations (RfL) | Cxxx-NCR-001975 | NCR | Intermediate Level - Elliptical Column C9 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-11-13 | 2015-11-13 16:18 | 0 | 2015-09-14 10:34 | Structural Engineering - Reinforcement | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Drawing Numbers: Cxxx-SKC-C-DWG-B071_WS077-51764 Rev C01 Cxxx-SWN-S-DDA-M171_3-01568 Rev C04 With reference to Cxxx-NCR-001940, additional issues were discovered during steel fixing works, details are as follows: 1. Bottom north & south first 5No. B20 links BM 10 cover reduced to 30mm. 2. Bottom south side first 3No. B16 bar BM 11 cover reduced to 30mm. 3. Single double hook 27B16 BM 16 require cut and splice as it’s unable to fix through the vertical bar BM 14. 4. Underside flared head 1No. Link B20 BM10, cover reduced to 35mm 5. Underside __ soffit first 1No. Link B25 BM19c, unable to be fixed due to flared head threaded bars BM20 clashing with threaded vertical bar BM14 & lacers BM10 6. Flared head lacer 2No. B25 BM 19 a&b (bottom first 2 from the flared head) scheduled/bend too short.
| 03SR - Stations (RfL) | Cxxx-NCR-001976 | NCR | Intermediate Level - Elliptical Column C15 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-11-13 | 2015-11-13 16:17 | 0 | 2015-09-14 10:49 | Structural Engineering - Reinforcement | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Drawing Numbers: Cxxx-SKC-C-DWG-B071_WS077-51764 Rev C01 Cxxx-SWN-S-DDA-M171_3-01569 Rev C05 Issue: Bottom north & south first 6No. B20 links BM 22 cover reduced to 30mm.
| 03SR - Stations (RfL) | Cxxx-NCR-001977 | NCR | Wall IL-T-01 _cover & 2No. nibs |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-12-15 | 2015-12-08 11:58 | -7 | 2015-09-14 18:10 | Structural Engineering - Reinforcement | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Drawing Numbers: Cxxx-SKC-C-DWG-B071_WS077-51766_Wall IL-T-01 cover Cxxx-SWN-S-DDA-M171_3-01567 Cxxx-SWN-S-DDC-M171_Z-04560 Cxxx-SWN-S-DDD-M171_3-01520 Cxxx-SKC-C-DWG-B071_WS077-51774_IL-L-01 Cxxx-SKC-C-DWG-B071_WS077-51765_IL-L-08 ISSUE 1. Discrepancy in detail for positioning of lacers: Refer to drawing 51766. Main wall elevation details the lacers to be fixed on the outside, section 2-2 details the lacers fixed on the inside. ISSUE 2. __ Soffit Starter bars: 8No. couplers cast in the soffit have 40mm or less cover to the vertical bar. 18No. couplers cast in the soffit have 50mm or less cover to the vertical bar. Please refer to highlighted survey and drawing. ISSUE 3. Excess cover for starter bars cast within IL slab: Starter bar projection = 900mm. Kicker already cast @ 150mm Remaining projection of bar above the kicker = 750mm ISSUE 4. 2No. Nibs (IL-L-01 & IL-L-08) as per drawing 51774 & 51765 The nibs will be cast along with Wall IL-T-01 General dowel bar connection is: at 500mm long with 200mm embed to soffit and fixed at 300mm c/c. I) IL-L-01 details a typical soft joint, on drawing 51774. However, only 190mm nib that would be cast. Refer to highlighted area on drawing 3-01520. II) IL-L-08 details a typical soft joint, on drawing 51765. However, only approximately 200mm remains still to be cast. Refer to highlighted area on drawing 3-01520.
| 03SR - Stations (RfL) | Cxxx-NCR-001978 | NCR | Wall IL-T-08 _cover & 2No. nibs |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-12-15 | 2015-12-08 12:06 | -7 | 2015-09-15 11:20 | Structural Engineering - Reinforcement | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Drawings: Cxxx-SWN-S-DDD-M171_3-01520 Cxxx-SKC-C-DWG-B071_WS077-50876___ slab starter bars Cxxx-SKC-C-DWG-B071_WS077-51799_Wall IL-T-08 Cxxx-SKC-C-DWG-B071_WS077-51809_Wall-L-27 Cxxx-SKC-C-DWG-B071_WS077-51816_Wall IL-L-20 ISSUE 1. Discrepancy in detail for positioning of lacers: Refer to drawing 51799. IL-T-08 wall elevation details the U-bars to be fixed on the outside NF1/FF1, but other wall elevations on this drawing details the U-bars fixed on the inside NF2/FF2. ISSUE 2. __ Soffit Starter bars: Various areas have been identified to have insufficient cover to the main vertical bars. 1No. bar in particular on the East face has only 27mm cover to the vertical. ISSUE 3. Excess and reduced cover of starter bars cast within IL slab: Starter bar projection = 900mm. Kicker already cast @ 150mm Remaining projection of bar above the kicker = 750mm ISSUE 4. 2No. Nibs (IL-L-20 & IL-L-27) as per drawing 51816 & 51809. The nibs will be cast along with Wall IL-T-08 General dowel bar connection is: at 500mm long with 200mm embed to soffit and fixed at 300mm c/c. I) IL-L-20 does not detail a typical soft joint, on drawing 51816. Note, only 190mm nib would be cast. Refer to highlighted area on drawing 3-01520. II) IL-L-27 details a typical soft joint, on drawing 51809. However, the __ soffit currently has cast in Ferbox pull out bars in this location. Refer to __ slab starter bars drawing 50876.
| 03SR - Stations (RfL) | Cxxx-NCR-001979 | NCR | East & West Liner Walls - Missing Couplers |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-11-14 | 2015-11-03 17:34 | -11 | 2015-09-15 11:59 | Structural Engineering - Reinforcement | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | East Liner Wall Drawings: Cxxx-SKC-C-DWG-B071_WS077-51776 Rev. P04; Cxxx-SWN-S-DDD-M171_5-01522 Rev. C09 West Liner wall Drawings: Cxxx-SKC-C-DWG-B071_WS077-52391 Rev. C01 Cxxx-SWN-S-DDD-M171_5-01525 Rev. C08 Section to East & West Liner wall Cxxx-SKC-C-DWG-B071_WS077-51777 Rev. P03 The couplers cast into the D-wall at the East & West liner walls are not cast in at the correct positions. The D/wall couplers connect with threaded bars detailed on drawing 52391 & 51766 as following 11B32 BM 10; 10B32 BM19; 21 B32 BM16; 9B32 BM13. The total No. of lacers detailed in R&R drawings 52391 & 51766 are 51No. lacers. The intent drawings Z-55560 shows B32-150links varying length. As-built survey reveals D/wall cast firsty couplers for lacer connection are as follows (same for east and west walls): NORTH D-wall 45 FF – therefore 6No missing 46 NF – therefore 5No missing SOUTH D-wall 45 FF – therefore 6No missing 46 NF – therefore 5No missing Total No. of missing d/wall couplers are 22No. at each liner wall.
| 03SR - Stations (RfL) | Cxxx-NCR-001980 | NCR | Self Compacting Concrete Mix 295 (MCR 50487) – 2hr Placement Time exceeded (__F-282) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-11-16 | 2015-09-28 11:21 | -49 | 2015-09-17 15:02 | Structural Engineering - Reinforcement | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Specification Clause KF11.3221. - 2hr time limit from batching to end of placement exceeded. Details of the pours relating to this are as follows. 1) Date:03/08/2015 , Ticket No.813743 , Location: C22N, C23N (IL), 2hr 50mins from batching to end placement 2) Date:05/08/2015 , Ticket No.813901 , Location: C21N&S, C22S, C23S (IL), 2hr 26mins from batching to end placement 3) Date:05/08/2015 , Ticket No.813907 , Location: C21N&S, C22S, C23S (IL), 2hr 54mins from batching to end placement
| 03SR - Stations (RfL) | Cxxx-NCR-001981 | NCR | Self Compacting Concrete Mix 444 (MCR 50477) – 2hr Placement Time exceeded (__F-283) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-11-16 | 2015-09-28 11:21 | -49 | 2015-09-17 15:07 | Structural Engineering - Reinforcement | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Specification Clause KF11.3221. - 2hr time limit from batching to end of placement exceeded. Details of the pours relating to this are as follows. 1) Date:04/08/2015 , Ticket No.813838 , Location: C18N&S (SPL) 2nd lift , 2hr 13mins from batching to end placement
| 03SR - Stations (RfL) | Cxxx-NCR-001982 | NCR | Non conformance Architectural concrete finish, soffit BLL Box adit |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2016-05-30 | 2016-05-23 14:21 | -7 | 2015-09-17 16:51 | Architectural - Finishes | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Cxxx-NCR-001808 was closed out by accident. This NCR is raised to track the progress of remedial work to be undertaken. ---------NCR-1808---------- As per drawing Cxxx-SWN-A-DDA-M171_7-31332, the finish of the BLL adit is "exposed concrete" which requires architectural finish. Cxxx-SWN-A-RSP-B071-00001 (Architectural Specification) JE80.1202 requires a "dense, even-coloured, blemish-free surface". After the BLL Box excavation completion it was found a decolouration in the concrete surface and misalignment of the shutters which does not comply with the requirements. Please find pictures attached.
| 03SR - Stations (RfL) | Cxxx-NCR-001983 | NCR | Wall CL-T-08_cover & 1No. nib (__F-311) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-12-17 | 2015-12-10 11:11 | -7 | 2015-09-17 20:08 | Structural Engineering - Reinforcement | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Drawing: Cxxx-SWN-S-DDD-M171_4-01510_CL-T-08 Cxxx-SKC-C-DWG-B071_WS077-51698_CL-T-08 CL-T-08_cover survey soffit & base Cxxx-SKC-C-DWG-B071_WS077-51748_CL-L-27 ISSUE 1. CL Soffit Starter bars cast in with reduced cover to threaded bars BM50. Please refer to highlighted survey and drawing. ISSUE 2. Excess & reduced cover for starter bars cast within CL slab: Starter bar projection = 900mm. Kicker not yet cast ISSUE 3. The 640mm nib will be cast along with Wall CL-T-08. The Nib requires 2No. dowel bars for installation.
| 03SR - Stations (RfL) | Cxxx-NCR-001984 | NCR | IL-T-01_Soffit firstycast couplers (__F-309) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-11-16 | 2015-10-05 15:37 | -42 | 2015-09-17 20:21 | Structural Engineering - Reinforcement | 1500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Drawing Numbers: Cxxx-SKC-C-DWG-B071_WS077-51766_Wall IL-T-01 Cxxx-SWN-S-DDA-M171_3-01567 Cxxx-SWN-S-DDC-M171_Z-04560 Cxxx-SWN-S-DDD-M171_3-01520 Cxxx-SKC-C-DWG-B071_WS077-51718_slab IL firsty couplers At wall IL-T-01 (__ soffit) there are 6No. B16 firsty cast couplers which are fill with concrete/damaged/missed out.
| 03SR - Stations (RfL) | Cxxx-NCR-001986 | NCR | Wall CL-T-01_cover & 1No. nib (__F-308) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-12-17 | 2015-12-10 11:12 | -7 | 2015-09-18 11:49 | Structural Engineering - Reinforcement | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Drawing Numbers: Cxxx-SWN-S-DDD-M171_4-01510_CL-T-01 Cxxx-SKC-C-DWG-B071_WS077-51662_CL-T-01 Cxxx-SKC-C-DWG-B071_WS077-51747_CL-L-08 nib CL-T-01_cover survey soffit & base Cxxx-SWN-S-DDD-M171_Z-57731 ISSUE 1. Soffit Starter bars cast in with reduced cover to threaded bars BM30. Please refer to highlighted survey and drawing. ISSUE 2. Excess & reduced cover for starter bars cast within CL slab: Starter bar projection = 900mm. Kicker already cast @ 150mm Remaining starter projection above kicker = 800mm ISSUE 3. The 640mm nib will be cast along with Wall CL-T-01. The Nib requires 2No. dowel bars for installation.
| 03SR - Stations (RfL) | Cxxx-NCR-001987 | NCR | Drip rebate covered - Concourse soffit |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-04-30 | 2016-04-14 09:50 | -16 | 2015-09-28 08:59 | Structural Engineering - Concrete Member | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | The drip rebate in the concourse soffit will in some locations be covered by the sub-platform diaphragm wall fireproofing coating.
| 03SR - Stations (RfL) | Cxxx-NCR-001988 | NCR | __-T-04_damaged MBT/starter bars & reduced cover & New CJ (__F-312) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-11-21 | 2015-11-04 14:12 | -17 | 2015-09-22 10:41 | Structural Engineering - Reinforcement | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Cxxx-SKC-C-DWG-B071_WS077-50524_X02_wall starter bars Cxxx-SKC-C-DWG-B071_WS077-51571_drilled bars survey&CJ Cxxx-SKC-C-DWG-B071-WS077-51605_C01___-L-105 & return wall __-T-04 __-T-04 drilled bars survey Cxxx-SWN-S-DDA-M171_2-01562 Cxxx-SWN-S-DDA-M171_2-01563 ISSUE 1. Starter bars and M__ couplers cast in slab damaged; reduced cover and snapped. Refer attached survey detailing locations: 14No. starter bars BM 54 damaged or bent over 3No. M__ couplers starters reduced cover 1No. M__ coupler starter snapped/cranked ISSUE 2. __-T-04 return wall missing reinforcement details. ISSUE 3. Connection details for __-L-105 & __-T-04 is not practicably constructible. Due to the location of the CJ this would make difficulty in threading the "L" shaped lacer connections into couplers as they would clash when threading in.
| 03SR - Stations (RfL) | Cxxx-NCR-001991 | NCR | Self Compacting Concrete Mix 444 (MCR 50477) – 2hr Placement Time exceeded (__F-283) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-11-30 | 2015-11-27 16:55 | -3 | 2015-09-23 12:15 | Structural Engineering - Structural Engineering - General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Specification Clause KF11.3221. - 2hr time limit from batching to end of placement exceeded. Details of the pours relating to this are as follows. Date Ticket Mix Location Time 15/09/15 894217 444 BLL C13 1st lift 2hr 59mins 15/09/15 894225 444 BLL C12 2nd lift 3hr 4mins
| 03SR - Stations (RfL) | Cxxx-NCR-001992 | NCR | IL-T-34 wall re-construction RC details (__F-314) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-02-29 | 2016-02-05 16:09 | -24 | 2015-09-23 14:34 | Structural Engineering - Reinforcement | 1500 |  | Planning | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Refer FCD-1863: Section of wall T-34 has been cut out (including reinforcement) to allow sufficient working space for construction of C16 elliptical column. Therefore the in-situ steel, as it stands currently is not sufficient to allow for proper connection when re-casting the 'cut out' section.
| 03SR - Stations (RfL) | Cxxx-NCR-001993 | NCR | SPL-T-01_soffit cast couplers & openings in wall (__F-316) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-02-05 | 2016-01-28 13:31 | -8 | 2015-09-23 15:23 | Structural Engineering - Reinforcement | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Drawings: Cxxx-SWN-S-DDC-M171_Z-04575 Cxxx-SKC-C-DWG-B071_WS077-52070 SPL-T-01 cover survey to vertical bars at CL soffit Issue 1: 2No. cast soffit couples at end bars missing. 2No. cast soffit couplers too close to opening. Refer attached survey for details. Issue 2: Excess cover (140mm) of 2No. soffit couplers. Issue 3: Reduced cover at south end of wall. Refer attached survey. Issue 4: Wall opening clashes with in-situ cast starter bars. Issue 5: Nib 50mm, as highlighted, no rebar detailing.
| 03SR - Stations (RfL) | Cxxx-NCR-001994 | NCR | HV Trench floor finish |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-01-06 | 2015-09-29 14:08 | -99 | 2015-09-28 08:55 | Structural Engineering - Finishes | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | This NCR will supersede the following NCRs NCR-1731, 1735, 1755, 1790, 1793, 1807, 1824, 1826, 1827, 1842, 1843, 1844, 1865, 1873, 1876, 1877 and 1973 These NCRs relate to the finish in the HV trench built into the sub-platform slab. A number of defects have been identified in the concrete finish of the HV trench through the sub-platform slab. This NCR covers the Blowholes/craters in the trench floor.
| 03SR - Stations (RfL) | Cxxx-NCR-001995 | NCR | HV Trench shamfer and side wall finish |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-04-30 | 2016-04-15 13:28 | -15 | 2015-09-28 08:58 | Structural Engineering - Finishes | 3500 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | This NCR will supersede the following NCRs NCR-1731, 1735, 1755, 1790, 1793, 1807, 1824, 1826, 1827, 1842, 1843, 1844, 1865, 1873, 1876, 1877 and 1973 These NCRs relate to the finish in the HV trench built into the sub-platform slab. A number of defects have been identified in the concrete finish of the HV trench through the sub-platform slab. This NCR covers Delamination of side walls and chipping to 50mmx50mm rebate.
| 03SR - Stations (RfL) | Cxxx-NCR-001996 | NCR | Elliptical Column C10 Flared Head - Damage to Architectural Finish Concrete (__F-318) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-04-30 | 2016-04-28 09:06 | -2 | 2015-09-26 12:46 | Structural Engineering - Finishes | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Damage to Architectural Finish Concrete when striking moulds. Refer attached photos. 1. Areas of damage to West side around the top shadow gap to the flared head. 2. Damage to East side of column above the cladding zone.
| 03SR - Stations (RfL) | Cxxx-NCR-001997 | NCR | Pull out bars missing for __-T-05 RC connection with __-L-25 (__F-319) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-12-07 | 2015-11-30 12:35 | -7 | 2015-09-28 09:21 | Structural Engineering - Reinforcement | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Drawings: Cxxx-SWN-S-DDC-M171_Z-04533 Cxxx-SWN-S-DDD-M171_2-01530_GA Cxxx-SKC-C-DWG-B071_WS077-51154_C01_prop Cxxx-SKC-C-DWG-B071_WS077-51158_C01___-L-25 Cxxx-SKC-C-DWG-B071_WS077-51594_C01___-T-05 Precast RC wall __-L-25 – lacers for wall __-T-05 are - One side FF2 pull-out bars have been installed. - On side NF2 there are NO pull-out bars or couplers installed Please refer to drawings and sketches for clarification.
| 03SR - Stations (RfL) | Cxxx-NCR-001998 | NCR | Intermediate Level: Slab infill Mole Hole 1 at Gl. 4 to 5 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-12-01 | 2015-11-12 16:04 | -19 | 2015-10-02 09:25 | Structural Engineering - Reinforcement | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Please refer to Drawings: Cxxx-SWN-S-DDA-M171_3-01567 Rev C06 Cxxx-SKC-C-DWG-B071_WS077-52045 Rev. C02 2 No BM 59 could not be engaged with its Herisson coupler because the couplers were cast-in at an angle. To resolve this issue, 2 No 25mm will be drilled and resined using __ Hit 500 to a depth of 700mm.
| 03SR - Stations (RfL) | Cxxx-NCR-001999 | NCR | Concourse Slab Soffit Damage - GL 7.5D |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-04-30 | 2016-04-28 10:34 | -2 | 2015-09-29 10:32 | Civil - Civil Engineering General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A section of concrete approx. 600mm long has been broken off the underside of the Concourse slab soffit. The damage is located on the north face of the opening at GL 7.5/D. The fault occurred during removal of the blinding for the excavation works below concourse slab.
| 03SR - Stations (RfL) | Cxxx-NCR-002000 | NCR | Concourse Slab C1 Soffit Damage GL D/2-3 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-03-25 | 2016-03-17 09:35 | -8 | 2015-09-29 14:35 | Civil - Civil Engineering General | 2500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A section of concrete approx. 500mm long has been broken off the underside of the soffit to C1 GL D/2-3 at the Tunnel Ventilation Fan Opening during removal of the blinding for the excavation works below concourse slab.
| 03SR - Stations (RfL) | Cxxx-NCR-002001 | NCR | Concourse Slab Soffit Damage - GL 7.5/D-E |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-01-31 | 2016-01-26 14:30 | -5 | 2015-09-30 09:20 | Civil - Civil Engineering General | 2500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A section of reinforcement has been exposed on the soffit of the Concourse slab while attempting to remove blinding concrete (see picture below). The damage is located north of the opening at GL 7.5/D.
| 03SR - Stations (RfL) | Cxxx-NCR-002002 | NCR | Damage to IPI E17-14 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-11-19 | 2015-10-16 12:28 | -34 | 2015-09-30 16:29 | Surveying - Instrumentation and Monitoring | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | In-Place Inclinometer E17-14 was damaged on 29/09/2015 as a result of changes to the haul road access. Following placement of a crawler crane to the south of the instrument the traffic barriers were repositioned around the crane. This new arrangement removed protection and directed traffic within the vicinity of the up stand cover as shown in the attached photographs. The cable between the IPI instrument and transmitter box has since been severed and the up stand cover in now loose. Results from the latest trend plot also show loss of data form the instrument (see attached plot) on 29/09/2015.
| 03SR - Stations (RfL) | Cxxx-NCR-002003 | NCR | Int 4-5 Infill - BM50, 1no. cut. |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-11-26 | 2015-11-02 11:41 | -24 | 2015-09-30 15:48 | Structural Engineering - Reinforcement | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 1no. BM 50 has been cut short as it protrudes into the Infill opening, and lapped with a B25 T2/B2 U bar bent on site. This has been caused by an intermediate slab coupler positioned at the wrong angle.
| 03SR - Stations (RfL) | Cxxx-NCR-002004 | NCR | SPL-T-08_Reduced cover to soffit cast couplers and missing (__F-322) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-02-05 | 2016-01-28 13:30 | -8 | 2015-10-01 12:58 | Structural Engineering - Reinforcement | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Drawing Cxxx-SWN-S-DDD-M171_5-01500_PL Cxxx-SKC-C-DWG-B071_WS077-52074_SPL-T-08 SPL-T-08 survey soffit CL SPL-T-08 soffit of Concourse level: ISSUE 1. Reduced cover to coupled soffit starters on the West & East ISSUE 2. 4No. soffit couplers missing from the North wall end ISSUE 3. 4No. soffit couplers at the South wall end are cast in too close to the adjacent precast unit (i.e. they are abutting the PC unit).
| 03SR - Stations (RfL) | Cxxx-NCR-002005 | NCR | Elliptical Column C12 Flared Head - Damage to Architectural Finish Concrete (__F-324) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-04-30 | 2016-04-28 08:55 | -2 | 2015-10-03 10:29 | Structural Engineering - Finishes | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Damage to Architectural Finish Concrete when striking moulds. Refer attached photos. 1. Areas of damage to South side around the shadow gap below the flared head. 2. Damage to West side around the shadow gap below the flared head.
| 03SR - Stations (RfL) | Cxxx-NCR-002007 | NCR | West Liner Wall (southern section) All issues (__F-330) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-12-08 | 2015-11-27 16:56 | -11 | 2015-10-09 09:55 | Structural Engineering - Reinforcement | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Drawing Cxxx-SWN-S-DDA-M171_6-01522 Cxxx-SKC-C-DWG-B071_WS077-51630_CL slab bottom mat Cxxx-SKC-C-DWG-B071_WS077-51633_CL slab section Cxxx-SKC-C-DWG-B071_WS077-51776_mark up all issues Cxxx-SKC-C-DWG-B071_WS077-51777_section Issue 1: Soffit cast firsty couplers 9No. have been cast out of position (refer asbuilt dimensions on attached drawing mark-up) due to clashing with d/wall couplers/congestion rebar as shown in section 51633 CL. Wall is 450 thick + the gap behind the d/wall (max. 300mm). Issue 2: D/wall cast firsty couplers, approx. 4No. have been cast out of position (refer asbuilt dimensions on attached drawing mark-up). Issue 3: Approx 4No. South side Dwall cast firsty couplers damaged.
| 03SR - Stations (RfL) | Cxxx-NCR-002008 | NCR | Infills to Non Stuctural walls (__F-331) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-07-15 | 2016-06-17 13:34 | -28 | 2015-10-09 12:24 | Structural Engineering - Reinforcement | 1500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Refer attached "Intermediate Slab Infill.pdf" for detail of the locations in question: Issue 1: Cast in protruding B12 lacer bars have been bent back to enable sufficient working space required to undertake adjacent works on structural columns. The time has come to use these bars for RC connection to complete non-structural walls to full length. Issue 2: Damaged/Missing couplers Issue 3: Damage to Concrete to Structural Column while exposing couplers Issue 4. Bent or missing starter bars. Issue 5. Reduced lap length for lacers. This is due to only a small length of the wall remaining to be cast (i.e. the length of wall which remains to be cast is shorter than the specified B12 lap length)
| 03SR - Stations (RfL) | Cxxx-NCR-002009 | NCR | CL-T-01 Opening Out of Position (__F-333) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-12-08 | 2015-11-12 16:14 | -26 | 2015-10-09 17:45 | Structural Engineering - Structural Engineering - General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A shutter forming the south side of opening to wall CL-T-01 shifted during concreting causing the opening not to be formed square. Refer attached photos for clarification
| 03SR - Stations (RfL) | Cxxx-NCR-002011 | NCR | Elliptical Column C13 Flared Head - Damage to Architectural Finish Concrete (__F-332) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-11-20 | 2016-09-21 16:11 | -60 | 2015-10-14 17:24 | Structural Engineering - Finishes | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Damage to Architectural Finish Concrete when striking moulds. Refer attached photos. 1. Areas of damage to South side around the top shadow gap to the flared head. 2. Damage to North side of column above the cladding zone.
| 03SR - Stations (RfL) | Cxxx-NCR-002012 | NCR | Walls - SPL-L-01 and SPL-L-08: GL B&D/3-4 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-12-11 | 2015-12-11 16:03 | 0 | 2015-10-12 11:21 | Structural Engineering - Concrete Member | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Please refer to Drawing Cxxx-SWN-S-DDA-M171_6-01522 Rev. C10 Cxxx-SKC-C-DWG-B071_WS077-51808 Rev. C01 Cxxx-SKC-C-DWG-B071_WS077-51810 Rev. C02 SPL-L-01 Issue 1: The wall steps in by 225mm at platform level. 2No. Near face starter bars on the column C3-N are cast out of the PL wall 225mm (see sketch below). __F propose cut flush the bars that are out of position and drill and fix 2No. B12 at the required location at 525mm embed using __ Hit 500 Resin. Issue 2: 2No. slab threaded starter bar are damaged and cannot be used. __F propose to drill and fix 2No. B12 bars at 525mm embed. at the same location using __ Hit 500 Resin. SPL-L-08 Issue 3: The wall steps in by 225mm at platform level. 2No. Near face starter bars on the column C3-S are cast out of the PL wall 225mm (see sketch below). __F propose cut flush the bars that are out of position and drill and fix 2No. B12 at the required location at 525mm embed. using __ Hit 500 Resin Issue 4: 3No. slab starter bars were below the box opening. Cxxx/ agreed to omit the 3No. starter bars. Issue 5: 1No. Near face starter bars on the column C4-S are cast out of position (see attached RC drawing). __F propose keep the starter bar as it is but drill and fix 1No. B12 at the required location at 525mm embed. using __ Hit 500 Resin.
| 03SR - Stations (RfL) | Cxxx-NCR-002013 | NCR | Scabbling back Dwall Panels no Inspection requests rasied (LIGHTWELL ONLY) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-02-16 | 2016-02-04 15:46 | -12 | 2015-10-12 11:53 | Structural Engineering - Concrete Member | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | Please see Cxxx-NCR-001453 - This NCR has been raised to allow the closeout of 1453 as areas in the lightwell are currently not accessible. The face of many of the Dwall panels has been scabbled back without giving the PM's team the opportunity to inspect, there is no specific WPP in place to indicate how depth control was achieved, nor an ITP requiring a test to prove the remaining cover. This is in contravention of part 20 of the works information. This has occurred on south side panels N42, 43, 50, 51.
| 03SR - Stations (RfL) | Cxxx-NCR-002014 | NCR | Windpost non-conforming welds from independant N__ report |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-06-15 | 2016-05-13 13:49 | -33 | 2015-10-12 13:34 | Architectural - Brickworks/Blockworks | 200000 |  | Manufacturing Defect | Rework | 1 (>60k) | Complete | Material/Preservation Problems - Other | Completed |  | An N__ test survey report produced independently by __s, carried out 19 N__ tests on butt welds that were accessible on site. The N__ test used ultrasonic and surface (dye penetrant) testing methods. 8 of the 19 butt welds tested were confirmed as non-conforming to the requirement of ISO 5817 Level B or C.
| 03SR - Stations (RfL) | Cxxx-NCR-002015 | NCR | IL Intermediate – Slab (Temporary Opening) Infill GL4-5 – 1hr Concrete placement time exceeded |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-12-01 | 2015-11-19 09:36 | -12 | 2015-10-12 15:37 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | 1hr limit for fresh concrete to be placed against fresh concrete (Spec KF11:3205 h) exceeded between ticket Nos. 807175 and 807184 (1hr 5mins) 807200 and 807205 (1hr 25mins)
| 03SR - Stations (RfL) | Cxxx-NCR-002016 | NCR | Concourse slab Soffit damage - GL 11/D_E NW corner opening |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-03-30 | 2016-03-22 14:58 | -8 | 2015-10-16 13:38 | Structural Engineering - Reinforcement | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Damage to concrete on the NW corner of the opening downstand. Area of reinforcement is exposed
| 03SR - Stations (RfL) | Cxxx-NCR-002017 | NCR | Cavity drainage missing cube results |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-03-18 | 2016-03-17 09:43 | -1 | 2015-10-19 09:19 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | There is missing cube results for screed batches used in the construction of concourse and intermediate level cavity drainage.
| 03SR - Stations (RfL) | Cxxx-NCR-002018 | NCR | DLR-L-10 Post fix horizontal lacers |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-12-18 | 2015-11-16 13:28 | -32 | 2015-10-19 16:31 | Structural Engineering - Load Bearing Walls | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Misalignment of couplers has meant that cover is not achieved on 3no Horizontal lacer bars located at the bottom of wall __-L-10.
| 03SR - Stations (RfL) | Cxxx-NCR-002019 | NCR | BLL Wall 2 - Excess Cover |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-01-21 | 2016-01-26 14:33 | 5 | 2015-10-19 17:32 | Structural Engineering - Structural Engineering - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The north side of the shutter on BLL wall pour 2 moved whilst being poured. This has lead to excess cover, up to 70mm, on the north side of the wall.
| 03SR - Stations (RfL) | Cxxx-NCR-002020 | NCR | West Sump - Blinding and pile backfill - Low 56day cube result |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-12-21 | 2015-10-30 11:31 | -52 | 2015-10-22 14:48 | Civil - Civil Engineering General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | 56day cube result of 39.4N/mm2 failed to achieve the mix design requirement of 45N/mm2 at 56days. (Refer to MCR Cxxx-SKC-O-TSC-B071_WS077-50203). 7 and 28 day results were as follows: 1990A 7day: 22.0N/mm2 1990B 28day: 35.9N/mm2 1990C 28day: 36.3N/mm2
| 03SR - Stations (RfL) | Cxxx-NCR-002021 | NCR | East Liner Wall firsty coupler damaged. |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-12-23 | 2015-12-02 16:53 | -21 | 2015-10-26 12:29 | Structural Engineering - Reinforcement | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A 40dia soffit firsty coupler has been damaged beyond usable condition and therefore cannot be engaged to form the NF2 reinforcement(find attached photo). Coupler is located approx. 4.350m from the south.
| 03SR - Stations (RfL) | Cxxx-NCR-002022 | NCR | Installation of Mterials not accepted non MCR process |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2015-11-30 | 2015-11-19 10:28 | -11 | 2015-10-26 12:46 | Mechanical - Public Health Engineering | 2500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Lack or improper material identification and traceability | Completed |  | The product accepted through the MCR process for a pumping main cast into the base slab of the BLL adit was not installed within the slab, instead an alternative product was sourced and installed. this alternative product does not have the assurance documentation nor is it accepted via the MCR process. Consequently the pour di not occur last week.
| 03SR - Stations (RfL) | Cxxx-NCR-002023 | NCR | IL-T-27 infill 250mm kwikastrip installed |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-11-30 | 2015-11-12 16:14 | -18 | 2015-10-26 13:31 | Structural Engineering - Reinforcement | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | A 250mm kwikastrip has been cast in to wall IL-L-37 to allow for a construction joint from IL-L-37 to IL-T-27. IL-T-27 wall thickness is 300 and therefore the pull out bar will compromise cover on the eastern face of the wall.
| 03SR - Stations (RfL) | Cxxx-NCR-002024 | NCR | East Liner wall soffit 652mm gap between couplers. |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-12-22 | 2015-12-21 11:21 | -1 | 2015-10-26 14:13 | Structural Engineering - Reinforcement | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Between the 3rd & 4th NF2 coupler from the north there is a gap of 652mm. Therefore vertical c/c of 150mm is not met. The correct number of bars are in NF2 reinforcement layer.
| 03SR - Stations (RfL) | Cxxx-NCR-002025 | NCR | Cover on non-structural walls |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-06-30 | 2016-05-19 16:25 | -42 | 2015-10-27 08:12 | Structural Engineering - Reinforcement | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Concourse slab couplers are located to provide min 30mm cover to walls CL-L-20 & CL-T-24.
| 03SR - Stations (RfL) | Cxxx-NCR-002026 | NCR | Missing couplers in concourse level slab for walls CL-L-20, CL-T-24 & CL-T-25 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-03-25 | 2016-02-23 12:43 | -31 | 2015-10-27 08:28 | Structural Engineering - Reinforcement | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Wall couplers are missing in the concourse level slab at the location of non-structural walls CL-L-20, CL-T-24 & CL-T-25. CL-L-20: 1 coupler is missing. CL-T-24: 2 couplers are missing. CL-T-25: 6 couplers are missing.
| 03SR - Stations (RfL) | Cxxx-NCR-002028 | NCR | East Liner Wall 9no soffit couplers missing. |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-12-18 | 2015-12-10 11:15 | -8 | 2015-10-27 12:15 | Structural Engineering - Reinforcement | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There are 9no soffit couplers missing at the soffit at the East liner wall. (See attachment for approx. locations) 3 in north & 6 in south section of East liner wall.
| 03SR - Stations (RfL) | Cxxx-NCR-002029 | NCR | CL – Non Structural Walls – Infill Sections |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-06-30 | 2016-06-17 13:37 | -13 | 2015-10-28 11:37 | Structural Engineering - Reinforcement | 1500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Request that project requirements from Cxxx-NCR-002008 for the Intermediate level non-structural walls apply to the Concourse level non-structural walls which reads: "Issue 1: Cast in protruding B12 lacer bars have been bent back to enable sufficient working space required to undertake adjacent works on structural columns. The time has come to use these bars for RC connection to complete non-structural walls to full length. Issue 2: Damaged/Missing couplers Issue 3: Damage to Concrete to Structural Column while exposing couplers Issue 4. Bent or missing starter bars. Issue 5. Reduced lap length for lacers. This is due to only a small length of the wall remaining to be cast (i.e. the length of wall which remains to be cast is shorter than the specified B12 lap length) "
| 03SR - Stations (RfL) | Cxxx-NCR-002030 | NCR | East Liner wall South side angled couplers |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-12-16 | 2015-12-15 10:27 | -1 | 2015-10-28 08:15 | Structural Engineering - Reinforcement | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Couplers in the D-wall panel are angled, therefore when NF2 reinforcement bars are installed the distance is made greater which effects cover.
| 03SR - Stations (RfL) | Cxxx-NCR-002031 | NCR | BLL Wall 12/East wall - Lacer Arrangement and reduced cover. |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-03-27 | 2016-02-27 11:33 | -29 | 2015-10-28 08:50 | Structural Engineering - Reinforcement | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Drawing Cxxx-SKC-C-DWG-B071_WS077-51793_mark up The rebar arrangements previously agreed in Cxxx-FCD-001905, Cxxx-FCD-001911, Cxxx-FCD-001918, Cxxx-FCD-001930 changed to incorporate B16 to NF1 lacer and B32/B25 bars to be moved on NF3 layer. However, Wall No. 12 (East wall) has couplers cast into the sub platform slab with 45mm cover to NF2 vertical threaded bar (BM02/BM03), at the return from the east wall into the south wall (GL: D/13+). The lacers in this location have been changed to suit, as following: /__F propose to replace the B16 NF1 with doubled B12 bars coupled bars allowing min. cover of 33mm. The following arrangements can be fixed at the top of the wall: 6No. NF1 B12 lacers doubled to replace B16mm (cover remaining 33 mm) 3No. B16 NF1 left - as per Cxxx-FCD-001930 9No. B32 moved from NF1 to NF3 to allow cover to face. Top 2no. Lacers FF1 B16 Top 2no. Lacers FF3 B32/B25 Please see attached marked up drawing for clarity.
| 03SR - Stations (RfL) | Cxxx-NCR-002032 | NCR | East Liner Wall D-wall/slab coupler interface. |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-01-28 | 2016-01-19 14:24 | -9 | 2015-10-28 16:36 | Structural Engineering - Reinforcement | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | NF1 & NF2 Couplers have been cast into the slab and D-wall on the same plane. Therefore approx 15no reinforcement bars clash when engaging them to said couplers. There is a similar case on the FF2 however it occurs for one vertical bar only. (see photos). ***Further findings whilst installing steel showed that a clash occurs in 9no locations not 15 as approximated as the bars were placed in the NF3. Therefore 9no bars were post fixed to NF3 adjacent to couplers. ***2no additional locations 1no NF2 & 1no FF2 were found to clash and were therefore post fixed bars were installed adjacent to couplers. ***The 1no vertical bar in FF2 was found to clash at only 2no locations, therefore the vertical bar remained engaged. 2no horizontal post fixed bars were installed adjacent to couplers.
| 03SR - Stations (RfL) | Cxxx-NCR-002033 | NCR | __-T-19 missing bar & incorrect centres to ES4. |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-11-20 | 2015-11-19 11:54 | -1 | 2015-10-28 18:00 | Structural Engineering - Reinforcement | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 1No 16dia bar cast in coupler in the wall __-T-19 is no engaged. The bar is part of the T2 layer of ES4 slab reinforcement. Additionally 3no bars (BM22 & BM62) in top and bottom mats are also at incorrect centres (12/16 alternating diameter bars at between 270-230mm c/c ).
| 03SR - Stations (RfL) | Cxxx-NCR-002034 | NCR | ES4 Minimum lap length not achieved |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-11-20 | 2015-11-19 11:53 | -1 | 2015-10-30 13:52 | Structural Engineering - Reinforcement | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | At slab ES4 GL/8-9 6No 12dia bars (BM-61) have a reduced lap length of 450mm where 950mm is detailed.(see annotated DWG)
| 03SR - Stations (RfL) | Cxxx-NCR-002035 | NCR | __-L-45 Cabinet recess waterproof. |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-12-15 | 2015-11-20 14:31 | -25 | 2015-11-02 17:05 | Structural Engineering - Joints | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The external joint at cabinet recess wall __-L-45 requires the waterproof detail of an __ hydrophilic strip to run along the construction joint. Due to works conducted for the close out of Cxxx-RFI-002685, rebar has been exposed to post fix some starter bars and will not provide a suitable surface to install the __ hydrophilic strip.
| 03SR - Stations (RfL) | Cxxx-NCR-002036 | NCR | E__ Slab ES4 reinforcement steel at canopy column location at GL/9. |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-11-22 | 2015-11-16 13:30 | -6 | 2015-11-02 18:26 | Structural Engineering - Reinforcement | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Canopy column base steel reinforcement congestion has lead to 5no steel bars in B2 layer being omitted and centres in T2 being incorrect in 2no locations when constructing slab ES4's reinforcement. This issue has previously been addressed in Cxxx-RFI-001357.
| 03SR - Stations (RfL) | Cxxx-NCR-002037 | NCR | Concourse Opening GL8-9 Reinforcement Detailing |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-03-11 | 2016-03-10 12:26 | -1 | 2015-11-05 10:21 | Structural Engineering - Reinforcement | 2500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Concourse level opening at GL8-9 contains the following reinforcement detailing issues, discussed on site and proposals agreed in reinforcement meeting (02/11/2015) between __, Cxxx & . Issue 1: Openings have been omitted from C05 and are now included in east side of the GL8-9 opening. Therefore, rebar re-detailing has been agreed with Cxxx to leave reinforcement as per detail, but cut short straight bars and splice with 2No. B25 L-Bars. The lap length on the south side is limited due to the location of the opening CJ. Cxxx to confirm any requirement for post drilling these B25 bars at 700mm embedment. This is not an NCR, but recorded here for clarity. Issue 2: A 420mm gap (C/C) is present in the spacing of the B40 B1 BM02 bars on the south side. This is believed to have been due to gantry crane fixings. Proposal, as agreed, is to post drill and resin 1No. B25 at 700mm embed and 1000mm projection. Issue 3: B40 B2 BM35 is detailed for 9No. bars, however in the South-East corner only 8No. couplers have been exposed. 1No. bar is believed to be cast into the slab. 9No. couplers have been located in the top mat. Issue 4: 1No. B32 B2 BM27 coupler clashes with a U-Bar cast into the slab. Proposal, as agreed, is to drill 1No. B25 at 700mm embedment and 1000mm projection. Issue 5: In the North-West corner 1No. B40 B2 BM14 clashes with CJ. Proposal, as agreed, is to post drill 1No. B25 at 700mm embed and 1000mm projection. Issue 6: Investigation has shown this issue to no longer be relevant. Issue 7: 3No. B32 (T2 layer) BM61 in the North East corner clash with 3No. B40 T1 BM59. Proposal, as agreed, to cut back T2 BM61 B32 to enable T1 bars to be engaged and post drill at each B32 bar location B25mm at 700mm embed with min. 1000mm projection. Issue 8: BM64 bars/couplers are not as detailed due to opening moved west. Cxxx proposal is to use bob bars, with the bob turned outwards. The same number of bars, 6 @200 spacing, as detailed, are to be used. This is not an NCR, but recorded here for clarity.
| 03SR - Stations (RfL) | Cxxx-NCR-002038 | NCR | Wall IL-L-27 Infill sections out of position. |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-02-09 | 2016-02-03 15:10 | -6 | 2015-11-05 14:38 | Structural Engineering - Formwork | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | South side of infill sections adjacent to columns C22S and C23S are not flush with the existing sections of wall IL-L-27. Up to 15mm step.
| 03SR - Stations (RfL) | Cxxx-NCR-002039 | NCR | SPL : Structural Walls and Columns :Self Compacting Concrete Mix 444 (MCR 50477) – 2hr Placement Time exceeded (__F-339) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-01-21 | 2016-01-14 13:22 | -7 | 2015-11-06 12:46 | Structural Engineering - Structural Engineering - General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | LOCATION: SPL - GL 9,10,14,15 & 16 Specification Clause KF11.3221. 2hr time limit from batching to end of placement exceeded for the following pours as detailed below. Date; Ticket; Mix; Location; Time; 18/06/15; 725748; 444; C5 N&S 1st Lift; 2hr 33mins 18/06/15; 725758; 444; C16 1st Lift; 2hr 30mins 20/06/15; 806732; 444; C10 2nd Lift; 2hr 16mins 25/06/15; 725318; 444; BLL C15 Kicker & C5 N&S 1st Lift; 2hr 30mins 14/07/15; 810819; 444; C15 2nd lift & SPL-T-04 Kicker; 2hr 30mins 28/07/15; 812271; 444; C16 3rd Lift; 2hr 8mins 31/07/15; 813602; 444; C14 3rd Lift; 2hr 1 min 25/08/15; 892315; 444; C9 Kicker; 2hr 31mins 25/08/15; 892363; 444; C15 3rd Lift & C13 kicker; 2hr 51mins
| 03SR - Stations (RfL) | Cxxx-NCR-002040 | NCR | Sub-platform walls - SPL-L-52 kicker - pressure relief duct holes with insufficent cover. |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-02-05 | 2016-01-29 12:05 | -7 | 2015-11-06 13:08 | Civil - Drainage | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | In SPL-L-52 between GL 5-6.5 and GL 11-14, void formers to form the pressure relief duct holes were installed without the required cover in the kicker pour. See attached photographs
| 03SR - Stations (RfL) | Cxxx-NCR-002041 | NCR | SPL Elliptical Columns : C9-C11 and C14-16 - Damage to recess for cladding – First Lift (__F-279) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-08-20 | 2016-07-16 11:44 | -35 | 2015-11-06 13:30 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Damage to Plain finish of columns: 1. Spalling of concrete edges at the cladding recess at the top of lift one (refer photo 1). 2. Section of lower nib to the north side of the drainage recess broke off during striking of the shutters (C9 only) (refer photo 2). 3. Breaking off of the vertical edges to the drainage recess nibs on columns C9 and C15 (refer photo 3).
| 03SR - Stations (RfL) | Cxxx-NCR-002042 | NCR | CL Elliptical Columns: Self Compacting Concrete Mix 295 (MCR 50487) – 2hr Placement Time exceeded (__-355) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-01-08 | 2016-01-12 15:31 | 4 | 2015-11-09 12:30 | Structural Engineering - Structural Engineering - General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Date; Ticket; Mix; Location; Time; 27/08/15; 894512; 295; CL EC 9&10 1st Lift; 2hr 38mins; Specification Clause KF11.3221. 2hr time limit from batching to end of placement exceeded for the above pours.
| 03SR - Stations (RfL) | Cxxx-NCR-002043 | NCR | Wall CL-L-35: 1hr Time between loads exceeded : Concrete Mix 263 (MCR 50319) (__-356) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-01-21 | 2016-01-14 13:23 | -7 | 2015-11-09 17:47 | Structural Engineering - Structural Engineering - General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Location Description: CL-L-35 GL20-21/D Date; Ticket; Mix; Location; Time between Loads; 04/11/15; 898806 & 898821; 263; CL-L-35; 2hr 5mins; Specification Clause KF11.3204. Fresh concrete shall not be placed against existing fresh in-situ concrete which has been in position for more than 60 minutes.
| 03SR - Stations (RfL) | Cxxx-NCR-002044 | NCR | Concourse Level: Columns & Wall connection 350mm return (__-1355) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-01-21 | 2016-01-14 13:28 | -7 | 2015-11-09 13:31 | Structural Engineering - Reinforcement | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Refer attached marked up drawings to clarify location details: These short length section of walls were left out temporarily to allow for construction of the adjacent square columns. It is noted that the infill gaps remaining to be cast are only 350mm long. Therefore, the lap lengths of the B12 lacers here are only able to achieve ~300mm lap. We note that these walls are a non-structural element. Please confirm this is acceptable.
| 03SR - Stations (RfL) | Cxxx-NCR-002045 | NCR | CL-T-08 Non-structural wall 200mm kwickastrip installed. |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-01-08 | 2015-12-10 14:50 | -29 | 2015-11-09 16:24 | Structural Engineering - Reinforcement | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A 200mm kwikastrip has been cast in to wall CL-L-50 to allow for a construction joint from CL-L-50 to CL-T-08. CL-T-08 wall thickness is 250 and therefore the pull out bar will compromise cover on the eastern face of the wall. (Similar occurrence as NCR-2023).
| 03SR - Stations (RfL) | Cxxx-NCR-002046 | NCR | East liner wall damaged D-wall couplers |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-12-18 | 2015-12-15 13:59 | -3 | 2015-11-11 15:18 | Structural Engineering - Reinforcement | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 5No couplers could not be engaged with steel bars due to prior damage. (bar locations highlighted yellow in embedment survey)
| 03SR - Stations (RfL) | Cxxx-NCR-002047 | NCR | Heat damage to structural wall GL 17 from plunge column removal |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2017-05-18 | 2017-05-12 16:21 | -6 | 2015-11-11 14:26 | Civil - Structural Engineering | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | External Phenomenon - Other | Completed |  | During removal of plunge column 39 the adjacent structural wall has suffered heat damage.
| 03SR - Stations (RfL) | Cxxx-NCR-002048 | NCR | BLL Lining wall 14 shutter movement |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-01-29 | 2016-01-29 12:08 | 0 | 2015-11-11 17:09 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During BLL lining wall pour 14 (02/11/2015), the top section of the shutter bulged out. See attached drawings and photos for clarification.
| 03SR - Stations (RfL) | Cxxx-NCR-002050 | NCR | Heat damage to strutural wall T01 at concourse level |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-05-01 | 2017-03-30 12:58 | -32 | 2015-11-12 15:43 | Civil - Civil Engineering General | 2500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Due to burning operations on PC8 structural wall T01 has sustained surface heat damage on the concourse at slab level.
| 03SR - Stations (RfL) | Cxxx-NCR-002051 | NCR | CL-T-08 non-structural wall 1hour between loads and use of SCC Mix 295 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-01-15 | 2015-12-11 09:19 | -35 | 2015-11-16 08:29 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Upon post pour inspection of non-structural section of wall CL-T-08 pour, a line is visible on the face of the concrete (photo attached) and therefore this pour was investigated to find that there had been a pause in concrete placement greater than 1 hour. Details to add: This is the non-structural part of the wall CL-T-08, (reduced thickness of 250mm and has soft top). The mix used was a self compacting mix and therefore no vibration took place throughout the pour. Concrete grade used RC40/50 has higher strength than that specified for Non-Structural walls RC35/45INT. The initial set time for this mix is 5hrs 30mins which is far in excess of the 2hrs between loads 054407 & 054432. (Refer also to previous closed Cxxx-NCR-001980).
| 03SR - Stations (RfL) | Cxxx-NCR-002052 | NCR | BLL lining wall surface water |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-05-01 | 2017-05-02 12:56 | 1 | 2015-11-16 12:13 | Civil - Civil Engineering General | 10000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | At the construction joint between BLL lining walls 2 and 3 (see attached), there has been surface water identified at 3 locations (see mark-up).
| 03SR - Stations (RfL) | Cxxx-NCR-002053 | NCR | IL Elliptical Columns: Self Compacting Concrete Mix 295 (MCR 50487) – 2hr Placement Time exceeded ticket (__-362) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-01-15 | 2016-01-14 13:19 | -1 | 2015-11-16 16:16 | Structural Engineering - Structural Engineering - General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Specification Clause KF11.3221. 2hr time limit from batching to end of placement exceeded for the below pours. Date; Ticket; Mix; Location; Time; 27/08/15; 893988; 295; IL-C9 1st lift and kickers C16 & T-05; 2hr 11mins 17/09/15; 894429; 295; IL-C16 3rd lift & IL-C9 4th Lift; 2hr 9 mins
| 03SR - Stations (RfL) | Cxxx-NCR-002054 | NCR | Slab ES4 Poured without approved MCR approval for concrete mix. |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-01-16 | 2015-12-21 11:20 | -26 | 2015-11-17 08:39 | Materials - Approval | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Slab ES4 was poured on 04/11/15 using C40/50 FND (20mm Aggregate) concrete MCR Cxxx-SKC-O-TSC-B071_WS077-50054 which was approved on 12/11/15.
| 03SR - Stations (RfL) | Cxxx-NCR-002055 | NCR | WLW Water seepage though < 0.3mm cracks. |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-10-01 | 2019-03-26 08:06 | 176 | 2015-11-17 17:47 | Civil - Civil Engineering General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Previous Construction - Other | Completed |  | Water found seeping through <0.3mm cracks in WLW North section. (See attachment)
| 03SR - Stations (RfL) | Cxxx-NCR-002056 | NCR | non-structural wall CL-L-35 GL D/21 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-01-18 | 2016-01-14 13:20 | -4 | 2015-11-19 08:41 | Structural Engineering - Finishes | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Wall was constructed in separate pours, when second pour was completed it was made apparent that there was a 15mm step in the wall as the formwork had failed (see IMG_2017).
| 03SR - Stations (RfL) | Cxxx-NCR-002058 | NCR | BLL Elliptical columns GL/12 and 13 Exceedance of 2Hr between batching and final placement |  | Contr | SKC | PAD - Paddington Station (West) |  | 2015-12-19 | 2015-12-08 11:21 | -11 | 2015-11-19 16:40 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | LOCATION: SPL - GL 12 & 13 Specification Clause KF11.3221. 2hr time limit from batching to end of placement exceeded for the following pours as detailed below. Date; Location; Time; 15/09/15 EC BLL C13 1st Lift 2hr 59mins 15/09/15 EC BLL C12 2nd Lift 3hr 4mins 17/09/15 EC BLL C12 3rd lift & C13 2nd lift 2hr 15mins 18/09/15 EC BLL C12 4th lift 2hr 17mins 25/09/15 EC BLL C13 4th lift & SPL-T-01 kicker 2hr 10mins
| 03SR - Stations (RfL) | Cxxx-NCR-002059 | NCR | Sub-platform walls - Damaged corbel on SPL-L-52 GL 5-6 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-01-23 | 2015-12-11 16:13 | -43 | 2015-11-24 18:19 | Structural Engineering - Concrete Member | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please refer to Drawing Cxxx-SWN-S-DDA-M171_6-01522 and Cxxx-SKC-C-TSC-B071_WS077-52409, and MCR record Cxxx-SKC-O-TSC-B071_WS077-50319 Wall SPL-L-52 between gridlines 5-6 was poured Afternoon of Friday 20th November. The formwork was struck on Saturday 21st November Morning. Due to early striking, the corbel was damaged.
| 03SR - Stations (RfL) | Cxxx-NCR-002060 | NCR | Wall __-L-45 Out of Position at GL20-21 (__-373) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-04-30 | 2016-04-14 09:31 | -16 | 2015-11-26 09:51 | Structural Engineering - Structural Engineering - General | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Location: Departures Road Level GL D+2.85m/20-21 Stop end of wall to East side of the opening is not square and out of position. See attached photo, as-built position and cover survey.
| 03SR - Stations (RfL) | Cxxx-NCR-002061 | NCR | (SC1) SPL Structural walls and columns: Self Compacting Concrete Mix 444 (MCR 50477) – 2hr Placement Time exceeded (__-372) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-01-21 | 2016-01-14 13:36 | -7 | 2015-11-26 10:02 | Structural Engineering - Structural Engineering - General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Specification Clause KF11.3221. 2hr time limit from batching to end of placement exceeded for the pours as detailed in the attached table.
| 03SR - Stations (RfL) | Cxxx-NCR-002062 | NCR | PES/PSD - Missing/damaged cast-in couplers |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-05-03 | 2016-04-12 16:21 | -21 | 2015-11-30 16:29 | Structural Engineering - Bolted Connections | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | A small number of couplers cast into the soffit of the concourse slab, to support pre-cast smoke ducts, have been damaged or not found/cast in. Please see attached photos and drawing layout for locations.
| 03SR - Stations (RfL) | Cxxx-NCR-002063 | NCR | Omission of edge fillets on exposed concrete arrises |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-02-16 | 2016-02-05 16:12 | -11 | 2015-12-01 15:50 | Structural Engineering - Structural Engineering - General | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | In various locations on site, exposed arrieses of concrete have been cast without edge fillets.
| 03SR - Stations (RfL) | Cxxx-NCR-002064 | NCR | PES/PSD - 4 no. Smoke ducts cast without up rev'd ITP |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-01-27 | 2016-01-20 14:46 | -7 | 2015-12-02 09:15 | Structural Engineering - Concrete Member | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Precast Fabrication ITP, Cxxx-SKC-C-ITP-B071_WS077-50100, has been accepted Code 2. 4no. Smoke ducts were cast on 01/12/15, with welded reinforcement cages, without a new revision of the Precast Fabrication ITP to include welded cages.
| 03SR - Stations (RfL) | Cxxx-NCR-002065 | NCR | Missing Cube Results for Screed - Roof Slab Waterproofing |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-11-15 | 2016-11-15 14:44 | 0 | 2015-12-03 11:19 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Cubes results for screed used as a protection layer to the Roof Slab Waterproofing, Eliminator System are not available. Dates and volumes below; Date - Vol m3 3rd October 2013 - 107.8 4th October 2013 - 21.4 (Cubes available) 8th October 2013 - 46.2 22nd October 2013 - 35.1 8th November 2013 - 27.1 22nd November 2013 - 11 4th December 2013 - 15.4 13th December 2013 - 6 17th December 2013 - 15.4 20th December 2013 - 7.7
| 03SR - Stations (RfL) | Cxxx-NCR-002066 | NCR | BLL Elliptical Columns: Self Compacting Concrete Mix 444 (MCR 50477) – 2hr Placement Time exceeded (__F-363) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-01-21 | 2016-01-14 14:04 | -7 | 2015-12-02 13:12 | Structural Engineering - Structural Engineering - General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Location Description; BLL Elliptical Columns GL12 and GL13 Specification Clause KF11.3221. 2hr time limit from batching to end of placement exceeded for the following pours. Date; Ticket; Mix; Location; Time; 15/09/15; 894217; 444; EC BLL C13 1st Lift; 2hr 59mins; 15/09/15; 894225; 444; EC BLL C12 2nd Lift; 3hr 4mins; 17/09/15; 894430; 444; EC BLL C12 3rd lift & C13 2nd lift; 2hr 15mins; 18/09/15; 893031; 444; EC BLL C12 4th lift; 2hr 17mins; 25/09/15; 889610; 444; EC BLL C13 4th lift & SPL-T-01 kicker; 2hr 10mins;
| 03SR - Stations (RfL) | Cxxx-NCR-002067 | NCR | Suspected damage to waterproofing on wall __-T-15 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-06-15 | 2016-06-10 10:46 | -5 | 2015-12-08 10:09 | Structural Engineering - Surface Treatment | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Suspected damage to the waterproofing surface treatment on the western face of wall __-T-15
| 03SR - Stations (RfL) | Cxxx-NCR-002068 | NCR | CL-T-116 25mm nib to doorway not constructed. |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-03-25 | 2016-02-19 13:58 | -35 | 2015-12-09 11:30 | Civil - Civil Engineering General | 1000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The 25mm nib of CL-T-116 to the south side of the doorway was not constructed where the wall joins CL-L-36 see attachment.
| 03SR - Stations (RfL) | Cxxx-NCR-002070 | NCR | Self Compacting Concrete Mix 295 (MCR 50487) – 2hr Placement Time exceeded (__-376) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-02-09 | 2016-01-14 13:39 | -26 | 2015-12-11 14:45 | Structural Engineering - Structural Engineering - General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Specification Clause KF11.3221. 2hr time limit from batching to end of placement exceed. Refer attached for location of pours and placement time details.
| 03SR - Stations (RfL) | Cxxx-NCR-002071 | NCR | Concourse Level; Self Compacting Concrete Mix 285 (MCR 50031) – 2hr Placement Time exceeded (__-375) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-02-09 | 2016-01-14 14:00 | -26 | 2015-12-11 14:52 | Structural Engineering - Structural Engineering - General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Specification Clause KF11.3221. 2hr time limit from batching to end of placement exceed. Location of pours as per attachment
| 03SR - Stations (RfL) | Cxxx-NCR-002072 | NCR | Concourse Level Concrete Mix 233& 243 (MCR 50322 and 50321) – 2hr Placement Time exceeded (__-374) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-02-09 | 2016-01-14 14:07 | -26 | 2015-12-11 15:13 | Structural Engineering - Structural Engineering - General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Specification Clause KF11.3221. 2hr time limit from batching to end of placement exceed. Location details as per attachment.
| 03SR - Stations (RfL) | Cxxx-NCR-002073 | NCR | Self Compacting Concrete Mix 285 (MCR 50031) – 2hr Placement Time exceeded (__-381) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-02-09 | 2016-01-14 14:29 | -26 | 2015-12-11 15:16 | Structural Engineering - Structural Engineering - General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Specification Clause KF11.3221. 2hr time limit from batching to end of placement exceed. Location details as per the attached.
| 03SR - Stations (RfL) | Cxxx-NCR-002074 | NCR | Self Compacting Concrete Mix 295 (MCR 50487) – 2hr Placement Time exceeded (__-380) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-02-09 | 2016-01-14 14:09 | -26 | 2015-12-11 15:32 | Structural Engineering - Structural Engineering - General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Specification Clause KF11.3221. 2hr time limit from batching to end of placement exceed. Location details as per attached.
| 03SR - Stations (RfL) | Cxxx-NCR-002075 | NCR | PES/PSD - Smoke duct making good procedure. |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-02-17 | 2016-01-29 12:41 | -19 | 2015-12-11 16:28 | Structural Engineering - Structural Engineering - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Precast concrete smoke ducts have had blowholes made good using a cement and fine aggregate paste which is yet to be submitted and approved as an MCR. This NCR is to capture a failure in the quality process, there is not a concern with the material used. are aware this is outside the agreed ITP and is preventing the acceptance of a bench mark unit.
| 03SR - Stations (RfL) | Cxxx-NCR-002076 | NCR | Re-injection ports sub-platform level |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-02-09 | 2016-01-04 14:08 | -36 | 2015-12-11 18:33 | Civil - Civil Engineering General | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Re-injection of the sub-platform re-injectio tubes has been under taken from GL1-7 It has been found by the injection contractor that a number of the re-injecto tubes are blocked making injection into the tube unlikely.
| 03SR - Stations (RfL) | Cxxx-NCR-002077 | NCR | IL-T-01 Damage to top of fist lift (__-327) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-02-12 | 2016-01-14 14:13 | -29 | 2015-12-14 15:51 | Structural Engineering - Structural Engineering - General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Two sections of the top of IL-T-01 first lift were damaged during striking of the shutters.
| 03SR - Stations (RfL) | Cxxx-NCR-002078 | NCR | Use of spraycrete without an approved MCR |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-02-12 | 2016-01-13 18:13 | -30 | 2015-12-14 16:21 | Structural Engineering - Structural Engineering - General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Location: GL1 & GL24 below concourse level. Spraycrete was used at the tunnel head walls without an approved MCR.
| 03SR - Stations (RfL) | Cxxx-NCR-002079 | NCR | Non-complaint finish and colour to PC panels |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2016-10-30 | 2016-09-22 14:40 | -38 | 2015-12-15 10:10 | Architectural - Finishes | 1500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Struck finish to exposed concrete within public area should be dense, even-coloured, blemish free and as-struck. The finished concrete should also be uniform in colour and appearance throughout the works in accordance to JE80. 2 number PC panels (ref. type W-02) installed within concourse infill slab at GL13-14/B are deemed non-compliant as they do not meet the architectural specification JE80 and Benchmark record Cxxx-SKC-O6-STD-B071_WS077-50003. The panels’ appearance and texture are notably different to that of the other PC panels. Similar non-conformance to PC panels at GL14-15 concourse infill slab was also reported. The Contractor to verify and confirm.
| 03SR - Stations (RfL) | Cxxx-NCR-002080 | NCR | Concourse slab soffit damage NORTH |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-03-25 | 2016-03-22 15:05 | -3 | 2015-12-16 11:00 | Structural Engineering - Finishes | 5000 |  | Damaged | Rework | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | Please see Cxxx-NCR-001555 During the removal of blinding at the concourse soffit level, impact damage has occurred to the to the soffit. This NCR covers the Northern Trackside area.
| 03SR - Stations (RfL) | Cxxx-NCR-002081 | NCR | Concourse slab soffit damage SOUTH |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-03-04 | 2016-02-27 11:41 | -6 | 2015-12-16 11:00 | Structural Engineering - Finishes | 5000 |  | Damaged | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Please see Cxxx-NCR-001555 During the removal of blinding at the concourse soffit level, impact damage has occurred to the to the soffit. This NCR covers the Southern Trackside area
| 03SR - Stations (RfL) | Cxxx-NCR-002082 | NCR | BLL Lining wall concrete placement time |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-02-17 | 2016-02-05 16:18 | -12 | 2015-12-19 08:50 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | The 2hr time limit from batching to end of placement as specified in clause KF11.3221 has been exceeded for the pours detailed in the attached PDF document.
| 03SR - Stations (RfL) | Cxxx-NCR-002083 | NCR | Concrete Mix 313 and 323 (MCR 50388 & 50389) – Placement Time exceeded (__-391) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-03-11 | 2016-03-22 15:07 | 11 | 2015-12-21 09:40 | Structural Engineering - Structural Engineering - General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Specification Clause KF11.3221. 2hr time limit from batching to end of placement exceed. Refer attached details for each pour location.
| 03SR - Stations (RfL) | Cxxx-NCR-002084 | NCR | Unapproved Material used in Platform Construction - Plastic Shims - West Bound Platform GL 20 -22 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-02-24 | 2016-02-02 17:54 | -22 | 2015-12-22 17:48 | Structural Engineering - Concrete Member | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Unapproved plastic shims were used in the construction of the west bound platform between GL 20 and 22. The shims were used as follows: 1. To form a bearing for the pre-cast concrete planks at the top of the sub-platform wall - in this situation the shims were bedded in mortar and the pre-cast planks placed 2. To form a spacer between precast concrete planks - in his situation the joints of the pre-cast planks were sealed up with grout and the shims covered over. In both situations the
| 03SR - Stations (RfL) | Cxxx-NCR-002085 | NCR | Platform Slab - Platsic Shimmers GL 3-7 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-04-30 | 2016-04-12 16:23 | -18 | 2015-12-24 12:10 | Structural Engineering - Formwork | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Further to the discovery of plastic shimmer in GL 20-22 (See Cxxx-NCR-002084), there is a possibility that unapproved plastic shimmers may have been used in platforms GL 3-7.
| 03SR - Stations (RfL) | Cxxx-NCR-002086 | NCR | Design Manageemnt Plan Review |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2016-03-09 | 2016-03-22 14:49 | 13 | 2016-01-04 16:12 | Systems - Other | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | NCR has been raised for a number of deficiencies in the current Design Management Plan as listed in the surveillance report eB ref. no. Cxxx-XRL-O4-RGN-CR001-50042.
| 03SR - Stations (RfL) | Cxxx-NCR-002087 | NCR | PES Bolt Thread Damaged - GL3.5 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-02-03 | 2016-01-25 14:04 | -9 | 2016-01-06 15:35 | Civil - Structural Engineering | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During install of PES frame at GL3.5 the thread was damaged The coupler had not been cleaned out properly and so therefore the bolt could not be installed to the correct embedment depth. In the attempt to install the bolt, the thread of the bolt was damaged. The bolt has been cut and will be drilled out.
| 03SR - Stations (RfL) | Cxxx-NCR-002088 | NCR | IL - west staircase incorrectly positioned & missing couplers in non-structural wall. |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-03-25 | 2016-02-19 14:07 | -35 | 2016-01-08 09:01 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 7No. Couplers are positioned to give reduced cover to the soffit of the staircase in wall, IL-L-28. 4No. Couplers missed out at bottom of stairs 250mm thick north wall, IL-L-30. (attached survey)
| 03SR - Stations (RfL) | Cxxx-NCR-002089 | NCR | Trackslab Pour 2 concrete segregation |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-05-03 | 2016-04-14 11:15 | -19 | 2016-01-12 08:15 | Civil - Civil Engineering General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During pour 2 of the track slab pours at SPL. It became apparent that the concrete line had a blockage. Low levels of aggregate and high levels grout were flushed into the pour. The pour was stopped after the line blockage and is therefore 120mm approx low.
| 03SR - Stations (RfL) | Cxxx-NCR-002090 | NCR | East/West Liner walls concrete placement Time exceeded. |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-02-25 | 2016-02-27 11:49 | 2 | 2016-01-12 11:52 | Civil - Civil Engineering General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The following placement times were exceeded using Concrete Mix 470 (MCR 50486) when casting East/West liner walls/tunnel eyes: Ticket no. /Location /Time exceeded the 2hrs from batching to placement /Time exceeded 1 hr between pours 055301 N.west headwall 32mins 055303 N.west headwall 32mins 054340 S.West tunnel head wall 5mins 054341 S.West tunnel head wall 10mins 890652 S/East tunnel head wall kicker 28mins 052203 S.East tunnel head wall 9mins 890346 NW tunnel head wall 1mins 890366 NW tunnel head wall 5mins 890381 NW tunnel head wall 11mins 725085 kicker for E&W wall pour 1 3mins 895167 N/west tunnel head wall kicker 12mins 809459 East liner wall pour 1 5mins 051834 S/East tunnel head wall 3mins 051839 S/East tunnel head wall 19mins 051848 S/East tunnel head wall 5mins 42mins 051878 S/East tunnel head wall 7mins
| 03SR - Stations (RfL) | Cxxx-NCR-002092 | NCR | __-T-37 & __-L-43 GL/8-9 starter bars |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-03-18 | 2016-02-19 14:21 | -28 | 2016-01-18 14:47 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The following was discussed and in PTR meeting 18/12/15 (with DK(Cxxx) GF(XRL) CM(__L) & __()): 1) __-L-43 9No B20 starter bars are cast out of position (into the NF2 instead of NF1) and are therefore giving excessive cover. 2) __-L-43 8no incorrect dia starter bars were installed in the FF1 (B12 & B16Alt) 9 B20's 3) __-T-37nib - __-L-43 3no bars cast with no cover and 1no bar missing at B20 starter bar locations.
| 03SR - Stations (RfL) | Cxxx-NCR-002093 | NCR | __-L-45 (cabinet recess) – 28 Day Cube Results 2230 (NCR-401) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-02-17 | 2016-01-29 12:43 | -19 | 2016-01-18 17:42 | Structural Engineering - Concrete Member | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Location: __-L-45 G/L 16.5 28day cube results for cube 2230 achieved compressive strength of 46.7N/mm2 and 48.2N/mm2.
| 03SR - Stations (RfL) | Cxxx-NCR-002094 | NCR | Wall __-L-41 – starter bars to be re drilled |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-03-11 | 2016-02-27 12:03 | -13 | 2016-01-18 17:39 | Civil - Civil Engineering General | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 12No (6EF) NF1BM17 B12 & FF1 BM18 B16 starter bars cut flush with slab to allow access. Temporary skip placed in the location.
| 03SR - Stations (RfL) | Cxxx-NCR-002096 | NCR | Intermediate Level Infill - Concrete Mix 102 (MCR 50223)– Placement Time exceeded |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-02-08 | 2016-02-05 16:24 | -3 | 2016-01-19 15:21 | Structural Engineering - Structural Engineering - General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | During the pour of the Intermediate Level infill at GL8-9 there was a gap of 82mins between loads. Specification Clause KF11.3204 states fresh concrete shall not be placed against existing fresh in-situ concrete which has been in position for more than sixty minutes. Ticket no. Truck Location Time exceeded 1 hr b/n the pours 899022 6th load Infill G/L 8-9 22mins 899026 7th load Infill G/L 8-9
| 03SR - Stations (RfL) | Cxxx-NCR-002097 | NCR | PES Backing Angle to Infill Plate - Incorrect Installation |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-05-03 | 2016-02-17 17:16 | -76 | 2016-01-20 10:31 | Structural Engineering - Structural Engineering - General | 2500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Further to Cxxx-FCD-002009, the angle to the PES infill backing plate was unable to be installed as per the detailed design due to the curvature of the rolled steel. Therefore the angle was installed 'track' side of the backing plate to enable it to be installed.
| 03SR - Stations (RfL) | Cxxx-NCR-002098 | NCR | 56 Day Cube Failures – Mix 132 – MCR 50055 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-03-25 | 2016-02-19 14:33 | -35 | 2016-01-20 14:58 | Civil - Civil Engineering General | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | 56day cube results for cubes 2206,2207, 2194 and 2195 failed to achieve the mix design requirement of 50N/mm2 at 56days. (Refer to MCR Cxxx-SKC-O-TSC-B071_WS077-50055). Results range from 40.1N/mm2 to 43.9N/mm2 with a mean result achieved of 42.3N/mm2. __ slab infill GL 4-5 poured 12/11/15 and GL 20-21 poured 7/11/15 Attached are the following documents: 1. Location Plan 2. Concrete Mix Design Certificate (MCR 50055) 3. Cube Results Table 4. Cube test reports for 56 day tests 5. Batching records 6. Concrete delivery records and delivery tickets
| 03SR - Stations (RfL) | Cxxx-NCR-002099 | NCR | PES/PSD - Missing/damaged cast-in couplers GL 11 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-02-04 | 2016-01-25 13:46 | -10 | 2016-01-21 10:54 | Structural Engineering - Structural Engineering - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Further to Cxxx-NCR-002062 and Cxxx-RFI-003142 a pair of missing couplers for precast smoke duct installation have been identified at grid line 11, south track side. Please see attached coupler location. The type of backing angle in this location will be a Type A2 as per the attached sketch, -Cxxx-S-XSK-00150-P02-A3.pdf
| 03SR - Stations (RfL) | Cxxx-NCR-002100 | NCR | Bakerloo Link Box – Mass Concrete Pour 1 14/01/16 – Poor Finish (__F-487-NCR-405) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-02-12 | 2016-01-29 14:30 | -14 | 2016-01-21 15:07 | Structural Engineering - Finishes | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Mass Concrete Pour 1 in the Bakerloo Link Box extended from the west liner wall to the stepped level change between grid-lines 12 and 13. Please see attached markup drawing titled 'Cxxx-SWN-S-DDA-M171_8-21002 MARKUP'. The plain finish specified for the unformed surface of the pour (see NSCS specification clause 8.6.2.3) requires a dense, smooth, level and uniform surface. A small area of the finished surface to the north of the column on grid-line 12 has some minor indentations from footprints and some surface laitance.
| 03SR - Stations (RfL) | Cxxx-NCR-002101 | NCR | IL-__ Staircase at GL/5 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-03-16 | 2016-02-23 12:49 | -22 | 2016-01-22 16:55 | Civil - Civil Engineering General | 1500 |  | Design | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | No connection detail has been cast into __ slab DS2.
| 03SR - Stations (RfL) | Cxxx-NCR-002102 | NCR | Pressure relief drainage/Diaphragm wall interface. |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-03-18 | 2016-02-23 13:14 | -24 | 2016-01-22 17:35 | Civil - Civil Engineering General | 2500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Where the D-wall was broken back to expose couplers for base slab construction, hollows have been left at some locations. These hollows do not meet the surface requirements from the delta membrane manufacturers recommendations.
| 03SR - Stations (RfL) | Cxxx-NCR-002103 | NCR | Platform slab incorrect crack inducer installed |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-04-30 | 2016-04-14 09:14 | -16 | 2016-01-22 18:05 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | A 75mm bottom crack inducer was incorrectly installed in the top of the platform slab between GL’s 8-9. See location plan attached.
| 03SR - Stations (RfL) | Cxxx-NCR-002104 | NCR | Damage to Precast Smoke Duct Type 5 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-03-04 | 2016-03-03 17:14 | -1 | 2016-01-23 10:10 | Civil - Civil Engineering General | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Precast smoke duct type 5 has been damaged in transit. The damage affects a corner of the smoke duct unit which is accessible after installation. As the smoke duct is a special unit and the damaged area is accessible after installation, on this occasion the smoke duct has been installed while the feasibility of a repair is investigated. will propose a repair method for consideration and suggest a collaborative meeting to discuss this in light of the imminent handover of this area to Cxxx.
| 03SR - Stations (RfL) | Cxxx-NCR-002105 | NCR | Support Angles for Type 7 Smoke Duct Drilled on Site Due to Lack of Fit |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-03-17 | 2016-03-29 13:49 | 12 | 2016-01-23 10:28 | Civil - Civil Engineering General | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Support angles to the east face of smoke duct type 7 have been drilled on site due to lack of fit for the standard support angles. Early indications would suggest this is due to the couplers being cast out of position in the concourse slab. propose to complete a survey of the affected area and detail a suitable new type of support angle for consideration by Cxxx. The support angles drilled on site will then be removed and replaced.
| 03SR - Stations (RfL) | Cxxx-NCR-002106 | NCR | IL-__ western staircase GL/5 couplers missing/out of position |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-03-04 | 2016-02-29 18:05 | -4 | 2016-01-23 17:12 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Couplers in the staircase are missing or out of tolerance (see attached survey): __ West staircase/landing coupled bar connection drawing ref 52049 South Wall IL-L-28 (200mm thick wall): Top flights 3No. Missing in slab 2No. Missing in wall Bottom flight 5No. bars no cover 5No. bars cover of 25mm North Wall IL-L-30 (250mm thick): Top flight: 3No. Missing in slab 4No. Missing in wall Bottom flight: 4No. bars out of position. 4No. bars no cover
| 03SR - Stations (RfL) | Cxxx-NCR-002107 | NCR | FSC incorrect track slab reinforcement U-bars |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-08-23 | 2016-07-08 09:42 | -46 | 2016-01-23 17:32 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | U bars and links in bending schedules are bent 40mm shorter providing excess cover to track slab from P revision to C revision. Steel was procured from P rev schedules.
| 03SR - Stations (RfL) | Cxxx-NCR-002108 | NCR | PES/PSD - Missing/damaged cast-in couplers GL 15 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-02-08 | 2016-01-29 13:25 | -10 | 2016-01-25 08:46 | Structural Engineering - Bolted Connections | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Further to Cxxx-NCR-002099, Cxxx-NCR-002062 and Cxxx-RFI-003142 a pair of missing couplers for precast smoke duct installation have been identified at grid line 15, south track side. Please see attached coupler location. The type of backing angle in this location will be a Type A2 as per the attached sketch, -Cxxx-S-XSK-00150-P02-A3.pdf
| 03SR - Stations (RfL) | Cxxx-NCR-002110 | NCR | Sumps - East and west sump slab levels |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-10-15 | 2016-08-19 13:30 | -57 | 2016-01-25 14:29 | Civil - Civil Engineering General | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The slab elevation of both east and west sump is average 35mm to high. The design elevation 101.03 & 101.08.m. are recorded on site 101.070m and 101.115m respectively. The possible cause of this error was the kicker were poured at the same time as the slab to minimize the occurrence of a construction joint, it would appear, due to the large width of the kicker that there was an overspill on to the slab
| 03SR - Stations (RfL) | Cxxx-NCR-002111 | NCR | Bedding joint mortar depth greater than 10mm |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-04-30 | 2016-04-29 13:01 | -1 | 2016-01-25 20:08 | Architectural - Brickworks/Blockworks | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The bedding mortar below the 1st course of block is greater than 10mm in some locations for the internal blockwork.
| 03SR - Stations (RfL) | Cxxx-NCR-002112 | NCR | Wall SPL-L-51 GL7-8 not cast with 50dia core hole |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-03-11 | 2016-02-27 12:30 | -13 | 2016-01-26 11:31 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The 50mm diameter "core hole" detail from Cxxx-SWN-S-DDD-M171_6-05020 detail 6 was not cast into the wall at 3no locations. Post coring this hole could cause damage to reinforcement bars and/or pressure relief drainage dependant on the stage of construction.
| 03SR - Stations (RfL) | Cxxx-NCR-002114 | NCR | Smoke Duct Type 5 rebate issues |  | Contr | COS | PAD - Paddington Station (West) |  | 2016-03-30 | 2016-03-29 11:42 | -1 | 2016-01-27 14:39 | Civil - Civil Engineering General | 1500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Type 5 smoke duct was cast with extended rebate to the western face of the duct. The rebate was intended to terminate to match adjacent type1 smoke duct for sealing purposes. Identical smoke duct types 6 and 7 are designed to have extended rebate hence the error does not affect the structural integrity of the duct. shall scan the expose rebate area for adequate rebar cover and propose to use as-is if deemed adequate as per construction drawings.
| 03SR - Stations (RfL) | Cxxx-NCR-002115 | NCR | Sub-platform walls - SPL-T-55 - omitted trimmer bars |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-02-24 | 2016-02-23 13:11 | -1 | 2016-01-27 15:56 | Structural Engineering - Reinforcement | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Please refer to Drawing Cxxx-SWN-S-DDD-M171_6-01523 and Cxxx-SKC-C-DWG-B071_WS077-52053 SPL-T-55 is located at GL 11(-6880) Trimmer above 2 No doorway, B20 BM 38 missed out from adjacent cast walls, SPL-L51 & SPL-L52)
| 03SR - Stations (RfL) | Cxxx-NCR-002116 | NCR | Platform Slab - thicken platform slab at GL 23.5-24 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-03-04 | 2016-02-19 15:53 | -14 | 2016-01-28 11:22 | Structural Engineering - Reinforcement | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The couplers in the headwall to connect the platform slab is located approximately 50mm too low.
| 03SR - Stations (RfL) | Cxxx-NCR-002117 | NCR | UTX duct dislodged during pour |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-05-03 | 2016-04-11 12:29 | -22 | 2016-01-29 11:45 | Civil - Civil Engineering General | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Whilst casting concrete the UTX duct (identified in attachment) became dislodged. The 90degree bend came out of the coupler and the duct filled with concrete.
| 03SR - Stations (RfL) | Cxxx-NCR-002119 | NCR | Smoke Duct - Nordlock washer Omitted to halfen/back angle connection |  | Contr | COS | PAD - Paddington Station (West) |  | 2016-03-18 | 2016-03-29 11:44 | 11 | 2016-02-02 15:56 | Civil - Civil Engineering General | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Smoke duct installed with no nordlocks between halfen bolts/back angles. Note 6 on Drawing Cxxx-SWN-S-DDD-M171_5-05523 states that , all steel connections to be grade 8.8 bolts with Nord-Lock anti-vibration washers (or similar acceptable to the Project Manager). propose to remove the halfen bolt one at a time and reinstall as per note 6 above.
| 03SR - Stations (RfL) | Cxxx-NCR-002120 | NCR | IL-T-24 service riser burst shutter |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-03-03 | 2016-02-19 15:58 | -13 | 2016-02-02 18:31 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | South End of Wall is up to +30mm out of position (south).
| 03SR - Stations (RfL) | Cxxx-NCR-002121 | NCR | Pile 1- No concrete cube taken |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-05-03 | 2016-02-16 16:06 | -77 | 2016-02-02 19:22 | Civil - Civil Engineering General | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Please refer to Cxxx-NCR-001645 BLL 600dia Pile 1 repair had no test cubes taken for it. Reason- agreed repair method was undertaken at night. No one available to take cubes.
| 03SR - Stations (RfL) | Cxxx-NCR-002122 | NCR | FSC Pour 20 – missing couplers in kerb pour |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-04-03 | 2016-02-23 17:20 | -40 | 2016-02-03 14:46 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 21no Couplers were not installed in the top mat of pour 20 (GL18.5-20).
| 03SR - Stations (RfL) | Cxxx-NCR-002123 | NCR | Precast concrete smoke ducts - T-bolt connection to __ Channel |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-03-24 | 2016-03-29 13:53 | 5 | 2016-02-04 09:33 | Civil - Civil Engineering General | 5000 |  | Material | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | As discussed at several collaborative meetings (notably a joint meeting with Cxxx on 4/2/16), the halfen T-bolt connection to the precast smoke duct has been installed using zinc electroplated halfen fixings. - These fixings were proposed and accepted on MCR Cxxx-SKC-O-TSC-B071_WS077-50501 Rev 2.0. - __ do not (as standard) manufacture a suitable galvanised fixing to suit the requirements of KV10.1409 in 8.8 grade - However galvanised fixing to suit the specified halfen channel is available in 4.6 grade
| 03SR - Stations (RfL) | Cxxx-NCR-002124 | NCR | Wall SPL-L-52 GL7-8 not cast with 50dia core hole. |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-04-07 | 2016-03-31 07:50 | -7 | 2016-02-04 10:51 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Similarly to Cxxx-NCR-002112 wall SPL-L-52 was not cast with 50dia void formers for "core hole" detail from Cxxx-SWN-S-DDD-M171_6-05020 at 3no locations.
| 03SR - Stations (RfL) | Cxxx-NCR-002125 | NCR | Wall SPL-L-52 GL9.5 not cast with 50dia core hole. |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-04-30 | 2016-04-01 07:39 | -29 | 2016-02-04 10:58 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Similarly to Cxxx-NCR-002112 wall SPL-L-52 at GL9.5 was not cast with 50dia void former for "core hole" detail from Cxxx-SWN-S-DDD-M171_6-05020 at 1no locations.
| 03SR - Stations (RfL) | Cxxx-NCR-002126 | NCR | Concrete Mix 219 - Placement Time Exceeded - Concourse Infill Concrete |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-06-30 | 2016-06-11 09:01 | -19 | 2016-02-10 12:58 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | During the construction of the Concourse Level Infills the time between batching and placement completion was exceeded. Please see attached for details.
| 03SR - Stations (RfL) | Cxxx-NCR-002127 | NCR | Fireproofing/FSC gap |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-06-30 | 2016-05-13 08:43 | -48 | 2016-02-07 15:42 | Civil - Civil Engineering General | 3500 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | at the FSC trackbed and fireproofing interface there are some locations where the fireproofing did not finish low enough to meet the FSC.
| 03SR - Stations (RfL) | Cxxx-NCR-002128 | NCR | PES Frame Missing Bolt |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-03-24 | 2016-03-21 15:51 | -3 | 2016-02-08 10:03 | Structural Engineering - Structural Engineering - General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | PES frame Pos No. 14, at GL 7.5 north has 1No. bolt which cannot be installed. The western base plate has 5No. bolts installed and the eastern base plate has all 6No. bolts installed. Using various orientations of Top Hat washers (predominantly type 4) the frame has been manoeuvred as close as is possible to the cast in coupler in order to install. However, it is still not possible to install the remaining bolt (see attached sketch and photographs.)
| 03SR - Stations (RfL) | Cxxx-NCR-002129 | NCR | West Sump - Bottom slab 56 day cube result 2054D |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-06-30 | 2016-05-27 13:41 | -34 | 2016-02-08 12:17 | Civil - Civil Engineering General | 1500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 56day cube result of 34.9N/mm2 failed to achieve the mix design requirement of 45N/mm2 at 56days. (Refer to MCR Cxxx-SKC-O-TSC-B071_WS077-50388). Refer to attached spreadsheet for cube results 2053-2056 at 7,28 and 56 days
| 03SR - Stations (RfL) | Cxxx-NCR-002130 | NCR | Damage to Type 10 Smoke Duct |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-03-17 | 2016-03-08 15:58 | -9 | 2016-02-11 09:43 | Structural Engineering - Concrete Member | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The type 10 PCSD on the South West corner has a chip on the lower western face. A cover survey has been carried out to this chipped area. The minimum cover to the western face there is 56mm and to the soffit of the unit the minimum cover is 42mm, see attached. The proposal is to leave as is, as the cover to the reinforcement has been compromised. Please confirm acceptability of this proposal.
| 03SR - Stations (RfL) | Cxxx-NCR-002131 | NCR | __ - Escalator Pit (GL 10) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-04-10 | 2016-03-22 14:17 | -19 | 2016-02-10 09:31 | Structural Engineering - Reinforcement | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Please refer to the following drawings: Cxxx-SWN-S-DDA-M171_2-01563 Cxxx-SKC-C-DWG-B071_WS077-52446 B1 BM 01 35 No firsty + 2 No. lenton couplers + 350mm spacing on North side only T1 BM 02 35 No firsty + 2 No. lenton couplers + 270mm spacing on North side only Issue 1: The threaded bars cannot be used on the 2 EF lenton couplers due to duration of the delivery of specified threaded coupler. Issue 2: Additionally spacing is greater than 250mm and require post fixing. Cxxx David Knowles and Jon Sinclair any spacing greater than 250mm to be post fixed.
| 03SR - Stations (RfL) | Cxxx-NCR-002132 | NCR | Smoke Duct Bolted Connection to Soffit - No Isolation for Bimetalic Corrosion Designed, Detailed or Installed |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-03-25 | 2016-03-29 15:19 | 4 | 2016-02-10 14:11 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | As discussed in collaborative meetings (notably a joint meeting with Cxxx on 4/2/16), smoke ducts have been designed, detailed and installed with no isolation for bimetallic corrosion at the connection between the smoke duct hanging bracket and soffit coupler.
| 03SR - Stations (RfL) | Cxxx-NCR-002133 | NCR | Concrete Mix 580 (MCR 50530) NCR416 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-07-31 | 2016-06-10 15:21 | -51 | 2016-02-10 17:20 | Civil - Civil Engineering General | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Time between loads 060331 2nd load __ East Stair Case top pour & 060344 3rd load __ East Stair Case top pour was 1hour 50minutes.
| 03SR - Stations (RfL) | Cxxx-NCR-002134 | NCR | Departure Road Level, __ Staircase GL9.5 - Step connection with stairs |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-03-04 | 2016-02-29 18:02 | -4 | 2016-02-11 11:37 | Civil - Structural Engineering | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | No accurate detailing shown in any drawings (see attached): Cxxx-SKC-C-DWG-B071_WS077-50528 Cxxx-SKC-C-DWG-B071_WS077-50582 Cxxx-SKC-C-DWG-B071_WS077-52454 Slab drawing starter bars shown in DWG No. 50528 shows 28 EF L bars, shape code 11 BM 31. Staircase DWG No. 52454 shows in section U bar and 2 splay bars. Neither drawings show connection detailing for staircase. No connection detailing in Wall DWG No. 50582 also.
| 03SR - Stations (RfL) | Cxxx-NCR-002135 | NCR | Cube 2286 – 28 day Cube Test Report Failure NCR-423 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-06-30 | 2016-06-02 09:16 | -28 | 2016-02-10 17:38 | Civil - Civil Engineering General | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 28 Day cube results failed to achieve required strength of 45N/mm2. Cube 2286D 38.3N/mm2 Cube 2286E 40.1N/mm2 7 day cube result 2286C achieved 49N/mm2 which is in excess of the 28 day strength requirement. 3 and 5 day results for 2286A and 2286B achieved 28N/mm2 and 38.8N/mm2 which are consistent with the 7 day result. Affected elements: Intermediate IL-L-28 (GL4-5) SPL-L-20 &SPL-L-27 (GL 20-21)
| 03SR - Stations (RfL) | Cxxx-NCR-002136 | NCR | PES/PSD - Type 1 Smoke duct, aggregate tolerances exceeded. |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-03-10 | 2016-02-26 14:12 | -13 | 2016-02-11 13:04 | Structural Engineering - Concrete Member | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | On the 02/12/2015 at Ebor concretes Ltd at 16:22, a non compliant concrete batch was used in one precast mould of Type 1B (Mould No.2) The batch ID in questions is 789. KF11.1400 states that a batch tolerance of 3% is applicable in regards to constituents of materials used in concrete mixes. Batch ID 789 however was minus 6.18% (Sand) and plus 8.41% (Limestone). Please see attached for further information and cube results.
| 03SR - Stations (RfL) | Cxxx-NCR-002137 | NCR | PES/PSD - Smoke duct backing angles re-drilled on site (South) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-03-24 | 2016-03-24 09:43 | 0 | 2016-02-11 12:35 | Structural Engineering - Structural Engineering - General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Galvanised backing angles, which have been re-drilled on site, have been fitted to the 3no. Type 11's GL 1 South, 3no Type 11's GL 24 south, and 1no Type 10 GL 4 South. This is due to the cast in coupler positions not suiting the backing angle design.
| 03SR - Stations (RfL) | Cxxx-NCR-002138 | NCR | Track Bed South GL1-24 and Track Bed North GL 19-24 Levels out of tolerance. |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-06-30 | 2016-05-19 16:28 | -42 | 2016-02-11 16:23 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Sections of the trackbed have been surveyed and they are out of specified tolerance: As-built slab levels outside of specified tolerance of +0mm to -10mm (see attached) As-built positions of kerbs/drainage channels outside of specified tolerance of +/-10mm (see attached)
| 03SR - Stations (RfL) | Cxxx-NCR-002139 | NCR | Platform Slab Levels – Out of Tolerance GL 8-9 South |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-04-11 | 2016-03-22 14:13 | -20 | 2016-02-11 16:31 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | See attached survey for areas of the south platform slab GL 8-9 that are out of tolerance. Maximum +18mm recorded (permissible +10mm)
| 03SR - Stations (RfL) | Cxxx-NCR-002140 | NCR | Inspection Request Forms not issued for Thorpe offsite Works |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2016-03-23 | 2016-03-22 14:05 | -1 | 2016-02-12 13:05 | Civil - Structural Engineering | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | It has been reported by the fit out Construction Manager that precast units for the brick slip cladding have been manufactured by Thorpe. The Supervisor's Representative has not received any Inspection Request Forms for such offsite works, this is contrary to the requirements of the Works Information
| 03SR - Stations (RfL) | Cxxx-NCR-002141 | NCR | Blockwork Lintel - reduced bearing |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2016-07-30 | 2016-07-01 10:00 | -29 | 2016-02-12 13:11 | Civil - Structural Engineering | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Blockwork at concourse level is supported on a lintel that only has approximately 50mm bearing. This is contrary to the blockwork specification which requires a minimum of 150mm
| 03SR - Stations (RfL) | Cxxx-NCR-002142 | NCR | Concrete Mix 263 Placement exceeded (MCR50319) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-06-30 | 2016-06-28 14:53 | -2 | 2016-02-12 15:11 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Please see attached table that indicates
| 03SR - Stations (RfL) | Cxxx-NCR-002143 | NCR | Track Bed Concrete – SW & SE Tunnel Tie –ins – Use of Concrete Mix 253 (MCR50320) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-04-12 | 2016-03-22 14:03 | -21 | 2016-02-12 16:54 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | 1. SW tunnel kerbs before GL1 and SE tunnel kerbs beyond GL24 Concrete mix 253 (MCR 50320) used in lieu of Concrete mix 640 (MCR 50520). Note Concrete mix 253 has been sanctioned for use for Track Bed Stage 1 Concrete in the main box as per __F-RFI-1609.
| 03SR - Stations (RfL) | Cxxx-NCR-002144 | NCR | Missing 100x50 channel in trackslab. |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-04-30 | 2016-04-12 16:08 | -18 | 2016-02-19 18:01 | Civil - Civil Engineering General | 2500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The 100x50 trackbed drainage channel located under the concourse drainage system downpipe was not installed at GL/5. The reinforcement was lowered locally as per the drainage channel detail, but due to miscommunication the 100x50 formwork mould was not installed. This is proved by attached cover meter survey.
| 03SR - Stations (RfL) | Cxxx-NCR-002145 | NCR | Stage 1 Concrete – As-Built Levels – North GL1-19 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-06-30 | 2016-05-20 10:10 | -41 | 2016-02-15 16:53 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | In addition to Cxxx-NCR-002138 further sections of the trackbed have been surveyed and they are out of specified tolerance: As-built slab levels outside of specified tolerance of +0mm to -10mm (see attached highlighted survey)
| 03SR - Stations (RfL) | Cxxx-NCR-002147 | NCR | Consructing blockwork to P-Status elevation drawings |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-09-02 | 2016-08-25 10:09 | -8 | 2016-02-15 20:11 | Architectural - Brickworks/Blockworks | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | The assured blockwork elevation drawings for intermediate level have been revised and updated to P-status to account for the changes to the builderswork holes as part of the developemnt of MEPH design. Due to the late revision change, we are currently constructing to these P-status drawings in advance of them going through the gate impact assessment and being issued for construction.
| 03SR - Stations (RfL) | Cxxx-NCR-002148 | NCR | Blockwork Lintels missing on drawing Cxxx-SKC-A-DDC-M171_3-04609 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-09-02 | 2016-08-25 10:11 | -8 | 2016-02-15 20:28 | Architectural - Brickworks/Blockworks | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | reference to Cxxx-SKC-A-DDC-M171_3-04609 rev C01 Some of the builders work holes that are 300mm or more are shown as not having a lintel support above the opening. This contradicts the design note for lintels, shown on the windpost location drawing, which states the lintel requirement for openings 300mm and above.
| 03SR - Stations (RfL) | Cxxx-NCR-002149 | NCR | Blockwork unsafe design for large builderswork hole 3-370 adjacent to door Intermediate GL15.5 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-05-30 | 2016-05-13 09:04 | -17 | 2016-02-15 20:48 | Architectural - Brickworks/Blockworks | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | On Intermediate level corridor, GL15.5, Builderswork hole 3-370 is constructed as per the design, on elevation drawing Cxxx-SKC-A-DDC-M171_3-04603. This detail shows a large builderswork hole next to a double door with a column of blockwork in between. This column of stacked blocks is supporting two lintels each greater than 1.4m and does not look stable if it were to have an impact load applied. We have requested an alternate design detail from the Design Consultant.
| 03SR - Stations (RfL) | Cxxx-NCR-002151 | NCR | Lintel close to windpost supported with steel angle not as per design - Concourse GL16/17 - BW hole 4-210 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-09-06 | 2016-07-29 14:18 | -39 | 2016-02-16 09:40 | Architectural - Brickworks/Blockworks | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The builderswork hole (ref 4-217) located on Concourse level GL16/17 is approximately 60mm from a windpost. The Subcontractor attached a stainless steel angle to the WP2 windpost to support the lintel, because 60mm width of block would be insufficient. This is not as per an approved design.
| 03SR - Stations (RfL) | Cxxx-NCR-002152 | NCR | PES Backing Infill Angle - Unable to be installed (South) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-04-13 | 2016-04-01 07:59 | -12 | 2016-02-16 12:05 | Structural Engineering - Steel Member | 1500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | 13No. PES Backing Infill Angles cannot be installed on the South side either track-side or platform-side. The preferred solution is to install an infill angle of 5mm thickness.
| 03SR - Stations (RfL) | Cxxx-NCR-002153 | NCR | Concrete Mix 121 (MCR 50053)– Placement Time exceeded |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-04-30 | 2016-04-12 16:03 | -18 | 2016-02-17 16:20 | Civil - Base Course | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Date: Ticket No: Load: Location in Works: Non-compliance with KF11: 04/11/2015 054106 3rd load EBT time exceeded the 2hrs from batching to placement 15 minutes 04/11/2015 054107 4th truck E__ time exceeded the 2hrs from batching to placement 27 minutes 01/12/2015 052909 4th load E__ slab infill GL 16-17 time exceeded the 2hrs from batching to placement 4 minutes 10/12/2015 899280 1st load __ slab infill 8-9 Exceeded 1hr between placement by 43 min 10/12/2015 051240 2nd load __ slab infill 8-9 Exceeded 1hr between placement by 43 min
| 03SR - Stations (RfL) | Cxxx-NCR-002154 | NCR | Concrete Mix 171 (MCR 50255)– Placement Time exceeded (NCR 429) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-04-30 | 2016-04-12 16:01 | -18 | 2016-02-17 16:28 | Civil - Civil Engineering General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Date: Ticket No: Location: Time exceeded the 2hrs from batching to placement: 16/10/2015 808261 __-L-10 18 minutes 11/11/2015 898034 L-45, __ 23 minutes
| 03SR - Stations (RfL) | Cxxx-NCR-002155 | NCR | Concrete Mix 263 (MCR 50319)– Placement Time exceeded (430) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-04-30 | 2016-04-12 15:57 | -18 | 2016-02-17 17:30 | Civil - Civil Engineering General | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Attached table of exceeded concrete times.
| 03SR - Stations (RfL) | Cxxx-NCR-002156 | NCR | PES - Frame 74 1No. Bolt Unable to be Installed |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-04-13 | 2016-04-01 08:07 | -12 | 2016-02-18 16:55 | Structural Engineering - Steel Member | 1500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | On the Western Base Plate of PES frame in location 74 only 5No. bolts have been able to be installed due to the alignment of the cast-in couplers. See attached sketch of required deviation of hole centre from design. Please advise of any overall dimensional change requirements to the Base Plate or other PES frame elements to accommodate the change in hole location.
| 03SR - Stations (RfL) | Cxxx-NCR-002157 | NCR | SPL-T-43: Missed connections bars from SPL-L-02 and SPL-L-09 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-03-30 | 2016-03-22 13:57 | -8 | 2016-02-18 17:04 | Civil - Civil Engineering General | 1500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | SPL-T-43 coupled connections missed out from existing cast wall SPL-L-02 SPL-T-43 coupled connections missed out from existing cast wall SPL-L-09 Due to R&R detailing not providing connection detailing to drawings from SPL-L-02 & SPL-L-08, the SPL-T-43 has provided U bars connection, BM 11. Drawing No: Cxxx-SWN-S-DDA-M171_6-01522-SPL-T-43 Cxxx-SKC-C-DWG-B071_WS077-51808 Cxxx-SKC-C-DWG-B071_WS077-51810-SPL-L-02 Cxxx-SKC-C-DWG-B071_WS077-51815-SPL-T-43
| 03SR - Stations (RfL) | Cxxx-NCR-002158 | NCR | E__ Beam on Gridline 3 - Missing couplers |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-04-30 | 2016-04-12 15:39 | -18 | 2016-02-22 17:42 | Civil - Civil Engineering General | 1500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Most couplers were fixed in the adjacent walls however some are missing at GL3 for the beam connection detail. The walls between the beam are 300mm thick but require 3 x B16 bar and 1 X B25 post drilling as illustrated in the attached drawing. Note that for the North wall, 3 x B20 couplers were fixed instead of B16 and an extra B20 coupler was fixed meaning the integrity of the beam connection is greater than originally designed. Considering the wall thicknesses, is it acceptable that the B16s can only reach an embedment of 230mm? Lastly, the B25 for the south wall connection, what is the appropriate embedment as there is a nib and the thickness of the wall to post drill into? See attached drawings: Cxxx-SWN-A-DDA-M171_1-33502 GA for E__ West side Cxxx-SKC-C-DWG-B071_W5077-51566 Annotated revision
| 03SR - Stations (RfL) | Cxxx-NCR-002159 | NCR | Cube 2191 – 28 day Cube Test Report Failure – Precast Grouting CL8-9 Infill |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-04-30 | 2016-04-11 14:38 | -19 | 2016-02-22 18:25 | Civil - Civil Engineering General | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 28 Day cube results failed to achieve required strength of 50N/mm2. Cube 2191B 38.6N/mm2 Cube 2191C 39.5N/mm2 7 day cube result 2191A achieved 63.4 N/mm2 60 day cube result 2191D achieved 54.7N/mm2 Both of which are in excess of the 28 day strength requirement.
| 03SR - Stations (RfL) | Cxxx-NCR-002160 | NCR | E__ slab ES4 GL:B-C/8-9 connective bars. |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-10-15 | 2016-07-08 08:49 | -99 | 2016-02-25 09:08 | Civil - Civil Engineering General | 0 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | E__ slab ES4 GL: B-C/8-9 Bars have been cast as per sketch: Cxxx-SWN-S-DDD-M171_1-57611 in adjacent pours. Therefore: 2.5m length where 6No B40's are missing in B1 layer. (Pink in sketch) 1.5m length where B20/25Alt layer was installed at T3 instead of B1 layer. (Red in sketch)
| 03SR - Stations (RfL) | Cxxx-NCR-002161 | NCR | PES/PSD - Damaged Smoke duct couplers No 28 & 45 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-03-24 | 2016-03-04 15:13 | -20 | 2016-02-25 11:39 | Structural Engineering - Bracing | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Smoke duct No 28 and No 45 both have 1 of the 4no. cast in couplers damaged, as per the marked up sketch. The couplers in this location have also been cast out of position, dimensions are highlighted in the attached sketch.
| 03SR - Stations (RfL) | Cxxx-NCR-002162 | NCR | PES/PSD - Type 11 Damaged Coupler (No. 305) North East corner. |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-03-24 | 2016-03-04 15:09 | -20 | 2016-02-25 14:23 | Structural Engineering - Bolted Connections | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Type 11 smoke duct, no. 305, has been installed using 7no. of the 8no. backing angles due to 1no coupler being damaged. Please see attached sketch for location.
| 03SR - Stations (RfL) | Cxxx-NCR-002163 | NCR | PES/PSD - A4-70 Bolts used to install Smoke ducts |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-03-10 | 2016-03-10 12:33 | 0 | 2016-02-25 14:43 | Structural Engineering - Bolted Connections | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | __ have installed smoke ducts, as highlighted on the attached mark up, using A4-70 bolts. This occurred due to limited stock of A4-80 16mm bolts in the required bolt length to achieve the correct level and bolt embedment. Using A4-70 bolts allowed installation to continue as per the installation programme.
| 03SR - Stations (RfL) | Cxxx-NCR-002164 | NCR | Acoustic blockwork not in accordance with Cxxx-PMI-796 |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2016-08-19 | 2016-08-11 09:07 | -8 | 2016-02-27 15:51 | Architectural - Walls | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Cxxx-PMI-796 instructs the use of 100mm thick blocks laid flat with alternate course aligning with the standard blockwork coursing. These walls have been built using 140mm thick blocks
| 03SR - Stations (RfL) | Cxxx-NCR-002165 | NCR | IL-Level GL22-24 shrinkage cracks |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-07-31 | 2016-05-11 13:38 | -81 | 2016-02-29 18:21 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | On Intermediate level, following slab surface scabbling and screeding preparation, shrinkage cracks have appeared and are evident in the slab surface between GL22-24. Cracks to be surveyed and investigated.
| 03SR - Stations (RfL) | Cxxx-NCR-002166 | NCR | Chips and scrapes visible on installed 2hr fire rated lintels |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-07-25 | 2016-07-01 10:08 | -24 | 2016-02-29 19:00 | Architectural - Brickworks/Blockworks | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | At Concourse level, south side, the installed lintels above the door openings have some visible along the corridor have visible scrapes and chips.
| 03SR - Stations (RfL) | Cxxx-NCR-002167 | NCR | Blockwork setting out differes from earlier installed perimeter tie position - Concourse South GL7-8 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-05-30 | 2016-05-13 09:30 | -17 | 2016-02-29 19:20 | Architectural - Brickworks/Blockworks | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | At Concourse level, south side GL 7-8, the setting out of the blockwork walls do not line up with the previously installed windpost tie sleeve locations that were installed with the perimeter wall. The previously installed tie sleeves for 5no. of the walls look to be 150mm out of position, in the same direction.
| 03SR - Stations (RfL) | Cxxx-NCR-002168 | NCR | Concourse GL 8 South Blockwork wall line clashes with opening in slab overhead (int. slab) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-05-30 | 2016-05-13 09:24 | -17 | 2016-02-29 19:29 | Architectural - Brickworks/Blockworks | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | At Gridline 8 on Concourse level. The line of the blockwork wall, as per the design drawing, would clash with a slab penetration in the intermediate level. The blockwork would clash by approximately 140mm.
| 03SR - Stations (RfL) | Cxxx-NCR-002169 | NCR | Lintels bearing on wall nibs that appear less than 150mm at concourse level south east |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-06-30 | 2016-06-02 08:26 | -28 | 2016-02-29 20:31 | Architectural - Brickworks/Blockworks | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Lintels bearing on wall nibs that appear less than 150mm - concourse level south
| 03SR - Stations (RfL) | Cxxx-NCR-002170 | NCR | PES - Frame 57 1No. Bolt Unable to be Installed |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-04-18 | 2016-04-11 12:23 | -7 | 2016-03-03 10:06 | Structural Engineering - Structural Engineering - General | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | On the Western Base Plate of PES frame in location 57 only 5No. bolts have been able to be installed due to the alignment of the cast-in couplers. See attached sketch of required deviation of hole centre from design. Please advise of any overall dimensional change requirements to the Base Plate or other PES frame elements to accommodate the change in hole location.
| 03SR - Stations (RfL) | Cxxx-NCR-002171 | NCR | EBT: Beam GL 21, Section C-D |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-05-02 | 2016-04-12 15:31 | -20 | 2016-03-03 16:33 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Drawings: Cxxx-SWN-S-DDA-M171_1-01575 Cxxx-SWN-S-DDB-M171_Z-04559 Cxxx-SKC-C-DWG-B071_WS077-51566-C01 with survey Couplers were fixed in the adjacent walls however some are missing. The walls between the beam are 250mm thick with a south side recess of 550mm. Refer to GA 01575 for clarity. South beam, missing: 1) 2B16 sides 2) 1B25 at bottom 3) 1B16 at top North beam, missing: 4) 1B16 on side
| 03SR - Stations (RfL) | Cxxx-NCR-002173 | NCR | GL/11.5-12 SOUTH __ channel on platform nib positioning. |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-10-15 | 2016-08-11 13:37 | -65 | 2016-03-04 10:29 | Civil - Civil Engineering General | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | At GL/11.5-12 on the south section of platform slab edge. A __ channel has dislodged moved out of level during a pour. The edge is approximately 30mm down from its original position. (see photo) *Note* The halfen channel does not protrude out from the nib into the track.
| 03SR - Stations (RfL) | Cxxx-NCR-002174 | NCR | PES/PSD - 20mm cast in coupler position |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-04-11 | 2016-04-01 07:37 | -10 | 2016-03-07 10:16 | Structural Engineering - Bolted Connections | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 20no. 20mm Cast in couplers for hanging precast smoke duct have been positioned out of tolerance. The distance between the centre line of a pair of bolts varies from 90mm to 140mm which is greater than the 90mm to 110mm allowed. Please see highlighted bolts in the attached -Cxxx-G-XSK-00480_06.pdf and identified as "surveyed Data Rev 06" at GL 11.5 and 12.5 North track side. A set of backing angles have been sketched as per the attached -Cxxx-S-XSK-00155 rev1.pdf. Please confirm their acceptance for this installation location.
| 03SR - Stations (RfL) | Cxxx-NCR-002175 | NCR | EBT: Beam GL 4, Section C-D |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-04-30 | 2016-04-12 15:23 | -18 | 2016-03-04 11:19 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Similarly to Cxxx-NCR-002171. Cxxx-SWN-S-DDA-M171_1-01572-E__ Beam @ GL 4 Cxxx-SKC-C-DWG-B071_WS077-51566-C01 Couplers were fixed in the adjacent walls however some are missing. The walls between the beam are 250mm thick with a south side thickening of 300mm to make 550mm. Refer to GA Cxxx-SWN-S-DDA-M171_1-0157 for clarity. North Missing 2No B16 side – __F propose to post fix at 155mm embedment 2No B16 top – __F propose to post fix at 155mm embedment South Missing 2No B16 side – __F propose to post fix at 155mm embedment 1No B16 top – __F propose to post fix at 455 embedment 1No B25 bottom – __F propose to post fix at 455 embedment Please note spacing between bars is on average 100mm.
| 03SR - Stations (RfL) | Cxxx-NCR-002176 | NCR | Bakerloo Link Box - RC stairs bottom step rebar connection to mass fill |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-05-30 | 2016-05-10 15:44 | -20 | 2016-03-04 17:34 | Structural Engineering - Structural Engineering - General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | As shown within the attached mark-up drawings and bar schedule, the reinforcement within the bottom step of the Bakerloo Link Box staircase is detailed to connect to the adjacent mass fill concrete (TOC 100.010m). The reinforcement bars that form this connection are BM 29 and BM 30, shape code 15. No steel reinforcement was cast into the mass fill concrete. During a PTR meeting on 29/02/16, Cxxx requested that the reinforcement was to be fixed into the mass fill concrete with an embedment depth of 450mm.
| 03SR - Stations (RfL) | Cxxx-NCR-002177 | NCR | MCR not approved for SHS windpost sections |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-05-30 | 2016-05-13 09:10 | -17 | 2016-03-05 17:50 | Architectural - Brickworks/Blockworks | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | 4no. Square hollow section windposts were installed at platform level prior to accepted code 1 MCR
| 03SR - Stations (RfL) | Cxxx-NCR-002178 | NCR | Track slab Pour 2 post fixing reinforcement. |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-04-30 | 2016-04-12 15:21 | -18 | 2016-03-07 13:32 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Further to Cxxx-NCR-002089. Track slab removal works have damaged 12dia reinforcement steel on both mats of the adjacent trackslab pour (connection bars between Pour 2&3).
| 03SR - Stations (RfL) | Cxxx-NCR-002179 | NCR | Pour 2 - Damage to Base slab GL 3-4 North |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-04-30 | 2016-04-12 15:18 | -18 | 2016-03-07 18:07 | Civil - Civil Engineering General | 2500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Pour 2 removal works (the remedial action for NCR-002089) have damaged the base slab. Damage was caused by diamond coring operations to remove the segregated concrete. (see photos). Surveys have taken place and concluded the location of struck and severed reinforcement bars and depth of core as per Drawings_Damage to Base slab rev2.0 (attachment).
| 03SR - Stations (RfL) | Cxxx-NCR-002180 | NCR | N__ test results not provided for installed SHS windpost at platform level |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-05-30 | 2016-05-13 08:35 | -17 | 2016-03-07 19:35 | Architectural - Brickworks/Blockworks | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | We still have not received N__ test results for the SHS windposts installed at platform level
| 03SR - Stations (RfL) | Cxxx-NCR-002181 | NCR | E__ Upper Beam GL21 Mising couplers (__F NCR 436) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-05-07 | 2016-04-12 15:04 | -25 | 2016-03-08 11:42 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Drawings: Cxxx-SWN-S-DDA-M171_1-01575 Cxxx-SWN-S-DDB-M171_Z-04559 Cxxx-SKC-C-DWG-B071_WS077-51566-C01 with survey Couplers were fixed in the adjacent walls however some are missing. The walls between the beam are 225mm thick with a south side recess of 525mm. Refer to GA 01575and section Z-04559 for clarity.
| 03SR - Stations (RfL) | Cxxx-NCR-002182 | NCR | Wall IL-L-27 blowholes [GL23-24] |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-05-07 | 2016-04-14 09:11 | -23 | 2016-03-08 17:33 | Structural Engineering - Finishes | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Wall IL-L-27 between GL23-24 is seen to have blowholes in the concrete surface. Refer attached photographs.
| 03SR - Stations (RfL) | Cxxx-NCR-002183 | NCR | EBT-T-12 lacers & starter bars connection |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-07-31 | 2016-05-20 10:51 | -72 | 2016-03-09 10:00 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | 1. Starter bars have been cast in the wrong position (see survey ELT-T-12). The correct number of bars have been installed. 2. ELT-T-01 has pull out bars specified from Cxxx-SKC-C-DWG-B071_WS077-51611 (see attachment). A Ferbox has not been installed at this location, however 4no B12 bars have been installed to be bent down. 3. A Ferbox has been cast in wall ELT-L-01 below above issue where an opening is shown on Cxxx-SWN-S-DDC-M171_Z-04562 (see attachment).
| 03SR - Stations (RfL) | Cxxx-NCR-002184 | NCR | Wall __-L-41 GL 7 incorrect lacer diameter. |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-04-30 | 2016-04-12 15:02 | -18 | 2016-03-09 10:25 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Existing wall __-L-41 (cast in 2014) incorrectly with B12's instead of B16's at the connection. Location is displayed in drawing Cxxx-SKC-C-DWG-B071_WS077-50567 attached as above an opening.
| 03SR - Stations (RfL) | Cxxx-NCR-002185 | NCR | Thorp Brickslip Precast Panels - __ Channel Installation Extents |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-03-24 | 2017-03-24 11:44 | 0 | 2016-03-11 12:17 | Architectural - Brickworks/Blockworks | 2500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Within the base of the __ Brickslip panels __ HTA-CE 28/15 chanenls have been cast to recieve a fixing to provide a spacing bracked for the panels to be held off the wall and to be aligned. Within a number of panels the __ channel units have been cast the full width of the panels this was identified during a inspection in the factory. This does not comply with the manufactuers installation guidance given by __ that indictes for the HTA-CE 28/15 channels a minimum edge distance of 15mm should be observed. The panels this effected are units: P2 P41 P49 P45 P47 P48 P37 P36
| 03SR - Stations (RfL) | Cxxx-NCR-002186 | NCR | Eastbourne Terrace Level: EBL-T-08 Lacer connection |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-07-31 | 2016-05-20 11:15 | -72 | 2016-03-10 16:42 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Drawings: Cxxx-SWN-S-DDA-M171_1-01575 Cxxx-SWN-S-DDB-M171_Z-04557 Cxxx-SKC-C-DWG-B071_WS077-51584_C01_location of missing bars Wall ELT-T-08 is remaining to be constructed. Side wall bars from ETL-L-20 (North) & ETL-L-44 (South) have bars missing/damaged. 1. ELT-L-20 is 200mm thick, the top of the wall has 10 No. bars (5EF) with no coupled bar connection to ELT-T-08. 2. ELT-L-44 is 225mm thick, top of the wall 4 No. bars (2EF) and approx. 2No. bars NF1 300mm below where all bars are damaged. Total: 6 No. bars damaged ferbox bars connection to ELT-T-08.
| 03SR - Stations (RfL) | Cxxx-NCR-002187 | NCR | Wall ELT-T-08 lacer connection to adjacent walls. ELT-L-20 & ELT-L-44. |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-04-30 | 2016-04-12 14:44 | -18 | 2016-03-11 15:06 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Wall ELT-L-20 has not been cast without 10no 5EF coupled connections Cxxx-SKC-C-DWG-B071_WS077-51584. Wall ELT-L-44 has been cast with pull out bars however 6no 3EF have been damaged to the point that they cannot be used.
| 03SR - Stations (RfL) | Cxxx-NCR-002188 | NCR | E__ slab pour: missing coupler connection @ GL 17 __-L-45 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-04-13 | 2016-04-12 14:42 | -1 | 2016-03-14 13:52 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | In the upper (beam) section of wall __-L-45 at GL/17 the reinforcement steel BM44 (3No B16's) have missing coupler connections for the continuation of the beam. see attachment Cxxx-SKC-C-DWG-B071_WS077-50587. *note* this beam forms part of the E__ slab pour.
| 03SR - Stations (RfL) | Cxxx-NCR-002189 | NCR | Base slab arrangement at BLL breakthrough |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2017-01-25 | 2017-01-12 08:27 | -13 | 2016-03-14 16:16 | Civil - Structural Engineering | 15000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | The provision to be cast into the base slab for the BLL connection should be 5m wide in accordance with Cxxx-SWN-S-DDB-M171_Z-24205
| 03SR - Stations (RfL) | Cxxx-NCR-002191 | NCR | Concrete Mix 263 (MCR 50319)– Placement Time exceeded |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-06-30 | 2016-06-24 14:00 | -6 | 2016-03-15 08:40 | Civil - Civil Engineering General | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Further to Cxxx-NCR-002155 Attached table of exceeded concrete times.(attached)
| 03SR - Stations (RfL) | Cxxx-NCR-002193 | NCR | Departures Roal Level: __ Slab Infill GL 10 – As-built Levels |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-10-30 | 2016-09-28 10:31 | -32 | 2016-03-18 17:50 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | As-built top of slab levels are out of tolerance > +/-10mm, ranging from +26 to +29mm. See survey attached. The theoretical cover is +75mm. A cover meter survey reading was attempted but no readings were obtained as the instrument cannot read over 100mm therefore the top mat of reinforcement is deemed to be at the correct level.
| 03SR - Stations (RfL) | Cxxx-NCR-002194 | NCR | Incorrect bricks sent for strength testing |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-04-04 | 2016-04-26 16:19 | 22 | 2016-03-21 09:15 | Civil - Structural Engineering | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Bricks were removed in 5 locations of MacMillan House Block C basement as part of the intrusive survey works scoped in Cxxx-SWN-S-RSW-B071-50001. Two bricks were mistakenly sent for testing in January 2016 which were not from MacMillan House. The error was spotted when the correct bricks were later sent for testing.
| 03SR - Stations (RfL) | Cxxx-NCR-002195 | NCR | Screed retention angle hold down bolts not Stainless steel |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-06-30 | 2016-06-02 10:15 | -28 | 2016-03-21 13:55 | Architectural - Flooring | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | For the first 5 rooms to have screed laid, the screed has been laid up to the retention angles at the door threshold locations. These are held in position using hold down blots The hold down bolts are not stainless steel, they are zinc plated carbon steel. The retention angle is stainless steel. This has occurred in the following rooms on intermediate level east end; - MCC II 766 - MCC II CWU 932 - FCR II 764 - MIST II 397 - AAR FAN 957
| 03SR - Stations (RfL) | Cxxx-NCR-002196 | NCR | D wall North water ingress GL 6,7 and 10 at SPL |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-10-01 | 2018-10-17 13:02 | 16 | 2016-03-24 11:00 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | reference Cxxx-NCR-001745; Diaphragm wall - Water ingress. As per Cxxx-PMI-00696 all joints have now been injected. raise this NCR to highlight specific areas on the north SPL where water ingress is still visible;GL6,6.5,7.5 and 10. Please see attached photos
| 03SR - Stations (RfL) | Cxxx-NCR-002197 | NCR | Concourse Slab - Missing Cast Ins around Escalator Openings |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-10-10 | 2016-08-19 13:41 | -52 | 2016-03-24 14:25 | Architectural - Balustrade | 5000 |  | Incomplete Works | Rework | 3 (3-6k) | Complete | Management Problem - Other | Completed |  | Balustrade Fixing Cast-Ins have not been cast-in at the Concourse Slab around the escalator openings at GL9-10 and GL10-11. Some, but not all, of the cast-in fixings have also been missed from the escalator openings at GL13-14 & GL14-15.
| 03SR - Stations (RfL) | Cxxx-NCR-002198 | NCR | Platform level wall PL-10 GL 7 (__-448) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-06-30 | 2016-05-20 11:16 | -41 | 2016-03-24 17:33 | Structural Engineering - Reinforcement | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Refer attached drawings for further details: ISSUE 1: Starter bars (B12's BM04) cast for wall PL-L-10 have been positioned without taking account for 60mm recess adjacent to column C7-S. Refer dwg no. 51817. ISSUE 2: 2no couplers were missing on slab adjacent to column C7-N. Refer dwg no. 52063.
| 03SR - Stations (RfL) | Cxxx-NCR-002199 | NCR | GL13.5 South Platform Slab - Incorrect installation of contraction joint (BFF 451) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-07-30 | 2016-06-15 15:00 | -45 | 2016-03-31 07:54 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The platform crack inducer was not correctly fixed and moved during the concrete pour. It is out of position by 40mm at the north end.
| 03SR - Stations (RfL) | Cxxx-NCR-002200 | NCR | Painting commenced without ITP code 1 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-04-15 | 2016-04-14 11:03 | -1 | 2016-04-01 17:06 | Architectural - Finishes | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Painting commenced prior to the ITP being accepted as code 1.
| 03SR - Stations (RfL) | Cxxx-NCR-002201 | NCR | Departures Road Level: __-L-41 GL8-8.5 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-07-31 | 2016-05-19 13:59 | -73 | 2016-04-04 14:06 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Drawing: Cxxx-SKC-C-DWG-B071_WS077-50567 C01 Cxxx-SKC-C-DWG-B071_WS077-52398 C03 1) East connecting face to beam: 4 no. B12 existing couplers do not have required cover. (BM08) 1 no. B16 missing coupler at Top of the beam (BM19) 2) West connecting face to the beam: 3 No. B20 couplers present at an angle making it difficult to position the rebar correctly. (BM22)
| 03SR - Stations (RfL) | Cxxx-NCR-002202 | NCR | Sub Platform Level: SPL-T-44 GL19-20 Missing couplers |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-06-04 | 2016-05-26 13:25 | -9 | 2016-04-05 10:11 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Drawings: Cxxx-SWN-S-DDA-M171_6-01525 Cxxx-SKC-C-DWG-B071_WS077-52062 South end of SPL-T-44 require 3 No. B12 to be post fixed however minimum embed into slab of 525mm can not be acquired. Drilling 3 No. B12 have reached an embed of 450mm, 350mm, 270mm and cannot drill further. In an attempt to find alternate areas for post fix, an additional 3 No. B12 holes were drilled but only reached 180mm embed each. See attached sketch.
| 03SR - Stations (RfL) | Cxxx-NCR-002203 | NCR | Omitted windpost ties adjacent to lintel support blocks due to coursing arrangement |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-07-07 | 2016-06-03 10:11 | -34 | 2016-04-05 16:57 | Architectural - Brickworks/Blockworks | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Windpost ties omitted at 2-3 courses where lintel supports are local to the windpost.This is due to the full block underneath the lintel staggering the block coursing.
| 03SR - Stations (RfL) | Cxxx-NCR-002204 | NCR | E__ EN14 Slab: Gap between Ferbox and Missing couplers |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-06-04 | 2016-05-20 10:05 | -15 | 2016-04-05 16:21 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | See attached sketch: Cxxx-SWN-S-DDA-M171_1-01572 5 Areas between GL3-6 where post fixing of B16 bars are required. 3 Areas along the 250mm thick wall ETL-L-39 highlighted have gaps between the ferbox therefore require post fixing. 1 Area on ETL-L-39, couplers were installed however do not have the correct cover so post fixing required, maximum cover present is 25mm. 1 Area at GL4.5 requires post fixing of B16.
| 03SR - Stations (RfL) | Cxxx-NCR-002205 | NCR | __ not installed to full depth between windpost and blockwork and not ensuring the rockwall is in compression. |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-05-30 | 2016-05-27 14:57 | -3 | 2016-04-06 09:22 | Architectural - Brickworks/Blockworks | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | There are areas where the rockwool isnt installed to the full depth between the windpost and the blockwork . In these areas rockwool is damaged and so not in compression between the windpost and the blockwork.
| 03SR - Stations (RfL) | Cxxx-NCR-002206 | NCR | Intrumescent filler installation between internal blockwork and soffit with no approval of MCR |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-05-30 | 2016-05-27 14:53 | -3 | 2016-04-07 16:59 | Architectural - Brickworks/Blockworks | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Intrumescent filler was installed between the internal blockwork and the soffit without an approved MCR.
| 03SR - Stations (RfL) | Cxxx-NCR-002207 | NCR | Lack of quality plan |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-01-23 | 2017-02-17 15:06 | 25 | 2016-04-08 12:15 | Architectural - Flooring | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The contractor, __ Ltd, carrying out construction of the Back of House Screeding have not issued an accepted quality plan.
| 03SR - Stations (RfL) | Cxxx-NCR-002208 | NCR | BLL- Waffle slab, Placement Time exceeded |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-06-30 | 2016-06-16 11:40 | -14 | 2016-04-08 14:56 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Date Ticket no. Truck Location time exceeded the 2hrs from batching to placement 24/03/2016 140134 2nd load BLL waffle slab 7mins 24/03/2016 140136 3rd load BLL waffle slab 6mins 24/03/2016 140147 5th load BLL waffle slab 3mins 24/03/2016 140151 6th load BLL waffle slab 13mins Specification Clause KF11.3221. 2hr time limit from batching to end of placement exceed for the above pours. Please find attached test data from __ confirming initial set times for the Topflow SCC mixes. For mix 295 initial set time is 5.5hrs and final set time is 8hrs which exceeds actual maximum placement time on site of 2hr 13min for ticket
| 03SR - Stations (RfL) | Cxxx-NCR-002209 | NCR | West Retaining Wall - Inncorrect starter bars |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-06-10 | 2016-05-13 13:13 | -28 | 2016-04-11 10:00 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Cxxx-SKC-C-DWG-B071_WS077-51628 Cxxx-SKC-C-DWG-B071_WS077-51629 The west side of the West retaining wall have 32 No. B12 starter bars whereas the drawings states 32 No. B16.
| 03SR - Stations (RfL) | Cxxx-NCR-002210 | NCR | Sub Platform Level: SPL-L-133 Misaligned Couplers |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-06-14 | 2016-05-13 15:01 | -32 | 2016-04-15 13:01 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Drawings: Cxxx-SKC-C-DWG-B071_WS077-52412 Cxxx-SKC-C-DWG-B071_WS077-52411 GL19-20: 1. On the south east face of the wall, the couplers are misaligned by 20mm so do not provide enough concrete cover if built to the designed thickness of 200mm. To allow for enough cover, the wall will have to be increased to 260mm thickness if built As Is with the couplers in their current position. 2. As highlighted in the attached (Cxxx-SKC-C-DWG-B071_WS077-52411), 5 No. FF and 5 No. NF couplers for SPL-L-133 (at the south west end of the wall) are missing.
| 03SR - Stations (RfL) | Cxxx-NCR-002211 | NCR | __ Waterproofing - West Vent Head House |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-07-15 | 2016-06-10 16:05 | -35 | 2016-04-14 14:55 | Structural Engineering - Structural Engineering - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Elastomeric waterproofing membrane which has been applied to the west vent head house, by _Laser, has been incorrectly installed. The following defects have been identified: 1. Dywidag holes have not been made good prior to waterproofing being applied. 2. The elastomeric waterproofing membrane has not bonded to the concrete surface. Photos of defects attached.
| 03SR - Stations (RfL) | Cxxx-NCR-002213 | NCR | Bended windpost ties |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-07-30 | 2016-07-29 14:24 | -1 | 2016-04-18 10:39 | Architectural - Brickworks/Blockworks | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | The windpost ties located at the lift shaft wall on Concourse level GL 6 have been bent downwards. The blockwork is incomplete in this area as its waiting completion of concrete walls. The blockwork wall has been left down exposing the windpost ties.
| 03SR - Stations (RfL) | Cxxx-NCR-002214 | NCR | PES/PSD Low Dry Pack C 28 day compressive strength cube result |  | Contr | COS | PAD - Paddington Station (West) |  | 2017-10-06 | 2017-10-07 10:31 | 1 | 2016-05-31 15:56 | Civil - Civil Engineering General | 20000 |  | Material | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | 28 day cube result for material (Dry Pack C) used for dry packing to PES and smoke duct is lower than expected as shown below. Set 1 and Set 2 at later dates has compressive strength exceeding 40N/mm^2 however, there are no spare cubes available for post 28 day testing for set 3. Cube Set 1 (KIL 99972) 34N/mm^2 at 28 days and 40.4N/mm^2 at 31 days Cube Set 2 (KIL 101170) 36N/mm^2 at 28day and 46N/mm^2 at 72days Cube Set 3 (KIL 104615) 34.1N/mm^2 at 28days and no spare.
| 03SR - Stations (RfL) | Cxxx-NCR-002215 | NCR | Damaged drainage at concourse level GL16.2 North |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-11-10 | 2016-10-13 10:22 | -28 | 2016-04-19 07:08 | Civil - Drainage | 10000 |  | Damaged | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Refer to GL16.2 North on drawing Cxxx-SKC-M-DDA-M171_4-83218 and to the attached photo illustrating the damage to the drain connection point at CL soffit. The piece damaged is a 90deg bend.
| 03SR - Stations (RfL) | Cxxx-NCR-002217 | NCR | BLL - Concrete finish to in-situ staircase ramp |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-06-30 | 2016-06-17 14:49 | -13 | 2016-04-19 14:01 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The ramp to the east side of the stair flight from 101.308 to 102.893 has a poor top surface finish and poor compaction at the side face where the stop end shutter was placed. The two sloping B12 T1 and B1 bars at the side of the ramp are partially exposed in placed and not fully surrounded by concrete.
| 03SR - Stations (RfL) | Cxxx-NCR-002218 | NCR | Departures Road Canopy Prototype - water test |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2016-06-22 | 2016-06-21 15:33 | -1 | 2016-04-20 08:59 | Civil - Structural Engineering | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A water test was carried out to the canopy prototype to an agreed methodology. the methodology required the pressure to be 220kpa +/-20 kpa. The pressure dial was reading 1.8 bar ie 180kpa as shown on the attached photos
| 03SR - Stations (RfL) | Cxxx-NCR-002219 | NCR | BLL adit - waterproofing not installed to manufacturers requirements |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2017-01-20 | 2016-12-06 12:50 | -45 | 2016-04-20 09:02 | Civil - Structural Engineering | 2500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | The water bar at the 1.5m offset from diaphragm wall in the BLL is not properly adhered to the __ and appears to have been filled with foam.
| 03SR - Stations (RfL) | Cxxx-NCR-002220 | NCR | Damaged Gully pots at Concourse & Intermediate Level (__-464) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-01-20 | 2016-12-13 10:59 | -38 | 2016-04-21 08:51 | Civil - Drainage | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | In several locations, cast-in Gully pots have been damaged through impact, which has resulted in parts of the gully pots being cracked or chipped (See attached photo + mark-up drawing – locations shown in blue). In other locations, only the flanges of the gully have been chipped, yet the main body of the cast-in pot remains intact (see attached drawing – locations shown in pink).
| 03SR - Stations (RfL) | Cxxx-NCR-002221 | NCR | Waterproofing |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-01-20 | 2017-01-25 12:08 | 5 | 2016-04-21 14:24 | Structural Engineering - Structural Engineering - General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | On the 30th of December Section 14 of the Waterproofing protection was poured. This section is directly above the Diaphragm wall from GL 15-24. The concrete used for this section was a C40/50 FND Pump mix. This mix did not contain Polypropylene fibres and as such is non-compliant.
| 03SR - Stations (RfL) | Cxxx-NCR-002222 | NCR | Ommission of downpipes for Cavity drainage (GL/3 North & GL/22 South) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-10-15 | 2016-10-13 10:14 | -2 | 2016-04-22 15:06 | Civil - Drainage | 10000 |  | Incorrect Installation | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | We record the following as-built information regarding spigot's in the concourse level slab: Spigot was not installed at GL22 south [S73; DP42; S/E corner] Spigot was dislodged during C02 pour at GL3 north [N5; DP60; N/W corner] Drainage pipes were not able to be installed from concourse to subplatform level as there are no connection points at the soffit. At GL3 North the cavity drainage was installed as per the levels on the CWD drawings. At GL22 South the CWD channel levels were adjusted to suit, with a high point at the location of the missing spigot, draining away both east and west to the adjacent downpipes.
| 03SR - Stations (RfL) | Cxxx-NCR-002223 | NCR | Inspection Request forms not raised for __ installatione East and West ends |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2016-11-30 | 2016-10-28 10:51 | -33 | 2016-04-25 08:04 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Inspection Request forms are not being raised for the duratell smoke duct installations
| 03SR - Stations (RfL) | Cxxx-NCR-002224 | NCR | Hollowcore planks not to finish specification |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-10-07 | 2016-09-07 15:56 | -30 | 2016-04-27 18:16 | Architectural - Brickworks/Blockworks | 1500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | The hollowcore planks that have arrived to site would not meet all of the finish requirements as per the specification.
| 03SR - Stations (RfL) | Cxxx-NCR-002225 | NCR | Platform Slab Precast – __F __ NCR 041 (__-466) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-07-27 | 2016-06-30 08:08 | -27 | 2016-04-28 08:01 | Structural Engineering - Pre-cast | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate resources | Completed |  | Location = SPL – North and Middle GL13-15: See attached plan for unit locations See attached internally raised __F NCR41 for __ Precast Yard. Failure to take cubes on one day for casting reference P-237 on 11/01/2016.
| 03SR - Stations (RfL) | Cxxx-NCR-002226 | NCR | Painting Benchmark |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-05-13 | 2016-05-13 13:43 | 0 | 2016-04-29 07:46 | Architectural - Interior Design & Art | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | As per ITP Cxxx-SKC-C-ITP-B071_WS077-50118 Item 7 a benchmark must be signed off prior to continuing works. Paperwork has yet to be signed off although painting decoration in BoH areas is underway.
| 03SR - Stations (RfL) | Cxxx-NCR-002227 | NCR | Painting ITP |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-05-13 | 2016-05-13 15:35 | 0 | 2016-04-29 07:52 | Architectural - Interior Design & Art | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | As per ITP Cxxx-SKC-C-ITP-B071_WS077-50118 Item 8 and 9 and IRF is to be submitted to Crossrail Engineer to witness the protection of adjacent surfaces and preparation. This was not submitted.
| 03SR - Stations (RfL) | Cxxx-NCR-002228 | NCR | Back of House Floor Levels |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-12-23 | 2016-11-28 14:02 | -25 | 2016-04-29 13:17 | Architectural - Flooring | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The screed Isopol SBR in rooms SCR I 746 and SCR II 747 on Intermediate between GL11 and 12 has been installed at the wrong level. Isopol SBR should have been installed at 118.169 allowing 6mm for FL-117 Rubber tile to be installed on top to F.F.L 118.175. Isopol has been installed at 118.175.
| 03SR - Stations (RfL) | Cxxx-NCR-002229 | NCR | Intermediate Level, IL-L-18, GL17-GL18: Starter bars (__ NCR 468) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-07-02 | 2016-05-24 16:09 | -39 | 2016-05-03 10:46 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Drawing: Cxxx-SWN-S-DDD-M171_3-01570 Cxxx-SKC-C-DWG-B071_WS077-51770 Wall IL-L-18 has 18 no. missing starter bars on each face requiring a total of 36 no B12 bars to be post fixed. This will be drilled on to the upstand.
| 03SR - Stations (RfL) | Cxxx-NCR-002230 | NCR | Precast Unit, Concourse Level, GL14: Escalator Opening South (__ NCR 470) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-08-23 | 2016-07-15 08:23 | -39 | 2016-05-03 11:07 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Paint has been applied at the edge of the South side of the Escalator Opening where the Haki stair is installed for the access to Platform Level. This damage to unit type W-2 was not carried out by Byrnes. See attached image.
| 03SR - Stations (RfL) | Cxxx-NCR-002231 | NCR | Concrete Mix 263 (MCR 50319)– Placement Time exceeded (__ NCR 459) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-07-02 | 2016-06-28 14:51 | -4 | 2016-05-03 14:59 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Specification Clause KF11.3221. 2 hour time limit from batching to end of placement exceeded for the pours stated in the attached document.
| 03SR - Stations (RfL) | Cxxx-NCR-002232 | NCR | Concrete Mix 580/585 (MCR 50530)– Placement Time exceeded |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-07-02 | 2016-06-28 14:52 | -4 | 2016-05-03 15:11 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Specification Clause KF11.3221. 2 hour time limit from batching to end of placement exceeded for the pours in the attached table of exceeded.
| 03SR - Stations (RfL) | Cxxx-NCR-002233 | NCR | Concrete Mix 121 & 122 (MCR 50053 & 50054)– Placement Time exceeded (__ NCR 461) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-07-02 | 2016-06-29 12:39 | -3 | 2016-05-03 15:36 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Specification Clause KF11.3221. 2 hour time limit from batching to end of placement exceed pours in the attached table.
| 03SR - Stations (RfL) | Cxxx-NCR-002234 | NCR | Concrete Mix 219 (MCR 50326)– Placement Time exceeded (__ NCR 462) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-07-02 | 2016-06-28 14:55 | -4 | 2016-05-03 15:44 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Specification Clause KF11.3221. 2hour time limit from batching to end of placement exceed the pours in attached table. Specification Clause KF11.3204. Fresh concrete shall not be placed against existing fresh in-situ concrete which has been in position for more than 60 minutes.
| 03SR - Stations (RfL) | Cxxx-NCR-002235 | NCR | Self-Compacting Concrete Mix 285 (MCR 50031) – 2hr Placement Time exceeded (__ NCR 463) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-07-09 | 2016-07-06 13:15 | -3 | 2016-05-10 13:56 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Specification Clause KF11.3221. 2 hour time limit from batching to end of placement exceeded, indicated attached table.
| 03SR - Stations (RfL) | Cxxx-NCR-002236 | NCR | Inconsistant Mortar Joints |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-06-30 | 2016-06-17 14:45 | -13 | 2016-05-06 14:36 | Architectural - Brickworks/Blockworks | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Inconsitent mortar joints on intermediate level south between GL 14-15. This NCR was raised as part of surveillance carried out on 27/01/2016.
| 03SR - Stations (RfL) | Cxxx-NCR-002237 | NCR | Protruding Lintel Intermediate South Room SER CWR |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-07-30 | 2016-07-01 12:52 | -29 | 2016-05-06 14:57 | Architectural - Brickworks/Blockworks | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Protruding lintel located south intermediate level room SER CWR. This NCR was raised during a survellance on 27/01/2016
| 03SR - Stations (RfL) | Cxxx-NCR-002238 | NCR | Panel N75 Level |  | Contr | COS | PAD - Paddington Station (West) |  | 2016-07-15 | 2016-05-20 11:45 | -56 | 2016-05-06 15:47 | Structural Engineering - Diaphragm Walls | 1500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Panel N75 is constructed 277mm higher than the theoretical. The original as-built guide wall survey levels for N75 indicated that the average guide wall level was 125.195 and the cage was constructed based on this level. However the as-built survey undertaken after the panel was concreted indicates that the guide wall level for panel N75 is 125.472mm (average). See attached Designers to assess whether there is a structural implication for the panel.
| 03SR - Stations (RfL) | Cxxx-NCR-002239 | NCR | Orientation of precast vent ducts (__-471) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-07-09 | 2016-06-17 15:08 | -22 | 2016-05-10 18:53 | Civil - Civil Engineering General | 5000 |  | Supervision/Management | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Location = Western Retaining Wall: Drawing Cxxx-SWN-S-DDD-M171_Z-04571 rev.C01 shows vent duct inlets and outlets vertically aligned (north-south elevation). Rev. C04 shows the outlets repositioned. Refer attached extracts from each drawing respectively. Cxxx-SKC-O7-XCS-B071_WS077-50517 Western Retaining Wall Precast Vent Ducts has been accepted and shows ducts vertically aligned. Units have all been cast and first phase installation has commenced (first three units of each duct).
| 03SR - Stations (RfL) | Cxxx-NCR-002240 | NCR | BLL Staircase landing |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-06-30 | 2016-06-10 15:27 | -20 | 2016-05-11 15:36 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Couplers have been omitted from the platform wall which connect to the BLL stair landing at 105.712SSL (see attached drawing for clarification). The proposal has been discussed with Cxxx designers and CRL Cxxx architects (A. Hotchkis, R. Brown) and has been agreed in principle, having no impact on follow on works.
| 03SR - Stations (RfL) | Cxxx-NCR-002241 | NCR | Isopol SBR Benchmark |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-07-20 | 2016-07-13 11:34 | -7 | 2016-05-12 12:03 | Architectural - Flooring | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | As per item Activity 4 Item 18 of the BoH Floor Screed ITP Cxxx-SKC-C-ITP-B071_WS077-50109 a benchmark is to be approved by Crossrail prior to continuing works on the remaining areas. Works continued with a benchmark not approved.
| 03SR - Stations (RfL) | Cxxx-NCR-002242 | NCR | __ Precast Low 28 day cube results P184,P189,P192 and P214 (__-472) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-07-21 | 2016-06-30 08:02 | -21 | 2016-05-12 14:27 | Structural Engineering - Testing | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Location = Various units (see Traceability sheets attached). Refer attached table of "Cube Results": 1. 28 day Cubes P184, P189 and P189 failed to reach required strength of 60N/mm2. 2. One of the 28 day Cubes 214 failed to reach required strength of 50N/mm2 and is less than permitted deviation of fck -4N for an individual result.
| 03SR - Stations (RfL) | Cxxx-NCR-002243 | NCR | Intermediate Level Slab GL6.8 missing couplers (Underside of IL-T-03) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-07-16 | 2016-06-10 15:30 | -36 | 2016-05-17 12:50 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Drawing Cxxx-SKC-C-DWG-B071_WS077-51719 Cxxx-SKC-C-DWG-B071_WS077 -51721 Cxxx-SWN-S-DDA-M171_4-01567 Couplers to connect the infill into the slab are missing: Issue 1: 4 No. B25 U bars BM132 Issue 2: 2 No. B40 BM60 and BM128 See attachment for details.
| 03SR - Stations (RfL) | Cxxx-NCR-002244 | NCR | Anti-Graffiti paint to Brick slip Cladding |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2016-08-02 | 2016-07-29 11:53 | -4 | 2016-05-19 12:01 | Architectural - Finishes | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Specification clause JH42.1209 (n) requires a factory applied anti-graffiti coating to the brick slip cladding. This has not been carried out and The Contractor is proposing to apply the coating on site
| 03SR - Stations (RfL) | Cxxx-NCR-002245 | NCR | No evidence of off-site testing for brick slip cladding spec clause JH42.2202 |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2017-06-30 | 2017-08-30 11:35 | 61 | 2016-05-19 12:14 | Civil - Structural Engineering | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | It appears that the offsite testing required for Brick Slip Cladding by specification Cxxx-SKC-A-RSP-B071_WS077-50003 clause JH42.2202 has not been carried out
| 03SR - Stations (RfL) | Cxxx-NCR-002246 | NCR | Lift shaft wire loops not installed |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-10-17 | 2016-09-07 07:10 | -40 | 2016-05-20 06:54 | Structural Engineering - Pre-cast | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Location = Lift shaft precast wall connections GL 06-07 and GL 18-19: With reference to Cxxx-RFI-003432: Please see the attached mark-up showing locations where wire loops are required for precast wall connections but were omitted during slab construction.
| 03SR - Stations (RfL) | Cxxx-NCR-002247 | NCR | Brickslip precast panels (ref:P-SW-P21 & P-SW-P16) clash with the Permanent RC structure |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-10-09 | 2017-10-07 10:42 | -2 | 2016-05-21 07:24 | Architectural - Walls | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | 2no. of the brickslip precast panels that have been cast will clash with the permanent RC structure. These are panel reference numbers P-SW-P17 and P-SW-P16, which sit near GL 10 and 14 respectively on the South wall at EBT/Dept Rd. These panels sit at the edge of the Departures Road level slab. Prior to these panels being installed, it became apparent from the on site survey that they would clash with the Departures Road level slab by approximately 200mm if they were to be installed in their correct position. See the attached drawings. the 1100mm dimension on each panel should be 1300mm. Panels have not been installed on site and sent back to the factory to await further agreement on action.
| 03SR - Stations (RfL) | Cxxx-NCR-002248 | NCR | Half Landing GL 7-8 109.675m Section1- 1 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-07-22 | 2016-06-14 08:48 | -38 | 2016-05-23 12:44 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Issue 1. North East end: Couplers to connect the half landing were fixed in the surrounding walls, however 2 No. set are missing, see attached drawing. 2 No. B16 Top and 2 No. B16 Bottom BM56. Issue 2. The connection between the insitu half landings and precast stairs requires a recess for the connection of the stairs however to accommodate the precast stairs the U bar (BM11) need to be reduced from 180mm to 100mm. This is applicable to the two half landing on this level.
| 03SR - Stations (RfL) | Cxxx-NCR-002249 | NCR | Half Landing GL 7-8 Section 2-2 112.850m |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-07-22 | 2016-06-14 08:50 | -38 | 2016-05-23 13:14 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Issue 1. 5 areas of missing couplers highlighted in the attached drawing Cxxx-SKC-C-DWG-B071_WS077-52460 and Concourse Half landing - post fixing detail. Issue 2 A recess is required in the half landings for the connection between the half landings and the precast stairs however this will require the U bar with BM11 to be reduced from 180mm to 100mm.
| 03SR - Stations (RfL) | Cxxx-NCR-002250 | NCR | Half landing GL 7-8 Section 3-3 115.588m |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-07-22 | 2016-06-14 08:51 | -38 | 2016-05-23 16:58 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Issue 1: See attached Cxxx-SKC- C-DWG-B071_WS077-52460 Section 3-3 for detailing on achievable post fixing for missing couplers (3 No. B1 B16 and 2 No. T1 B16). Issue 2: A recess is required in the half landings for the connection between the half landings and the precast stairs however this will require the U bar with BM11 to be reduced from 180mm to 100mm.
| 03SR - Stations (RfL) | Cxxx-NCR-002251 | NCR | __ to E__ Staircase, GL9: As-Built Tolerances (__ NCR 476) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-09-15 | 2016-09-07 07:13 | -8 | 2016-05-24 08:12 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A section of stair threads were poured to a lower elevation and the stair nosing is out of position. Please see attached drawing - Cxxx-NCR-002251 __ stair GL9 As built survey.
| 03SR - Stations (RfL) | Cxxx-NCR-002252 | NCR | __ to E__ Stairs GL15: As built Levels (__ NCR 477) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-09-15 | 2016-09-01 11:21 | -14 | 2016-05-24 08:22 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A section of the stair threads and landing has been poured to a lower elevation. Please see attached drawing - Cxxx-NCR-002252 __ stair GL15 As built survey.
| 03SR - Stations (RfL) | Cxxx-NCR-002253 | NCR | CMS Installation in Intermediate Rooms West End using Stage F Drawings |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-02-25 | 2017-02-15 14:24 | -10 | 2016-05-25 09:10 | Electrical - Cable Management | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Through consultation between and __, installation of CMS in the intermediate rooms on the west End of the Main Box has been agreed to proceed using Stage F drawings for the installation process due to the Stage J drawings not having been approved yet. This CMS installation will only involve fitting unistrut channels to the existing halfen channels installed in the soffit of these rooms / corridors. This is a risk mitigation in order to progress the MEPH installation on site.
| 03SR - Stations (RfL) | Cxxx-NCR-002254 | NCR | Windpost ties cut to shorter length in areas where a builderswork hole in next to the windpost |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-01-25 | 2017-02-23 09:19 | 29 | 2016-06-02 13:24 | Architectural - Masonary | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Windpost ties were cut down to 10 mm (min) in areas where the windpost is located next to a builderswork hole
| 03SR - Stations (RfL) | Cxxx-NCR-002255 | NCR | Intermediate Level Wall IL-L-22 – Full Height not achieved (__-479) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-08-05 | 2016-06-17 15:13 | -49 | 2016-06-06 06:37 | Structural Engineering - Structural Engineering - General | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A small section of the south side of wall IL-L-22 was not poured full height up to the soft top joint (see attached photo and location diagram).
| 03SR - Stations (RfL) | Cxxx-NCR-002256 | NCR | PES - Hoarding PES interface |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-02-28 | 2017-01-25 11:41 | -34 | 2016-06-06 17:03 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Non-compliant sealant has been used on the permanent PES frame works as part of the temporary platform hoarding.
| 03SR - Stations (RfL) | Cxxx-NCR-002257 | NCR | Concrete Mix 263 (MCR 50319)– Placement Time exceeded (__-484) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-08-07 | 2016-06-24 14:03 | -44 | 2016-06-08 06:54 | Structural Engineering - Structural Engineering - General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Specification Clause KF11.3221. 2hr time limit from batching to end of placement exceed. Location details as per the attached table.
| 03SR - Stations (RfL) | Cxxx-NCR-002258 | NCR | Concrete Mix 570 (MCR 50612)– Placement Time exceeded (__-482) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-08-07 | 2016-07-08 08:46 | -30 | 2016-06-08 07:00 | Structural Engineering - Structural Engineering - General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Date Ticket no. Mix line Ref; Truck Location; time exceeded the 2hrs from batching to placement; 28/05/2016. 107748; 570; TVP, Maintenance stairs GL20+kicker PL-T-25; 13mins; Specification Clause KF11.3221. 2hr time limit from batching to end of placement exceed for the above pours.
| 03SR - Stations (RfL) | Cxxx-NCR-002259 | NCR | Concrete Mix 80 (MCR 50599) – Placement Time exceeded (__-483) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-08-07 | 2016-06-24 14:09 | -44 | 2016-06-08 07:39 | Structural Engineering - Structural Engineering - General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Ticket no; Mix line Ref; Truck Location; time exceeded the 2hrs from batching to placement time exceeded 1 hr b/n the pours; 20/04/2016; 107096; 80; west retaining wall; 21mins; 17/05/2016; 108332; 80; West retaining wall before GL1; 13 mins; Specification Clause KF11.3221. 2hr time limit from batching to end of placement exceed for the above pours.
| 03SR - Stations (RfL) | Cxxx-NCR-002260 | NCR | Concrete Mix 171 (MCR 50255)– Placement Time exceeded (__-485) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-08-07 | 2016-06-24 14:15 | -44 | 2016-06-08 07:43 | Structural Engineering - Structural Engineering - General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Date; Ticket no; Truck Location; time exceeded the 2hrs from batching to placement time exceeded 1 hr. b/n the pours; 04/04/2016; 109611; L-39 wall infill<GL4; 26mins; Specification Clause KF11.3221. 2hr time limit from batching to end of placement exceed for the above pours.
| 03SR - Stations (RfL) | Cxxx-NCR-002261 | NCR | __ Ductwork IRF's - North East & South East |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-11-30 | 2016-10-28 10:53 | -33 | 2016-07-12 06:33 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | IRF's not raised in line with ITP.
| 03SR - Stations (RfL) | Cxxx-NCR-002262 | NCR | __ Ductwork IRF's - North West & South West |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-11-30 | 2016-11-04 14:38 | -26 | 2016-07-12 06:39 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | IRF's not raised in line with ITP
| 03SR - Stations (RfL) | Cxxx-NCR-002263 | NCR | IRF on cast iron downpipes |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-10-11 | 2016-10-20 08:51 | 9 | 2016-07-12 06:41 | Mechanical - Public Health Engineering | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | IRF not raised in line with ITP on Cast iron downpipes and north wall
| 03SR - Stations (RfL) | Cxxx-NCR-002264 | NCR | Bracketry on durasteel |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-11-30 | 2016-11-25 13:53 | -5 | 2016-07-12 06:56 | Mechanical - Heating Ventilation & Air Conditioning | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Bracketry on durasteel northwest corner installed out of plumb and level
| 03SR - Stations (RfL) | Cxxx-NCR-002265 | NCR | Bracketry on durasteel |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-11-30 | 2016-11-25 13:57 | -5 | 2016-07-12 06:54 | Mechanical - Heating Ventilation & Air Conditioning | 5000 |  | Workmanship | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | bracketry on durasteel southwest corner not installed plumb or level
| 03SR - Stations (RfL) | Cxxx-NCR-002266 | NCR | Bracketry on durasteel |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-11-30 | 2016-11-25 13:58 | -5 | 2016-07-12 06:59 | Mechanical - Heating Ventilation & Air Conditioning | 5000 |  | Workmanship | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Bracketry on durasteel southeast corner installed out of plumb and level
| 03SR - Stations (RfL) | Cxxx-NCR-002267 | NCR | Bracketry on durasteel |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-01-31 | 2016-11-25 14:12 | -67 | 2016-07-12 07:01 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Supporting drop rods on southeast durasteel installed incorrect length
| 03SR - Stations (RfL) | Cxxx-NCR-002268 | NCR | Earthing connections onto durasteel ductwork |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-01-31 | 2016-11-25 14:35 | -67 | 2016-07-12 07:03 | Mechanical - Heating Ventilation & Air Conditioning | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Earthing bolts incorrect size and in wrong location on ductwork
| 03SR - Stations (RfL) | Cxxx-NCR-002269 | NCR | Installation of __ different to DDCD |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-05-31 | 2017-04-18 10:50 | -43 | 2016-07-12 07:06 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The sub-contractor has changed the install of the durasteel ductwork from the approved DDCD
| 03SR - Stations (RfL) | Cxxx-NCR-002270 | NCR | __ drop rods |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-01-31 | 2017-02-01 12:51 | 1 | 2016-07-12 07:07 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | All corners of station where durasteel is installed some supporting drop rods are bent/twisted
| 03SR - Stations (RfL) | Cxxx-NCR-002272 | NCR | __ support beams |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-09-10 | 2016-09-28 11:35 | 18 | 2016-07-12 07:10 | Mechanical - Heating Ventilation & Air Conditioning | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | __ support beams in all corners, have holes in the channel iron from incorrectly drilled holes .
| 03SR - Stations (RfL) | Cxxx-NCR-002273 | NCR | Wall __-L-19 cast outside tolerance |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-10-15 | 2016-08-24 16:09 | -52 | 2016-06-16 10:52 | Structural Engineering - Structural Engineering - General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The concrete in-situ wall __-L-19 has been cast 30mm out of position at one end. The wall end elevation is now 3665mm from Gridline 19 The correct dimension is 3635mm. Refer attached marked up drawings for details.
| 03SR - Stations (RfL) | Cxxx-NCR-002274 | NCR | __ - Machouse basement retaining wall cores |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-07-29 | 2016-07-27 10:42 | -2 | 2016-06-16 16:58 | Civil - Civil Engineering General | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Please refer to NCR-000858. A further 8 areas in the machouse basement retaining wall were cored into when core samples were taken from the D-wall between GL17 and GL 24. See attached photos.
| 03SR - Stations (RfL) | Cxxx-NCR-002275 | NCR | West Retaining Wall – 28 day Cube Failures cube 2624 and 2637 (__-489) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-10-05 | 2016-09-07 08:00 | -28 | 2016-06-22 06:52 | Structural Engineering - Structural Engineering - General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | 1. Cubes 2624 and 2637 have failed to reach required strength of C45N for the West Retaining Wall. (Note a C50 mix has been used). Cube 2637 is predicted to exceed the 45N strength requirement at 56days whereas cube 2624 is predicted to achieve around 42N . Once the 56day results are obtained there are no further remaining cubes for crushing at 91 days. The mix used in these locations is Mix 122 (MCR 50053) 2. Cube 2627 has failed to reach required strength of C45N for the West Retaining Wall. This cube is predicted to exceed the 45N strength requirement at 56days. Cube 2644 has a low 7day result of 22.6N and whilst it is predicted to fail at 28days like cube 2627 it is predicted to pass at 56days. The mix used for these cubes is mix 80 (MCR 50599) which has a 66% GGBS content and thus low early strength gain.
| 03SR - Stations (RfL) | Cxxx-NCR-002276 | NCR | West Retaining Wall – 28 day Cube Failures cube 2616 (__-491) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-10-05 | 2016-09-05 14:38 | -30 | 2016-06-22 06:58 | Structural Engineering - Structural Engineering - General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Cube 2616 has failed to reach required strength of C50N for the concrete collars to the precast ducts joints in the West Retaining Wall. The mix used in these locations is Mix 122 (MCR 50053). This mix was also used for a small pour to the Western Retaining Wall on the West side of the Osborne Tunnel. As the concrete grade for this wall is specified as C35/45, the concrete whist not achieving 50N, has met the required strength of 45N. Also to note is that the result is a very marginal fail on the fck -4N rule for an individual failure (average 45.55N, 46N required to still achieve compliance. See conformity table attached. Note cube failures for cube 2624 and 2637 have been raised under a separate NCR.)
| 03SR - Stations (RfL) | Cxxx-NCR-002278 | NCR | Concrete Mix 263 (MCR 50319)– Placement Time exceeded (__-493) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-09-06 | 2016-08-05 09:59 | -32 | 2016-06-23 15:29 | Structural Engineering - Structural Engineering - General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Specification Clause KF11.3221. 2hr time limit from batching to end of placement exceed. Pour location details are found in the attached table.
| 03SR - Stations (RfL) | Cxxx-NCR-002279 | NCR | Brickslip Cladding - South Elevation Panel P25 Clash with Permanent RC structure |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-10-09 | 2017-10-07 10:51 | -2 | 2016-06-25 10:20 | Architectural - Brickworks/Blockworks | 5000 |  | Manufacturing Defect | Rework | 3 (3-6k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | During the installation of the south brickslip cladding elevation it was discovered from a site survey that the most easternly panel (P25) clashed with the permanent RC structure by approximately 25mm. In order to resolve this issue the panel was removed from site and 40mm was cut from it to retain the tolerance gap.
| 03SR - Stations (RfL) | Cxxx-NCR-002280 | NCR | Brickslip Cladding - Missing dowel pockets in wall L43 (GL12) for south elevation installation |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-11-04 | 2016-09-16 14:26 | -49 | 2016-06-25 10:31 | Structural Engineering - Load Bearing Walls | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Shortly before the installation of the south brickslip cladding elevation it was discovered that 2 no. 300x300x400mm dowel pockets (box outs) in the top of wall L43 were omitted during its construction. These pockets are the main fixing point for the brickslip cladding panels.
| 03SR - Stations (RfL) | Cxxx-NCR-002281 | NCR | Service corrdior waterproofing damage, GL 9-16 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-08-31 | 2018-12-04 09:36 | 95 | 2016-06-25 10:42 | Civil - Drainage | 5000 |  | Damaged | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | During the installation of the south elevation of brickslip panels, a temporary restraint scheme was required. This was in the form of push pull props, attached to the southern wall of the service corridor. In order to install these props, the protective screed and waterproof membrane in these areas had to be compromised. In the short term, any areas where the waterproofing was potentially compromised was covered with grout to limit water ingress. This was mainly where the 2 no. stainless steel all-thread fixings were drilled into the wall. These were cut flush before being covered with grout. The grout mounds will also clearly define their position for future works.
| 03SR - Stations (RfL) | Cxxx-NCR-002283 | NCR | Brickslip Cladding - Unapproved material - Parex drypack C |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-12-05 | 2016-11-25 14:52 | -10 | 2016-06-25 12:09 | Architectural - Brickworks/Blockworks | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The MCR for "Parex drypack C" (Cxxx-SKC-O-TSC-B071_WS077-50698) was not code 1 or 2 when the product was installed on site.
| 03SR - Stations (RfL) | Cxxx-NCR-002284 | NCR | Brickslip Cladding - Unapproved material - Injection Mortar FIS V |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-12-05 | 2016-11-25 14:55 | -10 | 2016-06-25 12:31 | Architectural - Brickworks/Blockworks | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | A code 1 or 2 MCR for the injectable mortar Fiscer FIS V was not in place before it was used in the bottom fixings of the 'staircase' panels on the south elevation of the brickslip.
| 03SR - Stations (RfL) | Cxxx-NCR-002285 | NCR | Brickslip Cladding - Unapproved material - nuts, bolts, washers and shims |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-12-05 | 2016-11-25 15:02 | -10 | 2016-06-25 12:34 | Architectural - Brickworks/Blockworks | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The MCR for nuts, bolts, washers and shims (Cxxx-SKC-O-TSC-B071_WS077-50690) was not code 1 or code 2 before works began on site.
| 03SR - Stations (RfL) | Cxxx-NCR-002286 | NCR | Brickslip Cladding - unapproved material - concrete backing |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-07-21 | 2017-07-06 09:54 | -15 | 2016-06-25 12:38 | Architectural - Brickworks/Blockworks | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The MCR for the backing concrete (Cxxx-SKC-O-TSC-B071_WS077-50629) was not in place code 1 or 2 before fabrication occured.
| 03SR - Stations (RfL) | Cxxx-NCR-002287 | NCR | Brickslip Cladding - Unapproved material - Acoustic material coating |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-12-05 | 2016-11-25 15:07 | -10 | 2016-06-25 12:41 | Architectural - Brickworks/Blockworks | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | A code 1 MCR for the acoustic material coating (Cxxx-SKC-O-TSC-B071_WS077-50697) was not in place before fabrication occured.
| 03SR - Stations (RfL) | Cxxx-NCR-002288 | NCR | Brickslip Cladding - South elevation bottom fixing - halfen channel loading |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-10-15 | 2016-11-25 15:16 | 41 | 2016-06-25 12:50 | Architectural - Brickworks/Blockworks | 2500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The bottom fixings of the south elevation of brickslip cladding are connected to a halfen channel cast into wall L43. This fixing caries axial load in compression and tension (due to blast pressure loading). __ seemingly only assure the product in tension, therefore the fixing has been installed outside of the manufacturer's recommendations.
| 03SR - Stations (RfL) | Cxxx-NCR-002289 | NCR | Intemediate level Corridor Blockwork Wall Damaged at Rooms CER IV CWU & SER CWU |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-08-30 | 2016-08-22 16:10 | -8 | 2016-06-29 08:39 | Architectural - Brickworks/Blockworks | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Blockwork wall cracked due to collision with MEWP going through the room. Cracks appearing in three diferent locations along rooms CER IV CWU & SER CWU. Crack appear only in the mortar joints
| 03SR - Stations (RfL) | Cxxx-NCR-002290 | NCR | BLL - Public staircase soffit Architectural finish |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-10-31 | 2016-09-15 12:26 | -46 | 2016-06-29 13:41 | Civil - Construction Health & Safety | 2500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The soffit of the public staircase in the Bakerloo Line Link does not conform with the architectural specification, JE80 CONCRETE - ARCHITECTURAL REQUIREMENTS.
| 03SR - Stations (RfL) | Cxxx-NCR-002291 | NCR | Precast vent duct connection to western retaining wall |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-09-12 | 2016-07-29 16:02 | -45 | 2016-06-29 13:37 | Structural Engineering - Structural Engineering - General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Precast vent ducts once installed should terminate at the south face of the western retaining wall. An as-built was provided following accepted remedy to Cxxx-NCR-002239 & Cxxx-NCR-002076, showing the distance from the near faces of the wall to the 900x400mm precast vertical units as 2365mm (refer attached). The revised production details were incorrect and only provided 2220mm. Therefore ducts terminate 145mm too short.
| 03SR - Stations (RfL) | Cxxx-NCR-002293 | NCR | Plunge Column in-fill tile GL15-16 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-02-26 | 2017-02-15 14:28 | -11 | 2016-07-06 11:19 | Civil - Structural Engineering | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The plunge column in-fill tile at Gridline 15-16, (FS-45B) concourse level soffit, was initially installed incorrectly. The attached photograph shows severeley cranked bars and bars which have been fixed with resin which is not in accordance with the DDCD Furthermore, the reinforcement bars for the cast-in items are not a typical detail and similarly not in accordance with the DDCD for plunge column in-fill works. These issues were noted before the grout had time to set and the tile has since been lowered onto the platform level. A new as-built has been taken of the dowel bar locations and a new tile is to be manufactured.
| 03SR - Stations (RfL) | Cxxx-NCR-002294 | NCR | Unpaid lift shaft - Offset sleeves - L-43 - south wall |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-06-01 | 2017-06-01 15:56 | 0 | 2016-07-14 17:29 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following discussions with design Team and after site survey, attached (see detail 8) on L-43, south wall, GL12, note that the cast-in sleeves to fix the "T" stubs for the Unpaid lift shaft are in wrong position according the drawing Cxxx-SWN-S-DDD-M171_Z-05060.
| 03SR - Stations (RfL) | Cxxx-NCR-002295 | NCR | Working to P status drawings |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-02-12 | 2017-02-15 16:03 | 3 | 2016-07-18 14:39 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Ducting was installed with drawings at P status.
| 03SR - Stations (RfL) | Cxxx-NCR-002298 | NCR | draiange pipeworjk commenced on P rev drawings |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2017-02-28 | 2017-02-15 16:38 | -13 | 2016-07-16 12:05 | Mechanical - Public Health Engineering | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Pipework being constructed from P rev drawings
| 03SR - Stations (RfL) | Cxxx-NCR-002299 | NCR | Use of P status drawings for construction |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-03-15 | 2017-02-17 14:48 | -26 | 2016-07-18 13:01 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | Ventilation ductwork has been installed using P status drawings in contradiction to the Works Information and approved ITP for the works.
| 03SR - Stations (RfL) | Cxxx-NCR-002301 | NCR | Non palletised delivery of materials |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-09-16 | 2016-09-06 08:12 | -10 | 2016-07-18 14:44 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Materials were delivered into the main box via a skip dropped in using the crane. This does not comply with the works information and approved ITP for these works. Materials should be palletised for delivery to site.
| 03SR - Stations (RfL) | Cxxx-NCR-002302 | NCR | IRF not issued for ductwork |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-09-16 | 2016-09-22 12:13 | 6 | 2016-07-18 14:57 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | IRFs were not issued within a reasonable notice period or not at all during the installation of ductwork
| 03SR - Stations (RfL) | Cxxx-NCR-002303 | NCR | Brickslip Cladding - South elevation drypack failure to reach specified strength |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-06-30 | 2017-08-19 08:03 | 50 | 2016-07-20 20:42 | Architectural - Brickworks/Blockworks | 2500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Upon receipt of cube results for dry pack used during the installation of South Wall Precast Brick Slips Units (Paddington Main Box, GL 9-15) cube results were found to not have achieved the strength as stated in the product technical specifications (See MCR Cxxx-SKC-O-TSC-B071_WS077-50698). The target material strength in 48kN @ 28 days. Cubes were achieving between 10 and 38 Kn @ 28 Days testing
| 03SR - Stations (RfL) | Cxxx-NCR-002304 | NCR | RC Corbel - Failure of pull test in top left corbel |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-11-04 | 2016-09-22 12:11 | -43 | 2016-07-21 17:42 | Structural Engineering - Reinforcement | 15000 |  | Workmanship | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | As per ITP Cxxx-SKC-C-ITP-B071_WS077-50131 for the corbel and beam construction, pull testing was carried out on a series of H10 and H12 bars fixed into the north diaphragm wall with __ Hit 200. 4 no. bars have failed the pull test, as specififed by the corbel designer.
| 03SR - Stations (RfL) | Cxxx-NCR-002305 | NCR | __ Installation of ventilation ductwork on intermediate level GL9 to 20 |  | Contr | COS | PAD - Paddington Station (West) |  | 2016-11-14 | 2016-11-04 11:15 | -10 | 2016-07-22 14:28 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | It was discovered during surveillance on the installation of ventilation ductwork on intermediate level GL9 to 20, that the materials listed below had not been submitted to CRL for approval. Square washers (CRL-MCR-003407), Ductwork (CRL-MCR-003535), G clamps (CRL-MCR-003202), Calcium silica blocks (CRL-MCR-003515), Vent hatches (CRL-MCR-003382) are in the process to submit the above materials to CRL within the next 7 days.
| 03SR - Stations (RfL) | Cxxx-NCR-002306 | NCR | Eastbourne Terrace Level: EN15 Slab post fix |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-09-24 | 2016-09-12 10:03 | -12 | 2016-07-26 15:05 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Slab EN15 at ETL requires B12 post fixing due to missing couplers/shortfall of kickerstrip as identified in Cxxx-SKC-C-DWG-B071_WS077-50607 and attached annotated image.
| 03SR - Stations (RfL) | Cxxx-NCR-002307 | NCR | Concrete Mix 122 (MCR 50053)– Placement Time exceeded (__F 496) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-09-26 | 2016-08-24 07:29 | -33 | 2016-07-28 14:03 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Please see attached Table of Exceedance. Specification Clause KF11.3221. 2hr time limit from batching to end of placement exceed for the above pours.
| 03SR - Stations (RfL) | Cxxx-NCR-002308 | NCR | Concrete Mix 263 (MCR 50319)– Placement Time exceeded (__F 494) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-09-26 | 2016-09-05 14:42 | -21 | 2016-07-28 14:09 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | See attached Table of Exceedance. Specification Clause KF11.3221. 2hr time limit from batching to end of placement exceed for the above pours.
| 03SR - Stations (RfL) | Cxxx-NCR-002309 | NCR | Concrete Mix 171 (MCR 50255)– Placement Time exceeded (BFF 495) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-09-26 | 2016-08-11 14:48 | -46 | 2016-07-28 14:24 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | See attached Table of Exceedance. Specification Clause KF11.3221. 2hr time limit from batching to end of placement exceed for the above pours.
| 03SR - Stations (RfL) | Cxxx-NCR-002310 | NCR | Low 28day cube results Mix 171 (MCR50255) (__F 497) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-10-26 | 2016-10-07 11:29 | -19 | 2016-07-28 14:37 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | See Concrete attached delivery records attached for locations and results. The cubes have failed to reach 28day compliance strength of 50N. Cube 2664 has a 7day result of 56.9N which would appear to be an anomaly and therefore be discounted.
| 03SR - Stations (RfL) | Cxxx-NCR-002311 | NCR | Front of House flooring perimeter edge strip |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-11-22 | 2016-11-25 13:30 | 3 | 2016-07-29 12:50 | Architectural - Flooring | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The screeding contractor for the front of house public areas has installed __ perimeter edge strip without a Code 01 MCR in place due to insufficient design.
| 03SR - Stations (RfL) | Cxxx-NCR-002312 | NCR | Base plates - Unpaid Lift- Concourse level |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-10-28 | 2016-11-25 15:36 | 28 | 2016-08-01 16:50 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | After Subcontractor survey (__) on the cast-in bolts, (check attached __ survey cast-in - Sketch 11 Jul 16) for the Unpaid lift on Concourse slab level, inform that the cast in bolts are not per the design intent (Cxxx-SKC-S-DDD-M171_Z-05050). For that reason the new setting-out/proposal of the correct locations of the bolts on the base plates will be issued for acceptance as a FCD.
| 03SR - Stations (RfL) | Cxxx-NCR-002313 | NCR | Low 28day cube results Mix 122, MCR50053 (__F 500) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-10-26 | 2016-10-12 06:29 | -14 | 2016-08-02 16:41 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The cubes results attached have failed to reach 28day compliance strength of 50N.
| 03SR - Stations (RfL) | Cxxx-NCR-002314 | NCR | Pull testing for Chemical Fixing and Anchors |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-12-31 | 2017-06-30 16:08 | -184 | 2016-08-04 12:30 | Electrical - Cable Management | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The current Pull tests have been conducted to 2Kn for 2 mins. Formal documentation is not in place to demonstrate the type of testing. The testing must in compliance with manufactures recommendations, CRL guidelines and the Structural Engineer assessment.
| 03SR - Stations (RfL) | Cxxx-NCR-002315 | NCR | P Status Drawing |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-01-25 | 2017-02-17 15:03 | 23 | 2016-08-07 12:26 | Electrical - Lighting | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | The following drawings are P Status and are currently the installation work is progressing to these drawings: Cxxx-SKC-E-DDA-M171_1-31600 and Cxxx-SKC-E-DDA-M171_1-31601
| 03SR - Stations (RfL) | Cxxx-NCR-002316 | NCR | P status Drawings |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-04-30 | 2017-02-20 11:33 | -69 | 2016-08-07 12:33 | Electrical - Cable Management | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | Drawings Cxxx-SKC-E-DDA-M171_1-31670 and Cxxx-SKC-E-DDA-M171_1-31671 are at P status
| 03SR - Stations (RfL) | Cxxx-NCR-002317 | NCR | P Status Drawings |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-02-21 | 2017-02-17 15:18 | -4 | 2016-11-23 09:46 | Fire - Detection | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | Lack of accepted design to progress installation.
| 03SR - Stations (RfL) | Cxxx-NCR-002318 | NCR | Not offering CSJV and CRL the opportunity to inspect the CMS installation. |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-10-07 | 2016-10-28 13:03 | 21 | 2016-08-08 11:29 | Electrical - Cable Management | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The installation of the CMS in the Intermediate corridor has not been issued up to and CRL for inspection.
| 03SR - Stations (RfL) | Cxxx-NCR-002319 | NCR | Eastbourne Terrace Level: ETL-T-03 Kicker, Reduced Cover |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-10-08 | 2016-09-13 09:51 | -25 | 2016-08-09 07:57 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | See attached drawings. ETL Wall ETL-T-03 wall kicker does not have enough cover. In some areas cover is as less as 15mm.
| 03SR - Stations (RfL) | Cxxx-NCR-002320 | NCR | Departures Road Level: __-L-06 GL 6-7, Wall Change |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-10-08 | 2016-09-28 10:34 | -10 | 2016-08-09 09:10 | Civil - Civil Engineering General | 2500 |  | Planning | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Drawing: Cxxx-SWN-S-DDC-M171_Z-04534 The beam at __-L-06 is non-structural and will be cast to the underside of the E__ slab soffit. To pour this last section of wall will require a pump and concrete pump line which have both been removed from the site.
| 03SR - Stations (RfL) | Cxxx-NCR-002321 | NCR | Public area floor Screed - Fibre type |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-11-20 | 2016-11-18 14:13 | -2 | 2016-08-09 08:57 | Architectural - Flooring | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The flooring contractor for the public areas at platform level used an acceptable product within the screed (Isocrete HD K Screed) but this was not within the approved MCR. The product used was Fibrecast 500 fibres. This is acceptable to use. MCR Number: Cxxx-SKC-O-TSC-B071_WS077-50014 Isocrete HD K Screed
| 03SR - Stations (RfL) | Cxxx-NCR-002322 | NCR | Quality plan - __ Contracts |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-01-23 | 2017-01-25 12:09 | 2 | 2016-08-10 15:33 | Architectural - Flooring | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The flooring subcontractor screeding the public areas at Platform level started and continued screed before an authorised Quality Plan was approved.
| 03SR - Stations (RfL) | Cxxx-NCR-002323 | NCR | P Status Drawings |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-11-30 | 2016-11-08 12:07 | -22 | 2016-08-10 15:44 | Fire - Fire Systems & General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | The following drawings are P Status and are currently the installation work is progressing to these drawings: Cxxx-SKC-E-DDA-M171_1-31700
| 03SR - Stations (RfL) | Cxxx-NCR-002324 | NCR | P Status Drawings - Eastbourne Terence |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-11-30 | 2016-11-25 16:13 | -5 | 2016-08-10 15:48 | Electrical - Electrical Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | The following drawings are P Status and are currently the installation work is progressing to these drawings: Cxxx-SKC-E-DDA-M171_1-31760
| 03SR - Stations (RfL) | Cxxx-NCR-002325 | NCR | P Stataus drawings - intermediate level lighting |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-12-01 | 2016-11-04 14:52 | -27 | 2016-08-10 15:54 | Electrical - Lighting | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The following drawings are P Status and are currently the installation work is progressing to these drawings:Cxxx-SKC-E-DDA-M171_3-31532 to 6
| 03SR - Stations (RfL) | Cxxx-NCR-002326 | NCR | P Status Drawing - Intermediate level CMS |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-02-21 | 2017-02-17 15:19 | -4 | 2016-11-23 09:42 | Electrical - Cable Management | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Lack of design to progress installation
| 03SR - Stations (RfL) | Cxxx-NCR-002327 | NCR | __ - Elastomeric- __ waterproofing lapping detail |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-06-28 | 2018-06-29 14:56 | 1 | 2016-08-10 17:17 | Civil - Civil Engineering General | 500 |  | System Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The waterproofing detail installed at GL24 according to the agreed Stirling Lloyd detail, in particular the 'LT tape' used to connect the two systems has not adhered to the substrate properly. The current system has been protected by a layer of ply board.
| 03SR - Stations (RfL) | Cxxx-NCR-002328 | NCR | P Status Drawings |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-12-23 | 2016-11-25 16:20 | -28 | 2016-08-11 16:07 | Electrical - Electrical Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | The following drawings are P Status and are currently the installation work is progressing to these drawings: Cxxx-SKC-E-DDA-M171_3-31662 to 7
| 03SR - Stations (RfL) | Cxxx-NCR-002329 | NCR | P status drawings |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-12-23 | 2016-11-25 16:21 | -28 | 2016-08-11 16:15 | Fire - Fire Systems & General | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | The following drawings are P Status and are currently the installation work is progressing to these drawings: Cxxx-SKC-E-DDA-M171_3-31732 to 7
| 03SR - Stations (RfL) | Cxxx-NCR-002330 | NCR | P Status Drawings |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-12-23 | 2016-11-25 16:31 | -28 | 2016-08-11 16:34 | Electrical - Lighting | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | The following drawings are P Status and are currently the installation work is progressing to these drawings: Cxxx-SKC-E-DDA-M171_3-31732 to 7
| 03SR - Stations (RfL) | Cxxx-NCR-002331 | NCR | P Status Drawings |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-01-31 | 2016-11-25 16:33 | -67 | 2016-08-12 07:36 | Electrical - Cable Management | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | The following drawings are P Status and are currently the installation work is progressing to these drawings: Cxxx-SKC-E-DDA-M171_3-41602 to 7
| 03SR - Stations (RfL) | Cxxx-NCR-002332 | NCR | Late provision of Mock Up - Vent Head House |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2016-10-07 | 2016-11-04 10:07 | 28 | 2016-08-18 16:18 | Archaeology - General | 25000 |  | Supervision/Management | Rework | 2 (6-60k) | Complete | Management Problem - Other | Completed |  | The vent head house mock up has not been progressed as part of the design process
| 03SR - Stations (RfL) | Cxxx-NCR-002333 | NCR | Red Line Drawing - Cxxx-SKC-Y-DDA-M171_3-63611 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-04-30 | 2017-02-11 15:32 | -78 | 2016-08-25 07:01 | Electrical - Cable Management | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Drawing No. Cxxx-SKC-Y-DDA-M171_3-63611 is not issued to eB nor CRL. The drawing is being used as Red Line drawing as per IRF Cxxx-SKC-E-RSP-B071_WS077-50002
| 03SR - Stations (RfL) | Cxxx-NCR-002334 | NCR | Red Line drawings |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-02-28 | 2017-02-11 15:41 | -17 | 2016-08-25 07:18 | Electrical - Cable Management | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Drawings Cxxx-SKC-Y-DDA-M171_4-63416, Cxxx-SKC-Y-DDA-M171_4-66407, Cxxx-SKC-Y-DDA-M171_4-63413, Cxxx-SKC-Y-DDA-M171_4-63410, Cxxx-SKC-Y-DDA-M171_4-63404 and Cxxx-SKC-Y-DDA-M171_4-63400 are P Status. The drawings aqre being used a Red Line Drawing. The CMS has been installed differently to suit the site requirements
| 03SR - Stations (RfL) | Cxxx-NCR-002335 | NCR | GL 1-9 Diaphragm Wall External Face Low Reinforcement Cover |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-10-07 | 2016-10-13 10:43 | 6 | 2016-08-31 07:18 | Structural Engineering - Diaphragm Walls | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | As shown within the attached survey titled ‘D-wall cover meter survey 24.08.16 and 25.08.16’, there are areas of low rebar cover on the external face of the diaphragm wall between gridlines 1-9E. These areas have been identified following the construction of a King post wall between gridlines 1-9E, to allow for installation of the __ waterproofing. The D-wall panels shown within the cover meter survey correspond to D-wall panels N1-N21 (see attachments ‘Cxxx-SKC-C-DWG-B071_WS077-50001’ and ‘King Post Wall numbering system’). Cxxx-RFI-003619 has been raised regarding the nominal reinforcement cover required on the external face of the D-wall, with 75mm stated on D-wall reinforcement drawings. The attached survey identifies areas of cover below 75mm in red, and areas of cover below 50mm in yellow. propose to build up cover to a minimum of 50mm nominal cover with Monomix HD, as per internal face diaphragm wall repairs. Once made good the cover meter survey will be repeated, and the D-wall panels will be offered to Crossrail for inspection prior to the application of waterproofing (see Cxxx-FCD-000949). Please refer to Cxxx-NCR-002336 regarding a repair proposal for the area of exposed reinforcement between King posts 22 and 24 (D-wall panels N3 and N4).
| 03SR - Stations (RfL) | Cxxx-NCR-002336 | NCR | GL 2-3 Diaphragm Wall External Face Exposed Reinforcement |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-05-24 | 2017-06-02 14:18 | 9 | 2016-09-02 10:15 | Structural Engineering - Diaphragm Walls | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | *** 15.09.2016 Second Investigation *** An additional 750mm of Diaphragm wall panel N4 has been exposed, on the external face. The area has been cover surveyed, as attached “Cover Survey Photos.pdf”. propose to locally make good by building up cover with Monomix HD around exposed spacers and horizontal link reinforcement to the nominal 45mm required as per Cxxx-RFI-003619. The area of exposed vertical reinforcement identified in the initial NCR has been broken out to 50mm behind the reinforcement and is to be made good with repair concrete. Please confirm this is an acceptable solution. *** 25.08.2016 Initial Cover Survey *** As shown within the attached survey titled ‘D-wall cover meter survey 24.08.16 and 25.08.16’, there is an area of exposed reinforcement on the external face of the diaphragm wall between gridlines 2-3E. This area has been identified following the construction of a King post wall between gridlines 1-9E, to allow for installation of the __ waterproofing. The D-wall panels that correspond to the location of the exposed reinforcement are panels N3 and N4, between King posts 22 and 24 (see attachments ‘Cxxx-SKC-C-DWG-B071_WS077-50001’ and ‘King Post Wall numbering system’). Cxxx-RFI-003619 has been raised regarding the nominal reinforcement cover required on the external face of the D-wall, with 75mm stated on D-wall reinforcement drawings. The attached survey identifies areas of cover below 75mm in red, and areas of cover below 50mm in yellow. propose to break back the existing D-wall concrete around the exposed reinforcement to a distance equal to that of the bar diameter i.e. 40mm. As shown within the attachment titled ‘N3 and N4 D-wall repair’, propose an initial repair area of approximately 3m x 0.5m x 0.080m. Subject to temporary works approval, this repair area will increase in size/height between 500-750mm below the current blinding level. As per internal face diaphragm wall repairs, will repair the exposed area using a concrete repair material, subject to MCR approval. As proposed within Cxxx-NCR-002335, nominal cover shall be built up to a minimum nominal cover of 50mm using the repair concrete. Once made good the cover meter survey will be repeated, and the D-wall panels will be offered to Crossrail for inspection prior to the application of waterproofing (see Cxxx-FCD-000949). Please confirm whether this proposal is acceptable.
| 03SR - Stations (RfL) | Cxxx-NCR-002337 | NCR | Eastbourne Terrace, GL 5 and GL 20: Nibs to doorway not constructed (__F 501) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-06-30 | 2017-06-29 07:50 | -1 | 2016-09-05 13:08 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Nibs to the doorways at GL 5 and 20 have not been constructed. ETL GL5 and GL20 : ETL-T-11, ETL-T-12, ETL-T-24, ETL-T-25 See marked up plan of drawings Cxxx-SWN-S-DDA-M171_2-01562 and 01565 attached.
| 03SR - Stations (RfL) | Cxxx-NCR-002338 | NCR | Installation of small power and lighting - without accepted ITP |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2017-01-31 | 2016-11-17 16:48 | -75 | 2016-09-01 12:22 | Electrical - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The Contractor has installed items of small power and lighting on site without the ITP being accepted by the Supervisor. This is in contravention of the works information and strictly prohibited by the 's own Quality Management system. Continued deliberate contravention of the 's QMS and non-compliance with the WI will result in a review of the effectiveness of the Quality Management System in accordance with 20.9 of the works information.
| 03SR - Stations (RfL) | Cxxx-NCR-002339 | NCR | Transformer room and HV Switchroom at west end of site have CMS installed without any design drawings in place |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2016-11-30 | 2016-11-17 16:55 | -13 | 2016-09-01 16:41 | Electrical - Cable Management | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | When invited to inspect CMS installation in three rooms, it became clear that design drawings did not exist for the CMS layout. The installation was installed to drawings produced for 'similar' rooms
| 03SR - Stations (RfL) | Cxxx-NCR-002340 | NCR | Wiring commenced on site in contravention of ITP hold point |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2017-01-31 | 2017-02-01 13:40 | 1 | 2016-09-02 08:59 | Electrical - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | CMS is not completed which is a hold point prior to cabling. Cabling commenced on 01.9.2016\02.09.2016 prior to completion of the CMS
| 03SR - Stations (RfL) | Cxxx-NCR-002341 | NCR | No accepted ITP for fabrication or installation of pipework for gaseous fire suppression system |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2017-08-01 | 2017-08-14 08:54 | 13 | 2016-09-05 08:19 | Systems - Fire Detection systems and Mains | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Pipework for gaseous fire suppression system commenced 3rd September 2016 without ITP in place for either fabrication or installation
| 03SR - Stations (RfL) | Cxxx-NCR-002342 | NCR | No ITP in place for installation of fire suppression system cabling |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2017-08-01 | 2017-08-14 08:50 | 13 | 2016-09-05 08:23 | Systems - Fire Detection systems and Mains | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | cabling associated with gaseous fire suppression system installed 2nd September by Protec, without an ITP
| 03SR - Stations (RfL) | Cxxx-NCR-002343 | NCR | Installation of gaseous fire suppression system without an accepted design in place |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2017-07-30 | 2017-07-07 12:45 | -23 | 2016-09-05 08:27 | Systems - Fire Detection systems and Mains | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The drawings for the gaseous fire suppression system have not been accepted by the designer nor offered to the PM for acceptance. All installations to date are to unofficial drawings that are subject to change
| 03SR - Stations (RfL) | Cxxx-NCR-002344 | NCR | Gaseous fire suppression system cabling installed in trunking in contravention of trunking ITP hold point |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2017-06-30 | 2017-06-28 15:26 | -2 | 2016-09-05 08:32 | Electrical - Cable Management | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | cabling for the gaseous fire suppression system was installed on 2nd September 2016 into trunking that has not been signed off as complete. this is in direct contravention of the hold point in the CMS ITP
| 03SR - Stations (RfL) | Cxxx-NCR-002345 | NCR | Brickslip Cladding - Corbel - Incomplete Pour |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-11-25 | 2016-09-21 16:27 | -65 | 2016-09-06 18:45 | Civil - Structural Engineering | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The lower level RC corbel and beam arrangement which supports the brickslip cladding panels was intended to be poured in one attempt. On the morning of the pour, a mechanical issue with one of the two required concrete pumps was identified, and the subcontractor installed "stop-ends" to limit the pour extent (05/09/2016). The subsequent pour was planned for the next day, and the stop ends were struck, scabbled back, inspected by and then re-poured. During this pour, the second concrete delivery was significantly delayed, but the supplier consistently re-assured the subcontractor that it was en-route. The end result was that a "cold joint" was at risk, and the Contractor instructed the subcontractor to install a stop end along from the pour and work backwards, with the intention of breaking out the end of the pour to create a construction joint. This was all done on 06/09/2016. The final 3m (linear) section of concrete will be poured on the 07/09/2016. Both ends (i.e. both construction joints) will be vertical and sufficiently scabbled, with the reinforcement inspected by both the Contractor and the Client in advance.
| 03SR - Stations (RfL) | Cxxx-NCR-002346 | NCR | Concrete Mix; 171 (MCR 50255), 161 (MCR 50255), 122 (MCR 50053) & 121 (MCR 50054) – Placement Time exceeded (BFF 502) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-11-08 | 2016-09-13 09:44 | -56 | 2016-09-09 13:50 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Ref Table of exceedance (Specification Clause KF11.3221. 2hr time limit from batching to end of placement exceed for the attached pours).
| 03SR - Stations (RfL) | Cxxx-NCR-002347 | NCR | KD 13 rooms, Presure Relief Dampers |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-04-30 | 2017-04-18 08:27 | -12 | 2016-09-12 11:34 | Mechanical - Heating Ventilation & Air Conditioning | 2500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | Provision of __ Pressure relief Dampers Gaseous Fire Suppression systems –the selected product still awaits approval. We have re-submitted proposing an LU approved finish in matt black. In the mean time instruct the Sub-contractor to install the currently unapproved damper.
| 03SR - Stations (RfL) | Cxxx-NCR-002349 | NCR | Sealing of KD13 room floors without ITP |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2016-12-23 | 2016-11-25 16:48 | -28 | 2016-09-12 11:40 | Architectural - Flooring | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | floor sealing of KD13 rooms was carried out on 10th September2016 without an accepted ITP in place
| 03SR - Stations (RfL) | Cxxx-NCR-002351 | NCR | __ and __R rooms - luminaires fixed at 2360mm above FFL |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2017-01-31 | 2016-11-17 16:37 | -75 | 2016-09-12 11:52 | Electrical - Lighting | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Luminaires have been fitted at 2360 above FFL rather than 2400mm. The designer has stated that there is a site wide issue with clashes between doors and light fittings \ CMS so NCR raised to focus attention to these key date rooms
| 03SR - Stations (RfL) | Cxxx-NCR-002352 | NCR | Winching points agreed to be omitted in KD 13 rooms, SR HV I, TR I, TR II, TR III, TR IV, SR HV II |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-04-14 | 2019-03-26 09:26 | 346 | 2016-09-14 12:31 | Architectural - General | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | The winching points in the KD13 rooms (room ref: SR HV I, TR I, TR II, TR III, TR IV, SR HV II ) have been omitted as per agreement with Cxxx. The pockets that were left out for the winch points have been infilled with screed to match the rest of the floor.
| 03SR - Stations (RfL) | Cxxx-NCR-002353 | NCR | Fire suppression system no MCR |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-07-31 | 2017-07-07 12:56 | -24 | 2016-09-13 15:14 | Fire - Suppression | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Concourse Level, HVI, HVII, TRI, TRII, TRIII and TRIV - The MCR was not approved prior to commencing the Fire Suppression installation.
| 03SR - Stations (RfL) | Cxxx-NCR-002354 | NCR | Fire alarm system not approved MCR |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-07-30 | 2017-07-07 13:20 | -23 | 2016-09-13 15:22 | Fire - Fire Systems & General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Concourse Level - HVI, HVII, TRI, TTRII, TRIII, TRIV - The Fire Alarm equipment was not MCR approved prior to installation.
| 03SR - Stations (RfL) | Cxxx-NCR-002355 | NCR | ITP for Comms Equipment not approved |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-02-28 | 2016-12-22 16:17 | -68 | 2016-09-14 12:39 | Communications and Control Systems | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The ITP for Installation of Comms equipment is not CRL approved.
| 03SR - Stations (RfL) | Cxxx-NCR-002356 | NCR | RAMS 440 for Installation of Equipment |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-10-14 | 2016-10-13 11:05 | -1 | 2016-09-14 12:47 | Communications and Control Systems | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The RAMS 440 for the Installation Comms Equipment needs to be accepted prior to commencing installation works.
| 03SR - Stations (RfL) | Cxxx-NCR-002357 | NCR | RAMS 380 latest rev 06 is not accepted. |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-10-14 | 2016-10-13 11:06 | -1 | 2016-09-14 13:03 | Electrical - Cable Management | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The RAMS Rev 06 is not approved which detailed the working in the confined space.
| 03SR - Stations (RfL) | Cxxx-NCR-002358 | NCR | Cast in bolts - BLL lift12 - Missed |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-05-14 | 2017-06-23 14:36 | 40 | 2016-09-15 14:21 | Civil - Civil Engineering General | 1500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | notes that, there is a discrepancy in the setting out of the counterweight support column and centre columns between, drawing Cxxx-SKC-S-DDD-M171_Z-21080 and __'s drawing 42139019-010-B-1-1_en_A.4. (both attached). We have reviewed onsite and the cast in anchors have been positioned to the Cxxx setting out, photo attached, with red marks. An FCD will be raised to close the NCR, regarding the post drill solution required as long with Cxxx checks on the structure.
| 03SR - Stations (RfL) | Cxxx-NCR-002362 | NCR | Surface Hairline crack within __-R room (Intermediate Level) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-02-28 | 2017-02-28 11:37 | 0 | 2016-09-21 14:35 | Architectural - Flooring | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Surface hairline crack within __-R on Intermediate level.
| 03SR - Stations (RfL) | Cxxx-NCR-002363 | NCR | Escalator Cladding Holder Clash with Concrete Intermediate Support (Esc 1-13) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-04-24 | 2017-04-21 11:00 | -3 | 2017-01-24 09:59 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | See attached the Cladding Layout Holders Drawings for Esc 1-13 for Paddington Cxxx. Note that there is currently no cladding holders installed on the trusses for Esc 14-15. Please also see image attached showing an example of the cladding holders which are located directly above the intermediate concrete supports under all Esc 1-13. As a result of this positioning, there are the following issues: a) Cladding Holder on bottom of truss clashes with the concrete thus preventing the escalator from being lined and leveled in its permanent position; or b) Cladding Holder just clears the concrete by a few millimetres which along with the issue above will still not provide enough clearance for the cladding to be fixed to these brackets.
| 03SR - Stations (RfL) | Cxxx-NCR-002364 | NCR | Materials used on site without MCR submitted |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2017-01-31 | 2017-01-30 11:08 | -1 | 2016-09-27 09:22 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | MCR for insulation hangers (pins) is not approved and has not been submitted to CRL for review.
| 03SR - Stations (RfL) | Cxxx-NCR-002365 | NCR | Fire Dampers to Sitewide |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-12-23 | 2017-02-15 08:35 | 54 | 2016-09-30 13:33 | Mechanical - Mechanical Engineering General | 60000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | __ dampers not Compliant with LU Fire stopping requirements. __ dampers installed with unapproved Fire Stopping detail.
| 03SR - Stations (RfL) | Cxxx-NCR-002366 | NCR | __ stained with epoxy resin grout |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-12-03 | 2016-11-04 10:02 | -29 | 2016-10-04 13:25 | Civil - Civil Engineering General | 2500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Refer attached photos of examples where an Epoxy Resin Grout has spilled (and set) onto the surface of the sprayed __ M11 at platform level. This has occurred in various locations on both the North and South D-Walls. FYI - details of the Epoxy resin grout material can be found in MCR # Cxxx-SKC-O-TSC-B071_WS077-50150 (__ __ EP and EPR).
| 03SR - Stations (RfL) | Cxxx-NCR-002367 | NCR | Cube 2547 – 28 day Cube Test Report Failure (__-478) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-03-31 | 2017-03-30 13:10 | -1 | 2016-10-05 11:23 | Structural Engineering - Structural Engineering - General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | 28 Day cube results failed to achieve required strength of 50N/mm2. Cube 2547B 41.4N/mm2 Cube 2547C 41.7N/mm2 7 day cube result 2547A achieved 27.6 N/mm2 56 day result 2547D achieved 50.9N/mm2 so has met strength requirement. Details regarding the location of this pour can be found in the attached documents.
| 03SR - Stations (RfL) | Cxxx-NCR-002368 | NCR | Unpaid lift shaft low capacity spigot connection |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2017-01-23 | 2017-02-01 13:47 | 9 | 2016-10-10 16:01 | Civil - Structural Engineering | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | It could not be demonstrated that the spigot connection met the fire engineering requirements
| 03SR - Stations (RfL) | Cxxx-NCR-002369 | NCR | Sealing of Back of House Screeds |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2017-01-23 | 2017-02-01 13:49 | 9 | 2016-10-12 07:44 | Architectural - Finishes | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Following a risk reduction meeting held on 7th October 2016, the have stated that they will no longer be sealing back of house screeded floors. This is in contravention of the specification and therefore any areas where sealing does not occur are non-conforming.
| 03SR - Stations (RfL) | Cxxx-NCR-002370 | NCR | Copex to lighting |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-01-25 | 2017-05-19 11:01 | 114 | 2016-10-14 13:20 | Electrical - Lighting | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Copex conduit not been installed in accordance with works information.
| 03SR - Stations (RfL) | Cxxx-NCR-002371 | NCR | Fireproof box on emergency light fittings |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-11-30 | 2017-12-05 10:29 | 5 | 2016-10-14 13:19 | Electrical - Lighting | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Emergency light fittings do not have a fireproof box.
| 03SR - Stations (RfL) | Cxxx-NCR-002372 | NCR | Non-Compliance with cleaning and maintenance strategy - BoH screeding |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2016-11-29 | 2016-11-25 14:25 | -4 | 2016-10-15 10:23 | Architectural - Flooring | 5000 |  | Incomplete Works | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The has stated that they will not be sealing back of house screed. This is in contravention of their own cleaning and maintenance strategy and finishes schedules that have been submitted to provide gate 3 design assurance
| 03SR - Stations (RfL) | Cxxx-NCR-002373 | NCR | LER room - No MCR in place for C40 concrete at time of pour |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-11-14 | 2016-11-17 17:10 | 3 | 2016-10-17 15:22 | Civil - Structural Engineering | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The C40 concrete for the RC roof slab for the LER room on intermediate level west was mixed and poured on 5/10/16, without a code 1 MCR in place.
| 03SR - Stations (RfL) | Cxxx-NCR-002375 | NCR | Incorrect fire alarm cable installed in KD rooms |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-01-20 | 2017-01-17 16:58 | -3 | 2016-10-22 12:37 | Fire - Fire Systems & General | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Incorrect fire alarm cable installed within KD rooms- Cable not as per specification. Subcontractor has installed FP200 gold cable and it should have been FT120
| 03SR - Stations (RfL) | Cxxx-NCR-002376 | NCR | Chiller units not compliant to 1085 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-03-31 | 2017-03-25 10:02 | -6 | 2016-10-22 13:09 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Chiller units found to not be compliant on recent FAT test to Carrier
| 03SR - Stations (RfL) | Cxxx-NCR-002378 | NCR | Non working to ITP on chilled water |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-01-22 | 2017-02-01 13:51 | 10 | 2016-10-24 11:17 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | installation has commenced on Chilled water pipework on intermediate level, __ have failed to raise any IRF for deliveries of materials
| 03SR - Stations (RfL) | Cxxx-NCR-002379 | NCR | Screed Finishes |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2016-11-09 | 2016-11-25 13:28 | 16 | 2016-10-26 15:45 | Architectural - Flooring | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During a joint site inspection of KD rooms it was noted in room SR LV IB that cracking had appeared in different locations, see attached photos. are to seek guidance from Screeding contractor and supplier and follow approved replacement or repair methods. CRL are to be invited to witness and inspect any repairs.
| 03SR - Stations (RfL) | Cxxx-NCR-002380 | NCR | Cracking to screed/architectural finish |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2016-12-23 | 2016-11-28 14:46 | -25 | 2016-10-26 16:01 | Architectural - Flooring | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During a joint site inspection of KD rooms it was noted in room FCR I that cracking had appeared in different locations and the finish was not in compliance with the specification. are to seek guidance from Screeding contractor and supplier and follow approved replacement or repair methods. CRL are to be invited to witness and inspect any repairs.
| 03SR - Stations (RfL) | Cxxx-NCR-002381 | NCR | Brickslip Cladding - Damaged Brick on P-NW-42 and P-NW-35-1 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-12-26 | 2017-02-20 12:47 | 56 | 2016-10-27 12:03 | Architectural - Brickworks/Blockworks | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the installation of the Brickslip panels on the north elevation, 2 no. panels (P-NW-42 and P-NW-25-1) received small damage to the bottom left and right corner respectively. This is expected during installation, and plans were made well in advance for any necessary remedial works. Technically, this is part of the installation but it was decided that as this is a prefabricated item it made sense to raise an NCR to capture the making good.
| 03SR - Stations (RfL) | Cxxx-NCR-002382 | NCR | VSHH - Use of non-standard HSFG Bolts within columns |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-01-13 | 2017-02-03 13:57 | 21 | 2016-11-01 17:28 | Structural Engineering - Structural Engineering - General | 250000 |  | Material | Use As-Is | 1 (>60k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | It has been noted that M16 HSFG bolts within the columns for the VSHH have been supplied and installed during fabrication to the wrong standard. The bolts have been supplied to BS4395 and not EN14399-7 as per the specification. Therefore it is not possible to provide assurance for these bolts. BS4395 is also a superseeded document. It is also noted works commenced prior to final MCR approval, and in turn did not follow the ITP. This will be raised on a seperate NCR.
| 03SR - Stations (RfL) | Cxxx-NCR-002383 | NCR | Wiring commenced on site in contravention of ITP hold point |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2017-03-29 | 2017-02-27 14:56 | -30 | 2016-11-02 14:11 | Electrical - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | CMS is not completed which is a hold point prior to cabling. Cabling commenced on 01.11.2016 prior to completion of the CMS
| 03SR - Stations (RfL) | Cxxx-NCR-002384 | NCR | Brickslip Cladding - North elevation dowel connection, misaligned pockets |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-02-01 | 2016-11-29 17:10 | -64 | 2016-11-03 10:21 | Architectural - Brickworks/Blockworks | 50000 |  | Manufacturing Defect | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | A dimensional error on the precast concrete brickslip cladding north elevation sectional drawing has resulted in the dowel pockets cast into the packets being 80mm too far to the brick face (south). A remedial solution either using a rock drill to the capping beam or a joggle dowel connection is required.
| 03SR - Stations (RfL) | Cxxx-NCR-002385 | NCR | Wiring commenced on site in contravention of ITP hold point |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2017-06-30 | 2017-06-30 15:29 | 0 | 2016-11-03 15:41 | Electrical - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | CMS lid being fitted within OHLE SR I (#781) before cabling installation is witnessed which is a hold point.
| 03SR - Stations (RfL) | Cxxx-NCR-002386 | NCR | GL24 Vent Head house low cover |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-03-14 | 2017-03-07 14:54 | -7 | 2016-11-07 15:30 | Civil - Civil Engineering General | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Areas of low cover have been uncovered on the Eastern face of the East Vent head house, after remediation works took place to facilitate the installation of the VHH steel work.
| 03SR - Stations (RfL) | Cxxx-NCR-002387 | NCR | KD12 - shrinkage crack - SR LV I B |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-01-03 | 2017-01-18 17:12 | 15 | 2016-11-04 10:11 | Architectural - Flooring | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Surface shrinkage crack has been identified within SR LV I B and SR LV I A
| 03SR - Stations (RfL) | Cxxx-NCR-002388 | NCR | KD12 - Shrinkage crack - SR LV II A |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-01-03 | 2017-01-18 17:13 | 15 | 2016-11-04 10:15 | Architectural - Flooring | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A surface shrinkage crack has been identified in KD12 room SR LV II A.
| 03SR - Stations (RfL) | Cxxx-NCR-002389 | NCR | KD19 - Shrinkage Crack: MCC I, FCR I, FCR II |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-01-03 | 2016-11-25 13:39 | -39 | 2016-11-04 10:21 | Architectural - Flooring | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Surface shrinkage cracks have been identified in KD19 rooms MCC I, FCR I and FCR II.
| 03SR - Stations (RfL) | Cxxx-NCR-002390 | NCR | KD16 - Shrinkage cracks: CER I and CER IV |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-01-03 | 2016-11-25 13:36 | -39 | 2016-11-04 10:25 | Architectural - Flooring | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Surface shrinkage cracks have been identified within the KD16 rooms CER I and CER IV.
| 03SR - Stations (RfL) | Cxxx-NCR-002391 | NCR | Scaffold Structure Resting on LV Transformer in TR I |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-01-25 | 2017-02-24 15:30 | 30 | 2016-11-04 13:34 | Structural Engineering - Structural Engineering - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Access Deck errected for work on the dampeners. In order to stop any horizontal movement of the scaffold it must be braced. With limited room to place the brace they decided to restrain the horizontl movement by clamping on the bund and situate a scaffold tube so that its touching the transformer.
| 03SR - Stations (RfL) | Cxxx-NCR-002394 | NCR | __ Ductwork |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-03-31 | 2017-03-18 10:53 | -13 | 2016-11-07 16:39 | Mechanical - Mechanical Engineering General | 10000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | __ ducts have been smoke tested and have failed, see attached drawing for details.
| 03SR - Stations (RfL) | Cxxx-NCR-002395 | NCR | Precast Concrete Smokeducts |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-03-31 | 2017-03-30 11:18 | -1 | 2016-11-07 16:52 | Mechanical - Mechanical Engineering General | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Two sections of pre cast concrete smoke ducts (of four in total)have been smoke tested and have failed, see attached drawing for details.
| 03SR - Stations (RfL) | Cxxx-NCR-002396 | NCR | Brickslip Cladding - Offsite Fabrication ITP for structural steelwork |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-11-16 | 2017-10-07 10:53 | -40 | 2016-11-07 19:38 | Architectural - Brickworks/Blockworks | 1500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The Brickslip cladding package requires structural steelwork for the support bracketry on the north and south elevations. The package manager misunderstood the process and thought that as the materials were being provided from a separate supplier with CE marking to EX2 as per the designer's requirements, that an offsite ITP was not required. The steelwork has been fabricated and installed on site without this ITP.
| 03SR - Stations (RfL) | Cxxx-NCR-002397 | NCR | Diamond Drilling in the Wrong Location |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-03-15 | 2017-02-27 15:04 | -16 | 2016-11-11 14:10 | Civil - Civil Engineering General | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | In acordance with Cxxx-PMI-00894 to core drill 2no. 125mm holes through intermedaite slab in the SRV I room. The location of these holes were marked out in the wrong room (SRV II). The core drill went 205mm deep before it was found out this was the wrong location. This core has cut through the top rebar at approximately 10mm. See drawing attached. location attached.
| 03SR - Stations (RfL) | Cxxx-NCR-002398 | NCR | Windpost Ties Cut to Correct Length in KD12 rooms |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-12-23 | 2017-01-18 15:36 | 26 | 2016-11-11 14:31 | Architectural - Brickworks/Blockworks | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Incorrect windpost ties installed where the windpost meets a builderswork hole openings. This is located in SR LV IA, SRLV IIA, SRLV IB, SRLV IIB rooms
| 03SR - Stations (RfL) | Cxxx-NCR-002399 | NCR | No Evidence of Caretaker Maintenance being carried out on Escalators whilst in Storage |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-01-23 | 2016-12-19 13:31 | -35 | 2016-11-14 15:56 | Mechanical - Escalators | 1500 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | To date have received no evidence or records that ‘Item 4.23 – Caretaker Maintenance’ as per the Code 1 ITP for __ Escalators Factory ITP (Cxxx-SKC-M1-ITP-B071_WS077-50005) has been undertaken. __ issued a proposed maintenance schedule via Aconex Correspondence OT-GC-000310 for which the above inspections should have been completed and then issued to for information. completed a surveillance at the storage location of the escalators in Keighley to verify Item 4.23 of the ITP and Cxxx-PMC-03257, as both the Contractor and Sub-contractor share responsibility for all caretaker maintenance / assurance requirements with the Client and other Works Information obligations during the period of storage. The contents of the document C740-OTS-M1-RGN-CRG03-50021_3.0 was also reviewed during this surveillance. The results of the surveillance are captured in document Cxxx-SKC-O-RGN-B071_WS077-50303. __ where unable to provide completed Caretaker Maintenance check sheets during the surveillance and thus assume that no maintenance has been undertaken to date as there has been no evidence provided by __ despite many requests.
| 03SR - Stations (RfL) | Cxxx-NCR-002400 | NCR | No Copy of Relevant __ Escalators Factory ITP at Storage Location of Escalators |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-01-23 | 2016-12-06 12:58 | -48 | 2016-11-14 16:09 | Mechanical - Escalators | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | It was found during a schedule surveillance at Keighley that a copy of the __ Manufacturing ITP (Cxxx-SKC-M1-ITP-B071_WS077-50005) was not available to hand in the location where the Paddington Cxxx escalators are stored. __ should have a copy of this on the storage location site with the Paddington Cxxx escalators as this is what __ operatives should be working to when carrying out the check sheet for Item 4.23 on the ITP.
| 03SR - Stations (RfL) | Cxxx-NCR-002401 | NCR | Incorrect cable sizes |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2017-05-31 | 2017-08-22 15:53 | 83 | 2016-11-11 16:35 | Electrical - General | 1500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | During an inspection of cabling associated with IRF 113, The CRL Electrical Field Engineer identified that the distribution board schedule for DB6/AS/W does not tie up with the __ calculations
| 03SR - Stations (RfL) | Cxxx-NCR-002402 | NCR | Doors - __ __ - checksheets |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-01-25 | 2017-02-10 16:18 | 16 | 2016-11-14 18:16 | Architectural - Doors | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The Contractor invited the Client for the inspection of KD12 doors installed (IRF issued), but the subcontractor did not have the checksheets filled in progressively. Thus, the Client was not able to witness them.
| 03SR - Stations (RfL) | Cxxx-NCR-002403 | NCR | Doors - __ __ - mastic application |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-06-30 | 2017-06-28 15:28 | -2 | 2016-11-14 18:32 | Architectural - Doors | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Design Problem - Not Defined | Completed |  | The subcontractor using PFC __ LUL Intumescent Sealant, has not been installed as per the manufacturer's instructions, i.e to back it with PFC __ C144 Firestop Strip mineral wool backer material of 30mm.
| 03SR - Stations (RfL) | Cxxx-NCR-002404 | NCR | PES III Damaged RC Slab During Breakout Works |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-01-23 | 2017-02-17 15:57 | 25 | 2016-11-15 20:26 | Civil - Structural Engineering | 100 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During breakout works to remove screeding to allow the expansion of the slab penetration for firestopping, the operatives have broken away some of the reinforced structural slab and exposed the reinforcement.
| 03SR - Stations (RfL) | Cxxx-NCR-002406 | NCR | KD12 - PES III Floor Sealer Damaged around hatch |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-02-28 | 2018-04-18 14:18 | 49 | 2016-11-17 11:56 | Architectural - Flooring | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Within the PES III room the floor sealer (__ XF895) have come away from the substrate around the perimeter of the hatch.
| 03SR - Stations (RfL) | Cxxx-NCR-002407 | NCR | Concrete making good by decorators wuith unapproved concrete repair materials |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2017-03-31 | 2017-03-22 16:13 | -9 | 2016-11-17 15:30 | Civil - Structural Engineering | 2500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During a KD12 inspection carried out on 14th November 2016 the PM and Supervisor's Representative observed decorators filling holes in the structural concrete slab with material that was described by the painter as polyfilla. The holes are blind holes for MEP installation which did not achieve the required depth due to clashing with rebar. This same methodology has been used in PES rooms on the end walls where shrinkage of the filler can be identified. The end walls of the PES is formed of waterproof concrete as it is a tunnel headwall.
| 03SR - Stations (RfL) | Cxxx-NCR-002408 | NCR | Escalator 8/9 pit (Concourse GL9) 5no. ducts cast at wrong height |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-01-25 | 2017-01-18 15:38 | -7 | 2016-11-17 18:53 | Civil - Structural Engineering | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | At concourse level GL9 escalator pit (for escalators 8/9) the spine section of RC between the two escalator trusses should have 5no. cable ducts cast into position 100mm off the floor of the pit. In this pit only, the 5no. cable ducts have been cast 520mm off the pit floor. Please see the attached drawing, and sketch to illustrate this. This is extracted from drawing Cxxx-SWN-S-DDB-M171_3-04011 rev C01 (escalator ducts cross-section)
| 03SR - Stations (RfL) | Cxxx-NCR-002409 | NCR | Wrong Fire Rated Lintel Installed Over Doorway in Room OHLE |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-01-10 | 2017-01-18 15:42 | 8 | 2016-11-17 18:53 | Architectural - Brickworks/Blockworks | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 1 hr fire rated installed above doorway in room OHLE when fire strategy report says the room is 2 hour fire rated.
| 03SR - Stations (RfL) | Cxxx-NCR-002410 | NCR | CMS Design Changes |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-05-31 | 2017-05-19 11:09 | -12 | 2016-11-23 09:29 | Electrical - Electrical Engineering General | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | KD12 - PES Room strip out, alter CMS route to provide further access provision for cabling next to __
| 03SR - Stations (RfL) | Cxxx-NCR-002411 | NCR | CMS associated with KD12 & 19 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-02-21 | 2017-02-17 15:40 | -4 | 2016-11-23 09:28 | Electrical - Electrical Engineering General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | KD12 & 19 Strip out & adjust CMS to suit revised design in accordance with January 2016 systemwide work shop.
| 03SR - Stations (RfL) | Cxxx-NCR-002412 | NCR | Unpaid lift strucutre - base plates (3No) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-05-08 | 2017-05-26 15:07 | 18 | 2016-11-18 15:01 | Civil - Civil Engineering General | 1500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Prior to installation of the Unpaid lift shaft steel works, a survey check identified an error on 3no eastern column base plates. informs that base plates (see attached photos), were modified prior to delivery to accommodate the cast in bolts. Holes in the 3nr base plates needed to be slotted. The plates were treated with primer following modification, however, the top coating was not applied.
| 03SR - Stations (RfL) | Cxxx-NCR-002413 | NCR | P Status drawings... |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-02-21 | 2017-02-17 15:46 | -4 | 2016-11-23 09:28 | Electrical - Electrical Engineering General | 2500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Rooms routes and risers have been installed to P status drawings and NOT as required by CRL Works Information ie C Status drawings in relationship to KD12, KD13, KD14, KD15, KD16, KD17, KD18 & KD19.
| 03SR - Stations (RfL) | Cxxx-NCR-002414 | NCR | Partition wall - Unpaid lift-Concrete damage |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-10-09 | 2017-10-16 09:35 | 7 | 2016-11-18 15:44 | Civil - Civil Engineering General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the installation of the unpaid lift shaft on concourse level, the concrete partition wall on the lift pit was damage, as per the attached photo (document1). New photos added (photo1 and photo2)
| 03SR - Stations (RfL) | Cxxx-NCR-002415 | NCR | SR LV 1B (#670) - CMS not installed to gated design |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2017-05-31 | 2017-08-14 07:57 | 75 | 2016-11-18 16:05 | Electrical - Switchgear | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The 2 x 1000mm cable ladders have been installed over the centre of the switch panel which does not allow for the Bus-Bar link to the LV switch Panel within SR LV 1A to terminate into the top of the switch panel. As per the gated design drawing No. Cxxx-SKC-E-DDA-M171_3-63615 rev. C01
| 03SR - Stations (RfL) | Cxxx-NCR-002416 | NCR | SR-LV 1A (#669) - LV Switch panel and lighting co-ordination |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2017-06-30 | 2017-06-02 08:19 | -28 | 2016-11-18 16:14 | Electrical - Switchgear | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The co-ordination of the lighting and the LV switch panel within the switch room is not co-ordinated and restricts maintenance access.
| 03SR - Stations (RfL) | Cxxx-NCR-002417 | NCR | LV SR - kinked cabling to light fittings |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2017-07-27 | 2017-08-10 12:53 | 14 | 2016-11-18 17:12 | Electrical - Lighting | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During an inspection of KD12 rooms, the cable between light fittings and the socket was observed to be kinked in some areas
| 03SR - Stations (RfL) | Cxxx-NCR-002418 | NCR | Survey of Winch Points for TV FAN rooms Intermediate level |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-02-21 | 2017-02-17 16:42 | -4 | 2016-11-18 18:03 | Civil - Structural Engineering | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Refer to the attached survey of the winchpoint locations in the TV FAN rooms on intermediate level. The detail for the winch points will be developed as per: Cxxx-FCD-001198 and Cxxx-FCD-001356 We would have expected to see 4no. couplers at each winch point location in the structural slab. The survey shows the points where the screed has been left out for the winch point couplers. there are some that cannot be accessed at time of survey. In some locations the screed has not been left out at the winchpoint location
| 03SR - Stations (RfL) | Cxxx-NCR-002419 | NCR | __ Access Hatches installed without MCR Code01 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-12-19 | 2016-11-25 13:32 | -24 | 2016-11-21 12:21 | Architectural - Flooring | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | __ Access Hatches installed without MCR Code01
| 03SR - Stations (RfL) | Cxxx-NCR-002420 | NCR | Bracketry on Flame shield duct bolts penetrating through the duct work |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-04-20 | 2017-04-20 15:05 | 0 | 2016-11-21 14:45 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The sub-contractor __ have installed bracketry to the Flame shield fire duct work system where the fixing bolts penetrate the fire duct work therefore possibly affecting the integrity of the duct work.
| 03SR - Stations (RfL) | Cxxx-NCR-002421 | NCR | FP200 Fire Alarm Cable |  | Contr | SKC | PAD - Paddington Station (West) |  | 2016-12-07 | 2016-12-06 17:05 | -1 | 2016-11-23 09:26 | Fire - Fire Systems & General | 5000 |  | Material | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | The of non-compliant cable FP200 GOLD raised under NCR No: Cxxx-NCR-002375 on the 22/10/2016 - __ Have failed to remove/quarantine the faulty material.
| 03SR - Stations (RfL) | Cxxx-NCR-002422 | NCR | Additional Builderswork Holes Required |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-11-22 | 2017-10-07 10:56 | -46 | 2016-11-22 14:50 | Architectural - General | 500000 |  | Design | Rework | 1 (>60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | A significant number of builderswork holes have been required post installation of the partitioning blockwork and structural concrete. This is leading to additional costs and time in having to create these openings post completion of this element.
| 03SR - Stations (RfL) | Cxxx-NCR-002423 | NCR | Concrete placement Time exceeded-concretemix 171;MCR 50255 (__F NCR 454) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-02-28 | 2017-02-02 14:51 | -391 | 2016-11-23 12:20 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | A per the attached NCR various loads either exceeded the 2hrs from batching to placement or exceeded 1 hr. between loads which does not comply with the KF11 specification
| 03SR - Stations (RfL) | Cxxx-NCR-002424 | NCR | __ Precast Low 28 day cube results P259 – Unit PC-07A (__F NCR 503) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-02-28 | 2017-02-02 14:29 | -26 | 2016-11-23 12:51 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | West Retaining Wall – Precast Unit Ref PC-07A 1. 28 day Cubes P260 failed to reach the required strength of 60N/mm2. 2. Results CUBE MIX DATE CAST 7 7 28 28 56 P-259 50/60 14/04/2016 36.9 40.4 51.0 50.5 62.9
| 03SR - Stations (RfL) | Cxxx-NCR-002426 | NCR | Unpaid lift paint missing on fin plate (top of shaft) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-04-30 | 2017-04-11 15:53 | -19 | 2016-11-23 14:53 | Architectural - Glazing | 1500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Paint on the fin plates located at the top of the shaft is missing. This is due to the fin plates being cut too wide, which was only noticed after the structure had been painted. Subsequently the edge of the fin plates had to be trimmed and coated with grey primer. See attached photo.
| 03SR - Stations (RfL) | Cxxx-NCR-002427 | NCR | Use of concrete fixings on damper benchmark without MCR approved |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-02-21 | 2017-02-20 12:40 | -1 | 2016-11-23 14:51 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Concrete fixings ( screws ) used to fix wall plates for fire dampers on benchmark installed without MCR approval.
| 03SR - Stations (RfL) | Cxxx-NCR-002428 | NCR | Brickslip Cladding - Extra acoustic holes on lower level underslung panels |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-09-25 | 2017-11-10 15:44 | 46 | 2016-11-24 08:17 | Architectural - Brickworks/Blockworks | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | A conflict in the Cxxx drawings for the lower level brickslip cladding on the north elevation below the intermediate slab has led to an extra row of acoustic holes being created in the fabrication drawings. This is not the intent shown on the drawing Cxxx-SKC-A-DDD-M171_Z-04040 (attached). The extra acoustic holes are in fact 'fake' and have concrete backing behind them, as shown in drawings such as Cxxx-SKC-Y-DDD-M171_Z-40101.
| 03SR - Stations (RfL) | Cxxx-NCR-002429 | NCR | Unauthorised attachment of scaffolding to __ cladding supports |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2017-03-03 | 2017-03-10 16:02 | 7 | 2016-11-25 13:29 | Architectural - Finishes | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During a site visit on 25.11.2016, a CRL site manager witnessed scaffolding tied back to cladding supports installed for the bronze cladding. The scaffold tubes were wedged into two supports and clipped to provide lateral restraint. The cladding system is not designed for this purpose, the restraint is not of a recognised scaffold tie detail and has an uncertain load carrying capacity in this arrangement. There is a substantial risk of damage to the permanent works.
| 03SR - Stations (RfL) | Cxxx-NCR-002431 | NCR | Brickslip Cladding - North elevation bottom fixing - halfen channel loading |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-03-08 | 2017-06-30 13:08 | 114 | 2016-11-28 09:15 | Architectural - Brickworks/Blockworks | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | The bottom fixings of the north elevation of brickslip cladding are connected to a halfen channel cast into back face of the brickslip panels. This fixing caries axial load in compression and tension (due to blast pressure loading). As __ seemingly only assure the product in tension, it seems that the fixing may have been installed outside of the manufacturer's recommendations. This is to be further investigated.
| 03SR - Stations (RfL) | Cxxx-NCR-002432 | NCR | LV Switchrooms LVIA (669), LVIB (670), LVIIA (673), LVIIB (674) - Luminaire mounting height |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2017-05-31 | 2017-07-11 12:32 | 41 | 2016-11-28 12:53 | Electrical - Lighting | 15000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | The luminaires within the Intermediate Level LV switch rooms have not been installed to the gated design drawings (shown as soffit mounted).
| 03SR - Stations (RfL) | Cxxx-NCR-002433 | NCR | Damaged blockwork departure level BOH escalator room area |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-02-13 | 2017-02-23 09:24 | 10 | 2016-11-28 13:20 | Architectural - Brickworks/Blockworks | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Damage blockwork on departures level in the escalator rooms. Blockwork repaired using mortar which isnt suitable.
| 03SR - Stations (RfL) | Cxxx-NCR-002434 | NCR | Vertical Mastic Joint Damaged and Mastic made Flush with Blockwork Face on Departure Level in the Escalator Control Room |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-01-17 | 2017-01-18 15:40 | 1 | 2016-11-28 13:42 | Architectural - Brickworks/Blockworks | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Vertical mastic damaged and needs repair work on departures level in the escalator room. The mastic was made flush eith block face when there should be a 5mm recess this needs to be redone.
| 03SR - Stations (RfL) | Cxxx-NCR-002437 | NCR | Flange connection - Unpaid lift - Installation |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-06-01 | 2017-06-30 15:31 | 29 | 2016-11-29 11:02 | Civil - Civil Engineering General | 5000 |  | Manufacturing Defect | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Following the successful installation of the 4th module of the Unpaid lift shaft it has become apparent we have minor issue with the connection to the first fix stubs. The washers for the HSFG bolts in the pipe flange style connection are sometimes not sitting flush due to the adjacent weld, photo attached. This was always a very tight fit but we think where some of the factory welds are slightly oversized it has created this problem. In addition, for these type of connections to work both mating surfaces as well as the surface under the washer and under the bolt, need to be unpainted. However the surfaces on the module side have not been masked off, photos and LEER room fix detail mark up, attached.
| 03SR - Stations (RfL) | Cxxx-NCR-002438 | NCR | Plasterboard ITP Testing Not Compliant with Spec JK10.2200 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-02-17 | 2017-07-07 13:33 | 140 | 2016-11-29 11:31 | Architectural - Walls | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The Rev17 Cxxx Spec Clause JK10.2200 requires testing to be carried out on the plasterboard. Following discussions between __ (), __ (CRL), __ (CRL) and __ (CRL) destructive testing is not preferred. As per Code 01 ITP testing will not be carried out but an IRF inspection prior and post skim will be carried out in lieu. However, this is not as per the specification.
| 03SR - Stations (RfL) | Cxxx-NCR-002439 | NCR | Aluminium Flashing - No Code 1 MCR in Place Prior to Installation |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-01-18 | 2017-01-24 14:55 | 6 | 2016-11-29 13:58 | Architectural - Finishes | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | A code 1 MCR was not in place prior to the installation of the aluminium flashings to protect the fire board protection to the blockwork wind posts.
| 03SR - Stations (RfL) | Cxxx-NCR-002440 | NCR | FAT Test Sub-Switch Panel |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-07-31 | 2018-11-14 10:46 | 106 | 2016-11-29 11:41 | Electrical - Electrical Engineering General | 1500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Sub-Switchpanels ref 1E2, 2E2, 3W2, 4W2, CRL-A & CRL-B have been delivered to site prior to witnessed FAT (Factory Acceptance Tests) tests taking place at the factory. Affected rooms = ESR I, ESR II, SR LV III A, SR LV III B
| 03SR - Stations (RfL) | Cxxx-NCR-002441 | NCR | Platfrom __ level south (CH1360.564) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-04-06 | 2017-03-16 10:53 | -21 | 2016-11-29 13:31 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | At chainage 1360.564 westbound (South platform) the top halfen channel is 18mm low (8mm out of tolerance) . Please see attachedas-built survey
| 03SR - Stations (RfL) | Cxxx-NCR-002442 | NCR | Blocked Duct in Escalator Equipment / Control Room for Esc 12 Upper Pit |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-01-31 | 2018-02-02 15:34 | 2 | 2016-11-29 16:25 | Civil - Civil Engineering General | 2500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During a recent pre-start inspection for Esc 12&13 install, it was discovered that 1no. 100mm diameter duct cast into the Concourse slab going from the upper pit of Escalator 12 to the Escalator Electrical / Control Room is blocked with concrete. This prevented the duct from having a draw rope installed and thus means that there is no passageway for future cables or suppression.
| 03SR - Stations (RfL) | Cxxx-NCR-002443 | NCR | MAP dampers installed to original MCR that showed 90minute fire rating. |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-03-01 | 2017-02-01 14:07 | -28 | 2016-12-01 14:55 | Mechanical - Heating Ventilation & Air Conditioning | 50000 |  | Documentation and Records | Rework | 2 (6-60k) | Complete | Design Problem - Other | Completed |  | MAP BSK-4 fire dampers installed in accordance with the schedules as indicated in SI 967. Dampers to be installed in the wall as per MAP BSK-4 crossrail detail to comply with EI120-S and not as per __ drawings.
| 03SR - Stations (RfL) | Cxxx-NCR-002444 | NCR | Seimens Communications Cabinets stored in MIST room with blockwork cutting activity |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-03-24 | 2017-06-07 08:44 | 75 | 2016-12-01 17:28 | Communications and Control Systems | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Blockwork Subcontractor operatives were cutting out a large builders work opening in the MIST room which had some __ Communications Cabinets (for the SCR rooms) temporarily stored inside.
| 03SR - Stations (RfL) | Cxxx-NCR-002445 | NCR | Brickslip cladding - Damage to concrete P-SW-P30 during remedial bracket installation |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-10-18 | 2017-10-20 09:54 | 2 | 2016-12-02 13:56 | Architectural - Brickworks/Blockworks | 2500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | A localised area of breaking out damage to the backing concrete of pre-cast brickslip panel no. P-SW-P30 occurred during the installation of remedial bottom fixings on South elevation. It appears that the ends of two reinforcement bars have been exposed. This is to be further investigated.
| 03SR - Stations (RfL) | Cxxx-NCR-002446 | NCR | Cable ducts from trackside to UPD in main box all 4 corners |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-05-30 | 2017-04-18 09:02 | -42 | 2016-12-02 14:36 | Electrical - Cable Management | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Cable ducts from trackside into main box upd has been installed in 80mm ducting instead of 100mm as shown on the design
| 03SR - Stations (RfL) | Cxxx-NCR-002448 | NCR | LV Distribution Boards |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-03-03 | 2017-02-21 13:06 | -10 | 2016-12-03 07:58 | Electrical - Electrical Engineering General | 5000 |  | Material | Use As-Is | 3 (3-6k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | MCR no. CRL-MCR-000148 covering the Acti-9 Isobar range of __ distribution boards has been approved with an additional comment stating that approval did not include the IP 30 range. The specification requires Distribution Boards to be IP31 rated so we believe it is for this reason the IP30 range was excluded from the approval. This exclusion has been missed and we have installed the IP30 range with a __ proprietary gland plate which when installed increases protection to IP41. The DBs installed are compliant to the specification and are approved under the LU APR.
| 03SR - Stations (RfL) | Cxxx-NCR-002449 | NCR | Cxxx Trunking allocation - General Comms |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2017-08-31 | 2017-05-18 14:04 | -105 | 2016-12-06 16:49 | Communications and Control Systems - General | 4000 |  | Design | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | The general comms provision in the multi compartment trunking is 150mm at concourse level, located in the central section of the trunking. At intermediate level it is 75mm wide located at the side of the trunking.
| 03SR - Stations (RfL) | Cxxx-NCR-002450 | NCR | Failure to comply with IRF Process |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-01-31 | 2017-02-27 15:21 | 27 | 2016-12-07 09:26 | Electrical - Electrical Engineering General | 1500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | CIR-PL VII (#78), CIR-PL IX (#79), CER IV CWU (#925) & SER CWU (#926) – Cabling installation commenced even though the CMS IRF has not been signed off.
| 03SR - Stations (RfL) | Cxxx-NCR-002451 | NCR | CSJV design not co-ordinated with C690 gateline |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2017-05-10 | 2017-05-05 08:40 | -5 | 2016-12-07 13:14 | Architectural - General | 25000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Current gateline drawings are not co-ordinated with C690. Discussions with the Design Manager have confirmed that will not update their drawings to the gateline layout produce by the Employer's Systemwide Contractor
| 03SR - Stations (RfL) | Cxxx-NCR-002452 | NCR | Brickslip Cladding - North elevation bottom fixing - Remedial works carried out without approval |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-08-29 | 2017-07-07 13:35 | -53 | 2016-12-08 12:32 | Architectural - Brickworks/Blockworks | 3000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | During inspection on site it has been noticed that remedial works as per Cxxx-NCR-002431 on the Brickslip panels, North elevation, are being carried out without approved FCD in place. Relevant documents have been issued by the sub-contracor, however these were not yet approved by the designers.
| 03SR - Stations (RfL) | Cxxx-NCR-002453 | NCR | Contractor wiring in areas where CMS has been removed |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2017-05-31 | 2017-02-17 17:01 | -103 | 2016-12-08 15:51 | Electrical - General | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Wiring has installed in an area where the CMS has been removed. This area has not been offered for up for inspection/witness.
| 03SR - Stations (RfL) | Cxxx-NCR-002454 | NCR | Fire Insulation to __ Ductwork |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2017-09-01 | 2017-08-31 09:31 | -1 | 2016-12-09 12:28 | Fire - Compartmentation | 116000 |  | Incorrect Installation | Rework | 1 (>60k) | Complete | Design Problem - Not Defined | Completed |  | The Supervisor Representative Team have been requested on two occasions to witness insulation to the __ fire Ducting. The insulation on the proposed benchmark is 45kg\m^3 and 50mm thick This does not meet the project specification
| 03SR - Stations (RfL) | Cxxx-NCR-002455 | NCR | Incorrect protection of waterproofing - West VSHH |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-07-05 | 2018-12-04 09:51 | 152 | 2016-12-09 12:44 | Civil - Civil Engineering General | 5000 |  | Damaged | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Improper protection of waterproofing on the Western end of the VSHH. Potential damage to the waterproofing. This area is going to be used and tracked over for the installation of the VSHH and will need re-checking of waterproofing once these works have been completed. It will be prudent to check both ends.
| 03SR - Stations (RfL) | Cxxx-NCR-002456 | NCR | Undesigned supports for cable management system |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2017-02-28 | 2017-02-17 17:03 | -11 | 2016-12-12 10:03 | Electrical - Cable Management | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Intermediate level CMS is supported irregularly with no accepted design for the support system. Unistut supported by unistrut on 3 levels, without direct load path
| 03SR - Stations (RfL) | Cxxx-NCR-002457 | NCR | Firestopping without design or accepted materials |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2017-07-25 | 2017-06-26 14:26 | -29 | 2016-12-12 10:12 | Fire - Compartmentation | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Refer photo attached. Damper fixed into an oversized hole. The hole is infilled with a punched sheet material similar to durasteel. There are no accepted design details for this arrangement, in particular when considering the fire compound below.
| 03SR - Stations (RfL) | Cxxx-NCR-002458 | NCR | Unaccepted unistrut attachement and unpainted cut ends |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2017-06-29 | 2017-06-30 15:34 | 1 | 2016-12-12 10:23 | Mechanical - Heating Ventilation & Air Conditioning | 1500 |  | Design | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | __ installed to support ductwork is screwed to screed with unaccepted screw detail. The ends of the unistrut are not prepared or painted with zinc rich paint
| 03SR - Stations (RfL) | Cxxx-NCR-002459 | NCR | Flame shield Duct work Take off with mez flange interference |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-03-13 | 2017-02-06 17:18 | -35 | 2016-12-13 10:40 | Mechanical - Mechanical Engineering General | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A take-off has been installed to the flame shield duct work. The take-off 'bridges' a mez flange on the main causing interference to the air flow. Also a drop rod has been ignored in front of the take-off. See attached photographs. __ to remove section of duct work, send beck to Flame shield and have replacement section remade in factory.
| 03SR - Stations (RfL) | Cxxx-NCR-002462 | NCR | ESR 1 CWU - Poor Workmanship on __ Board Installation |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-02-02 | 2017-01-17 17:04 | -16 | 2016-12-14 16:28 | Fire - Compartmentation | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following a site inspection by Crossrail inspectors, they discovered poor workmanship on the __ board installation within ESR 1 CWU.
| 03SR - Stations (RfL) | Cxxx-NCR-002463 | NCR | pipework left with open ends on all levels |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-03-16 | 2017-02-17 17:05 | -27 | 2016-12-16 14:44 | Mechanical - Piping | 2500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Various installed pipework CHW and Cast iron is left with open ends that aren't capped off- thus allowing dirt/dust to gather inside the pipework. As per WI volume 2 clauses JA6512 & JP12.3215/3216
| 03SR - Stations (RfL) | Cxxx-NCR-002464 | NCR | Holding down bolts on vent shaft head houses for cladding |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-12-13 | 2018-02-02 17:09 | 51 | 2016-12-14 12:15 | Civil - Structural Engineering | 5000 |  | Material | Rework | 3 (3-6k) | Complete | External Phenomenon - Other | Completed |  | Located in multiple locations on the vent shaft head houses are are steel holding down bolts. These bolts are to be used to fix the steelwork for the cladding of the houses. The condition of some of these bolts shows corrosion. From the MCR the bolts installed were to be galvanised and therefore should not have the level of corrosion that we have seen. It may be that the corrosion is leakage from another part such as a non-galvanised nut. All the bolts have been exposed from their protective tape, inspected and recorded. Attached is a spreadsheet showing the number of bolts with corrosion and photos. Five pairs of bolts need to be repaired.
| 03SR - Stations (RfL) | Cxxx-NCR-002465 | NCR | Wiring commenced on site in contravention of ITP hold point |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2017-04-30 | 2017-04-21 11:01 | -9 | 2016-12-14 13:36 | Electrical - LV Equipment | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Benchmark signoff/comments are not completed which is a hold point prior to cabling. Cabling observed on 12.12.2016 prior to benchmark (110V Tx & DB Benchmark - Cxxx-SKC-06-STD-B071_WS077-50054) signoff/comments completion.
| 03SR - Stations (RfL) | Cxxx-NCR-002466 | NCR | Breach of Segregation within Multi-Compartment Trunking |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2017-05-31 | 2017-04-27 14:40 | -34 | 2016-12-15 14:55 | Electrical - General | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | On a site inspection a breach has been identified in the compartments between the emergency and normal power supplies (see attached photo). has confirmed the reason for this is for the DALI control cabling to the emergency luminaires. This is considered ALARP when the final connection to the luminaires is via a __ plug and socket arrangement mounted to the trunking. Cxxx-NCR-002371 has introduced a different method of final connection to the emergency luminaires by adding a fire rated box. Therefore, the ALARP solution should now be changed as the DALI control cables can now be routed through the normal lighting compartment of the multi-compartment trunking up to the fire rated box. CRL understand there is a cost implication to re-working the already installed breached tee pieces and therefore accept this was the ALARP solution at the time. However, from this point onwards the above solution should now be adopted.
| 03SR - Stations (RfL) | Cxxx-NCR-002469 | NCR | No Shrink wrap to LV Switchgear busbar |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-03-19 | 2017-01-04 15:27 | -74 | 2016-12-19 10:12 | Electrical - LV Equipment | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Clause JY71.3201n from the Electrical Specification Volume 3 (Cxxx-SKC-E-RSP-B071_WS077-50002) calls for:- Interconnections between the busbar system and protective devices shall be carried out using adequately sized busbars covered with heat shrink insulation along their entire length. The secondary busbars procured are adequately spaced apart, (this was viewed and accepted at the FAT) and are also enclosed in their own chamber within the switchboard. Therefore, consider that the factory assembled unit is fit for purpose, and does not require the secondary bars to be shrink wrapped, as called for in the above mentioned clause. As part of the response to Cxxx-RFI-003672 and Cxxx-FCD-002148, raise this NCR.
| 03SR - Stations (RfL) | Cxxx-NCR-002470 | NCR | Drainage pipework connection to cast-in floor gullies |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-04-30 | 2018-05-14 09:52 | 14 | 2016-12-22 12:16 | Mechanical - Public Health Engineering | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | As recorded by email on 31st October 2016 (attached), the Contractor has informed CRL that floor gullies cast into the intermediate to concourse slab, cannot be connected to the drainage pipework below the slab. This is due to restricted access preventing the manal tightening of the jointing clamps. The Contractor was requested by email in investigate the availability of a push-fit transition fitting. Location: multiple. Attached is photo taken from concourse level (behind ticket machines) looking up at soffit. Impact: Potential cost and time
| 03SR - Stations (RfL) | Cxxx-NCR-002471 | NCR | Fire rated ductwork access hatch in ESR (#671) |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2017-04-28 | 2017-04-21 11:08 | -7 | 2016-12-22 14:33 | Mechanical - Mechanical Engineering General | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Access hatch for fire rated extract ductwork in ESR room is impossible to access due to multiple tiers of CMS underneath it. The access hatch is the only one in the ESR room, hence there are no accessible cleaning points for the ductwork within ESR room. Also, as per DW/144, for each change in direction of ductwork there should be an access point. The issue was raised during site walk with and recorded on CRL snag list, item #562 on 24-Nov-2016.
| 03SR - Stations (RfL) | Cxxx-NCR-002472 | NCR | No access to VCD and access hatch on EA ductwork by ATTN01/EF3/W |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2017-02-28 | 2017-02-20 11:48 | -8 | 2016-12-22 13:37 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | There is no access to the extract air ductwork VCD and access hatch; location is in the intermediate corridor outside the CERI-CWU (#923), by attenuator ATTN01/EF3/W (not yet installed). The Contractor was alerted to this issue during IRF (__-152) inspection of intermediate ductwork on 02-Dec-2016. It was also recorded on CRL's snag list, item #412 on 29-Sept-2016.
| 03SR - Stations (RfL) | Cxxx-NCR-002473 | NCR | Installation of CMS |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-03-30 | 2017-03-18 11:21 | -12 | 2016-12-22 09:15 | Mechanical - Mechanical Engineering General | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | CMS Installed on Departure Road Corridor without walls/soffit being painted.
| 03SR - Stations (RfL) | Cxxx-NCR-002474 | NCR | Protection of installed asset at Platform level |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-01-31 | 2017-01-17 17:08 | -14 | 2016-12-22 09:29 | Structural Engineering - Finishes | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Protection to Bronze Cladding between escalators 8 & 9 has become dislodged!
| 03SR - Stations (RfL) | Cxxx-NCR-002475 | NCR | Inadequate Contractor Design Assurance Process |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2017-04-16 | 2017-05-19 11:13 | 33 | 2016-12-22 13:30 | Architectural - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | The F2 design is currently checked by the F1 designer to ensure gate conditions have not been compromised during the development to F2. This is captured by the Detailed drawing comment document (DDCD). The DDCD provides traceability for the design assurance from the gated F1 design to the suppliers drawings and therefore should be a deliverable.
| 03SR - Stations (RfL) | Cxxx-NCR-002476 | NCR | Design/suitability of __ Fixings EB/WB |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-12-31 | 2017-12-12 11:29 | -19 | 2016-12-23 10:16 | Mechanical - Mechanical Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | It is confirmed that the __ calculations for fixings to the durasteel are rated to 300 degrees C rather than to the requirements of BS 476.
| 03SR - Stations (RfL) | Cxxx-NCR-002477 | NCR | CMS Installation __ Corridor GL9 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-04-04 | 2017-03-30 13:05 | -5 | 2017-01-04 08:31 | Electrical - Electrical Engineering General | 1500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | CMS Installation __ Corridor GL9 Damage to concrete soffit at __ locations after the soffit has been painted. CMS installation has proceeded before making good tp the concrete. No trade to trade handover documentation in place prior to CMS installation Note: Further investigation to be undertaken on the use of CMS Bracketry hanging off of CMS Bracketry
| 03SR - Stations (RfL) | Cxxx-NCR-002478 | NCR | SCR I Intermediate Level - Plasterboard Defect - Board peeling off Wall |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-05-24 | 2018-03-01 09:45 | -84 | 2017-08-17 12:40 | Architectural - Walls | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Plasterboard within the SCR I room has begun to peel away from the wall in a local area on the West wall. This was due to the contractor not applying the correct adhesive and without notifying .
| 03SR - Stations (RfL) | Cxxx-NCR-002479 | NCR | Additional access hatches on __ installation |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-11-30 | 2017-12-04 15:20 | 4 | 2017-01-05 09:47 | Mechanical - Mechanical Engineering General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | The __ cleaning and maintenance strategy has highlighted the need for 2 additional access doors to each of the 4 __ systems in each corner of the station.
| 03SR - Stations (RfL) | Cxxx-NCR-002480 | NCR | Bronze wall cladding first fix setting out error |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-06-01 | 2017-05-19 11:15 | -13 | 2017-01-05 15:08 | Architectural - Walls | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | First fix brackets for the bronze wall cladding on platform level (GL 17-20 south elevation) have been set out and installed incorrectly. This is down to incorrect setting out by the subcontractor. Brackets are to be removed and reinstalled in their correct positions, bolt holes to be filled (filler TBC).
| 03SR - Stations (RfL) | Cxxx-NCR-002481 | NCR | Intermediate Corridor GL 24 - 19 encroachment service removal |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-05-31 | 2017-05-19 11:18 | -12 | 2017-05-13 12:16 | Electrical - Electrical Engineering General | 500000 |  | Design | Rework | 1 (>60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | South Side of Corridor Services required for removal: - Lower level CMS - Mid Level CMS - Pipe work - Trapeze - Not all. Exact Trapezes to be agreed on site and tagged (dependent on MEWP access) North Side of Corridor Services required for removal: - Lower level CMS - Mid level CMS - Trapeze - Not all. Exact Trapezes to be agreed on site and tagged (dependent on location of RC core)
| 03SR - Stations (RfL) | Cxxx-NCR-002482 | NCR | Intermediate Corridor GL19 - 15 Encroachment - service removal |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-05-31 | 2017-05-19 11:19 | -12 | 2017-05-13 12:18 | Electrical - Electrical Engineering General | 500000 |  | Design | Rework | 1 (>60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Southside CMS to be removed as per drawing locations - Southside ductwork to be removed as per drawing locations - North side CMS to access wind post to remain. Scaffold to be utilised instead. - North side CMS outside CSR-XIV 1014 to remain until instruction from MEP team received.
| 03SR - Stations (RfL) | Cxxx-NCR-002483 | NCR | Protruding windpost baseplate through the screed |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-04-30 | 2018-03-05 09:08 | -56 | 2017-01-13 11:00 | Architectural - Masonary | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Two windpost (WP2) baseplates protruding partly out of screed located aproximately GL 6.5 GL B Concourse level.
| 03SR - Stations (RfL) | Cxxx-NCR-002484 | NCR | Intermediate Level Level Windpost Fire Proofing |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-04-12 | 2017-02-27 16:04 | -44 | 2017-01-12 14:35 | Fire - Fire Systems & General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Wind post @ GL 19 - 18 has been defaced
| 03SR - Stations (RfL) | Cxxx-NCR-002486 | NCR | No MCR for Fixings for Windpost Fire Protection |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-04-23 | 2017-02-10 16:41 | -72 | 2017-01-13 11:08 | Fire - Compartmentation | 30000 |  | Documentation and Records | Rework | 2 (6-60k) | Complete | Management Problem - Inadequate supervision | Completed |  | The fixings used within the windpost fire protection have not been MCR approved.
| 03SR - Stations (RfL) | Cxxx-NCR-002488 | NCR | Unpaid lift shaft - fin plate/CHS interface rusting |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-08-01 | 2017-08-24 14:12 | 23 | 2017-01-16 12:35 | Architectural - Glazing | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The fin plates used for the construction of the glazing clamps have been stitch welded to their respective CHS members. In areas that have not been welded, the steelwork is exposed to the elements causing it to rust.
| 03SR - Stations (RfL) | Cxxx-NCR-002490 | NCR | Design Life of Brick Slip Cladding |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2018-11-26 | 2020-04-08 14:10 | 499 | 2017-01-17 11:54 | Architectural - Finishes | 20000 |  | Design | Use As-Is | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The specification for the gated design for brick slip panels states a design life of 120 years. subcontract to Thorpe Precast appears to state 60 years.
| 03SR - Stations (RfL) | Cxxx-NCR-002491 | NCR | Intermediate Corridor GL15 - 10 Encroachment - service removal |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-05-31 | 2017-05-19 11:21 | -12 | 2017-05-13 12:19 | Electrical - General | 500000 |  | Design | Rework | 1 (>60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | South Side of Corridor Services required for removal: - Lower level CMS - Mid Level CMS - Pipe work - Trapeze - Not all. Exact Trapezes to be agreed on site and tagged (dependent on MEWP access) - Ductwork
| 03SR - Stations (RfL) | Cxxx-NCR-002492 | NCR | Intermediate Corridor GL 10 - 05 encroachment service removal |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-05-31 | 2017-05-19 11:22 | -12 | 2017-05-13 12:20 | Electrical - General | 500000 |  | Design | Rework | 1 (>60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Removal of identified MEPH Services... South Side of Corridor Services required for removal: - Lower level CMS - Mid Level CMS - Pipe work - Trapeze - Not all. Exact Trapezes to be agreed on site and tagged (dependent on MEWP access) - High Level Ductwork Services required for removal: - Lower level CMS - Mid level CMS - Trapeze - Not all. Exact Trapezes to be agreed on site and tagged (dependent on location of RC core/opening) Key Note: North side services will not be removed until instruction received from MEPH team.
| 03SR - Stations (RfL) | Cxxx-NCR-002494 | NCR | KD13 HV1 - Conduit disconnected from final location c/w cable installed |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-04-20 | 2017-04-20 16:50 | 0 | 2017-01-20 15:39 | Electrical - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | KD13 HV1 - Conduit disconnected from final location c/w cable installed. Conduit disconnected to allow the MAP Damper to be installed
| 03SR - Stations (RfL) | Cxxx-NCR-002495 | NCR | Damage to Blockwork Following Flashing Removal |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-04-23 | 2017-02-24 10:15 | -58 | 2017-01-23 10:23 | Architectural - Brickworks/Blockworks | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following the removal of the aluminium flashing protection to the windpost fire stopping within TR II, some blockwork has been damaged that will require repairing.
| 03SR - Stations (RfL) | Cxxx-NCR-002496 | NCR | DURASTEEL Accessories - Zinc Plated |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-12-07 | 2017-12-04 12:22 | -3 | 2017-01-25 16:33 | Mechanical - Mechanical Engineering General | 25000 |  | Design | Rework | 2 (6-60k) | Complete | Management Problem - Other | Completed |  | __ ductwork accessories have been installed as Zinc plated items rather than Hot Dip Galvanized finish.
| 03SR - Stations (RfL) | Cxxx-NCR-002497 | NCR | On-site Welding wire - deviates from MCR_code01 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-03-25 | 2017-02-01 14:50 | -52 | 2017-01-24 18:36 | Structural Engineering - Structural Engineering - General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | __ is carrying out on-site welding with a non-code01 material. The attached code 01 MCR, mentioned a __ SG2 wire electrode and the attached photo (Onsite wire-__), taken from the wire box used for on site welding its __. The standard designation and the classification are the same, but different trade. Our subcontractor will stop any onsite welding till we get code01 MCR or get the __ SG2.
| 03SR - Stations (RfL) | Cxxx-NCR-002498 | NCR | Incorrect Finished Concrete Level on Intermediate Support (Esc 8, 9 & 12) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-03-26 | 2017-03-24 12:10 | -2 | 2017-01-25 17:35 | Civil - Civil Engineering General | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the line & leveling process of the recent installed Esc 8, 9 & 12, it has become apparent that the finished concrete level of the intermediate supports under these escalators is currently too high. As per drawings Cxxx-SWN-S-DDB-M171_Z-04567 and Cxxx-SWN-S-DDB-M171_Z-04568, the concrete level of the supports between GL9-10 and GL14-15 should be 108.905m. Currently on site the uneven concrete surface is the following height (in certain areas) above the level 108.905m under the following escalators: a) Esc 12 intermediate support is approx. 5mm too high, Esc 9 intermediate support is approx. 8mm too high and Esc 8 intermediate support is approx. 5mm too high.
| 03SR - Stations (RfL) | Cxxx-NCR-002499 | NCR | MCR 145 (Sapphire Range of Galvanised Heavy Duty tray and ladder rack |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-06-30 | 2017-04-18 09:17 | -73 | 2017-01-26 14:01 | Electrical - Cable Management | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | CRL-MCR-%145 MCR Spwcifies the use of All the catalogue pages (of Cxxx-SKC-E-XDS-CR094-50007) indicated below refer to the Sapphire Heavy Duty series ladders (600mm and 900mm wide, 125mm deep) only. (Unclear weather this approves only the 600mm and 900mm wide 125mm deep) and not other sizes of Sapphire Heavy Duty series ladders.
| 03SR - Stations (RfL) | Cxxx-NCR-002500 | NCR | Temporary supply cabling inadequately supported (Site Wide) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-03-12 | 2017-03-10 16:05 | -2 | 2017-01-26 14:21 | Electrical - Electrical Engineering General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Temp supply cabling throughout site is not supported correctly.
| 03SR - Stations (RfL) | Cxxx-NCR-002502 | NCR | CSJV architectural and MEPH design not co-ordinated with Cxxx |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2017-08-05 | 2017-07-17 12:45 | -19 | 2017-01-30 17:22 | Architectural - Finishes | 10000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Other | Completed |  | Upon review of the architectural and MEPH designs, it is clear that the designs are not co-ordinated with Cxxx platform screen doors.
| 03SR - Stations (RfL) | Cxxx-NCR-002503 | NCR | Intermediate Corridor GL 05 - 01 encroachment service removal |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-07-31 | 2017-05-19 12:01 | -73 | 2017-02-01 09:07 | Electrical - General | 500000 |  | Design | Rework | 1 (>60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Removal of identified MEPH Services... South Side of Corridor Services required for removal: - Lower level CMS - Mid Level CMS - Pipe work - Trapeze - Not all. Exact Trapezes to be agreed on site and tagged (dependent on MEWP access) All the remedial works can be done without the removal of any CMS. But for the dampers where marked needs access. Currently most of the area between GL5-GL1 are scaffolded and can be used as access for any remedial work by painters. There are no wind posts in the corridor between GL5-GL1. But in some areas mastic touch ups require access.
| 03SR - Stations (RfL) | Cxxx-NCR-002504 | NCR | non approved material being used (Threaded Fasteners) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-05-02 | 2017-04-21 11:13 | -11 | 2017-02-01 16:42 | Mechanical - Mechanical Engineering General | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | non approved material being used (Threaded Fasteners) CRL-MC-%3392
| 03SR - Stations (RfL) | Cxxx-NCR-002505 | NCR | __ __ __ Waterproofing Damage - Canopy GL 82. |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-04-15 | 2017-02-22 14:26 | -52 | 2017-02-02 11:20 | Civil - Civil Engineering General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Having exposed __ on the north face of the __ capping beam, at GL 82, pockets of water have been identified between the membrane and the concrete.
| 03SR - Stations (RfL) | Cxxx-NCR-002506 | NCR | Unapproved drainage design and MCR running through PES-IV room |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2017-04-30 | 2017-03-22 16:21 | -39 | 2017-02-02 15:39 | Mechanical - Public Health Engineering | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | No design has been submitted for the drainage passing through the PES rooms. Also, there is no MCR in place for the connection with the slab. From ground level visual observation it appears the connection material is non 1-085; as it is not encased in cast iron (like a coupling) it cannot be covered by MCR-2919 (__ cast iron). See attached photo.
| 03SR - Stations (RfL) | Cxxx-NCR-002507 | NCR | SWA Cabling Partially installed and unprotected |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-06-02 | 2017-04-11 16:37 | -52 | 2017-02-02 15:50 | Electrical - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | SWA cabling has been partially installed with little support and no protection of remaining cable on drum /dropping from wall
| 03SR - Stations (RfL) | Cxxx-NCR-002508 | NCR | 230V MK LUDEN Style socket outlets (Safety Mechanism non functional) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-04-30 | 2018-01-20 10:57 | -100 | 2017-02-02 16:12 | Electrical - General | 2500 |  | Equipment Breakdown | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | 230v socket outlet safety mechanism non functional across percentage of site
| 03SR - Stations (RfL) | Cxxx-NCR-002509 | NCR | CER equipment cooling loads |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2017-07-13 | 2017-07-06 14:58 | -7 | 2017-02-02 17:09 | Mechanical - Heating Ventilation & Air Conditioning | 30000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The Project Manager notes that the equipment cooling loads in the 3 CER’s and other rooms have been reduced since the gated design. The changes are summarised below: CER’s • CER-I: o Gated design = 11kW o Current = 9.72kW o Reduction => 1.28kW • CER-II: o Gated design = 15kW o Current = 9.865kW o Reduction => 5.135kW • CER-IV o Gated design = 18kW o Current = 3kW o Reduction => 15kW Other Rooms: • FCR1 o Gated design = 26kW o Current = 10.5kW o Reduction => 15.5kW • SOR o Gated design = 3.27kW o Current = 2.27kW o Reduction => 1.0kW • TR1 to IV o Gated design = 24.7kW o Current = 17.5kW o Reduction => 7.2kW • SER o Gated design = 13.0kW o Current = 1.0kW o Reduction => 12.0kW References: 1. Gated loads taken from document Cxxx-SKC-M-XCL-B071_WS077-50001 Rev. 3 (30th April 2015). 2. Current loads taken from Cxxx-SKC-M-XCL-B071_WS077-50001 Rev. 6. (12th Oct 2016). Note: The current Cxxx equipment loads refer to third party information (email correspondence from __ 20/04/2016); this has not been instructed by Crossrail.
| 03SR - Stations (RfL) | Cxxx-NCR-002510 | NCR | Attenuation Tanks - Units 51, 50, 49. __ DP |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-04-16 | 2017-03-24 11:46 | -23 | 2017-02-03 16:35 | Civil - Civil Engineering General | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Attenuation Tanks, Units 51, 50 & 49 arrived on site 23/01/2017, without any __ DP applied to the base of the Tanks. Repair works have been carried out by __, however their installation ITP does not account for apply __ on site. This activity is covered within __'s Fabrication ITP.
| 03SR - Stations (RfL) | Cxxx-NCR-002511 | NCR | Missing drop rod for CMS support in front of ventilation take-off |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-08-31 | 2017-02-27 16:15 | -185 | 2017-02-06 09:38 | Mechanical - Mechanical Engineering General | 1500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Support drop rod missing from CMS. when loaded with cables, CMS will lag due to being unsupported. Also in front of ductwork take-off
| 03SR - Stations (RfL) | Cxxx-NCR-002512 | NCR | Inadequate design co-ordination with Cxxx for PSD cabinets |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2017-04-30 | 2017-04-27 14:41 | -3 | 2017-02-07 16:48 | Systems - Other | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The Contractor has designed the PSD cabinets without taking into account the dimensional requirements of Cxxx. The dimensional requirements for the cabinets is shown on Cxxx--E-XSK-CR001-50001 included in the instructed RIR Cxxx--A-LRG-CR001-50001.
| 03SR - Stations (RfL) | Cxxx-NCR-002513 | NCR | Use of contrasting floor tiles at platform edge |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2017-07-14 | 2017-07-14 15:06 | 0 | 2017-02-07 16:55 | Architectural - Finishes | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The platform edge has been designed with a contrasting tile pattern. This is not in accordance with the works information and should be removed from the drawings
| 03SR - Stations (RfL) | Cxxx-NCR-002514 | NCR | Damage to Blockwork Located GL 5-6 Concourse Level |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-04-09 | 2017-02-23 09:26 | -45 | 2017-02-08 17:30 | Architectural - Brickworks/Blockworks | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Hairline crack in the mortar join on Concourse GL 5-6. The blockwork around the combined riser. Hairline crack extending approximately 1m metre across 3 blocks. Hairline mortar crack shallow in block .
| 03SR - Stations (RfL) | Cxxx-NCR-002515 | NCR | Ductwork Installation – Inadequate access for firestopping |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-12-31 | 2017-05-19 13:05 | -226 | 2017-02-09 11:14 | Mechanical - Mechanical Engineering General | 15000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Issue 1. Hole sizes in both blockwork and RC walls leave insufficient gap around ductwork after installation through the opening for firestopping. Issue 2. Installation of adjacent sections of ductwork after the section of ductwork has been installed in the wall opening prevents access by the firestopping contractor to install their works. Works have proceeded without checking if there is adequate access for firestopping. This is a check item on Ductwork Installation Checksheet- Inspection Form 027a-16 incorporated in the ITP for Installation of Air Supply and Extract systems, Document Ref: Cxxx-SKC-M-ITP-B071_WS077-50007 Check Item: Is there adequate access for firestopping?
| 03SR - Stations (RfL) | Cxxx-NCR-002516 | NCR | Vertical splices - Unpaid lift - Additional bolts |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-05-10 | 2017-04-21 11:19 | -19 | 2017-02-09 18:36 | Civil - Civil Engineering General | 2500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | __ welder coordinator, advises that the on-site FSBW on the vertical connection will not be achievable due the existence of the spigot that might contaminate the weld. Attached is a brief of the scope of works that __ is proposing.
| 03SR - Stations (RfL) | Cxxx-NCR-002517 | NCR | Unpaid lift - Fin plate gap at joints |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-05-10 | 2017-03-31 14:54 | -40 | 2017-02-09 18:50 | Civil - Civil Engineering General | 2500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Due to site access and structure buildability it has become necessary to cut 100 mm of the fin plate, that will support the glazed panels.
| 03SR - Stations (RfL) | Cxxx-NCR-002518 | NCR | Unpaid lift - Missing fin rear plates (2No) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-05-10 | 2017-03-31 13:57 | -40 | 2017-02-09 18:56 | Civil - Civil Engineering General | 1500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | /__ informs that 2No fin plates were not welded during the manufacture. Manufacture defect that need to be captured and resolved with a onsite weld. Drawing and scope of works attached.
| 03SR - Stations (RfL) | Cxxx-NCR-002519 | NCR | Incorrect Density Mineral Wool Installed within __ Board Installations |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-05-21 | 2017-05-09 16:07 | -12 | 2017-02-10 13:49 | Fire - Compartmentation | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | It has been discovered by that an incorrect density mineral wool has been installed within __ board systems on site. 100kg/m3 density mineral wool has been installed where 140kg/m3 density mineral wool is required. This NCR affects 120 minute partitions only as 100kg/m3 density mineral wool satisfies the insulation requirements for 60 minutes as confirmed by __ Thermal Ltd. (see attached email).
| 03SR - Stations (RfL) | Cxxx-NCR-002531 | NCR | Unpaid Lift Paint Defects 2 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-05-11 | 2017-03-31 13:53 | -41 | 2017-02-10 16:09 | Architectural - Finishes | 2500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | There are a number of areas of damage sustained during installation/construction of the unpaid lift.
| 03SR - Stations (RfL) | Cxxx-NCR-002532 | NCR | Unpaid Lift Missing Threshold Plates |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-05-11 | 2017-06-23 15:05 | 43 | 2017-02-10 16:20 | Architectural - General | 1500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | 3 No. Threshold plates are missing off of the unpaid lift structure. These could not be factory welded because their inclusion would hamper access to the steel members behind resulting in it being impossible to butt weld them together after installation.
| 03SR - Stations (RfL) | Cxxx-NCR-002533 | NCR | Unpaid Lift Missing fin plates rear of structure |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-05-11 | 2017-03-31 13:59 | -41 | 2017-02-10 16:25 | Architectural - General | 1500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 2 No. Finplates to the rear of the structure were missing due to a design error.
| 03SR - Stations (RfL) | Cxxx-NCR-002535 | NCR | Working to P status drawings (Intermediate level - Fiber Backbone Route 30m Section) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-10-31 | 2017-04-21 13:28 | -193 | 2017-02-13 10:40 | Electrical - Electrical Engineering General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Fiber Back Bone CMS route changed due to design review between grid line 23 and 19 (30m section).
| 03SR - Stations (RfL) | Cxxx-NCR-002536 | NCR | ERC Enclosure - No F2 Design in Place and No Code 1 MCR for Mineral Wool |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-04-14 | 2017-03-20 12:28 | -25 | 2017-02-13 11:12 | Fire - Compartmentation | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Construction on the ERC enclosures on platform level commenced without F2 assured design or a code 1 MCR for the mineral wool. The mineral wool aspect of this NCR relates to Cxxx-NCR-002519.
| 03SR - Stations (RfL) | Cxxx-NCR-002537 | NCR | Damage to Concrete Upstand of Escalator Pit Departures Road Level (Esc 3-5) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-06-01 | 2017-04-04 14:39 | -58 | 2017-02-28 12:31 | Civil - Structural Engineering | 1500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During an inspection of the Escalator 3-5 pit at Departures Road Level it was observed that the concrete upstand at the rear of the escalator pit was damaged with a section of concrete removed on the Northern end of the upstand. As a result the design profile has not been met and the cover to steel reinforcement is potentially compromised. The damage sustained to the concrete has not exposed any steel reinforcement and is not located in the direct vacinity where Escalator 3-5 supports rest.
| 03SR - Stations (RfL) | Cxxx-NCR-002538 | NCR | Centreline of Escalator out of Tolerance (Esc 13) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-10-31 | 2017-04-04 15:39 | -210 | 2017-02-16 15:30 | Mechanical - Escalators | 2500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During IRF1946 it was observed that lower curve of Escalator 13 was out of alignment by 4 mm to the approved datum centreline. Given the alignment tolerance for the escalator is 1 mm this constitutes a failure for the inspection of this escalator under Specification for Heavy Duty Metro Escalators SPC-LAE-301941170 (Rev7) as referenced in Cxxx-SKC-M1-ITP-B071_WS077-50004. Note that this inspection was checked prior to offering to CRL by the __ independent tester (__) and Escalator Accredited Inspector (Ray Wall) on 09/02/2017. On conclusion of the inspection it was found that all items met the parameters of the specification, this initiated the process of raising the inspection under IRF1946.
| 03SR - Stations (RfL) | Cxxx-NCR-002539 | NCR | VSHH: Steel Clash with HD Bolts |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-05-17 | 2017-05-06 10:04 | -11 | 2017-02-16 12:03 | Structural Engineering - Steel Member | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The have become aware that the steel columns for the chiller end of the east vent shaft head house, currently have a clash between the HD bolts and the base plates of the steel columns. The bolts are currently at 340mm centres and the base plates at 250mm centres.
| 03SR - Stations (RfL) | Cxxx-NCR-002541 | NCR | Fixing bolts within trunking joints protrude into trunking. |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-06-30 | 2017-03-18 11:29 | -104 | 2017-03-04 13:17 | Electrical - General | 10000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Electric specification (Cxxx-SKC-E-RSP-B071_WS077-50002 rev 2.0) clause JY60.1306 (v) states: “Maintain electrical continuity at each joint by a copper link, this can be achieved via an external mounted earth link or an integrated earth link on the trunking coupling system. Screws must not project through the nut. Make provision for continuity to be achieved without need to remove paint from ferrous metal where trunking has a painted finish.
| 03SR - Stations (RfL) | Cxxx-NCR-002542 | NCR | Brickslip - Cavity Drainage North wall |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-06-30 | 2017-06-30 14:26 | 0 | 2017-02-20 08:00 | Civil - Drainage | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During Installation of the brickslip cavity drainage underneath the Northern brickslip, the installation does not comply with; - Workmanship and finishing specifications. (very poor finishing) - Straigth edge dimensional tolerances in certain locations.
| 03SR - Stations (RfL) | Cxxx-NCR-002543 | NCR | VSHH - Drilling Through South East Service Corridor Roof Slab |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-05-21 | 2017-05-26 11:55 | 5 | 2017-02-20 16:37 | Structural Engineering - Concrete Member | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | This NCR relates to the installation of the HD bolts of the permanent shoe for column C19 on the South of the East VSHH. The embedment depth of the anchors was specified as 180mm (into the 200mm thick roof slab). During the installation of 2No. of these anchors the bottom 20mm of the slab has spoiled off, see attached photograph.
| 03SR - Stations (RfL) | Cxxx-NCR-002545 | NCR | Windpost Ties Missing at Top Course of Blocks at GL 10.5 Intermediate Level |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-05-12 | 2017-05-12 12:43 | 0 | 2017-02-21 16:12 | Architectural - Brickworks/Blockworks | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Windpost ties missing or snapped on the top courses of blockwork at GL10.5 Intermediate Level.
| 03SR - Stations (RfL) | Cxxx-NCR-002546 | NCR | CE Marking for Armoduct CMS |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-03-25 | 2017-03-17 15:48 | -8 | 2017-02-23 13:24 | Electrical - General | 50000 |  | Documentation and Records | Use As-Is | 2 (6-60k) | Complete | Material/Preservation Problems - Other | Completed |  | Confirm all products provided by Armoduct are compliant with the requirements of 305/2011
| 03SR - Stations (RfL) | Cxxx-NCR-002547 | NCR | Unpaid Lift Painting Surface Profile Roughness Exceeded |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-05-24 | 2017-03-02 17:22 | -83 | 2017-02-23 16:24 | Architectural - Finishes | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | With referance to the onsite painting ITP Cxxx-SKC-C-ITP-B071_WS077-50150, item 4.4, the first weld area to be painted achieved a surface profile of 150 microns. This exceeds the 70-100 microns range specified in the ITP.
| 03SR - Stations (RfL) | Cxxx-NCR-002548 | NCR | Conduit accessories CE marked to the incorrect standard |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2017-05-26 | 2017-05-26 15:26 | 0 | 2017-02-23 16:33 | Electrical - Cable Management | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | A quality surveillance was undertaken at Cxxx Paddington Station to review the materials compliance process for Mechanical, Electrical and Public Health (MEP) systems. Conduit accessories (terminal boxes) were located in the electrical storeroom, 10 per box. The boxes were CE marked to BS EN 50086. Following post surveillance review it was noted that this standard had been superseded by BS EN 61386 which came into effect in 2004. The M&W Specification JY60 Conduit & Cable Trunking also states “provide conduit systems to BS EN 61386”. The Barton UK product catalogue also stated that the terminal boxes were produced to BS EN 50086.
| 03SR - Stations (RfL) | Cxxx-NCR-002549 | NCR | Windpost Fire Protection - Indentation Caused by Fixing Installation |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-03-10 | 2017-03-01 11:42 | -9 | 2017-02-24 12:19 | Fire - Compartmentation | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | It has been identified that there has been some minor indentation to the windpost fire protection that has been caused during the fixings installation. The manufacturer of the board is to be consulted to see whether this jeopardises the firestopping capabilities of the installation.
| 03SR - Stations (RfL) | Cxxx-NCR-002551 | NCR | Thread damage to canopy holding down bolts |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-11-14 | 2017-11-24 17:02 | 10 | 2017-02-24 14:40 | Structural Engineering - Structural Engineering - General | 1500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | There is damage to some of the upper threads on the pre-installed canopy holding down bolts (South). These bolts are in the process of being cleaned and inspected following a long period of being covered.
| 03SR - Stations (RfL) | Cxxx-NCR-002552 | NCR | VSHH - Paint Finish to Steelwork |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-04-11 | 2017-04-04 14:32 | -372 | 2017-02-24 15:49 | Architectural - Finishes | 15000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | In some locations the finish to the paint works for the VSHH steel is not as per the approved mock up. In particular relating to the slight indentations around the bolts locations. Other small areas have small amouts of damage and scuff marks from lifting and transportation.
| 03SR - Stations (RfL) | Cxxx-NCR-002553 | NCR | Waterproofing to E__ slab GL17 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-06-01 | 2019-01-24 09:34 | 237 | 2017-02-27 13:11 | Civil - Civil Engineering General | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Waterproofing to E__ slab was applied but not protected in the temporary state or in the permanent (I.e protection screed) as such the area have been used as lay down area for materials potentially damaging the permanent waterproofing layer
| 03SR - Stations (RfL) | Cxxx-NCR-002554 | NCR | SR LV 11B Light Fittings - additional drilled holes |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-05-29 | 2017-08-14 08:51 | 77 | 2017-02-28 09:58 | Electrical - General | 25000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | Additional holes in SR LV 11B Light housing, potential contravention of manufactures gaurantee.
| 03SR - Stations (RfL) | Cxxx-NCR-002555 | NCR | Holes Created in Mortar Joint for Fireproof Protection and Temporary Cable Installation |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-08-31 | 2019-07-26 13:21 | 329 | 2017-02-28 11:43 | Architectural - Brickworks/Blockworks | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Holes created in the mortar joint so temporary protection for the suplex board can be installed. Further to this the holes are also created for feeding temporary lighting. This is located on all windposts concourse and intermediate level.
| 03SR - Stations (RfL) | Cxxx-NCR-002556 | NCR | Precast Canopy Foundation (UPR-CP2-02) - Bolts cast out of tolerance |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-03-28 | 2017-03-27 14:43 | -1 | 2017-02-28 16:37 | Structural Engineering - Bolted Connections | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The 4no 48mm diameter bolts cast into the Precast Canopy Foundation, UPR-CP2-02, are out of tolerance. Specification Cxxx-SKC-S-RSP-B071-WS077-50004, clause KH10 – B2 states "Position of each dowel bar at 123.375m: ± 3mm combined total in all directions." check this combined tolerance with a template of the canopy baseplate, which has 51mm diameter holes. If the template fits, the centre point of this bolt cluster is then set out to within +/- 3mm. The canopy column baseplate has 4no. 60mm diameter holes at centres of 243mm apart, that fit on a 343mm diameter circle. This is as shown on drawing Cxxx-SKC-Y-DDD-M171_1-50013 and as confirmed in -RFI-001965. The cast in bolts on UPR-CP2-02 are spaced at centres as per the marked up drawing. Bolts spaced at 237mm and 239mm are out of tolerance however will fit into a baseplate with 60mm holes. proposed to use this item at GL 70. Please confirm this proposal is acceptable, and what is required to close out this NCR. An FCD can be raised to record this change?
| 03SR - Stations (RfL) | Cxxx-NCR-002557 | NCR | VSHH: Steel installation without below ground corrosion protection |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-06-15 | 2017-04-19 16:26 | -57 | 2017-03-01 18:26 | Structural Engineering - Surface Treatment | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | On GL E6 of the East VSHH, 2No. columns and 2No. permanent shoes were installed without the application of the below ground corrosion protection.
| 03SR - Stations (RfL) | Cxxx-NCR-002558 | NCR | Attenuation Tanks - Grade of SS dowel bar |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-03-30 | 2017-03-09 17:26 | -21 | 2017-03-02 11:28 | Structural Engineering - Reinforcement | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Following a surveillance on the materials delivered against the approved MCRs for attenuation tank and canopy foundation works, carried out by the site team, It was identified the stainless steel dowel bar supplied was a different grade to the approved MCR. This material is grouted in between the Lid and U-section connection. MCR number: Cxxx-SKC-O-TSC-B071_WS077-50949 Page 7 of the MCR highlights Grade “1.4301 (304)”, however the delivery ticket shows grade “1.4362” Comparing the suitability of the two materials with the supplier, the delivered material is of a higher grade material. The materials have already been installed and propose to use the material as is. Please confirm what is required to close this NCR. suggest an FCD to record the location of the material. See attachments: MCR = Cxxx-SKC-O-TSC-B071_WS077-50949 Rebar Dowel.pdf Email from __ Supplier.pdf __ POD - Rebar Dowel Delivery ticket.pdf Surveillance report = Cxxx-SKC-O4-RGN-B071-WS077-50109 Unsigned.pdf
| 03SR - Stations (RfL) | Cxxx-NCR-002559 | NCR | Corbel Cavity Drainage Chanel - SS Retention angel not installed as per drawing |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-08-09 | 2017-10-13 15:00 | 65 | 2017-03-02 11:10 | Civil - Drainage | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | As per drawing detail Cxxx-SKC-A-DDD-M171_Z-04041 section 04 details a retention angel for the cavity drainage chanel. This is not installed on site.
| 03SR - Stations (RfL) | Cxxx-NCR-002560 | NCR | SCR I Staff Room - Finished Vinyl Stained by Stagnant fluid |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-05-31 | 2019-03-12 14:58 | 285 | 2017-03-02 11:57 | Architectural - Flooring | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Within the SCR I room a contractor has carried out works leading to a mix of water and, what is believed to be, the residue from grinding off the adhesive dabs of the plasterboard, sitting on the Vinyl. This has led to staining which looks like discolouration of the Vinyl. UPDATE 02/02/18 Realise close out date applied (31/05/2018). Vinyl to be changed.
| 03SR - Stations (RfL) | Cxxx-NCR-002561 | NCR | Bakerloo Box – __ HUS-HF Fixing Type and length – SI 1203 (Bakerloo Box - GL 12) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-12-22 | 2017-11-06 11:13 | -46 | 2017-03-09 13:54 | Electrical - Electrical Engineering General | 2500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Installation of Unistut Channel to the soffit of the Bakerloo slab has proceeded using 70mm and 60mm __ HUS3 H10 type fixings contrary to SI 1203 which states: The Subcontractor is to use either fixing 100mm HUS-HF and maintain a maximum spacing of 1m between each header or if the Subcontractor finds that there is insufficient concrete cover to use a 100mm fixing the Contractor will approve the use of 75mm length HUS-HF fixings where necessary. The Subcontractor has since notified the Contractor via Aconex __-GC-007021 regarding previous correspondences for intermediate level for use of HUS-H fixings and requesting acceptance of shorter 65mm fixings. This fixing type reference and length also appears to be different to the fixings being installed.
| 03SR - Stations (RfL) | Cxxx-NCR-002562 | NCR | Pipe sleeves left unpainted at cut ends |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-05-31 | 2017-05-19 13:09 | -12 | 2017-03-02 15:31 | Mechanical - Piping | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Various locations along intermediate level at both east and west ends where pipe sleeves have been installed through block work where pipe sleeves have been cut to size from plain lengths the cut end has not been painted with protective primer ( red oxide)
| 03SR - Stations (RfL) | Cxxx-NCR-002564 | NCR | VSHH: Clash between Temporary and Permanent Works |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-12-28 | 2018-02-02 17:11 | 36 | 2017-03-03 14:50 | Structural Engineering - Bracing | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | On the East & West VSHH there is a clash between the secondary steel work and temporary access deck above the void between GL 20 and GL23. The proposed construction sequence is to install the primary structural steel and majority of secondary steelwork, leaving out the beams which clash. Once the majority of steel work is installed, the access deck will be removed and reinstalled at a higher level. The lower level beams will then be installed. However in 2 No. locations the lower beam that clashes is welded to other secondary steelwork with a 6mm fillet weld, this weld will have to be cut through inorder to install the steelwork. Sketch of beam to be cut attached to NCR - Note beam to be cut in following location; GL E5-E6 North and South, GL W5-W6 North and South
| 03SR - Stations (RfL) | Cxxx-NCR-002565 | NCR | Unpaid lift shaft - Paint Defects 3 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-06-04 | 2017-03-31 13:52 | -65 | 2017-03-06 15:15 | Architectural - Finishes | 2500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | General paint defects identified on the Unpaid lift shaft structure - lift 6/7 and as per the attached report/locations/scope of works
| 03SR - Stations (RfL) | Cxxx-NCR-002567 | NCR | Unpaid Lift Damages To Fin Plate |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-06-04 | 2017-03-30 13:12 | -66 | 2017-03-06 16:49 | Architectural - Finishes | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Grinding blade damage was sustained to the fin plate next to weld No. 9 whilst a section of fin plate was removed.
| 03SR - Stations (RfL) | Cxxx-NCR-002568 | NCR | BLL 12 Potential Non-Compliant Welds |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-06-04 | 2017-03-27 15:58 | -69 | 2017-03-06 16:57 | Architectural - General | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | In various locations on the structure on the Bakerloo Lift No.12 there is a concern that the welds are not full strength butt welds due to the appearance of the welds.
| 03SR - Stations (RfL) | Cxxx-NCR-002570 | NCR | BLL 12 Paint Defect 1 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-07-27 | 2017-07-28 11:52 | 1 | 2017-03-06 17:01 | Architectural - Finishes | 1500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | On the Bakerloo Lift No. 12 there is a red stain to a location on the structure/
| 03SR - Stations (RfL) | Cxxx-NCR-002571 | NCR | BLL 12 - Paint defects 2 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-07-27 | 2017-07-28 11:55 | 1 | 2017-03-07 12:18 | Architectural - Finishes | 1500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Spotted paint defects along the No3 structural modules, as per the attached report with Key Plan/Photos/Scope of works.
| 03SR - Stations (RfL) | Cxxx-NCR-002572 | NCR | Cables being stored in the wrong place. |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-06-06 | 2017-03-24 12:16 | -74 | 2017-03-08 12:14 | Electrical - Electrical Engineering General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | It has been observed in __ stores that cables are being stored in the wrong areas. __ L.SIFER (FT L-SIFER Fire Resistant Cable) is being stored with the __ SAFFIRE (OHLS Power Cables (Non Fire Survivable Loads)).
| 03SR - Stations (RfL) | Cxxx-NCR-002573 | NCR | Unapproved MCR luminaire within site stores |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-07-06 | 2017-08-14 08:00 | 39 | 2017-03-08 12:30 | Electrical - Electrical Engineering General | 2500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | A Bega 66714 luminaire has been observed within the __ site storage area, which does not have an approved MCR. (See attached photo).
| 03SR - Stations (RfL) | Cxxx-NCR-002574 | NCR | Unapproved MCR luminaire within transit to site stores |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-09-04 | 2017-09-07 07:55 | 3 | 2017-03-08 14:57 | Electrical - Electrical Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | A WE-EF (manufacturer) 195-9525 luminaire has been observed on a pallet presumably in transit to the __ site storage area, which does not have an approved MCR. (See attached photo).
| 03SR - Stations (RfL) | Cxxx-NCR-002575 | NCR | Unpaid Lift Fin Plate Bent |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-06-06 | 2017-06-01 16:08 | -5 | 2017-03-08 15:42 | Architectural - Finishes | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | As can be seen from the attached photo, damage was sustained to the a fin plate which is used to clamp the anti-bird glazing panels.
| 03SR - Stations (RfL) | Cxxx-NCR-002577 | NCR | Brickslip - Marking / Staining / water to Lower northern panel |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-07-01 | 2017-06-30 13:22 | -1 | 2017-03-08 17:39 | Architectural - Brickworks/Blockworks | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | It has been noted some dirty / stained water running down the face of the bottom brickslip panel, on the Northern side of the lightwell. (see photos attached). The water has left a dry stain mark over the brickslip, which can be cleaned off. It appears the water has run through the joint between the upper precast panel and lower precast panel and spilled through the upper acoustic holes.
| 03SR - Stations (RfL) | Cxxx-NCR-002580 | NCR | __ Lateral Support brackets (restraints). lack of MCR. |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-09-30 | 2017-09-15 08:23 | -15 | 2017-09-05 15:13 | Mechanical - Mechanical Engineering General | 20000 |  | Design | Rework | 2 (6-60k) | Complete | Management Problem - Inadequate supervision | Completed |  | No MCR for Lateral Restraint Brackets
| 03SR - Stations (RfL) | Cxxx-NCR-002581 | NCR | __ Lateral Support brackets (restraints). lack of MCR. |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-02-28 | 2017-11-06 11:14 | -114 | 2017-09-19 11:32 | Mechanical - Mechanical Engineering General | 25000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | __ Lateral (restraints) support brackets have been fabricated and installed without and accepted MCR being in place.
| 03SR - Stations (RfL) | Cxxx-NCR-002582 | NCR | Construction of bronze cladding on platform level columns to P status drawings |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-10-25 | 2017-10-20 09:57 | -5 | 2017-03-15 11:03 | Architectural - Finishes | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Due to project requirements and the urgent requirement to install the bronze cladding to columns prior to escalator installs, the bronze cladding for the columns have been constructed to P status drawings in advance of them going through the gate impact assessment and being issued for construction.
| 03SR - Stations (RfL) | Cxxx-NCR-002583 | NCR | __ __ __ Waterproofing Damage - Canopy GLs 72-66 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-04-15 | 2017-03-22 14:55 | -24 | 2017-03-15 17:52 | Civil - Civil Engineering General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | As per Cxxx-NCR-002505, having exposed __ on the north face of the __ capping beam, between GLs 72-66, pockets of water and de-bonded sections of the __ have been identified at the interface between the membrane and the concrete.
| 03SR - Stations (RfL) | Cxxx-NCR-002585 | NCR | Brickslip Corbel - low 28 day strength cube result |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-05-16 | 2017-07-17 10:18 | 62 | 2017-03-17 14:56 | Civil - Civil Engineering General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | For the Brickslip corbel works - a 28 day cube result returned a result less than the specification of 50N/mm2. Location : Top Corbel Left Ticket : 122344 Request sheet number : S1644559_M1 Lab Ref : 24138390 Result 43.7N/mm2
| 03SR - Stations (RfL) | Cxxx-NCR-002586 | NCR | Attenuation tank lid UNIT-L18 - Rebar dowel openings |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-04-06 | 2017-04-05 08:51 | -1 | 2017-03-23 17:09 | Structural Engineering - Structural Engineering - General | 1000 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Attenuation tank lid UNIT-L18, as shown within drawings Cxxx-SKC-D-DWG-B071_WS077-50012 and Cxxx-SKC-D-DWG-B071_WS077-50029 (Type B), has been cast with the rebar dowel openings in the wrong position. As shown within the attached images, the dowel bar openings have been cast along the East and West edges of the lid unit rather than the North and South edges of the unit.
| 03SR - Stations (RfL) | Cxxx-NCR-002587 | NCR | Inadequate design interfacing with systemwide contractors |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2017-10-13 | 2017-08-16 14:11 | -58 | 2017-03-25 14:47 | Architectural - Finishes | 10000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The contract requires to interface with systemwide contractors. Recent RFI requests to the PM's team demonstrates that the and their designer is not adequately interfacing and instead, attempting to get the PM's team to take on the interface management. This ultimately leads to confusion and potential delays
| 03SR - Stations (RfL) | Cxxx-NCR-002589 | NCR | LOIS List Items for Escalator 6 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-06-30 | 2018-08-20 16:07 | 51 | 2017-03-31 11:00 | Mechanical - Escalators | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Prior to shipping the escalator from the __ factory, remedial items that had not been closed in the factory were identified on a Rev 1 - List of Outstanding Items Schedule (LOIS). These items where spotted during the quality inspection of each escalator by accredited __, & CRL inspectors in line with the __ Escalators Factory ITP (Cxxx-SKC-M1-ITP-B071_WS077-50005). Items identified on this LOIS list need to be closed out / actioned on site prior to handover to the Client from the Tier 1 contractor. Upon inspection of the escalator trusses that have recently been delivered to site, it has been identified that there have been items damaged possibly during transit from the __ factory to the UK. These have only been discovered once the escalator shrink wrap protection was removed on site. New items such as these identified on site will be captured on new updated revisions of the LOIS list. In agreement with the CRL (__) and CEG (__), an NCR will be raised for each escalator at Paddington Cxxx and the defective items on the escalator or associated escalator control room will be captured on the updated revisions of the LOIS lists which will have a trackable document number. Note that any NCRs relating to workmanship, installation error, etc. shall be raised and tracked by a separate NCR. This LOIS list for Escalator 6 is captured on document (Cxxx-SKC-M1-LST-B071_WS077-50006) on eB.
| 03SR - Stations (RfL) | Cxxx-NCR-002590 | NCR | Staining of Blockwork Wall Intermediate West Riser & Repair of __ |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-09-22 | 2017-11-10 11:23 | 49 | 2017-03-28 15:46 | Architectural - Brickworks/Blockworks | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Water ingress through the Riser has passed through the horizontal corofil causing the water to change colour and stain the blockwork. corofil damaged in thi process
| 03SR - Stations (RfL) | Cxxx-NCR-002592 | NCR | LOIS List Items for Escalator 7 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-06-30 | 2018-11-12 11:40 | 135 | 2017-03-31 11:09 | Mechanical - Escalators | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Prior to shipping the escalator from the __ factory, remedial items that had not been closed in the factory were identified on a Rev 1 - List of Outstanding Items Schedule (LOIS). These items where spotted during the quality inspection of each escalator by accredited __, & CRL inspectors in line with the __ Escalators Factory ITP (Cxxx-SKC-M1-ITP-B071_WS077-50005). Items identified on this LOIS list need to be closed out / actioned on site prior to handover to the Client from the Tier 1 contractor. Upon inspection of the escalator trusses that have recently been delivered to site, it has been identified that there have been items damaged possibly during transit from the __ factory to the UK. These have only been discovered once the escalator shrink wrap protection was removed on site. New items such as these identified on site will be captured on new updated revisions of the LOIS list. In agreement with the CRL (__) and CEG (__), an NCR will be raised for each escalator at Paddington Cxxx and the defective items on the escalator or associated escalator control room will be captured on the updated revisions of the LOIS lists which will have a trackable document number. Note that any NCRs relating to workmanship, installation error, etc. shall be raised and tracked by a separate NCR. This LOIS list for Escalator 7 is captured on document (Cxxx-SKC-M1-LST-B071_WS077-50007) on eB.
| 03SR - Stations (RfL) | Cxxx-NCR-002593 | NCR | LOIS List Items for Escalator 8 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-06-30 | 2019-03-15 14:01 | 258 | 2017-03-31 11:40 | Mechanical - Escalators | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Prior to shipping the escalator from the __ factory, remedial items that had not been closed in the factory were identified on a Rev 1 - List of Outstanding Items Schedule (LOIS). These items where spotted during the quality inspection of each escalator by accredited __, & CRL inspectors in line with the __ Escalators Factory ITP (Cxxx-SKC-M1-ITP-B071_WS077-50005). Items identified on this LOIS list need to be closed out / actioned on site prior to handover to the Client from the Tier 1 contractor. Upon inspection of the escalator trusses that have recently been delivered to site, it has been identified that there have been items damaged possibly during transit from the __ factory to the UK. These have only been discovered once the escalator shrink wrap protection was removed on site. New items such as these identified on site will be captured on new updated revisions of the LOIS list. In agreement with the CRL (__) and CEG (__), an NCR will be raised for each escalator at Paddington Cxxx and the defective items on the escalator or associated escalator control room will be captured on the updated revisions of the LOIS lists which will have a trackable document number. Note that any NCRs relating to workmanship, installation error, etc. shall be raised and tracked by a separate NCR. This LOIS list for Escalator 8 is captured on document (Cxxx-SKC-M1-LST-B071_WS077-50008) on eB.
| 03SR - Stations (RfL) | Cxxx-NCR-002594 | NCR | LOIS List Items for Escalator 9 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-06-30 | 2019-03-16 11:35 | 259 | 2017-03-31 11:43 | Mechanical - Escalators | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Prior to shipping the escalator from the __ factory, remedial items that had not been closed in the factory were identified on a Rev 1 - List of Outstanding Items Schedule (LOIS). These items where spotted during the quality inspection of each escalator by accredited __, & CRL inspectors in line with the __ Escalators Factory ITP (Cxxx-SKC-M1-ITP-B071_WS077-50005). Items identified on this LOIS list need to be closed out / actioned on site prior to handover to the Client from the Tier 1 contractor. Upon inspection of the escalator trusses that have recently been delivered to site, it has been identified that there have been items damaged possibly during transit from the __ factory to the UK. These have only been discovered once the escalator shrink wrap protection was removed on site. New items such as these identified on site will be captured on new updated revisions of the LOIS list. In agreement with the CRL (__) and CEG (__), an NCR will be raised for each escalator at Paddington Cxxx and the defective items on the escalator or associated escalator control room will be captured on the updated revisions of the LOIS lists which will have a trackable document number. Note that any NCRs relating to workmanship, installation error, etc. shall be raised and tracked by a separate NCR. This LOIS list for Escalator 9 is captured on document (Cxxx-SKC-M1-LST-B071_WS077-50009) on eB.
| 03SR - Stations (RfL) | Cxxx-NCR-002595 | NCR | LOIS List Items for Escalator 10 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-06-30 | 2018-07-13 08:05 | 13 | 2017-03-31 11:47 | Mechanical - Escalators | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Prior to shipping the escalator from the __ factory, remedial items that had not been closed in the factory were identified on a Rev 1 - List of Outstanding Items Schedule (LOIS). These items where spotted during the quality inspection of each escalator by accredited __, & CRL inspectors in line with the __ Escalators Factory ITP (Cxxx-SKC-M1-ITP-B071_WS077-50005). Items identified on this LOIS list need to be closed out / actioned on site prior to handover to the Client from the Tier 1 contractor. Upon inspection of the escalator trusses that have recently been delivered to site, it has been identified that there have been items damaged possibly during transit from the __ factory to the UK. These have only been discovered once the escalator shrink wrap protection was removed on site. New items such as these identified on site will be captured on new updated revisions of the LOIS list. In agreement with the CRL (__) and CEG (__), an NCR will be raised for each escalator at Paddington Cxxx and the defective items on the escalator or associated escalator control room will be captured on the updated revisions of the LOIS lists which will have a trackable document number. Note that any NCRs relating to workmanship, installation error, etc. shall be raised and tracked by a separate NCR. This LOIS list for Escalator 10 is captured on document (Cxxx-SKC-M1-LST-B071_WS077-50010) on eB.
| 03SR - Stations (RfL) | Cxxx-NCR-002596 | NCR | Unpaid - liftshaft - oversized holes - fin plates |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-06-29 | 2017-04-07 08:13 | -83 | 2017-03-31 12:04 | Structural Engineering - Finishes | 1500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | We were informed by our subcontractor __, this morning, that due to a drafting error the holes in the fin plates to the Unpaid lift have been slightly oversized, they are 20mm diameter but should be 14mm diameter as per approved DDCD.
| 03SR - Stations (RfL) | Cxxx-NCR-002597 | NCR | LOIS List Items for Escalator 11 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-06-30 | 2018-07-13 08:09 | 13 | 2017-03-31 11:50 | Mechanical - Escalators | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Prior to shipping the escalator from the __ factory, remedial items that had not been closed in the factory were identified on a Rev 1 - List of Outstanding Items Schedule (LOIS). These items where spotted during the quality inspection of each escalator by accredited __, & CRL inspectors in line with the __ Escalators Factory ITP (Cxxx-SKC-M1-ITP-B071_WS077-50005). Items identified on this LOIS list need to be closed out / actioned on site prior to handover to the Client from the Tier 1 contractor. Upon inspection of the escalator trusses that have recently been delivered to site, it has been identified that there have been items damaged possibly during transit from the __ factory to the UK. These have only been discovered once the escalator shrink wrap protection was removed on site. New items such as these identified on site will be captured on new updated revisions of the LOIS list. In agreement with the CRL (__) and CEG (__), an NCR will be raised for each escalator at Paddington Cxxx and the defective items on the escalator or associated escalator control room will be captured on the updated revisions of the LOIS lists which will have a trackable document number. Note that any NCRs relating to workmanship, installation error, etc. shall be raised and tracked by a separate NCR. This LOIS list for Escalator 11 is captured on document (Cxxx-SKC-M1-LST-B071_WS077-50011) on eB.
| 03SR - Stations (RfL) | Cxxx-NCR-002598 | NCR | LOIS List Items for Escalator 12 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-06-30 | 2019-03-16 11:57 | 259 | 2017-03-31 11:54 | Mechanical - Escalators | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Prior to shipping the escalator from the __ factory, remedial items that had not been closed in the factory were identified on a Rev 1 - List of Outstanding Items Schedule (LOIS). These items where spotted during the quality inspection of each escalator by accredited __, & CRL inspectors in line with the __ Escalators Factory ITP (Cxxx-SKC-M1-ITP-B071_WS077-50005). Items identified on this LOIS list need to be closed out / actioned on site prior to handover to the Client from the Tier 1 contractor. Upon inspection of the escalator trusses that have recently been delivered to site, it has been identified that there have been items damaged possibly during transit from the __ factory to the UK. These have only been discovered once the escalator shrink wrap protection was removed on site. New items such as these identified on site will be captured on new updated revisions of the LOIS list. In agreement with the CRL (__) and CEG (__), an NCR will be raised for each escalator at Paddington Cxxx and the defective items on the escalator or associated escalator control room will be captured on the updated revisions of the LOIS lists which will have a trackable document number. Note that any NCRs relating to workmanship, installation error, etc. shall be raised and tracked by a separate NCR. This LOIS list for Escalator 12 is captured on document (Cxxx-SKC-M1-LST-B071_WS077-50012) on eB.
| 03SR - Stations (RfL) | Cxxx-NCR-002599 | NCR | LOIS List Items for Escalator 13 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-06-30 | 2018-07-13 08:13 | 13 | 2017-03-31 11:57 | Mechanical - Escalators | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Prior to shipping the escalator from the __ factory, remedial items that had not been closed in the factory were identified on a Rev 1 - List of Outstanding Items Schedule (LOIS). These items where spotted during the quality inspection of each escalator by accredited __, & CRL inspectors in line with the __ Escalators Factory ITP (Cxxx-SKC-M1-ITP-B071_WS077-50005). Items identified on this LOIS list need to be closed out / actioned on site prior to handover to the Client from the Tier 1 contractor. Upon inspection of the escalator trusses that have recently been delivered to site, it has been identified that there have been items damaged possibly during transit from the __ factory to the UK. These have only been discovered once the escalator shrink wrap protection was removed on site. New items such as these identified on site will be captured on new updated revisions of the LOIS list. In agreement with the CRL (__) and CEG (__), an NCR will be raised for each escalator at Paddington Cxxx and the defective items on the escalator or associated escalator control room will be captured on the updated revisions of the LOIS lists which will have a trackable document number. Note that any NCRs relating to workmanship, installation error, etc. shall be raised and tracked by a separate NCR. This LOIS list for Escalator 13 is captured on document (Cxxx-SKC-M1-LST-B071_WS077-50013) on eB.
| 03SR - Stations (RfL) | Cxxx-NCR-002600 | NCR | LOIS List Items for Escalator 14 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-06-30 | 2019-03-16 11:59 | 259 | 2017-03-31 12:01 | Mechanical - Escalators | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Prior to shipping the escalator from the __ factory, remedial items that had not been closed in the factory were identified on a Rev 1 - List of Outstanding Items Schedule (LOIS). These items where spotted during the quality inspection of each escalator by accredited __, & CRL inspectors in line with the __ Escalators Factory ITP (Cxxx-SKC-M1-ITP-B071_WS077-50005). Items identified on this LOIS list need to be closed out / actioned on site prior to handover to the Client from the Tier 1 contractor. Upon inspection of the escalator trusses that have recently been delivered to site, it has been identified that there have been items damaged possibly during transit from the __ factory to the UK. These have only been discovered once the escalator shrink wrap protection was removed on site. New items such as these identified on site will be captured on new updated revisions of the LOIS list. In agreement with the CRL (__) and CEG (__), an NCR will be raised for each escalator at Paddington Cxxx and the defective items on the escalator or associated escalator control room will be captured on the updated revisions of the LOIS lists which will have a trackable document number. Note that any NCRs relating to workmanship, installation error, etc. shall be raised and tracked by a separate NCR. This LOIS list for Escalator 14 is captured on document (Cxxx-SKC-M1-LST-B071_WS077-50014) on eB.
| 03SR - Stations (RfL) | Cxxx-NCR-002601 | NCR | LOIS List Items for Escalator 15 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-06-30 | 2019-03-16 12:01 | 259 | 2017-03-31 12:04 | Mechanical - Escalators | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Prior to shipping the escalator from the __ factory, remedial items that had not been closed in the factory were identified on a Rev 1 - List of Outstanding Items Schedule (LOIS). These items where spotted during the quality inspection of each escalator by accredited __, & CRL inspectors in line with the __ Escalators Factory ITP (Cxxx-SKC-M1-ITP-B071_WS077-50005). Items identified on this LOIS list need to be closed out / actioned on site prior to handover to the Client from the Tier 1 contractor. Upon inspection of the escalator trusses that have recently been delivered to site, it has been identified that there have been items damaged possibly during transit from the __ factory to the UK. These have only been discovered once the escalator shrink wrap protection was removed on site. New items such as these identified on site will be captured on new updated revisions of the LOIS list. In agreement with the CRL (__) and CEG (__), an NCR will be raised for each escalator at Paddington Cxxx and the defective items on the escalator or associated escalator control room will be captured on the updated revisions of the LOIS lists which will have a trackable document number. Note that any NCRs relating to workmanship, installation error, etc. shall be raised and tracked by a separate NCR. This LOIS list for Escalator 15 is captured on document (Cxxx-SKC-M1-LST-B071_WS077-50015) on eB.
| 03SR - Stations (RfL) | Cxxx-NCR-002602 | NCR | LOIS List Items for Escalator 1 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-06-30 | 2018-07-13 08:16 | 13 | 2017-03-31 12:07 | Mechanical - Escalators | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Prior to shipping the escalator from the __ factory, remedial items that had not been closed in the factory were identified on a Rev 1 - List of Outstanding Items Schedule (LOIS). These items where spotted during the quality inspection of each escalator by accredited __, & CRL inspectors in line with the __ Escalators Factory ITP (Cxxx-SKC-M1-ITP-B071_WS077-50005). Items identified on this LOIS list need to be closed out / actioned on site prior to handover to the Client from the Tier 1 contractor. Upon inspection of the escalator trusses that have recently been delivered to site, it has been identified that there have been items damaged possibly during transit from the __ factory to the UK. These have only been discovered once the escalator shrink wrap protection was removed on site. New items such as these identified on site will be captured on new updated revisions of the LOIS list. In agreement with the CRL (__) and CEG (__), an NCR will be raised for each escalator at Paddington Cxxx and the defective items on the escalator or associated escalator control room will be captured on the updated revisions of the LOIS lists which will have a trackable document number. Note that any NCRs relating to workmanship, installation error, etc. shall be raised and tracked by a separate NCR. This LOIS list for Escalator 1 is captured on document (Cxxx-SKC-M1-LST-B071_WS077-50016) on eB.
| 03SR - Stations (RfL) | Cxxx-NCR-002603 | NCR | LOIS List Items for Escalator 2 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-06-30 | 2018-07-13 08:19 | 13 | 2017-03-31 12:10 | Mechanical - Escalators | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Prior to shipping the escalator from the __ factory, remedial items that had not been closed in the factory were identified on a Rev 1 - List of Outstanding Items Schedule (LOIS). These items where spotted during the quality inspection of each escalator by accredited __, & CRL inspectors in line with the __ Escalators Factory ITP (Cxxx-SKC-M1-ITP-B071_WS077-50005). Items identified on this LOIS list need to be closed out / actioned on site prior to handover to the Client from the Tier 1 contractor. Upon inspection of the escalator trusses that have recently been delivered to site, it has been identified that there have been items damaged possibly during transit from the __ factory to the UK. These have only been discovered once the escalator shrink wrap protection was removed on site. New items such as these identified on site will be captured on new updated revisions of the LOIS list. In agreement with the CRL (__) and CEG (__), an NCR will be raised for each escalator at Paddington Cxxx and the defective items on the escalator or associated escalator control room will be captured on the updated revisions of the LOIS lists which will have a trackable document number. Note that any NCRs relating to workmanship, installation error, etc. shall be raised and tracked by a separate NCR. This LOIS list for Escalator 2 is captured on document (Cxxx-SKC-M1-LST-B071_WS077-50017) on eB.
| 03SR - Stations (RfL) | Cxxx-NCR-002604 | NCR | LOIS List Items for Escalator 3 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-06-30 | 2019-03-16 12:03 | 259 | 2017-03-31 12:12 | Mechanical - Escalators | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Prior to shipping the escalator from the __ factory, remedial items that had not been closed in the factory were identified on a Rev 1 - List of Outstanding Items Schedule (LOIS). These items where spotted during the quality inspection of each escalator by accredited __, & CRL inspectors in line with the __ Escalators Factory ITP (Cxxx-SKC-M1-ITP-B071_WS077-50005). Items identified on this LOIS list need to be closed out / actioned on site prior to handover to the Client from the Tier 1 contractor. Upon inspection of the escalator trusses that have recently been delivered to site, it has been identified that there have been items damaged possibly during transit from the __ factory to the UK. These have only been discovered once the escalator shrink wrap protection was removed on site. New items such as these identified on site will be captured on new updated revisions of the LOIS list. In agreement with the CRL (__) and CEG (__), an NCR will be raised for each escalator at Paddington Cxxx and the defective items on the escalator or associated escalator control room will be captured on the updated revisions of the LOIS lists which will have a trackable document number. Note that any NCRs relating to workmanship, installation error, etc. shall be raised and tracked by a separate NCR. This LOIS list for Escalator 3 is captured on document (Cxxx-SKC-M1-LST-B071_WS077-50018) on eB.
| 03SR - Stations (RfL) | Cxxx-NCR-002605 | NCR | LOIS List Items for Escalator 4 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-06-30 | 2019-03-16 12:04 | 259 | 2017-03-31 12:15 | Mechanical - Escalators | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Prior to shipping the escalator from the __ factory, remedial items that had not been closed in the factory were identified on a Rev 1 - List of Outstanding Items Schedule (LOIS). These items where spotted during the quality inspection of each escalator by accredited __, & CRL inspectors in line with the __ Escalators Factory ITP (Cxxx-SKC-M1-ITP-B071_WS077-50005). Items identified on this LOIS list need to be closed out / actioned on site prior to handover to the Client from the Tier 1 contractor. Upon inspection of the escalator trusses that have recently been delivered to site, it has been identified that there have been items damaged possibly during transit from the __ factory to the UK. These have only been discovered once the escalator shrink wrap protection was removed on site. New items such as these identified on site will be captured on new updated revisions of the LOIS list. In agreement with the CRL (__) and CEG (__), an NCR will be raised for each escalator at Paddington Cxxx and the defective items on the escalator or associated escalator control room will be captured on the updated revisions of the LOIS lists which will have a trackable document number. Note that any NCRs relating to workmanship, installation error, etc. shall be raised and tracked by a separate NCR. This LOIS list for Escalator 4 is captured on document (Cxxx-SKC-M1-LST-B071_WS077-50019) on eB.
| 03SR - Stations (RfL) | Cxxx-NCR-002606 | NCR | LOIS List Items for Escalator 5 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-06-30 | 2019-03-16 12:06 | 259 | 2017-03-31 12:17 | Mechanical - Escalators | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Prior to shipping the escalator from the __ factory, remedial items that had not been closed in the factory were identified on a Rev 1 - List of Outstanding Items Schedule (LOIS). These items where spotted during the quality inspection of each escalator by accredited __, & CRL inspectors in line with the __ Escalators Factory ITP (Cxxx-SKC-M1-ITP-B071_WS077-50005). Items identified on this LOIS list need to be closed out / actioned on site prior to handover to the Client from the Tier 1 contractor. Upon inspection of the escalator trusses that have recently been delivered to site, it has been identified that there have been items damaged possibly during transit from the __ factory to the UK. These have only been discovered once the escalator shrink wrap protection was removed on site. New items such as these identified on site will be captured on new updated revisions of the LOIS list. In agreement with the CRL (__) and CEG (__), an NCR will be raised for each escalator at Paddington Cxxx and the defective items on the escalator or associated escalator control room will be captured on the updated revisions of the LOIS lists which will have a trackable document number. Note that any NCRs relating to workmanship, installation error, etc. shall be raised and tracked by a separate NCR. This LOIS list for Escalator 5 is captured on document (Cxxx-SKC-M1-LST-B071_WS077-50020) on eB.
| 03SR - Stations (RfL) | Cxxx-NCR-002607 | NCR | Incorrect Drainage Level of Bakerloo Box Escalator Pits (Esc 14 & 15) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-10-31 | 2017-06-27 15:07 | -126 | 2017-04-03 15:36 | Civil - Civil Engineering General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The drainage grates of both escalator pits in the Bakerloo Box (Escalator 14 & 15) have been installed at the wrong level, resulting in standing water which cannot drain freely. In each escalator pit, 1 no. drainage grate has been installed approx. 10-15mm above finished concrete level as shown in the attached document. It is also evident that the surface finish of the escalator pits do not have a common gradient which falls to the drainage grate, when dewatering these pits water ingress from the concrete construction joints showed high and low sections of the concrete in each pit as shown in the attached document. The maximum depth of standing water recorded in both pits was 20mm. Note the following: - Cxxx-SWN-S-DDB-M171_Z-24201 shows no fall to be constructed for the escalator pit base; and - Cxxx-SKC-P-DDA-M171_7-21114 shows conflicting information in regards to the outlet to be installed on the drawing - one being a __ parapet outlet and the other being a __ parapet outlet.
| 03SR - Stations (RfL) | Cxxx-NCR-002608 | NCR | Mastic Joint in Blockwork De-bonding from Blockface |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-09-22 | 2017-11-10 11:33 | 49 | 2017-04-03 14:00 | Architectural - Brickworks/Blockworks | 1500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Vertical and horizontal joint de-bonding from the blockwork. This de-bonding causes a gap between the mastic and the blockwork. This has occured on the perimeter wall intermedaite level and concourse level in a number of locations. This has also occured on vertical mastic joints predominately the perimeter walls intermediate and concourse but also on the internal walls.
| 03SR - Stations (RfL) | Cxxx-NCR-002609 | NCR | Intermediate Level - FCR II Room - Damage to Finished Sealer |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-10-13 | 2017-06-13 10:35 | -122 | 2017-04-06 12:49 | Architectural - Flooring | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Within the FCR II room on Intermediate Level there has been damage to the Finished Floor Sealer.
| 03SR - Stations (RfL) | Cxxx-NCR-002610 | NCR | Firestop Compound with Deflection head - Unsuppoorted Detail by Manufacturer |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-06-27 | 2017-05-18 07:50 | -40 | 2017-04-08 09:05 | Fire - Compartmentation | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | s firestopping subcontractor (__) has installed a detail on site that is not supported by the product manufacturer. This detail is regarding the installation of compound within a service penetration with a soft joint (deflection joint) against the top of the compound and the soffit in 2no. locations as shown on the attached marked up drawings. After consultation with the products manufacturer __ Ltd., they have confirmed that they do not recognise this detail and cannot assure its install. Rework will be required.
| 03SR - Stations (RfL) | Cxxx-NCR-002611 | NCR | CMS & Trunking adjacent to TRIII & ECR Room 12 & 13 Concourse Level |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-10-04 | 2017-10-30 14:26 | 26 | 2017-04-07 12:42 | Electrical - Electrical Engineering General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Poorly fitted bends/returns and pacers - see attached pictures.
| 03SR - Stations (RfL) | Cxxx-NCR-002612 | NCR | __ HY-200 Chemical Resin Fixing Compound in Blockwork not specified for use. |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-10-31 | 2017-11-18 09:48 | -347 | 2017-04-07 14:02 | Electrical - Electrical Engineering General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | __ have used the __ HY-200 resin compound to install 10mm stud into concrete blockwork. This type has been specified by hilti for use in c20/25 cracked poured concrete and not the blockwork installed. __ have raised an MCR that has been approved for use in blockwork for __ HY-270 resin compound, however __ have not specified its use in the particular type of blockwork on the project. Also covered by __ 000052 (attached)
| 03SR - Stations (RfL) | Cxxx-NCR-002613 | NCR | Incorrect Finished Concrete Level on Intermediate Support (Esc 10 & 11) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-10-31 | 2017-10-25 13:19 | -6 | 2017-04-07 15:33 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Following remedial works undertaken on Esc 8, 9 & 12 intermediate supports, a survey check was performed on the intermediate supports for Esc 10 & 11. It was found that the intermediate supports under these escalators is currently too high. As per drawing Cxxx-SWN-S-DDB-M171_Z-04568, the concrete level of the supports between GL13-14 should be 108.720m. Currently on site the uneven concrete surface is the following height (in certain areas) above the level of 108.720m: - Escalator 10 intermediate support is approx. 12mm too high; and - Escalator 11 intermediate support is approx. 5mm too high.
| 03SR - Stations (RfL) | Cxxx-NCR-002614 | NCR | Installation of permanent shoes without a confirmed design |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-09-30 | 2017-08-31 12:10 | -30 | 2017-04-10 09:39 | Civil - Structural Engineering | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | On the vent shaft head houses (VSHH) steel is currently being erected. To support the bottom of the steel columns temporary and permanent shoes have been and are being installed at Eastbourne Terrace level. On GL E1, the East end of the East VSHH two permanent shoes are to be installed. One on the North side and one on the South side. It was discovered that the original design was not correct as these permanent shoes could not be installed directly into the corridor roof slab below due to a level change. This was not noticed by __ at tender and not questioned. __, via __, has completed a re-design of this area and has submitted it to who has passed it to our designers for a full check. In the meantime (Thursday 6th April) __ have instructed __ to install these shoes according to their new design and continue the steel installation under their own risk. They are fully aware of this risk.
| 03SR - Stations (RfL) | Cxxx-NCR-002615 | NCR | Vent shaft head house steelwork not fitting on site |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-10-14 | 2017-09-15 07:40 | -29 | 2017-04-10 10:12 | Civil - Structural Engineering | 2500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | On the East vent shaft head house (VSHH) a trapezoidal beam has been delivered to site. Laskesmere/__ attempted to install this beam and it did not fit on site. Steel EB 9 Has a 10mm kick outwards in the steel and steel EB 8 has a 10mm kick inwards thus creating a 20mm step in alignment of the steel work on grid line E1 to the north corner of the East VSHH. This is outside of the manufacturing/site tolerances.
| 03SR - Stations (RfL) | Cxxx-NCR-002616 | NCR | Water Ingress in Soffit of Pressurization Fan Room 1 (PFR-1 #938) Causing damage to Ductwork Supports |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-01-17 | 2018-01-20 10:59 | 3 | 2017-04-12 07:17 | Mechanical - Mechanical Engineering General | 1500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Water ingress in Soffit of Pressurization Fan Room (PFR-1 # 938). In turn this is causing damage to fire rated ductwork support.
| 03SR - Stations (RfL) | Cxxx-NCR-002618 | NCR | Cutting Naylor Ultra-Fire Lintels |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-11-14 | 2018-01-05 13:35 | 52 | 2017-04-12 16:16 | Architectural - Brickworks/Blockworks | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The sub-contractor has been cutting ulta-fire lintels to suit new builderswork holes on site.
| 03SR - Stations (RfL) | Cxxx-NCR-002619 | NCR | Service Support Bracketry Under a Fire Condition. |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-10-16 | 2017-08-15 08:38 | -62 | 2017-04-19 15:06 | Fire - Fire Systems & General | 30000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Service Support Bracketry lacks design input to comply with 'Under a Fire Condition' as per BS8519:2010 .
| 03SR - Stations (RfL) | Cxxx-NCR-002620 | NCR | SCR cooling arrangement |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-05-30 | 2018-09-11 16:10 | 104 | 2017-04-25 15:57 | Mechanical - Heating Ventilation & Air Conditioning | 5000 |  | Design | Use As-Is | 3 (3-6k) | Complete | Design Problem - Not Defined | Completed |  | The gated design included for duty and standby cooling units (CU05 and CU06) located within SCR-II. These two cooling units have been omitted by the Contractor. The current cooling arrangement for the Station Computer Rooms (SCR-I #746 and II #747) provides for a supply air feed into SCR-II and a, through the wall, air transfer damper into SCR-I (Refer to drawings: Cxxx-SKC-M-DDA-M171_3-31587_C05 and Cxxx-SKC-M-DDA-M171_3-31537_C04). 1. Contractor to confirm systemwide heat loads: - The Contractor is to confirm the latest / final heat loads from C690, for the Station computer assembly in SCR-I, and distribution board in SCR-II. The current C690-Cxxx Interface Control Document (Cxxx-SKC-Z-RGN-B071_WS077-50003v3.0) states the following: SCR-I contains C690 Autofare station computer assembly: SC2 (Station Computer) assembly operates over a range from -10 OC to +50OC Total heat generation: 108Watts max per Station Computer assembly. 1) SC2: 31 Watt (max) 2) HP1410-24G Port Switch dissipates 22W (max) 3) __ Unmanaged Ethernet Switch – WSC29605-24PS-L – Maximum power consumption: 55W. The SC2 shall be superseded by SC Assembly (9529-10003) Issue 1 Awaiting Approval SCR-II contains C690 distribution board: No load information in the ICD 2. Contractor to address open CEG’s Main Box SDR comment: - Refer to comment sheet Cxxx-XRL-Z-XCS-B071_WS077-50006; - Comment #119.5 made against drawing Cxxx-SKC-M-DDA-M171_3-31587: “The SCR is a critical room with communications equipment within it and CU05 / 06 need to be placed outside of the room in CER II-CWU 924. (CEG 03/03/2015)”
| 03SR - Stations (RfL) | Cxxx-NCR-002621 | NCR | __ Pressure Relief Dampers – Fixings into Lintels - Concourse level TR1, TR2, TR3, TR4 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-10-24 | 2017-11-03 12:52 | 10 | 2017-04-27 11:55 | Fire - Fire Systems & General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The Fixings to the perimeter of the outer grilles to the pressure relief dampers have achieved an insufficient edge distance of between 5-22mm for each fixing. Refer to attached photos ref P1 and P2 The 215mm Ultrafire lintels in these locations have an outer 20mm fire resistant coating of __ which has resulted in all of the fixing being located within this material which is not acceptable to the Lintel manufacturer Naylor. Note. The manufacturer’s detail from __ is for the fixings to have a 22.5mm edge distance from the edge of the opening to the centerline of the fixing holes. Refer to attached extract of CRl-MCR-003293 showing fixing detail information.
| 03SR - Stations (RfL) | Cxxx-NCR-002622 | NCR | Repair to Screed and Floor Sealant (ECR 12 & 13) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-06-28 | 2017-05-09 16:04 | -50 | 2017-04-28 12:58 | Architectural - Flooring | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 4 no. cabinets for Escalator Control Room (ECR) 12 & 13 have been installed 100mm out of tolerance. The most Eastern cabinet, Esc 13 Controller encroaches on the free space provided at the Eastern end of the room that will eventually house the coil fan units for the ECR. Rectification will require moving each cabinet 100mm West to the correct positions as per Cxxx-SKC-M1-DWG-B071_WS077-50233 (P02), as a result 16 no. holes require repair to the screed inclusive of floor sealant repair at each location as shown in the attached photos.
| 03SR - Stations (RfL) | Cxxx-NCR-002623 | NCR | Precast Canopy Foundation GL 74 - Bolts cast out of tolerance |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-05-12 | 2017-05-10 15:06 | -2 | 2017-04-28 14:06 | Structural Engineering - Structural Engineering - General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The 4 no. 48mm diameter bolts cast into the precast canopy foundation installed at GL 74 are out of tolerance. Specification Cxxx-SKC-S-RSP-B071-WS077-50004, clause KH10 – B2 states ‘Position of each dowel bar at 123.375m: ± 3mm combined total in all directions.’ check this combined tolerance with a template of the canopy baseplate, which has 51mm diameter holes. If the template fits, the centre point of this bolt cluster is then set out to within +/- 3mm. The canopy column baseplate has 4 no. 60mm diameter holes at centres of 243mm apart that fit on a 343mm diameter circle. This is as shown on drawing Cxxx-SKC-Y-DDD-M171_1-50013 and as confirmed in -RFI-001965. The cast in bolts for the foundation unit installed at GL 74 are spaced out of tolerance, however the bolts will fit into a baseplate with 60mm holes. propose to use the foundation unit ‘as-is’ at GL 74. The metal baseplate template, with 60mm holes, fits the bolts and can be centred correctly. Please see pictures attached IMG_7904.jpg, IMG_7905.jpg, IMG_7906.jpg, and IMG_7907.jpg. IRF 2061 has been raised for site inspection. As per the response within Cxxx-NCR-002556, confirm there will be no welding of a larger washer over the baseplate. Please review Cxxx-RFI-001965 with this NCR. Please confirm this proposal and evidence is acceptable.
| 03SR - Stations (RfL) | Cxxx-NCR-002624 | NCR | Attenuation tank lid UNITS L09 and L10: Cut and repair |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-05-01 | 2018-09-10 07:27 | 132 | 2017-04-28 14:51 | Structural Engineering - Structural Engineering - General | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Attenuation tank lid UNITS L09 and L10 have been incorrectly cast 1500mm wide, with the associated tank UNITS 11 and 12 cast to suit an east-west dimension of 1450mm. A discrepancy has been highlighted on drawing Cxxx-SKC-D-DWG-B071_WS077-50030 EDIT.
| 03SR - Stations (RfL) | Cxxx-NCR-002625 | NCR | Attenuation tank UNIT 13 - West joint edge chamfer |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-06-02 | 2017-06-17 12:33 | 15 | 2017-04-28 15:30 | Structural Engineering - Pre-cast | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | Attenuation tank UNIT 13 was incorrectly cast without a chamfered edge on the west joint, as highlighted within drawing Cxxx-SKC-D-DWG-B071_WS077-50021 EDIT, and shown within image '100_5193.jpg'.
| 03SR - Stations (RfL) | Cxxx-NCR-002626 | NCR | __ __ __ Waterproofing Damage - Canopy GLs 64-50 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-06-02 | 2017-05-12 14:13 | -21 | 2017-05-03 16:11 | Civil - Civil Engineering General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | As per Cxxx-NCR-002505 and Cxxx-NCR-002583, having exposed __ on the north face of the __ capping beam, between GLs 64-50, pockets of water and de-bonded sections of the __ have been identified at the interface between the membrane and the concrete.
| 03SR - Stations (RfL) | Cxxx-NCR-002627 | NCR | Missing fin plates BLL 12 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-08-02 | 2017-07-28 12:11 | -5 | 2017-05-04 13:11 | Structural Engineering - Steel Member | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | It was noticed on site, previous to the lifting operation, that when the modules are to be up righted, the lifting chains would clash with the fin plates, causing it to stop. The fin plates were removed as otherwise the lift would not have been able to continue. In 4 locations on the third module of BLL 12, the fin plates were removed from the structure in order to allow the lift to commence.
| 03SR - Stations (RfL) | Cxxx-NCR-002628 | NCR | Missing test certification for Main Earthing Stucture |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-12-13 | 2017-12-02 08:36 | -11 | 2017-05-04 13:54 | Systems - Earthing and Bonding | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Missing continuity test record for plunge column 33 to base slab connection
| 03SR - Stations (RfL) | Cxxx-NCR-002629 | NCR | Glazed panels - Unpaid lift - bent fin plate |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-08-02 | 2017-06-01 16:10 | -62 | 2017-05-04 13:57 | Architectural - Glazing | 2500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the installation of the 2nd level of glazed panels on the unpaid lift shaft lift 6/7, __ glazers and notes that there's a misalignment between the top clamping plates and the North/West corner, that needs to be fixed. notes also the fin plate welded to the structure is not levelled and there's a 4/5 mm difference, and for consequence the glazed panel and the SS clamping plate doesn't fit properly, where the fin is bent. See attached photos. Potential impact in other locations. The glazing works are now stopped.
| 03SR - Stations (RfL) | Cxxx-NCR-002630 | NCR | Non-Conforming CMS Installation (ECR I & II) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-10-31 | 2017-09-23 08:00 | -38 | 2017-05-15 15:37 | Mechanical - Escalators | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following a spot check carried out by on the recently passed off CMS installation in Escalator Control Rooms for Esc 8&9 (ECR I) and Esc 6&7 (ECR II) it was found that the CMS installed in both rooms does not comply fully with Section 29 of Part 3 of the CRL Pan TfL Specification (SPC-LAE-301941170). In particular Cable Tray in the rooms has been supported off the structure using 21mm unistrut which does not comply with Item 29.3.2, nor is the cross bonding on the CMS installed in accordance with BS 7671.
| 03SR - Stations (RfL) | Cxxx-NCR-002632 | NCR | Attenuation Tanks Insitu Walls - MCRs not revised for steel and spacers |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-06-02 | 2017-05-12 16:05 | -21 | 2017-05-07 10:15 | Structural Engineering - Structural Engineering - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The attenuation tank in-situ walls were installed between GLs 58-60 (as per Cxxx-FCD-002196) prior to the approval of the revised MCR documents for the steel reinforcement and the concrete spacers, MCR documents Cxxx-SKC-O-TSC-B071_WS077-50793 revision 3.0 and Cxxx-SKC-O-TSC-B071_WS077-50786 revision 5.0 respectively. Please find the revised MCRs attached, now at code 1 status.
| 03SR - Stations (RfL) | Cxxx-NCR-002633 | NCR | Unpaid Lift __ Channels Removed |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-08-09 | 2017-09-07 07:58 | 29 | 2017-05-11 11:05 | Architectural - General | 1000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | __ have removed 1 No. __ channel and partially removed 1 No. __ Channel from the second level down in the middle partition.
| 03SR - Stations (RfL) | Cxxx-NCR-002634 | NCR | __ __ __ Waterproofing Damage - Canopy GLs 84 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-06-09 | 2017-05-12 14:11 | -28 | 2017-05-11 13:22 | Civil - Civil Engineering General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | As per Cxxx-NCR-002505, 002583 and 002626, having exposed __ on the north face of the __ capping beam, between GLs 82-84, de-bonded sections of the __ have been identified at the interface between the membrane and the concrete.
| 03SR - Stations (RfL) | Cxxx-NCR-002636 | NCR | West VSHH Bolts Installed In the Wrong Locations |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-01-24 | 2018-02-02 17:12 | 9 | 2017-05-12 15:37 | Civil - Structural Engineering | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On the West vent shaft head house (VSHH), between gridlines W1 and W2, on both the North and the South walls the cast-in holding down bolts have been set out and installed incorrectly. The location of these bolts is highlighted in the attachment. The bolts have been set out approximately 185mm out from the correct positions. We have looked into the Cxxx and the Cxxx drawings but are unsure why they were located in such a position at this time. In the attachment I also include a sketch showing the dimensions of the bolts to the concrete and the column centre line and their comparison to the drawings. I have attached old photos showing the bolts in addition.
| 03SR - Stations (RfL) | Cxxx-NCR-002637 | NCR | SOR 751 - Damage to __ FireBoard |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-07-31 | 2018-03-01 09:38 | -152 | 2017-05-16 15:50 | Architectural - Walls | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Site Operatives have placed ductwork within the SOR 751 room and damaged the Finished Work Painted __ Fireboard. The work/ decision to place the ductwork within the room was not identified to any supervisors and seems to be an individual decision.
| 03SR - Stations (RfL) | Cxxx-NCR-002638 | NCR | BLL - Water ingress 17' |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-08-03 | 2018-08-03 14:28 | 0 | 2017-05-17 17:09 | Civil - Hydraulic Engineering | 10000 |  | Design | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | Further points of water ingress have been identified in the BLL box, post water ingress remediation works from April - May 2017. After a long period of dry weather, Paddington experienced heavy rain over the Weekend 6th/7th May, it was after this, water ingress was identified. 7 locations have been identified, as per the attached BLL schematic. Points 1 and 4 were injected on the 13th May and are being monitored. Points 2 and 3 were injected on the 17th May and are being monitored. The remaining points will be injected in the coming days. Once 7 points have been injected, will monitor the area again. The Points will be injected with the approved polyurethane resin, (MCR-50642)
| 03SR - Stations (RfL) | Cxxx-NCR-002640 | NCR | Damage blockwork in ESR II room due to removal of fixings |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-10-13 | 2017-10-30 08:46 | 17 | 2017-05-19 14:12 | Architectural - Brickworks/Blockworks | 1500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | In ESR II room on intermediate level the fixings for CMS have been removed from the blockwork creating holes. These holes are approximately 30mm wide and 35mm deep.
| 03SR - Stations (RfL) | Cxxx-NCR-002641 | NCR | Lift 8/9 - Paid lift - Missing concrete recess - Survey |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-12-20 | 2017-12-18 16:30 | -2 | 2017-05-22 09:35 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | notes that during a concrete survey, 3no concrete recesses on the Paid lift 8-9 to accommodate the base plates, are missing. Find attached mark-up drawings with survey details.
| 03SR - Stations (RfL) | Cxxx-NCR-002643 | NCR | Minor Core Hole Made in the Incorrect Location. |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-06-27 | 2017-06-28 15:33 | 1 | 2017-05-30 14:54 | Architectural - Walls | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | A minor core hole has been made in the wrong location. This core hole has gone approximately 20mm through the RC wall. From observation this core has not penetrated any rebar.
| 03SR - Stations (RfL) | Cxxx-NCR-002644 | NCR | Concrete nib on East VSHH out of tolerance |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-12-30 | 2018-02-02 17:13 | 34 | 2017-05-31 14:43 | Civil - Structural Engineering | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | On gridline E3 - EC on the East VSHH concrete nibs have been cast into the RC walls. Since the installation of the steel columns for the roofing and cladding it has been discovered that one of the nibs is out of tolerance laterally. This will cause problems with rainscreen panels and GFRC fins that are to be installed in these areas. Given the reinforcement requirements we do not believe the nib is structural. I have attached a mark-up that shows the nib in plan view and its position out of tolerance as well as a couple of photos.
| 03SR - Stations (RfL) | Cxxx-NCR-002645 | NCR | Intermediat Level - Water damaged Ductwork |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-02-14 | 2018-02-05 09:41 | -9 | 2017-06-01 08:33 | Civil - Civil Engineering General | 1500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Water damage to installed ductwork located in the following areas (drgs attached): · Intermediate level GL 6-7/D CWP / Lift V lobby; · Intermediate level GL 9/E-D PFR1.
| 03SR - Stations (RfL) | Cxxx-NCR-002646 | NCR | __ Paddington Station Platform 12 Waiting Room - Macalloy Gusset Plate 6mm Weld MPI Test Failure |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-07-05 | 2017-06-29 14:04 | -6 | 2017-06-05 16:54 | Structural Engineering - Welding | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | As part of the new __ platform 12 waiting room build, stainless steel macalloy tension bars are to be installed to the existing and new structural steel work. The proposed detail for fixing the new macalloy tension bars to the existing structural steel PFC's is for 2 no. gusset plates welded with a 6mm fillet weld to the internal flange of the PFC's. Once welding was complete, both gusset plate 6mm fillet welds were inspected and MPI test carried out - results for both weld tests proved to be a failure and rework required.
| 03SR - Stations (RfL) | Cxxx-NCR-002647 | NCR | __ HY200 chemical fixing |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-11-29 | 2017-11-18 09:50 | -11 | 2017-06-02 13:40 | Mechanical - Piping | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | Further to issue of Cxxx-NCR-002612 (__-NCR-000052), __ have recommenced works on Intermediate East using __ HY-200 resin compound to install 10mm stud into concrete blockwork in the MCC-CWU room to fix the 100 mm dia vent pipe to the wall. This type of resin has been specified by hilti for use in c20/25 cracked poured concrete and not the blockwork installed (Refer to CRL-MCR-002495). __ have raised an MCR (CRL-MCR-002445) that has been approved for use in blockwork for __ HY-270 resin compound, however __ have not specified its use in the particular type of blockwork on the project.
| 03SR - Stations (RfL) | Cxxx-NCR-002651 | NCR | RD threads sockets cast in - Main box - |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-11-15 | 2018-10-31 13:58 | -15 | 2017-06-05 16:00 | Civil - Civil Engineering General | 5000 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | The drawing Cxxx-SKC-S-XSK-B071_WS077-50031 - insitu RC cast in fixing is the detail for cast in fixing anchor around the escalator openings to take the glass balustrade fixings, the advertising screens and the glass track at BLL level. On review the CFS catalogue for a CFA-FA SS (flat steel anchor) only round threads are available and this has what has been installed by . However, metric fixings are specified in the Works Information - Cxxx Architectural Specification - clause JZ20.1102 Bolts, nuts and washers reference BS EN 3506
| 03SR - Stations (RfL) | Cxxx-NCR-002652 | NCR | Unpaid Lift Flange Connection HSFG Bolts Installed Incorrectly |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-09-04 | 2017-06-30 15:35 | -66 | 2017-06-06 13:27 | Structural Engineering - Bolted Connections | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Upon inspection of completed works on the Unpaid Lift HSFG bolted flange connections, it was noted that there was a nominal gap between nut and __I washer (See attached "Nominal gap.JPG"). With further investigation into HSFG BS documents, it was noted that the configuration of the system installed on site, is incorrect. Please find attached BS 14399-9:2009. Please reference page 20. Configuration 7b was the intended configuration to be installed on site. The nut was the tightened element of the system, which was witnessed by engineer. Please see attached picture of the configuration on site. It is apparent that the configuration we have on site is as follows: Bolt thread - __I washer - Flange connections - Hardened washer - Bolt head (See attached "Whole system.JPG"). This is incorrectly installed, as the system requires a nut facing washer between nut and __I washer.
| 03SR - Stations (RfL) | Cxxx-NCR-002653 | NCR | Unpaid lift -2nd level- glass panel dent (break) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-08-03 | 2018-08-20 16:15 | 17 | 2017-06-08 10:14 | Architectural - Finishes | 1500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the quality inspection with CRL architects and , on the 2nd level of glazing panels on the Unpaid lift shaft, a small (see attached picture) dent on the glass panel was noted.
| 03SR - Stations (RfL) | Cxxx-NCR-002654 | NCR | Benchmark acceptance |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2017-08-04 | 2017-08-14 07:56 | 10 | 2017-06-08 11:55 | Architectural - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | A planned Crossrail surveillance was undertaken on 16th May 2017 to look at Management of Architectural, Samples and Benchmarks. During the Exit Meeting the Contractor was requested to provide evidence of acceptance for the following Benchmark acceptance records; Door Set’s, Brick Slip Cladding Panels and Bronze Column Cladding. Cxxx Architectural Specification Cxxx-SKC-A-RSP-B071_WS077-50003 JA.4010 Benchmarks states: “Upon commencement of installation, erect complete sections of elements of the works for the acceptance of the Project Manager”. The Contractor was unable to provide the following evidence for Benchmark acceptance; Bronze column cladding installed on the platform, Door sets installed on the intermediate level and Brickslip pre-cast cladding installed in the station box. A planned inspection had taken place and the benchmarks were accepted, but the Contractor has failed to formally record the acceptance.
| 03SR - Stations (RfL) | Cxxx-NCR-002655 | NCR | Siemans Cabinets in Mist I Room Exposure to Dust |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-08-31 | 2018-08-10 12:29 | -21 | 2017-06-11 15:25 | Archaeology - General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | __ cabinets in the MIST I room were exposed to dust when a cutting activity was carried out. This dust then went on to the wrapped up siemans cabinets. Sieman cabinets now encase with a dust blanket as stated in Cxxx-NCR-002444.
| 03SR - Stations (RfL) | Cxxx-NCR-002656 | NCR | Canopy - Holding Down Bolts |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-11-30 | 2017-11-24 16:29 | -6 | 2017-06-12 16:15 | Structural Engineering - Structural Engineering - General | 25000 |  | Workmanship | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | The cast in holding down bolts for the E__ canopy columns were installed 4 years ago. At the time the __ pre-cast bases were being installed (2017), these bolts have been re-surveyed by two different methods as well as the __ bases bolts. The results have shown inconsistent results. This suggests that the bolts are slightly out of tolerance.
| 03SR - Stations (RfL) | Cxxx-NCR-002657 | NCR | Attenuation tanks concrete pipe connection - GL 60 invert level |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-12-15 | 2017-11-24 16:56 | -21 | 2017-09-25 15:11 | Structural Engineering - Structural Engineering - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The 750mm dia. concrete pipe connection between attenuation tank units 15 and 16 (between GLs 58 and 60) has been installed on site as per the following drawings: Cxxx-SKC-D-DWG-B071_WS077-50012 Cxxx-SKC-D-DWG-B071_WS077-50022 Cxxx-SKC-D-DWG-B071_WS077-50023 Having installed the concrete pipe inside the 200x100mm recesses cast into units 15 and 16, there is a 10-20mm protruding edge between the invert level of the concrete pipe and the invert level of the attenuation tank units (as shown in the photo attached).
| 03SR - Stations (RfL) | Cxxx-NCR-002659 | NCR | Incorrect Drainage Levels (Lift 10 & 11) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-01-31 | 2017-11-24 16:40 | -68 | 2017-07-28 14:12 | Civil - Drainage | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | 1 no. drainage pipe has been installed in both Lift 10 & 11 respectively, the levels of the drainage terminate at the wrong level approx. 120mm above that of 104.310m SSL contrary to the that noted on Cxxx-SKC-M-DDA-M171_6-83212 and Cxxx-SKC-M-DDA-M171_6-83219 Detail 'C'. Refer 20170628_093327.jpg for photo.
| 03SR - Stations (RfL) | Cxxx-NCR-002660 | NCR | RC Core Intermediate GL20 Riser Return Wall Rebar Exposed |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-09-29 | 2017-10-12 10:09 | 13 | 2017-06-21 09:35 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Using the RC Coring Method for the RC Core on Section 18 - Drawing: Cxxx-SKC-Y-DDB-M171_3-69316 the return wall in the riser was made contact with. This led to the Reinforcement Cover being removed during the coring process. Upon inspection the Reinforcement was not damaged. Please see attached image. UPDATE: In response to Comment 21.06.17, this hole ISTR08, was an pre-existing opening which was enlarged to meet the new __ design. ISTR08 has been reviewed under 'Comment Sheet - __ GL 24-20 Cxxx Comments V2'. Final version attached.
| 03SR - Stations (RfL) | Cxxx-NCR-002661 | NCR | Winching Points - wall mounted fixings |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-07-09 | 2017-07-07 13:42 | -2 | 2017-06-25 10:08 | Structural Engineering - Inserts | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During installation of wall mounted winching points on Intermediate Level, the subcontractor used M16 __ HIT-HY 200 Injection Mortar with HIS-(R)N Sleeve fixings, but this material has not been accepted for use.
| 03SR - Stations (RfL) | Cxxx-NCR-002664 | NCR | Luminaire position has not been co-ordinated with the cable ladder Transformer Room III |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-03-31 | 2017-11-10 16:42 | -141 | 2017-06-30 13:40 | Electrical - Cable Management | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Luminaire position has not been co-ordinated with the cable ladder Transformer Room III
| 03SR - Stations (RfL) | Cxxx-NCR-002666 | NCR | TV Fan Room Intermediate East Perimeter Wall Debonding Mastic |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-10-31 | 2017-11-10 11:25 | 10 | 2017-07-05 14:23 | Architectural - Brickworks/Blockworks | 1500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | On Intermediate level East in TV FAN Room the LUL intrumescent sealant on the perimeter wall has debonded from the blockface and the soffit. Creating a gap between 1-3mm.
| 03SR - Stations (RfL) | Cxxx-NCR-002667 | NCR | VSHH - Bracketry Paint |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-10-13 | 2017-10-13 12:17 | 0 | 2017-07-04 08:22 | Civil - Civil Engineering General | 5000 |  | Manufacturing Defect | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | A number of the gable end brackets on the East VSHH have insufficient paint thickness and are showing signs of damage / rust. See attached quality report; in general, it seems the face plates of the bracketry do not comply with the minimum DFT requirement (275 microns).
| 03SR - Stations (RfL) | Cxxx-NCR-002668 | NCR | VSHH East - Isolation Tape |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-10-31 | 2017-10-11 13:25 | -20 | 2017-07-04 08:43 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The VSHH bracketry calls for aluminium shims/packers to be used for levelling purposes. These shims need to be isolated from potential bimetallic corrosion, as the bracketry material is stainless steel. Recent observations on the East VSHH shows a mixture of grey tape (visually looks like standard gaffer tape/cloth tape), black PVC tape and no tape at all.
| 03SR - Stations (RfL) | Cxxx-NCR-002669 | NCR | Screed breakout platform level |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-10-02 | 2017-07-28 12:13 | -66 | 2017-07-04 15:52 | Structural Engineering - Grouting | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | is breaking out screed in 2 No. locations (See attached details) on platform level. Location 1 (See location 1 detail) is on the south side of the Bakerloo box lift, and location 2 (see location 2 detail) is around the Paid lift pit. The reason for the screed to be broken out is to accommodate for ferrous scanning for base plate details, and post fixing for the glazing, which was not taken into account when placing screed in these areas.
| 03SR - Stations (RfL) | Cxxx-NCR-002670 | NCR | Brick slip - Horseshoe washers not bearing correctly to Concrete |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-10-04 | 2017-10-18 16:13 | 14 | 2017-07-06 13:09 | Architectural - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | The location for these horseshoe washers, is the bottom brackets of the Northern Brickslip lower level panels. Upon approval of Cxxx-FCD-002233 an inspection was undertaken of the horseshoe washers placed onto the brackets of the panels. These horseshoe washers are used to span the halfen channel and bear the load directly onto the concrete. The inspection showed (and photos attached) - show that the horseshoe washers do not bear directly onto the concrete - with some edges of the washer showing 2-5mm gap and some bearing onto the edge of the halfen channel. This has occured due to inconsistency of the halfen channels.
| 03SR - Stations (RfL) | Cxxx-NCR-002671 | NCR | Lift Shaft 10 Openings |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-09-30 | 2017-09-23 08:01 | -7 | 2017-07-11 11:53 | Civil - Structural Engineering | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | As per Cxxx-RFI-004035 it was noted that 2 no. openings in Lift Shaft 10 that Cxxx propose to fill in are not known to Cxxx. Please see below clarification as requested: - Opening cast in IL-T-02 has been captured on Cxxx-SKC-C-DWG-B071_WS077-51411 (X01); and - Opening cast in PL-L-02 is consistent with the space between the pre-cast coffer light sections in the Platform Level soffit and appears that Cxxx-SWN-S-DDC-M171_Z-04530 has been interpreted incorrectly resulting in the opening being cast in.
| 03SR - Stations (RfL) | Cxxx-NCR-002672 | NCR | East __ Terrace Canopy Hold Down Bolts - Concrete alterations |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-11-30 | 2018-01-08 11:37 | 39 | 2017-07-10 16:42 | Structural Engineering - Structural Engineering - General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Due to a number of issues regarding the installation of cast-in hold down bolts, shear Pin recess' and Canopy MEP services within the concrete foundations along the E__ side of the canopy, are currently unable to install a few of the columns and canopy MEP services as required. - Column Installation Clashes - In some locations, the 250 x 250mm Shear Key void clashes with the shear pin on the base plate of the columns. This either prevents the column from being installed in the correct location completely, or will prevent the required minimum grout from being installed around the shearkey. - Canopy Services Installation - - Similar to the shear keys, a number of raceways installed to allow for services installation for the Canopy are cast in the wrong position to align with the openings in the base plates. This prevents the services from being correctly installed to supply Power and Water to the canopy.
| 03SR - Stations (RfL) | Cxxx-NCR-002673 | NCR | Canopy - MMH Hold Down bolts |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-12-30 | 2017-11-24 16:31 | -36 | 2017-09-01 12:00 | Structural Engineering - Bolted Connections | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Due to incorrect details shown on the precast-fabrication drawings, column hold down bolts along MMH side of the main canopy are installed too short. Allowing for installation tolerances on the bolts, as well as on the foundations, the average total bolt protrusion from concrete slab is 147mm. From the __ design drawings, the design thickness of the hold down items (grout, base plate, washers and nuts) is 166mm plus 15mm of spare thread as per NSSS.
| 03SR - Stations (RfL) | Cxxx-NCR-002674 | NCR | East VSHH - Incomplete Grout Pads |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-09-30 | 2017-10-13 14:55 | 13 | 2017-07-28 10:20 | Civil - Structural Engineering | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | observed the subcontractor __ preparing and pouring grout for the steel column bearing pads, which were located at the Chiller Farm area. See attached map for location references. Timber shutters had been prepared and sealed with silicon. inspected and noted that columns CE7 & CE15 had existing grout underneath the steel baseplates, but were partially poured. When it was clear that __ intended to 'top up' the old grout, immediately contacted the __ supervisor to stop the works.
| 03SR - Stations (RfL) | Cxxx-NCR-002676 | NCR | JM41 Public Tile (Granazzo) Testing Not Compliant with Specification JM41.2200 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-02-25 | 2018-06-15 15:26 | 110 | 2017-07-20 15:30 | Architectural - Flooring | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Following a CRL surveillance on the Granazzo Tile Manufacturer it was found that the testing is not compliant with the specification JM41.2200 (see attached email). to propose Action Plan following communication with the Specialist subcontractor.
| 03SR - Stations (RfL) | Cxxx-NCR-002677 | NCR | West VSHH - Steel Installation Damage |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-12-18 | 2018-02-02 17:14 | 46 | 2017-07-21 12:28 | Civil - Civil Engineering General | 2500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Damage has been observed around the West VSHH steelwork and concrete nibs; initial investigation shows damage has been caused where steel shims or packers have been used to assist in installing the steel columns. Concrete nibs have suffered spalling damage and the rear face of the columns have damage to the protective paint coating.
| 03SR - Stations (RfL) | Cxxx-NCR-002678 | NCR | Damage to RC Wall During Coring Operation |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-10-07 | 2017-10-20 09:52 | 13 | 2017-08-08 09:48 | Structural Engineering - Concrete Member | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Damage sustained to top of __ during core drilling works.
| 03SR - Stations (RfL) | Cxxx-NCR-002679 | NCR | Manufacture of Bracketry without ITPs |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-04-04 | 2018-02-07 16:26 | -56 | 2017-07-28 11:35 | Civil - Civil Engineering General | 1500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The subcontractor has manufactured and installed two types of bespoke brackets without having approved ITPs in place. Brackets are part of the external cladding system for both East & West Vent Shaft Head Houses and include a stainless steel bracket along the north/south walls and a painted steel bracket on the gable ends.
| 03SR - Stations (RfL) | Cxxx-NCR-002681 | NCR | Contractor not Accredited to carryout Firestoping |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2017-09-27 | 2017-12-21 16:01 | 85 | 2017-07-28 14:34 | Architectural - Brickworks/Blockworks | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Whilst carrying out a planned surveillance on fire stopping on the 13/07/2017, it was found that the Blockwork Sub-Contractor Lee Marley had carried out the fire stopping to the vertical and horizontal joints, but was not an Accredited Firestop Company.
| 03SR - Stations (RfL) | Cxxx-NCR-002682 | NCR | Fire stopping not installed to the Specification. |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2017-09-26 | 2017-11-06 08:47 | 41 | 2017-07-28 14:44 | Architectural - Brickworks/Blockworks | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Whilst carrying out a planned surveillance on fire stopping on the 13/07/2017, it was witnessed that the vertical block work fire stop mastic joints are recessed. The Contractor stated that __ had recommended that the mastic joint be recessed as opposed to the specified flush finish.The Contractor was unable to provide evidence of the recommendation.
| 03SR - Stations (RfL) | Cxxx-NCR-002683 | NCR | __ Platform 12 Waiting Room - Fire Retardant Treated Timber Backing Matieral |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-08-17 | 2017-08-14 15:33 | -3 | 2017-08-03 12:19 | Architectural - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During an onsite inspection (IRF) of general building works progress of the platform 12 waiting room, it was queried by a Crossrail lead field assurance engineer whether or not a specific material element of the front facade was of a particular fire retardant class. The specific material in question was the fire retardant treated timber backing board. In response to this raised query, site engineer contacted the subcontractor to speak to the supplier of the material to confirm it was fire retardant and of what class. It was confirmed that the material was fire retardant and the right level being class 0 /class B. During this check it was identified that the material was not covered by an in place & approved MCR.
| 03SR - Stations (RfL) | Cxxx-NCR-002685 | NCR | Canopy - Paintwork Damage |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-05-17 | 2018-05-02 09:34 | -15 | 2017-08-04 13:45 | Architectural - Finishes | 5000 |  | Damaged | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Some of the steelwork for the main canopy has damage to the paintwork. This has occurred during transportation to site
| 03SR - Stations (RfL) | Cxxx-NCR-002686 | NCR | TV-Fan I (#779) – 75mm x 75mm single compartment trunking close to top tray |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2017-10-31 | 2017-11-03 12:57 | 3 | 2017-08-04 12:06 | Electrical - Earthing & Bonding | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | 75mm x 75mm single compartment trunking (believed to be Signals?) is installed to close to the top tray (less than 50mm). This has been bought up previously, in weekly walk around and the CEG site visit.
| 03SR - Stations (RfL) | Cxxx-NCR-002687 | NCR | TV-FAN I (#779) – 75mm x 75mm single compartment trunking (believed to be Signals?) 90 degree gusset bend at riser end of room. |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2017-10-31 | 2017-11-03 12:59 | 3 | 2017-08-07 09:56 | Electrical - Cable Management | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | 75mm x 75mm single compartment trunking (believed to be Signals?) 90 degree gusset bend at riser end of room appears to be a very tight bend for the cable sizes and types to be installed within. (See attached photo).
| 03SR - Stations (RfL) | Cxxx-NCR-002689 | NCR | Architectural acoustic requirements for the louvre system. (Spec Ref JH43.1204) on the East and West sides of intermediate Level |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2017-10-06 | 2017-12-18 17:06 | 73 | 2017-08-07 11:27 | Architectural - Finishes | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | It has become apparent that the gated design for the Intermediate level Louvres does not comply with acoustic performance requirements set forth by Cxxx. Cxxx are responsible for acoustically modelling the space for the design of the PA/VA systems The current gated design for the louver ‘blade’ forms in essence a solid ‘wall’ for sound and hence the louvre design as shown at the bottom of the sketch will only achieve Class D (alpha_w 0.4).
| 03SR - Stations (RfL) | Cxxx-NCR-002692 | NCR | Incorrect Finished Concrete Level Lift 10 & 11 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-11-30 | 2017-11-24 16:38 | -6 | 2017-08-17 08:51 | Civil - Structural Engineering | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Whilst conducting a level survey of Lifts 10 & 11 it has become apparent that the finished concrete level of the lift pit is currently too high. As per drawings Cxxx-SWN-S-DDB-M171_Z-04566 and Cxxx-SWN-S-DDB-M171_Z-04569, the concrete level of the pits should be 104.310m. On site the concrete surface (in certain areas) is approximately 4mm and 6mm too high for Lift 10 & 11 respectively.
| 03SR - Stations (RfL) | Cxxx-NCR-002694 | NCR | Inadequate toothing of lintel into corridor blockwork in the ESR II room |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-09-15 | 2017-09-19 08:19 | 4 | 2017-08-16 10:35 | Architectural - Brickworks/Blockworks | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | In the ESR II return wall there is lintel that is toothed into the corridor wall to acommodate a new __ . From inspection on the other side there is no visibility of the lintel flush with the blcokwork face on the corridor. This implies the lintel isnt toothed to the full depth of the corridor blockwork.
| 03SR - Stations (RfL) | Cxxx-NCR-002695 | NCR | ITP - bronze panels - manufacture |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-10-16 | 2017-10-16 15:49 | 0 | 2017-08-17 17:15 | Architectural - Finishes | 5000 |  | Documentation and Records | Rework | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | ITP - bronze panels - off site manufacture, not submitted to cover the panels fabrication.
| 03SR - Stations (RfL) | Cxxx-NCR-002696 | NCR | Base track - Unpaid lift - enlarged holes |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-11-16 | 2017-11-24 17:06 | 8 | 2017-08-18 16:14 | Civil - Civil Engineering General | 2500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | notes that __ subcontractor enlarge some holes (see attached photos for evidence) on the stainless steel angle plates, for the glazed track on the Unpaid lift 6-7 to accommodate the cast in threaded bar (cast in by others). Apparently, no site and steel tolerances were considered during design phase and consequent manufacture.
| 03SR - Stations (RfL) | Cxxx-NCR-002697 | NCR | Cracking to Blockwork when Drilling/Fixing into for __ Board System |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-10-09 | 2017-08-25 13:22 | -45 | 2017-08-20 14:32 | Architectural - Brickworks/Blockworks | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the installation of the __ board system to service penetrations into the SER and __-R CWU, the blockwork has cracked that will require replacement. The cracking into __-R CWU occurred during the tightening of the fixings and the cracking into SER occurred during the drilling of the pilot holes.
| 03SR - Stations (RfL) | Cxxx-NCR-002699 | NCR | Unpaid lift - internal angles - alignment |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-11-18 | 2017-11-06 11:16 | -12 | 2017-08-23 16:43 | Architectural - Finishes | 1500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | notes that due to a design/manufacture error the internal SS clamping angle is not aligned (in height) with the external clamping plate (only on the landing areas/architrave level) The proposed remedial solution was agreed with CRL architects during a site visit and attached to the NCR.
| 03SR - Stations (RfL) | Cxxx-NCR-002700 | NCR | Late provision of spares list |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-09-30 | 2017-09-16 08:01 | -14 | 2017-08-24 14:11 | Information Management | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The WI requires the Contractor to provide a spares list to the PM for acceptance no later than 365 days prior to completion. Planned completion is 3rd August 2018 and at 22nd August 2017 the spares list is still outstanding.
| 03SR - Stations (RfL) | Cxxx-NCR-002701 | NCR | Incorrect fire-rating lintels installed in the CER I CWU & CER IV CWU |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-09-18 | 2017-09-22 14:43 | 4 | 2017-08-24 13:53 | Architectural - Brickworks/Blockworks | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 1 hour fire-rated lintels have been installed in the CER I CWU and the CER IV CWU. These rooms are 2 hour fire-rated.
| 03SR - Stations (RfL) | Cxxx-NCR-002702 | NCR | TATA 'Install Plus Pipework' Delivered out of tolerance. |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-12-31 | 2017-11-06 10:21 | -55 | 2017-08-25 09:10 | Mechanical - Mechanical Engineering General | 1500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | __ 'Install Plus 235 Pipework' is supplied 'pre-grooved'. During a sample __ dimensional check it was found that a number (32 off - with date codes 1017 - 1317) of the grooved ends are out of tolerance to receive the __ couplings - as demonstrated by using the VICTAULIC GROOVE GAUGE. Out of tolerance pipes are to be separated and quarantined so the supplier (TATA) can inspect the non-conforming items. This to include the section of pipework all ready installed. Going forward the __ groove gauge will be used 100% of the time to inspect all deliveries of this product.
| 03SR - Stations (RfL) | Cxxx-NCR-002703 | NCR | West VSHH - Saddle Plates |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-10-13 | 2017-10-13 13:14 | 0 | 2017-08-29 09:59 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | When installing the structural steel on the West VSHH, there were two locations in which the steel saddle plates did not fit on top concrete correctly. To allow the installation to proceed, the saddle back plates were cut off with a grinder. Refer to drawing sketch for details.
| 03SR - Stations (RfL) | Cxxx-NCR-002704 | NCR | Incorrect Finished Concrete Level on Intermediate Support (Esc 1-5) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-11-30 | 2017-11-08 13:48 | -22 | 2017-08-26 14:39 | Mechanical - Escalators | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The intermediate supports of Escalator 1-5 have been constructed too high. As per drawing Cxxx-SWN-S-DDB-M171_3-04010, the concrete level of the intermediate support should be 115.395m. The attached asbuilt of the finished concrete works show that in a worst case scenario the highest point of the intermediate support is 115.400m, 5mm higher than design. This will not allow or the minimum packing to be installed during line and levelling of these escalators. Escalators 1-5 cannot be lifted in the same manner to grind the concrete down to level as was done in Cxxx-NCR-002498 and Cxxx-NCR-002613, and in this instance it is proposed that the intermediate supports will be used as is. -RFI-002250 was submitted to __ to confirm that using the intermediate supports as is would not adversely affect the running operation of Escalators 1-5. In reply to -RFI-002250, __ have proposed to change the 15mm plate (__ Part# GAA386DAP-L816) to 8mm thickness, where the supports are the worst at 5mm high these will still allow for 2mm of packing to be installed. This proposal has been accepted by both __ (CEG) and __ (LU) as per the attached.
| 03SR - Stations (RfL) | Cxxx-NCR-002705 | NCR | Attenuation tanks - Construction of drainage connections to P status drawing |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-12-04 | 2017-11-25 11:30 | -9 | 2017-08-29 11:12 | Civil - Drainage | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The rocker pipe drainage connections between the canopy foundations (GLs 50-90) and the attenuation tank units (units 01-60) have been installed using details A and B on drawing Cxxx-SKC-D-DDD-M171_1-01546 revision P08.
| 03SR - Stations (RfL) | Cxxx-NCR-002706 | NCR | Incorrectly Fabricated Gutter End Stops |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-11-03 | 2017-10-13 13:20 | -21 | 2017-09-04 12:29 | Civil - Civil Engineering General | 1500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Two gutter end stops were delivered to site incorrectly fabricated with the end walls on the opposite side. This means the end stop sections currently have the incorrect fall and gutter outlet offset.
| 03SR - Stations (RfL) | Cxxx-NCR-002707 | NCR | Canopy - Signs of Corrosion between Main Rafter and Stainless Steel Brackets |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-01-09 | 2017-12-13 17:10 | -27 | 2017-09-01 09:05 | Structural Engineering - Surface Treatment | 5000 |  | Workmanship | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | There are signs of corrosion around the joint where the stainless steel brackets are welded to the main rafters.
| 03SR - Stations (RfL) | Cxxx-NCR-002708 | NCR | Attenuation tank UNIT 58 - Construction joint cracks |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-10-13 | 2017-10-13 15:04 | 0 | 2017-09-05 12:07 | Civil - Drainage | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Attenuation tank UNIT 58 (Type B5) has been delivered to site with two cracks along the construction joints of the North-South tank walls (see 'Atten tanks delivery checks 01.09.17' and photos 'IMG_3917 to IMG_3934'). __ have identified the cracks as being 'not indicative of any significant structural issues...[but] from a durability and potential leakage perspective, the width of the cracks is excessive'. A repair proposal shall follow.
| 03SR - Stations (RfL) | Cxxx-NCR-002709 | NCR | ITP - Cxxx-SKC-Z-ITP-B071_WS077-50004 - grout activity |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-11-16 | 2017-10-13 15:06 | -34 | 2017-09-07 08:26 | Civil - Civil Engineering General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Grout activity not included on the ITP - Cxxx-SKC-Z-ITP-B071_WS077-50004_rev5.0_code1. to resubmit rev 6.0 ITP. However the grout activity is included on the check sheets procedure. (see attached)
| 03SR - Stations (RfL) | Cxxx-NCR-002710 | NCR | PES Framework - Drypack insufficient packing |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-12-14 | 2018-01-20 11:07 | 37 | 2017-09-06 15:48 | Structural Engineering - Structural Engineering - General | 25000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During trials to prove the correct installation of the dry-pack for the PES frame, it was shown to have voids within the frame. The specification requires complete compaction / packing and to not leave voids. It was also noted that bonding to existing surfaces was also considered unsatisfactory.
| 03SR - Stations (RfL) | Cxxx-NCR-002711 | NCR | VSHH - Stainless steel Brackets fabricated without an accepted DDCD |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-01-31 | 2018-01-26 09:32 | -5 | 2017-09-06 17:35 | Structural Engineering - Structural Engineering - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | The stainless steel brackets for the VSHH cladding have been fabricated without an accepted DDCD. These are the same brackets which are subject to Cxxx-NCR-002679
| 03SR - Stations (RfL) | Cxxx-NCR-002712 | NCR | VSHH - Incorrect installation of bracketry |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-01-31 | 2018-01-22 08:34 | -9 | 2017-09-06 17:47 | Structural Engineering - Structural Engineering - General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | It has been identified that some of the bracketry for the cladding on the east Vent Headhouse has been installed incorrectly. This has included the bolts and washers installed incorrectly
| 03SR - Stations (RfL) | Cxxx-NCR-002713 | NCR | Rust Staining |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-04-30 | 2018-02-12 15:10 | -77 | 2017-09-12 14:19 | Architectural - Finishes | 2500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Some brown rust staining has occurred under locations where structural steel welding, grinding and grit blasting has occurred. Potential cause of issue is the minor iron content of the brown alumina grit or grinding/welding residue. Some particular concrete surfaces have significant brown staining.
| 03SR - Stations (RfL) | Cxxx-NCR-002715 | NCR | Weld testing has been carried out by a non UKAS Accredited Company without Crossrail Acceptance |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2017-10-09 | 2017-10-13 12:45 | 4 | 2017-09-11 09:03 | Structural Engineering - Testing | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | A planned surveillance of the Canopy installation in Departures Road was carried out on the 23rd August 2017. During the a post surveillance review of on-site weld testing it was found that __ that carried out the Visual and Dye Penetrant and __ that carried out the Ultrasonic testing weld testing on the Departures Road Canopy Steelwork are not UKAS Accredited. Both Companies’ are conducting onsite weld testing on behalf of Cornelius UK who is carrying out the welding for Wagner Biro. The Contractor was unable to provide evidence of the Project Managers acceptance to an alternative testing proposal.
| 03SR - Stations (RfL) | Cxxx-NCR-002716 | NCR | Ductwork Grills within the CER rooms |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-07-31 | 2017-10-07 11:15 | -297 | 2017-10-05 07:12 | Materials - Approval | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Duct work Grills do not have an approved MCR
| 03SR - Stations (RfL) | Cxxx-NCR-002717 | NCR | Attenuation tank UNIT-59 - Rebar dowel openings |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-10-20 | 2017-10-07 11:19 | -13 | 2017-09-14 09:42 | Civil - Drainage | 500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Attenuation tank unit 59 (Type C1) has been cast with the rebar dowel sleeves in the wrong positions. Please see attached drawing (Attenuation tank unit 59 dowel sleeve positions) that illustrates the non-conformance. The drawing shows the following: - Tank units 59+60 drawn in pencil, with the as-built dowel sleeve positions shown in black. - Lid units 56+57, with the as-built dowel sleeve positions, shown in red. - Design position of the dowel sleeves for unit 59 and lid 56 shown in blue (to demonstrate that lid 56 has been cast correctly).
| 03SR - Stations (RfL) | Cxxx-NCR-002718 | NCR | Incorrect drawing revisions used on site |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-07-31 | 2018-06-20 12:25 | -41 | 2017-09-19 14:41 | Electrical - General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Surveillance check carried out on sub-contractors of CMS & Bracketry drawings to check correct revision being used as issued on RIR 15. Drawings Cxxx-SKC-Y-DDB-M171_5-63501-C03 & Cxxx-SKC-Y-DDB-M171_5-63550-C04 were meant to be in use-Rev's 02 (5-63501) & 03 (5-63550). The subcontractor was using the incorrect revision
| 03SR - Stations (RfL) | Cxxx-NCR-002719 | NCR | Vertical glass fins - Bolts - Unpaid lift shaft |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-09-30 | 2018-11-05 16:17 | 36 | 2017-09-19 12:04 | Architectural - Finishes | 500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Due to the missing holes on the vertical glass panel, as per the attached mark-up drawings and photos, notes that some of the M10 CSK, have been missed from the stainless steel clamping system. notes the lack of access which will compromise and limit the fixings options.
| 03SR - Stations (RfL) | Cxxx-NCR-002720 | NCR | Canopy foundation GL 86 drainage connection |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-10-27 | 2017-10-13 12:15 | -14 | 2017-09-19 14:09 | Civil - Drainage | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The top canopy foundation unit at GL 86 on Departures Road Level has been cast with the 100mm Timesaver pipe connection fixed 15mm lower than the intended design position (see drawing 50038). Drawing 'GL 86 pipe levels', as attached, shows that the pipe run between the cast in connections at foundation GL 86 and tank unit 54 has a back-fall from the tank to the canopy foundation (8mm change in level over approximately 2m length of pipe).
| 03SR - Stations (RfL) | Cxxx-NCR-002721 | NCR | Incorrect Finished Concrete Level Lift 12 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-11-30 | 2017-11-24 14:56 | -6 | 2017-09-25 11:29 | Civil - Structural Engineering | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Whilst conducting a level survey of Lift 12 it has become apparent that the SSL concrete level of the lift pit is currently too high. As per drawings Cxxx-SWN-S-DDB-M171_Z-24201 (X01), the concrete level of the pits should be 98.460m. On site the concrete surface (in certain areas) is approximately 10mm and 20mm too high for Lift 12 respectively.
| 03SR - Stations (RfL) | Cxxx-NCR-002722 | NCR | Replacement of blockwork Around installed permanent door frames |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-03-30 | 2018-07-24 09:39 | 116 | 2017-09-28 09:37 | Architectural - Doors | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During re-design for MEP services existing services needed to be removed from blockwork adjacent to permanentently installed doors. This damaged the blockwork signficantly so that the blocks required to be replaced. As the Lintel was required to be temporarily supported - the mastic / sealant needed to be removed. Therefore the assurance of the door will be voided.
| 03SR - Stations (RfL) | Cxxx-NCR-002723 | NCR | Brickslip - Exposed Dowel bars - top of panels |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-06-27 | 2018-08-20 07:43 | 54 | 2017-09-28 10:11 | Architectural - General | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | The Dowel bars used for attaching the Brickslip panels to the D-wall do not have sufficient cover to the top of the brickslip panel within the grouted tubes. This is evident along the top of the Brickslip panels.
| 03SR - Stations (RfL) | Cxxx-NCR-002724 | NCR | Metalwork - Combined Service Riser - gille clash with drain pipe |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-06-01 | 2019-12-23 10:39 | 570 | 2017-09-29 15:44 | Architectural - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the DDCD review process of __ steelwork, a drain pipe detail coming through a concrete ledge in the Concourse East combined service riser room has been missed. __ manufactured the grille as per the approved design and in order to accommodate the site condition and not delay the completion of the works, they have cut around to allow the drain pipe to go through and applied zinc paint locally. After discussions with __, this drain pipe should not have been above FFL level of the grille, but to finish above SSL level having a cover on the top. An RFI has been raised to __ for clarification and waiting the formal response.
| 03SR - Stations (RfL) | Cxxx-NCR-002725 | NCR | CER I, II & IV Rooms Unprotected Panels |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-06-02 | 2018-05-24 13:27 | -9 | 2017-10-04 06:42 | Electrical - Electrical Engineering General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | CER Rooms I, II & IV Installed Panels unprotected and subsequently sustained surface damage see pictures
| 03SR - Stations (RfL) | Cxxx-NCR-002726 | NCR | Drawing/Document Control |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-06-30 | 2018-09-18 13:16 | 80 | 2017-10-04 13:45 | Electrical - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | RIR/Drawing control. Site operative (EMICO) are currently working to superseded drawings, in Room SRLVIIB and MCCI- EMICO are currently installing to Drawing Numbers; SRLVIIB Cxxx-SKC-Y-DDA-M171_3-63214 CO3 RIR 4 (22.06.2017) Photo evidence attached Cxxx-SKC-Y-DDA-M171_3-63605 CO5 RIR 4 (22.06.2017) Photo evidence attached Cxxx-SKC-Y-DDB-M171_3-63246 CO3 RIR 4 (22.06.2017) Photo evidence attached Cxxx-SKC-Y-DDB-M171_3-63243 CO3 RIR 4 (22.06.2017) Photo evidence attached Latest drawing up rev’d and issued under RIR22 30.08.2017 issued under SIO1573: Cxxx-SKC-Y-DDA-M171_3-63214 CO4 Cxxx-SKC-Y-DDA-M171_3-63605 CO6 Cxxx-SKC-Y-DDB-M171_3-63246 CO4 Cxxx-SKC-Y-DDB-M171_3-63243 CO4 MCCI Cxxx-SKC-Y-DDA-M171_3-60501 CO2 RIR 22 (03.08.2017) Photo evidence attached Cxxx-SKC-Y-DDA-M171_3-63612 C02 RIR 18 (18.07.2017), Latest drawing up rev’d and issued under, RIR24 (18.09.2017) and RIR 25 (20.09.2017): Cxxx-SKC-Y-DDA-M171_3-60501 CO3 RIR 27 (25.09.2017) Cxxx-SKC-Y-DDA-M171_3-63612 C03 RIR 24 (18.09.2017) + C04 RIR 25 (20.09.2017) RIR Rev 28 attached.
| 03SR - Stations (RfL) | Cxxx-NCR-002727 | NCR | RCP Concourse - Removal of Concrete nib Precast Service Cover SC06 East GL14 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-11-30 | 2017-12-02 08:38 | 2 | 2017-10-05 07:06 | Structural Engineering - Pre-cast | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Return nib cast at end of unit prohibits fitting of coffer lighting trunking to head of precast service cover SC06. Concrete nib to broken out and face of concrete to be made good with Monomix HD to enable lighting trunking to be installed as per design.
| 03SR - Stations (RfL) | Cxxx-NCR-002728 | NCR | Failure to comply with the IRF Process |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-11-30 | 2018-05-24 13:33 | -190 | 2017-10-06 08:19 | Electrical - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Failure to comply with the CRL IRF Process. Fibre Cable installation has taken place without a CMS IRF being raised or CMS inspections taking place in riser locations and the Intermediate West location Fibre Route - installation without a IRF being raised/offered or accepted by and CRL. __ in-house Quality Team have raised a NCR also identifying and addressing this __-NCR-000059 Applicable ITP reference: Cxxx-SKC-E-ITP-B071_WS077-50008 Installation of Support Bracketry and Cable Management System Activities 4.1, 4.2, 4.3 & 4.4
| 03SR - Stations (RfL) | Cxxx-NCR-002729 | NCR | Hole Reference 3-433 - Poor Workmanship - __ Firestopping |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-11-25 | 2017-10-13 13:47 | -43 | 2017-10-06 13:23 | Fire - Compartmentation | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following a review of some completed __ boarding firestopping installation, poor workmanship has been recognised that was not able to be rectified within the same shift. The cover board on one side of the aperture protrudes into the opening that exceeds the allowable tolerance for the BSK4 damper install. The board is to be removed, altered to the correct dimensions and then reinstalled.
| 03SR - Stations (RfL) | Cxxx-NCR-002730 | NCR | VSHH West Base Plate Misalignment Bolt CW20 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-12-31 | 2018-02-02 17:16 | 33 | 2017-10-10 11:40 | Civil - Civil Engineering General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | During the installation structural steel for the West Went House, post fixed bolts had been installed in incorrect centers and clashed with the steel base plate. To enable critical works to proceed, the clashing bolt was cut down and coated with Zincrich __ Plus, resulting with the steel base plate installed with one bolt installed.
| 03SR - Stations (RfL) | Cxxx-NCR-002731 | NCR | Working to P Status Drawing |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-12-31 | 2018-08-29 15:52 | -124 | 2017-10-11 11:00 | Electrical - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | Drawing No. Cxxx-SKC-Y-DDB-M171_4-63422 is issued as a P01 status drawing within this IRF Cxxx-IRF-0217 OHLE CR2 (As agreed with CRL).
| 03SR - Stations (RfL) | Cxxx-NCR-002732 | NCR | Unpaid Lift Waterproofing - Hold points not adhered to |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-11-05 | 2017-11-03 14:37 | -2 | 2017-10-16 14:40 | Architectural - Finishes | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During installation of waterproofing in and around the bolt clusters for the Unpaid Lift Bridge, the hold points in the waterproofing ITP (Cxxx-SKC-Z-ITP-B071_WS077-50168) were not adhered to, and the installation continued without CRL inspection.
| 03SR - Stations (RfL) | Cxxx-NCR-002733 | NCR | Canopy - N__ Testing 16/10/2017 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-01-31 | 2018-01-20 11:11 | -11 | 2017-10-17 16:53 | Structural Engineering - Welding | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | On-site N__ testing was completed on a number of Canopy Column welded connections on 16/10/2017. From the Ultrasonic testing completed, a number of locations were identified as having internal imperfections in the on-site completed butt welds. __ welding sub-contractor was in attendance during the testing to document all defects identified. Defects were identified on different welds on the following connections - MMH Column - GL 78 (Joint 15) - E__ Columns - GL 82 (Joint 26), GL 80 (Joint 27), GL 78 (Joint 28), GL 54 (Joint 40), GL 52 (Joint 41), GL 50 (Joint 42)
| 03SR - Stations (RfL) | Cxxx-NCR-002734 | NCR | CER Distribution Boards - __ |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-09-28 | 2019-08-22 13:41 | 328 | 2017-10-19 11:46 | Electrical - General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | __ protection design within the CER distribution boards requiring to be reworked due to the __ design not taking into account the latest Cxxx cabinet __ information.
| 03SR - Stations (RfL) | Cxxx-NCR-002735 | NCR | Void in Intermediate level Soffit GL17-18 to Departures road (CIR-PL XVIII 128) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-12-29 | 2017-11-18 10:31 | -41 | 2017-10-23 08:31 | Civil - Civil Engineering General | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A 100mm void is located within the Intermediate level Soffit GL17-18 to Departures road (CIR-PL XVIII 128). It is unknown what this void is for as its not required for MEP works. Upper level of void has been filled and waterproofed over on Departures road as shown through historical photos.
| 03SR - Stations (RfL) | Cxxx-NCR-002736 | NCR | Brickslip - Staining to Acoustic holes |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-12-07 | 2017-12-21 16:36 | 14 | 2017-10-23 14:41 | Architectural - Brickworks/Blockworks | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | It has been noted there is some staining to the back of the Acoustic holes on the Northern brickslip panels. It appears to be a staining to the mesh from the brick interface with the rockwool
| 03SR - Stations (RfL) | Cxxx-NCR-002737 | NCR | Bronze cladding acoustic design not co-ordinated nor in accordance with gated design |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2018-06-27 | 2018-05-24 12:23 | -34 | 2017-10-24 11:48 | Architectural - Finishes | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | The acoustic absorption associated with the __ bronze cladding is not in accordance with the gated design, nor is it co-ordinate with the acoustic report as required by the works information
| 03SR - Stations (RfL) | Cxxx-NCR-002738 | NCR | Un-Approved Material used on site |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-07-30 | 2018-10-17 13:09 | 79 | 2017-10-25 14:00 | Materials - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Spray adhesive (ULTRA - Spraytack Multi-purpose Aerosol Adhesive) used by __ Laggers without an accepted MCR in place, __ raising their own internal NCR (tba). Area of usage understood to be CER I/II & IV... Product to be MCR approved, if not acceptable effected area to be removed and replaced using approved materials.
| 03SR - Stations (RfL) | Cxxx-NCR-002739 | NCR | Use of un-approved IMO Isolators |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-06-24 | 2018-08-10 12:37 | 47 | 2017-10-26 07:27 | Electrical - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 5 x IMO 40amp Isolators in CER I (2) & CER II (3) installed as temporary items, correct Isolators (Cxxxt) to be installed at a later date in coordination with Cxxx.
| 03SR - Stations (RfL) | Cxxx-NCR-002740 | NCR | On-site drawing control |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-05-30 | 2018-09-12 15:39 | 105 | 2017-10-30 12:08 | Electrical - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | __ Site operatives working to a superseded drawing - Cxxx-SKC-Y-DDB-M171_4-63540 CO1, Superseded by CO2 under RIR 25.0 on 20.09.2017...
| 03SR - Stations (RfL) | Cxxx-NCR-002742 | NCR | water leakage in BLL box |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2018-08-03 | 2018-08-03 14:30 | 0 | 2017-11-03 16:08 | Civil - Structural Engineering | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The BLL box is designed to resist the ingress of groundwater. Injection grouting has been carried out in the past which appeared to resolve the problem, however H2Ox have recently been in to grout up further leakage. This further leakage was not highlighted by the , but discovered by the Project Manager's team during an inspection, hence the NCR has been raised by the Supervisor's Representative
| 03SR - Stations (RfL) | Cxxx-NCR-002743 | NCR | Corrosion of fixing accessories in HV trench |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2017-12-01 | 2017-11-15 17:25 | -16 | 2017-11-03 16:13 | Electrical - Cable Management | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | The unistrut in the HV trench was installed in stainless steel due to the damp environment. The fixings however were not stainless and corroded in the past year.
| 03SR - Stations (RfL) | Cxxx-NCR-002745 | NCR | Alteration to Installed SHS Windpost (IWF-151) due to Changing MEPH Design |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-02-12 | 2017-12-01 13:48 | -73 | 2017-11-04 12:48 | Structural Engineering - Structural Engineering - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Due to the continually changing MEPH design, the SHS windpost located within the 60 minute compartment wall at gridline 8.5 on the intermediate corridor, will need to be altered. The changes to be made are shown in the attached document ref.: IL Windpost IWF151 Angle Removal and includes the removal of the welded halfen channel, the welded angle to support the blockwork lintel and alteration to the deflection joint. The attached document ref.: Cxxx - Windpost bracket F1575-SK-0001 shows the new detail for the deflection head and document ref.: -RFI-02626 response shows the assurance of this detail by __. All work to this windpost will be carried out by __ (windpost manufacturer) and therefore the CE marking is not affected. As agreed with __, this NCR will be closed out upon completion of the work.
| 03SR - Stations (RfL) | Cxxx-NCR-002746 | NCR | Incorrect AMTEC Schedules |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-07-28 | 2018-11-12 12:38 | 107 | 2017-11-06 09:08 | Electrical - Electrical Engineering General | 50000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | incorrect AMTEC schedules issued
| 03SR - Stations (RfL) | Cxxx-NCR-002747 | NCR | Unpaid Lift - Guide Rail Bracket Missing |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-01-22 | 2018-01-28 10:41 | 6 | 2017-11-07 13:05 | Structural Engineering - Steel Member | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | During an inspection on the Unpaid Lift shaft (6&7), it was identified that a guide rail bracket required by __ is missing. Please see attached picture of on site condition(Missing guide rail bracket Unpaid Lift.JPG), and a marked up C02 3D view drawing (Cxxx-SKC-Y-DDD-M171_Z-42007-C02 Missing guide rail bracket mark-up.pdf).
| 03SR - Stations (RfL) | Cxxx-NCR-002748 | NCR | Precast Brickslip - Non compliant nominal cover to reinforcement |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-02-28 | 2019-08-30 10:51 | 548 | 2017-11-08 11:55 | Architectural - Brickworks/Blockworks | 50000 |  | Workmanship | Rework | 2 (6-60k) | Complete | Design Problem - Other | Completed |  | With reference to the attached Brick-faced Precast Concrete Panels report (Ref. REF/257951/R001), section 12 - Commentary. The quality control records do not record actual measurements of cover to reinforcement, just a tick in a box, but no failures (i.e. a cross in the box) were recorded. Measurements of cover, performed by on a random sample of 13 in situ panels where some access to the rear of the panels was possible, showed (section 6.2) higher than expected variation for precast concrete produced under factory conditions. The nominal 25mm cover was achieved in just 9 of the 13 panels measured. Moreover, in 4 of the 13 panels there were significant instances of cover below the required 20mm minimum, with the lowest cover recorded as low as 15.2mm
| 03SR - Stations (RfL) | Cxxx-NCR-002749 | NCR | Counterweight bracket - __-__ - holes misalignment - Lift 12 and Lift 6-7 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-03-08 | 2019-03-23 10:27 | 380 | 2017-11-10 14:48 | Civil - Civil Engineering General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | During the installation of the __ brackets (only affecting the counterweight) and as per the attached photos, it has become apparent that there's a hole misalignment on the __ counterweight bracket. Further details of the NCR are now being investigated by design team.
| 03SR - Stations (RfL) | Cxxx-NCR-002750 | NCR | TR I - __ Hus Fixings |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-08-15 | 2018-09-06 15:04 | 22 | 2017-11-11 12:41 | Electrical - General | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On 10.11.2017 at 21.00 Night Time Supervisor attended TR I __ had planned works in that area. Noted on top of __ ECO model number 62 there were 4 x __ HUS fixing that had been cut down in size. There are hacksaw marks along the bolt where somebody has tried to cut them down (see pics). MEWP pre-use checklist reviewed to ascertain who last used the ECO, however it had not been completed. A review of the WAD Permits for that room showed both __ and __ had works in the West HV Corridor Rooms. __ advised the ECO was in the room at the start of the shift. NOTE:__ have been installing steelwork installed along the HV Corridor this week and also use these fixings.
| 03SR - Stations (RfL) | Cxxx-NCR-002751 | NCR | PES Frames - Missing pre-drilled holes in Web for beams |  | Contr | SKC | PAD - Paddington Station (West) |  | 2017-12-12 | 2017-12-04 12:16 | -8 | 2017-11-14 08:08 | Structural Engineering - Structural Engineering - General | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | On 3 number I beams for the PES Frame on Platform level - it has been highlighted that they are missing the pre-drilled bolt holes. This will not allow for __ framework to be installed in this location for the CMS Install
| 03SR - Stations (RfL) | Cxxx-NCR-002752 | NCR | Paid lift 8-9 - working with P status drawings |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-02-28 | 2018-02-17 08:08 | -11 | 2017-11-14 15:17 | Civil - Civil Engineering General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In order to avoid future delays, on the paid lift 8-9 installation, please find attached list of P status drawings that /__ will work. The last comment on the comment sheet from MMI, regarding the design assurance (cast-in/post drilling) is in the process to be closed out. Permission to start work is also attached.
| 03SR - Stations (RfL) | Cxxx-NCR-002754 | NCR | Floor Sealer BoH - Damage |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-03-30 | 2018-02-06 11:57 | -52 | 2017-11-15 10:54 | Structural Engineering - Finishes | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Floor sealer Back of House HV rooms has been damaged. need to scrape off the damaged seal and reseal, however, the sealer used (__ XF895) has been discontinued, therefore a new method for continuation needs to be agreed with Crossrail.
| 03SR - Stations (RfL) | Cxxx-NCR-002755 | NCR | Spalling of Blockwork Following __ Board Installation |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-01-04 | 2017-11-24 15:06 | -41 | 2017-11-15 13:02 | Architectural - Brickworks/Blockworks | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Blockwork has spalled following __ board installation.
| 03SR - Stations (RfL) | Cxxx-NCR-002756 | NCR | Coring to RC Wall with Incorrect Approval |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-03-16 | 2018-06-19 15:12 | 95 | 2017-12-01 12:17 | Structural Engineering - Concrete Member | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 2no. new penetrations have been cored into wall CL-L-34 at GL11.5 and GL12.5. Refer to Dwg. Cxxx-SKC-Y-DDB-M171_4-69410 (CSTR55) and Cxxx-SKC-Y-DDB-M171_4-69411 (CSTR64) for locations. No Cxxx approval was received prior to coring.
| 03SR - Stations (RfL) | Cxxx-NCR-002757 | NCR | __ Platform 12 Waiting Room - NICEIC Certification Issues |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-02-28 | 2018-02-27 10:15 | -1 | 2017-11-17 14:41 | Electrical - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | As part of the IRF process for the __ platform 12 waiting room electrical small power & lighting testing and commissioning, it has been raised by Crossrail's electrical field assurance engineer that there is a number of queries and issues with the supplied NICEIC certificate. These queries/issues relate to emergency lighting completion and electrical installation as well as some general comments against the certificate as a whole.
| 03SR - Stations (RfL) | Cxxx-NCR-002758 | NCR | Intermediate Level ESR I - Soffit Concrete Sprawl damage |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-02-15 | 2018-01-30 10:15 | -16 | 2017-11-17 15:21 | Architectural - Ceilings & Soffits | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During installation of MEP services within the ESR I room concrete cracked and sprawled around a fixing (see attached image). As a remedial action the soffit will be cleaned and repair using the Approved RC Core 'making good' procedure.
| 03SR - Stations (RfL) | Cxxx-NCR-002759 | NCR | __ - Fire Pins |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-09-19 | 2018-08-20 16:25 | -30 | 2017-11-21 14:19 | Materials - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Flame-shield Fire Pins not installed to the correct spacing.
| 03SR - Stations (RfL) | Cxxx-NCR-002760 | NCR | Type 11 concrete smoke duct |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-08-31 | 2018-08-08 15:53 | -23 | 2017-11-24 08:47 | Mechanical - Mechanical Engineering General | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | While drilling the corner fixing on the transition piece of Flame shield duct to the type 11 concrete duct in PES room 1 Northwest corner a small section of concrete cracked but remained in position. To prevent the cracked section from falling onto the system wide walkway the section was removed and made safe.
| 03SR - Stations (RfL) | Cxxx-NCR-002761 | NCR | CER V - Install to P Status drawings |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-12-31 | 2018-08-28 09:16 | -125 | 2017-11-25 10:31 | Electrical - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate resources | Completed |  | __ provided P Status drawings under SIO1709 for CER V. __ have raised their own NCR -NCR-00062
| 03SR - Stations (RfL) | Cxxx-NCR-002762 | NCR | Paid Lift 8&9 - CHS Arm Removed From East & West Platform Level Cruciform CHS Columns |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-02-28 | 2018-03-01 10:08 | 1 | 2017-11-28 15:14 | Civil - Structural Engineering | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | __ have removed 1 glazing support CHS arm on each of the middle cruciform columns on the East and West side of the Platform structure. This was to aid the delivery of the columns to the Paid Lift 8&9 location, from Mole Hole 4.
| 03SR - Stations (RfL) | Cxxx-NCR-002763 | NCR | Poor Workmanship to BWIC Ref.: ISTR 02 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-01-18 | 2017-12-11 15:49 | -38 | 2017-11-29 15:11 | Fire - Compartmentation | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | From a snag inspection of room ref.: UNA II on intermediate level east, it was discovered that there is some poor workmanship to completed firestopping that will require rework.
| 03SR - Stations (RfL) | Cxxx-NCR-002764 | NCR | No Cavity Barrier installed behind the Brick Slip Cladding as Required |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-08-30 | 2019-03-16 12:16 | 198 | 2017-12-04 14:34 | Architectural - General | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | During a planned surveillance of cladding systems it was found the Contractor has failed to install the cavity barriers behind the Brick Slip Cladding in the Station Concourse, as required in the Cxxx Architectural Specification Cxxx-SKC-A-RSP-B071_WS077-50003 JH42.1520
| 03SR - Stations (RfL) | Cxxx-NCR-002765 | NCR | Lightning Protection at GL50 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-06-30 | 2019-03-13 11:32 | 256 | 2017-12-04 15:06 | Electrical - Electrical Engineering General | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Interfacing problems | Completed |  | Lightning protection at canopy GL 50. Protection straps have been installed and bent around the temporary formwork for the grout, and then straight across the drainage connections into the Attenuation tanks. See pic.
| 03SR - Stations (RfL) | Cxxx-NCR-002766 | NCR | TR II CWU Damage to installed works |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-06-30 | 2018-11-12 14:02 | 135 | 2017-12-05 07:34 | Electrical - General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Installed SPEAKER in TR II, damaged (see pic).
| 03SR - Stations (RfL) | Cxxx-NCR-002767 | NCR | IE-CSR9-SV Single Service Bracket # 8A |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-05-16 | 2018-08-24 12:51 | 100 | 2017-12-05 08:24 | Electrical - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Single Service Bracket # 8A in IE-CSR9-SV has been installed using only 1 __ Hus Fixing, this was un-covered as part of the investigation into CUT DOWN __ Hus Fixings (Cxxx-NCR-002750).
| 03SR - Stations (RfL) | Cxxx-NCR-002768 | NCR | Scaffold tube damaging damper fin on platform level west |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-03-23 | 2018-03-03 09:29 | -20 | 2017-12-06 17:12 | Communications and Control Systems - General | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Scaffold handrail was being adapted on GL 5 Platform level for general access. When the adaption of the scaffold was complete the horizontal handrail was errected so that the tube end was butting up to the damper fin. This tube should of been cut to the correct length so it fall short of the damper. The scaffold tube also had no end cap. Once discovered the scaffold tube was removed and the damper fin was inspected. As shown in the photo attached the scaffold tube scratched the damper fin.
| 03SR - Stations (RfL) | Cxxx-NCR-002769 | NCR | Cleveland cable SY Control Flex |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-09-28 | 2018-10-11 07:41 | 13 | 2017-12-08 15:19 | Electrical - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Observation on 07/12/17 of Cleveland cable SY Control Flex being used to supply temporary 400V power to LV switch panels for Site Acceptance Testing (see attached photo IMG_0254). Also, a number of drums were observed outside of the site office (see attached photos IMG_0262, IMG_0263 & IMG_0261). Attached is a screenshot of __ website which shows this cable is only rated for 300/500 volts and constructed to BS EN 50525-2-11.
| 03SR - Stations (RfL) | Cxxx-NCR-002770 | NCR | BoH luminaire ¬(Design Plan Tuscan 880 S12) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-06-06 | 2018-08-20 13:30 | 75 | 2017-12-08 15:48 | Electrical - General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Observation on 07/12/17 of BoH luminaire - (Design Plan Tuscan 880 S12) at low level on intermediate corridor wall (see attached photo IMG_0260). When questioned to site supervisor stated this luminaire had been mounted at low level to assist in producing the mock up. However, by mounting this mock up at low level rather than the designed mounting height, this not only causes un-necessary holes within the blockwork wall but also does not provide any indication of any access and maintenance issues arising from this method of support.
| 03SR - Stations (RfL) | Cxxx-NCR-002771 | NCR | Brickslip cladding North Elevation - Grout cube testing ITP non-compliance |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-01-31 | 2018-01-20 10:53 | -11 | 2017-12-11 15:12 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During the installation of the pre-cast brick slip panels on the north, CS Brickslp grout (MCR 50601), was used. As per ITP Cxxx-SKC-C-ITP-B071_WS077-50111 revision 3, it is required that 6 No. cubes are taken for testing. 2 are to be tested at 7 days, and another 2 are to be tested at 28 days. The strength is to be 50N/mm2 at 28 days. Due to administration errors. and poor management, a number of batches did not follow the ITP, and in many cases between 1 and 3 cubes were tested. It is also noted that in many cases the cubes were tested at dates exceeding 7 and 28 days. Please find a table summarising the cube testing schedule for each pour. Please also find attached the cube results, provided by __ Limited, which was an UCAS accredited testing laboratory. Do note that all cubes (with the exception of the corbel pour 1, which has been covered under a seperate NCR) passed requirement of 50N/mm2, and as such this NCR is being raised not as a defect, but to record this issue for certification purposes, and for CRL acceptance to use as-is.
| 03SR - Stations (RfL) | Cxxx-NCR-002772 | NCR | Brickslip cladding North Elevation - Corbel pour 1 insufficient grout strength at 28 days |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-02-28 | 2018-01-20 11:24 | -39 | 2017-12-11 15:54 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | As part of the pre-cast brick slip panels installation, grout was poured, as per ITP Cxxx-SKC-C-ITP-B071_WS077-50111, revision 3. 12 No. cubes were taken as it consisted of 2 pours, as per the ITP. At 28 days, 2No. of 4No. cubes failed the requirement of 50N/mm2 in the batch. 4 No. cubes which were taken as spares were tested at 42 days, all of which passed the 50N/mm2 requirement. Please find attached the pour tracker, and the results. It is believed that the failure of the two cubes at 28 days were due to poor manufacture of cubes.
| 03SR - Stations (RfL) | Cxxx-NCR-002773 | NCR | Protection of assets for the DB on the Concourse Level, West End, South side |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-09-11 | 2018-08-28 09:40 | -14 | 2017-12-12 11:01 | Electrical - General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Weather or ambient condition | Completed |  | DB installed Concourse Level (West End/Southside) Picture below show water ingress.
| 03SR - Stations (RfL) | Cxxx-NCR-002774 | NCR | Bakerloo Link Switchboard Locations |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-07-03 | 2018-09-24 14:06 | 83 | 2017-12-12 11:03 | Electrical - General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Sub-Switchpanels ref CRL-A & CRL-B have been delivered to site with the identifying labels switched over. Subsequently these boards have been installed in the wrong rooms (i.e. CRL A board installed in SR LV III B and CRL B board installed in SR LV III A). __ NCR - __-NCR-000065 also raised 11.12.2017
| 03SR - Stations (RfL) | Cxxx-NCR-002776 | NCR | LV Switch Panels. |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-09-28 | 2018-08-28 09:52 | -31 | 2017-12-18 12:06 | Electrical - LV Equipment | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | During a visit to site on Thursday 7th December by CEG representatives to witness the SAT testing on the LV switch boards. It was noted the incoming ACB’s on the LV switch panels were 4 pole and not 3 pole and fixed neutral as instructed in - PMC 2438 Adoption of UPS Neutral Switch Arrangements.
| 03SR - Stations (RfL) | Cxxx-NCR-002777 | NCR | Scabbling Structural Slab on Concourse Level |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-04-30 | 2018-03-24 09:45 | -37 | 2017-12-19 12:07 | Structural Engineering - Reinforcement | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | SSL on Concourse deviates from the designed SSL. Therefore when laying in screed trunking, the high spots of the structural slab reduce the screed cover of the CMS. This requires to scabble down the high spots, no less than 40mm cover to rebar beneath. A covermeter survey will be done prior to and after any scabbling of the structural slab.
| 03SR - Stations (RfL) | Cxxx-NCR-002778 | NCR | Canopy MCRs do not demonstrate compliance with the Cxxx Integrated fire Strategy. |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-07-13 | 2019-05-20 15:49 | 311 | 2017-12-21 09:39 | Architectural - Glazing | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | A planned Surveillance was carried on the Canopy Glass Installation and Painting of Steelwork, A post review of the following MCR’s Canopy Glazing Panels Cxxx-SKC-O-TSC-B071_WS077- *50943 (Rev 2), Glazing Silicone Gaskets *50950 (Rev 1), Dow Corning DC791 Silicone Sealant *50986 (Rev 1) and Dow Corning Structural Silicone DC 993 *50987. On Checking found that each are annotated as ‘n/a’ for their compliance with LU Fire Regulations. On checking the current revision of the ‘Integrated fire Strategy’ Cxxx-SKC-O9-STP-B071_WS077-50001 (Rev 8) Code 2 (20/09/2017), clause 8.10.3 states; “the canopy materials above the Crossrail station are subject to the requirements of LU 1-085. Materials compliance reports available for these components demonstrate that they comply with this Standard.” The Contractor has not supplied evidence through the MCR process that materials used on the Station Canopy comply with LU 1-085 as required in the Cxxx Architectural Specification and the Cxxx Integrated fire Strategy.
| 03SR - Stations (RfL) | Cxxx-NCR-002779 | NCR | Canopy gaskets joints not heat sealed in line with Cxxx Architectural Specification. |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-03-30 | 2018-01-20 10:50 | -69 | 2017-12-21 09:54 | Architectural - Glazing | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | A planned Surveillance was carried on the Canopy Glass Installation and Painting of Steelwork. During the surveillance It was witnessed that at grid lines 58-60, the silicone gasket joints had been bonded with silicone sealant, see attached photograph. On a checking the Cxxx Architectural Specification Cxxx-SKC-A-RSP-B071_WS077-50003 clause JZ23.1101 states; “all gasket to gasket joints shall be butt jointed and heat sealed. The bonding of gaskets using other materials shall not be acceptable. The gaskets shall perform and appear as a single continuous material”. This statement is included in the submitted MCR for the ‘Silicone Gasket’ Cxxx-SKC-O-TSC-B071_WS077-50950 and annotated as ‘Y’ for their compliance with the Clause.
| 03SR - Stations (RfL) | Cxxx-NCR-002780 | NCR | PSD - Damage to header box |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-08-31 | 2018-09-03 15:56 | 3 | 2017-12-21 11:42 | Mechanical - Platform Edge Doors | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Damage has occured to the bottom plate of the PSD header box. (Exact door TBC)
| 03SR - Stations (RfL) | Cxxx-NCR-002781 | NCR | Wall bronze cladding - Working with P status / DDCD not signed of |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-04-05 | 2018-01-20 11:22 | -75 | 2018-01-05 14:09 | Architectural - Finishes | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | have instructed __ to proceed with manufacture of Bronze Wall Cladding Panels, __ have commenced manufacture of panels with drawings at P status. The list of drawings at P status below: Cxxx-SKC-Y-DDC-M171-4-31001 to Cxxx-SKC-Y-DDC-M171-4-31003 Cxxx-SKC-Y-DDC-M171-5-31001 to Cxxx-SKC-Y-DDC-M171-5-31005
| 03SR - Stations (RfL) | Cxxx-NCR-002782 | NCR | Incorrect overlapping of D49 mesh at day joints |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-08-29 | 2018-02-16 16:01 | -194 | 2018-01-08 13:57 | Structural Engineering - Joints | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Thoroughout the installation of day joints in the wet fix screed, there have been localised areas where the D49 Mesh does not have the correct overlap. Day joint detail shows there should be 250mm overlap at day joints, in some areas the joints only overlaps by 100mm.
| 03SR - Stations (RfL) | Cxxx-NCR-002783 | NCR | Voids underneath tiles at edges |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-08-15 | 2018-02-09 12:56 | -187 | 2018-01-08 14:08 | Architectural - Flooring | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | It is evident that voids have been produced beneath tiles at the edges (day joints, access hatches). This raises concerns that the tiles on the edges may not be completely bedded. Going forward, we would advise that any light voids to the edges of the tiles will be filled with slurry and screed when the adjacent tiles are laid, and that this is normal industry practice.
| 03SR - Stations (RfL) | Cxxx-NCR-002784 | NCR | Paid Lift 8&9 - Weld MCR Incrorrect |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-02-19 | 2018-01-20 11:28 | -30 | 2018-01-08 16:25 | Civil - Structural Engineering | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | During welding of the Paid Lift 8&9 the coded welder on the weld pack suddenly left, leaving the sub-contactor no choice but to bring in additional welders onto site at short notice to complete the steelwork on time. The MCR with the code pack includes the details of the welders qualifications, which did not include the qualitfications of the additional welders.
| 03SR - Stations (RfL) | Cxxx-NCR-002785 | NCR | Redundant RC Openings - Lifts 8&9 and 11 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-05-31 | 2018-03-01 09:57 | -91 | 2018-01-09 16:25 | Civil - Structural Engineering | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Lifts 8&9 The soffit of Lifts 8 & 9 contain 3 no. openings, two are nominated service openings for each respective lift that connect Lifts 8 & 9 shaft and LER IV. The third opening is one that was originally intended to house a drainage pipe that was not a part of the __ design. As per SPC-LAE-SMVT-307458307 Part 1 Cl 10.2.3 this design intention is non-compliant. "Lift machinery spaces (including LEERs) shall only be used for accommodating the equipment or services necessary for the operation or maintenance of the lift" Lift 11 The location of the services opening in IL-L-19 is within 1.0m of the wall containing the landing door in Lift 11. Installation of __ equipment within the shaft require this service opening to be greater than 1.0m from the wall containing the landing door as per BS EN 81-72 Cl 5.3.1 and Annex D.
| 03SR - Stations (RfL) | Cxxx-NCR-002786 | NCR | Escalator cables manufactured too short - Esc 3-5 & ECR VI |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-06-30 | 2018-03-01 10:21 | -121 | 2018-01-18 11:44 | Mechanical - Escalators | 500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following installation of the escalator control units as per Cxxx-SKC-M1-DWG-B071_WS077-50155 it has been discovered during pulling of the cables to their respective controllers that the cables for Escalator 3 are too short in order to reach the controllers. As a result the fit out ECR VI cannot be completed.
| 03SR - Stations (RfL) | Cxxx-NCR-002788 | NCR | Not complying with Quality Management System - Wiring commenced prior to CMS sign off |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-03-27 | 2018-05-14 09:48 | 48 | 2018-01-10 13:33 | Electrical - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Further to an invite from for IRF witness of the CMS installation within MIST II room (#397). As can be seen from the attached photo’s the contractor has begun wiring prior to the witness point in the agreed ITP. The contractor is also preparing to wire within EFAN II (#956). The cable type being installed is a non-fire rated cable (__ Saffire) feeding fire dampers. As these are life safety items of equipment, they should be wired in fire rated single core cable (__ FT Sifer).
| 03SR - Stations (RfL) | Cxxx-NCR-002789 | NCR | Clash with Tile Access Hatch & Floor Trunking Access Lid |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-08-30 | 2018-02-16 15:58 | -195 | 2018-01-10 14:42 | Architectural - Flooring | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Whilst attempting to install access hatches on Concourse Level, it has been made aware that the junction box does not align with the access hatch by 10-12mm one side. This means that when the juction box needs accessing, the lid on top of the box cannot be removed.
| 03SR - Stations (RfL) | Cxxx-NCR-002790 | NCR | Paid Lift 8&9 - Missing Middle Partition Spigots |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-03-31 | 2018-03-17 10:11 | -14 | 2018-01-10 16:34 | Civil - Structural Engineering | 2500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | It has been identified that the spigots for the movement joints on the middle partition steelwork of the Paid Lift 8&9 are incorrect as per the approved Cxxx drawings. The male member of the spigot joint which have been brought on site are 100x10 SHS, but are supposed to be 70x8 SHS sections.
| 03SR - Stations (RfL) | Cxxx-NCR-002791 | NCR | Pipe sleeve and fire stopping not in accordance with workmanship standards |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-07-26 | 2018-07-13 09:09 | -13 | 2018-01-12 17:16 | Mechanical - Piping | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Pipe sleeves have been installed on site oversized relative to service pipework, with a clearance greater than 25mm between service pipe and sleeve. __ mineral wool has been loosely packed out and fire stopping has not been complete. Pipe sleeves and fire stopping are not in line with M&W JP12.1305b (Fire Systems Reference Manual G7321 Issue 2 September 2012 or equivalent). No design drawings for pipe sleeve arrangement or fire stopping details have been provided to CRL.
| 03SR - Stations (RfL) | Cxxx-NCR-002792 | NCR | Potential Water Damage to Floor Penetration __ Boarding |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-03-06 | 2018-01-29 12:18 | -36 | 2018-01-15 11:03 | Fire - Compartmentation | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following a site inspection of completed works, it was recognised that a section of __ boarding that has been installed to the underside of a floor penetration is showing signs of potential water damage. Through an inspection of the location above, the joints between the screed protection shows signs of water ingress.
| 03SR - Stations (RfL) | Cxxx-NCR-002793 | NCR | Mid Bay Fin HD Bolts |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-04-15 | 2018-02-02 17:23 | -72 | 2018-01-15 15:03 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | After performing a survey of the existing bolts installed by the previous subcontractor, all the mid-bay fin bolts spacings were found to be incorrect.
| 03SR - Stations (RfL) | Cxxx-NCR-002794 | NCR | Paid Lift - Fixing Details |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-03-30 | 2018-03-01 10:18 | -29 | 2018-01-18 09:00 | Civil - Structural Engineering | 1000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Two No. fixing issues with the design were raised during installation: 1. On one the middle partition crusiform steel members, re-bar was hit whilst drilling the bottom two sets of holes @ 100mm (Enbedment required was 180mm). Installation was put on hold to assess whether the enbedment of 100mm was structurally sufficient. __'s designers confirmed this was permissable, and so installation continued. 2. It was identified that the fixings for top base plate for the main structural column at Intermediate Level, was to use __ Resin. delivery team stood down __, pending a structural assessment on whether M24 mechanical bolts could be used. Confirmation was receieved and construction continued. 3. One the main structural column on Intermediate level, when drilling the holes for the bottom base plate, re-bar was hit at 150mm. Despite ferrous scanning, re-bar was still struck. Works were held until structural calculation confirmation for use of the 150mm embedment. Confirmation was received, and construction continued.
| 03SR - Stations (RfL) | Cxxx-NCR-002795 | NCR | Paid Lift - Middle Partition Top Fixing Change |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-02-15 | 2018-02-16 16:56 | 1 | 2018-01-18 10:09 | Civil - Structural Engineering | 1000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | On the Cxxx drawings, the detail for the fixings for the top base plate for the middle partition steelwork shows __ resin. The delivery team held works on this location, and is suggesting to change to __ mechanical bolts.
| 03SR - Stations (RfL) | Cxxx-NCR-002796 | NCR | Not complying with Quality Management System - Wiring commenced prior to CMS sign off |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-03-23 | 2018-03-17 10:13 | -6 | 2018-01-22 14:34 | Electrical - Cable Management | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Further to an invite from for IRF witness of the CMS installation within TR III CWU room (#917). As can be seen from the attached photo’s the contractor has begun wiring of the PAVA system prior to the witness point in the agreed ITP.
| 03SR - Stations (RfL) | Cxxx-NCR-002798 | NCR | Not complying with Quality Management System - CMS removed post IRN sign off. |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-07-23 | 2018-08-10 12:59 | 18 | 2018-01-23 16:03 | Electrical - Cable Management | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During a site inspection on 19/01/2018. It was found the CMS installation within the ERC area on the eastbound Platform at the east end of the station has been removed (See attached photo). This has occurred after IRN 406 was signed off for the system wide Cxxx contractor and is against the Quality Management System.
| 03SR - Stations (RfL) | Cxxx-NCR-002799 | NCR | Incorrect Breaker installation within LV Switchboards |  | Contr | HYD | PAD - Paddington Station (West) |  | 2018-07-27 | 2018-08-28 09:25 | 32 | 2018-01-25 11:21 | Electrical - Switchgear | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | 4 Pole Breakers, specifically with Switched Neutral, have been installed as opposed to 3 Pole and fixed Neutral required. This is contrary to Cxxx-PMC-02438 & Cxxx-PMI-00570 (Ref: CRL1-CEC-00017) which requires the UPS to have a fixed neutral reference to safely operate and additionally protect any authorised person working on the system.
| 03SR - Stations (RfL) | Cxxx-NCR-002800 | NCR | Deficient Design of Fire Fighting / Means of Escape Pressurisation System |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-09-07 | 2018-09-18 12:46 | 11 | 2018-01-25 14:36 | Mechanical - Mechanical Engineering General | 15000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Further to Cxxx-EWN-02658, Risk Review meetings (first held 08-Dec-2017) and a site walk on 22-Jan-2018 with the Contractor’s Designer. The Contractor is informed that the Fire Fighting / Means of Escape Pressurisation System is deficient design as notified in EWN-2658. Pursuant to Cxxx-PMI-00146, the Contractor is required to develop a fit for purpose design.
| 03SR - Stations (RfL) | Cxxx-NCR-002801 | NCR | LOIS List Items for Lift 6 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-07-31 | 2019-04-26 15:03 | 269 | 2018-01-26 15:56 | Mechanical - Lifts | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following delivery and receipt of Lift 6 car and components to Paddington Cxxx remedial items have been identified on site to be captured on ongoing revisions of the LOIS List. An NCR will be raised for each lift at Paddington Cxxx and the defective items on the lift or associated lift equipment room will be captured on the updated revisions of the LOIS lists which will have a trackable document number. Note that any NCRs relating to workmanship, installation error, etc. shall be raised and tracked by a separate NCR. This LOIS list for Lift 6 is captured on document (Cxxx-SKC-M1-LST-B071_WS077-50038) on eB.
| 03SR - Stations (RfL) | Cxxx-NCR-002802 | NCR | LOIS List Items for Lift 12 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-07-31 | 2019-04-26 15:04 | 269 | 2018-01-26 16:14 | Mechanical - Lifts | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following delivery and receipt of Lift 12 car and components to Paddington Cxxx remedial items have been identified on site to be captured on ongoing revisions of the LOIS List. An NCR will be raised for each lift at Paddington Cxxx and the defective items on the lift or associated lift equipment room will be captured on the updated revisions of the LOIS lists which will have a trackable document number. Note that any NCRs relating to workmanship, installation error, etc. shall be raised and tracked by a separate NCR. This LOIS list for Lift 12 is captured on document (Cxxx-SKC-M1-LST-B071_WS077-50044) on eB.
| 03SR - Stations (RfL) | Cxxx-NCR-002803 | NCR | LOIS List Items for Lift 11 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-07-31 | 2019-04-26 15:05 | 269 | 2018-01-26 16:14 | Mechanical - Lifts | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following delivery and receipt of Lift 11 car and components to Paddington Cxxx remedial items have been identified on site to be captured on ongoing revisions of the LOIS List. An NCR will be raised for each lift at Paddington Cxxx and the defective items on the lift or associated lift equipment room will be captured on the updated revisions of the LOIS lists which will have a trackable document number. Note that any NCRs relating to workmanship, installation error, etc. shall be raised and tracked by a separate NCR. This LOIS list for Lift 11 is captured on document (Cxxx-SKC-M1-LST-B071_WS077-50043) on eB.
| 03SR - Stations (RfL) | Cxxx-NCR-002804 | NCR | LOIS List Items for Lift 10 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-07-31 | 2019-04-26 15:08 | 269 | 2018-01-26 16:14 | Mechanical - Lifts | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following delivery and receipt of Lift 10 car and components to Paddington Cxxx remedial items have been identified on site to be captured on ongoing revisions of the LOIS List. An NCR will be raised for each lift at Paddington Cxxx and the defective items on the lift or associated lift equipment room will be captured on the updated revisions of the LOIS lists which will have a trackable document number. Note that any NCRs relating to workmanship, installation error, etc. shall be raised and tracked by a separate NCR. This LOIS list for Lift 10 is captured on document (Cxxx-SKC-M1-LST-B071_WS077-50042) on eB.
| 03SR - Stations (RfL) | Cxxx-NCR-002805 | NCR | LOIS List Items for Lift 9 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-07-31 | 2019-04-26 15:09 | 269 | 2018-01-26 16:14 | Mechanical - Lifts | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following delivery and receipt of Lift 9 car and components to Paddington Cxxx remedial items have been identified on site to be captured on ongoing revisions of the LOIS List. An NCR will be raised for each lift at Paddington Cxxx and the defective items on the lift or associated lift equipment room will be captured on the updated revisions of the LOIS lists which will have a trackable document number. Note that any NCRs relating to workmanship, installation error, etc. shall be raised and tracked by a separate NCR. This LOIS list for Lift 9 is captured on document (Cxxx-SKC-M1-LST-B071_WS077-50041) on eB.
| 03SR - Stations (RfL) | Cxxx-NCR-002806 | NCR | LOIS List Items for Lift 8 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-07-31 | 2019-04-26 15:10 | 269 | 2018-01-26 16:14 | Mechanical - Lifts | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following delivery and receipt of Lift 8 car and components to Paddington Cxxx remedial items have been identified on site to be captured on ongoing revisions of the LOIS List. An NCR will be raised for each lift at Paddington Cxxx and the defective items on the lift or associated lift equipment room will be captured on the updated revisions of the LOIS lists which will have a trackable document number. Note that any NCRs relating to workmanship, installation error, etc. shall be raised and tracked by a separate NCR. This LOIS list for Lift 8 is captured on document (Cxxx-SKC-M1-LST-B071_WS077-50040) on eB.
| 03SR - Stations (RfL) | Cxxx-NCR-002807 | NCR | LOIS List Items for Lift 7 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-07-31 | 2019-04-26 15:12 | 269 | 2018-01-26 16:14 | Mechanical - Lifts | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following delivery and receipt of Lift 7 car and components to Paddington Cxxx remedial items have been identified on site to be captured on ongoing revisions of the LOIS List. An NCR will be raised for each lift at Paddington Cxxx and the defective items on the lift or associated lift equipment room will be captured on the updated revisions of the LOIS lists which will have a trackable document number. Note that any NCRs relating to workmanship, installation error, etc. shall be raised and tracked by a separate NCR. This LOIS list for Lift 7 is captured on document (Cxxx-SKC-M1-LST-B071_WS077-50039) on eB.
| 03SR - Stations (RfL) | Cxxx-NCR-002808 | NCR | CSR east on intermediate level without allowing access to firestop |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-05-31 | 2018-07-13 09:19 | 43 | 2018-01-27 15:12 | Electrical - General | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | CMS has been installed within __ board wall into the CSR east on intermediate level without allowing access to firestop. As a result, CMS will be required to be removed for access
| 03SR - Stations (RfL) | Cxxx-NCR-002809 | NCR | Inadequate design co-ordination of station access gates |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2019-01-18 | 2019-01-02 14:34 | -16 | 2018-01-31 10:49 | Architectural - Security | 15000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The station access gates have not been co-ordinated with the structure. It has become apparent that the recessed opening is of insufficient height to accommodate the station access gates.
| 03SR - Stations (RfL) | Cxxx-NCR-002810 | NCR | Crossrail Rail Arch - GL91 RC Plugs |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-04-02 | 2018-04-11 14:59 | 9 | 2018-02-01 09:07 | Structural Engineering - Structural Engineering - General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Within the Crossrail Rail arch on the 1st floor East wall (block E), concrete subcontractor has poured & installed 6 no. RC plugs at high level within the wall face. On striking & removing the shuttering it was evident that 3 no. RC plugs had issues where expanding foam that had been used to seal the joint between the shutter and existing heritage masonary wall had gone within and behind the shutter not allowing concrete to fill the full space of the shutter.
| 03SR - Stations (RfL) | Cxxx-NCR-002811 | NCR | Contractor not working to Quality management Plan |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2018-09-28 | 2018-08-28 09:36 | -31 | 2018-01-31 12:18 | Electrical - Cable Management | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | On 29th January the Supervisor's Representative was made aware of sub main cabling being installed on CMS that had not been notified to the Project manager's Team as being complete. This contravenes the Inspection and Test Plans and the Quality Management System. Continued deliberate contravention of the accepted Quality Management System undermines self certification. This is a fundamental requirement of the Contract to support demonstration of compliance in accordance with the Employer's Technical Assurance Plan. The Contractor has stated that he raised an NCR to demonstrate this non-conformance, however on reviewing eB PTR 2 days later there is no evidence that this has been raised.
| 03SR - Stations (RfL) | Cxxx-NCR-002812 | NCR | Use of Nullifire mastic on smoke extract volume control dampers - no MCR in place |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2018-08-17 | 2018-04-07 13:55 | -132 | 2018-01-31 12:50 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The installation of the volume control dampers was offered for and accepted as a benchmark as detailed in Cxxx-SKC-O6-STD-B071_WS077-50124 accepted at Code 2 on 14th December 2017. This benchmark was sealed using Promoseal Acrylic sealant as detailed in the benchmark document accepted at Code 1 on 16th May 2017. However during an routine inspection of the site by the Supervisor's Representative on 29th January 2018, a box of Nullifire intumescent sealant was identified stored with the VCDs. During email correspondence attached, it was confirmed that this sealant has been used on the VCDs. there is no MCR in place for this product and the installation is therefore in contravention of the Contractor's Quality Management System
| 03SR - Stations (RfL) | Cxxx-NCR-002813 | NCR | Not complying with Quality Management System - Wiring commenced prior to CMS sign off (FCR II CWU) |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-03-27 | 2018-03-17 10:18 | -10 | 2018-02-01 12:53 | Electrical - General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Further to an invite from for IRF witness of the CMS installation within FCR II room (#931). As can be seen from the attached photo’s the contractor has begun wiring of the telephone system prior to the witness point in the agreed ITP.
| 03SR - Stations (RfL) | Cxxx-NCR-002814 | NCR | Not complying with Quality Management System - Wiring commenced prior to CMS sign off (FCR I CWU) |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-03-27 | 2018-03-17 10:19 | -10 | 2018-02-02 16:11 | Electrical - General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Further to an invite from for IRF witness of the CMS installation within FCR I CWU room (#922). As can be seen from the attached photo’s the contractor has begun wiring of the telephone system prior to the witness point in the agreed ITP.
| 03SR - Stations (RfL) | Cxxx-NCR-002816 | NCR | Not complying with Quality Management System - Wiring commenced prior to CMS sign off (TR IV CWU) |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-03-27 | 2018-05-14 09:47 | 48 | 2018-02-06 12:52 | Electrical - General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Further to an invite from for IRF witness of the CMS installation within TR IV CWU room (#919). As can be seen from the attached photo’s the contractor has begun wiring of the PAVA system prior to the witness point in the agreed ITP.
| 03SR - Stations (RfL) | Cxxx-NCR-002817 | NCR | Not complying with Quality Management System - Wiring commenced prior to CMS sign off (FCR I) |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-03-27 | 2018-05-14 13:56 | 48 | 2018-02-08 08:43 | Electrical - Power Distribution | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During a site walk around it was noted within FCR I room (#763), the sub mains cabling has been commenced prior to the witness point in the agreed ITP. See attached photo.
| 03SR - Stations (RfL) | Cxxx-NCR-002818 | NCR | Not complying with Quality Management System - Wiring commenced prior to CMS sign off (MCC I CWU) |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-03-27 | 2018-05-14 13:57 | 48 | 2018-02-08 09:02 | Electrical - Power Distribution | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Further to an invite from for IRF witness of the CMS installation within MCC I CWU room (#937). As can be seen from the attached photo’s the contractor has begun wiring of the sub main LV distribution and earthing system cabling prior to the witness point in the agreed ITP.
| 03SR - Stations (RfL) | Cxxx-NCR-002819 | NCR | Not complying with Quality Management System - Wiring commenced prior to CMS sign off (MCC I CWU) |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-03-27 | 2018-05-14 13:58 | 48 | 2018-02-08 09:56 | Electrical - General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Further to an invite from for IRF witness of the CMS installation within MCC I CWU room (#937). As can be seen from the attached photo’s the contractor has begun wiring of the small power circuits to the Fire Dampers prior to the witness point in the agreed ITP.
| 03SR - Stations (RfL) | Cxxx-NCR-002820 | NCR | Not complying with Quality Management System - Wiring commenced prior to CMS sign off (BAT I) |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-03-27 | 2018-05-14 13:59 | 48 | 2018-02-08 11:15 | Electrical - General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Further to an invite from for IRF witness of the CMS installation within BAT I room (#761). As can be seen from the attached photo’s the contractor has begun wiring of the PAVA system cabling prior to the witness point in the agreed ITP.
| 03SR - Stations (RfL) | Cxxx-NCR-002821 | NCR | Not complying with Quality Management System - Wiring commenced prior to CMS sign off (BAT I) |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-03-27 | 2018-05-14 14:00 | 48 | 2018-02-08 14:30 | Electrical - Power Distribution | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Further to an invite from for IRF witness of the CMS installation within BAT I room (#761). As can be seen from the attached photo’s the contractor has begun wiring of the sub main LV distribution and earthing system cabling prior to the witness point in the agreed ITP.
| 03SR - Stations (RfL) | Cxxx-NCR-002822 | NCR | Not complying with Quality Management System - Wiring commenced prior to CMS sign off (BAT I CWU) |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-03-27 | 2018-05-14 14:01 | 48 | 2018-02-09 10:00 | Electrical - Power Distribution | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Further to an invite from for IRF witness of the CMS installation within BAT I CWU room (#928). As can be seen from the attached photo’s the contractor has begun wiring of the sub main LV distribution and earthing system cabling prior to the witness point in the agreed ITP.
| 03SR - Stations (RfL) | Cxxx-NCR-002823 | NCR | Not complying with Quality Management System - Wiring commenced prior to CMS sign off (BAT I CWU) |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-03-27 | 2018-05-14 14:02 | 48 | 2018-02-09 10:05 | Electrical - Cable Management | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Further to an invite from for IRF witness of the CMS installation within BAT I CWU room (#928). As can be seen from the attached photo’s the contractor has begun wiring of the small power circuits feeding the fire dampers prior to the witness point in the agreed ITP.
| 03SR - Stations (RfL) | Cxxx-NCR-002824 | NCR | Not complying with Quality Management System - Wiring commenced prior to CMS sign off Intermediate Concourse |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-03-27 | 2018-05-14 14:03 | 48 | 2018-02-09 12:22 | Electrical - Power Distribution | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Further to a site walk of the intermediate level corridor. As can be seen from the attached photo the contractor has begun wiring of the LV distribution sub-main cabling prior to the witness point in the agreed ITP.
| 03SR - Stations (RfL) | Cxxx-NCR-002825 | NCR | Not complying with Quality Management System - Wiring commenced prior to CMS sign off (AAR FAN) |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-06-27 | 2018-06-19 15:28 | -8 | 2018-02-09 13:22 | Electrical - General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Further to an invite from for IRF witness of the CMS installation within ARR FAN room (#957). As can be seen from the attached photo’s the contractor has begun wiring of the small power circuits prior to the witness point in the agreed ITP.
| 03SR - Stations (RfL) | Cxxx-NCR-002826 | NCR | Installing lagged fire rated smoke extract ductwork (concourse level) without notifying CRL |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-07-31 | 2018-05-24 13:47 | -68 | 2018-02-12 16:16 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | CRL observed that smoked extract fire rated ductwork has been lagged, and installation of the ductwork has commenced in rooms PSE I and II (Concourse West and East respectively). CRL have not been invited to witness any of this ductwork being assembled and installed prior to lagging, in PSE-I and PSE-II. The ITP intervention points for ductwork install (Cxxx-SKC-M-ITP-B071_WS077-50007) and insulation (Cxxx-SKC-M-ITP-B071_WS077-50008) have not been followed. In addition, the duct internal walls were observed as dirty when stored at ground level. See attached photo 'internal cleanliness.jpg' observed in PSE-II
| 03SR - Stations (RfL) | Cxxx-NCR-002827 | NCR | Not complying with Quality Management System - Wiring commenced prior to CMS sign off Intermediate Concourse (Grids 1-9) |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-06-30 | 2018-06-19 15:29 | -11 | 2018-02-13 12:13 | Electrical - General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Further to an invite from for IRF witness of the CMS installation within the intermediate corridor CIR-PL V (#76). As can be seen from the attached photo’s the contractor has begun wiring of the small power circuits prior to the witness point in the agreed ITP.
| 03SR - Stations (RfL) | Cxxx-NCR-002828 | NCR | Not complying with Quality Management System - Wiring commenced prior to CMS sign off Intermediate Concourse (Grids 1-9) |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-06-30 | 2018-06-19 15:30 | -11 | 2018-02-13 13:29 | Electrical - Cable Management | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Further to an invite from for IRF witness of the CMS installation within the intermediate corridor CIR-PL V (#76). As can be seen from the attached photo’s the contractor has begun wiring of the small power circuits prior to the witness point in the agreed ITP.
| 03SR - Stations (RfL) | Cxxx-NCR-002829 | NCR | Departures Road Canopy/NR Form B |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-09-28 | 2018-10-19 10:49 | 21 | 2018-02-13 15:22 | Electrical - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | MEPH works commenced on the Departures Road Canopy in advance of completion of __s Form B
| 03SR - Stations (RfL) | Cxxx-NCR-002830 | NCR | Thorp PC Brick Slip Panels - Non-Compliant (Code 3) Mastic Primer Used |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-06-01 | 2018-06-04 11:04 | 3 | 2018-02-16 14:28 | Architectural - Brickworks/Blockworks | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | MCR Cxxx-SKC-O-TSC-B071_WS077-50614 has been used on site on the brickslip cladding panels which is has been rejected by CRL.
| 03SR - Stations (RfL) | Cxxx-NCR-002831 | NCR | Not complying with Quality Management System - Wiring commenced prior to CMS sign off Intermediate Concourse (Grids 17-24) |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-06-30 | 2018-06-19 15:31 | -11 | 2018-02-19 13:02 | Electrical - General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Further to an invite from for IRF witness of the CMS installation within the intermediate corridor CIR-PL VIII (#79). As can be seen from the attached photo’s the contractor has begun wiring of the small power circuits prior to the witness point in the agreed ITP.
| 03SR - Stations (RfL) | Cxxx-NCR-002832 | NCR | Not complying with Quality Management System - Wiring commenced prior to CMS sign off Intermediate Concourse (Grids 17-24) |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-12-31 | 2018-08-20 16:30 | -133 | 2018-02-19 13:17 | Fire - Detection | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Further to an invite from for IRF witness of the CMS installation within the intermediate corridor CIR-PL VIII (#79). As can be seen from the attached photo’s the contractor has begun wiring of the Fire Alarm System circuits prior to the witness point in the agreed ITP.
| 03SR - Stations (RfL) | Cxxx-NCR-002833 | NCR | Not complying with Quality Management System - Wiring commenced prior to CMS sign off Intermediate Concourse (Grids 17-24) |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-06-30 | 2018-06-19 15:32 | -11 | 2018-02-19 16:02 | Electrical - General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Further to an invite from for IRF witness of the CMS installation within the intermediate corridor CIR-PL VIII (#79). As can be seen from the attached photo’s the contractor has begun wiring of the PAVA System circuits prior to the witness point in the agreed ITP.
| 03SR - Stations (RfL) | Cxxx-NCR-002834 | NCR | Armoured cables with exposed cut ends |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-06-30 | 2018-11-12 15:17 | 135 | 2018-02-20 14:24 | Electrical - Power Distribution | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | During a site walk around it was noted within FCR I room (#763) and BAT I (#761), the sub mains armoured cabling has been installed and cut leaving an exposed cut ends without protection. (see attached photo's). This can lead to moisture and damage to the cable, a suitable cable sleeve/sock should be installed on all armoured cable cut ends, as per the agreed and accepted RAMS Cxxx-SKC-O1-GMS-B071_WS077-50468 rev. 2.0.
| 03SR - Stations (RfL) | Cxxx-NCR-002835 | NCR | Not complying with Quality Management System - Wiring commenced prior to CMS sign off (BAT II) |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-06-30 | 2018-07-31 08:27 | 31 | 2018-02-20 14:35 | Electrical - Cable Management | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Further to an invite to witness the access & maintenance within BAT II (#762). As can be seen from the attached photo’s the contractor has begun wiring of the Fire Alarm System prior to the witness point in the agreed ITP.
| 03SR - Stations (RfL) | Cxxx-NCR-002836 | NCR | Not complying with Quality Management System - Wiring commenced prior to CMS sign off (SER CWU) |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-06-30 | 2019-01-02 14:36 | 186 | 2018-02-20 14:39 | Electrical - General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Further to an invite to witness the access & maintenance within BAT II (#762). As can be seen from the attached photo’s the contractor has begun wiring of the small power and lightingf within SER CWU (#926) prior to the witness point in the agreed ITP.
| 03SR - Stations (RfL) | Cxxx-NCR-002837 | NCR | Cleveland cable SY Control Flex |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-06-30 | 2019-03-02 10:15 | 245 | 2018-02-20 14:49 | Electrical - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Observation on 16/02/17 of Cleveland cable SY Control Flex being used to supply temporary 400V power. As can bee seen from the attached photo, the contractor continues to use of the above cable type for the site temporary's despite the previous Cxxx-NCR-002769.
| 03SR - Stations (RfL) | Cxxx-NCR-002838 | NCR | Not complying with Quality Management System - Wiring commenced prior to CMS sign off (BAT II CWU) |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-06-30 | 2018-07-31 08:35 | 31 | 2018-02-20 14:53 | Electrical - Cable Management | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Further to an invite to witness the access & maintenance within BAT II (#762). As can be seen from the attached photo’s the contractor has begun wiring of the Fire Alarm System within BAT II CWU (#929) prior to the witness point in the agreed ITP.
| 03SR - Stations (RfL) | Cxxx-NCR-002839 | NCR | Canopy - Cantilever access panel welded stud failure |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-05-31 | 2018-05-14 14:28 | -17 | 2018-02-27 12:59 | Structural Engineering - Welding | 2500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | became aware on 22/02 that there had been a failure of a small number of studs welded to the top face of the access panels in the Bullnose/Cantilever along EBT. The studs provide the connection between the Panel and the hinge. Upon further investigation, __ have removed all panels from site, both installed and awaiting installation, and returned them to the manufacturers for investigation. Attached marked up drawing, ????????, shows the studs.
| 03SR - Stations (RfL) | Cxxx-NCR-002840 | NCR | VSHH - Anodised Rainscreen Colour |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-06-27 | 2018-05-10 11:12 | -48 | 2018-02-27 11:40 | Architectural - Finishes | 5000 |  | Manufacturing Defect | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | During the initial inspection on site of the anodised rainscreen panels for the East VSHH it was identified that the colour on some of the panels was outside of the agreed upper and lower colour limits.
| 03SR - Stations (RfL) | Cxxx-NCR-002841 | NCR | Smoke Down Screens - Glass Manufacture/Installation Without Code 1 MCR |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-05-31 | 2018-05-24 13:48 | -7 | 2018-02-28 17:14 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Smoke down screen glass manufacture/installation has commenced without a Code 1 MCR. Two number EWN's (Cxxx-EWN-02653 and Cxxx-EWN-02784) were raised by in regards to the MCR, as no review was recieved until 3 months after submission. Due to the long manufacturing lead times, and the short duration until the projects end date, decided to manufacture and install without a MCR accepted for the glass system, as it believed the product meets the Works Information. It is noted the MCR was made code 3 due to the mastic type applied in the system, not the glass itself. Installation of the mastic is on hold until an acceptable product has been agreed between and CRL, and officially captured through the MCR process.
| 03SR - Stations (RfL) | Cxxx-NCR-002842 | NCR | Mechanical IRF and IRN documentation received not fit for submission |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-05-01 | 2018-05-14 14:31 | 13 | 2018-03-01 09:52 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | CRL field engineering received a Mechanical IRF on 27-Feb-2018 for IRN-395 - supply air fire dampers (AHU01 East). There are many basic errors within this document, hence it is not fit for submission to CRL. The following are comments based on a sample review by CRL, a full review has not been performed: * IRF cover page: 1. IRF doc. number is ‘TBC’ 2. RAMS 341 (Cxxx-SKC-O1-GMS-B071_WS077-50300) is not approved at revision 3 3. Volume 2 M&W Mechanical Specification (Cxxx-SKC-M-RSP-B071_WS077-50004) is at revision 3 on eB 4. Incorrect room references i.e. TRII CWU should be TR-III CWU; OHLE SRI should be OHLE SR-II * Fire damper FD25/AHU01/E 5. Incorrect room reference on check sheet, it should be TR-III (917) 6. No signature on check sheet 7. Location on Label Install Record Sheet is incorrect, it is gridlines 16-17 * Fire damper FD26/AHU01/E 8. Location on Label Install Record Sheet is incorrectly stated as ‘Bakerloo Link Passage…’, should be TR-IV CWU * Fire damper FD27/AHU01/E 9. Incorrect ComLot description on check sheet, it should be CSR ‘IV’ – FD27 / AHU01 / E 10. Location on Label Install Record Sheet is incorrect, it is gridlines 18-19 * Fire damper FD28/AHU01/E 11. Location on Label Install Record Sheet is incorrect, it is gridlines 18-19 * Fire damper FD29/AHU01/E 12. Incorrect room reference on check sheet, it should be OHLE SR-II (668) 13. Incorrect ComLot description on check sheet, it should be OHLE SRII – FD29 / AHU01 / E 14. Two versions of the check sheet have been submitted for this fire damper 15. Location on Label Install Record Sheet is incorrect, it is gridlines 19-20 * Pull test records 16. Note: only two pull test records have been submitted for rooms TRIV CWU and SR HV-II CWU
| 03SR - Stations (RfL) | Cxxx-NCR-002843 | NCR | __ installed - Tubeline |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-09-17 | 2018-05-09 16:31 | -131 | 2018-03-01 13:24 | Architectural - Finishes | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | __ are currently installing 1st fix tubeline ceiling at concourse level. have identified the __ currently being installed is not as per the approved MCR and as per the specification. As such has advised __ not continue with installation until they can provide evidence that the 30mm 60kg/m3 installed product meets the acoustic performance. The approved MCR and Specification, refer to a 50mm 45kg/m3 __.
| 03SR - Stations (RfL) | Cxxx-NCR-002844 | NCR | IRF: __-284/367/377 & 387. |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-06-16 | 2019-03-23 10:30 | 280 | 2018-03-02 14:48 | Electrical - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Personnel Error - Not Defined | Completed |  | IRF numbers 284, 367, 377 and 387 incorrectly signed as ''not witnessed'' + intervention points shown as Y rather than S/W or H
| 03SR - Stations (RfL) | Cxxx-NCR-002845 | NCR | Failure to comply with QMS/ITP on Floor Trunking |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-06-30 | 2018-10-25 09:40 | 117 | 2018-03-05 12:03 | Electrical - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Screeding to Concourse level GL 9 - 16 (FLOOR TRUNKING) commenced before IRF Inspection has been offered to CRL, in contravention of ITP: Cxxx-SKC-E-ITP-B071_WS077-50008 R5.0 and IRF: __-395 (attached). NOTE: This has been internally inspected by __ - See attaches IRF.
| 03SR - Stations (RfL) | Cxxx-NCR-002846 | NCR | Impact and Strength, Adhesion, and Roughness testing not completed on installed screed. |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-04-02 | 2018-06-08 13:29 | 67 | 2018-03-05 14:30 | Architectural - Flooring | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A planned Crossrail surveillance was undertaken on 15th February 2018 to look at installation associated with screeding and tiling at Paddington Station, in particular Concourse and Platform. A request was made for Screed Test Results for Testing completed on the installed Screed as required by Architectural Specification Section JM10 (Screeds); this being Impact and Strength Adhesion, Slip Resistance and Roughness testing as stated below. The Contractor could only supply Test Results for Impact and Strength results for the platform screed. On discussion, it was identified that no Screed Testing had been completed to ensure compliance with the above. No agreement relaxing such requirements existed, i.e. FCD.
| 03SR - Stations (RfL) | Cxxx-NCR-002847 | NCR | Damaged drop rod - __ smoke extract ductwork (PSE I #778) |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-05-20 | 2018-05-24 13:51 | 4 | 2018-03-06 10:42 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Damaged support drop rod on the smoke extract ductwork, within the PSE-I (#778); observed by CRL on 05-March-2018. See attached photos. To date, smoke extract ductwork within PSE-I and PSE-II has not been offered up for CRL IRF inspection.
| 03SR - Stations (RfL) | Cxxx-NCR-002848 | NCR | Loose mez flange clamps - Concourse West - PSE I |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-05-01 | 2018-05-14 14:33 | 13 | 2018-03-08 13:17 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Loose mez flange clamps were identified when spot checks were undertaken on the 1800x1800 smoke extract ductwork in PSE I - joint identified on the attached drawing. The clamps were only found to be loose above the duct. These works were not offered to __//CRL for inspection however due to the inaccessibility of the location it was agreed by all parties (__, __, and CRL) that works (insulation) can continue on the provision the works are snagged by __ and found to be acceptable prior to insulation.
| 03SR - Stations (RfL) | Cxxx-NCR-002849 | NCR | Removal of CMS after cabling |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-09-19 | 2018-09-10 07:32 | -9 | 2018-03-08 11:54 | Electrical - Cable Management | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | CMS has been removed while cabling has been complete to access locations above.
| 03SR - Stations (RfL) | Cxxx-NCR-002851 | NCR | Incorrect recording and reporting of monitoring data for the Crossrail Arch |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2018-04-20 | 2018-04-18 14:16 | -2 | 2018-03-08 14:05 | Civil - Structural Engineering | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | The data that is being recorded and presented in the CTC I&M weekly report is incorrect and not as per Action Plan for __ Assets and Instrumentation and Monitoring Plan (Cxxx-SWN-SRGN-B071-50014). The trigger levels are set at 3mm/m and 5mm/m rotation this is incorrect. The trigger levels should be net horizontal movement of 5mm on GL 74 and 91 and 10mm on the rest. This could potentially mean that trigger levels have been exceeded.
| 03SR - Stations (RfL) | Cxxx-NCR-002852 | NCR | Intermediate Level Corridor - Access & Maintenance Issues - High Level CMS |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-06-30 | 2019-12-11 17:42 | 529 | 2018-03-08 15:44 | Electrical - Cable Management | 5000 |  | Design | Use As-Is | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | As identified under Inspection Request Form __-386. There are a number of areas within the intermediate level corridor where access to previously IRF'd high level CMS has been restricted due to installation of bracket work to support lower level CMS (see attached email). Cxxx were asked to demonstrate if access was achievable, which was carried out on 16/02/18 and is evidenced within the attached videos. It was proven access was not achievable from a one man MEWP. However, Cxxx have now stated access is achievable from a fixed scaffold, this has not been demonstrated and CRL believe the use of fixed scaffolding cannot achieve the required access to these trays.
| 03SR - Stations (RfL) | Cxxx-NCR-002853 | NCR | First fix sign |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-09-26 | 2019-04-02 08:05 | 188 | 2018-03-10 15:18 | Architectural - Signage | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Please find NCR, in relation to projecting sign installed at platform level. The sign has been fixed to the concrete wall, due to the edge distance being to close the fixing has split the concrete as it is outside the reinforcement area. __ action: This situation was discussed with __ prior to him leaving the project, he confirmed the blast/structural reports confirm 4 fixings are sufficient for this sign. __ to provide the extract which confirms this, the bolt can then be removed and the crack can be filled using a resin to correct the defect.
| 03SR - Stations (RfL) | Cxxx-NCR-002854 | NCR | Platform Level - Access & Maintenance Issues - High Level luminaires over BLL Escalators |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-06-26 | 2018-08-28 09:32 | 63 | 2018-03-12 15:10 | Electrical - Lighting | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | As identified under Inspection Request Form __-389. CRL have raised the question of access & maintenance of the high level luminaires and coffer trunking over the BLL escalators. Cxxx have responded stating access will be captured within the O&M manual for access and maintenance to CMS systems. There is no evidence of any agreement in place for this or how this will be achieved.
| 03SR - Stations (RfL) | Cxxx-NCR-002855 | NCR | No MCR in place for attenuators being installed on site |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-05-30 | 2018-06-29 14:37 | 30 | 2018-03-13 14:00 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Attenuators being installed on site for Fans and AHU do not have an approved MCR. A sample material observation was carried out by CRL and found that for Smoke Extract System (West) attenuator ATTN03/SEF/W, make / model: Caice EG05V/--/L/SF/X; was in line with the latest accepted attenuator schedule Cxxx-SKC-M-TSC-B071_WS077-50010 Rev. 2.0. However, it was in line with CRL-MCR-2192, which listed different model (EG03V/--/L/SF/X). Also the dimensions and weights were different between schedule and MCR. A sample check of other attenuators found similar discrepancies between schedule and MCR-2192
| 03SR - Stations (RfL) | Cxxx-NCR-002856 | NCR | Paid Lift 8&9 - Cast in Soffit Sockets |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-06-20 | 2018-12-10 14:27 | 173 | 2018-03-13 14:44 | Civil - Civil Engineering General | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | During the installation of the Paid Lift Structural Steel, and Glazing Support, a number of the cast in sockets used to fix steel to concrete have refused bolts. A mark up of the affected areas is attached.
| 03SR - Stations (RfL) | Cxxx-NCR-002858 | NCR | Paid Lift 8&9 - Glazing Support Track Support |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-06-28 | 2018-11-21 11:37 | 146 | 2018-03-13 15:54 | Civil - Civil Engineering General | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | As can be seen in the attached picture, the North Eastern Structural Column on Platform has had one of its glazing support track support arms welded incorrectly at manufacturing. The glazing support track is supposed to fit flush onto the support arm.
| 03SR - Stations (RfL) | Cxxx-NCR-002859 | NCR | Ductwork installation works progressing on site without __ fabrication drawings |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-08-27 | 2018-05-24 15:14 | -95 | 2018-03-13 16:42 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Management Problem - Other management problem | Completed |  | Ductwork installation works progressing on site without __ fabrication drawings being submitted to CRL. CRL has received only a fraction of __ fabrication drawings for the ductwork, on RIR Cxxx-SKC-Z-LRG-B071_WS077-50062 rev. 2. This features only 14 drawings covering Intermediate East and risers. Therefore, there are no drawings to cover ductwork systems including smoke extract system, pressurisation west, supply air west etc.
| 03SR - Stations (RfL) | Cxxx-NCR-002860 | NCR | Installation of __ claddings on site without drawings available to the PM team |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2018-07-25 | 2018-08-20 16:36 | 26 | 2018-03-13 16:44 | Architectural - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | __ cladding and support frameworks are being installed on site, however the RIR Cxxx-SKC-Z-LRG-B071_WS077-50053 \ 50063 for __ remains as a placeholder. All drawings are to be issued for Construction and published on eB
| 03SR - Stations (RfL) | Cxxx-NCR-002861 | NCR | Installing cable where there is no CMS |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2018-07-10 | 2018-08-28 09:33 | 49 | 2018-03-13 17:16 | Electrical - General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The earthing cable installed at the west end of intermediate level is installed on bare hangers with cable tray missing. This contravenes the Quality Management Plan and shows that ITP hold point on the CMS was not applied.
| 03SR - Stations (RfL) | Cxxx-NCR-002862 | NCR | Incorrect Skirting Installation in the Bakerloo Line Link |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-07-16 | 2018-08-21 15:15 | 36 | 2018-03-16 14:24 | Architectural - Flooring | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Skirting along one side off the wall within the Bakerloo Line Link bows 8mm in a localised area, reducing the width of the Bakerloo Line Link from 3200mm to 3192mm. Each end of the link is installed correctly, however spanning over 10m, the skirting has an 8mm deviation from design.
| 03SR - Stations (RfL) | Cxxx-NCR-002863 | NCR | Not complying with Quality Management System - Cutting holes in trunking after wiring has been installed |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-06-30 | 2018-08-31 15:30 | 62 | 2018-03-20 11:27 | Electrical - Cable Management | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | There are a number of instances where, upon an invite to witness the CMS installation, it has been noted the wiring has already commenced prior to the final installation of the secondary CMS system (conduit boxes/adaptable boxes) has not been drilled into the trunking. The is contrary to the agreed RAMS Cxxx-SKC-O1-GMS-B071_WS077-50340.
| 03SR - Stations (RfL) | Cxxx-NCR-002864 | NCR | Damage to Air Handling Unit (AHU01/W) |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-07-03 | 2018-10-22 07:48 | 111 | 2018-03-20 11:39 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Air Handling Unit (AHU01/W), which is being stored unprotected in FAN-I has damage to a number of panels and seal (see attached photos).
| 03SR - Stations (RfL) | Cxxx-NCR-002865 | NCR | Damage to smoke extract attenuators |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-07-03 | 2018-08-10 15:27 | 38 | 2018-03-20 11:52 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A number of the smoke extract attenuators have damage to them. See attached photos of example ATTN01/SEF/E located in PSE-II.
| 03SR - Stations (RfL) | Cxxx-NCR-002866 | NCR | SOR Room Chasing into lignacite blockwork |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-10-06 | 2019-03-20 15:10 | 165 | 2018-03-20 14:11 | Architectural - Brickworks/Blockworks | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The current W.I requires 140mm blockwork to be installed in the BoH room, SOR, on intermediate level. In order to accommodate MEP services, the block work has been chased: - South wall - up to 55mm - East and West wall - 40mm this works were carried out with verbal confirmation from the manufacturer but not formal RFI confirmation. will submit __ assurance once received.
| 03SR - Stations (RfL) | Cxxx-NCR-002867 | NCR | Blank __ Departure Rd combined service section drawings |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-07-03 | 2018-07-31 08:10 | 28 | 2018-03-20 16:33 | Mechanical - Mechanical Engineering General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The following are an example of __ Departure Rd combined service drawings, that are on eB with blank content: Cxxx-SKC-Y-DDA-M171_2-69246 Cxxx-SKC-Y-DDA-M171_2-69247 Cxxx-SKC-Y-DDA-M171_2-69248 Cxxx-SKC-Y-DDA-M171_2-69249 Cxxx-SKC-Y-DDA-M171_2-69250 Cxxx-SKC-Y-DDA-M171_2-69251 Cxxx-SKC-Y-DDA-M171_2-69252 Cxxx-SKC-Y-DDA-M171_2-69253 Cxxx-SKC-Y-DDA-M171_2-69254 Cxxx-SKC-Y-DDA-M171_2-69255 Cxxx-SKC-Y-DDA-M171_2-69256 Cxxx-SKC-Y-DDA-M171_2-69257 Cxxx-SKC-Y-DDB-M171_2-60120 Cxxx-SKC-Y-DDB-M171_2-60121 Cxxx-SKC-Y-DDB-M171_2-60122 Cxxx-SKC-Y-DDB-M171_2-60123 Cxxx-SKC-Y-DDB-M171_2-60124 Cxxx-SKC-Y-DDB-M171_2-60125 Cxxx-SKC-Y-DDB-M171_2-60126 Cxxx-SKC-Y-DDB-M171_2-60127 Cxxx-SKC-Y-DDB-M171_2-60128 Cxxx-SKC-Y-DDB-M171_2-60129 Cxxx-SKC-Y-DDB-M171_2-60130 Cxxx-SKC-Y-DDB-M171_2-60131 Cxxx-SKC-Y-DDB-M171_2-60132 Cxxx-SKC-Y-DDB-M171_2-60133
| 03SR - Stations (RfL) | Cxxx-NCR-002868 | NCR | use of galvanised CMS in pump sump |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2018-05-23 | 2018-08-10 08:18 | 79 | 2018-03-21 15:09 | Electrical - Cable Management | 10000 |  | Design | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | Galvanised CMS has been used in the pump sump rooms contrary to specification. the agreed solution resulting from Cxxx-EWN-02117 dated 19.1.17 was to install stainless steel.
| 03SR - Stations (RfL) | Cxxx-NCR-002869 | NCR | Water mist system instsalled on site without ITP, MCRs or design acceptance |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2018-08-10 | 2019-03-02 10:21 | 204 | 2018-03-26 08:47 | Fire - Suppression | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | The water mist system is currently being installed on site, however the ITP hadn't been submitted to the PM team, the MCRs are not on eB and the DDCD (design assurance) is not in place.
| 03SR - Stations (RfL) | Cxxx-NCR-002870 | NCR | Canopy - Cantilever Cladding Bullnose Welded Studs |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-05-26 | 2018-04-26 15:19 | -30 | 2018-03-27 11:42 | Architectural - General | 2500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The welded studs to the aluminium cantilever bullnose were tested to confirm their capacity. The manufacture’s concluded the following are two tests that could be considered in terms of testing bolt capacity for these panels. • A pure tension test of 1KN. ( The bullnose panels studs in question receive tension) • A more stringent bending test was brought into the testing via a torque bending test using 3N-m. From factory testing conducted, the conclusion was that any bolt that passed the torque bending test would more than pass the tension test. Similarly, any bolt that failed the torque bending test would most likely have passed the tension test. Thus on site, the more stringent test, the torque bending test was carried out. On site, this torque bending test was carried out within the elastic range of the welded studs (non-destructive). The studs that are on site are not affected by the torque bending test. That means their capacity is not reduced. EN ISO 14555 Welding ― Arc stud welding of metallic materials chapter 11 Examination and testing contains the test carried out. Page numbers 16 and 20 of the standard attached show the “Torque wrench for bend testing” carried out. Tested on site were 50 bullnose panels which is over 50% of the in total 92 bullnose panels. 28 out of 403 studs (on these 50 panels) did not pass the more stringent torque bending test. That is under 7%. As mentioned previously, from pre-testing carried out in the workshop / factory, the ‘not-passing’ percentage for the 1kN tension test would be significantly less than that ‘not-passing’ the torque test. Please note, there are panels with studs missing and therefore in the calculations (attached) and summarised in the technical requirements section of this NCR, takes into account the worst case (28% capacity) for a stud missing.
| 03SR - Stations (RfL) | Cxxx-NCR-002871 | NCR | GFRC Sub-structure |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-04-30 | 2018-05-01 16:26 | 1 | 2018-03-26 12:58 | Architectural - Glazing | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | started fabrication of the GFRC substructure steelwork without an approved WPS/WPQR. Welding procedure Cxxx-SKC-O-TSC-B071_WS077-51412, was raised retrospectively. This document has been code 1 approved. As a formality, are raising the NCR. Please review and consider for closure.
| 03SR - Stations (RfL) | Cxxx-NCR-002872 | NCR | Non compliance with quality plan - __ tubular soffit |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2018-07-31 | 2018-12-19 13:59 | 141 | 2018-03-26 13:26 | Architectural - Ceilings & Soffits | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | The __ tubular soffit has commenced on site. The acoustic cladding associated with this has not been fitted in accordance with the gated design which states acoustic lining to be cut back locally for the MEP trunking. On site the lining is omitted, exposing the concrete soffit. Further investigation shows that there is no accepted DDCD, RIR or drawings for this work, although a readiness to start work has been signed off without informing the Project Manager of the contraventions in the Contractor's Quality Plan. The trunking is galvanised and will 'shine' through the tubular soffit. The works information states; JH11.1202 Services a) Systems shall accommodate services, as indicated in the Services Engineer's Works Information, in a concealed manner to the acceptance of the Project Manager. Galvanised trunking does not fulfil this requirement and has not been accepted by the Project Manager
| 03SR - Stations (RfL) | Cxxx-NCR-002873 | NCR | Utilisation of mixed cables within a common single system |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-10-01 | 2018-09-07 16:05 | -24 | 2018-03-26 14:23 | Electrical - Cable Management | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | The sub-contractor has bee instructed to use Exane version 1.5mm2 Brown cable, this has been mixed with previously installed __, also other cores within the system are still __ Cable i.e. Neutral (blue) and Protective Conductor/Earth (green/yellow).
| 03SR - Stations (RfL) | Cxxx-NCR-002875 | NCR | Spacing between MEPH in Floor Penetration - Firestopped with Minimum Spacing not Provided |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-06-15 | 2018-05-18 09:18 | -28 | 2018-03-27 10:52 | Fire - Compartmentation | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A minimum spacing of 20mm was not provided between MEPH within a floor penetration at gridline 1 on concourse level. This aperture has then been firestopped.
| 03SR - Stations (RfL) | Cxxx-NCR-002876 | NCR | Stainless Steel Fins |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2018-07-31 | 2018-12-07 14:34 | 129 | 2018-03-29 13:50 | Architectural - General | 5000 |  | Design | Use As-Is | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | Further to a joint site inspection on 27-03-2018 to view the east and west vent shaft head houses, it would appear that the stainless steel fins fabricated and installed differ from those in the gated design. Drawing Cxxx-SKC-A-DDD-M171_Z-96002 details a stainless steel fin AM-105 with a closer piece at the rear and appears to be 2 separate SS angle sections bolted to the structure. What has been installed on site is different in that it is SS strips with brackets welded and bolted to the structure with no closer piece at the rear. See attached photo. The NCR is raised as this site installation is a change to the gated design, I have no access to and can't locate any updated drawings on eB
| 03SR - Stations (RfL) | Cxxx-NCR-002877 | NCR | Room OHLE 1 MS146 Cabinet Drilled/Damaged by others. |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-08-03 | 2018-09-18 12:48 | 46 | 2018-04-05 11:30 | Electrical - General | 2500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | __ NCR - __-NCR-00078 Applies Critical OHLE switches have been found to have been drilled and defected (see attached photo). Items (OHLE1/2to be assessed prior to being replaced or re-tested. __/CRL/__ request all T1 contractors are re-brief to avoid re-occurrence ie cabinets are not to be drilled whilst control equipment is in place.
| 03SR - Stations (RfL) | Cxxx-NCR-002878 | NCR | Grooved pipe galvanised coating coming away |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-10-01 | 2018-09-18 13:18 | -13 | 2018-04-05 15:08 | Mechanical - Piping | 1500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Corrosion protection coming away on the inside and outside of the grooved portion of the galvanised pipework. The cut ends also have corrosion protection coming away. See attached photos taken from site on 05-April-2018, intermediate corridor outside CER IV-CWU.
| 03SR - Stations (RfL) | Cxxx-NCR-002879 | NCR | VSHH Cladding Washer Size |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-05-11 | 2018-05-10 13:17 | -1 | 2018-04-10 11:15 | Civil - Civil Engineering General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Further to a joint site inspection on 27-03-2018 to view the east and west vent shaft head houses, concerns were raised regarding the suitability of the washer sizes used for a slotted hole. Fixing Schedule (Cxxx-SKC-Y-DDJ-M171_1-41950, 51, 52) showed the correct HILTI bolt assembly had been installed; however, no specific details was provided on washer requirements. Washer requirements to be confirmed with designers and rectified if required.
| 03SR - Stations (RfL) | Cxxx-NCR-002880 | NCR | __Water Mist Bracketry Install Intermediate Level STR II |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-07-09 | 2018-08-08 11:04 | 30 | 2018-04-10 12:42 | Mechanical - Mechanical Engineering General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Water Mist pipework bracketry (STR II) fixed into Fire stopping - see attached picture.
| 03SR - Stations (RfL) | Cxxx-NCR-002881 | NCR | Critical Cooling Units (CCUs) clashing with CMS in plant cooling rooms |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-08-24 | 2018-09-10 08:02 | 17 | 2018-04-10 15:10 | Mechanical - Heating Ventilation & Air Conditioning | 2500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Critical Cooling Units (CCUs) clashing with CMS in plant cooling rooms. It is not possible to open CCU cabinet doors as they are clashing with CMS and lighting. High level pipework valves are also inaccessible in these plant rooms. Rooms observed with the clashes are as follows: ESR-I CWU FCR-II CWU TR-III CWU TR-IV CWU See attached photos.
| 03SR - Stations (RfL) | Cxxx-NCR-002882 | NCR | __ P Status Elect/Mech & Public Health drawings issued for Construction |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-09-28 | 2019-08-02 11:54 | 308 | 2018-04-11 10:55 | Electrical - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | __ P Status issued as current C status to follow CI to follow List of drawings attached below
| 03SR - Stations (RfL) | Cxxx-NCR-002883 | NCR | Canopy - Damaged Glazing Panels |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-09-30 | 2018-08-24 14:12 | -37 | 2018-04-20 12:30 | Architectural - Glazing | 20000 |  | Damaged | Rework | 2 (6-60k) | Complete | Design Problem - Other | Completed |  | 3 No. glazing panels to the canopy have been damaged post installation. The location of these panels are shown on the attached marked up drawing. The references are Y at GL70-72, panel 14-01 (GL76-78) and panel 18-05 (GL84-86). The replacement panels have been ordered and the damaged panels replaced when the replacement panels are manufactured
| 03SR - Stations (RfL) | Cxxx-NCR-002884 | NCR | Insufficient space to fire stop ductwork in SWC-II |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-10-31 | 2018-09-18 12:49 | -43 | 2018-04-17 13:35 | Mechanical - Heating Ventilation & Air Conditioning | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | There is less than 50mm clearance between the top of the ductwork and the 2 __ lintels in the SWC-II room (see photos). Therefore, it will not be possible to fire stop the ductwork at its current level.
| 03SR - Stations (RfL) | Cxxx-NCR-002885 | NCR | FCR II CWU 931 Removal of FIRE CAbling CMS |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-07-21 | 2018-11-12 14:56 | 114 | 2018-04-21 08:07 | Electrical - General | 5000 |  | Supervision/Management | Rework | 3 (3-6k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Installed CMS in FCR II CWU 931 have been removed by others without informing __ Fire, Scott Deamer (Package Manager) or QA. See attached pic Fire cables left unsupported.
| 03SR - Stations (RfL) | Cxxx-NCR-002886 | NCR | Canopy - Painting to Columns |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-11-30 | 2020-11-10 09:49 | 711 | 2018-04-23 11:52 | Architectural - Finishes | 5000 |  | Damaged | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | The canopy columns have slight damage to the paintwork during transportation. The paintwork will be repaired inline with the N4 specification after the urban realm works are completed in the area.
| 03SR - Stations (RfL) | Cxxx-NCR-002887 | NCR | Canopy - Water Test |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-07-04 | 2018-10-25 09:17 | 113 | 2018-04-24 17:19 | Architectural - Glazing | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the water test, it was observed that water was was making its way through the joint near the gutter beam / MMH column at GL 56.
| 03SR - Stations (RfL) | Cxxx-NCR-002888 | NCR | Unsupported PSD Erth Cables PES II & III |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-05-25 | 2018-08-20 16:39 | 87 | 2018-04-25 08:27 | Electrical - Cable Management | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | PSD Earth Cables in PES II & III are unsupported see pics IMG_0956 (PES II) & pic IMG_0993 (PES III).
| 03SR - Stations (RfL) | Cxxx-NCR-002889 | NCR | BLL Box - GFRC Support Framing - Bolted fixing washers where slotted |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-05-31 | 2018-08-20 16:46 | 81 | 2018-04-25 14:28 | Architectural - Walls | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | The vertical s/s support frames for the GFRC panels are predominantly fixed using expanding threaded stud anchors through a horizontal slot in the pressed bracketry. A further large format square washer sits over the slot, some of which have a circular hole sized for the stud. This arrangement is terminated by a small circular washer and nut and is perfectly satisfactory. However, in the majority of fixing locations, the square washer features a large slot matching its bracket behind. These too are terminated with a small washer and nut which does not accord with industry standards and good practice resulting in a fixing of reduced capacity (both in terms of pull out and particularly under blast conditions. See attached photo.
| 03SR - Stations (RfL) | Cxxx-NCR-002890 | NCR | Lack of Waterproofing Protection to VSHH & __ Retaining Wall |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-05-23 | 2020-02-06 13:38 | 624 | 2018-04-25 15:17 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Protective measures to the sprayed waterproofing membrane (Eliminator system) have not been installed as detailed in Clause KW10.3226 of Specification Cxxx-SWN-S-RSP-B071_00013 Rev4.0 to the following areas: i) Top of __ retaining wall to the north of the VSHH (U/R GL26 to 49 and GL; and GL91 to 116). ii) A range of locations around the perimeter of both the East and West VSHH at Eastbourne Terrace level.
| 03SR - Stations (RfL) | Cxxx-NCR-002891 | NCR | Lack of Waterproofing Protection to Attenuation Tanks - GL60 to 70 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-06-29 | 2018-08-08 15:46 | 40 | 2018-04-25 15:04 | Civil - Civil Engineering General | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The sprayed waterproofing membrane applied to the __ attenuation tanks between U/R GL60 - 70 has been loaded with materials prior to installation of waterproofing protection measures, resulting in potential damage to the system. Refer to attached image 20180425_085503.
| 03SR - Stations (RfL) | Cxxx-NCR-002893 | NCR | Canopy - Balustrade - WPS and WPQR |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-06-10 | 2018-06-08 13:04 | -2 | 2018-04-26 07:49 | Structural Engineering - Structural Engineering - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The Welding Procedure Specification (WPS) and the Welding Procedure Qualification record (WPQR) for the balustrade welding were not accepted prior to fabrication
| 03SR - Stations (RfL) | Cxxx-NCR-002894 | NCR | Canopy - Aluminium - WPS and WPQR |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-06-10 | 2018-06-08 13:06 | -2 | 2018-04-26 07:53 | Structural Engineering - Structural Engineering - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The Welding Procedure Specification (WPS) and the Welding Procedure Qualification record (WPQR) for the aluminium cladding welding were not accepted prior to fabrication
| 03SR - Stations (RfL) | Cxxx-NCR-002895 | NCR | VSHH Rainscreen Studs |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-08-24 | 2018-05-10 13:15 | -106 | 2018-04-26 15:45 | Civil - Civil Engineering General | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Several rainscreens have had their M6 aluminium studs affected by the anodising process; the threads have been reduced resulting in the specified M6 aluminium nuts no longer biting.
| 03SR - Stations (RfL) | Cxxx-NCR-002896 | NCR | Canopy - Access Panel - WPS |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-06-11 | 2018-06-08 13:02 | -3 | 2018-04-27 09:30 | Structural Engineering - Structural Engineering - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The Welding Procedure Specification (WPS) for the canopy access panel welding was not submitted on eB for acceptance prior to fabrication.
| 03SR - Stations (RfL) | Cxxx-NCR-002897 | NCR | Out of date drawings on eB |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-06-14 | 2018-07-24 09:44 | 40 | 2018-04-30 11:00 | Electrical - LV Equipment | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Drawings used within Method statement 'Cxxx-SKC-O1-GMS-B071_WS077-50617 ' are several revisions higher than those loaded and approved on eB. This raises questions as to if the Tier 1 contractor is working to CRL approved drawings and following their own assurance process.
| 03SR - Stations (RfL) | Cxxx-NCR-002898 | NCR | Canopy - Water Leakage through Cantilever Cladding |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-06-21 | 2018-07-02 14:42 | 11 | 2018-04-30 14:42 | Structural Engineering - Structural Engineering - General | 2500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | have become aware of a minor water leak through the Cantilever cladding, around the Balustrade posts, along GL50 & GL90. This causes water to drip from the outside edge of the rafters along these Grid lines.
| 03SR - Stations (RfL) | Cxxx-NCR-002900 | NCR | MCR 5941 not approved before install |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-06-13 | 2018-05-24 16:08 | -20 | 2018-05-03 13:36 | Mechanical - Mechanical Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | MCR for Alloway anti vibration mounts in process - NCR to close once CRL approve MCR
| 03SR - Stations (RfL) | Cxxx-NCR-002901 | NCR | DC8 & DC9 Cabinet Damage to __ F/I Items |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-10-31 | 2019-10-15 13:36 | 349 | 2018-05-03 14:35 | Communications and Control Systems - General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | __ F/I DC8 & DC9 Cabinets damaged during installation. See attached pictures.
| 03SR - Stations (RfL) | Cxxx-NCR-002902 | NCR | support frames to water chiller manifold - pump room |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2018-09-28 | 2018-08-31 15:57 | -28 | 2018-05-09 12:51 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The support frames for the chiller manifolds were installed in unistrut and there appears to be no design in place, despite requests for the design calculations \ drawings. During an inspection on 3-May-18 the supports were visibly deflecting under load even though the installation is incomplete and not charged with water.
| 03SR - Stations (RfL) | Cxxx-NCR-002903 | NCR | Vent Head Houses - GFRC design for fins |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2018-07-31 | 2019-07-06 11:19 | 340 | 2018-05-09 13:01 | Architectural - Finishes | 500000 |  | Material | Rework | 1 (>60k) | Complete | Design Problem - Other | Completed |  | The Supervisor's Representative has been given informal results of bending tests carried out following the issue of Cxxx-PMI-1342 which show that the results do not meet the expected values for the MOR and __. In addition, the GFRC elements do not have a fibreglass mesh which is a requirement of the Site Specific Loading Requirements when using short fibres.
| 03SR - Stations (RfL) | Cxxx-NCR-002904 | NCR | Damaged Seal on Platform Access Hatches |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-02-14 | 2021-01-27 15:12 | 348 | 2018-05-09 13:00 | Architectural - Flooring | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Damage has occurred to the rubber seal on the bottom side of the escalator. Rubber seal to be ordered from __ and reinstalled by __.
| 03SR - Stations (RfL) | Cxxx-NCR-002905 | NCR | Luminaires below escalators - Platform areas |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2018-09-28 | 2018-08-31 13:44 | -28 | 2018-05-09 13:43 | Electrical - Lighting | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The Luminaires currently being fitted to the underside of the escalators at platform level are white and fixed with galvanised unistrut. The luminaire schedule shows these as finished in silver.
| 03SR - Stations (RfL) | Cxxx-NCR-002906 | NCR | Urban realm constuction started to 'P' status drawing |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-08-08 | 2018-08-21 15:09 | 13 | 2018-06-01 15:04 | Architectural - Urban Realm | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Construction has starting within the Urban realm with 'P' Status drawings
| 03SR - Stations (RfL) | Cxxx-NCR-002907 | NCR | Inaccessible fixings to GFRC cladding & removal methodology - contrary to cleaning and maintenance strategy |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2018-08-03 | 2019-06-08 08:27 | 309 | 2018-05-11 09:28 | Architectural - Urban Realm | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | 1) Review of the cleaning and maintenance strategy has revealed that GFRC fixings are to checked for tightness every 6 years. The majority of these bolts are inaccessible. 2) It has been stated that the installation and removal of GFRC fins has to be carried out with a specialist frame. This is not clear in the cleaning and maintenance strategy 3) The cleaning and maintenance strategy describes the fins installed as an integral part of the rainscreen cladding assembled offsite - these are completely independent
| 03SR - Stations (RfL) | Cxxx-NCR-002908 | NCR | Vent Head House - GFRC fins - DDCD comments do not match design calculations |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2018-06-29 | 2018-07-03 08:16 | 4 | 2018-05-11 13:42 | Architectural - Urban Realm | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | 1) A DDCD has been produced to assure the F2 fin design, however wind loads used within the F2 calculations do not match the responses made to the __ comment that wind loads appear low.
| 03SR - Stations (RfL) | Cxxx-NCR-002909 | NCR | Bakerloo Link (BLL) Addit Drain Pipe channel |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-09-14 | 2018-08-21 15:03 | -24 | 2018-05-17 13:47 | Civil - Drainage | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | The Drainage Pipe passing through the Bakerloo Box Addit RC Wall from the Bakerloo Link draining into the Cxxx Ronafix Drainage channel has been incorrectly cut flush to the RC wall instead of the top half to allow GFRC installation. Please see attached photo mark up. In order to create the channel propose to form a channel using Monomix HD as per attached mark up. Please confirm if this is acceptable.
| 03SR - Stations (RfL) | Cxxx-NCR-002910 | NCR | Ductwork Access Hatches not in accordance with Industry Standards |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2020-04-30 | 2020-11-18 13:19 | 202 | 2018-05-17 15:18 | Mechanical - Heating Ventilation & Air Conditioning | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | Access hatches in large ductwork are below the minimum industry standard and not aligned with cleaning and maintenance strategy
| 03SR - Stations (RfL) | Cxxx-NCR-002911 | NCR | Deficient Fire Main support system |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-11-30 | 2019-03-16 12:21 | 106 | 2018-05-18 14:46 | Fire - Fire Systems & General | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The station and tunnel falling mains are not being installed in line with the F2 detailed drawings from __. For example: - Intermediate level GL18, the support bracketry appears inadequate and has not been installed in line with __'s support details. Refer to attached photos, and drawings: Cxxx-SKC-E1-DWG-B071_WS077-50030 Rev. P01; Cxxx-SKC-E1-DWG-B071_WS077-50027 Rev. P03; Cxxx-SKC-Y-DDA-M171_3-67565 P07 - The 200mm diameter tunnel falling main has not been installed to 'Support B' detail (see Cxxx-SKC-E1-DWG-B071_WS077-50027). Also, Support B detail does not appear on support detail drawing Cxxx-SKC-E1-DWG-B071_WS077-50030. In addition, thrust force calculations have not been formally submitted to CRL.
| 03SR - Stations (RfL) | Cxxx-NCR-002912 | NCR | Stacked fan removal |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-12-25 | 2020-03-15 16:18 | 446 | 2018-05-29 13:42 | Mechanical - Heating Ventilation & Air Conditioning | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | In a number of mechanical equipment plant rooms (PSE, PFR and AAR), the duty / standby fan arrangement is that the fans are stacked, with the upper fan sitting on a frame that straddles the lower fan. The Project’s Access and Maintenance Strategy (Cxxx-SKC-A-STP-B071_WS077-50004 Rev. 19.0) describes both the procedure for removing the lower fan or the upper fan, without the upper fan or lower fan respectively being disturbed. Following CRL site walks, it is evident that the upper fan will not be able to be removed using the procedure described in the Access and Maintenance Strategy. This is due to CMS and lighting adjacent to stacked fans clashing with the pallet stacker methodology described in the removal of the upper fan. Confirm the pallet stacker equipment that will be used to remove the fans, considering the fans weigh circa 750kg. In addition, confirm there is sufficient space to operate the pallet stacker when the fan is retracted. CRL observed the following areas where the removal of the fans needs to be coordinated with the MEP services in the room: * Smoke Extract Fan rooms West and East (PSE-I and PSE-II) – example photo Smoke Fan in PSE-I * Pressurisation Fan Rooms West and East (PFR-I and PFR-II) - example photo Air Release Fan West in PFR-I * Air Release Fan Room East (AAR Fan) - example photo Air Release Fan East
| 03SR - Stations (RfL) | Cxxx-NCR-002913 | NCR | Damaged Cable Tray - Intermediate Corridor SR LV IA & MIST II |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-09-28 | 2018-08-31 13:49 | -28 | 2018-05-22 13:19 | Electrical - Cable Management | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Whilst carrying out an inspection this morning with CRL we noticed two cable trays have been damaged by what appears to be by a MEWP. The trays and locations are as follows: • 100mm FA cable tray outside SR LV I A – IMG_1799; • 300mm Radio cable tray outside MIST II – IMG_1803 & IMG_1804. Can the length of each of these cable trays be replaced.
| 03SR - Stations (RfL) | Cxxx-NCR-002914 | NCR | Deleterious materials - PES sound insulation not encapsulated |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2018-07-31 | 2021-05-28 10:29 | 1032 | 2018-05-22 16:28 | Architectural - General | 25000 |  | Design | Rework | 2 (6-60k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | PES screens incorporate a mineral fibre sound absorbent material. This is encapsulated on the front face but there are no measures to prevent fibre migration on the rear face. There is only an RIR placeholder on eB for these drawings making them near impossible to find on eB.
| 03SR - Stations (RfL) | Cxxx-NCR-002915 | NCR | VSHH GFRC mix design and requirement for glass fibre mesh |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2018-07-27 | 2019-07-06 12:14 | 344 | 2018-05-22 16:43 | Architectural - Security | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | The GFRC fins have been manufactured using 12mm fibre length without a mesh on the rear face. Architectural specification Cxxx-SKC-A-RSP-B071_WS077-50003 JH40.1409 e) vii) states; vii) Fibre length: 30mm to 50mm, except where a glass fibre mesh is introduced to the rear face of the element (East and West Vent Shaft Head House only), in which case fibres in the rest of the unit should have a minimum length of 12mm
| 03SR - Stations (RfL) | Cxxx-NCR-002917 | NCR | GFRC BLL - Straightness of Panels |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-07-28 | 2018-08-21 15:01 | 24 | 2018-05-23 11:30 | Architectural - Finishes | 3000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The straightness tolerances for the GFRC panels as specified in JH40.3203 of the architectural specification should be: Up to 3m = 4mm 3m to 6m = 6mm have noted, some of the GFRC panels currently being installed in the Bakerloo Box have not been manufactured in accordance with the specification. Upon inspection, the panels appear to be concave in profile, in both axis, horizontal and vertical. The worst case panel is along the horizontal plane and is measuring from the straight edge 10mm to the face of concrete. We are currently working with our contractor to find a solution to the problem.
| 03SR - Stations (RfL) | Cxxx-NCR-002919 | NCR | No design calculations for pumped main installation |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2018-09-26 | 2019-03-23 10:40 | 178 | 2018-05-26 08:29 | Mechanical - Public Health Engineering | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Over the past 3 months the Supervisor's Representative has requested calculations to demonstrate that the pumped rising mains are adequately designed to resist thrust and dead weight. to date the have not been able to provide these calculations or drawings showing the designed arrangements. Increasingly there is evidence of ad-hoc unistrut solutions.
| 03SR - Stations (RfL) | Cxxx-NCR-002921 | NCR | Damage to Lintel in TR III (3) During Protect Pipe Install |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-08-08 | 2018-08-08 11:01 | 0 | 2018-05-30 13:55 | Architectural - Brickworks/Blockworks | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the installation of the __fire suppression pipe, the subcontractor fixed a section of unistrut to the concrete lintel. This has caused damage that can be seen in the attached photos.
| 03SR - Stations (RfL) | Cxxx-NCR-002922 | NCR | Damaged Access Hatch Frames |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-06-29 | 2019-03-18 14:59 | 262 | 2018-05-30 16:02 | Architectural - Flooring | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | An access hatch frame and screed on Platform FoH has been damaged whilst operatives used the hatches as access to sub-platform. See photo attached.
| 03SR - Stations (RfL) | Cxxx-NCR-002923 | NCR | Water Ingress Platform Level CSR I |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-12-21 | 2018-12-15 09:03 | -6 | 2018-05-31 07:22 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Please see attached picture in Platform level West CSR 1 - showing water ingress. We are also forecast a major rain fall in London this morning please can mitigation be put in place to reduce the risk of potential damage to already installed equipment. We have equipment in risers that will be damaged by this water and may need replacing.
| 03SR - Stations (RfL) | Cxxx-NCR-002924 | NCR | Crossrail Arch - GL83 Padstone TOC |  | Contr | SKC | PAD - Paddington Station (West) |  | 2021-01-21 | 2021-01-19 12:06 | -2 | 2021-01-19 10:11 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Concrete poured low - 0.023mm
| 03SR - Stations (RfL) | Cxxx-NCR-002926 | NCR | NR Earthing schematic at P Status |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-12-31 | 2019-09-13 11:00 | 256 | 2018-06-01 09:07 | Electrical - Earthing & Bonding | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | NR Earthing Schematics issue at P Status under -CI-007524: MEPH SIO 1951 - Urban Realm RIR 1 - Supply and Install Cxxx-SKC-E-DDE-M171_Z-50560 P10 attached Cxxx-SKC-E-DDE-M171_Z-50572 P09 attached
| 03SR - Stations (RfL) | Cxxx-NCR-002927 | NCR | Fixings allowance within precast soffit - Byrnes Brothers |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-06-15 | 2018-06-04 12:14 | -11 | 2018-06-01 14:35 | Architectural - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Fixings had been cast into the precast soffit at platform level, the cast in fixings were to be used for the installation of acoustic (Spec Ref: CLG-110) & tubular (Spec Ref: CLG-103) ceilings by __. Upon development of design the setting out dimensions changed due to information obtain by __, as such the holes have now been drilled on site as opposed to utilising the precast fixings. The client identified the need to ensure the holes were filled using an approved grout, do not believe this is required as the cast in fixing are stainless steel as such this will not have an issue in terms of corrosion or the lifetime of the fixing becoming loose within the concrete. A __ drawing has been attached confirming the cast in fixing is Stainless steel. This has been discussed with the client who has accepted there is not a requirement to fill the holes as the fixing is Stainless steel. Refer to pictures attached for references of cast in fixings. NOTE: the holes will not be visible once ceilings noted above have been installed.
| 03SR - Stations (RfL) | Cxxx-NCR-002928 | NCR | cracking of long GFRC fins at top connection |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2018-08-31 | 2018-07-03 08:57 | -59 | 2018-06-01 15:32 | Architectural - Finishes | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Approximately 10 GRFC long fins have cracked when installing the top bolt and a further 11 of those installed have been found to be cracked at the top fixing.
| 03SR - Stations (RfL) | Cxxx-NCR-002929 | NCR | TR III & IV WATER MIST DAMAGE |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-11-21 | 2019-03-02 10:27 | 101 | 2018-06-02 06:56 | Mechanical - Mechanical Engineering General | 1500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Please see attached photo of damage caused to the water mist brackets and possibly the pipe work due to scaffold being erected adjacent to the pipe run. way. Probably the 4th occasion the water mist pipe and brackets have been damaged "by others".
| 03SR - Stations (RfL) | Cxxx-NCR-002930 | NCR | Damage to __Installed Fire System - Various locations |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-11-21 | 2019-03-02 10:31 | 101 | 2018-06-02 14:00 | Fire - Fire Systems & General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | At a number of locations as outlined below the __installed Fire pipework has been damaged after installation: 1. Damage to LPWM pipework on __ by others - Refer to drawing Cxxx-SKC-E1-DWG-B071_WS077-50211 - see pic EWN 0014 2. Damage to LPWM pipework on Intermediate Level corridor near riser by others - Cxxx-SKC-E1-DWG-B071_WS077-50220 - see pic EWN 0015 3. Damage to LPWM pipework on Intermediate Level corridor near Mist Room by others - Cxxx-SKC-E1-DWG-B071_WS077-50219 - see pic EWN 0016 A & B 4. Damage to LPWM pipework on __ corridor near MAE-II - Cxxx-SKC-E1-DWG-B071_WS077-50210 - see pic EWN 0021 5. Damage to LPWM pipework on Intermediate Level corridor West side - Cxxx-SKC-E1-DWG-B071_WS077-50220 - see pic EWN 0022A
| 03SR - Stations (RfL) | Cxxx-NCR-002931 | NCR | Crossrail Arch - GL83/H Trus Column (Beam Stub & Temporary Works Clash) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-09-12 | 2019-09-05 15:16 | 358 | 2018-06-14 16:07 | Structural Engineering - Steel Member | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | During installation of the GL83/H steel column a clash was identified between the permanent works steel to connection at Sub Roof level and the existing temporary works beam supporting the existing RC roof beams. This clash prevented the column from being installed in its correct position. The stub was notched by 150mm x 100mm on site as per the attached photographs. This allowed the column to be installed correctly and then allowed the Gridline H truss to be installed.
| 03SR - Stations (RfL) | Cxxx-NCR-002932 | NCR | Crossrail Arch - Structural Steelwork Protective Coating Damage |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-09-12 | 2019-09-05 15:14 | 358 | 2018-06-14 16:05 | Structural Engineering - Surface Treatment | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following the delivery of Phase 1 structural steelwork for the Crossrail Arch, it has been noted that the paint finish has been damaged from handling and transportation to a number of sections of individual steel members. A sample snap shot of photos has been attached to this NCR to reflect/capture level of damage to the protective coating.
| 03SR - Stations (RfL) | Cxxx-NCR-002933 | NCR | VSHH __ Roof - Ponding |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-09-03 | 2021-05-07 10:09 | 977 | 2018-06-05 12:35 | Civil - Civil Engineering General | 30000 |  | Workmanship | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | Minor ponding has been observed on the __ roof, consistently along the edge of the gutter eaves. Ponding is evident by presence of water during rainfall or the beginning of sediment build up.
| 03SR - Stations (RfL) | Cxxx-NCR-002934 | NCR | Pipe sleeves missing for Fire Main |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-09-28 | 2018-12-18 09:07 | 81 | 2018-06-06 15:19 | Fire - Fire Systems & General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Following CEG VAP on 22-May-2018, it was noted that in a number of locations pipe sleeves are missing for the fire main. See attached photo taken from Intermediate level GL18 in LB-S VIII
| 03SR - Stations (RfL) | Cxxx-NCR-002935 | NCR | Fire Main supported off secondary containment |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-11-21 | 2018-11-12 12:49 | -9 | 2018-06-06 15:34 | Fire - Fire Systems & General | 1000 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During a CEG VAP on 22-May-2018, it was noted that the fire main was supported from CMS containment. See attached photo from CIR-PL XVIII
| 03SR - Stations (RfL) | Cxxx-NCR-002936 | NCR | Brick Slip Panels - No provision for maintenance or inspection |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2018-09-18 | 2019-05-20 15:12 | 244 | 2018-06-07 10:42 | Architectural - Finishes | 10000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Other | Completed |  | The brick slip panels have been designed without provision for inspection or maintenance to the rear of the panels.
| 03SR - Stations (RfL) | Cxxx-NCR-002937 | NCR | BLL GFRC - Damaged panel |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-07-31 | 2018-08-28 10:03 | 28 | 2018-06-14 08:12 | Architectural - General | 1500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | At some point during the fabrication, curing, delivery of the GFRC a panel has been damaged and subsequently dented. A repair test will be completed on the condemned panel on site, offered for inspection to the CRL architects for approval. This NCR will be updated with the outcome of the post repair inspection.
| 03SR - Stations (RfL) | Cxxx-NCR-002938 | NCR | PCC Stairs - Landing Upstand Detail |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-06-26 | 2018-07-24 09:49 | 28 | 2018-06-12 15:57 | Structural Engineering - Structural Engineering - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | __ have casted the steel angle on Flight F03 at the incorrect level. Please see attached proposal to rectify the issue.
| 03SR - Stations (RfL) | Cxxx-NCR-002939 | NCR | The Contractor has Commenced manufacturing without an accepted ITP in place. |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-08-31 | 2018-10-01 15:17 | 31 | 2018-06-13 10:16 | Architectural - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A planned Crossrail surveillance was undertaken on 12th June 2018. This looked at the GFRC Cladding installation at Paddington Station – Bakerloo Interchange.. On checking the ITPs for these works it was found that the Contractor had no ITP in place for the Offsite manufacturer of the Galvanised Steelwork that supports the GFRC Cladding.
| 03SR - Stations (RfL) | Cxxx-NCR-002940 | NCR | BLL GFRC - Rejection of Silicone rubber gasket MCR |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-03-28 | 2020-03-05 14:33 | 343 | 2018-06-14 09:08 | Archaeology - General | 5000 |  | Documentation and Records | Rework | 3 (3-6k) | Complete | External Phenomenon - Other | Completed |  | are currently installing the GFRC cladding without an approved MCR for the silicone rubber gasket. The MCR was submitted to CRL on the 05/10/2017 Counter comments on the comment sheet Cxxx-SKC-O-XCS-B071_WS077-50767 were submitted on the 12/01/2018. An email off __ states extruded silicone is semi-compliant as in all other GFRC (email attached). The material has been approved at Cxxx Bond street in the exact same system. Evidence of the materials approval can be found on Cxxx-SKC-A-XCS-Cxxx-50180 and Cxxx-SKC-A-LRC-Cxxx-50051. A verbal conversation between __ and __ regarding installing the system despite the MCR not being approved was held prior to the install. It was deemed appropriate to continue installation without an approved MCR as it was deemed acceptable the product had been approved and installed at Bond Street on a much greater scale.
| 03SR - Stations (RfL) | Cxxx-NCR-002941 | NCR | VSHH Chiller Farm - Shrinkage Cracks |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-09-25 | 2020-01-31 16:39 | 493 | 2018-06-27 12:59 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Some minor shrinkage cracks have appeared on the surface of the screed in the chiller farms, both East and West. Unable to
| 03SR - Stations (RfL) | Cxxx-NCR-002942 | NCR | Contractor progressing Cladding works using un-accepted ‘P’ Revision drawings |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-12-30 | 2019-08-09 15:37 | 222 | 2018-06-19 13:40 | Architectural - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | A planned Crossrail surveillance was undertaken on 12th June 2018. This looked at the GFRC Cladding installation at Paddington Station – Bakerloo Interchange. During the surveillance it was noted that the Contractor is installing the GFRC Cladding System using unaccepted P Status installation drawings; ‘Corner Profile at End of Passage link’ Cxxx-SKC-Y-DDD-M171_7-34022 (Rev P04), ‘Passage Link South-East Orientation’ Cxxx-SKC-Y-DDC-M171_7-34005 (Rev P02) and ‘Chamfer Wall-Connection to Passage Link’ Cxxx-SKC-Y-DDD-M171_7-34017. On checking eB the drawings could not be found.
| 03SR - Stations (RfL) | Cxxx-NCR-002943 | NCR | Contractor progressing GFRC Cladding works without accepted Structural Calculations in place |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-07-17 | 2018-12-07 16:18 | 143 | 2018-06-19 14:25 | Architectural - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Management Problem - Other management problem | Completed |  | A planned Crossrail surveillance was undertaken on 12th June 2018. This looked at the GFRC Cladding installation at Paddington Station – Bakerloo Interchange. On review of ‘GFRC Site Installation’ ITP *50204, inspection number 1.3 Structural Calculations; acceptance criteria “Code 1 Acceptance”. On checking the Structural Calculations for the GFRC Cladding System it was found that ‘Structural Calculation BLL GFRC - Steelwork in Public Stairs’ Cxxx-SKC-S-XCL-B071_WS077-50152 (Rev 1) (place holder), ‘GFRC Wall Cladding Structural Calculations’ Cxxx-SKC-S-XCL-B071_WS077-50150 (Rev 1) (place holder) and Structural Calculation-Steelwork in Public Staircase’ Cxxx-SKC-S-XCS-B071_WS077-50585 (not on eB).
| 03SR - Stations (RfL) | Cxxx-NCR-002945 | NCR | The Contractor was unable to supply evidence that Bolted Connections and __ M8 Anchors have been installed correctly |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-08-31 | 2018-12-04 09:48 | 95 | 2018-06-19 14:48 | Architectural - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A planned Crossrail surveillance was undertaken on 12th June 2018. This looked at the GFRC Cladding installation at Paddington Station – Bakerloo Interchange. On Request the Contractor was unable to supply evidence that the __ HST3 M8 anchors and the galvanised primary and S/S Secondary Steelwork Bolted Connections that forms part of the GFRC Cladding System have been installed to the required Torque parameters. It was also noted that the __ HST3 M8 fixings did not form part of Cxxx-SKC-C-ITP-B071_WS077-50204 Inspection Number 5.8 Torqueing of Anchors and the Bolted Galvanised Primary and S/S Secondary Steelwork Connections had not been referenced in Cxxx-SKC-C-ITP-B071_WS077-50204.
| 03SR - Stations (RfL) | Cxxx-NCR-002946 | NCR | Cxxx North GL10 Brick slip Panel brick damaged |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-09-06 | 2020-02-08 07:36 | 155 | 2018-06-19 16:40 | Architectural - Brickworks/Blockworks | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Please refer to attached image. North GL10 Brick slip Panel brick damaged. Finished works remedial to be carry out by Thorp Installers.
| 03SR - Stations (RfL) | Cxxx-NCR-002947 | NCR | __ ductwork not independently supported |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-09-30 | 2018-11-12 12:53 | 43 | 2018-06-21 11:25 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During CRL IRF-576 witness inspection of Air Release east ductwork (in AAR FAN room); it was observed that the lower tier __ ductwork was supported from the upper tier ductwork, and therefore not independently supported.
| 03SR - Stations (RfL) | Cxxx-NCR-002948 | NCR | PCC Stairs - Damaged Stair Treads |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-07-20 | 2018-09-03 13:40 | 45 | 2018-06-22 10:09 | Structural Engineering - Pre-cast | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Precast stair has been damaged whilst lifting into Mole Hole 1.
| 03SR - Stations (RfL) | Cxxx-NCR-002949 | NCR | __ __ __ Waterproofing Damage - GL7 to 9 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-08-24 | 2018-07-18 09:44 | -37 | 2018-06-22 13:23 | Civil - Civil Engineering General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The __ __ waterproofing membrane to the d-wall capping beam between GL7 to 9 (exact extent TBC) has been damaged during excavation works for the Urban Realm and king post wall demolition. Sections of the membrane have separated from the concrete surface, compromising the integrity of the waterproofing system in this area. See Cxxx-NCR-002583 for proposed repair method.
| 03SR - Stations (RfL) | Cxxx-NCR-002950 | NCR | Long FLexes for advertising supply in the BLL Box |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-07-12 | 2018-11-15 16:01 | 126 | 2018-06-28 13:50 | Electrical - Cable Management | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | Inspection within the BLL Box showed several over length sections of flexible conduit. Supply cable had been run within the section which where not secured to the wall. The contractor is required to reduce the length of flex to a minimal. Less than 500mm should be sufficient in these locations.
| 03SR - Stations (RfL) | Cxxx-NCR-002951 | NCR | Cxxx Precast Stair Installation - Damage to stair during installation |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-11-25 | 2018-09-04 08:07 | -82 | 2018-06-28 08:53 | Architectural - Flooring | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Precast Stair steps damaged during installation. Solution to be agreed with __, trialled and agreed prior to close out of NCR. Proposal TBC.
| 03SR - Stations (RfL) | Cxxx-NCR-002952 | NCR | Crossrail Arch - GL89 Foundation |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-08-12 | 2018-08-10 15:01 | -2 | 2018-07-03 11:41 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Within the Crossrail Arch substation N concrete scope of works, at the location of GL89 foundation and during removal of concrete shuttering works - temporary ties to the formwork are unable to be removed from concrete foundation.
| 03SR - Stations (RfL) | Cxxx-NCR-002953 | NCR | Busbar Verticle support |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-07-16 | 2018-09-25 07:22 | 71 | 2018-07-02 13:58 | Electrical - Switchgear | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | CEG raised a concern on the vertical fixing methodology applied to the vertical sections of busbar rising from the transformer rooms to the LV switch board. The weight of the busbar appeared excessive for the fixings used. See attached photo
| 03SR - Stations (RfL) | Cxxx-NCR-002954 | NCR | Contractor unable to provide offsite manufacturing records for GFRC Cladding System |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-07-31 | 2018-07-31 08:42 | 0 | 2018-07-03 09:57 | Architectural - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A planned Crossrail surveillance was undertaken on 12th June 2018. This looked at the GFRC Cladding installation at Paddington Station – Bakerloo Interchange. At the time of the surveillance the Contractor was unable to submit the offsite records for; GFRC, Stainless and Galvanised Steelwork. A request was made for the Contractor to supply the records, post Surveillance but after 21 days the records are still not forthcoming.
| 03SR - Stations (RfL) | Cxxx-NCR-002955 | NCR | __ Documentation - Platform End Wall PEW ITP Code 01 not in place prior to works |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-03-31 | 2018-12-06 09:27 | -115 | 2018-07-04 11:20 | Architectural - Glazing | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | __ Documentation for Platform End Wall (PEW) ITP Code 01 [Cxxx-SKC-Z-ITP-B071_WS077-50112] not in place prior to works. The ITP is available and checked by but not submitted to Crossrail. ITP Code 01 to be in place to close NCR.
| 03SR - Stations (RfL) | Cxxx-NCR-002956 | NCR | POM Steelwork Mesh not on design as per Cxxx-PMI-001023 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-11-01 | 2019-03-01 15:48 | 120 | 2018-07-04 11:29 | Architectural - Glazing | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | POM Steelwork Mesh and grille separation closure piece not on design as per Cxxx-PMI-001023 (JH43.1226 TYPE IWS-139 Metal Vent Grille). Drawing number: Cxxx-SKC-A-DDD-M171_Z-04206 Design to be rectified and mesh/ closure installed. UPDATE 14/08/18: Further to discussions between __ (CRL) and __ () the Contractor has removed the incorrect panel and will re-install in line with the requirement. - The fixings will be front faced so that the panel can be removed without removing the POM machines - A black fly-mesh will be installed to the back of the panel - A Stainless steel closure piece will be install to bridge the gap between panels. The Contractor will rectify this and understands this NCR to be closed.
| 03SR - Stations (RfL) | Cxxx-NCR-002957 | NCR | Damage to bracket works for LV Bus Bar in SRLV 1 A |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-07-20 | 2018-09-13 14:14 | 55 | 2018-07-06 15:40 | Electrical - LV Equipment | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | __ Fire Stopping Operatives were observed striking the unistrut channels that serve as the Vertical runners as part of the Busbar support system. On further inspection it was observed that some of the fixings on this frame had been loosened and some accessories removed. This resulted in the __ frame moving slightly away from the wall
| 03SR - Stations (RfL) | Cxxx-NCR-002958 | NCR | Canopy - Damaged Aluminium Panel |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-10-10 | 2019-04-17 15:15 | 189 | 2018-07-12 15:13 | Architectural - General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Aluminium bullnose panel on the eastern edge of the Canopy bullnose along GL 91 has been noted to be damaged
| 03SR - Stations (RfL) | Cxxx-NCR-002959 | NCR | MaxE Channel Concrete Surround Strength Grade |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-08-17 | 2018-08-20 07:41 | 3 | 2018-07-13 08:50 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | An incorrect concrete strength grade has been used for the Max-E channel low level surrounds between GL 56 to 66 and GL 102 to 110. An ST2-S1 dry mix was installed whilst drawing Cxxx-SKC-D-DDD-M171_1-05450 and Specification Cxxx-SKC-D-RSP-B071_WS077-50001 Clause 5/6.2 4) calls for minimum C25/30 concrete surround. BS 8500-1 2015 Table A.17 provides ST2 with an equivalent strength of C8/10 and as such the installed surround does not comply with the required strength grade.
| 03SR - Stations (RfL) | Cxxx-NCR-002960 | NCR | Road, Paving & Drainage Specification Revision References |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-08-27 | 2018-10-25 09:04 | 59 | 2018-07-13 10:07 | Civil - Civil Engineering General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The latest Urban Realm ITP submissions for approval reference the Road, Paving and Drainage Specification as Revision 9, however, this Revision has not yet been approved for use by Crossrail.
| 03SR - Stations (RfL) | Cxxx-NCR-002961 | NCR | Lack of DB Covers |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-09-28 | 2018-09-10 10:23 | -18 | 2018-07-15 13:21 | Electrical - LV Equipment | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | 2 DBs on the departures road level are collecting dust and dirt internally due to a lack of protection.
| 03SR - Stations (RfL) | Cxxx-NCR-002963 | NCR | Working without Code 1 MCR - __ect L500 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-09-04 | 2018-08-24 13:37 | -11 | 2018-07-16 06:27 | Fire - Compartmentation | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The work to install __ect L500 around the HV cables prior to power on, has commenced without a code 1 MCR. Reasons for this late submission was due to a late design received from __, a requirement to have the cables fire protected prior to power on, and the fact that Sam Sambasivan (LUL Materials compliance engineer) has requested to review the MCR prior to approval.
| 03SR - Stations (RfL) | Cxxx-NCR-002964 | NCR | Increase in size of earth bars |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-08-02 | 2018-09-07 16:09 | 36 | 2018-07-19 08:25 | Electrical - Earthing & Bonding | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The client is aware that several busbars have increased in size through out the station which does not tie in with the initial design solution. The increase in size is to provide additional spare ways and in some cases this has resulted in re running earth cable.
| 03SR - Stations (RfL) | Cxxx-NCR-002966 | NCR | Un-coordinated design CMS clashes with door heights D3-79b, D3-767b, D3-770a, D3-770b, D4-104, D4-408 |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2018-08-22 | 2018-08-15 12:37 | -7 | 2018-07-23 12:35 | Architectural - Doors | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | During review of Cxxx-SKC-A-TSC-B071_WS077-50002 it has been established that the currently designed door heights for D3-79b, D3-767b, D3-770a, D3-770b, D4-104, D4-408, clash with the Contractor's designed CMS layout. The Contractor is required to co-ordinate MEP and Architectural design elements
| 03SR - Stations (RfL) | Cxxx-NCR-002967 | NCR | Ductwork internal supports/system resistance |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-10-31 | 2018-11-12 12:57 | 12 | 2018-07-24 09:21 | Mechanical - Mechanical Engineering General | 1500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | PFR west system has a number of internal bracing sections, that cause additional resistance to the air flow, and thus reduce the efficiency of the fan, and therefore does not meet the operating criteria. ( all other systems checked and found to be compliant)
| 03SR - Stations (RfL) | Cxxx-NCR-002968 | NCR | Air Release Fan (east) access and maintenace - clash with CMS |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2020-02-07 | 2020-01-30 14:53 | -8 | 2018-07-25 16:16 | Mechanical - Heating Ventilation & Air Conditioning | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | The 2 Air Release (east) fans located in AAR Fan were observed by CRL to have access and maintenance issues. These are detailed below and in attached photos: 1. There is low level trunking installed close to the lower fan that will obstruct the pallet lift used for removing the lower fan. 2. There is lighting installed close to the upper fan that will obstruct the pallet lift used for removing the upper fan. Hence, both points 1 and 2 are not compliant to the Cleaning and Maintenance strategy methodology for removing fans using a pallet lift.
| 03SR - Stations (RfL) | Cxxx-NCR-002969 | NCR | Inadequate flexural testing carried out on GFRC fins |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2018-07-31 | 2019-07-06 11:30 | 340 | 2018-07-25 15:15 | Architectural - Finishes | 2500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | have stated that the results from the recent flexural testing carried out by __s on the GFRC fins as instructed by Cxxx-PMI-1342 cannot be used as the test was not carried out in accordance with the standard
| 03SR - Stations (RfL) | Cxxx-NCR-002970 | NCR | EMO interface |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-08-14 | 2019-04-27 08:16 | 256 | 2018-07-31 17:31 | Architectural - General | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | It has been noted that the detail for the EMO to be incorporated into the bronze panel, notes a 10mm shadow gap around the EMO box. The sequence for installation needs to be the bronze panel installation followed by the EMO box being installed through the clear open space. The clients representative has stated this will affect the maintainability of the bronze panel. This situation also occurs at the locations of the 110V sockets.
| 03SR - Stations (RfL) | Cxxx-NCR-002971 | NCR | Escalator side cladding interface |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-11-30 | 2019-10-03 08:37 | -58 | 2018-08-02 14:59 | Mechanical - Escalators | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Interfacing problems | Completed |  | Whilst installing and checking the escalator outer cladding __ have experienced alignment issues. On closer inspection escalators E1, 2, 3, 5 appear to be dipping along their length up to a maximum of approx. 20mm. Additional survey works are being undertaken to confirm the exact errors being encountered. All other escalators are also being checked.
| 03SR - Stations (RfL) | Cxxx-NCR-002972 | NCR | AM103 (Coffer covers) Design level |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-08-18 | 2018-08-20 16:50 | 2 | 2018-08-04 13:09 | Architectural - Finishes | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | __ are currently installing AM103 stainless steel coffer covers on concourse level. The installation of these works are not as per the accepted design in which the coffer cover should be sitting within the recces inset from the level of soffit. Please see attached mark up and photos.
| 03SR - Stations (RfL) | Cxxx-NCR-002973 | NCR | Fan isolation dampers - access panel clash with ductwork insulation |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-09-26 | 2018-10-08 15:40 | 12 | 2018-08-06 15:40 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | The Fan isolation damper panels cannot be accessed or opened due to a clash with the fire rated insulation. The isolation dampers are installed in the following systems: smoke extract; pressurisation; air release.
| 03SR - Stations (RfL) | Cxxx-NCR-002974 | NCR | Concourse Balustrades - ESC 10-11 - As built discrepancy |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-09-23 | 2019-02-16 12:00 | 146 | 2018-08-09 09:36 | Architectural - Finishes | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the installation and setting out of the balustrades around ESC10-11 void at concourse level, it becomes apparent that the site conditions doesn't match with the approved design by 30-35mm. In fact the void is smaller, it means that the precast wall panel out of tolerance. In the centre sections of the void (as per the attached mark-up) the concrete coffer wall is creating a "belly" towards the void side in both sides. The plates are already pre-drilled to match the original cast in sockets (RD threads) at the East side of ESC 10-11 void.
| 03SR - Stations (RfL) | Cxxx-NCR-002975 | NCR | Missing ductwork access doors on Platform Smoke Extract west and east (PSE-I and PSE-II) |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-10-05 | 2019-01-02 14:38 | 89 | 2018-08-16 11:07 | Mechanical - Heating Ventilation & Air Conditioning | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 1. PSE-I (West) is missing 1 access door on the lower intake side of the fan in the transition ductwork section. 2. PSE-II (East) is missing 2 access doors on the discharge sides of the fan in the transition ductwork section. 3. The transition ductwork sections installed are not consistent with __ installation drawings. Reference __ drawings * Cxxx-SKC-M-DWG-B071_WS077-50164 C02 (west) - Layout * Cxxx-SKC-M-DWG-B071_WS077-50170 C02 (west) - Section * Cxxx-SKC-M-DWG-B071_WS077-50153 C02 (east) - Layout * Cxxx-SKC-M-DWG-B071_WS077-50165 C01 (east) - Section
| 03SR - Stations (RfL) | Cxxx-NCR-002976 | NCR | Glass chip - bridge balustrade - East face |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-10-12 | 2018-12-15 09:05 | 64 | 2018-08-13 11:06 | Architectural - Balustrade | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the inspection of the bridge balustrades - East side, the contractor found a broken glass (middle panel) - see attached photo for reference - "Glass chip - bridge level_mark-up"
| 03SR - Stations (RfL) | Cxxx-NCR-002977 | NCR | Defective Design Coordination of the Platform ESCR walls (and associated elements) and the RC Escalator Plinths |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-11-12 | 2018-09-11 16:17 | -62 | 2018-08-14 17:47 | Architectural - Brickworks/Blockworks | 1500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | It has come to light that the doors and lintel for the platform ESCR rooms cannot be installed due to the fixing location falling directly onto the end of the plinth. therefore there is nothing to embed into. From identifying the issue on site, we have discussed with __ and the only feasible solution is to extend the RC escalator plinths by 60mm. This will provide the required embedment for the door and lintel angle fixing.
| 03SR - Stations (RfL) | Cxxx-NCR-002978 | NCR | FCU filter access in SOR room |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-09-30 | 2018-09-07 16:10 | -23 | 2018-08-16 12:36 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | False ceiling support struts and electrical services are uncoordinated with mechanical plant and services in SOR room: 1. FCU filter access obstructed by ceiling support and niphan socket. 2. Flexible ducting (when insulated) clashes with niphan socket and ceiling support.
| 03SR - Stations (RfL) | Cxxx-NCR-002979 | NCR | CER I - socket outlet impinging on door. |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-08-31 | 2018-08-31 10:51 | 0 | 2018-08-17 08:46 | Communications and Control Systems - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | At CDN Cabinet PAD-02-CAB-3731U2 the access to the cabinet is restricted due to the door opening being impeded by the wall mounted electrical socket outlet assembly, this may also cause future damage to the cabinet door and wall socket.
| 03SR - Stations (RfL) | Cxxx-NCR-002980 | NCR | Urban Realm - Cxxx-PMI-00050 - FGW Toilets not incorporated into design |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2019-05-23 | 2019-10-12 10:22 | 142 | 2018-08-21 07:27 | Civil - Streets & Highways | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | The FGW Ladies Toilets were discovered in early 2012 when excavations for a hoarding post penetrated the roof. The Project manager issued Cxxx-PMI-00050 to survey the roof, assess the structural capacity and design the UR paving accordingly. The raised Cxxx-EWN-003001 on 4th June 2018 stating that the roof of the toilets clashed with the urban realm design and it was first known about on 1st June 2018. A second early warning notice was raised by on 12th July 2018 (Cxxx-EWN-3062)
| 03SR - Stations (RfL) | Cxxx-NCR-002981 | NCR | Spine Wall L-21-08 – Damaged Reinforcement |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-09-29 | 2018-11-26 14:33 | 58 | 2018-08-31 11:18 | Structural Engineering - Pre-cast | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Reinforcement at the top of spine wall L-21-08 in MH4 (East Escape Stairs) has been damaged and is no longer continuous.
| 03SR - Stations (RfL) | Cxxx-NCR-002982 | NCR | damaged fibre cable (s) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-09-19 | 2019-02-15 11:38 | 149 | 2018-08-22 09:37 | Communications and Control Systems - Fibre Optic Network | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | Damage to fibres cables installed to supply the 2 x PSD ‘s from the CERs IRN-334 - PSD Cabinets & Associated Cabling Installed IRN-337 - PSD Cabinets & Associated Cabling Installed
| 03SR - Stations (RfL) | Cxxx-NCR-002983 | NCR | Damaged wet riser fire main cabinet (concorse) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-10-21 | 2018-11-09 10:58 | 19 | 2018-08-22 12:17 | Fire - Fire Systems & General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | wet riser fire main cabinet glass has been cracked and labelling should state wet riser currently states dry
| 03SR - Stations (RfL) | Cxxx-NCR-002984 | NCR | EMO position |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-03-01 | 2019-04-03 11:20 | 33 | 2018-08-22 18:40 | Architectural - Finishes | 500 |  | Design | Reject | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The EMO position within the bronze cladding has not been set out as per the requirement of 1400mm from FFL. Due to uncoordinated design the cut out within the bronze panel has been cut out at 1550mm from FFL thus meaning the position will need to change vertically by 150mm, this has been discussed with CRL representative who has confirmed TFL/RFL accept the new position of 1560mm from FFL. It will need to be set at 1560mm to accommodate the 10mm shadow gap between the bronze panel. Cxxx-FCD-002562 will be raised upon confirmation from CRL representative to close out the NCR.
| 03SR - Stations (RfL) | Cxxx-NCR-002985 | NCR | PAD Escalators 1-5 - Failure to carry out monthly caretaker maintenance |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-11-15 | 2019-03-15 13:58 | 120 | 2018-08-24 10:31 | Mechanical - Escalators | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | It is observed that __ failed to carry out monthly caretaker maintenance (which includes movement of the escalators) for escalators 1-5 since March.
| 03SR - Stations (RfL) | Cxxx-NCR-002986 | NCR | P Status Drawings |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-10-31 | 2019-01-02 14:40 | 63 | 2018-08-30 12:22 | Electrical - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | __ have started MEPH works to MacMillian House and Crossrail arch with 'P' Status, Code 2 drawings. __ are at the moment addressing the comments which do not affect the installation of the MEPH works. The code 2 comments are very minor in nature and do not affect the design / installation. This has been discussed with CRL (__) informally and it is suggested that the works can go ahead while NG Baily addresses these comments.
| 03SR - Stations (RfL) | Cxxx-NCR-002987 | NCR | Pumped main and drainage pipe supports not in accordance with the design drawings - risers |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2018-11-30 | 2019-06-29 08:46 | 211 | 2018-09-10 07:56 | Civil - Structural Engineering | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A review of the support to the pumped main and drainage in the risers has revealed that the design drawings have not been followed. The fixings are in blockwork not concrete, the incorrect number and type of fixings back to the substrate have been used and the connections have half the number of bolts, refer photo and attached email
| 03SR - Stations (RfL) | Cxxx-NCR-002988 | NCR | Fan Room Doors and __ infills |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2018-12-14 | 2019-03-20 15:06 | 96 | 2018-09-10 11:08 | Architectural - Doors | 20000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Other | Completed |  | Techentrup acoustic doors are fitted to fan rooms and draught relief shafts within a __ frame and shaft wall construction. The design for the installation does not include structural calculations to demonstrate the kemwell shaft wall is stable with the doors weighing approx. 880kg installed. During installation, the doors and or the frame have moved \ deflected such that the door grounds onto the floor as it opens. In addition the doors have been fabricated with key access to one side only.
| 03SR - Stations (RfL) | Cxxx-NCR-002989 | NCR | __Flange Couplers |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-09-24 | 2018-10-03 15:08 | 9 | 2018-09-10 13:14 | Fire - Suppression | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As per JY60.1303 (e) there should be a flange coupler installed where the flexible conduit is connected to adaptable boxes on the gaseous suppression system. __have not followed this installation which needs to be rectified.
| 03SR - Stations (RfL) | Cxxx-NCR-002990 | NCR | Canopy - WPS & WPQR for Stainless Steel Fins |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-11-13 | 2018-11-26 14:29 | 13 | 2018-09-14 15:16 | Structural Engineering - Welding | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The WPS and the WPQR for the stainless Steel Fin Welding (Cxxx-SKC-S-RGN-B071_WS077-500094) was not submitted and accepted prior to the works
| 03SR - Stations (RfL) | Cxxx-NCR-002991 | NCR | Location of ductwork access doors - staircase pressurisation east |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-11-30 | 2019-04-03 11:52 | 124 | 2018-09-18 15:37 | Mechanical - Heating Ventilation & Air Conditioning | 1500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | As jointly observed on 06-Sept-2018 site walk for IRF-897 - the staircase pressurisation ductwork located in intermediate level east (GL18) has limited access doors and is not in accordance with DW/144 section 20 and TR/19. There should be access doors located either side of air turning vanes. The closest access door is currently located approx. 15 away. Reference drawings Cxxx-SKC-M-DWG-B071_WS077-50129 and Cxxx-SKC-M-DWG-B071_WS077-50130
| 03SR - Stations (RfL) | Cxxx-NCR-002992 | NCR | chilled water Non-compliant Phenolic blocks installed |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-10-17 | 2018-12-15 09:10 | 59 | 2018-09-19 13:10 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Non-compliant(MCR) Phenolic blocks installed in multiple locations
| 03SR - Stations (RfL) | Cxxx-NCR-002993 | NCR | Insufficient space to enable pipes to be lagged |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-10-17 | 2019-04-05 12:08 | 170 | 2018-09-19 13:25 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In TR-II CWU, Unit CCU01/TR-II, the LL flow/return pipework for the CCU is touching; it will not be possible to lag the pipework. The installation is not in line with agreed benchmark.
| 03SR - Stations (RfL) | Cxxx-NCR-002994 | NCR | Damage to LL panel in TR II |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-11-30 | 2019-01-18 13:33 | 49 | 2018-09-19 13:34 | Mechanical - Heating Ventilation & Air Conditioning | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Damage to LL panel of CCU01/TR-II.
| 03SR - Stations (RfL) | Cxxx-NCR-002995 | NCR | Couplers on flexable conduits |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-10-05 | 2019-01-07 14:56 | 94 | 2018-09-21 09:20 | Electrical - Cable Management | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | __have installed flexible conduit to non threaded equipment without the use of couplers. This is against CRL requirement JY60.1303 See attachments
| 03SR - Stations (RfL) | Cxxx-NCR-002996 | NCR | Canopy - Bullnose Panels |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-12-21 | 2019-04-17 15:24 | 117 | 2018-09-24 08:36 | Structural Engineering - Structural Engineering - General | 5000 |  | Damaged | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | During the adverse weather experienced on 21.09.2018, some of the canopy bullnose panels along Gridline 50, have become loose and been removed pending investigation. More information will be provided following investigation and inspection of the panels.
| 03SR - Stations (RfL) | Cxxx-NCR-002997 | NCR | Smoke down screens - bracket - GL 13 - Platform level |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-11-24 | 2018-11-21 11:42 | -3 | 2018-09-25 08:26 | Architectural - Finishes | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Following the installation of the smoke down screens brackets balance, at platform level GL 13, notes that 1no bracket cannot be aligned with the adjacent brackets due to a precast panel belly. The concrete panel distortion is pushing the panel out by aprox. 17mm. See attached photos.
| 03SR - Stations (RfL) | Cxxx-NCR-002998 | NCR | NCR - BLL GFRC - Damaged Panel |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-10-27 | 2019-08-02 11:16 | 279 | 2018-09-26 16:10 | Architectural - General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | At some point during the installation of the GFRC panel within the staircase, a corner on the GFRC panel has been damaged and subsequently repaired to a poor standard / without approval. A repair test will be carried out on a condemned panel and offered for inspection to the CRL architects prior to repair. This NCR will be updated with the outcome of the post repair inspection.
| 03SR - Stations (RfL) | Cxxx-NCR-002999 | NCR | Water Ingress within OHLE SR I 664 |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-10-11 | 2019-01-21 15:06 | 102 | 2018-09-27 15:05 | Electrical - OHLE | 500 |  | System Defect | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | On the 27th September water ingress was apparent within OHLE SR I 664. Equipment within this room should be free from damp and moisture
| 03SR - Stations (RfL) | Cxxx-NCR-003000 | NCR | Access door cable tether failing |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-12-31 | 2020-09-22 10:53 | 266 | 2018-10-01 13:49 | Mechanical - Heating Ventilation & Air Conditioning | 5000 |  | Manufacturing Defect | Rework | 3 (3-6k) | Complete | Design Problem - Not Defined | Completed |  | The ductwork access door cable tether support was observed failing. The eyelet connection cannot take the weight of the door (see attached photos). There are multiple examples of this failure on site on the __ ducting system. Photos taken on Pressurisation East (Fan-II room). notified by email on 25-Sept-2018 (attached)
| 03SR - Stations (RfL) | Cxxx-NCR-003001 | NCR | Thermal lagging of chilled water pipework prior to hydaulic testing |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-10-31 | 2018-11-06 17:24 | 6 | 2018-10-01 14:25 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The chilled water pipework has been thermally lagged in the corridors prior to hydraulic testing. Cxxx M&W Mechanical Specification (Cxxx-SKC-M-RSP-B071_WS077-50004) states “JY51.2201 On Site Testing b) Pipework pressure testing; iv) Pipework installations shall be hydraulically tested after erection and before thermal insulation is applied.” This was communicated to Contractor on 22-August-2018 (see attached email)
| 03SR - Stations (RfL) | Cxxx-NCR-003002 | NCR | Insufficent space for lagging of low level CCU pipework in CER-I CWU |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-12-31 | 2019-04-10 12:20 | 100 | 2018-10-01 14:35 | Mechanical - Heating Ventilation & Air Conditioning | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Insufficient space to lag low level pipework adjacent to floor CCU unit (observed in CER-I CWU). A minimal amount of screed to be channelled out. All CWU rooms to be checked. Contractor notified on 22-August-2018 (email attached)
| 03SR - Stations (RfL) | Cxxx-NCR-003003 | NCR | Lift lobby intermediate level (LFT III, IV) - dutwork clash with lighting and station fire main supports |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-12-31 | 2019-01-18 13:38 | -347 | 2018-10-01 14:56 | Materials - General | 1500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | * Ductwork to be installed by lift lobby will clash with lighting and station fire main supports (attached photos IMG_2125.jpg and IMG_2126.jpg) * __ drawing (Cxxx-SKC-M-DDA-M171_3-41534) does not align with __ (Cxxx-SKC-M-DWG-B071_WS077-50130) or __ (Cxxx-SKC-Y-DDA-M171_3-61534) drawings or the installation on site. Contractor was informed about these issues on 24-August-2018 (see attached email).
| 03SR - Stations (RfL) | Cxxx-NCR-003005 | NCR | Canopy - Column Waterproofing Prior to Paint Repair |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-11-14 | 2019-02-06 16:33 | 84 | 2018-10-17 12:14 | Structural Engineering - Steel Member | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Canopy Columns along East __ Terrace (south) side, at GL52, 54 and 56 ONLY, prior to minor paint repairs being completed on any damaged painted surfaces. Columns have been sprayed with the project standard "Eliminator (one Part)Bridgedeck Waterproofing System" as per approved MCR Cxxx-SKC-O-TSC-B071_WS077-50110 NCR "Cxxx-NCR-002886" was already open for the damage to the paintwork. Note that under this NCR, all columns already had the full paint thickness installed, and there is only minor damage to the paintwork due to shipping and installation.
| 03SR - Stations (RfL) | Cxxx-NCR-003006 | NCR | Main entrance gate fabrication and installation |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-12-20 | 2019-10-10 13:25 | 294 | 2018-10-10 12:16 | Architectural - Doors | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | The contractor raises NCR in relation commencing fabrication and installation of the main entrance gate steel work (primary steelwork (RSS) gate track and leafs (__) with P status drawings. This has been progressed after conversation and agreement with CRL to meet programme and client demand.
| 03SR - Stations (RfL) | Cxxx-NCR-003007 | NCR | CRL-LV Duct Removal - E__ GL50 to 66 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-12-06 | 2018-12-04 11:56 | -2 | 2018-10-11 12:28 | Civil - Utilities Engineering | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The Contractor is to remove 2x1xB19 ducts on run 'CRL-LV' between GL50 and 66 (see drawing Cxxx-SKC-E-DDA-M171_Z-51543) to enable access for BAL-113 installation equipment. This is due to a change in works sequencing whilst the canopy column LV ducting design is resolved.
| 03SR - Stations (RfL) | Cxxx-NCR-003009 | NCR | conduit instalation aeway from BS7671 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-11-30 | 2018-11-12 15:26 | -18 | 2018-10-12 11:08 | Electrical - Cable Management | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | conduit was installed for 110v light in BLL escalator pit with more than 180 degrees in the run and no pull box
| 03SR - Stations (RfL) | Cxxx-NCR-003010 | NCR | Canopy - Bullnose - Number of screws installed |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-04-26 | 2019-06-01 09:49 | 36 | 2018-12-05 08:34 | Architectural - General | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | The bullnose panels along Gridline 50 of the canopy have potentially been installed with a reduced number of self drilling screws. There is no section on the drawing (Cxxx-SKC-Y-DDD-M171_1-50004) that shows this exact detail. However when viewing the detail for the length that is parallel to Eastbourne Terrace (Cxxx-SKC-Y-DDD-M171_1-50003), section D shows that there should be 2 No. screws. Thus the assumption would be that along gridline 50 there should be the same detail of 2 No. screws
| 03SR - Stations (RfL) | Cxxx-NCR-003012 | NCR | Canopy - Column stiffner encroaching on finished surface level |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-11-21 | 2019-02-27 09:51 | 98 | 2018-10-17 13:55 | Structural Engineering - Steel Member | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | On approx. 6 of the E__ side canopy columns, it has been picked up that the stiffeners at the connection point between the baseplate and the columns will protrude above the finished surface level of the Urban Realm package. This applies to GL 90, 88, 86 & 84 which will be above ground level. On GL 82 & 80 the stiffeners will be below finished surface level, but will be within the paving and bedding zone. Attached photo shows the worst case scenario at GL 90. Note that this happens only at the Eastern end as the Finished Ground level drops from West to East whilst the canopy bases are all at the same level.
| 03SR - Stations (RfL) | Cxxx-NCR-003013 | NCR | VSHH - East Steelwork paint damage to top of Steel and Fin brackets |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-11-14 | 2018-11-26 12:02 | 12 | 2018-10-17 13:59 | Structural Engineering - Surface Treatment | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Steelwork at the top of the East VSHH damaged during installation and other works in the area. Minor damage only to already completed steelwork
| 03SR - Stations (RfL) | Cxxx-NCR-003014 | NCR | VSHH - West Steelwork paint damage to top of Steel and Fin brackets |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-10-31 | 2018-11-26 12:00 | 26 | 2018-10-17 14:00 | Structural Engineering - Surface Treatment | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Steelwork at the top of the West VSHH damaged during installation and other works in the area. Minor damage only to already completed steelwork
| 03SR - Stations (RfL) | Cxxx-NCR-003015 | NCR | VSHH - West Steelwork paint damage to bottom of Columns |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-11-13 | 2019-01-24 09:25 | 72 | 2018-10-16 15:08 | Structural Engineering - Surface Treatment | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Steelwork at the bottom of the VSHH steelwork has been damaged during installation and during other operations in the area
| 03SR - Stations (RfL) | Cxxx-NCR-003016 | NCR | VSHH - West Steelwork paint damage to bottom of Columns |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-11-13 | 2019-01-24 09:23 | 72 | 2018-10-16 15:24 | Structural Engineering - Surface Treatment | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Steelwork at the bottom of the West VSHH steelwork has been damaged during installation and during other operations in the area
| 03SR - Stations (RfL) | Cxxx-NCR-003017 | NCR | Stainless steel cladding - middle panel - Unpaid bridge |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-12-16 | 2018-11-16 13:30 | -30 | 2018-10-17 09:05 | Architectural - Finishes | 1500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | notes, that the Stainless steel cladding (middle panel) at Bridge level on the lift 6-7, is not in accordance with the approved design. The middle stainless steel cladding panel, shows a wider gap between the MAP panels (see attached photos for reference), comparing with the approved drawing - shows 5 mm - see drawing - Cxxx-SKC-Y-DDD-M171_Z-42017
| 03SR - Stations (RfL) | Cxxx-NCR-003018 | NCR | E__ level balustrades - installation - plate distortion |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-12-01 | 2020-03-07 09:31 | 462 | 2018-10-17 09:19 | Architectural - Balustrade | 1000 |  | Material | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Following the installation of E__ balustrades base plates - BAL113, would like to highlight the fact that the base plates are not as per the installation/fabrication tolerances specified in the contractual WI. Please see attached photos, showing the plates distortion and inconsistent gaps/misalignment between adjacent panels. The current works information says: clause JL13.3104 - c) All finished metal surfaces shall be flat and free from undulations and irregularities. i) Twist: ±1.5mm - there shall be no warping of any frame. ii) Line of panel: ±2mm overall difference between adjacent standards. d) Tolerances shall not be cumulative. and Workmanship Tolerances - clause JL13.3206 - j) The bow of any flat surface shall not exceed more than ±2mm from a 2000mm straightedge placed against it in any direction. k) The straightness of any surface of an edge shall not deviate by more than ±2mm from a 2000mm straightedge placed against it in any direction parallel to the long axis of the element. l) The centre section of any linear element shall not bow by more than the lesser of ±2mm or 0.075% of the length of the element measured from a straight line between the ends of the element. The subcontractor __ is to present a mitigation procedure to - CRL as a matter of urgency, in order to rectify the non-conformance
| 03SR - Stations (RfL) | Cxxx-NCR-003019 | NCR | DR balustrades 2No base plates - adjacent to bridge |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-12-31 | 2019-07-19 11:45 | 200 | 2018-10-17 09:31 | Architectural - Balustrade | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | notes that 2no base plates installed at DR level - around GL 12, adjacent to the pedestrian bridge are not in accordance and coordinated as per the latest __ movement joint drawings, issued by __ for review under the transmittal - __ Ltd-TRANSMIT-000311 (via ACONEX). The base plates already installed are clashing with the vertical movement joint posts and bridge balustrades. The subcontractor __ is to remanufacture the base plates.
| 03SR - Stations (RfL) | Cxxx-NCR-003020 | NCR | Bi-metallic isolation has not been installed between dissimilar metals as specified |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-09-19 | 2020-01-17 13:16 | 120 | 2018-10-17 09:59 | Architectural - Signage | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | A planned surveillance was carried out on Station Signage, during an inspection of first fix bracket for sign type 120 that was connected to the PES framework, it was noted that there was not Bi-metal separation between the stainless steel bracket and the galvanised framework. Specification that requires the following: JN15 ‘Signs’ 1401 states; b) “Fixings shall accord with Section JZ20 of the Specification”. Cxxx Architectural Specification clause JZ20 ‘Fixings’.1101 states; h) “Adequate measures shall be taken to prevent bi-metallic corrosion between dissimilar metals”.
| 03SR - Stations (RfL) | Cxxx-NCR-003021 | NCR | VAP ELEC 3.1 Trunking Transfers |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-12-31 | 2018-11-12 15:23 | -49 | 2018-10-17 10:28 | Electrical - Cable Management | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not trained for the work being performed | Completed |  | The attached photos where taken in the Bakerloo Line Box. 1. The cut out made on the trunking protrude past the filler knock outs creating a sharp edge within the cable route. This defect could have cause unknown damage to the cables installed and any future cable to be run through the transfer. 2. Too many knock outs have been removed losing the segregation between compartments. Cables have been run before the CMS IRF was held.
| 03SR - Stations (RfL) | Cxxx-NCR-003022 | NCR | Canopy - Bullnose - Bi-metallic Corrosion |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-12-10 | 2020-05-15 13:34 | 522 | 2018-10-18 09:56 | Architectural - General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | This NCR is being raised at the request of the Supervisor's representative. The Supervisor's representative is concerned that there are stainless steel fixings in contact with aluminium within the canopy bullnose. This detail of where there are stainless steel fixings connecting the internal aluminium support sheet to the brackets is shown in the detailed design drawings - Cxxx-SKC-Y-DDD-M171_1-50003 and Cxxx-SKC-Y-DDD-M171_1-50004.
| 03SR - Stations (RfL) | Cxxx-NCR-003024 | NCR | BMS - Works starting without an approved ITP |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-12-01 | 2018-11-16 16:08 | -15 | 2018-10-19 13:09 | Communications and Control Systems | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | It is observed that __ / __ is carrying out the BMS works without and an approved ITP in place.
| 03SR - Stations (RfL) | Cxxx-NCR-003025 | NCR | Structural claculations |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-06-11 | 2020-02-01 09:27 | 235 | 2018-10-20 14:52 | Architectural - Signage | 2500 |  | Design | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | __ structural calculations have not yet been approved. Works on site have progressed in order to achieve programme dates and ensure works for follow on contractors can continue.
| 03SR - Stations (RfL) | Cxxx-NCR-003026 | NCR | Installation of __ RWA45 without Code 1 MCR - To Facilitate HV Power On |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-11-23 | 2018-11-29 09:02 | 6 | 2018-10-24 15:25 | Fire - Compartmentation | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | To facilitate the HV power on at late notice, we were required to install the internal firestopping to the HV ladder rack that had only just been approved. We had not had time to get the product MCR approved by the time of install.
| 03SR - Stations (RfL) | Cxxx-NCR-003027 | NCR | ES12 & ES13 Saw Cut Damage |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-03-20 | 2019-08-22 14:28 | 155 | 2018-10-25 15:21 | Civil - Demolition/Site Clearance | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The Contractor has damaged roofs slabs ES12 and ES13 during demolition works of the existing E__ sacrificial road slab between GL20 and 24, to the south of the eastern VSHH. The extent of the damage is subject to further intrusive surveys, however initial findings suggest the reinforcement damage is limited to approximately GL19.5 to GL21 on slab ES12 only. Refer to the attached 'Cxxx-SWN-S-DDA-M171_1-01575 Markup' for the anticipated damage extent. Photos of the intial investigations into ES12 and ES13 are also attached.
| 03SR - Stations (RfL) | Cxxx-NCR-003028 | NCR | Contractor unable to supply welding compliance records. |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-03-15 | 2020-05-27 08:55 | 439 | 2018-10-26 08:22 | Architectural - Signage | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | The contractor submitted manufacturing check sheets for signage elements sampled. On checking, it was found that the check sheets submitted do not define the welder so could not be crosschecked against WPQR. The Contractor was requested to provide evidence of which operative(s) completed this welding and to provide the Weld Procedure Specifications (WPS) that are referenced in the WPQR. In addition the Contractor __ who are the F2 designer were requested to confirm if any signs have steel elements classed as structural to BS EN-1090 and the Construction Products Regulations (for CE Marking). If steelwork is classified as ‘structural’ a design Execution Class (EXC) to BS EN 1090 will be required including evidence of W&W FPC and RWC to fabricate according to this EXC class. The Contractor has not been able to provide the requested records and assurance.
| 03SR - Stations (RfL) | Cxxx-NCR-003029 | NCR | VSHH - GFRC - Fibre Content Testing |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-12-12 | 2018-12-07 16:28 | -5 | 2018-10-26 15:06 | Architectural - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | This NCR has been raised at the request of the Supervisor's representative, following the design review under taken on the VSHH cladding system which includes the GFRC fins and panels. The GRCA specification calls for glass fibre content testing. See technical requirements section of this NCR. The glass fibre content has been determined as per the accepted ITP - Cxxx-SKC-C-ITP-B071_WS077-50191 - revision 2. The deliverable, form L1 which confirms the mass of fibres has been produced for all batches.
| 03SR - Stations (RfL) | Cxxx-NCR-003031 | NCR | GL 14 Access Hatches - Incorrect Implementation of PMI 823 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-02-28 | 2019-04-29 10:30 | 60 | 2018-11-01 10:32 | Civil - Civil Engineering General | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | It has come to light that the instructed information under PMI #823 has been incorrectly implemented into the architectural design. Within RFI #3273, due to not being able to delete superseded documents from the communication, 2no. drawings are contained within it. The incorrect drawing has then been transmitted to __ and therefore the GA drawing does not reflect what has been constructed on site. The 2no. drawings in question are attached and I have assigned a Rev 1 and Rev 2 against each, according to the text within the RFI and what has been constructed on site. To confirm, the openings within the structural slab are designed as 600mmx750mm (approx.) and not 850x850mm as per the GA drawing. This has been constructed correctly as per the PMI and associated FCD. What this means however, is that these access hatches now clash with the blockwork wall and door and therefore could not be opened if the wall were constructed as per the design. Also what has been installed on site therefore does not correspond to the gated design. Furthermore, following an asbuilt survey, the hatch openings have in fact not been installed in accordance with the PMI as the correct detail drawing instructed shows a minimum of 900mm from gridline C, with the asbuilt being 830mm offset. This is shown on the attached drawing ref.: Asbuilt hatch and Associated mark-up.
| 03SR - Stations (RfL) | Cxxx-NCR-003032 | NCR | Uncoordinated mist suppression equipment, MEP services and electrical panels in MIST-I |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-12-21 | 2019-04-10 12:24 | 110 | 2018-10-31 17:28 | Fire - Suppression | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Uncoordinated mist suppression equipment, MEP services and electrical panels in MIST-I. This has resulted in significant rework within MIST-I. * Photos attached from 9-Sept and 21-Sept show sprinkler pipework on the north side of MIST-I and valvetrain installed on the tank.* Photos attached from 30-Oct and 31-Oct show the valvetrain has been stripped off and relocated to south wall of MIST-I. * Photo '31-Oct Photo 2' shows electrical panel installed. CMS was uncoordinated on this wall and had to be stripped removed and relocated to avoid clashing with electrical panel.
| 03SR - Stations (RfL) | Cxxx-NCR-003033 | NCR | Waterproofing Indicator Mesh Omission |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-05-08 | 2019-11-30 09:49 | 206 | 2018-10-31 18:07 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The Contractor has not installed the 'brightly coloured indicator mesh' above the elastomeric waterproofing protection screed in certain locations on the __ and E__ roof slab. This indicator mesh is called for in drawing Cxxx-SWN-S-DDD-M171_Z-05550.
| 03SR - Stations (RfL) | Cxxx-NCR-003034 | NCR | Platform Escape Stairs Landing - Non-Compliance with Building Regulations |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-03-31 | 2019-03-23 10:56 | -8 | 2018-11-01 09:08 | Architectural - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | It has come to light that the platform level landings from the base of the escape stairs to the fire door (as highlighted on the attached) are in non-compliance with the building regulations. This landing width was in the received design from Cxxx, but has only come to light now due to an RFI issued to __ relating to the door swing clash with the stairwell handrail. The landing space is to be the same length as the width of the escape stairs as stated in Approved Document B and K.
| 03SR - Stations (RfL) | Cxxx-NCR-003035 | NCR | MCC equipment supply cables |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-11-15 | 2019-03-04 12:31 | 109 | 2018-11-01 16:02 | Electrical - Power Distribution | 2000 |  | Design | Reject | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | Supply cables installed to MCC equipment are too big for the associated termination boxes. A section of cable has to be re run for MCC2 from the isolator to the box. This is a short run but it has been suggested this is not the only location.
| 03SR - Stations (RfL) | Cxxx-NCR-003037 | NCR | VSHH - GFRC - Cracking on upper GFRC test fin |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-12-01 | 2019-07-13 08:47 | 224 | 2018-11-02 14:11 | Architectural - General | 50000 |  | Material | Rework | 2 (6-60k) | Complete | Design Problem - Other | Completed |  | This NCR is being raised at the request of the Supervisor's representative. The upper GFRC fin used for the soft and hard body impact testing on site, was inspected once it was removed from the rails following the testing. This fin appeared to have fine hairline cracking along the edge of the fin
| 03SR - Stations (RfL) | Cxxx-NCR-003038 | NCR | VSHH GFRC fins - Deficient Design |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2019-08-16 | 2019-06-04 07:43 | -73 | 2018-11-05 11:50 | Architectural - Finishes | 50000 |  | Design | Repair | 2 (6-60k) | Complete | Design Problem - Other | Completed |  | When considering the requirement for impact testing the GRCA Design guide was reviewed. This document is part of the GRCA specification which is a requirement of the WI. The Design guide states that the design should ...consider the differences in behaviour between test coupons and the full size sections as well as the mode of collapse and consequences of failure. The design takes no account of accidental loading, therefore the impact testing was needed to satisfy this design requirement. In addition, the cladding system is to be designed and constructed and installed to BS8200, which is a requirement of the WI. This standard states that the risk of hazard to occupants or to people outside the building dues to the more severe but infrequent accidental impacts should be minimised. The standard then continues to define the requirement for impact testing and the acceptance criteria states that when subjected to impacts in Table 4 (the cladding) should not...make parts of the building liable to fall or cause serious injury to people inside or outside the building.
| 03SR - Stations (RfL) | Cxxx-NCR-003040 | NCR | IRN 228 - unauthorised signatories for T&C |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2019-03-31 | 2018-12-10 14:11 | -111 | 2018-11-06 08:55 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Improper resource allocation | Completed |  | signatories on IRN checked against authorisation matrix Cxxx-SKC-N1-LRC-B071_WS077-50010. -- has signed the IRN as an S3 signatory, but his name does not appear on the delegated signatories matrix
| 03SR - Stations (RfL) | Cxxx-NCR-003041 | NCR | Vent Head Houses - Damage and Marking to GFRC Cladding Components |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-11-29 | 2021-02-02 14:52 | 431 | 2019-07-10 15:44 | Architectural - Finishes | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | It was noted during an interim inspection of the vent head houses that a lot of minor damage in the form of chips and scuffs etc. had been inflicted on the installed GFRC panels and fins. It was not possible to establish whether this was as a result of inadequate protection or the double handling required to reconfigure the fixings or a combination of both. Photos attached.
| 03SR - Stations (RfL) | Cxxx-NCR-003042 | NCR | PAD - Concouse TVM Enclosure Surrounds - Coordination between Bronze Panels, Grille, Signage and C690 TVM's |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-07-24 | 2020-12-01 07:37 | 496 | 2019-07-10 15:45 | Architectural - Finishes | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The various components making up the clad surround to the TVM enclosure appear to be uncoordinated and currently incapable of providing a suitable landing surface for brush trims to the perimeter gaps. Also features such as the banner sign appears to have been installed out of line with the grille below and bronze panels to each side. Photos attached.
| 03SR - Stations (RfL) | Cxxx-NCR-003046 | NCR | Low level light fittings |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-11-26 | 2019-03-07 15:06 | -264 | 2018-11-12 14:43 | Electrical - Lighting | 20000 |  | Design | Use As-Is | 2 (6-60k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Lights installed within the pressurisation stair case are lower then the LU Guidance included within the works information. Lighting to be relocated as it is currently a hazard. G371A section 3.5 FCD to be produced.
| 03SR - Stations (RfL) | Cxxx-NCR-003048 | NCR | slot drain to west of entrance gates - incorrect location |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-06-11 | 2019-10-12 10:24 | 123 | 2018-11-13 10:16 | Civil - Drainage | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The slot drain to the west end of site, located just west of the entrance gates is constructed further north than shown on the current drawings on eB. This will result in ponding to the south of the drain. Details have been requested from the site team and design managers and to date no response as to how this can be resolved has been received
| 03SR - Stations (RfL) | Cxxx-NCR-003049 | NCR | west end entrance gates - lower channel removed from site |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-12-21 | 2019-02-26 14:29 | 67 | 2018-11-13 10:20 | Architectural - Urban Realm | 2500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | The lower channel to the west end entrance gates has been installed and subsequently removed from site.
| 03SR - Stations (RfL) | Cxxx-NCR-003050 | NCR | Kite marking - E__ level - glass panels |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-02-07 | 2020-01-30 15:39 | -8 | 2018-11-13 17:44 | Architectural - Glazing | 5000 |  | Material | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Following the recent findings during the installation of the BAL 113 glass panels at Eastbourne terrace level, would like to identify the following non conformance: The kite mark is not installed in accordance with the approved design. 25no glass panels have the kite mark symbol in the top right corner, as opposed to approved design, bottom left corner. Impact assessment been extended to the main box balustrades (concourse and platform level). All glass balustrades are under investigation.
| 03SR - Stations (RfL) | Cxxx-NCR-003052 | NCR | IRN 175 Access and maintainability |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-05-13 | 2019-03-07 14:43 | -67 | 2018-11-14 17:12 | Fire - Fire Systems & General | 3000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Limited access for maintainability of fir system equipment in multiple locations
| 03SR - Stations (RfL) | Cxxx-NCR-003053 | NCR | IRN 176 access and maintainibillity |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-05-13 | 2019-03-07 14:44 | -67 | 2018-11-14 17:22 | Fire - Fire Systems & General | 3000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | Limited access for the maintainability of the fire system
| 03SR - Stations (RfL) | Cxxx-NCR-003054 | NCR | BMS Control Panel Installation |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-11-30 | 2019-02-16 12:05 | 78 | 2018-11-16 15:12 | Communications and Control Systems | 500 |  | Incorrect Installation | Reject | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | __ control panel located in electrical room below escalator 15 has been installed in an area where access is restricted. Contractor to assess location against requirements of (see email and photograph attachment):
| 03SR - Stations (RfL) | Cxxx-NCR-003055 | NCR | Crossrail Arch - Structural Steelwork GL 82/H C1 Column & B17 Roof Beam Incorrect Connection |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-04-30 | 2019-08-22 14:37 | 114 | 2019-02-16 13:30 | Structural Engineering - Steel Member | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the installation of the GL82/H C1 structural steel column, it is apparent that this column has had a connection plate fabricated implying allowance for the column to be connected to the above B17 steel roof beam. No pre drilled holes are present within the above B17 steel roof beam ready to receive fixings (nut & bolt) and allowing the C1 steel column to be connected to it.
| 03SR - Stations (RfL) | Cxxx-NCR-003056 | NCR | Scabbling on JRC Slabs GL30-42 __ |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-01-23 | 2019-01-18 12:19 | -5 | 2018-12-04 10:01 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The contractor has carried out scabbling on the surface of the JRC slabs in areas to assist with the laying of paving to within tolerance. The action was taken to remove areas of humped concrete in the following locations: - Below the stainless steel paving angle to provide uniformity across the width of the slab and allow for a level finish - Below the interface of the stone cladding plinth and paviours to provide a uniform gap of 10mm between plinth and FFL The action of scabbling the concrete surface raises the issue of cover to reinforcement in the JRC slabs in these locations.
| 03SR - Stations (RfL) | Cxxx-NCR-003057 | NCR | CCTV Cab (IRN 320) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-12-31 | 2018-12-15 09:24 | -16 | 2018-11-29 15:47 | Communications and Control Systems | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | CCTV Cab drilled post installation to accommodate earth cable installed. Panel drilled at top to accommodate conduit for earth cable. See attached pic.
| 03SR - Stations (RfL) | Cxxx-NCR-003058 | NCR | CCTV Cab (IRN 321) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-01-25 | 2019-02-16 12:07 | 22 | 2018-11-29 15:57 | Communications and Control Systems | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | CCTV Cab drilled post installation to accommodate earth cable installed. Panel drilled at top to accommodate conduit for earth cable. See attached pic.
| 03SR - Stations (RfL) | Cxxx-NCR-003059 | NCR | CCTV Cab (IRN 329) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-12-31 | 2018-12-15 09:30 | -16 | 2018-11-29 15:59 | Communications and Control Systems | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | CCTV Cab drilled post installation to accommodate earth cable installed. Panel drilled at top to accommodate conduit for earth cable. See attached pic.
| 03SR - Stations (RfL) | Cxxx-NCR-003060 | NCR | Stone Cladding - Installation without approved drawings |  | Contr | SKC | PAD - Paddington Station (West) |  | 2018-12-24 | 2019-08-09 15:41 | 228 | 2018-12-10 10:09 | Architectural - Walls | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | are to commence elements of installation for Natural Stone Cladding package without an approved DDCD. The DDCD is with __ on final round of comments, therefore is confident to proceed installation without risk to design change.
| 03SR - Stations (RfL) | Cxxx-NCR-003061 | NCR | Adjustment of 2.5m Barrier Posts - Platform PES Ends |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-01-24 | 2019-08-02 10:42 | 190 | 2018-12-10 14:03 | Architectural - Partitions | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | It was discovered during a site inspection undertaken on 05.11.18 that there are inconsistent slab levels on the 4 x PES corners where the __ 2.5m barrier is to be installed. Please refer to the attached markup labelled Locations of Adjusted Base Plates. The slab levels in these regions have already been cast to FFL where there should be 100mm of screed. As a result the 9 x base plates to be fixed to these areas will need to be made smaller by 100mm. This has already been instructed to __. There are 3 reasons why this error has occurred: - __ did not complete site survey - __ could not access area to complete site survey and instructed them to proceed on construction drawings Regardless the 9 x posts (36 in total for the 4 corners) need to be re manufactured. As a result the base plates will not be fixed directly into the top of slab (instead of 100mm below FFL and covered with 100mm of screed - refer markup labelled Baseplate Adjustment for a visual representation). Also note the attachment labelled Tunnel Emergency Balusters Calculations. Based on Page 26, __ are able to reduce the size of the baseplates in this zone only down to 200mm x 200mm x 12mm thick instead of 350mm x 350mm x 15mm thick to reduce potential for tripping. Since these baseplates will not be fixed to the surface there is a potential trip hazard. Attached RFI from __ show the proposal to deal with this trip hazard by covering the base plate by a continuous galvanised PPC metal box painted in high visibility colour 150mm high and as wide as the base plate (50mm from face of barrier post)
| 03SR - Stations (RfL) | Cxxx-NCR-003063 | NCR | non-compliant plastic hose (Aquaflex) installed in main box |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-03-11 | 2019-02-01 16:11 | -38 | 2018-12-11 13:04 | Mechanical - Piping | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The waste water pump IRN-233 has non-compliant material installed. The plastic hose (Aquaflex, MCR-4896) is "F4" MCR approved, which means that the material can only be installed in non 1-085 environments. MCR-4896 was produced and approved only for __'s Platform 12, which is not part of the Cxxx's Main Box.
| 03SR - Stations (RfL) | Cxxx-NCR-003065 | NCR | DR/E__ Balustrades - Secondary plate - oversized holes |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-03-11 | 2019-04-03 12:02 | 23 | 2018-12-11 14:31 | Architectural - Balustrade | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following an inspection with and CRL around DR and E__ balustrades, would like to capture the following findings: On the __ secondary plate, there are ate least 6holes/bolts, with the incorrect washer. It appears also that the hole has been oversized onsite to accommodate any site tolerances. This can be seen on the attached photos. This is not as per the approved design - see drawing Cxxx-SKC-Y-DDD-M171_Z-42401_C01
| 03SR - Stations (RfL) | Cxxx-NCR-003066 | NCR | Floor tunking damaged by disk cutter |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-03-12 | 2019-03-11 17:16 | -1 | 2018-12-12 15:52 | Electrical - General | 7000 |  | Damaged | Rework | 2 (6-60k) | Complete | Subcontractor Problems - Other | Completed |  | between Escalators 12 & 13 . A contractor has cut a line in the floor and they have sliced through the underfloor trunking, resulting in the trunking and the cables inside the trunking being damaged
| 03SR - Stations (RfL) | Cxxx-NCR-003067 | NCR | Damaged Fire cable |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-03-13 | 2019-02-16 17:38 | -25 | 2018-12-13 12:34 | Fire - Fire Systems & General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | IRN-161 Fire Network Loop - Damaged Cable Departures Road Gridline 6B
| 03SR - Stations (RfL) | Cxxx-NCR-003068 | NCR | Revised __ Calcs not submitted with GIR 50012 |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2018-12-27 | 2019-03-07 14:55 | 70 | 2018-12-13 15:02 | Electrical - Electrical Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | In reviewing GIR 50135 submitted for changes to lighting layout on Departures Rd Urban Realm Lighting, it was identified that associated changes to __ calculations where yet to be submitted formally. The __ calculations are currently being revised to Rev10 and the relevant pages from the __ document where submitted with the GIR to show __ had carried out calculations.
| 03SR - Stations (RfL) | Cxxx-NCR-003069 | NCR | No Pin Racks for cable support in vertical containment over 3m. |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-07-31 | 2019-03-16 12:38 | -137 | 2018-12-17 10:39 | Communications and Control Systems | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During a planned Crossrail surveillance, the inspection of the vertical risers for the communication cables witnessed the absence of pin racks to support the cable over a 3m drop. This is a requirement of JY60.1306 Metal Trunking x) Provide all trunking with removable cable retainers or bridges to retain cables in situ. Provide vertical trunking with insulated pin racks to support cables at 3000mm centres.
| 03SR - Stations (RfL) | Cxxx-NCR-003070 | NCR | Additinal DALI LCMs Required |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-01-21 | 2019-03-05 14:56 | 43 | 2019-01-07 16:33 | Electrical - Lighting | 3000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Additional __ LCMs are required on site to reduce the circuit length
| 03SR - Stations (RfL) | Cxxx-NCR-003072 | NCR | Chiller Compound West Damage to Chillers |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-02-28 | 2019-03-24 11:39 | 24 | 2019-01-07 16:28 | Mechanical - Heating Ventilation & Air Conditioning | 1500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | As per EWN-3364 damage occurring to Chillers in West compound. Due to scaffolding works, Chillers unprotected.
| 03SR - Stations (RfL) | Cxxx-NCR-003073 | NCR | Critical Cooling Units - Removal of factory fitted PICV valves (IRN #454) |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-03-13 | 2019-09-14 09:10 | 185 | 2019-01-07 16:48 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | As per EWN-3359, factory fitted Pressure Independent Control Valves (PICV) have been removed from each of 38 Uniflair Critical Cooling Units (CCU). In doing it was observed that the factory units, specifically: the internal pipework; pipework insulation; and casings, which are suffering degradation and are no longer in a new condition. Also, the Project Manager is concerned that the manufacturer's warranty may have been invalided. See attached photo.
| 03SR - Stations (RfL) | Cxxx-NCR-003074 | NCR | VSHH - Top level Grillage West |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-03-29 | 2019-09-11 13:19 | 166 | 2019-01-09 15:11 | Structural Engineering - Bolted Connections | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Structural steel grillage framework at the top of the West VSHH draft relief shaft has been fabricated incorrectly. Attached __ Sketch "SK-1728-055-302" shows how the steel has been fabricated. Base plates marked in Pink, have been installed fabricated the wrong way around compared to approved design XXXXXXX. This causes them to clash with the GFRC Fins This was picked up at galvanising stage and they were able to be removed and galvanised so that there was no longer a clash, however fixings are now unable to be installed. Fixings in the centre, roughly along gridline D are able to be installed as per design.
| 03SR - Stations (RfL) | Cxxx-NCR-003075 | NCR | Lack of 25% spare capacity and segregation within the CMS |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2020-03-01 | 2021-03-02 10:05 | 366 | 2019-01-11 15:45 | Electrical - Cable Management | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | Cables installed within the BLL box and west bound departures road within the comms trunking are limiting the spare capacity available due to poor installation and possibly the installation of too many cables. See OBS 26062 A change from CAT6 to FO cables has also been witnessed on site for the MCC network cable. The change is a result because the distance from the MCC to the network point is longer than 95m which is not suitable for the CAT6 cable. As a FO is now required an additional cabinet is required to convert back to a CAT6. The FO cable is almost 3xthe diameter of the CAT6 which takes up additional space within the CMS and it has a larger bend radius. There is a risk here that will lose their 25% spare capacity and that the CMS bends may be too tight for the fibre optics. Cxxx should provide assurance that these risks have been considered within this change.
| 03SR - Stations (RfL) | Cxxx-NCR-003077 | NCR | PAD-04-CAB-51001U1 - RTU Cabinet - NCR |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-07-31 | 2019-08-14 07:44 | 14 | 2019-01-15 15:14 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Please see attached photos of PAD-04-CAB-51001U1 at Platform level in CSR. This cab has had severe water ingress and some superficial scuffs. Also a lot of dust and metal trimming from cables. In the attached photographs there seems to be some corrosion set into the cab itself as well as the cable entries. The cable entries have been replaced but Cxxx still have concerns about bringing this cab into service after the water damage
| 03SR - Stations (RfL) | Cxxx-NCR-003078 | NCR | Chilled water system cleaning, flushing and balancing phase – not following ITP and RAMS |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-04-18 | 2019-03-02 11:14 | -47 | 2019-01-15 12:10 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | In regard to Cxxx-EWN-03380, the following CTP and RAMS intervention points have not been adhered to for the Flushing, Chemical Cleaning and Balancing phases of the Chilled Water system. This is in contravention of the Contractor’s quality management plan. Flushing, Chemical Cleaning: - IRFs and accompanying documentation have not been provided for the Initial Dynamic Test, Second Dynamic Flush, and Third Dynamic Flush phases. This should include record sheets for the chemical cleaning and dosing phases. - Water sample test results have not yet been submitted to CRL. - Water discharge license has not yet been submitted to CRL. - Water flow checks to ensure system is fully flushed to be evidenced to CRL. - Cleaning out of strainers in the plantroom and CCU room units to be evidenced to CRL. Balancing: - IRFs and accompanying documentation have not been submitted to CRL. The following balancing activities are to be demonstrated to CRL: * balancing of plant room units in the following rooms: BAT-I CWU; CER-I CWU; TR-III CWU; FCR-I CWU; * balancing of the index leg (Bakerloo Line Link); * balancing of 4 sample locations in intermediate level corridor; * balancing of 2 sample locations in concourse level corridor. Applicable ITP and RAMS documents are as follows and linked to this NCR: * CTP for flushing and cleaning: Cxxx-SKC-M-ITP-B071_WS077-50010 * CTP for balancing ref: Cxxx-SKC-M-ITP-B071_WS077-50020 * RAMS 650 Chilled Water flushing, cleaning and chemical treatment: Cxxx-SKC-O1-GMS-B071_WS077-50510 * RAMS 651 Chilled Water balancing: Cxxx-SKC-O1-GMS-B071_WS077-50511
| 03SR - Stations (RfL) | Cxxx-NCR-003079 | NCR | EXT-301 Bench Foundation __ GL66 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-03-11 | 2019-03-16 12:44 | 5 | 2019-01-14 16:52 | Civil - Civil Engineering General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | 1no. EXT-301 bench foundation at __ GL66 has been installed without a fully assured design. The concrete slab surrounding the foundation has been constructed with 500mm2/m B503 reinforcement mesh however this does not align with the foundation intent provided in the supplier's initial design (PJ1501511-BD07, attached).
| 03SR - Stations (RfL) | Cxxx-NCR-003080 | NCR | Canopy - Damaged Glazing Panel (GL80-82 - Panel Type Z) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-06-28 | 2019-06-13 09:03 | -15 | 2019-01-18 14:05 | Architectural - Glazing | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A Glazing panel has been damaged between GL80-82, Panel Type Z.
| 03SR - Stations (RfL) | Cxxx-NCR-003081 | NCR | Use of Unapproved Sealant - Invicta __ |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-03-14 | 2019-03-21 09:13 | 7 | 2019-01-23 11:26 | Fire - Compartmentation | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Within an inspection of the completed __ shaft wall barrier for the stair pressurisation ductwork on concourse level, a silicone sealant has been used instead of the code 1 approved acrylic sealant contained within MCR ref.: Cxxx-SKC-O-TSC-B071_WS077-51474. Silicone can be used on LUL via the written notice to S1085, but CRL have not taken this notice on board and therefore the use of silicone sealant within sub-surface locations is prohibited.
| 03SR - Stations (RfL) | Cxxx-NCR-003083 | NCR | Glass - kite mark - BLL stairs balustrades |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-03-22 | 2020-02-13 13:40 | 328 | 2019-01-30 10:10 | Architectural - Glazing | 5000 |  | Manufacturing Defect | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | In addition to the NCR, Cxxx-NCR-003050, would like to highlight that during a pre inspection it was noted that the kite mark symbol is missing from 2no small glass panels on the Bakerloo stairs balustrades @ platform level (south and north face). See attached photos mark-up drawing with locations. This is again, creating uncertainty in relation to the correct orientation of the glass panels.
| 03SR - Stations (RfL) | Cxxx-NCR-003084 | NCR | __ PLC |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-03-22 | 2019-06-07 13:41 | 77 | 2019-01-30 10:14 | Electrical - General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | The Contractor does not have an approved MCR in place for __ Programmable __Controllers (PLC's).
| 03SR - Stations (RfL) | Cxxx-NCR-003085 | NCR | Bakerloo back of house CMS issue with PAVa Cables |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-09-30 | 2019-08-09 13:04 | -52 | 2019-02-04 12:45 | Electrical - Cable Management | 2500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | It was noticed in BOH corridor Bakerloo link, there is 100v Pava cables in the middle compartment of CMS with comms cables. We should not have LV cables and Comms cables sharing the same compartment. This affects Zone 14, 15 & 16 PAVA systems. Can this be fixed please
| 03SR - Stations (RfL) | Cxxx-NCR-003086 | NCR | Vent Head House CMS not fit for environment |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-08-01 | 2019-10-04 12:00 | 64 | 2019-02-05 11:50 | Electrical - Cable Management | 1500 |  | Design | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Materials used for the CMS within the vent head house is not suitable for the environment it ins installed in.
| 03SR - Stations (RfL) | Cxxx-NCR-003087 | NCR | Design coordination with structural openings in __ |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2019-07-31 | 2019-08-08 15:37 | 8 | 2019-02-06 15:34 | Civil - Civil Engineering General | 3000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The bottom of the structural openings for the doors to CIR-PL XIII, LB-S XII and LB-S XIII (main Box to __) are above the current designed FFL. It is not yet clear if the openings were cast incorrectly or if the current design has taken into account the dimensions of the structural openings. In either scenario there will be extensive rework, time and cost. RFI #4565 has been raised suggesting the responsibility is now with Cxxx to agree to lowering the finished level of the openings, this may not be possible and the design may need to be changed to reflect the current openings.
| 03SR - Stations (RfL) | Cxxx-NCR-003088 | NCR | VSHH - Aluminium Fins - Fabrication Records |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-06-08 | 2019-05-31 13:21 | -8 | 2019-02-08 15:35 | Architectural - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | For the manufacture of the demountable aluminium roof fins for the Vent Shaft Headhouses, there are no check sheets available for the fabrication process as per the accepted ITP (Cxxx-SKC-Z-ITP-B071_WS077-50157). The checksheet specified in the ITP is Production, Planning and Control Check Sheet AMF-04D-B.
| 03SR - Stations (RfL) | Cxxx-NCR-003089 | NCR | VSHH - Aluminium Rainscreen - Fabrication Records |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-06-08 | 2019-04-17 09:52 | -52 | 2019-02-08 15:47 | Architectural - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | The East Vent Shaft Head house rainscreens were fabricated by ITC on behalf of __. have not received the check sheets are per the accepted ITP (Cxxx-SKC-C-ITP-B071_WS077-50169) for the fabrication.
| 03SR - Stations (RfL) | Cxxx-NCR-003090 | NCR | Smoke damper clash with CMS in corridor (outside SOR room) |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-03-22 | 2019-03-04 12:46 | -18 | 2019-02-14 10:26 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | The transfer air duct between MIST-I and SOR features 2 in the wall fire dampers, FD13/AHU01/W and FD14/AHU01/W, respectively. There are a number of issues with the coordination of these fire dampers and MEP services in the vicinity: 1. FD14/AHU01/W has an actuator located in the SOR room which is not accessible. 2. The damper blade of FD14/AHU01/W clashes with corridor CMS and trapeze supports. (See attached photos.) The damper blade of FD13/AHU01/W to be checked to confirm if it does not clash with corridor CMS and trapeze supports. Reference drawing: Cxxx-SKC-Y-DDA-M171_3-61545
| 03SR - Stations (RfL) | Cxxx-NCR-003091 | NCR | Crossrail Arch - Block E Staircase PFC Supporting Beam Defect |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-04-17 | 2019-08-22 14:31 | 127 | 2019-02-16 12:58 | Structural Engineering - Steel Member | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | It has been identified that there is an incorrectly drilled hole within one of the newly installed block E staircase PFC steel supporting beams (see attached photo). The incorrect hole is roughly 400/500mm away from the end of the steel beam and does not form part of the required holes within the steel supporting beam for any connection points.
| 03SR - Stations (RfL) | Cxxx-NCR-003092 | NCR | Orientation of hydrant signs |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-05-31 | 2020-07-07 07:15 | 403 | 2019-02-18 12:50 | Architectural - Signage | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The contractor raises this NCR due to the incorrect orientation of the hydrant sign installed. The hydrant patch should be located at the furthest point from the wall, on the east side GL17 the sign installed has the patch closest to the wall.
| 03SR - Stations (RfL) | Cxxx-NCR-003093 | NCR | Lobby pressurisation ductwork not coordinated with fire compartment ceiling |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-03-22 | 2019-03-16 12:52 | -6 | 2019-02-19 12:07 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Lobby pressurisation duct on the intermediate level east (LB-S VIII #88)discharges into the fire compartmented ceiling area, not directly into the lobby. (See photos attached.) Ductwork and compartmented ceiling have not been coordinated. Contractor to coordinated the design and install to ensure the lobby pressurisation system functions correctly. Contractor to review all lobby areas to ensure ductwork and compartmented ceilings are coordinated.
| 03SR - Stations (RfL) | Cxxx-NCR-003094 | NCR | VSHH - Chiller Farm Upstand, Access hatch and Hoist co-ordination |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-05-10 | 2019-07-09 15:54 | 60 | 2019-02-23 14:57 | Architectural - Roofing & Exterior Treatment | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | Current design co-ordination around the Access hatches on the East and West VSHH Chiller Farms is insufficient causing clashes with the following items - Access Hatch and connection with, and waterproofing of, installed upstand. - existing __ for hatch incorrectly located in the slab causing reduced landing sizes, resulting in required changes to access ladders - insufficient __'s located through Chiller farm slab resulting in additional services being installed through access hatches requiring a further design change - Due to the above issues, design and location of man/material hoist is required to be changes and altered to allow for the above changes This applies to both the west and east Chiller farm access hatches.
| 03SR - Stations (RfL) | Cxxx-NCR-003095 | NCR | VSHH - Access Ladder design co-ordination |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-04-24 | 2020-09-21 10:44 | 516 | 2019-02-23 15:04 | Architectural - Balustrade | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | The design on the installed access ladders providing access to VSHH Mezzanine level, both east and west, is incorrect. Current design has no hand holds or grab rails at the top level to provide safe access onto and off of the ladder. There is also no way to secure the access hatch lid open once it has been opened to get access to the required levels.
| 03SR - Stations (RfL) | Cxxx-NCR-003096 | NCR | __ steelwork - ESC 10 & 11 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-05-31 | 2020-07-23 08:10 | 419 | 2019-02-25 17:35 | Structural Engineering - Structural Engineering - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Steel work interfacing with Bronze cladding and the hydrant enclosures located at platform level, has been identified as uncoordinated works. This impacts the escalator cladding, hydrant enclosures and installation of bronze.
| 03SR - Stations (RfL) | Cxxx-NCR-003097 | NCR | EXT-301 Bench Tops - Installation without Accepted MCR |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-03-26 | 2019-11-19 16:15 | 238 | 2019-02-26 08:38 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Not Defined | Completed |  | 9no. EXT-301 bench tops are to be installed prior to formal MCR acceptance. The benches are located between GL56 and GL76 on __.
| 03SR - Stations (RfL) | Cxxx-NCR-003098 | NCR | Water Sealant for the Canopy Column Conduit Couplers |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-08-21 | 2019-06-29 08:51 | -53 | 2019-02-26 12:15 | Electrical - Cable Management | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | FCR 1144 produced states that the couplers installed for the conduit should be encased with the same water proofing detail as the slab. However amalgamating tape has been used.
| 03SR - Stations (RfL) | Cxxx-NCR-003099 | NCR | Lack of isolation between (stone cladding) aluminium support bracket and concrete wall |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-03-13 | 2019-11-01 10:01 | 233 | 2019-02-27 15:40 | Architectural - Urban Realm | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The __ NV3 Rainscreen Cladding Support system is supplied with a polypropylene thermal isolator. By being situated between the aluminium wall bracket and the fixing substrate, the primary purpose of the pad is to prevent building heat loss through the system. During the MCR approval process it was requested, by Crossrail, to remove these pads from the installation process. As a result, approximately 60 linear metres of brackets and framework (between gridlines 28 - 36 and 102 - 112) were installed on the Departures Road wall without any isolation between the bracket and concrete substrate. As a consequence of this, the installation does not adhere to the ‘__A Agrement Certificate 09/4678 – __ Rainscreen Cladding Support Systems’ (attached); Section 10.2 states “Unprotected aluminium interacts with cement-based materials, resulting in severe corrosion. Therefore, aluminium brackets are supplied with polypropylene isolator pads, to be used when brackets are used in masonry walls”. Although not a masonry wall, the substrate does consist of a cement based material.
| 03SR - Stations (RfL) | Cxxx-NCR-003100 | NCR | EXT-310 Bollard Foundation Damage |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-05-31 | 2019-11-21 12:00 | 174 | 2019-02-28 12:37 | Civil - Civil Engineering General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | 1no. EXT-310 bollard foundation (western most leg) has been damage on E__ GL60-62 as shown in the attached photo.
| 03SR - Stations (RfL) | Cxxx-NCR-003101 | NCR | VSHH - Installation of __ Roof - Checksheets and Delivery Notes |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-05-31 | 2020-03-11 11:39 | 285 | 2019-02-28 12:09 | Architectural - Roofing & Exterior Treatment | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The Subcontractor, __, installed the __ Roof to the East VSHH. However, __ went into administration and ceased trading in 2017. __ had not provided the ITP deliverables / check sheets (items 4.1-4.6 of the ITP) prior to them entering into administration. Additionally, __ had ordered the materials for both the east and the west VSHHs __ roofs. Thus do not have the delivery notes for the materials (Item 3.2 of the ITP)
| 03SR - Stations (RfL) | Cxxx-NCR-003102 | NCR | Fire Main - pressure tested pipework being opened up to fit sleeves |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-07-31 | 2020-01-28 12:58 | 181 | 2019-02-28 13:46 | Fire - Suppression | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | CRL observed that both the tunnel and station fire main pipework have been opened up to facilitate installing pipe sleeves through the compartmented ceiling. The fire main pipework IRNs have been previously issued to CRL as completed works, including the static pressure testing (see IRNs 205 to 208 in reference documents). This issue was observed in the following locations: * Intermediate lift lobby East - Sleeves have been fitted on both tunnel and station fire main pipework. * Intermediate lift lobby West - Sleeve has been fitted on station fire main pipework See attached photos. CRL have not been consulted prior to the opening up of fire pipework systems, consequently have not been given the opportunity to accept the work. The Contractor is require to confirm the works have taken place, and to inform the Project Manger of how the works will be certificated and assured.
| 03SR - Stations (RfL) | Cxxx-NCR-003103 | NCR | LB S XIII 94 Departures Road GL17.5 Thrust Block fixings ineffective due to Core Hole |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-03-31 | 2020-02-15 10:31 | 321 | 2019-03-01 08:08 | Mechanical - Mechanical Engineering General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | A core hole was required as per the design in the LB S XIII 94 @ Departures Road GL17.5, however, the hole now renders the pipework thrust bracket ineffective. To rectify will revise the thrust bracket position design and alter the position.
| 03SR - Stations (RfL) | Cxxx-NCR-003104 | NCR | Maintaining Vent Head House Light Fittings |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-08-02 | 2019-09-07 10:55 | 36 | 2019-03-04 14:15 | Electrical - Lighting | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Light fittings have been installed within the vent head houses (east and west) opposite the maintenance walkway which can only be accessed using non standard methods
| 03SR - Stations (RfL) | Cxxx-NCR-003106 | NCR | Non-Installation of Blockwork Cavity Barrier - Concourse GL 9 & 16 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-04-26 | 2019-06-13 08:33 | 48 | 2019-03-07 17:53 | Fire - Compartmentation | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | There is a requirement to install a blockwork cavity barrier at grid line 9 & 16 on concourse level from the perimeter blockwork wall to the diaphragm wall. This was missed from the design and therefore will require localised demolition of the blockwork wall in these locations (UNA 1 and PCS 1).
| 03SR - Stations (RfL) | Cxxx-NCR-003107 | NCR | Access Blocked for MEPH Maintenance (GL 2 & 23 Ships Ladders) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-06-29 | 2019-07-06 12:42 | 7 | 2019-03-08 07:39 | Architectural - General | 1500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Whilst installing the ships ladders to the MNS IV & V rooms from __ to the mezzanine level, it was discovered that the installation of the ladder to the roof level will prevent access to a section of area that houses MEPH services in the future. These locations have been marked on the attached drawings. Note: __ have not raised this a comment within their design reviews.
| 03SR - Stations (RfL) | Cxxx-NCR-003111 | NCR | BLB Waffle Camera panel |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-05-10 | 2019-09-05 15:05 | 118 | 2019-03-11 10:58 | Architectural - Finishes | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Due to late release of information from the designer, a panel has been designed as a standard panel. A camera bracket has been installed within the waffle meaning the current panel does not work, in order to be utilized as an accessible panel this will have to be redesigned. allowing the panel to be hinged on two sides as opposed to one sided.
| 03SR - Stations (RfL) | Cxxx-NCR-003112 | NCR | VSHH East - Mezzanine area Steel access flooring |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-05-10 | 2019-09-05 15:07 | 118 | 2019-03-11 12:04 | Architectural - Flooring | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | During installation of the raised steel access flooring in the East VSHH at GL 23, it was discovered that the their was a clash with existing services along the Southern side of the flooring that was previously not picked up during the onsite survey and design drawing review and sign off.
| 03SR - Stations (RfL) | Cxxx-NCR-003113 | NCR | Handrail lengths - BLL |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-07-31 | 2019-08-01 07:34 | 1 | 2019-03-11 11:55 | Architectural - Finishes | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Handrails within the Bakerloo stairs have been fabricated to incorrect lengths therefore they cannot be completed. the handrails have been sent back to __ factory to ensure they fit as per requirement. This occurs in various areas within the staircase.
| 03SR - Stations (RfL) | Cxxx-NCR-003114 | NCR | Concourse drainage air leak |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-08-01 | 2019-07-06 12:44 | -26 | 2019-03-11 15:11 | Mechanical - Piping | 2500 |  | System Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | identified air leak within cast in drainage
| 03SR - Stations (RfL) | Cxxx-NCR-003115 | NCR | Tiling and access hatch interface - ESC 14&15 Platform level |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-05-20 | 2019-08-01 08:46 | 73 | 2019-03-11 13:59 | Architectural - Finishes | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Interfacing problems | Completed |  | The level of the tiling in relation to the access cover installed around the balustrades have discrepancy's therefore the access covers will need to be amended to suit the level of the tiling. This is just on the west bound side.
| 03SR - Stations (RfL) | Cxxx-NCR-003116 | NCR | EXT-310 Bollard Foundations - Locating Pin Omission |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-05-06 | 2020-02-01 10:10 | 271 | 2019-03-11 17:06 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The EXT-310 bollard foundations between GL50 and GL90 have been installed without the 'locating pin' connecting adjacent units. This pin position is shown in the attached image.
| 03SR - Stations (RfL) | Cxxx-NCR-003117 | NCR | Air Release Ductwork Eastbourne Terrace East - reduced clearance to fully lag duct (IRN-212) |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-06-28 | 2019-04-27 08:39 | -62 | 2019-03-14 15:04 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Clearance between air release duct and sump extract is ~60mm, and ~30mm at the sump extract flange. This clearance is insufficient to lag both ducts and overlap the extract flange. There is also a pinch point lower down where clearance between the 2 ducts is less than 50mm at the flange. (Ref. blue highlighted section on photo.)
| 03SR - Stations (RfL) | Cxxx-NCR-003118 | NCR | Intermediate and Concourse Staff Rooms Conduit not hidden/ chased |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-07-29 | 2019-08-01 09:33 | 3 | 2019-03-15 13:36 | Architectural - Partitions | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Within staff rooms on Intermediate and Concourse a bank of 3no conduits next to the room space heater are currently not chased into the blockwork and hidden as per the same detail as other single conduits within the room which are chased in, and then rendered over. Each room will be detailed below with a solution. As each room could not be access on visual inspection (12/03/19) the below rooms are anticipated to be affected: Intermediate: __F II SCR I GSM SMK Concourse: __F I [UPDATE 26.03.19] JAS TOOR Further to site walk and agreement between __ and __ the solution for each room is summarised as below: SCR I & GSM - These rooms are to remain as is. This is because the services & equipment mounted to the walls are required to be accessed. __F I, __F II & SMK - All Mechanical elements which are seen (pipework for heater & vertical pipework behind the kitchen unit on show) are to be boxed in using plasterboard, receive a skim coat and painted white. - All conduits which are 'single' (i.e on their own running down the wall) are already chased in to the blockwork, render applied and painted white. - The remaining electrical conduits which are in a 'cluster' of 3 next to the heater are to be boxed in using plasterboard, receive a skim coat and painted white. The box will finish in line with the front of the heater (with the switch being brought out to the face of the box out) and the box return installed enough to house the cluster of conduits. The box will be taken full up to the suspended ceiling. This solution should close the NCR as the conduit is 'hidden' in the applicable rooms.
| 03SR - Stations (RfL) | Cxxx-NCR-003119 | NCR | TRII-CWU (914) insufficient clearance between CCU and pipework to access junction boxes |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-07-31 | 2019-07-24 14:46 | -7 | 2019-03-15 16:52 | Mechanical - Mechanical Engineering General | 2500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | TRII-CWU (914) - insufficient clearance (~310mm) between CCU cooling unit and chilled water pipework to access 3 junction boxes located on wall. Pipework has yet to be lagged. See attached photo.
| 03SR - Stations (RfL) | Cxxx-NCR-003120 | NCR | Precast concrete finishes - minor chip[s and blemishes |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-08-31 | 2020-09-07 12:30 | 373 | 2019-03-17 11:27 | Civil - Structural Engineering | 5000 |  | Damaged | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Some of the precast soffit panels have minor chips and blemishes. To be addressed as part of a final snagging
| 03SR - Stations (RfL) | Cxxx-NCR-003121 | NCR | AM103 High level under balustrade |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-03-31 | 2019-08-08 23:08 | 130 | 2019-03-17 15:57 | Architectural - Finishes | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | The contractor raises this NCR in relation to deviation from gated design and having to adapt the installation due to conditions on site. The stainless steel cover panels which provide cover for the concrete and lighting under the balustrade located on Departures Road, has had to be changed from submitted design due to site condition. The panel should have originally sat under the balustrade flush with the balustrade, due to MEP interface the panel could not be installed in the intended manner. Attached the drawing shows the original intent as per detail 6, then change has also been marked up on the attachment. An approved Benchmark has also been attached, which has been viewed by the Project Manager Representative prior to works being installed.
| 03SR - Stations (RfL) | Cxxx-NCR-003122 | NCR | Stair Disconnect Steelwork (Intermediate to __ ONLY) - No Allowance for Slab Deflection Above |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-07-31 | 2019-07-09 15:32 | -22 | 2019-03-19 15:08 | Structural Engineering - Steel Member | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | It has come to light that the stair disconnect steelwork installed to the landing on the MNS III stairs from __ to intermediate level, will not allow deflection of the slab adjacent to the stairs landing with the provided detail from Cxxx. This has been missed by all parties involved in this task. Please see attached Cxxx detail, __ fabrication drawing, fire protection detail and a photo showing the issue. Note: The RC element to the left of the gap within the photo is the section that has been disconnected; this therefore is connected to the wall below the deflection joint and by default to the same part of the structure as the beam. The RC element to the right of the gap is the slab above that we are trying to disconnect from, hence the issue of a beam being flush finished.
| 03SR - Stations (RfL) | Cxxx-NCR-003123 | NCR | PMI 1290 - __ cladding |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-06-30 | 2019-08-15 14:07 | 46 | 2019-03-20 13:36 | Architectural - Finishes | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Due to late issue and incorporation of Cxxx-PMI-1290, all the information was not incorporated into the __ design. Further to this Cxxx-FCD-002462, later captured conflicting information in relation to Cxxx-PMI-1290. The panels for the bronze had been released for fabrication on the basis of meeting the client programme and to ensure the fabrication slot could be booked in the factory. 2 no panels, bronze panels at the west end on platform level GL 8 will need to be remanufactured. __ have shown the panels set on the outside whereas PMI 1290 changed this configuration for the 2 no bronze panels to be located on the inside and have an allowance to mount the postercases. This will have an impact on the power socket as it will have to be relocated to the adjacent as per verbal agreement with CRL architect and __ MEP team. The bigger impact is the bottom panels will need to be remanufactured with an approx. lead time of 6-8weeks, the panel above this which interfaces with the smoke down screen will have to be accessible thus meaning the last smoke down screen panel cannot be installed until the lower panels get on site. Refer to attached mark ups.
| 03SR - Stations (RfL) | Cxxx-NCR-003124 | NCR | Difficient Thrust bracket design (fire Main ) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-08-01 | 2019-12-15 10:24 | 136 | 2019-03-20 10:46 | Fire - Suppression | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | outstanding bracket design and calculations (floor mounted anchor)
| 03SR - Stations (RfL) | Cxxx-NCR-003125 | NCR | Height issues Dept Road by LER 4 |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-04-09 | 2019-08-17 09:34 | 130 | 2019-03-20 11:25 | Electrical - Cable Management | 2000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | It was noted that CMS installed on the east side of departures road by LER4 is below the required head height for back of house areas of 2.2m. Circuits on the CMS are fed from EDB6/U/E the IRN is not to be signed until the CMS has been raised.
| 03SR - Stations (RfL) | Cxxx-NCR-003127 | NCR | East Departures road stairs cast incorretly |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-07-19 | 2019-07-17 13:01 | -2 | 2019-03-20 13:33 | Architectural - Flooring | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Concrete stairs in east Departures road have been cast incorrectly.
| 03SR - Stations (RfL) | Cxxx-NCR-003128 | NCR | BLL sump pump - access and maintenance (IRN-449) |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-08-01 | 2019-08-30 15:36 | 29 | 2019-03-21 15:35 | Mechanical - Pumps | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | - The installation of the sump pumps is not in accordance with design and construction drawings: o Cxxx-SKC-P-DDD-M171_7-00007 P01 o Cxxx-SKC-Y-DDA-M171_7-68114 C01 - The installation is not in compliance with Project Specification Cxxx-SKC-M-RSP-B071_WS077-50004 “JY20.1407b… Each pump shall be complete with a chain and guide rails to enable withdrawal.” - The gate valves have not been installed with extender chain wheels for operating valves without entering the sump pit. - The installation of the sump pumps and isolation valves is non compliant with the removal methodology set out in Cleaning & Maintenance Report (Cxxx-SKC-A-STP-B071_WS077-50004 Rev. 19 Appendix K). - The maintenance verification requirements instructed under Cxxx-PMI-01442 need to be actioned by the Contractor. See attached photo
| 03SR - Stations (RfL) | Cxxx-NCR-003129 | NCR | Winching Points - Bolt Openings Blocked |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-04-21 | 2019-08-01 10:36 | 102 | 2019-03-22 09:09 | Architectural - General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the installation of the winching points, it was discovered that some of the bolts installed within the M16 stainless steel couplers had been removed and as such, the couplers were filled with screed and other detritus. Please see attached marked up drawings that are affected. Note: Only those highlighted are affected. All other floor and wall mounted winching points have been installed as per the design.
| 03SR - Stations (RfL) | Cxxx-NCR-003130 | NCR | ESS & INS Escape Stairs - Handrails |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-05-24 | 2019-07-23 14:04 | 60 | 2019-03-22 12:26 | Architectural - Handrail | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | This NCR covers issues that have arisen in the ESS & INS escape stairs. Please see below: Issue 1) Handrails are in non-compliance with LUL S1133 as they have been installed beneath the RC return. S1133 specifies that there must be a minimum of 600mm clearance above any handrail. As you can see from the photo's this is not the case. The F1 does not state that this clearance is required and instead states the importance of maintaining the 2000mm minimum spacing between adjacent handrails as the most important factor. Therefore, __ have designed a spacing of greater than 2000mm and the handrails now are installed beneath the RC return. Issue 2) The F1 design did not take into account the RC recess at the top of the INS 1 and INS 2 staircases (see highlighted section). As such, the __ design did not take this into account. Issue 3) The F1 design did not take into account the nib within the RC structure, as indicated on the Cxxx structural drawings, and therefore the __ F2 design was produced to indicate a straight handrail. Please see attached drawings and photo. Note: this affects the external handrail at platform only. Issue 4) The handrails have been terminated at the top of the ESS 2 staircase, where the gated design shows them passing around the corner and terminating at the top of the ramp. I have attached the LUL standard for Premises - Stairways and Ramps (1-133) for clarity.
| 03SR - Stations (RfL) | Cxxx-NCR-003131 | NCR | Bakerloo wall cladding |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-07-31 | 2020-01-13 16:56 | 166 | 2019-03-22 14:40 | Architectural - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Bakerloo wall cladding panels clashing will need to be refabricated.
| 03SR - Stations (RfL) | Cxxx-NCR-003132 | NCR | __ Balustrade - Primary plate washer |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-06-19 | 2019-07-13 08:50 | 24 | 2019-03-22 15:09 | Architectural - Balustrade | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | It has been noted some areas of the __ primary balustrade bracket outside the access hatch.
| 03SR - Stations (RfL) | Cxxx-NCR-003133 | NCR | Canopy - Aluminium Cladding Cleaning |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-09-17 | 2019-08-02 13:28 | -46 | 2019-03-27 16:47 | Architectural - General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The aluminium cantilever cladding around the perimeter of the canopy appears to have a small amount residue remaining from the protective film that had been applied to the panels after manufacture.
| 03SR - Stations (RfL) | Cxxx-NCR-003134 | NCR | IRN 174 Access and maintainability |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-07-31 | 2019-06-02 11:11 | -59 | 2019-03-29 16:44 | Fire - Fire Systems & General | 2500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Limited access for maintainability of fir system equipment in multiple locations All works has been completed NCR raised to capture inspection of completed works post milestone handover.
| 03SR - Stations (RfL) | Cxxx-NCR-003135 | NCR | IRN 169 Access and maintainability |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-07-31 | 2019-06-02 11:26 | -59 | 2019-03-29 16:50 | Fire - Fire Systems & General | 2500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Limited access for maintainability of fir system equipment in multiple locations All works has been completed NCR raised to capture inspection of completed works post milestone handover.
| 03SR - Stations (RfL) | Cxxx-NCR-003136 | NCR | IRN 170 Access and maintainability |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-07-31 | 2019-06-02 11:28 | -59 | 2019-03-29 16:37 | Fire - Fire Systems & General | 1500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Limited access for maintainability of fir system equipment in multiple locations All works has been completed NCR raised to capture inspection of completed works post milestone handover.
| 03SR - Stations (RfL) | Cxxx-NCR-003137 | NCR | Disabled Toilet Alarm |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-04-14 | 2019-07-06 12:46 | 83 | 2019-03-31 11:12 | Electrical - LV Equipment | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | A stand alone alarm system is required within the disabled toilet. An alert is required within the SOR and this has not been designed within the SOR room layout.
| 03SR - Stations (RfL) | Cxxx-NCR-003138 | NCR | Access to Smoke Damper FD16/AT/W in ESR-I |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-07-31 | 2019-09-19 14:36 | 50 | 2019-04-16 10:33 | Mechanical - Heating Ventilation & Air Conditioning | 2500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The Project Manager's Team have observed that air transfer smoke damper ' FD16/AT/W' located in the Emergency Switch Room (ESR-I) is not accessible due to CMS and electrical equipment being installed below. (See attached photo.)
| 03SR - Stations (RfL) | Cxxx-NCR-003139 | NCR | VSHH pipe and lifting beam clash |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-07-01 | 2019-10-11 14:36 | 102 | 2019-04-02 07:37 | Mechanical - Piping | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | the drain pipe currently clashes with the maintenance beam which is not in accordance with Cxxx Maintenance strategy
| 03SR - Stations (RfL) | Cxxx-NCR-003141 | NCR | AFIL cable chopped through in Central Concourse area |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-07-01 | 2019-06-29 08:59 | -2 | 2019-04-02 10:34 | Electrical - Electrical Engineering General | 1500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | AFIL cable chopped through in Central Concourse area by flooring contractor
| 03SR - Stations (RfL) | Cxxx-NCR-003143 | NCR | ATS MCC04 outgoing Cable (SWA) Termination Block position |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-04-16 | 2019-11-18 15:26 | 216 | 2019-04-02 15:49 | Electrical - General | 3000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Other | Completed |  | In order to accommodate additional cables in "ATS MCC04" in PFR II, outgoing cable termination block from ATS is been forced to an unacceptable position and also caused tension in outgoing cable bending radius.ATS and all associated cables are IRN's and signed off by Client CRL. This change is not notified to QA team or Client.
| 03SR - Stations (RfL) | Cxxx-NCR-003144 | NCR | Incorrect Ironmongery design for main box escaper stairs doors |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-07-31 | 2019-10-14 12:09 | 75 | 2019-04-03 07:22 | Architectural - Doors | 30000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | It was noted on a cross rail inspection on 19/03/19 that the escape stairs doors on platform level include bolt/pin lock on the non platform side of the doors. it was also noted that as these doors are escape stairs they may require push bar locks. Upon inspection of the door schedule and ironmongery schedule these doors have been fabricated to the __ design. Doors effected include: D4-74a, D4-634, D4-72b, D4-633,D5-53, D5-634c, D5-84, D5-632, D5-81, D5-633b, D5-82, D5-631 RFI 3867 has been raised to __ to confirm if push bars are required. Bolts/pins should be removed from the doors effected.
| 03SR - Stations (RfL) | Cxxx-NCR-003146 | NCR | Canopy Wash Drain Down Pump (West and East) IRN-232 & 233 |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-06-30 | 2019-12-06 15:38 | 159 | 2019-04-04 09:14 | Mechanical - Piping | 1500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Wiring not complete to pumps and solenoid valves. Electrical cabling exposed. Pumps in damaged condition. Pumps exposed without permanent protection.
| 03SR - Stations (RfL) | Cxxx-NCR-003147 | NCR | Water Services Departure Road East - Dead Leg |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-05-31 | 2019-06-01 10:17 | 1 | 2019-04-04 09:25 | Mechanical - Piping | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Branch to canopy wash down non-compliant with requirement for dead leg protection not more than 2 pipe diameters from pipe 'T'. IRN-445.
| 03SR - Stations (RfL) | Cxxx-NCR-003149 | NCR | Pressurisation ductwork intermediate West - non-compliant bracket (IRN-213) |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-06-30 | 2020-01-29 07:10 | 213 | 2019-04-04 10:18 | Mechanical - Heating Ventilation & Air Conditioning | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Cantilever bracket support is non-compliant with __ support detail S9 on Cxxx-SKC-M-DWG-B071_WS077-50152 C06. Location intermediate level west GL7 (outside CWP room)
| 03SR - Stations (RfL) | Cxxx-NCR-003150 | NCR | Canopy Drain Down West - Dead Leg |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-05-31 | 2019-06-01 10:21 | 1 | 2019-04-04 09:33 | Mechanical - Piping | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Canopy Drain down water pipe does not drain down on the, chilled water plant room, side of the high level pipework which runs in the Departures Road corridor.
| 03SR - Stations (RfL) | Cxxx-NCR-003152 | NCR | Platform Smoke Damper (West) - Installation not ss the design - IRN-394 |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-08-31 | 2019-10-03 07:34 | 33 | 2019-04-04 10:03 | Mechanical - Heating Ventilation & Air Conditioning | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Also refer to: Cxxx-EWN-03466 Room SWR1 - Smoke/Fire damper mounted at high level, ductwork not installed in accordance with the Construction issue drawing: * FD01/EF01/W (IRN-397 Platform West EF01/W dampers) * FD40/AHU01W (IRN-394 Platform West AHU01/W dampers) Off the wall damper installation has actuator facing wall and is not lagged with fire protection. Therefore incomplete fire compartmentation.
| 03SR - Stations (RfL) | Cxxx-NCR-003153 | NCR | H/L Exract Fan Intermediate West Plantroom EFR1 - IRN 218 |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-06-03 | 2019-08-07 14:13 | 65 | 2019-05-08 13:30 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | System Defect | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | High level maintenance access on top of unit. Drop rod supports move about, insecure. Flexible connections pulled off.
| 03SR - Stations (RfL) | Cxxx-NCR-003154 | NCR | EF03 Extract Fan West Intermediate Plantroom FAN1 |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-05-31 | 2019-06-29 09:07 | 29 | 2019-04-04 10:25 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | IRN- 219. Fan supports not as the __ drawings. Supports not secure and uprights too high. Top of fan casing requiresbuilders clean.
| 03SR - Stations (RfL) | Cxxx-NCR-003155 | NCR | Break in process for works carried out on IRN'd Assets |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-07-03 | 2019-06-01 10:25 | -32 | 2019-04-04 10:42 | Electrical - General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | General CMS housing cabling for PAVA currently owned by Cxxx has been altered without the correct process being followed or permissions
| 03SR - Stations (RfL) | Cxxx-NCR-003158 | NCR | Water Services Chiller Compound East - Dead Leg |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-06-30 | 2019-06-08 08:48 | -22 | 2019-04-09 09:47 | Mechanical - Piping | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Not Defined | Completed |  | Branch to chiller compound BIP tap non-compliant with requirement for dead leg protection to be provided not more than 2 pipe diameters from pipe 'T'. IRN-230.
| 03SR - Stations (RfL) | Cxxx-NCR-003159 | NCR | Water Services Chiller Compound East - Dead Leg |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-06-30 | 2019-06-08 08:50 | -22 | 2019-04-09 09:57 | Mechanical - Piping | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Not Defined | Completed |  | Branch to chiller compound BIP tap non-compliant with requirement for dead leg protection to be provided not more than 2 pipe diameters from pipe 'T'.
| 03SR - Stations (RfL) | Cxxx-NCR-003160 | NCR | Water Services Concorse Level - Dead Leg |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-05-31 | 2019-06-08 08:51 | 8 | 2019-04-09 10:12 | Mechanical - Piping | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Not Defined | Completed |  | Branch to Maintenance Equipment Room, BIP tap non-compliant with requirement for dead leg protection to be provided not more than 2 pipe diameters from pipe 'T'.
| 03SR - Stations (RfL) | Cxxx-NCR-003161 | NCR | Water Services Platform Level West - Dead Leg |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-06-30 | 2019-06-08 08:53 | -22 | 2019-04-09 10:18 | Mechanical - Piping | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Not Defined | Completed |  | Branch to Sump Pump Room, BIP tap non-compliant with requirement for dead leg protection to be provided not more than 2 pipe diameters from pipe 'T'.
| 03SR - Stations (RfL) | Cxxx-NCR-003162 | NCR | Water Services Platform Level East - Dead Leg |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-06-30 | 2019-06-08 08:55 | -22 | 2019-04-09 10:35 | Mechanical - Piping | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Not Defined | Completed |  | Branch to Sump Pump Room, BIP tap non-compliant with requirement for dead leg protection to be provided not more than 2 pipe diameters from pipe 'T'. Cxxx-IRN-230
| 03SR - Stations (RfL) | Cxxx-NCR-003164 | NCR | MEP Services Located Above Suspended Ceilings - Intermediate Level |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-07-31 | 2019-12-12 09:17 | 134 | 2019-04-09 13:48 | Mechanical - Mechanical Engineering General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Services affected: HVAC/CCU, Fire Suppression Control Vales, Smoke Dampers. Rooms Affected: Station Control Room, Locker Rooms, SCR. Suspended ceiling system has no facility to allow regular inspection and maintenance to services located above. Additionally no labelling is proved to identify the location of equipment requiring regular access.
| 03SR - Stations (RfL) | Cxxx-NCR-003165 | NCR | Chiller Compound Bib Taps - Anti Frost Tape |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-06-30 | 2019-06-29 09:10 | -1 | 2019-04-09 14:05 | Mechanical - Piping | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Anti-Frost electrical tape not installed for the full length of the pipe, approximately 4m of unprotected pipe. Thermal insulation and weatherproofing incomplete. IRN230
| 03SR - Stations (RfL) | Cxxx-NCR-003166 | NCR | Balustrade/ Entrance gate steel work interface |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-07-09 | 2019-07-19 11:38 | 10 | 2019-04-10 07:35 | Architectural - General | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The balustrade at GL 14 has been installed off grid as per approved drawing attached, it can be seen there is a 23mm discrepancy at the interface location of the entrance gate. This has had an impact on the secondary steelwork which has had to be sent off site for amendments and galvanising.
| 03SR - Stations (RfL) | Cxxx-NCR-003167 | NCR | Secondary steelwork - plate allignment |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-07-31 | 2019-10-01 12:50 | 62 | 2019-04-10 13:33 | Architectural - General | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The secondary steelwork installed on site does not line up with the predrilled holes, therefore this will have to be amended on site the subcontractor will be required to drill new holes on site. Due to this being the only area the holes will be drilled and protected with a zinga spray coating, this will require 4no holes to be drilled into the hollow section beam.
| 03SR - Stations (RfL) | Cxxx-NCR-003168 | NCR | UNA I - Lighting |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-08-01 | 2019-07-06 12:55 | -26 | 2019-04-10 14:14 | Electrical - Lighting | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Cxxx-SKC-E-DDA-M171_4-41524 shows lighting within UNA I feed from -DB6/AS/E/4L2 -DB8/BS/E/5L2 -EDB4/U/E/2L3 All have been IRNd which contained red lines with no lighting within the rooms.
| 03SR - Stations (RfL) | Cxxx-NCR-003169 | NCR | Water Services Departure Road East - Dead Leg |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-08-01 | 2019-07-06 12:57 | -26 | 2019-04-11 09:04 | Mechanical - Hot & Cold Water Supplies | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Redundant pipework has been installed between the tank room and riser. - One leg to ex water mist tank. - One leg to future drinking point. Drawing Ref: Cxxx-SKC-P-DDE-M171_Z-50510
| 03SR - Stations (RfL) | Cxxx-NCR-003170 | NCR | Water Services Departure Road East - Dead Leg - Fire Main |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-07-31 | 2019-07-26 15:09 | -5 | 2019-04-11 09:18 | Mechanical - Hot & Cold Water Supplies | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Tank Room, unprotected dead leg. Section of pipe between fire branch Double Non-Return valve and 'T' with incoming main supply pipe. Drawing Ref: Cxxx-SKC-P-DDE-M171_Z-50510 IRN 230
| 03SR - Stations (RfL) | Cxxx-NCR-003171 | NCR | Water Services Intermediate Level - Deg Leg - DW Branch |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-06-30 | 2019-07-18 16:09 | 18 | 2019-04-11 09:25 | Mechanical - Hot & Cold Water Supplies | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Redundant pipework to DW. Drawing Ref: Cxxx-SKC-P-DDE-M171_Z-50510. IRN 230.
| 03SR - Stations (RfL) | Cxxx-NCR-003172 | NCR | Water booster Tank - Chiller Water Plantroom - Intermediate Level |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-06-30 | 2020-01-24 13:27 | 208 | 2019-04-11 09:52 | Mechanical - Hot & Cold Water Supplies | 500 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Power wiring incomplete. Pipework lagging incomplete. IRN444.
| 03SR - Stations (RfL) | Cxxx-NCR-003173 | NCR | Water booster Tank - Chiller Water Plantroom - Intermediate Level |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-06-30 | 2019-11-03 09:44 | 126 | 2019-04-11 10:05 | Mechanical - Hot & Cold Water Supplies | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Booster Tank over flow does not terminate over floor gully.
| 03SR - Stations (RfL) | Cxxx-NCR-003174 | NCR | Water booster Tank - Chiller Water Plantroom - Intermediate Level |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-07-31 | 2019-07-13 08:57 | -18 | 2019-04-11 10:18 | Mechanical - Hot & Cold Water Supplies | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | 15mm tank valve connected to 35mm supply pipe. Design not verified by calculation and tank valve technical details. Drawing Ref: Cxxx-SKC-P-DDE-M171_Z-50510.
| 03SR - Stations (RfL) | Cxxx-NCR-003176 | NCR | Water Booster Tank - Departures Road |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-08-01 | 2019-07-13 09:01 | -19 | 2019-04-11 10:40 | Mechanical - Hot & Cold Water Supplies | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | 15mm tank valve connected to 35mm supply pipe. Design not verified by calculation and tank valve technical details. IRN445 Drawing Ref: Cxxx-SKC-P-DDE-M171_Z-50510.
| 03SR - Stations (RfL) | Cxxx-NCR-003177 | NCR | Water Services Departure Road East - Booster Tank Room - Gully |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2020-08-31 | 2019-06-02 10:02 | -456 | 2019-04-11 12:03 | Mechanical - Public Health Engineering | 500 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | No drain gully in floor.
| 03SR - Stations (RfL) | Cxxx-NCR-003178 | NCR | Water Services Departure Road East - Booster Tank Room -Tank Drain |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-07-31 | 2019-06-08 09:13 | -53 | 2019-04-11 12:16 | Mechanical - Hot & Cold Water Supplies | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Water booster tank drain is fitted with lever isolation valve.
| 03SR - Stations (RfL) | Cxxx-NCR-003179 | NCR | Water Services Intermediate Level - Chiller Water Plant Room - Tank Drain |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-07-31 | 2019-06-08 09:14 | -53 | 2019-04-11 12:23 | Mechanical - Hot & Cold Water Supplies | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Water booster tank drain is fitted with lever isolation valve.
| 03SR - Stations (RfL) | Cxxx-NCR-003180 | NCR | Departures Road Water Services - Connection to Hydrant Fill Tank |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-07-31 | 2019-06-29 09:22 | -32 | 2019-04-11 12:32 | Mechanical - Hot & Cold Water Supplies | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Incomplete pipework. IRN 445
| 03SR - Stations (RfL) | Cxxx-NCR-003181 | NCR | Departures Road - Mains Water Connetion - East and West |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-07-31 | 2019-07-06 13:13 | -25 | 2019-04-11 12:40 | Mechanical - Hot & Cold Water Supplies | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | No connections to incoming water main at East and West. IRN230, IRN444, IRN445 not exhaustive.
| 03SR - Stations (RfL) | Cxxx-NCR-003183 | NCR | Damage to vinyl flooring in __F I |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-07-31 | 2019-12-18 15:50 | 140 | 2019-04-11 15:43 | Architectural - Flooring | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | During inspection of __F I 4 number holes were discovered in the vinyl flooring. holes are ~6mm in diameter and are located in the centre of the room. Holes are consistent with the 6mm fixings used by contractor installing the pipework/conduit boxouts.
| 03SR - Stations (RfL) | Cxxx-NCR-003184 | NCR | 2no RHPs Damaged on Concourse Level (Lift Lobbies) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-07-31 | 2019-06-08 09:28 | -53 | 2019-04-11 15:01 | Communications and Control Systems - Telephony | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Damage has been caused to 2no RHPs on the Concourse level (RHP housing have been dented on both units). Located on the Concourse Level - Lift Lobbies (Related IRN 285). RHP references: PAD-03-RHP-00301 and PAD-03-RHP-00306.
| 03SR - Stations (RfL) | Cxxx-NCR-003185 | NCR | Poor screed finish in LB-S XII |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-05-19 | 2019-07-17 13:21 | 59 | 2019-04-17 09:35 | Architectural - Flooring | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Screed in LB-S XII has been laid to a poor quality.
| 03SR - Stations (RfL) | Cxxx-NCR-003186 | NCR | Change to mist suppression system without updated design |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-07-14 | 2019-06-29 09:32 | -15 | 2019-04-15 09:37 | Fire - Suppression | 15000 |  | Design | Rework | 2 (6-60k) | Complete | Management Problem - Inadequate supervision | Completed |  | Suppression pipework has been enlarged without design change submission
| 03SR - Stations (RfL) | Cxxx-NCR-003187 | NCR | JRC Slab Thickness GL16-18 & 20-22 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-05-03 | 2019-06-13 08:38 | 41 | 2019-04-17 07:28 | Civil - Concrete Pavement | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The as-constructed JRC slab thickness is out of tolerance in two locations, at GL16-18/E+4.6m and GL20-22/E+4.6m. The minimum slab thickness witnessed is ~160mm as shown in the attached photos.
| 03SR - Stations (RfL) | Cxxx-NCR-003188 | NCR | Oversized bolt slots in heritage railing support steelwork |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-05-07 | 2019-11-21 11:45 | 198 | 2019-04-23 09:35 | Civil - Structural Engineering | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | It has been found that the bolt slots in the heritage railing support steelwork (east end detail only) are oversized when comparing to the drawing (Cxxx-SKC-Y-DDD-M171_Z-50056 attached). Section B-B of the drawing shows that the slots are to be 16x58mm (to pass M12 __ HIT VR anchors). Site measurements taken have shown these slots to be 17-18mm in the smaller dimension. As a result, the proprietary washers are too small for the slots and do not provide adequate overlap. In addition, due to the large size difference between the slot and the bolt, there is potential for the steelwork to slip and damage the bolts.
| 03SR - Stations (RfL) | Cxxx-NCR-003189 | NCR | Waterproofing Indicator Mesh Omission - ETL GL1-7 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-09-06 | 2019-10-12 10:26 | 36 | 2019-04-24 07:32 | Civil - Civil Engineering General | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Further to Cxxx-NCR-003033, this NCR is raised to cover the omission of the 'brightly coloured indicator mesh' above the elastomeric waterproofing protection screed on ETL GL1 to 7, south of the western VSHH. This indicator mesh is called for in drawing Cxxx-SWN-S-DDD-M171_Z-05550.
| 03SR - Stations (RfL) | Cxxx-NCR-003190 | NCR | Radio assets relocated post IRN |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-09-18 | 2019-06-29 09:34 | -81 | 2019-04-26 12:55 | Communications and Control Systems - Radio | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | ANT 44 and 45 relocated due to head height clash
| 03SR - Stations (RfL) | Cxxx-NCR-003191 | NCR | Crossrail Arch - Structural Steelwork Paint Protection Finish Alterations |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-06-21 | 2019-08-21 13:03 | 61 | 2019-05-08 14:20 | Structural Engineering - Surface Treatment | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | See attached Cxxx structural steelwork drawing mark up's showing the steel columns which the paint finishes is proposed to change from N9 to N17 intumescent paint system. Please can Crossrail and their designers Cxxx review the proposal and confirm their acceptance? Please reference raised FCD which is linked to this NCR which captures the proposed change of structural steelwork protection paint system.
| 03SR - Stations (RfL) | Cxxx-NCR-003192 | NCR | Materials installed without MCR approval |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-09-30 | 2019-08-01 10:31 | -60 | 2019-04-29 11:57 | Architectural - Urban Realm | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | A planned surveillance was carried on the urban Realm Earth Works. During a post review of the Materials Compliance Records (MCRs) and delivery tickets found that the Contractor has installed multiple loads of Type 1 Material from __ Recycling into the permanent works without an accepted MCR in place. A check on eB found ‘Type 1 ex. __’ Cxxx-SKC-O-TSC-B071_WS077-51590 (Rev 1) is designated as draft and therefore not accepted.
| 03SR - Stations (RfL) | Cxxx-NCR-003193 | NCR | Dissimilar materials used for the matwell drain at concourse level - and other detailing |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-07-31 | 2019-09-14 09:15 | 45 | 2019-04-30 08:45 | Architectural - Flooring | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | During a site visit the supervisor's Representative noted that fixings into the slab that secure the aluminium matwell drainage had various embedments and appeared to be zinc plated. Furthermore the channel supports were packed up on precarious shimming. This was all raised to the package manager at the time over 1 month ago but to date no definitive responses have been received. A search of eB has revealed that the supplier drawings are not available
| 03SR - Stations (RfL) | Cxxx-NCR-003194 | NCR | Incorrect materials used in intermediate level staff toilets |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-07-26 | 2019-07-26 13:29 | 0 | 2019-05-02 07:55 | Architectural - Walls | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | It has been noted that timber/ply has been used in the construction of the partition walls at intermediate level. The Spec provided to __ in SI-17 states two layers of moisture resistant plasterboard in SSR. Instead a single layer of plasterboard has been used with a Ply backing. There are also sections of timber in the access hatch frames in SWC I & II.
| 03SR - Stations (RfL) | Cxxx-NCR-003195 | NCR | Handrails Delivered with Wrong Finish - Future Use Floor Opening (Concourse NE) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-06-01 | 2019-05-28 08:39 | -4 | 2019-05-02 09:34 | Architectural - Handrail | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The handrails for the NE handrail around the cooling ducts future use opening within the concourse corridor (CIR-PL III, 74) has been delivered with galvanised factory finish. As these are on an escape route these handrails are required to be painted yellow.
| 03SR - Stations (RfL) | Cxxx-NCR-003196 | NCR | removal of screed in east riser \ toilet and kitchen |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-06-25 | 2019-06-29 09:51 | 4 | 2019-05-07 13:58 | Architectural - Flooring | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The floor screed in the east riser \ driver toilet and staff tea point is being broken out due to inconsistent levels and required gullies. Although this work has been identified, planned and started on site have omitted to raise the issue with the Supervisor's Representative, nor raise a non-conformance report. This is a contravention of the Contract Quality Plan.
| 03SR - Stations (RfL) | Cxxx-NCR-003198 | NCR | Design coordination error - FFL and __ damper door interface |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-06-12 | 2019-08-01 09:46 | 50 | 2019-05-13 08:12 | Architectural - Doors | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Interfacing problems | Completed |  | FFL in LBS XI has not been coordinated with the __ louver doors. FFL inside and outside the box have been coordinated and line up correctly. Upon checking the structural opening height it was noted that the door is currently 15mm bigger than the opening. the door size cannot change as the dampers are at the maximum airflow therefore cannot be reduced in size. Structural opening above cannot be increased as this will clash with the soffit. Best option will be to break out the screed and relay a ramp down to the doorway
| 03SR - Stations (RfL) | Cxxx-NCR-003199 | NCR | Missing radio cable drum numbers and test sheet |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-10-09 | 2019-09-14 09:20 | -25 | 2019-05-13 10:25 | Communications and Control Systems - Radio | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | Missing radio cable drum numbers and test sheet
| 03SR - Stations (RfL) | Cxxx-NCR-003200 | NCR | Snapped off heads - Eastern heritage railings |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-08-02 | 2019-10-12 10:29 | 71 | 2019-05-13 11:44 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | 6 number heads have been snapped off from the heritage railing panels. This has occurred in the transport process from the Undercroft to site.
| 03SR - Stations (RfL) | Cxxx-NCR-003201 | NCR | Scabblied concrete - Glass Balustrade |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-08-22 | 2019-09-04 08:13 | 13 | 2019-05-14 08:20 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During installation of the Glazed balustrade along the staircase at E__ level, the top of the concrete has been scabbled by 20mm to accommodate the bracket. This was not captured by any RFI when works have been carried out, the area which has been broken out has a layer of waterproofing applied to it. To further ensure no water ingress the bracket will be overlapped with a waterproof detail.
| 03SR - Stations (RfL) | Cxxx-NCR-003202 | NCR | contamination of cableways in sub-platform level - through ductwork |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-08-01 | 2020-01-17 14:11 | 169 | 2019-05-14 12:33 | Communications and Control Systems - General | 6000 |  | Design | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | It has come to the attention of the Supervisor's Representative that various mixed cables including fire, PAVA, fibres CCTV etc have been pulled through ducting in the sub-platform causing contamination of routeways. this is contrary to the specification and although unauthorised works to remedy this situation are ongoing, the Contractor has failed to notify of this non-conformance which is in contravention of the contract quality plan. In attempting to rectify this problem, the Contractor ahs damaged cable and now requesting
| 03SR - Stations (RfL) | Cxxx-NCR-003203 | NCR | Cxxx assets unaccounted for at Paddington site - 39Nr cameras |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-06-30 | 2019-06-08 09:31 | -22 | 2019-05-16 15:30 | Communications and Control Systems - CCTV | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | A total of 39 cameras are unaccounted for at the Paddington site. the breakdown is as follows; 1/ 23 heated camera`s V4320FDW-DN-BLK 2/ 11 Gateline camera`s V4320FDW-DN-BLK 3/ 5 intermediate camera`s V4320FDZ-DN-BLK (already supplied). It is currently unclear as to whether these have been returned to __ or not, however a search of the site storage containers has been carried out and they cannot be found at present.
| 03SR - Stations (RfL) | Cxxx-NCR-003204 | NCR | Concrete stairs cast to incorrect level |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-05-31 | 2019-07-17 13:12 | 47 | 2019-05-17 07:50 | Archaeology - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Stairs to the CSR riser on west __ were shuttered with out taking in to account the 30mm of screed to be installed in the riser. this caused the top step to be cast at the incorrect level.
| 03SR - Stations (RfL) | Cxxx-NCR-003205 | NCR | No waterproofing detail for Intermediate disabled shower |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-07-26 | 2019-07-26 13:26 | 0 | 2019-05-17 09:06 | Architectural - Flooring | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Waterproofing detail was incorrectly omitted from the design of the staff disabled shower on intermediate level.
| 03SR - Stations (RfL) | Cxxx-NCR-003206 | NCR | Mist pipework bracketry spacing (IRN-204) |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-08-01 | 2020-02-15 10:37 | 198 | 2019-05-20 14:48 | Fire - Suppression | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Bracketry spacing on the 28mm Mist pipe is non-compliant. All sample spacing measurements taken were found to be over 2.4m (see example photo 2.6m spacing). The Protect drawings state the spacing of 23mm to 29mm pipework to be at 1.82m (see Cxxx-SKC-E1-DWG-B071_WS077-50210 C02 – see screenshot attached) Location: Mist pipework and supports in Departure Road Corridor
| 03SR - Stations (RfL) | Cxxx-NCR-003207 | NCR | Cantilever support brackets - Mist Suppression (IRN-204) |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-08-01 | 2019-08-14 14:19 | 13 | 2019-05-20 14:55 | Fire - Suppression | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | Non-compliant cantilever support brackets have been installed. The brackets installed are threaded rod; the __detail is for cantilever power arm (see drawing Cxxx-SKC-E1-DWG-B071_WS077-50230 C03 see attached screenshot). Location – outside MAE-R II Room in corridor. See attached photos
| 03SR - Stations (RfL) | Cxxx-NCR-003208 | NCR | Dept Rd Mist pipework low level protection |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-08-01 | 2020-01-24 23:39 | 176 | 2019-05-21 08:34 | Fire - Suppression | 3000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Low level pipework protection has been damaged and knocked in multiple locations along Departure (see attached photo). The frame is not adequately secured. Additionally, __ frame does not protect pipework in-between protection frame.
| 03SR - Stations (RfL) | Cxxx-NCR-003209 | NCR | Canopy - Rainwater Pipes - Clamps on __ Expansion Socket |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-08-21 | 2019-06-13 08:51 | -69 | 2019-05-23 12:24 | Architectural - General | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The clamps on the __ expansion socket on the new rainwater pipes above the canopy have been installed in the incorrect position
| 03SR - Stations (RfL) | Cxxx-NCR-003210 | NCR | Missing bearing capacity assessment under GL14 Bollards |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-09-02 | 2020-02-17 15:23 | 168 | 2019-08-19 16:36 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A bearing capacity assessment was not undertaken on the founding soil for the GL14 Retractable bollard foundation as per the notes on the construction drawing. The foundation was built in full before the issue was raised and therefore a sample could not be taken on the founding soil directly below.
| 03SR - Stations (RfL) | Cxxx-NCR-003211 | NCR | Water heater in room CLN has casing damage IRN-235 |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-07-31 | 2019-07-13 09:03 | -18 | 2019-05-28 15:00 | Mechanical - Mechanical Engineering General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Water heater in Cleaners rom (CLN - Platform East) has casing damage. This is an asset covered in IRN-235. See attached photos. Contractor to provide a proposal for rectification.
| 03SR - Stations (RfL) | Cxxx-NCR-003212 | NCR | Installation of Matwell drainage Departure Road |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-09-18 | 2020-08-13 13:54 | 330 | 2019-05-28 15:25 | Mechanical - Public Health Engineering | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Location - Departure Road East GL14: - Departure Road East (GL14) matwell drainage has major damage and a visible hole. See attached photos taken at GL14. - Pipe with access section (__ 840.000.11 S) has been left uninstalled - __ drawing (Cxxx-SKC-Y-DDA-M171_2-68539) does not show this pipe with access detail Location - Departure Road West GL10: - Departure Road East (GL14) matwell drainage - pipe with access section (__ 840.000.11 S) has been installed. See photo. - __ drawing (Cxxx-SKC-P-DDA-M171_2-31536) does not show pipe access detail (__ drawing has layers missing and is not useable). - The __ pipe has been wrapped in a non compliant brown paper type material. See photo. Contractor to submit proposal for rectification of above defects.
| 03SR - Stations (RfL) | Cxxx-NCR-003213 | NCR | Transformer cooling unit return air arrangement (relates to IRN-455) |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-08-31 | 2019-10-12 10:32 | 42 | 2019-05-30 16:00 | Mechanical - Heating Ventilation & Air Conditioning | 5000 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Transformer cooling unit in rooms; TR-I CWU, TR-II CWU, TR-III CWU and TR-IV CWU, have not been installed in accordance with the construction issue drawings. The latest construction drawings, listed below, shows extract plenums (with fire damper) ducted directly into the top of the Close Control Units (CCUs). On site, the return air path has been modified, with the extract duct and fire damper discharging into the CWU room, with no direct connection to the CCUs (see attached photos). Cxxx-SKC-Y-DDB-M171_4-61506 C05 Cxxx-SKC-Y-DDB-M171_4-61507 C05 Cxxx-SKC-Y-DDB-M171_4-61540 C04 Cxxx-SKC-Y-DDB-M171_4-61546 C05
| 03SR - Stations (RfL) | Cxxx-NCR-003214 | NCR | Smoke Extract Scematic Incorrect Detailing |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-08-31 | 2019-09-07 11:03 | 7 | 2019-05-31 11:18 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | (Associated to IRN-215 / IRN-216 and PCC-196 / PCC-197.) Following checking of commissioning data it became apparent that the schematic drawings (Drg Nos. Cxxx-SKC-M-DDE-M171_Z-30580 and Cxxx-SKC-M-DDE-M171_Z-40580) do not align with the HVAC layouts (Drg Nos. Cxxx-SKC-M-DDA-M171_5-41552 to Cxxx-SKC-M-DDA-M171_5-41556 (5 drawings) and Cxxx-SKC-M-DDA-M171_5-31553 to Cxxx-SKC-M-DDA-M171_5-31557 (5 drawings). The number of grilles on the schematic drawings is split evenly either side of the platform (34 each side). The HAVAC layout drawings indicate that the grille split is 32 and 36, which is what is built on site. On further checking the schematics contain additional errors, as follows: 1. Manual platform knock buttons are shown - which are not provided. 2. The number of damper motors does not match what is provided. 3. All fans are shown NO (Normally Open). The standby fan is NC (Normally Closed). The Contractor is requested to have the schematic drawings reviewed corrected.
| 03SR - Stations (RfL) | Cxxx-NCR-003215 | NCR | Public area signage - Artwork |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-07-31 | 2020-07-07 07:18 | 342 | 2019-06-13 12:32 | Architectural - Signage | 30000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Some of the installed signage in public areas has errors in message and/ or graphic consistency with TfL standards. A detailed review with CRL/ Cxxx of each sign is required, to verify against standards and determine extent of remedial work.
| 03SR - Stations (RfL) | Cxxx-NCR-003216 | NCR | Installation commenced without accepted Materials Compliance Record (MCR) in place |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-09-30 | 2019-10-06 08:28 | 6 | 2019-06-04 08:02 | Architectural - Urban Realm | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During a surveillance site visit to look at the Natural Stone Cladding in Departures Road, it was noted that the Contractor has used __ HDP Breathable Membrane to separate the aluminum primary grid bracketry from the concrete structure. On checking eB it was found that there is no accepted MCR in place for __ membrane, for specific location and use as witnessed. See attached photograph.
| 03SR - Stations (RfL) | Cxxx-NCR-003217 | NCR | Uncontrolled changes to drainage pipework within Emergency Stairs East Platform Level (relates to IRN-460) |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-07-31 | 2019-07-18 16:14 | -13 | 2019-06-05 14:12 | Mechanical - Piping | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | 100mm dia. plant room drainage pipe in Emergency Stairs East (ESS-II) at Platform Level lobby (LB-S IV) has been modified post IRN-460 sign off (see attached photos). The changes to the pipework do not follow Construction drawing Cxxx-SKC-Y-DDA-M171_5-68601. No FCD or redline has been submitted to CRL. The pipework was previously pressure tested and will require re-testing. The screed and fire stopping has been broken out and is to be made good.
| 03SR - Stations (RfL) | Cxxx-NCR-003218 | NCR | Non-compliant anchors have been installed to connect stone cladding to structure. |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-12-19 | 2019-10-11 12:08 | -69 | 2019-06-05 07:54 | Architectural - Urban Realm | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During a Stone cladding Quality Surveillance site visit to Departures Road, It was noted that M10 anchors are in use to connect the primary grid to the concrete structure. On checking ‘Architectural Specification’ Cxxx-SKC-A-RSP-B071_WS077-50003-JH51.1302 states; Section to be read in conjunction with: ‘Performance Specification Cladding Secondary Steelworks’ Cxxx-SKC-S-RSP-B071_WS077-50003 KM: JH10.1218 states; anchors to RC and bolted fixings shall be at least M12. Both the design and structural calculations for the Natural Stone Cladding System have not been accepted at the time of writing and no evidence of acceptance to a change in the requirements of the above specification could be provided.
| 03SR - Stations (RfL) | Cxxx-NCR-003219 | NCR | Lift 10 Lobby (__) Handrail - Incorrect Fabrication of Handrail |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-07-05 | 2019-07-23 13:39 | 18 | 2019-06-05 15:48 | Architectural - Handrail | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The eastern handrail within the lift 10 lobby at __ has been fabricated incorrectly. The survey was not carried out by __ accurately and therefore the handrail does not work with the ramp and landings. It has also been delivered with only one rail instead of two, as required within an escape route.
| 03SR - Stations (RfL) | Cxxx-NCR-003220 | NCR | Contractor unable to provide manufacturing or installation checksheets for the Natral Stone Cladding |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-12-19 | 2019-10-01 13:53 | -79 | 2019-06-07 12:25 | Architectural - Urban Realm | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | At the time of the surveillance the Contractor was unable to submit the manufacturing records for Natural stone cladding in line with Cxxx-SKC-Z-ITP-B071_WS077-50256 and installation records in line with Cxxx-SKC-Z-ITP-B071_WS077-50273 . A request was made for the Contractor to supply the records post Surveillance. However, after multiple requests no records had been produced to provide progressive assurance.
| 03SR - Stations (RfL) | Cxxx-NCR-003221 | NCR | Heritage railing steelwork - Installation without AFC drawings |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-06-23 | 2019-11-21 11:40 | 151 | 2019-06-09 11:49 | Civil - Civil Engineering General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | have commenced elements of installation for heritage railing steelwork package without an approved DDCD. The DDCD is with __ on final round of comments, therefore is confident to proceed installation without risk to design change. The remaining open comments have been provisionally agreed with __ that they can be closed.
| 03SR - Stations (RfL) | Cxxx-NCR-003222 | NCR | Damaged drop rod |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-08-31 | 2019-08-09 14:44 | -22 | 2019-06-10 11:53 | Electrical - Cable Management | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Drop rod for multi service bracket has been damaged
| 03SR - Stations (RfL) | Cxxx-NCR-003223 | NCR | Cxxx Failed test on pumped drainage |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-08-18 | 2019-08-09 14:47 | -9 | 2019-06-19 14:24 | Mechanical - Piping | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Pipe work leaking under test pressure
| 03SR - Stations (RfL) | Cxxx-NCR-003224 | NCR | Water pipes installed above DBs in ERN-I |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-10-28 | 2019-10-22 10:45 | -6 | 2019-06-10 15:38 | Mechanical - Piping | 2000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Domestic water pipes installed at HL passing directly above electrical distribution boards and transformer in ERN-I (Platform West, adjacent to Tea Room TEP). See photos and drawings. Equipment in room: - __ Acti 9 Isobar: o DB7/AS/W/EB o DB7/AS/W/WB o DB8/BS/W/EB – __ Acti 9 Isobar o Blakely transformer
| 03SR - Stations (RfL) | Cxxx-NCR-003225 | NCR | VSHH - East - Roof - Water Ingress |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-10-31 | 2021-04-27 13:30 | 544 | 2019-06-11 15:47 | Architectural - Roofing & Exterior Treatment | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | There has potentially been water ingress through the east vent shaft headhouse roof. To be investigated further
| 03SR - Stations (RfL) | Cxxx-NCR-003226 | NCR | CCTV installations at __ and E__ proceeding without Planning Consent |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-10-31 | 2019-10-12 10:36 | -19 | 2019-06-12 10:02 | Communications and Control Systems - CCTV | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The CCTV installation at E__ and __ are proceeding at risk because the planning consent is not in place. Comments were raised on the application by Westminster at the beginning of 2019 and these issues were not detailed in the associated Gate Impact Report that stated no additional consents were required.
| 03SR - Stations (RfL) | Cxxx-NCR-003227 | NCR | Depatures Road New Plant Room blockwork remedial works |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-06-27 | 2019-06-20 10:50 | -7 | 2019-06-13 07:23 | Architectural - Brickworks/Blockworks | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the construction of the New plant room on Departures Road one no. builderswork hole for a damper was formed to the wrong dimension, one no. builderwork hole around cable tray did not allow sufficient space for firestopping and the door structural opening was not square.
| 03SR - Stations (RfL) | Cxxx-NCR-003229 | NCR | Corroded pipe support - canopy washdown column section |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-08-01 | 2019-07-06 13:23 | -26 | 2019-06-17 13:22 | Mechanical - Piping | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Corroded pipe support - canopy washdown column section Eastbourne Terrace level. One defect observed at low level. Further defects may exist but access was only available at one column and at a low level. Contractor is required to check on site how many locations this bracket has been installed.
| 03SR - Stations (RfL) | Cxxx-NCR-003230 | NCR | Non compliant material used for chilled water lagging |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-08-29 | 2019-08-14 14:14 | -15 | 2019-06-17 13:36 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Non compliant material used for chilled water lagging. Armatape material (see attached picture) has been installed on the benchmark room (__-R CWU) and other CWU locations. Armatape has no MCR. The approved material is Armaflex Ultima (MCR-6375).
| 03SR - Stations (RfL) | Cxxx-NCR-003231 | NCR | Pipe sleeve allignment for fire stoping |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-02-07 | 2020-11-12 10:08 | 279 | 2019-06-19 16:03 | Fire - Compartmentation | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | pipe sleeve positioning is that there is a minimum of 50mm between sleeves and from the edge of the sleeves to edge of penetration
| 03SR - Stations (RfL) | Cxxx-NCR-003232 | NCR | Door Signage - FDKL & FDKS Usage - Incorrect on Door Schedule |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-08-04 | 2019-07-13 09:20 | -22 | 2019-06-20 09:07 | Architectural - Signage | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | It has come to light that the door schedule (Cxxx-SKC-A-TSC-B071_WS077-50002) may be incorrect with regards to the usage of the FDKL & FDKS signage. The fire engineer provided an extract from an internal LUL document that states when each sign should be used. This was not previously available to have raised Cxxx-RFI-004614 on this issue and require formal CEG confirmation to fully proceed.
| 03SR - Stations (RfL) | Cxxx-NCR-003233 | NCR | Cooling unit damage in SMK |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-08-30 | 2020-08-11 14:09 | 347 | 2019-06-20 16:18 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Superficial damage to cooling unit casing located in SMK Intermediate level (see photo). Contractor to put forward proposal for remedial work.
| 03SR - Stations (RfL) | Cxxx-NCR-003234 | NCR | Trace heating damage to controller cable in DRS room (401) Departure Road West - IRN-240 |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-09-11 | 2019-09-18 09:32 | 7 | 2019-06-21 10:22 | Mechanical - Mechanical Engineering General | 1500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | 1. Factory fitted cable to controller has been cut. (See photos 8 and 9.) 2. Trace heating cable has been stripped and left bare. Cable has been left dangling and unsecured. (See photos 4 and 5.)
| 03SR - Stations (RfL) | Cxxx-NCR-003235 | NCR | VSHH (East) - Drawbridge Hinges |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-09-30 | 2019-08-01 07:43 | -60 | 2019-06-24 15:20 | Architectural - General | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During installation of the drawbridge to the East VSHH it was found that the hinges had been fabricated in the incorrect position / not as per approved drawing
| 03SR - Stations (RfL) | Cxxx-NCR-003236 | NCR | Unfinished Ducts and Drawpits prior to cable being pulled |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-07-08 | 2020-04-09 13:38 | 276 | 2019-06-24 15:42 | Electrical - Cable Management | 3000 |  | Planning | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Cleaning and finishing of drawpits in the Urban Realm not completed prior to cables being pulled through the ducts.
| 03SR - Stations (RfL) | Cxxx-NCR-003237 | NCR | Speaker Misallignment - Platform level |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-10-02 | 2019-09-19 12:08 | -13 | 2019-06-24 15:51 | Architectural - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Interfacing problems | Completed |  | The speaker interfacing with the SS coffer panel at platform level do not all align in true line, some of the speakers deviate from the line by 50mm.
| 03SR - Stations (RfL) | Cxxx-NCR-003238 | NCR | Incorrect duct opening position in new boiler flue unit |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-07-09 | 2019-10-01 13:19 | 84 | 2019-06-25 14:18 | Civil - Civil Engineering General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Since excavation work for the boiler flue has been completed, it has been found that the location of one of the duct inlets in the new unit (Unit 1) does not match the duct location which is being connected to. Please refer to the attached items which provide further explanation: Plan and elevation drawings Cxxx-SKC-S-DDA-M171_Z-90020 and Cxxx-SKC-S-DDA-M171_Z-90022 Mark up of plan GA IMG_8141 - photograph of existing ducts with boiler flue opening locations spray marked
| 03SR - Stations (RfL) | Cxxx-NCR-003239 | NCR | Welding without approved welding procedure - heritage railing coping shims |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-07-09 | 2019-09-11 13:08 | 64 | 2019-06-25 15:40 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | __ have been welding shims without an approved welding procedure. The shims were required to lift the cast iron coping by approximately 20mm to prevent a clash with post socket.
| 03SR - Stations (RfL) | Cxxx-NCR-003240 | NCR | Gap between heritage railing and glazing screen - Eastbourne Terrace GL91 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-11-29 | 2020-10-15 13:39 | 321 | 2019-06-26 06:54 | Architectural - General | 30000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | It has been found that there is a gap between the last heritage railing post and the adjacent glazing screen of approximately 600mm. This is an unacceptable distance both from a safety and aesthetical perspective. It does not comply with drawing Cxxx-SKC-A-DDD-M171_Z-04047.
| 03SR - Stations (RfL) | Cxxx-NCR-003241 | NCR | Incorrect installation of door and frame within BLL (adjacent to bottom of staircase) |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-09-13 | 2021-03-09 07:17 | 543 | 2019-06-28 15:28 | Architectural - Doors | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The attached photo "IMG-4051" shows a gap between a GFRC column and a wall (adjacent to a door and frame located within Bakerloo Line Link - bottom of staircase). It appears that the door and frame have been incorrectly installed, and would need to be moved toward the GFRC column to 'remove' the gap. Please can provide details of how they intend to rectify this issue? Any similar issues should be highlighted to CRL.
| 03SR - Stations (RfL) | Cxxx-NCR-003242 | NCR | __ Doors - Damper Connection |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-07-29 | 2020-01-22 09:01 | 177 | 2019-06-29 10:05 | Architectural - Doors | 3000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The __ doors do not allow the pressure relief dampers to be installed on them as per design requirements.
| 03SR - Stations (RfL) | Cxxx-NCR-003243 | NCR | Damage to stone cladding panels |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-08-08 | 2020-03-27 09:50 | 232 | 2019-06-29 10:48 | Architectural - Urban Realm | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | A number of natural stone cladding panels have been damaged on Departures Road (between grid lines 102 and 112). In total 4 No full size panels and 4 No skirting pieces have been cracked. Please find attached photos
| 03SR - Stations (RfL) | Cxxx-NCR-003244 | NCR | Door fire certification - Lack of certifire tag |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-08-30 | 2019-12-23 10:16 | 115 | 2019-07-10 12:05 | Architectural - Doors | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | After a site inpsection with the fire engineer in the Bakerloo box it was identified that the doors listed below did not have installed their respective certifire tag indicating thier fire resistance of the door. It was highlighted by the fire engineer that for fire rated doors to be accepted from the fire protection perspecitve they should have a mark indicating fire resistance time, therefore, any door installed without the tag could not be accepted until this issue is addressed. SR LV III A BL017 door BLKD-3 LER V BL029 door BLKD-15 SAR II BL012 door BLKD-12 SAR I BL011 door BLKD-11 CWP I BL013 door BLKD-10 ECR IX BL015 door BLKD-6 MNS VI BL018 door BLKD-4 SR LV III A BL017 door BLKD-3 SR LV III B BL016 door BLKD-5 This situation may happen in doors on different levels, therefore, it should be considered a station wide situation.
| 03SR - Stations (RfL) | Cxxx-NCR-003245 | NCR | Mist supression |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-07-31 | 2019-10-08 12:59 | 69 | 2019-07-02 10:51 | Fire - Suppression | 2500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | snag items to be rectified as identified in the attached snag sheet
| 03SR - Stations (RfL) | Cxxx-NCR-003246 | NCR | Faulty circuits (Dead Shorts) DB4/AS/W 110V 1L1/4L1 & 7L1 DB4/AS/W 110V 1L2 IRN 021/PCC021 |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-10-29 | 2019-11-01 15:21 | 3 | 2019-07-02 12:08 | Electrical - General | 1500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | when DB4/AS/W was energised, faults were discovered on the 110v distribution boards circuits DB4/AS/W 110V 1L1 • Dead short between phases for circuit 4L1 • 55v fault for circuit 7L1 DB4/AS/W 110V 1L2 • Dead short to Earth The team are still looking into the fault, and are planning on rectifying the issue once found. Proposed action; an IRF is require to capture the replacement of the damaged cables, and the testing of said circuits, including witness of the testing
| 03SR - Stations (RfL) | Cxxx-NCR-003247 | NCR | Door Mastic Exceeds Tolerance |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-08-20 | 2019-09-12 14:38 | 23 | 2019-07-03 12:29 | Fire - Compartmentation | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | D2-1020 in CS-R XIX Departures Road East, was installed with a 50mm gap between the door frame and the walls, this exceeds the maximum allowable gap of 25mm that __ had previously agreed with __ and the fire engineers.
| 03SR - Stations (RfL) | Cxxx-NCR-003249 | NCR | Socket clash - BLB SS panel between escalators |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-11-15 | 2019-11-28 13:42 | 13 | 2019-07-05 09:00 | Architectural - Finishes | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | It has been noted a niphan socket has been installed on the bulkhead leading to BoH from FoH between escalator 14 and 15 at Bakerloo box level, the socket is clashing with the panel as such this will not allow the panel to be installed.
| 03SR - Stations (RfL) | Cxxx-NCR-003250 | NCR | BLL Smoke Damper FD07 and Transfer Grille (IRN 432) |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-07-19 | 2020-03-16 15:11 | 241 | 2019-07-05 11:15 | Mechanical - Heating Ventilation & Air Conditioning | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Ref Drawing No. Cxxx-SKC-Y-DDA-M171_7-61602 C02. With reference to the transfer grille located above the entrance door to the area beneath the escalators. 1. Smoke damper located off the wall, has no lagging, drawing indicates in-wall installation. 2. Grille and duct spigot not co-ordinated with external wall cladding (Ref drawings note: 'Further interface co-ordination required'.
| 03SR - Stations (RfL) | Cxxx-NCR-003251 | NCR | Damaged Radio Antenna |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-07-19 | 2019-10-12 09:59 | 85 | 2019-07-05 14:10 | Communications and Control Systems - Radio | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Radio antenna flying leads are found to be damaged after 3rd party removed antennas to close coffer panels. Damaged antennas are ANT 30, 33, 60 and 63
| 03SR - Stations (RfL) | Cxxx-NCR-003252 | NCR | Lifts 8&9 counterweight to tall |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-09-07 | 2020-03-20 12:40 | 195 | 2019-07-09 08:35 | Mechanical - Lifts | 10000 |  | Manufacturing Defect | Rework | 2 (6-60k) | Complete | Material/Preservation Problems - Other | Completed |  | As identified by __ on Tuesday 02/07/19 the counterweight frames for lifts 8&9 are oversized and causing issues that stop the lifts complying to certain clauses of EN81. __ have communicated via email that they have contacted their factory who have recommended replacing the frames with the correct size frames. __ also communicated that new ropes would be required to compensate for the change to the frame size.
| 03SR - Stations (RfL) | Cxxx-NCR-003253 | NCR | Outstanding drawings for BMS |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-08-31 | 2019-09-14 09:23 | 14 | 2019-07-10 07:41 | Communications and Control Systems | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Outstanding documentation yet to be coded
| 03SR - Stations (RfL) | Cxxx-NCR-003254 | NCR | outstanding PLC documents and records |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-09-08 | 2019-09-14 09:24 | 6 | 2019-07-10 07:47 | Communications and Control Systems | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Documentation and records are not at the correct coding
| 03SR - Stations (RfL) | Cxxx-NCR-003255 | NCR | 110v electrical socket outlet in entrance gate stacking recess |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-08-31 | 2020-01-28 15:27 | 150 | 2019-07-10 08:24 | Electrical - Power Distribution | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Electrical services, particularly the 110v socket outlet, have been installed without consideration for the gate control equipment yet to be designed and installed in these recesses or the kinetic envelope of the folding gate panels during the stacking process.
| 03SR - Stations (RfL) | Cxxx-NCR-003257 | NCR | Departures Road Escape Doors (__) - Incorrect Panic Bar Operation |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-07-31 | 2020-01-13 17:09 | 166 | 2019-07-10 11:47 | Architectural - Doors | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Interfacing problems | Completed |  | The double doorsets manufactured by __ have been delivered with non-compliant ironmongery. The double doors with panic bars on each leaf internally (doors open out) currently require the left hand leaf (from inside) to be opened first before the right hand panic bar is operated to release the leaf. Should the right hand bar be pushed first, both leafs partially open then jam whilst still locked together preventing exit. This arrangement is therefore unacceptable to CRL - see response from CRL Fire attached.
| 03SR - Stations (RfL) | Cxxx-NCR-003258 | NCR | East End Public Stairs E__ to DR - Manifestation Error in Glazed Side Balustrade Panel |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-08-30 | 2019-10-06 08:34 | 37 | 2019-07-10 12:23 | Architectural - Glazing | 1000 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | 1 No glazed balustrade side panel has been manufactured and installed with its manifestation in the wrong place. See attached photo.
| 03SR - Stations (RfL) | Cxxx-NCR-003259 | NCR | East End of West VSHH - Incorrect Installation of Sub-Pavement Ductwork |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2020-02-28 | 2020-03-04 16:05 | 5 | 2019-08-27 12:06 | Civil - Utilities Engineering | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | 4 No corrugated plastic ducts linking an adjacent manhole with entry holes at low level into the VSHH have been haunched together prior to paving with insufficient spacing between to afford adequate support via the bedding for the paving. See attached photo.
| 03SR - Stations (RfL) | Cxxx-NCR-003260 | NCR | Missing pipe sleeves on 50mm dia. Cat1 water pipe- Departure Road West IRN-444 |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-09-25 | 2019-10-09 14:50 | 14 | 2019-07-11 11:35 | Mechanical - Public Health Engineering | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Missing pipe sleeves on 50mm dia. Cat1 water pipe- Departure Road West IRN-444. Locations: *HFT-I *LB-S X *LB-S XI *DRS Missing pipe sleeve on 15mm dia. maintenance taped pipe also observed on Platform level West - Tea Room to WC See attached photos.
| 03SR - Stations (RfL) | Cxxx-NCR-003261 | NCR | Automatic shut off valves not fiited on water services - IRN 444 and 445 |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-09-25 | 2019-09-07 11:16 | -18 | 2019-07-11 12:16 | Mechanical - Public Health Engineering | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Ref. Water services Block Schematic - drawing Cxxx-SKC-P-DDE-M171_Z-50510 C03. In multiple location, listed below, 'SV' shut off valves are shown on the water services schematic but have not been installed on site. "Note 4. Automatic shut off valve (controlled by presence detectors) to be provided to all hot and cold water supplies to each toilet area." There is no design coordination with DALI lighting and BMS. Locations indicated on water services schematic: Intermediate Level: *SMK *Staff WCs * Disabled WC and shower *Concourse Level- cleaners room * Platform West Tea room * Platform West WC * Platform East cleaners room
| 03SR - Stations (RfL) | Cxxx-NCR-003262 | NCR | Missing Whip Antennas |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-07-26 | 2019-08-06 14:51 | 11 | 2019-07-12 08:21 | Communications and Control Systems - Public Address Systems | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Insufficient quantity of material to do the job | Completed |  | Ten whip antennas were delivered by __ to Paddington T1, but two gone missing. Hence, replacement is required. Antenna delivery record is attached
| 03SR - Stations (RfL) | Cxxx-NCR-003263 | NCR | Damaged Camera |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-10-18 | 2019-10-12 09:57 | -6 | 2019-07-12 08:52 | Communications and Control Systems - CCTV | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | The camera lenses bracket was damaged
| 03SR - Stations (RfL) | Cxxx-NCR-003264 | NCR | Damage to VSHH waterproofing (during excavation for boiler flue) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-07-29 | 2019-08-08 15:33 | 10 | 2019-07-15 07:14 | Civil - Civil Engineering General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | It was found that the Eliminator waterproofing to the side of the VSHH underground structure was damaged during excavation for the boiler flue/water mains. See photo
| 03SR - Stations (RfL) | Cxxx-NCR-003265 | NCR | Material Proposal Schedule (MPS) does not reflect accepted materials in use on site |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-08-30 | 2019-12-09 10:58 | 101 | 2019-07-15 13:16 | Architectural - Balustrade | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | During a planned CRL quality surveillance; The Contractor submitted ‘Cxxx Material Proposal Schedule (MPS) Cxxx-SKC-O-TSC-B071_WS077-50369 (Rev 8) dated 02/07/18. On checking it was identified that the above MPS submitted had been accepted at Code 1 and is current on eB. On reviewing the MPS it was found that the Balustrade, Heritage Railing and Natural Stone Cladding system materials are not referenced.
| 03SR - Stations (RfL) | Cxxx-NCR-003266 | NCR | Installation has commenced without accepted F2 design and structural/blast calculations |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-12-19 | 2020-07-27 08:50 | 221 | 2019-07-15 13:24 | Architectural - Balustrade | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | During a Planned CRL quality surveillance; it was found that The Contractor commenced installation of the Balustrade in Departures Road and Eastbourne Terrace without accepted F2 design and structural/blast calculations in place
| 03SR - Stations (RfL) | Cxxx-NCR-003267 | NCR | It cannot be verified that the __ fixings have been torqued to the correct value |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2020-04-30 | 2020-03-14 13:22 | -47 | 2019-07-15 13:51 | Architectural - Balustrade | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During a planned CRL quality surveillance; the Contractor submitted ITP ‘Balustrade Installation’ Cxxx-SKC-Z-ITP-B071_WS077-50008 (Rev 2), MCR ‘Non-Standard Balustrade Anchorage’ Cxxx-SKC-O-TSC-B071_WS077-*50658 (Rev 1) and balustrade installation checksheets. On review it was noted that neither ITP or check sheets reviewed, reference the torqueing of fixings. On checking the manufacturers technical information for the __ fixings it states that the M24 used in the installation are to be torqued to 200Nm. The Contractor was unable to provide documented evidence for torqueing of balustrade bolted connections. As such it cannot be verified that bolted connections where required have been torqued. The ITP will require revising to include all bolted connections that require torque values. The check sheets will also require revising to include the check item.
| 03SR - Stations (RfL) | Cxxx-NCR-003268 | NCR | Installation of Matwell at concourse level with no ITP in place |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-08-06 | 2019-10-01 13:28 | 56 | 2019-07-16 10:44 | Architectural - Flooring | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Matwell at concourse level has been installed without an ITP in place. The works were carried out by __ (specialist contractor), however, the installation was captured in the attached checksheet and supervised by representative as indicated in the checksheet.
| 03SR - Stations (RfL) | Cxxx-NCR-003269 | NCR | BLL Box - Incorrect Colour for PAVA Speakers |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-10-31 | 2020-01-31 10:49 | 92 | 2019-07-17 14:58 | Communications and Control Systems - Public Address Systems | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Circular surface mounted PAVA speakers have been delivered and installed in standard white finish which does not follow the general scheme agreed for the station, namely that fittings sitting within bronze or anodized blue/black should be finished in RAL 9011 Black with 30% gloss.
| 03SR - Stations (RfL) | Cxxx-NCR-003270 | NCR | BLL Box - Incorrect Colour for Light Fittings |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-11-30 | 2019-12-12 17:10 | 12 | 2019-07-17 15:08 | Electrical - Lighting | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Light fittings mounted in ceiling panels in the BLL stub are finished in standard white which does not follow the general scheme agreed for the station, namely that fittings sitting within bronze or anodized blue/black should be finished in RAL 9011 Black with 30% gloss.
| 03SR - Stations (RfL) | Cxxx-NCR-003271 | NCR | Concourse Totems - Incorrect Colours for Cxxx PAVA and CCTV Equipment and Associated Conduits mounted within Headboxes |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-07-31 | 2020-01-31 10:34 | 184 | 2019-07-17 15:27 | Communications and Control Systems - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Cxxx equipment, notably the column PAVA speakers and associated flexible conduits but also other equipment and conduits such as CCTV dome cameras have been delivered and installed in silver. The agreed finish for all equipment sitting with the headboxes is RAL 9011 Black with 30% gloss finish (Agreement and Schedule issued by __ to __ circa 23/10/2014). The headboxes are clad in vertical slats and fine mesh which renders anything inside visible.
| 03SR - Stations (RfL) | Cxxx-NCR-003272 | NCR | No accepted glass impact testing provided as required in Architectural Specification JL32.2202 |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2021-10-26 | 2021-10-28 08:38 | 2 | 2019-07-18 11:00 | Architectural - Balustrade | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | During a planned CRL Quality surveillance the Contractor was unable to provide accepted Glass Impact Testing as specified.
| 03SR - Stations (RfL) | Cxxx-NCR-003273 | NCR | Bronze wedges - ESCALATOR |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-10-28 | 2020-11-23 08:44 | 392 | 2019-07-20 12:45 | Architectural - Finishes | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Bronze wedges currently installed do not follow the design intent. There are various discrepancies with the dims in relation to adjacent cladding finishes and the finished floor level.
| 03SR - Stations (RfL) | Cxxx-NCR-003274 | NCR | Damage BLL Soffit |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-11-29 | 2020-02-06 13:29 | 69 | 2019-07-21 13:07 | Architectural - Ceilings & Soffits | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Anodized ceiling panel within the Bekerloo Link has been damaged.
| 03SR - Stations (RfL) | Cxxx-NCR-003275 | NCR | No manufacturing records provided for glass and stainless-steel balustrade components. |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2020-07-30 | 2020-05-07 13:26 | -84 | 2019-07-22 11:58 | Architectural - Balustrade | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | during a planned quality surveillance a request was made to the Contractor to supply balustrade manufacturing records for stainless steel components from __ and Glazing from __ in line with the respective ITPs. However, after multiple requests no records had been produced to provide progressive assurance. As such it cannot be verified welding had been carried in line with the accepted 'Weld Pack' Cxxx-SKC-Z-RGN-B071_WS077-50166 (Rev 2).
| 03SR - Stations (RfL) | Cxxx-NCR-003276 | NCR | BLL Staircase - Security and Safety Issues |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-09-10 | 2021-09-14 10:17 | 735 | 2019-08-27 12:20 | Architectural - Balustrade | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The design and installation of the balustrading presents a number of safety and security non-compliances - see communication __/__ 15/05/19 and attachments,
| 03SR - Stations (RfL) | Cxxx-NCR-003278 | NCR | Platform Doors to TVP 1 & TVP 2 - incorrect specification |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-09-10 | 2022-01-14 12:22 | 857 | 2019-08-27 11:54 | Architectural - Doors | 15000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Door Nos D5-576 and D5-577 have been observed to physically deform (particularly the active leaf with a single locking point to the slave leaf) when the Tunnel Vent Fans are active. It is evident from review of the Door Schedules (both Cxxx Stage E and Cxxx Stage F) that resistance to enhanced air pressure was not considered in their specification. As such they are unfit for purpose and pose a risk of injury and material damage should the doorsets or their associated components catastrophically fail.
| 03SR - Stations (RfL) | Cxxx-NCR-003279 | NCR | Earth Bar for 300mm ring is inaccessible within East side service riser |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-08-31 | 2019-10-08 12:01 | 38 | 2019-07-24 12:55 | Electrical - Earthing & Bonding | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Attached pictures is the main earth bar in the combined service riser East side of intermediate level which is part of the 300mm ring is inaccessible ,it is approx. 160mm behind the ducting this will have to be move to a more accessible area
| 03SR - Stations (RfL) | Cxxx-NCR-003280 | NCR | MLFD installed in incorrect location |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-01-31 | 2020-02-11 15:33 | 11 | 2019-07-26 07:56 | Civil - Civil Engineering General | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | During set-out of the ATG SP1000 bollard foundation at gridline 46; a clash was noted between the MLFD and the reinforced concrete foundation. This clash was due to incorrect set-out position of the MLFD channel as picked up on the as-built survey and overlay on the design model.
| 03SR - Stations (RfL) | Cxxx-NCR-003282 | NCR | Pressure Relief damper (PRF03/PRF/E) installed incorrectly - Departure Road East GL18 - IRN-214, PCC-195 |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-11-01 | 2019-10-22 10:43 | -10 | 2019-07-26 10:21 | Mechanical - Mechanical Engineering General | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Pressure Relief damper (PRF03/PRF/E) at Departure Road East GL18 has been installed incorrectly; the blades will not open against discharging airflow. Refer to manufacturer's datasheet (Waterloo air volume damper MCR-6480). See attached photos
| 03SR - Stations (RfL) | Cxxx-NCR-003283 | NCR | Access to Smoke Damper FD05/EF01/E in Cleaning Room Platform Level (IRN-399) |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-10-31 | 2019-10-26 08:51 | -5 | 2019-07-26 13:49 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | During RfL CIAC2 inspection, it was observed that smoke damper ' FD05/EF01/E', located in Cleaning Room Platform Level is not accessible due to MEP services and equipment that are installed below. (See attached photo.) Reference: Cxxx-SKC-Y-DDA-M171_5-61561 C04 Contractor to demonstrate accessibility to damper's actuator and electrical junction box.
| 03SR - Stations (RfL) | Cxxx-NCR-003284 | NCR | Access to Smoke Damper FD32/AHU01Ein Cleaning Room Platform Level (IRN-393) |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-10-31 | 2019-10-26 08:55 | -5 | 2019-07-26 13:56 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | During RfL CIAC2 inspection, it was observed that smoke damper ' FD32/AHU01E', located in Cleaning Room Platform Level is not accessible due to MEP services and equipment that are installed below. (See attached photo.) Reference: Cxxx-SKC-Y-DDA-M171_5-61561 C04 Contractor to demonstrate accessibility to damper's actuator and electrical junction box.
| 03SR - Stations (RfL) | Cxxx-NCR-003285 | NCR | Chilled water pipework - leaks in thermal lagging vapour seal (IRNs 225, 226, 227, 365, 366, 367, 368) |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-12-31 | 2020-06-22 10:32 | 174 | 2019-07-26 15:36 | Mechanical - Piping | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Condensation and leaking water through the pipework thermal lagging has been observed in multiple locations on the chilled water system. This is the causing to equipment in the vicinity and potential slip hazard. In addition, lagging remains incomplete in multiple locations and around builders work holes. Examples: 1. BLL outside ECR - condensation dripping on pump and valve handles rusting (see photos 1 and 2). 2. Chilled Water Plant Room - Condensation from CW pipes dripping on electrical cabinet (see photo 3) and pooling on floor (photo 4). 3. DRS departure road west - Condensation from CW pipes dripping on light fixture. Contractor to investigate and resolve source of leaks due to condensation on lagged pipes. Contractor to put forward proposal for any corroded / damaged equipment.
| 03SR - Stations (RfL) | Cxxx-NCR-003286 | NCR | EXT-321 Bollards - Damage to Galvanising |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-08-10 | 2020-03-10 10:34 | 213 | 2019-07-27 11:49 | Civil - Civil Engineering General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During transportation, the EXT-321 bollards have sustained damage to the galvanising in small patches on the base and bollard core.
| 03SR - Stations (RfL) | Cxxx-NCR-003287 | NCR | Damage - Gate Hanger (East) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-11-04 | 2020-10-21 13:48 | 352 | 2019-07-27 14:36 | Architectural - General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | A roller hanger for east entrance gate has been damaged.
| 03SR - Stations (RfL) | Cxxx-NCR-003288 | NCR | Contractor has no accepted welding documentation for Heritage Railing restoration |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-12-12 | 2020-01-31 16:27 | 50 | 2019-07-29 08:49 | Architectural - Balustrade | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During a CRL Quality Surveillance, the Contractor was asked to provide Welding Documentation; Weld Procedure Specification (WPS), Welding Procedure Qualification Record (WPQR) Non- Destructive Weld testing (N__) records, Weld Inspection Check sheets showing traceability to welder, for repairs carried to railings and the manufacturer of new section of railings.
| 03SR - Stations (RfL) | Cxxx-NCR-003289 | NCR | Contractor couldn’t provide accepted welding documentation and manufacturing records |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-08-26 | 2019-12-23 10:55 | 119 | 2019-07-29 08:59 | Architectural - Balustrade | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During a CRL Quality Surveillance the Contractor was unable to provide accepted Welding Documentation; Weld Procedure Specification (WPS), Welding Procedure Qualification Record (WPQR), Responsible Welding Coordinator (RWC) Certificate, Non Destructive Weld testing (N__) records, Weld Inspection Check sheets showing traceability to welder and evidence of compliance to BS EN 1090-1:2009+A1:2011 including Declaration of Performance (DOP) and Factory Production Control (FPC) for stainless steel railing support steelwork and balustrade fabrication, in line with ITP *50264. A request was made for the Contractor to supply the records post Surveillance. However, after multiple requests no records had been produced to provide progressive assurance.
| 03SR - Stations (RfL) | Cxxx-NCR-003290 | NCR | Grout testing has not been undertaken and installation and testing not referenced in ITP. |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-01-18 | 2020-02-06 10:06 | 384 | 2019-07-29 09:24 | Architectural - Balustrade | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During A CRL Quality Surveillance It was witnessed that grout had been installed in the sockets that encapsulates the heritage railings. On request the Contractor was unable to provide evidence of grout cube testing, the testing will verify that the grout has reached the specified compressive strength as stated in the design. On reviewing the ITP Cxxx-SKC-Z-ITP-B071_WS077-50265 it was found that there was no reference to the installation of grout
| 03SR - Stations (RfL) | Cxxx-NCR-003291 | NCR | Platform Level Damage to Smoke Screen Glass |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-12-03 | 2019-11-21 14:50 | -12 | 2019-08-05 16:04 | Architectural - Glazing | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | It has been identified that a Smoke Screen glazing panel on Platform level above the Bakerloo Box has been damaged. The damaged panel will need to be replaced.
| 03SR - Stations (RfL) | Cxxx-NCR-003293 | NCR | Fire Door Ironmongery has been installed without an accepted MCR |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-10-11 | 2020-03-10 09:11 | 151 | 2019-08-09 09:35 | Architectural - Doors | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Whilst carrying out a planned surveillance on Fire Door Installation it was found that the Contractor has commenced with the installation of door ironmongery without an accepted Material Compliance Record (MCR) in place. Door installation commenced in 2017.
| 03SR - Stations (RfL) | Cxxx-NCR-003294 | NCR | Contractor has commenced the installation of Fire Doors without accepted drawings |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-10-31 | 2020-01-28 16:47 | 89 | 2019-08-09 09:48 | Architectural - Doors | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Whilst carrying out a planned surveillance on Fire Door Installation it was found that the Contractor has commenced the installation of Fire Door sets without accepted drawings. The installation commenced in 2017.
| 03SR - Stations (RfL) | Cxxx-NCR-003295 | NCR | Chilled Water System - faulty PIC valves |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-11-01 | 2020-08-25 10:51 | 298 | 2019-08-12 12:26 | Mechanical - Heating Ventilation & Air Conditioning | 5000 |  | Damaged | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Re: Faulty PIC valves, chilled water system (PAC-036). An unspecified number of PIC Valves within the Critical Cooling Units (CCUs) on the chilled water system, have been reported as faulty. The Contractor is requested to provide details of the faults and the number of valves affected. The Contractor is also requested to confirm their proposals for corrective action.
| 03SR - Stations (RfL) | Cxxx-NCR-003296 | NCR | Chilled water plant room drainage gullies (IRNs 230, 444, 232) |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-09-30 | 2019-10-12 10:38 | 12 | 2019-08-12 12:41 | Mechanical - Public Health Engineering | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | 1. Lack of design details for 2 number new gullies within chilled water plant room 2. Pipe sleeves have been install on the new drainage pipework. Contractor needs to agree civil floor / cast in detail with CRL (__) 3. One of the gullies is proud of the floor. Contractor to provide details, as per item #1, above. 4. Contractor to confirm detail for trapped gully, as per item #1, above.
| 03SR - Stations (RfL) | Cxxx-NCR-003298 | NCR | __ Doors - unco-ordinated design leading to adaptations on site |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2020-02-20 | 2020-01-22 09:06 | -29 | 2019-08-13 11:34 | Architectural - Doors | 5000 |  | Supervision/Management | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The __ doors forming the pressure relief area of the means of escape stairway have not been adequately co-ordinated with the MEP requirements for the mounting of dampers and light fittings. Consequently the doors and or surrounds require modification. This was known about and adequately covered in GIR Cxxx-SKC-Z-RGN-B071_WS077-50332, however the suppliers drawings and procurement of the doors did not comply.
| 03SR - Stations (RfL) | Cxxx-NCR-003299 | NCR | VSHH - Top Level Removable Access Grillage - Fabrication - N__ testing |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-10-31 | 2019-09-11 13:20 | -50 | 2019-08-14 11:32 | Structural Engineering - Testing | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The fabrication of the removable access grillage and supporting steelwork for the east and west VSHHs was undertaken to ITP Number - Cxxx-SKC-Z-ITP-B071_WS077-50254. However, the deliverable for ITP inspection number 3.5 'Non Destructive Testing by N__ qualified personnel' is an 'N__ report' by '3rd Party accredited inspector'. This deliverable is not available.
| 03SR - Stations (RfL) | Cxxx-NCR-003300 | NCR | No MCR for __ channel in boiler flue chimney |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-10-15 | 2019-10-11 10:38 | -4 | 2019-08-14 13:57 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | It has been found that the __ channel used in the boiler flue chimney does not have an approved MCR.
| 03SR - Stations (RfL) | Cxxx-NCR-003301 | NCR | Chiiler 2 flow rate |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2020-02-20 | 2020-02-15 10:48 | -5 | 2019-08-15 08:28 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Chiller 2 flow rate (PCCs 273, 287, 203, 271 and 272) Commissioning Test records The pump flow rate for Chiller 2 shows 122% and is over capacity in the various combinations. This pump should have its speed reduced to be within the 110% limit. Contractor to demonstrate at PAC.
| 03SR - Stations (RfL) | Cxxx-NCR-003302 | NCR | Condensation Pumps – scope gap |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2020-02-20 | 2020-11-17 11:47 | 271 | 2019-08-15 08:33 | Mechanical - Heating Ventilation & Air Conditioning | 1000 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | Contractor to check that all condensate pumps are covered by an IRN and confirm the relevant IRN numbers. Contractor to provide commissioning sheets for all condensation pumps, at PCC.
| 03SR - Stations (RfL) | Cxxx-NCR-003304 | NCR | SOR Fire Alarm Panel - DDA |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-09-14 | 2019-10-11 08:49 | 27 | 2019-08-15 10:00 | Fire - Fire Systems & General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The Fire Alarm Panel (FAP) has been installed in the SOR 3-751 at a height on the wall which is outwith the reach of mobility impaired IM staff. This contradicts requirement of CPFR .
| 03SR - Stations (RfL) | Cxxx-NCR-003305 | NCR | Staff areas ceiling tiles- cut edges |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-09-14 | 2019-12-05 13:27 | 82 | 2019-08-15 10:13 | Architectural - Ceilings & Soffits | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Ceiling tiles are being installed in BOH staff rooms and SOR. At the perimeter, tiles have been cut which result in a sharp edge and an obvious visual sag. Speciifaction JK40.1214 h) iv) requires all cut tiles and services holes to be cut in the factory.
| 03SR - Stations (RfL) | Cxxx-NCR-003306 | NCR | BOH staff room celings - perforated tiles |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-10-04 | 2019-12-05 13:33 | 62 | 2019-08-15 10:24 | Architectural - Ceilings & Soffits | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Ceiling tiles are being installed in the BOH staff shower and toilet areas with perforated tiles, . Perforated tiles in these high humidity areas are likely to be subject to mould growth and are not appropriate.
| 03SR - Stations (RfL) | Cxxx-NCR-003307 | NCR | BLL Ceiling PAVA speaker colour mismatch |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-12-14 | 2020-01-28 15:56 | 45 | 2019-08-15 10:44 | Architectural - Ceilings & Soffits | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Cxxx speakers have been installed within the high level ceiling panels, the low level BLL adit ceiling and the BLL stair soffit. To date the ceiling is installed at high and low level and specified as a dark blue grey. The speaker colour is white which does not match with the design intent. ie to be as visually discrete as possible. White speakers inset against a dark background is not visually acceptable. Across all CRL stations colours of Cxxx PAVA speakers were limited to white , black or grey. In this instance the acceptable colour would be black.
| 03SR - Stations (RfL) | Cxxx-NCR-003308 | NCR | BLL ceilings- light fitting colour |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-11-30 | 2019-12-12 17:13 | 12 | 2019-08-15 10:56 | Architectural - Ceilings & Soffits | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Light fittings with white bezels have been installed at BLL low level adit ceiling and BLL stair soffit. The ceilings are specified and to date partially installed with a dark blue grey finish. The white bezel light fittings do not match the design intent ie be visually discrete. Adjacent to this mismatch, light fittings installed at BLL high level are black within dark blue grey ceiling panels and meet the design intent.
| 03SR - Stations (RfL) | Cxxx-NCR-003309 | NCR | Lift control panels Sharp edges |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-12-18 | 2019-12-05 13:29 | -13 | 2019-08-15 13:32 | Mechanical - Lifts | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | Adjacent to each BOH lift architrave a control box has been fitted. The box projects into the lift lobbies. They have sharp corners and thin metal edges all round which are hazardous.
| 03SR - Stations (RfL) | Cxxx-NCR-003310 | NCR | BLL level escalator newel- cladding interface |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-09-14 | 2021-03-09 07:23 | 542 | 2019-08-15 14:24 | Architectural - Walls | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | At BLL level gaps remain at the lower junction between the escalator newels and adjacent wall cladding. S steel cladding has been installed to the upper side but does not extend down wards to meet the terrazzo skirting and s steel trim. Refer attached image015.
| 03SR - Stations (RfL) | Cxxx-NCR-003312 | NCR | Fire Stopping details not referenced on accepted Fire Door Installation ITP |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2020-04-17 | 2020-04-02 10:14 | -15 | 2019-08-19 11:13 | Fire - Compartmentation | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During a planned CRL quality surveillance on manufacturing and installation of fire doors, on checking ITP SKC-Z-ITP-B071_WS077-50118 that is referenced on the Fire Stopping check sheet, it was found that Fire Stopping had not been referenced. The Contractor stated that SKC-Z-ITP-B071_WS077-50118 had been revised to include all relevant Control Documentation Acceptance Criteria, Verifying Documentation and Inspection Details in regard Fire Stopping, but due to an oversight the ITP had not been issued for acceptance.
| 03SR - Stations (RfL) | Cxxx-NCR-003313 | NCR | Electrical test results & IRFs for links between isolators/Spurs/Sockets and field equipment/Lighting |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-10-31 | 2020-05-01 12:56 | 183 | 2019-08-19 12:36 | Electrical - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | At present there is no assurance documentation to show test results for the electrical link between isolators/Spurs/Sockets and field equipment/Lighting. The different systems are close to partial acceptance, and have had IRN's/PCC's but there have yet to show any documents for the electrical link. This NCR should cover all systems with an Electrical supply.... Fire, Mechanical, BMS, Electrical... PACs close to submission but still no sign of IRFs to cover the electrical links; Fire PAC 21 & 15, Electrical PAC 2 & 4
| 03SR - Stations (RfL) | Cxxx-NCR-003314 | NCR | Damaged PAVA speakers |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-10-18 | 2019-10-12 09:56 | -6 | 2019-09-03 12:30 | Communications and Control Systems - Public Address Systems | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Two speakers at site found to be damaged and one missing, the speakers need replacement - __F I (Z12/ B38) – RCS 5 (missing) - SMK (Z11/A15) - RCS 5 (damaged) - PSE (Z12/ A65) - Horn Speaker (damaged) Pictures and delivery sheet are provided as evidence.
| 03SR - Stations (RfL) | Cxxx-NCR-003316 | NCR | Incorrect sleave oncoming services sleeve detail |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-12-17 | 2020-03-26 09:23 | 100 | 2019-09-03 12:48 | Civil - Sewage/Water services | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | incoming water main sleeve not installed as per design
| 03SR - Stations (RfL) | Cxxx-NCR-003318 | NCR | Tiling works undertaken by __ without approved ITP |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-09-19 | 2019-11-01 09:53 | 43 | 2019-09-05 13:09 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Wall and floor tiling at concourse and intermediate level have been installed without an ITP in place. The works were carried out by __ (specialist contractor), however, the installation was captured in the attached checksheet and supervised by representative as indicated in the checksheet.
| 03SR - Stations (RfL) | Cxxx-NCR-003319 | NCR | Installation of Stair nosings in BoH and FoH with no ITP in place |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-09-19 | 2019-10-11 10:27 | 22 | 2019-09-05 13:16 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Gooding stair nosings in BoH, ATTI nosings in FoH and corduroy tactiles have been installed without an ITP in place. The works were carried out by __ (specialist contractor), however, the installation was captured in the attached checksheets and supervised by representative as indicated in the checksheet.
| 03SR - Stations (RfL) | Cxxx-NCR-003320 | NCR | Heritage railing support steelwork fabrication - no approved weld procedure in place |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-09-20 | 2019-11-21 14:46 | 62 | 2019-09-06 09:41 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | It was noted that the heritage railing support steelwork fabrication is not accounted for in __'s approved weld pack MCR - Cxxx-SKC-O-TSC-B071_WS077-50718 Rev 1 The above mentioned MCR covers back of house steelwork fabrication (which does involve the same welding procedures as used for heritage railing steelwork). All welds have followed this weld pack and welding has been tested.
| 03SR - Stations (RfL) | Cxxx-NCR-003321 | NCR | Louvre Grilles between Escalators -BLB |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-11-15 | 2019-11-28 13:45 | 13 | 2019-09-10 13:05 | Architectural - Finishes | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The louvre grille over the door to back of house between escalators 14 and 15 (BLKD-13 )is not being constructed in accordance with the agreed CRL responses to RFI Cxxx-RFI-002799. The architectural requirement, bearing in mind that the door and louvre above are in a visible public facing elevation, is for a full width stainless steel louvre featuring horizontal blades. The current installation is based on a square grille set in the stainless steel sheet cladding above the door which is unacceptable. As a separate note, also included was a CRL response requiring triangular louvre grilles in the flank walls either side of the door. These have been supplied and installed as rectangular shapes. In this instance, they are acceptable as installed as their visibility from the public area is limited.
| 03SR - Stations (RfL) | Cxxx-NCR-003322 | NCR | Mechanical falure and damage to CCU in ESR 1 CWU |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-10-17 | 2019-12-06 15:42 | 50 | 2019-09-10 15:01 | Mechanical - Heating Ventilation & Air Conditioning | 2500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Mechanical failure and damage to ESR1 CCU Also see attached report from __ AP
| 03SR - Stations (RfL) | Cxxx-NCR-003323 | NCR | Surface Mounted Conduits and Boxout Clashes in Staff Rooms (Intermediate and Concourse Levels) |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-10-08 | 2019-11-28 13:37 | 51 | 2019-09-10 16:25 | Architectural - Walls | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | This NCR has been raised to consolidate the following 6 no. NCRs regarding the failure to install concealed conduits/services within staff rooms on Intermediate and Concourse Levels. This NCR also addresses issues with the boxouts that have since been installed to conceal these conduits without making adequate provision for the access/maintenance of the services, equipment, outlets and valves contained within or adjacent to these boxouts. Related NCRs that have been superseded by this NCR: • Cxxx-NCR-003108 • Cxxx-NCR-003118 • Cxxx-NCR-003145 • Cxxx-NCR-003156 • Cxxx-NCR-003163 • Cxxx-NCR-003197 Affected Rooms on Intermediate and Concourse Levels. Note that this is not an exhaustive list as other areas may be affected: • GSM = Group Station Manager’s Office • __F I = Interview Room (Concourse Level) • __F II = Interview Room (Intermediate Level) • SMK = Staff Kitchen The Contractor is to proceed with the proposed details agreed with the Contractor's Designer and CRL. These details include (but are not limited to) the following key points: • Any boxouts are to allow for access and maintenance of the conduits/services, equipment, outlets, valves and switches contained within or adjacent to any installed boxouts. • Hatches/doors/flaps are to be installed in boxouts to allow access and maintenance of items contained within, and without affecting any adjacent equipment. • Boxouts are to be flush with any heater units.
| 03SR - Stations (RfL) | Cxxx-NCR-003324 | NCR | Inaccessable damper control unit TEP platform level |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-10-05 | 2019-10-06 08:41 | 1 | 2019-09-21 12:57 | Fire - Compartmentation | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Pipe insulation is blocking interface unit from opening
| 03SR - Stations (RfL) | Cxxx-NCR-003325 | NCR | Incorrect structural height of door opening - West service riser |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-10-17 | 2020-03-10 10:37 | 145 | 2019-09-17 09:06 | Fire - Compartmentation | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The gap between the doors (D5-416,D5-417,&D5-689) and the Lintel is too big at 55mm which will not satisfy the fireproof detail.
| 03SR - Stations (RfL) | Cxxx-NCR-003326 | NCR | Electrical Switches - Motorised Dampers |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-10-31 | 2020-02-12 11:38 | 104 | 2019-09-13 11:57 | Mechanical - Heating Ventilation & Air Conditioning | 2500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | The Contractor has installed key operated damper switches that do not comply with the Works Information in that there is no requirement for key operated switches. This has been confirmed to the Contractor as per the attached correspondence.
| 03SR - Stations (RfL) | Cxxx-NCR-003327 | NCR | Trip hazard on __ door thresholds |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-10-17 | 2020-01-13 17:18 | 88 | 2019-09-17 09:50 | Architectural - Flooring | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | The __ Door threshold has been installed ontop of the screed and creates a trip hazard at the door openings. The trip hazard is present on the 6No. __ doors that have been installed on departures road level.
| 03SR - Stations (RfL) | Cxxx-NCR-003329 | NCR | HFT 1 Flooring Installation without ITP |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-10-31 | 2020-07-27 08:59 | 270 | 2019-09-17 11:07 | Architectural - Flooring | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | HFT 1 Howe green flooring has been installed without an approved ITP.
| 03SR - Stations (RfL) | Cxxx-NCR-003330 | NCR | Damage to Cavity Barrier Firestopping |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-10-03 | 2019-10-11 10:00 | 8 | 2019-09-19 09:47 | Fire - Compartmentation | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Damage of Firestopping to the Cavity Barriers in the Bakerloo Box.
| 03SR - Stations (RfL) | Cxxx-NCR-003331 | NCR | Departure Rd glazing adjacent to escalators |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2020-01-31 | 2020-01-20 12:30 | -11 | 2019-09-20 13:51 | Architectural - Glazing | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Error by manufacturer in shipping or marking | Completed |  | 3no. glazing panels adjacent to the top of the escalators east & west at Departures Rd have been installed with an incorrect frit pattern. The opaque frit correctly installed and which obscures the side of the escalators adjacent to the glass extends to the 3 no panels beyond the end of the escalator up to the entrance gate. This opaque band interrupts the visual link between inside and outside the glazing that supports wayfinding. It reduces effective surveillance and compromises visual contrast.
| 03SR - Stations (RfL) | Cxxx-NCR-003332 | NCR | Safety railling clash with Cxxx DR actuators |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-11-15 | 2020-01-27 11:57 | 73 | 2019-09-20 14:06 | Architectural - General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | In two locations at Concourse level DR-WB I 4-798 and DR WB-II 4-798 the installed Cxxx safety railings are too close to the installed Cxxx actuators which prevents maintenance.
| 03SR - Stations (RfL) | Cxxx-NCR-003333 | NCR | CCTV coverage issue- Intermediate level- Lift Lobby area |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-12-20 | 2020-01-03 14:23 | 14 | 2019-09-26 10:25 | Communications and Control Systems - CCTV | 1500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Design - coordination issue: The attached Cxxx-SKC-A-DDA-M171-3-44603 X01 drawing does not show the lift lobby area wall and entrance, as is built on site. Please confirm under what drawing is the wall shown and confirm that the addition of the wall was issued to Cxxx to incorporate in their CCTV design. Currently the design is not co-ordinated in that there is no camera covering the lift lobby area and no lobby wall shown on the Cxxx design as per the attached drawing Cxxx-SMN-R3-DDA-M171-3-30003 Attached PDFs details the issue
| 03SR - Stations (RfL) | Cxxx-NCR-003334 | NCR | No MCR in place for Fan anti vibration mounts |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-11-14 | 2020-01-25 11:38 | 72 | 2019-09-30 13:00 | Mechanical - Mechanical Engineering General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | No MCR in place for Fan anti vibration mounts which have been installed on site (see attached photo). Fan systems include: - Pressurisation / Mean of Escape Fans - Air Release - Smoke Extract.
| 03SR - Stations (RfL) | Cxxx-NCR-003335 | NCR | NR doors incorrectly monitored by Cxxx SCADA |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-10-31 | 2019-12-20 14:57 | 50 | 2019-10-01 10:36 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | The Contractor has notified Cxxx of the doors that require monitoring and incorrectly stated that NR doors are to be monitored by Cxxx SCADA. NR doors along __ are not part of the RfL system and should not be monitored by station SCADA. The affected doors are listed below; 1. 1016U1 to D2695 2. 1016U1 to D2903 3. 1016U1 to D2661a 4. 1016U1 to D2696 5. 1016U1 to D2904 6. 1016U1 to D2697 7. 1016U1 to D2409 8. 1016U1 to D2699 9. 1016U1 to D2698a 10. 1016U1 to D2905a
| 03SR - Stations (RfL) | Cxxx-NCR-003336 | NCR | Scope gap for canopy and flush down timer controllers for solenoid valves |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-10-31 | 2019-10-26 08:57 | -5 | 2019-10-01 13:20 | Mechanical - Public Health Engineering | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Timer controllers (MCR-7545) for canopy solenoid valves (SVNC01 and SVNC05) and foul drain flushing cistern (SLVNC02) have yet to be installed and are not captured on the __ register. (Note – scope of solenoid valves installation captured in mechanical IRN-235.) IRF to be raised for CRL inspection once controllers and associated wiring is complete – this is to be linked to the applicable electrical PCC / PAC. Reference water services schematic: Cxxx-SKC-P-DDE—M171_Z-50510
| 03SR - Stations (RfL) | Cxxx-NCR-003337 | NCR | Scope gap for presence detectors for automatic shut off solenoid valves |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-10-30 | 2020-02-11 16:18 | 104 | 2019-10-01 13:24 | Mechanical - Public Health Engineering | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other management problem | Completed |  | Presence detectors (two number PIR02) for automatic shut off solenoid valves in toilet areas (SLVNC03 and SLVNC03) have yet to be installed and are not captured on the __ register. (Note – scope of solenoid valves installation is captured in mechanical IRN-235.) IRF to be raised for CRL inspection once detectors and associated wiring is complete – this is to be linked to the applicable electrical PCC / PAC. Reference water services schematic: Cxxx-SKC-P-DDE—M171_Z-50510
| 03SR - Stations (RfL) | Cxxx-NCR-003338 | NCR | IRN 204 - Missing MCR |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-04-21 | 2020-04-14 09:16 | -7 | 2019-10-04 08:30 | Fire - Suppression | 5000 |  | Documentation and Records | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | It is observed that matearials are used in the site without an approved MCR in place
| 03SR - Stations (RfL) | Cxxx-NCR-003339 | NCR | No fire stopping detail for trace heated pipework passing through a wall (IRN-240) |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-11-08 | 2020-02-14 13:15 | 98 | 2019-10-09 14:38 | Fire - Compartmentation | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | There is no fire stopping detail in place for trace heated pipework passing through a wall. This was raised during benchmark inspection of internal fire stopping (25-July 2019), see attached email. The detail, and a benchmark, is to be approved by the Contractor’s Fire Engineer. This NCR supersedes Cxxx-NCR-003260.
| 03SR - Stations (RfL) | Cxxx-NCR-003340 | NCR | No relevant N__ report for the fabrication BLL Lift 12- Glazing Brackets |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-01-31 | 2020-05-01 12:44 | 91 | 2019-10-10 09:11 | Structural Engineering - Welding | 10000 |  | Documentation and Records | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | The tier 2 contractor (__) undertaking the fabrication and installation of BLL Lift 12, has not yet supply evidence of N__ test report for glazing brackets as per the approved ITP.
| 03SR - Stations (RfL) | Cxxx-NCR-003341 | NCR | Rust to pipe sleeves |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-12-09 | 2020-04-01 11:35 | 114 | 2019-10-10 15:13 | Mechanical - Piping | 5000 |  | Material | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Some pipe sleeves within the main box have been observed to show signs of corrosion.
| 03SR - Stations (RfL) | Cxxx-NCR-003342 | NCR | Insufficient clearance to lag and weather proof the trace heated pipe - VHH West (IRN-240) |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2020-09-30 | 2020-09-14 13:20 | -16 | 2019-10-10 15:04 | Mechanical - Piping | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Insufficient clearance to lag and weather proof the trace heated pipe - VHH West (IRN-240). Reference redline drawing: Cxxx-SKC-Y-DDB-M171_A-68501 See attached photos This supersedes Cxxx-NCR-3139
| 03SR - Stations (RfL) | Cxxx-NCR-003344 | NCR | Damage to Door D3-574 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-11-14 | 2020-01-31 16:35 | 78 | 2019-10-15 16:45 | Architectural - Doors | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Keys were locked inside D3-574 and operative cut the latch to open the door into the site office.
| 03SR - Stations (RfL) | Cxxx-NCR-003350 | NCR | Room SMK - Fit-out does not comply with BS 8300 |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2020-01-24 | 2020-03-04 13:29 | 40 | 2019-10-29 11:56 | Architectural - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | With reference to Architectural Specification Cxxx-SKC-A-RSP-B071_WS077-50003, Clauses JN10.1201 c) i) and ii), also JN10.1208 - Mess Room fixed furniture, it is evident that the fixed stainless steel fit-out does not comply with the requirements of BS8300 - Design of Buildings and their approaches to meet the needs of disabled people. Code of Practice
| 03SR - Stations (RfL) | Cxxx-NCR-003352 | NCR | Waste water pump west - ref. IRF-1876 (for IRN-233 / PAC-82) |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-12-20 | 2019-12-18 08:33 | -2 | 2019-10-30 11:25 | Mechanical - Mechanical Engineering General | 1500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Comments as per email dated 22-Oct-2019: o Plastic tube is too short and is pulling on connection at unit, which is not securely fastened o Copex has been damaged o No mechanical protection in place around pump
| 03SR - Stations (RfL) | Cxxx-NCR-003353 | NCR | Live Testing and Certification in Accordance with BS7671 and CRL M&W Spec JY81 |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-12-01 | 2020-01-17 14:07 | 47 | 2019-10-30 15:33 | Electrical - General | 2000 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | It has come to CRL's attention that the Contractor will not be live testing in accordance with BS7671 and CRL M&W Spec JY81.
| 03SR - Stations (RfL) | Cxxx-NCR-003354 | NCR | SAF File Update |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-11-14 | 2020-04-27 14:02 | 165 | 2019-10-31 12:05 | Communications and Control Systems | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | To update the SAF file Cxxx-SKC-E-LRC-B071_WS077-51038 to represent the actual install.
| 03SR - Stations (RfL) | Cxxx-NCR-003355 | NCR | Bronze cladding skirting |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-11-14 | 2020-03-16 14:59 | 123 | 2019-10-31 16:20 | Architectural - General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The stainless steel skirting under the bronze cladding on platform and concourse level have not enough rigidity.
| 03SR - Stations (RfL) | Cxxx-NCR-003358 | NCR | Redundant Socket Clash with Windpost Flashing Intermediate SLR-F 316 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-02-03 | 2019-12-11 09:54 | -54 | 2019-11-05 08:15 | Architectural - Finishes | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Previous Construction - Improper As Built | Completed |  | [05.11.19] Within the SLR-F Locker room there is a redundant switch which clashes with the windpost flashing. Location of socket: A looking at door from within the room, the socket is to the right of the door, clashing with the first windpost to the right of the door. In order to remedial this issue, the socket will be removed, box infilled using monomix HD or similar, the wall re-tiled, the flashing cut edge smoothed/ made good and mastic installed between the tile and flashing as agreed in the NCR RRM on 31/10/19.
| 03SR - Stations (RfL) | Cxxx-NCR-003359 | NCR | holes for isolator switch in bronze cladding |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-11-29 | 2020-07-23 08:03 | 237 | 2019-11-06 10:14 | Architectural - Finishes | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | Above all the escape doors on platform and concourse at the bottom of the perforated panel we have cut outs for isolator switch which are redundant, visually is unacceptable and distort the panels
| 03SR - Stations (RfL) | Cxxx-NCR-003361 | NCR | entrance gate east |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-12-06 | 2020-02-03 11:27 | 59 | 2019-11-06 11:58 | Architectural - Glazing | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | interface clash with __ balustrade glazing and posts at departure road East.
| 03SR - Stations (RfL) | Cxxx-NCR-003362 | NCR | cladding interfaces-main entrance |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-12-06 | 2020-03-16 14:49 | 101 | 2019-11-06 11:52 | Architectural - Finishes | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | cladding for the main entrances not coordinated with Cxxx speakers, antenna and gate sounder and EDNE signs, resulting panels not aligned with assets
| 03SR - Stations (RfL) | Cxxx-NCR-003363 | NCR | Bakerloo adit junction with LU- top cover panel |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-12-06 | 2020-03-23 17:44 | 108 | 2019-11-06 11:01 | Architectural - Finishes | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Aluminium trim end of Adit on Bakerloo level is not extended enough resulting a gap at the top of the trim
| 03SR - Stations (RfL) | Cxxx-NCR-003365 | NCR | Door Signage Falling from Doors - Main Box |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-12-31 | 2020-03-18 15:34 | 78 | 2019-11-14 07:38 | Architectural - Signage | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | It has been found that certain door signage has been falling from doors within the main box. It seems to be mainly the warning signage and a few minor incidences of the prohibition signage. From further inspection, the signs have been delivered from the approved TfL supplier __ with a bow in the middle. This bow causes the VHB tape on the reverse to pull away from the substrate and ultimately cause the signs to 'pop' off the door. We have discussed the issue with __ who advised that it may be due to construction dust on the door. We therefore cleaned the door and trialed installing the signs. Unfortunately the issue remains. We are still in contact with __ to try and resolve, but due to signs becoming damaged and therefore requiring replacing, along with the issues that signs could fall off in the future, this NCR is being raised. Should we not be able to find a resolution to this issue with __, we may require CRL/TfL assistance to escalate.
| 03SR - Stations (RfL) | Cxxx-NCR-003366 | NCR | SMK damper to be rotated 180 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-12-23 | 2020-02-15 10:46 | 54 | 2019-11-14 16:06 | Fire - Fire Systems & General | 2500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Damper is to be turned to enable access for maintenance
| 03SR - Stations (RfL) | Cxxx-NCR-003367 | NCR | Bakerloo Box - Water Ingress |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-12-15 | 2020-03-27 09:52 | 103 | 2019-11-15 16:06 | Civil - Civil Engineering General | 5000 |  | Damaged | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Water ingress has been found in the Bakerloo Box above the slab in MNS VI
| 03SR - Stations (RfL) | Cxxx-NCR-003368 | NCR | Door frame not flush with wall |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-11-30 | 2020-02-12 15:39 | 74 | 2019-11-16 10:32 | Architectural - Doors | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Interfacing problems | Completed |  | The door frame to MAE-R I on Concourse West protrudes by approximately 10mm from the wall on the inner side.
| 03SR - Stations (RfL) | Cxxx-NCR-003371 | NCR | Platform CCTV Bracketry |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-02-20 | 2020-01-29 09:37 | -22 | 2019-11-26 11:44 | Communications and Control Systems - CCTV | 2500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Cxxx have now twice reviewed the views obtained from the CCTV cameras at platform level, and have advised that the vision associated with 8 No CCTV cameras and the 7 brackets that they are attached to, require further reductions in length, from 30mm to 80mm to the brackets to allow full vision to their requirements
| 03SR - Stations (RfL) | Cxxx-NCR-003372 | NCR | No Torqueing and Proof Loading of fixings referenced in the Bronze Cladding Installation ITP |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2020-02-17 | 2020-11-12 10:31 | 269 | 2019-11-20 10:52 | Architectural - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During a planned CRL Quality surveillance carried out on Bronze Cladding. Evidence of proof loading the anchors that connect the secondary support to the structure. A review of ITP Installation of Bronze Cladding Panels to Columns and Walls Cxxx-SKC-Z-ITP-B071_WS077-*50006 (Rev 4), found that there is no line item for Proof Loading fixings including the values to be used. The fixings used in the cladding system were confirmed as being torqued. A further review of ITP *50006 found that there is no line item for this activity including the values to be used.
| 03SR - Stations (RfL) | Cxxx-NCR-003373 | NCR | Door D2-94b not in line with fire firestrategy INS |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-01-10 | 2020-03-17 15:02 | 67 | 2019-11-21 16:27 | Architectural - Doors | 100 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Ironmongery for Door D2-94b, installed on the east side of Departures Road (GL 17-18) does not align with the INS fire strategy . The handle of the door was installed as per design drawing but the drawing (Cxxx-SKC-Y-DDL-M171_2-32287) shows the handle inside INS II. The location is wrong as the handle should be inside LVS XIV to allow the fire brigade to operate the door in case of an emergency while the INS II area should be kept closed so the crowd evacuating the area will be "encouraged" to use door D2-94a to evacuate the station.
| 03SR - Stations (RfL) | Cxxx-NCR-003374 | NCR | TTL Core Network power supply for its cabinet in CERV (DC9) rated higher than requested |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2020-02-20 | 2020-02-05 11:14 | -15 | 2019-11-22 10:28 | Electrical - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | TTL Core Network requested the power supply for its cabinet in CERV (DC9) to be a 1 x 13amp UFS in the Design Interface Control Document: Cxxx-TFL-E-GPD-B071-5001 A 32amp breaker has instead been provided, which is now required to be downgraded for the connection to be compliant.
| 03SR - Stations (RfL) | Cxxx-NCR-003376 | NCR | SRLV 3A&B - Material supply issues |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-12-20 | 2020-09-18 08:42 | 273 | 2019-11-23 14:28 | Architectural - Flooring | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The manufacturer cannot deliver/procure the materials for the raised access floor within the time constraints. This will effect the SRLV 3A&B raised access flooring. Please see attached documents that show what part of the flooring cannot be procured in time.
| 03SR - Stations (RfL) | Cxxx-NCR-003378 | NCR | No Pull Test on winching Points |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-12-11 | 2020-01-31 16:32 | 51 | 2019-11-27 09:26 | Architectural - Flooring | 5000 |  | Documentation and Records | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | There was no pull tests carried out on the installation of the resin bolts used to fix the winch where it could not be mechanically fixed. These relate to the winch points installed on intermediate level. Cert pack reference: 5.6.7
| 03SR - Stations (RfL) | Cxxx-NCR-003379 | NCR | Winching Point Not Installed |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-12-11 | 2020-03-18 13:49 | 98 | 2019-11-27 09:39 | Architectural - Flooring | 5000 |  | Incomplete Works | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Winching point not installed. Winching Point W6 shown on the attached mark up was not installed and the location has been screeded over.
| 03SR - Stations (RfL) | Cxxx-NCR-003380 | NCR | UNA I internal floor level difference |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-12-11 | 2020-07-27 08:19 | 229 | 2019-11-27 09:54 | Architectural - Flooring | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The floor level is different from front of house and the screed inside UNA 1
| 03SR - Stations (RfL) | Cxxx-NCR-003381 | NCR | Damaged Grill/louver |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-12-31 | 2020-03-20 12:44 | 80 | 2019-11-28 13:36 | Mechanical - Mechanical Engineering General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | damaged chiller louver. Location - chiller compound West
| 03SR - Stations (RfL) | Cxxx-NCR-003382 | NCR | Bakerloo GFRC Panels Support Frame Tethers Not Installed |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-12-31 | 2020-03-04 14:48 | 64 | 2019-11-28 16:00 | Architectural - Walls | 5000 |  | Workmanship | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | During a site visit from __ (CRL) it has been identified that tethers for the GFRC support frame are not installed.
| 03SR - Stations (RfL) | Cxxx-NCR-003384 | NCR | Room STR I - Communication equipment installed in a water mist suppression room |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2020-08-31 | 2020-11-15 09:36 | 76 | 2019-12-02 17:26 | Communications and Control Systems | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | Room STR-I #571 (Concourse Level) has __ controls equipment (Distribution Cabinet - DC3) and TfL cabinet. The room has an installed water mist suppression system. Electrical and Controls assets should not be located in rooms with water suppression. Ref. mist suppression drawing: Cxxx-SKC-E1-DWG-B071_WS077-50222
| 03SR - Stations (RfL) | Cxxx-NCR-003385 | NCR | No evidence provided to confirm that torqueing of anchors had been carried out. |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2020-01-12 | 2020-02-01 09:37 | 20 | 2019-12-03 09:50 | Architectural - General | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | During a Surveillance on the Installation and assurance of Bronze Cladding, the Contractor was asked to provide evidence to support the torqueing of __ HKD SR anchors that connect the cladding hanging system to the concrete structure in line with the Manufacturers Technical Data Sheet. Despite several requests, evidence of this was not provided, it was also noted that there is no reference to the torqueing of fixings on the submitted check sheets, as such it cannot be verified that the activity has taken place.
| 03SR - Stations (RfL) | Cxxx-NCR-003386 | NCR | Access hatch for trace heating controllers (IRN-506) and fire main air relief valves Breeching Inlet East |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2020-01-31 | 2020-03-14 09:04 | 43 | 2019-12-04 10:38 | Mechanical - Piping | 1500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Location: Departure Road, Breeching Inlet East (GL18) Installed access hatch does not provide adequate access to trace heating controllers. Access frame has to be removed to gain access, requiring multiple bolts to be removed. Access hatch and frame assembly too heavy to be lifted by operatives. Contractor to proposal solution.
| 03SR - Stations (RfL) | Cxxx-NCR-003387 | NCR | Cxxx Omni directional antennae BLL celing Incorrect colour |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2020-01-17 | 2020-01-30 14:59 | 13 | 2019-12-06 12:56 | Architectural - Ceilings & Soffits | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | The ceiling panels at BLL level are anodized dark blue grey. The Cxxx omni directional antennae which is mounted on this ceiling is light grey In this context the antennae should be black.
| 03SR - Stations (RfL) | Cxxx-NCR-003388 | NCR | Gaseous fire suppression detector head zones |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-01-31 | 2020-09-09 15:45 | 222 | 2019-12-06 15:02 | Fire - Suppression | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Detector head zones are not wired in uniform in one of the four transformer rooms
| 03SR - Stations (RfL) | Cxxx-NCR-003390 | NCR | Zone 4 & 5 Speaker Cladding |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2020-03-31 | 2020-04-03 13:30 | 3 | 2019-12-09 14:56 | Communications and Control Systems - Public Address Systems | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Speaker cladding misalignment - There is an issue spotted with east & west entrance gateline façade panel grills, the speakers don`t line up with the grills. Attached picture shows this. __ Cxxx T&C team did the test, but the test have failed to produce required SPL coverage for the designed wattage.
| 03SR - Stations (RfL) | Cxxx-NCR-003391 | NCR | Incorrect installation of Data cables |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2020-04-01 | 2020-02-01 09:38 | -60 | 2019-12-10 12:09 | Communications and Control Systems - Crossrail Data Network | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | For LER 4- Please check the attached FOR 4252 raised by __ - the Lift 8 &9 cable has been swapped over. The cables crossed over Lift 8 CR081-CCC-00317 and Lift 9 CR081-CCC-00318
| 03SR - Stations (RfL) | Cxxx-NCR-003392 | NCR | Paint on Cxxx assets |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2019-12-25 | 2020-02-12 16:43 | 49 | 2019-12-11 14:15 | Communications and Control Systems | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 1/Camera PAD-01-CAM-0101 located on departures road has white paint on camera base and on metal plate for white asset label. Cxxx paint contractor`s __ are not taking necessary care near Siemen`s assets. 2/Paint damage on radio antenna PAD-02- Ant-124 on east lift lobby intermediate. Cxxx Paint contractors __ are not taking necessary care when painting near Siemen`s assets. 3/Contaminated paint to completed assets has been noted at various assets throughout the station.
| 03SR - Stations (RfL) | Cxxx-NCR-003393 | NCR | Platform end returns Architectural cladding internal corners |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2020-04-30 | 2020-07-23 08:56 | 84 | 2019-12-12 13:27 | Architectural - Walls | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Architectural cladding infill required at each internal corner between PES and platform end return walls have not been manufactured nor installed according to the concept sketches attached to PMI 1549 Please review, develop F2 drawings and /or templates and remanufacture taking into account each location and its particular constraints and dimensions.
| 03SR - Stations (RfL) | Cxxx-NCR-003394 | NCR | Platform Disabled Signs |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2020-02-11 | 2021-01-26 11:19 | 350 | 2019-12-13 10:05 | Architectural - Signage | 500 |  | Design | Reject | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | PMI 00810 was issued to Cxxx – 02.02 2016 with various signage requirements included. One of the requirements was for the design, fabrication and installation of 2no flag type signs, one westbd ,one east bd mounted on the PES above 5th train car , to identify where mobility impaired passengers may most readily join the train.
| 03SR - Stations (RfL) | Cxxx-NCR-003395 | NCR | Fire Extinguisher Omissions - Front of House |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2020-03-27 | 2020-06-11 10:38 | 76 | 2019-12-13 13:34 | Fire - Fire Systems & General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | There are a number of front of house locations where the provision of fire extinguishers has been omitted in the design (please see linked EWN)
| 03SR - Stations (RfL) | Cxxx-NCR-003396 | NCR | Canopy Column Base - Concrete around Rubber Drainage Coupler |  | Contr | SKC | PAD - Paddington Station (West) |  | 2019-12-30 | 2020-02-26 10:15 | 58 | 2019-12-16 14:28 | Civil - Civil Engineering General | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | The concrete poured into the bases for the canopy column protection rings has been overpoured around the drainage coupler for the downpipe of the roof drainage, this will restrict the long term maintenance of the coupler as the concrete doesn't allow the removal of the coupling.
| 03SR - Stations (RfL) | Cxxx-NCR-003397 | NCR | ATS Labeling, LED identification, and supply position consistancy |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2020-02-29 | 2021-01-06 10:33 | 312 | 2019-12-17 11:59 | Electrical - General | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | I am sure we all recognise that the safe and effective operation of electrical distribution networks depends on (amongst other considerations) the consistent application of an agreed connection convention in the case of equipment serviced via dual supplies. In the case of the ATSs, the applied convention appears to be that the ‘A’ derived supply is connected to the L/H incoming isolator and the ‘B’ derived supply is connected to the R/H incoming isolator. In the case of the unit installed in ‘Fan Room 2’, this convention is reversed. I haven’t looked at any of the other 32 units installed to understand whether this is reflected elsewhere – this is an exercise that needs to be completed.
| 03SR - Stations (RfL) | Cxxx-NCR-003398 | NCR | Corroded and spray painted valve handles in chilled water plant room |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2020-02-20 | 2020-10-08 08:47 | 231 | 2019-12-20 14:01 | Mechanical - Mechanical Engineering General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | CRL observed during white glove inspections (5-Dec) that a number of valve handles and bolts have started corroding (see 'corroded' photos). Subsequently CRL have observed that the bolts and handles have been spray painted to cover over the corrosion (see 'sprayed' photos). The valve area that has been spray has not been properly masked, causing overspray, and the film thickness of the spray appears inadequate.
| 03SR - Stations (RfL) | Cxxx-NCR-003399 | NCR | Platform Lift 12 Roundel White Background Misalignment |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-04-05 | 2020-01-28 13:47 | -68 | 2020-01-06 10:32 | Architectural - Signage | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | It has been identified that there is a misalignment of the white background on the Platform Lift 12 roundel sign. Proposal is to leave as is. Please confirm.
| 03SR - Stations (RfL) | Cxxx-NCR-003400 | NCR | Departure Road Gate Line Cameras Cladding Issue |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2020-03-21 | 2020-09-23 08:43 | 186 | 2020-01-07 14:05 | Communications and Control Systems - CCTV | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The cameras are too far forward and façade panel will not close over as the camera base is too far forward. Also, the Hole in the façade cover for the camera is small. please refer to pictures attached
| 03SR - Stations (RfL) | Cxxx-NCR-003401 | NCR | Installation of Kitchen unit without Assurance |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-02-21 | 2020-03-12 14:01 | 20 | 2020-01-07 16:00 | Architectural - Joinery | 1000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | The Kitchen Units in SMK (Intermediate Central) and TEP (Platform West) were installed by /__ without formally capturing or agreeing the assurance process via an ITP.
| 03SR - Stations (RfL) | Cxxx-NCR-003402 | NCR | Damage to __ Roof - VSHH East |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-10-31 | 2020-10-02 12:24 | -29 | 2020-01-13 08:43 | Architectural - General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A hole has been drilled through the __ roof on the VSHH East end to allow a water pipe passing through. This however affects the waterproofing of the area and should be rectified. See attached photo
| 03SR - Stations (RfL) | Cxxx-NCR-003404 | NCR | Earth fault protection on devices over 400Amp |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-03-31 | 2020-06-11 10:45 | 72 | 2020-01-13 16:45 | Electrical - Switchgear | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | CrossRail document CRL1-XRL-M-RSP-CR001-50082 Clause JY71.3204-L requires that "Earth fault protection shall be provided for devices rated 400A and above." we have currently not complied with this clause as it will not allow discrimination to be achieved.
| 03SR - Stations (RfL) | Cxxx-NCR-003405 | NCR | __ LER IV - Scada interface JB lift 8 Issues |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2020-01-28 | 2020-02-05 11:36 | 8 | 2020-01-14 10:45 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Issues below spotted by Cxxx, Quality Spotter attached 1)There is no protection over the 230v Supply. 2)There is no Earth Bond on the JB 3)There is a voltage segregation issue. 4)The is SWARF and debris in the JB. 5)There is no T1 Cable ID or Circuit Ref. 6)The T1 installation is of low quality. 7)Electrical Tape has been installed over Earth Cables instead of Sleeving. 8)There is no Lock on the front of the JB
| 03SR - Stations (RfL) | Cxxx-NCR-003406 | NCR | Drilled RTU Marshelling Box - Cabinet Damage |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2020-01-28 | 2020-02-18 15:28 | 21 | 2020-01-14 10:56 | Communications and Control Systems | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Subcontractor __ have drilled a 10mm2 hole in the side of RTU marshalling box PAD-01-CAB-1016U2. Refer to attached quality spotter by Cxxx.
| 03SR - Stations (RfL) | Cxxx-NCR-003407 | NCR | Platform SAP's Faulty |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2020-01-28 | 2020-01-29 09:39 | 1 | 2020-01-14 14:45 | Communications and Control Systems | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Equipment found to be faulty at site and need to be replaced. Part Code - L76117-MFL0509-SAP02. Asset details on both SAPs are: PAD-04-SAP-Z1001 & PAD-04-SAP-Z2001
| 03SR - Stations (RfL) | Cxxx-NCR-003408 | NCR | Wayfinding signage |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2020-03-27 | 2020-11-09 15:22 | 227 | 2020-01-23 14:27 | Architectural - Signage | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Cxxx verification audit of installed wayfinding signs at PAD Cxxx-ATK-A-RGN-CRG02050147 v2.0 has identified a number of signs where the artwork / message is not compliant. This audit was also carried out at other CRL stations to identify inconsistencies of application/ interpretation. This audit has also been mapped against the switchable signage PMI 01566 to identify where there is some overlap The audit also identifies some signage which had at the time not been installed and therefore these remain at risk. The audit also identifies a limited number of signs where requirements have changed. CRL will issue a PMI separately.
| 03SR - Stations (RfL) | Cxxx-NCR-003409 | NCR | G50 lighting driver and quality issue |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-04-08 | 2020-07-27 14:51 | 110 | 2020-01-17 13:19 | Electrical - Lighting | 15000 |  | Manufacturing Defect | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Other | Completed |  | as per the attached report from design plan the are agreed quality issues with the fitting build and driver design
| 03SR - Stations (RfL) | Cxxx-NCR-003410 | NCR | water damage to BLL switch panel |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-03-31 | 2021-03-04 13:40 | 338 | 2020-01-17 13:36 | Electrical - Switchgear | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | water damage to BLL switch panel derived from water ingress the concrete slab/wall
| 03SR - Stations (RfL) | Cxxx-NCR-003412 | NCR | Replacement Telephones |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-11-26 | 2020-10-30 09:02 | -27 | 2020-01-21 16:43 | Communications and Control Systems - Telephony | 2000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | consolidation to capture all telephones which require replacement as per existing NCR's Cxxx-NCR-003343, Cxxx-NCR-003292 Cxxx-NCR-003346,Cxxx-NCR-003347,Cxxx-NCR-003348,Cxxx-NCR-003357,Cxxx-NCR-003383,Cxxx-NCR-003392,Cxxx-NCR-003411
| 03SR - Stations (RfL) | Cxxx-NCR-003413 | NCR | FFL's at Departures Road Door Thresholds |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-02-05 | 2020-10-20 07:49 | 258 | 2020-01-22 14:44 | Civil - Civil Engineering General | 6000 |  | Design | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | During construction it has been uncovered that the finished floor levels on Departures Road do not tie in with two of the door thresholds on McMillan House, namely the Greater Western Rail and British Transport Police doorways. The design levels provided at the Greater Western Rail doorway are 80mm higher, the paving has been constructed to this level now a trip hazard is present and if the paving is reduced by 80mm to match the doorway then the area will hold water and not drain properly. A new drainage system is required to be installed in front of the door to allow the paving level to be reduced and the water to drain, this has been designed by the Cxxx design team. The design levels at British Transport Police result in the FFL being below the door threshold creating a trip hazard. The departures road levels have been lifted in this area to tie in to the doorway, there will be no issues with drainage as the levels still flow away from the doorway to the MAX-E channel.
| 03SR - Stations (RfL) | Cxxx-NCR-003414 | NCR | Doorset D2-697 NR Battery Room opening outward |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2020-04-24 | 2020-05-06 14:43 | 12 | 2020-01-22 14:21 | Architectural - Doors | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Review of __ __ F2 drawing Cxxx-SKC-Y-DDL-M171_2-32326 C01 NR Battery Room door which is adjacent to the eastern entrance gate is indicated as opening outward . This is not acceptable given its location. Where other doors open outward onto Departures Road , the risk of unexpected opening striking passers by is mitigate dby the use of floor mo0unted barriers. In this location mitigation is not possible. It is not understood why this door cannot open inwards.
| 03SR - Stations (RfL) | Cxxx-NCR-003415 | NCR | Ventilation in WMTR-2 (East) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-05-31 | 2020-06-23 14:15 | 23 | 2020-01-23 13:26 | Mechanical - Heating Ventilation & Air Conditioning | 2500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | There is no natural or forced ventilation in the East Water Meter Room - Departure Road Level, Id: 2/787. Contractor to provide design justification or propose action for provision of ventilation in the room.
| 03SR - Stations (RfL) | Cxxx-NCR-003416 | NCR | Platform Tiles Damaged |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-04-14 | 2021-02-19 17:22 | 311 | 2020-01-28 13:26 | Architectural - Flooring | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | [28.01.20] During the cleaning of the Platform Tiles it has been identified that some of the tiles are damaged. It is not yet certain of whether the damage is a scratch or a crack. To be investigated.
| 03SR - Stations (RfL) | Cxxx-NCR-003417 | NCR | Main Box Signage Artwork Rework Issues - Consistency, Cxxx and Errors |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-06-27 | 2021-07-14 17:01 | 382 | 2020-01-29 15:55 | Architectural - Signage | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Various errors in the signage artwork has been identified for the main box signage. Additionally, there are consistency discrepancies raised by a Cxxx audit on the main box signage. 4no NCRs have been raised around these issues. It has been agreed with __ and __ on 29.01.20 to amalgamate the below NCRs into this one (NCR-3417). This NCR has been raised to amalgamate the following NCRs: Cxxx-NCR-003092 Cxxx-NCR-003215 Cxxx-NCR-003394 Cxxx-NCR-003408 Action plan: A meeting has been held (we24-Jan-20) to organise all current issues, once issues are organised the artwork will be remanufactured to close outstanding issues.
| 03SR - Stations (RfL) | Cxxx-NCR-003418 | NCR | NR Matwell Drainage - Incompatible materials |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2021-10-22 | 2021-10-20 14:53 | -2 | 2020-01-30 12:53 | Architectural - Flooring | 10000 |  | Design | Use As-Is | 2 (6-60k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | The NR matwell drainage has been developed from F1 intent without acceptance of alternative details by the Project Manager. The developed design was already in progress on site when Cxxx-FCD-2900 was raised on 19th December 2019. This FCD was sent back to the team on 8th January 2020 with the following comments. There is no objection in principle to the proposal for the drained CRL matwell however the following are of concern; 1. The aluminium subframe is buried in a cementitious latex screed which will corrode. The matwell will be subject to water ingress and in winter with possible addition of salts, producing a very aggressive environment in which the subframe will be immersed. This not acceptable. 2. There is a combination of stainless steel, galvanized steel and aluminium dissimilar metals, possibly exacerbated by the conditions in 1. This not acceptable. 3 The subframe is bolted to the substrate It is not clear how the fixing will besealed. The holww section will fill with water which cannot drain out. 4. The Intramatting layout plan ( no drawing number) indicates the matting interspersed with linear stainless steel strips. This does not align with the design intent nor is it clear what function these fulfi. Please clarify. 5 Detail B identifies a T bar on same plan Please clarify material and function. 6. Detail section B and detail section A have stop trims of aluminium and stainless steel respectively. They should be consistent and given comments in 1/2 above and be 316 stainless steel. The works have continued and the aluminium channels now bedded in the cementitious screed. Aluminium should never be cast into cementitious material as it causes corrosion of the aluminium, particularly in a wet environment. (ie the purpose of the matwell is to provide drainage of foot trafficked water)
| 03SR - Stations (RfL) | Cxxx-NCR-003419 | NCR | Back of House Rooms Shoot Bolt Potential Clash with Active Double Door Leaf |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-03-31 | 2020-02-13 09:43 | -47 | 2020-01-31 10:51 | Architectural - Doors | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | [31.01.20] Issue: A concern has been raised by CRL that for some of the double door sets the shoot bolt can be rotated towards the active leaf causing a clash and stopping the door from closing. Solution: It has been agreed between __ and __ that it is to be left as is. However, as this is deemed to be within the control of the IM, will write how to control this into the training manual/ O&M for the doors, i.e. "When closing the doors the shoot bolt must be properly engaged and not facing the active leaf. This is to allow the door to close properly and the fire line maintained".
| 03SR - Stations (RfL) | Cxxx-NCR-003420 | NCR | Poster frames Departures Rd |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2020-03-27 | 2020-03-23 17:56 | -4 | 2020-01-31 13:39 | Architectural - Signage | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | Approved LU poster frames have been located correctly on the brick slip cladding Departures Rd level east & west, adjacent to the entrance gates. However the approved poster frames are too large in the vertical dimension to fit in the recess provided in the brick slip panels. The installed solution has been to cover the recess with a thin guage flat stainless steel sheet. This element is not acceptable as installed in terms of: 1. lack of quality with random joints, no edge returns , does not sit flat 2 is not coordinated with back ground on which it sits 3. it is unclear on how / to what the poster frames are fixed 4. unclear how are the sheets fixed 5. sharp corners and edges are hazardous.
| 03SR - Stations (RfL) | Cxxx-NCR-003421 | NCR | Platform Hydrant Enclosure - Site Clashes and Fabrication Issues |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-07-12 | 2020-12-01 13:02 | 142 | 2020-02-03 08:38 | Architectural - Glazing | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Multiple NCRs have been raised regarding site interface clashes and fabrication issues with the Hydrant Enclosures on Platform. This NCR has been raised to amalgamate the following NCRs: Cxxx-NCR-003375 Cxxx-NCR-003351 Cxxx-NCR-003369 [04.03.20] Further to RRM on 04.03.20, hydrant enclosures are to be remade with piano hinges and ensuring hydrant door opens to 180 degrees. Other snags will also be addressed.
| 03SR - Stations (RfL) | Cxxx-NCR-003422 | NCR | MEP Damage to kalzip roof VSHH East |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-03-02 | 2020-03-11 11:41 | 9 | 2020-02-03 10:33 | Architectural - General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Hole drilled through the __ Roof on the VSHH east end (see picture attached).
| 03SR - Stations (RfL) | Cxxx-NCR-003423 | NCR | Installed CMS (Adaptable box) non comformance to specifications, and is electrical unsafe (LIVE) - Departures road, CSR XI, 1011 |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2020-02-18 | 2020-03-20 12:49 | 31 | 2020-02-04 10:20 | Electrical - Cable Management | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Departures road level, East Side, CSR XI, 1011....CMS install was found to be electrically unsafe. Live services are passing through the CMS system. The adaptable box is not fixed correctly to the wall, and there is a missing bush on one of the conduit entry points. Live cables are passing through this box, and there is visible damage to the PVC coated cables, around the area where there is no bush
| 03SR - Stations (RfL) | Cxxx-NCR-003425 | NCR | Damaged Whip Antenna & CIS Screen Cable - Departures Road |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2020-02-20 | 2020-04-16 15:05 | 56 | 2020-02-06 14:20 | Communications and Control Systems | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | •1no x Whip Antenna ANT-Z5-001 – East Entrance Gate whip antenna has been snapped off and damaged •1no x CIS screen cable The manufacturer cable that connects to the CIS screen has been damaged/burnt refer to photos attached
| 03SR - Stations (RfL) | Cxxx-NCR-003426 | NCR | Failure to adhere to ITP holdpoints for cert pack 5.6.7 |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2020-03-31 | 2020-03-05 15:13 | -26 | 2020-02-10 12:29 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Whilst reviewing the package for winch points installation in September 19 it was identified the works hadn`t been progressively assured. The check sheet for the works had been filled in for a couple of months after the works were complete. This means hold points were missed on ITP Cxxx-SKC-C-ITP-B071_WS077-50186 by __. Additionally the witness points were signed by a engineer after the works were complete. An NCR was requested to be raised on the comment sheet dated September 19. The CRL ITP guidance has been attached for reference.
| 03SR - Stations (RfL) | Cxxx-NCR-003427 | NCR | Station Fire Main - failed pressure test 02-Feb-2020 |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2020-03-31 | 2020-03-14 09:13 | -17 | 2020-02-10 14:31 | Fire - Suppression | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | There was a failed __ coupling in East Fire Lift (LB-S VIII); see attached photo. This occurred when the station fire main was being statically tested, whilst the pressure was being released after the main test at approximately 10bar. Additionally, during the pressure test a drain valve on breaching inlet was dripping, which needs to be rectified. The testing was undertaken by __. The pipework installation was by __.
| 03SR - Stations (RfL) | Cxxx-NCR-003428 | NCR | Faulty waste water pumps - PCCs 266, PCC 267 and PAC 082 |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2020-02-24 | 2020-03-07 10:39 | 12 | 2020-02-10 15:53 | Mechanical - Pumps | 2500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The Project Manager has been advised by the Contractor that the waste water pumps, which had been signed off at IRN stage (IRNs 232, 233) were faulty and have recently been replaced.
| 03SR - Stations (RfL) | Cxxx-NCR-003429 | NCR | Low Level Ventilation Openings - Electrical Rooms |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2020-08-07 | 2020-08-24 12:36 | 17 | 2020-02-11 09:29 | Architectural - Walls | 2500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Floor level ventilation openings have not been made good in electoral rooms where supply and extract ductwork has been provided. Contractor is required to confirm a list of rooms where holes are required to be made good. Also reference - PAC36
| 03SR - Stations (RfL) | Cxxx-NCR-003430 | NCR | CIAC 2 Observation - Pair of __ Arms Hanging In HV Switchroom |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2020-02-25 | 2020-05-15 13:27 | 80 | 2020-02-11 10:09 | Electrical - Cable Management | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Ref: CIAC 2 Observation - A pair of __ arms hanging from the top near to the back of HV switchboard are currently serving no purpose. I f they are not needed, they require removal as they may obstruct access to the 22 KV HV cables. The Contractor is required to investigate and remove assets as necessary.
| 03SR - Stations (RfL) | Cxxx-NCR-003431 | NCR | Chiller compounds West and East - access bridge and walkway over CMS not installed (PAC-36) |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2020-02-26 | 2021-01-14 14:29 | 323 | 2020-02-12 13:22 | Mechanical - Mechanical Engineering General | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Location: Chiller compounds West and East. There is no clear and safe access route in the chiller compound areas to access the chilled water valve train and chiller panels. There is also no protection over the low level CMS. The accepted construction issued latest design drawings (reference: Cxxx-SKC-M-DDA-M171_A-33201 Rev. C01 and Cxxx-SKC-M-DDA-M171_A-44201 Rev. C01) show access bridges over the chilled water pipework and CMS; and indicative raised walkway route over CMS - neither bridge or walkway has been installed. Access bridge and raised walkway over CMS to be installed to facilitate safe access around chiller compound.
| 03SR - Stations (RfL) | Cxxx-NCR-003432 | NCR | Faulty water heaters in cleaner's rooms (concourse and platform levels) |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2020-03-12 | 2020-03-20 12:54 | 8 | 2020-02-27 16:59 | Mechanical - Public Health Engineering | 500 |  | Equipment Breakdown | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | During commissioning of the water heaters PCC- 269, the following units were observed as not functioning: - Platform Cleaners Room (PCR) - Unit EWH 05 (observed 31/Jan/2020) - Concourse cleaners room (CLN) - Unit EWH 03 (observed 29/Jan/2020 and 14/Feb/2020) Power to the heaters was checked and confirmed okay. CRL advised that internal thermal control was replaced following 31/Jan witness, however the fault was observed again on 14/Feb. Fault to be recorded on DRACUS. Units to be offered back up to CRL for witnessing of water temperatures.
| 03SR - Stations (RfL) | Cxxx-NCR-003433 | NCR | Earth bars 25% spare capacirty not met |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-04-30 | 2020-04-16 08:03 | -14 | 2020-02-12 16:06 | Electrical - Earthing & Bonding | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | 22 Earth bas do not met the 25% spare capacity as per specification
| 03SR - Stations (RfL) | Cxxx-NCR-003435 | NCR | BLL AHU damper orientation incorrect |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-02-27 | 2020-03-20 13:09 | 22 | 2020-02-13 11:43 | Mechanical - Mechanical Engineering General | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | AHU damper installed in the incorrect orientation to enable the correct fire compartmentation to be completed
| 03SR - Stations (RfL) | Cxxx-NCR-003436 | NCR | Grouting to 'BLL (fire boarding)' steelwork baseplates |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-03-18 | 2020-04-01 07:55 | 14 | 2020-02-17 14:18 | Structural Engineering - Grouting | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Non shrink grout(5 star) was used to grout baseplates at 'BLL (fire boarding)' steelwork. The following non conformance has been recorded: 1. Torque test done prior to grouting 2. No cube test taken
| 03SR - Stations (RfL) | Cxxx-NCR-003437 | NCR | BLL antenna to be relocated |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-03-18 | 2020-03-04 15:41 | -14 | 2020-02-14 14:22 | Communications and Control Systems - Radio | 1000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Antenna is at risk of damage due to Hight of location Antenna is to be relocated as per Cxxx updated design
| 03SR - Stations (RfL) | Cxxx-NCR-003438 | NCR | Damaged Speakers |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2020-03-02 | 2020-02-18 15:26 | -13 | 2020-02-17 09:44 | Communications and Control Systems - Public Address Systems | 500 |  | Damaged | Reject | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper handling of material | Completed |  | 3x speakers found damaged when doing room inspections. Speakers: PAD-04-LSP-Z13D18, PAD-04-LSP-Z13C17, and PAD-04-LSP-Z13A19 refer to attached photos
| 03SR - Stations (RfL) | Cxxx-NCR-003439 | NCR | Drainage pump panels Deviations from JR20 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-03-03 | 2020-12-21 15:26 | 293 | 2020-02-18 11:58 | Mechanical - Pumps | 2500 |  | System Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Deviations from JR20 1. Operational philosophy is duty/assist. This arrangement is duty/standby – The pumps have been sized at 5.5l/s@31.62m head each pump. The flow rate under duty/assist would need to be calculated by the consultant and the cable arrangements checked by NHP to ensure suitable 2. Pump not available (MOA switch set to off) – white indicator lamp illuminated. Not installed. 3. Pump over temperature – amber indicator lamp. Not installed. 3. Emergency Stop – amber indicator lamp. Not installed. No Emergency Stop installed. 4. Sump normal level – green indicator lamp. Not installed. 5. Duty pump required – amber indication lamp. Not installed 6. Assist pump required - red indication lamp. Not installed. Pumps Duty/Standby as per 7. Flood – purple indication lamp. Not installed. 8. Pump operation inhibited – purple indication lamp. Orange lamp installed.
| 03SR - Stations (RfL) | Cxxx-NCR-003440 | NCR | Drainage pump panels workmenship Deviations from JR20 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-03-31 | 2020-03-20 13:15 | -11 | 2020-02-18 12:10 | Mechanical - Pumps | 1500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 1. All external engraved labels to be 20mm font. 10mm font used. CEG Response: I am happy to leave it as it is as long as the wordings are readable. Electrical team to confirm? 2. No core identification markers attached to wires in terminals; 9&10, 14&15 (thermistors), 32,33,34,35 (level electrodes). 3. Drawings and operating instructions missing from panel. 4. All internal component labels should use a 10mm font size. All components labels are hand-written. CEG Response: I am happy to leave it as it is as long as the wordings are readable. Electrical team to confirm? 5. No segregation at terminals between LV and BMS. 6. No shrouds and warning labels over LV terminals. 7. No female bush fitted on incoming supply cables CMS transition. Cores are in contact with the edge of the male bush. Somebody has decided the cable insulation is at risk and so site applied insulation has been used to mitigate the problem rather than a female bush. All other transitions have been fitted with female bushes.
| 03SR - Stations (RfL) | Cxxx-NCR-003441 | NCR | Hot Water Taps - Not Installed as Design (PCC-269) |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2020-03-31 | 2020-03-14 09:18 | -17 | 2020-02-18 14:20 | Mechanical - Hot & Cold Water Supplies | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Hot water outlets at the following locations have been provided with mixing valves which are not in the design (drawing ref. Cxxx-SKC-P-DDE-M171_Z-50510). 1) Platform cleaners (PCR) 2) Platform Tea Room (TEP)3) 3) Concourse cleaners Room (CLN) 4) Intermediate Staff Mess Room (SMK)
| 03SR - Stations (RfL) | Cxxx-NCR-003442 | NCR | East and West Vent Shaft Head House Chiller Farm Access Hatches |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2020-05-26 | 2021-05-28 14:59 | 367 | 2020-02-18 15:05 | Architectural - General | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Access to the east and west VSHH chiller farms is via a ladder and access hatch, if a person is within the chiller farm area and the hatch closes there is no way of opening the hatch to leave or escape, a person will be trapped in the chiller farm area. This is a safety issue and the designer is to advise on a suitable proposal to eliminate this.
| 03SR - Stations (RfL) | Cxxx-NCR-003443 | NCR | Concourse Level Fire Hydrant Spacing |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2020-06-30 | 2020-07-09 11:18 | 9 | 2020-02-19 15:10 | Fire - Fire Systems & General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | It has been identified that the additional fire hydrants installed on concourse level are at a spacing of ~70.4m instead of the 69m spacing agreed with the LFB and instructed in Cxxx-PMI-01598.
| 03SR - Stations (RfL) | Cxxx-NCR-003444 | NCR | Crossrail Arch - Gutter Flood test |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-03-20 | 2020-03-13 13:11 | -7 | 2020-02-19 16:04 | Architectural - Roofing & Exterior Treatment | 5000 |  | Testing and Commissioning | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | During the flood test of the Crossrail Arch gutter, a leak was found at approximately Grid Line 82
| 03SR - Stations (RfL) | Cxxx-NCR-003445 | NCR | Concrete Cutting without Cxxx Acceptance - Platform Level for PAE Enclosure (GL 7) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-03-22 | 2020-03-26 09:12 | 4 | 2020-02-21 12:06 | Civil - Structural Engineering | 3000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | In the location of the gridline 7 PAE enclosure on platform level, an on site decision was made in error to cut concrete. This did not have Cxxx approval prior to works commencing. It further came to light that this was requested by __ due to minor discrepancies with their install. This will be investigated and if this is an issue a separate NCR will be raised accordingly.
| 03SR - Stations (RfL) | Cxxx-NCR-003446 | NCR | Gaps above Smoke Downstands on Platform Level |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-04-30 | 2020-06-15 14:37 | 46 | 2020-02-22 16:32 | Fire - Compartmentation | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Following the smoke tests on platform level, it was discovered that smoke was passing from one smoke reservoir to the next due to two elements of incomplete work above the smoke downstands: - Gaps between the precast concrete domes. - Coffers passing above downstands. This has been missed as there was no detail from __.
| 03SR - Stations (RfL) | Cxxx-NCR-003447 | NCR | Defective Handrail - CIR-S XIV (__) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-04-12 | 2020-08-06 14:42 | 116 | 2020-02-22 17:08 | Architectural - Handrail | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A previous NCR was raised for the flooring levels in CIR-S XIV (__ - GL 8.5). The handrail was manufactured to suit the previous incorrect FFL. We have since installed another step to bring the FFL in line with the gated design. This step addition renders the current handrail defective and will be required to be replaced.
| 03SR - Stations (RfL) | Cxxx-NCR-003448 | NCR | BLL stair Cxxx Antennae location |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2020-03-30 | 2020-03-04 17:47 | -26 | 2020-02-24 12:32 | Architectural - Walls | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Cxxx have installed a directional antennae on one of the intermediate BLL landings which: 1. Prevents installation and future use of the ceiling access panels 2. Its current location is within touching distance of anyone using the stair. An alternative location has been agreed which resolves each issue and accepted by Cxxx. Refer attachment below.
| 03SR - Stations (RfL) | Cxxx-NCR-003449 | NCR | Water Ingress - __ East Corridor |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-04-14 | 2021-01-21 15:44 | 282 | 2020-02-24 14:53 | Architectural - General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | It has been discovered that in space ref.: CIR-PL XIV, code 118; there was standing water beneath the temporary correx protection. The water seems to be running down the face of door ref.: D2-118 to the threshold and into the corridor. See attached photos of both the water and door in questions along with marked up plan GA drawings of the corridor in question for reference.
| 03SR - Stations (RfL) | Cxxx-NCR-003450 | NCR | Incorrect Fabrication of EVSHH Bollards |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-03-10 | 2020-10-12 08:28 | 216 | 2020-02-25 15:02 | Civil - Civil Engineering General | 5000 |  | Manufacturing Defect | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | An array of four bollards is to be installed at the eastern end of the EVSHH on Eastbourne Terrace. During fabrication the two EXT-317 bollards have been fabricated to the incorrect length due to an error in the fabrication drawings. The project specification is for the bollard core to extend 1000mm above the FFL, with the final bollard height at 1100mm above FFL. The core height above FFL on the EXT-317's is 930mm.
| 03SR - Stations (RfL) | Cxxx-NCR-003452 | NCR | Fire Alarm and Fire Detection system-related labels |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-03-17 | 2020-10-27 13:02 | 224 | 2020-03-03 09:47 | Information Management - Asset Information | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The basis of this request is that all installed Fire Alarm and Fire Detection system-related labels at Cxxx Paddington Station do not have the ‘Loop ID’ printed on the label (although this is captured in the data that is accessible when scanning the label Data Matrix code). The Asset Naming and Labelling Convention Document v9.0 (ANLCD) states that when a Designer Alternative ID (DAAID) is provided, it is to be on Label Line 3 of the physical Label. The Cxxx Asset Team has not included the DAAID (assumed to be the Loop ID) for the labels that are part of these Asset Classes on the Fire system for the following reasons: • The fire drawings have changed multiple times over the past two years, which is when labelling of fire Assets began. Had the Asset Information Team included the Loop IDs on all previously installed Fire System Asset labels, nearly all labels would have been required to be replaced, many more than once. • A separate site team have recently installed all British Standard circuit labels on all Fire Alarm and Fire Detection connected Assets. These labels contain the AS-Built Loop Identification number as per associated drawings/schematics and are always placed in the direct vicinity of the installed Asset Labels. The current number of labels that are installed as part of these Fire Loop/Damper Loop systems is approximately ~1000 labels. These are scattered about the entire Cxxx Paddington Site, from East__ Terrace to Bakerloo Line Link. Many of these Assets are also located at height and/or around safety critical plant meaning access is a considerable issue. An additional Non-Compliance was also observed by the CRL Cxxx Asset Information Lead, that all Fire Damper Interface Units have the DAAID stated as being the Fire Damper ID, rather than the Damper Control Loop ID. Although this Fire Damper ID is printed on the label, The Loop Circuit Reference is also captured in the Asset Data which is visible when scanning the Label’s Data Matrix Code. Please refer attached supporting documents for evidence of the current installed Asset Labels and also the British Standard labels that have been installed.
| 03SR - Stations (RfL) | Cxxx-NCR-003453 | NCR | EXT-301 and EXT-302 Benches Anti-Graffiti Coating |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-04-14 | 2020-09-02 06:30 | 141 | 2020-03-03 16:59 | Civil - Civil Engineering General | 500 |  | Manufacturing Defect | Reject | 4 (0.5-3k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | The EXT-301 and EXT-302 stone benches supplied by Bellitalia have been supplied and installed without the anti graffiti coating as required in the specification. The coating should have been applied in the factory environment prior to delivery to site.
| 03SR - Stations (RfL) | Cxxx-NCR-003454 | NCR | Canopy washdown solonoid supplies ( PCC 266 & PCC 267 ) |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2020-04-28 | 2020-04-03 13:53 | -25 | 2020-03-04 10:18 | Electrical - General | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Departures road corridor East and West, and __ Mewp Store. Some time ago we reviewed the IRF for the solenoid supply, which included all the cables and panel, this was an electrical IRF as part of a mechanical PCC. 1. It was agreed at the time that cables were to be bunched together as long as cable ID is visible…. Currently there is still no ID on these cables. There are no cable IDs at the Panel or the spurs, or anywhere on the length, and there is a question to what the cables are referenced as. 2. At the date of sign off, the solenoids were not connected, and on looking at the attached photos, the connection between spur and solenoid is non conforming…. A coupler must be used where a threaded termination is not present. Generally, flanged couplers are used on this project. 3. Currently, there are no BS labels on the spurs
| 03SR - Stations (RfL) | Cxxx-NCR-003455 | NCR | Dissimilar metals on drawbridge hinges (East & West) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-03-27 | 2021-09-20 08:17 | 542 | 2020-03-05 09:18 | Civil - Structural Engineering | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | There is dissimilar metals on the drawbridge that will cause corrosion over time. The dissimilar metals are between the stainless steel hinge and the galvanised fixings.
| 03SR - Stations (RfL) | Cxxx-NCR-003457 | NCR | VSHH Exposed catladders & structure |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2020-06-26 | 2020-12-16 11:57 | 173 | 2020-03-10 13:23 | Architectural - Roofing & Exterior Treatment | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | It has come to the attention of the Project Manager that catladders to access the VSHH roofs east and west have recently been installed between mezzanine level and underside of the roof on the E__ side of each. These catladders along with what appears to be an over engineered supporting structure are highly visible when viewed from EBT. In order to obtain consent, the architectural, structural and MEP design of each of these structures required intensive effort over a lengthy period, in consultation with WCC and English Heritage. The design includes many refinements and attention to detail in order to reduce the scale /impact of the structures and mitigate/screen its necessary functional requirements. The installed assembly, which is visually very crude, is not included on the consented S7 submission nor could it be considered de minimus change to that consent. Given this context, the installed visually over sized structure is not acceptable. Please arrange a RRM to review options for mitigation.
| 03SR - Stations (RfL) | Cxxx-NCR-003458 | NCR | Fire Damper Actuators |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-07-31 | 2020-07-20 09:01 | -11 | 2020-03-11 14:29 | Fire - Fire Systems & General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The Cxxx Asset Team wishes to submit a Non-Compliance Request for the installation on Asset Labels on Actuators for Fire Dampers at Paddington Station.
| 03SR - Stations (RfL) | Cxxx-NCR-003459 | NCR | Asset Class L7864 – Control Panel, for all free-standing Control Panels |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-07-31 | 2020-07-20 08:39 | -11 | 2020-03-11 14:33 | Information Management - Asset Information | 500 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | The Asset Naming and Labelling Convention (ANLCD) provides the following guidance for labelling this Asset Class: “An Asset Tag Label will be placed on a permanent structure next to the item in a position that can be can be viewed without the need for specialist access equipment or railway possessions and where the label will not be permanently covered.”
| 03SR - Stations (RfL) | Cxxx-NCR-003460 | NCR | Flexible Connection Assembly-L756161 and Sound Attenuation Equipment-L76119 Asset Classes |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-07-31 | 2020-07-20 08:44 | -11 | 2020-03-11 14:36 | Information Management - Asset Information | 500 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Flexible Connection Assembly-L756161 and Sound Attenuation Equipment-L76119 Asset Classes.
| 03SR - Stations (RfL) | Cxxx-NCR-003461 | NCR | Insufficient support for lighting under brick slip concourse. |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-03-25 | 2020-04-15 07:54 | 21 | 2020-03-11 14:41 | Architectural - Finishes | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Insufficient support for lighting under brick slip concourse is causing the lighting support channel to sag.
| 03SR - Stations (RfL) | Cxxx-NCR-003462 | NCR | Asset Labels relating to Test Points for Aspirating Detectors |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-03-25 | 2020-03-14 09:33 | -11 | 2020-03-11 14:40 | Information Management - Asset Information | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Asset Labels relating to Test Points for Aspirating Detectors. The Asset Class affected by this request is L7453 – Test Point.
| 03SR - Stations (RfL) | Cxxx-NCR-003463 | NCR | Lost/Missing LongSpan Extenders |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2020-04-28 | 2020-04-15 15:44 | -13 | 2020-03-17 10:28 | Communications and Control Systems - CCTV | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Insufficient quantity of material to do the job | Completed |  | No.8 long Span Extenders for CCTV equipment has gone missing on site. __ attached Material Handover document that reflects items have been delivered to T1.
| 03SR - Stations (RfL) | Cxxx-NCR-003464 | NCR | East staircase access to the platform - 110V circuit; Damage to cables, and corrosion damage to adaptable box |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2020-05-20 | 2020-08-11 14:22 | 83 | 2020-03-17 13:33 | Electrical - General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 17/03/2020 Photos were taken at the East staircase access to the platform; there has been some rewiring work going on within the junction box in the UPD, which is corroded.. When the cables have been pulled back, it has caused a lot of scuff damage on the cable, and brown tape has been used to cover some of these marks, the junction box also looks to have corrosion damage.
| 03SR - Stations (RfL) | Cxxx-NCR-003465 | NCR | VSHH - Change of grillage fixings |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-04-30 | 2020-09-18 10:35 | 141 | 2020-03-19 15:01 | Architectural - General | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | 5.5x80 self-drilling screws (TIMco H80W16B) have been installed instead of the FX47 (M8x50 bolts) shown in drawing '3-41655' to fix the gratings in the VSHH East Grillage DR Shaft to the supporting steel work.
| 03SR - Stations (RfL) | Cxxx-NCR-003466 | NCR | Trims not sitting correctly on the escalator cladding & Inconsistency in the finishes. |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-07-31 | 2021-11-17 11:32 | 474 | 2020-03-23 10:48 | Architectural - Finishes | 2500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Issue 1: The 2mm stainless steel trims installed on the escalator to hide the cladding dependencies are also causing gaps up to 6mm between plates which is not acceptable. Issue 2: The Contractor would like to notify the client of panels being installed at platform level and concourse not being of the finish specified, I refer to the picture attached which highlight the two different finishes installed. The F2 Contractor specialist is to rectify the escalator cladding inconsistencies by replacing the panels and comply with the current Works Information and specifications.
| 03SR - Stations (RfL) | Cxxx-NCR-003467 | NCR | Marshalls Benches - Cxxx comments |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-08-21 | 2020-07-13 08:53 | -39 | 2020-03-24 11:34 | Archaeology - General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | [24.03.20] Cxxx carried out a visual inspection on 28-Jan-20 on the Marshall Benches (2,4 and 12 seater). There are various snags/ comments which are "of concern" to Cxxx. the following steps are: 1. / CRL (JT/ RB) to review and agree which comments are to be implemented/ actioned 2. Close out agreed comments Note: The works captured in the NCR are considered snags and will be addressed as snags.
| 03SR - Stations (RfL) | Cxxx-NCR-003468 | NCR | escalator and lift supply information incorrect |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-04-30 | 2020-05-20 08:49 | 20 | 2020-03-24 16:27 | Electrical - Power Distribution | 2000 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Supply information incorrect against the below Escalators 6, 7, 8 & 9 Lifts 6 & 7
| 03SR - Stations (RfL) | Cxxx-NCR-003469 | NCR | TVP I & II Platform doors |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2020-04-14 | 2020-11-04 16:54 | 204 | 2020-03-31 09:51 | Architectural - Doors | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | TVP I & II Platform level bronze clad doors D5-576 & D5-577 have been installed it would appear, without being designed for pressure loading. Not withstanding that the specific loading performance is being clarified by Cxxx and subject to confirmation by site test, there is evidence that the welding of the door panels is showing signs of failure. Refer also EWN -3569
| 03SR - Stations (RfL) | Cxxx-NCR-003470 | NCR | Cxxx-PMI-01367 Architectural Design Not coordinated with Install (SOR Intercom Panel) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2021-04-03 | 2020-10-02 07:28 | -183 | 2020-04-03 15:56 | Architectural - Doors | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Further to Cxxx-PMI-01367 the WI required an SOR intercom panel to be installed with electronic door release systems. It has been identified that these have not been included into the design and currently installed doors or cladding. These elements are to be changed so that the PMI is satisfied.
| 03SR - Stations (RfL) | Cxxx-NCR-003471 | NCR | ECR V and VI - FOH Doors Not Installed in Accordance with the Design/Defective Design |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-09-16 | 2020-09-14 14:25 | -2 | 2020-04-07 15:43 | Architectural - Doors | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | This NCR relates to the defective design of the ECR V & VI FOH doors and their interface with the surrounding finishes and compliance with the security statement. Therefore there are several layers to this NCR. The first issue, is that the doors (D2-679 & D2-680) have been installed within the structural opening formed in the RC to maintain the fire line. Also, the GA detail shows the doors installed in line with the brickslip cladding that is not possible as these cannot be fixed into as well as they not being fire rated, hence the doors being installed within the RC. Following the install, it was discussed with __ (CRL) and the __ architects that this in fact does not comply with the Cxxx security statement with regards to blind recesses being no more than 150mm. Therefore an alternate detail that allows/provides the following is required to be created by __: - 60 minute fire line is maintained. - No fixing into brickslip panels. - Security rating for doors is not maintained. - Architectural intent is maintained. - Complies with the security statement for Cxxx. Therefore to close this NCR, a compliant design is required to be produced and issued to Crossrail for approval. The current in-situ doors, although fire compliant, will need to be removed and discarded when the new doors are ready for installation.
| 03SR - Stations (RfL) | Cxxx-NCR-003472 | NCR | Grouting below 2.5m barrier baseplates (__) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-04-28 | 2020-04-15 14:28 | -13 | 2020-04-14 11:29 | Architectural - Balustrade | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Non shrink grout(5 star) was used to grout baseplates of the 2.5m Barrier. The following non conformance has been recorded: 1. Torque test done prior to grouting 2. No cube test taken
| 03SR - Stations (RfL) | Cxxx-NCR-003473 | NCR | UPS batteries - insufficient maintenance and deep discharge of east comms UPS |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2020-06-30 | 2020-06-15 07:42 | -15 | 2020-04-16 09:10 | Electrical - General | 5000 |  | Damaged | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | The batteries were commissioned in November 2018 and the PM has seen no evidence that the batteries have been maintained periodically in accordance with the manufacturers recommendations. In addition, the east comms battery banks have undergone a deep discharge. This was identified by __ during phase 2.3 testing, however an NCR has not been raised by .
| 03SR - Stations (RfL) | Cxxx-NCR-003474 | NCR | Faulty CCTV Cables Eastbourne Terrace |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2020-07-31 | 2020-09-09 10:51 | 40 | 2020-04-17 10:03 | Communications and Control Systems - CCTV | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | T1 contractor have Identified two faulty/damaged cables for Eastbourne terrace CCTV CAM 142 and 143.
| 03SR - Stations (RfL) | Cxxx-NCR-003475 | NCR | Non-compliant and missing pipe labels with sub-platform areas (PAC-086 and VAP item 119) |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2020-07-01 | 2020-11-19 16:31 | 141 | 2020-04-21 15:37 | Mechanical - Public Health Engineering | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Pipe labels installed in the sub platform areas where the West and East foul sump pumps are located are not to BS 1710 standard. (See example photo attached, west foul pump) Also, there are missing pipe labels on some of the pipework.
| 03SR - Stations (RfL) | Cxxx-NCR-003476 | NCR | GL 2-6 Handrail Non-compliant with Hydraulic Bollard Pipework |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-05-06 | 2020-08-06 14:24 | 92 | 2020-04-22 14:47 | Architectural - Finishes | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Due to the installation of the hydraulic pipework containing the hydraulic fluid tubes along the NW __ corridor, the installed handrail is now non-compliant with LUL S1133. Handrail required to be altered.
| 03SR - Stations (RfL) | Cxxx-NCR-003477 | NCR | Corrosion to self-tapping screws of VSHH lighting channels |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-06-12 | 2020-05-27 08:50 | -16 | 2020-04-23 09:39 | Architectural - Urban Realm | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | For the VSHH lighting channel bottom trim, horizontal (grade 316 stainless steel) plate sections are fastened to the wall mounted angle sections by means of self-tapping screws at 900mm intervals (please refer to ‘Cxxx-SKC-Y-DDD-M171_1-41551 extract' attached, where the screw is highlighted). The self-tapping screws specified and used were SFS’s SX5/12-S16-5.5x35. These are in themselves a bi-metallic product; the fastener and head portion are stainless steel whereas the drill point is carbon steel. Please refer to the product data sheet attached (‘SFSintec SX5_12-S16-5,5X35-A4 Data Sheet'). Since installation, it has been found that a portion of the screws have shown visible signs of corrosion on the tips and part of the thread. No signs of corrosion have been found on the heads. A survey of all screws was completed in November 2019 (see ‘Self tapping screw corrosion survey 20.11.19' attached, where signs of corrosion are highlighted). Due to the bi-metallic nature of the screw, it would be expected to see some signs of corrosions (evident in the carbon steel portion). However, the main body of the screw is stainless steel.
| 03SR - Stations (RfL) | Cxxx-NCR-003478 | NCR | Intermediate Level SSR Door (D3-418) - Grab Rail not installed |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-10-20 | 2020-10-21 05:28 | 1 | 2020-04-24 10:44 | Architectural - Doors | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Following a review of this room, their is a requirement for a grab rail to be installed on the inside leaf of the door which has not been installed. After contacting the involved parties, have found that the design consultant failed to notify others of this requirement upon reviewing their drawings. The door is not fire rated so it is still currently compliant for access to the SSR. The current door will remain as installed until the replacement arrives onsite.
| 03SR - Stations (RfL) | Cxxx-NCR-003479 | NCR | BLL waffle lighting insuficccient |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-05-31 | 2020-09-29 14:37 | 121 | 2020-04-27 07:09 | Electrical - Lighting | 2500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | post installation completion and taking lux levels we have identified insufficient lighting levels
| 03SR - Stations (RfL) | Cxxx-NCR-003480 | NCR | 1.25.25 GFRC Support bolts cut incorrectly and replaced on site |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-05-12 | 2020-04-29 07:57 | -13 | 2020-04-28 15:44 | Archaeology - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | -NCR-000149 was an internal NCR raised to , the S/C who installed the GFRC within the BLB. It was identified by on 24/04/18 that has cut support fixing bolts incorrectly. This issue was closed internally on 21/05/18 where removed and replaced the cut bolts. This was never raised to CRL so this is a retrospective NCR to capture the issue. Please refer to the attached information. It has been agreed between __ () and __ (CRL) to raise this NCR to capture the issue whereby the attached information of the internal close out NCR on Aconex, site photos with no protruding bolts and a daily record sheet from carrying out the works will close the NCR.
| 03SR - Stations (RfL) | Cxxx-NCR-003481 | NCR | Urban Realm Glass Canopy Leak |  | Contr | SKC | PAD - Paddington Station (West) |  | 2022-05-27 | 2022-05-20 15:27 | -7 | 2020-05-05 17:00 | Architectural - Roofing & Exterior Treatment | 6000 |  | Workmanship | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | This NCR has been developped to incorporate PWK-01954 pertaining to replacement of one crack roof glazinf panel. 1. Roof Leaks: It has been reported and observed that the glass canopy that stretches the central section of the urban realm at the Paddington station, has several leaks within the glass steel structure. Due to the ongoing situation of Covid-19 and reduced site resource, yet have not been able to establish the full extent of the leaks during and after periods of rainfall. 2. Replacement of cracked glass: Subsequent to above; one glazing panel has sustained damage beyond repair, and requires replacement. See markup drawing Cxxx-SWN-A-DDA-M171_B-33501 attached.
| 03SR - Stations (RfL) | Cxxx-NCR-003482 | NCR | Platform Level __ Coffer Panels Require Cutting to align with PAVA and Fire Detection |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-08-31 | 2020-07-28 10:03 | -34 | 2020-05-05 07:23 | Architectural - Finishes | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | There is a clash between the __ Architectural coffer cladding and the MEP PAVA and Fire Detection for 2no panels on platform level. In order to overcome the issue it has been agreed with CRL (__) that these panels can be cut on site.
| 03SR - Stations (RfL) | Cxxx-NCR-003483 | NCR | Internal Firestopping - Unable to be installed due to sleeve size (ECR rooms) - Cxxx-FCD-002925 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-06-14 | 2020-09-23 08:03 | 101 | 2020-05-05 14:50 | Fire - Compartmentation | 1500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | This NCR is being raised due to the fact the internal firestopping to the escalator cables as they leave the ECR rooms is unable to be firestopped. The cables pass through a sleeve that has been installed around the cables and cast within firestopping compound. The sleeve is too small to allow internal firestopping. The cables then pass into cast in ducts within the RC Slab and travel to the escalators they are designated to supply. This NCR has been requested to be raised by __ in a reworked comment to Cxxx-FCD-002925.
| 03SR - Stations (RfL) | Cxxx-NCR-003484 | NCR | Non IP rateded conduit accessories utilised in external locations |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-06-30 | 2020-11-04 16:53 | 127 | 2020-05-14 08:41 | Electrical - Cable Management | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | In the vent head house there has been incorrect IP rated conduit accessories installed
| 03SR - Stations (RfL) | Cxxx-NCR-003485 | NCR | Installation of Platform Plinth Benches and Freestanding Benches without approved ITP |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-06-02 | 2020-06-15 09:51 | 13 | 2020-05-19 09:57 | Architectural - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Installation of Platform Plinth Benches and Freestanding Benches were installed without an approved an Approved ITP However during the installation, documentary evidence was captured and subsequent witness statement provided by __ who was present at time of installation. We have in place check sheets for fixing information as per manufacturers guidance. IRF-2976 was raised with reference to ITP Cxxx-SKC-C-ITP-B071_WS077-50182, the benches weren't installed to this ITP but it was referenced for Pull and Torque testing only.
| 03SR - Stations (RfL) | Cxxx-NCR-003486 | NCR | Concorse Hydrants installled away from design |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-08-31 | 2020-10-09 13:37 | 39 | 2020-06-01 07:42 | Fire - Suppression | 2500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | concourse level at GL11 & GL15. Due to the installation not being installed as per drawing and the fact that the outlet valve welded pipe sections being a considerable longer than identified on the drawing this has pushed the pipe work off the wall to approx. 600mm, when the drawing states 185mm (see extract from drawing 50257), subsequently when the fire rated enclosure was installed this has restricted the width of the corridor to less than the width of the door to which it leads to therefore non-compliant, please see attached photo
| 03SR - Stations (RfL) | Cxxx-NCR-003487 | NCR | Additional LV meters required |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-07-31 | 2020-10-26 15:49 | 87 | 2020-06-02 14:41 | Electrical - LV Equipment | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | following the progressive upgrade of supplies throughout the project. it has been noted that there are 6 number meters which have been missed and require installation
| 03SR - Stations (RfL) | Cxxx-NCR-003488 | NCR | Cxxx cabling too short due to CMS reworks |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-06-18 | 2020-07-20 09:11 | 32 | 2020-06-04 10:58 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Cabling is now short for Cxxx assets please see attached email
| 03SR - Stations (RfL) | Cxxx-NCR-003489 | NCR | Water Ingress into BLB Pit - Damage to Fire Boarding to LV Cables |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-07-28 | 2020-11-22 11:15 | 117 | 2020-06-08 18:47 | Fire - Compartmentation | 5000 |  | Damaged | Rework | 3 (3-6k) | Complete | External Phenomenon - Other | Completed |  | Following the COVID-19 shutdown and subsequent PMIs for part-remobilsation, an inspection was carried out in the BLB pits following the issue with water ingress earlier in the year identified with the BLL project. All pits were dry apart from the pit highlighted on the attached drawing. This pit contains A & B supply cables with 120 minute fire separation around the A supply. As you can see from the attached pictures the __ect boarding has become saturated and will require replacing. The boarding is also required to be removed to determine where the leak is coming from.
| 03SR - Stations (RfL) | Cxxx-NCR-003490 | NCR | Change Control to Firestopping within Service Penetrations |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-07-12 | 2020-07-08 09:47 | -4 | 2020-06-12 16:37 | Fire - Compartmentation | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During a site inspection carried out by __ (CRL) it was noticed that several service penetrations had had their firestopping removed yet checksheets were still included within the certification record pack that was due to be formally submitted along with them still being on the firestopping log updated and maintained by __. In one location the firestopping had changed from compound to __ Softseal yet the register and checksheet still referenced compound. __ () has since explained the process to control and manage change and in agreement with Paul this NCR has been raised to capture the discussion so the change control is documented.
| 03SR - Stations (RfL) | Cxxx-NCR-003491 | NCR | Missing Records From Telephony IRN |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2020-10-31 | 2020-09-30 15:06 | -31 | 2020-06-24 12:16 | Communications and Control Systems - Telephony | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | T1 have uploaded IRN package for the telephony system on EB, Cable and wiring Schedule is missing some of the cable records. Refer to attached email document.
| 03SR - Stations (RfL) | Cxxx-NCR-003492 | NCR | Escape Route from Tunnel/Track Handrail Blocked by Cxxx Phone - Lack of Design Coordination |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-07-24 | 2020-09-04 09:44 | 42 | 2020-06-24 14:34 | Architectural - Handrail | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | During a site inspection by CRL's Lead Architect __, it was discovered that the handrail on the 2.5m barrier in each PES end has been blocked by the installation of the Cxxx drivers phone that means the handrail is not continuous and creates an obstruction that therefore in non-compliance with LUL S1133, and for means of escape. Through investigation, the phone location was designed, in accordance with Cxxx requirements, by Fourway and approved by __ without consideration of the impact to the handrail. Therefore the design has not been adequately coordinated.
| 03SR - Stations (RfL) | Cxxx-NCR-003493 | NCR | Departures Road Canopy - Broken Glazing Panel |  | Contr | SKC | PAD - Paddington Station (West) |  | 2021-03-24 | 2021-03-24 14:10 | 0 | 2021-03-22 14:53 | Architectural - Glazing | 8000 |  | Damaged | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | Due to accidentally breakage, 2 no. canopy glazing panels have been damaged and require replacement. The 2 no. affected panels are panel no. 13/04 (artwork) and a standard Z panel.
| 03SR - Stations (RfL) | Cxxx-NCR-003494 | NCR | Bakerloo Box Stair Light & Speaker panels - Incorrect Cutouts |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-07-13 | 2020-11-12 08:37 | 122 | 2020-06-29 14:10 | Architectural - Finishes | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Subcontractor (__) Have installed the bakerloo stair soffit/ceiling panels without coordination of the MEP services. There are cutouts that do no match the size of the services and other services do have the cutout present. See photos Attached.
| 03SR - Stations (RfL) | Cxxx-NCR-003495 | NCR | Leak within SWR II (Platform East) from DR EB II & Prevention Work to DR EB I into SWR I |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-10-23 | 2020-11-12 10:24 | 20 | 2020-07-06 17:11 | Architectural - General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During a site inspection, it was noticed that a leak has appeared in the SWR II that has caused damage to installed electrical elements.
| 03SR - Stations (RfL) | Cxxx-NCR-003496 | NCR | Missing Segregation in floor Hatch Concourse |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2020-10-31 | 2021-02-12 16:56 | 104 | 2020-07-10 09:06 | Communications and Control Systems | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Missing floor compartment trunking separation in floor hatch for Totem at escalator 6 & 7 on concourse. LV & comms require separation. Cable separation panel is only missing in this floor hatch. Refer to Quality spotter Attached
| 03SR - Stations (RfL) | Cxxx-NCR-003497 | NCR | PHP's Installation |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2020-10-31 | 2020-10-07 09:53 | -24 | 2020-07-10 11:05 | Communications and Control Systems - Telephony | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Most of the PHP’s will need to be packed out to allow for maintenance access to the locking bolt. The cladding is too close to the bolt in some places. refer to attached survey.
| 03SR - Stations (RfL) | Cxxx-NCR-003498 | NCR | E__ Camera Cable Lengths Exceed 90m |  | Contr | SMN | PAD - Paddington Station (West) |  | 2020-10-31 | 2020-09-30 15:16 | -31 | 2020-07-13 09:52 | Communications and Control Systems - CCTV | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | This NCR has been raised to cover CCTV LAN camera cables that exceed 120m. No further works are required on site in relation to this NCR as Veracity Longspan Ethernet Extenders have been installed for all cables that exceed 120m.
| 03SR - Stations (RfL) | Cxxx-NCR-003499 | NCR | Urban Realm - E__ Level GL90-98 Roof Slab Waterproofing Failure |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-09-30 | 2021-04-14 07:25 | 196 | 2020-07-13 13:07 | Architectural - Roofing & Exterior Treatment | 15000 |  | Damaged | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | It was been brought to the attention of that water ingress is present within the main box structure east emergency escape staircase. Water can be seen on the soffit on this staircase structure which forms part of the roof slab within this area. As this slab is sealed and waterproofed externally, the only way for water ingress to be taking place is through some sort of damage and or penetration to the waterproofing in this area.
| 03SR - Stations (RfL) | Cxxx-NCR-003500 | NCR | Crack to Soffit in ESS II - Water Leakage |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-09-02 | 2021-04-27 13:18 | 237 | 2020-07-14 13:18 | Civil - Structural Engineering | 5000 |  | Damaged | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Cracks have been discovered in the soffit of the ESS II staircase at __. Water is leaking through from E__ above. This NCR is linked to Cxxx-NCR-003499.
| 03SR - Stations (RfL) | Cxxx-NCR-003501 | NCR | Staff Shower-toilet DDA compliance |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2020-08-03 | 2020-09-01 10:28 | 29 | 2020-07-20 15:19 | Architectural - Sanitary Fittings | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Shower unit and accessories have been installed that are not compliant with BS 8300 & B. Regulations Part M
| 03SR - Stations (RfL) | Cxxx-NCR-003502 | NCR | CCTV Marshalling box -damage to the IP Rating |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2020-08-05 | 2020-09-09 10:52 | 35 | 2020-07-22 08:47 | Communications and Control Systems - CCTV | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | hole drilled in the 2 x Marshalling Cabs on E__ CCTV Installation, attached email shows the pictures with issue
| 03SR - Stations (RfL) | Cxxx-NCR-003503 | NCR | Cavity Wall Inspection Hatch Spacing |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2020-08-11 | 2021-03-16 15:33 | 217 | 2020-07-28 13:58 | Architectural - General | 2500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Cxxx Cavity Wall Inspection Hatch Spacing Non-Conformance There are a number of installed cavity wall inspection hatches that have a spacing in excess of the maximum 10 metres allowed by approved Concession SP0371 (see Cxxx-XRL-A-QAP-B071-50001 attached). The Contractor is required to demonstrate that the cavity wall in these locations can still be satisfactorily cleaned, inspected and maintained using reasonable methods. The Contractor is also required to provide a marked up architectural general arrangement drawing to be inserted in the C&M strategy identifying the hatches that exceed the 10 metre limit required by the above Concession.
| 03SR - Stations (RfL) | Cxxx-NCR-003505 | NCR | UPS Battery Material Non-Compliance against LU S1-085 for rooms >200m3 |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2020-12-23 | 2021-02-12 11:28 | 51 | 2020-08-13 14:49 | Electrical - General | 25000 |  | Material | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | The material used for the outer casing of the __ XP6V2800 UPS batteries (found within rooms at PAD >200m3) has been found to be non-compliant with flammability and smoke emission requirements following __ flammability, smoke emission and toxicity testing. __ results attached. The smoke emission results in particular have been found to be exceptionally high, and as such, a concession against the relevant LU material standard will not be supported. This issue will need to be resolved to allow ATU to be achieved.
| 03SR - Stations (RfL) | Cxxx-NCR-003506 | NCR | Failing monitored doors |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2020-11-01 | 2020-10-30 15:56 | -2 | 2020-08-19 09:26 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | SCADA Door contacts test are failing for the following doors: PAD-D4-570MD22 failed due to magnet and door contact compatibility issue (magnet not strong enough to pull the DC closed) PAD-D2-90A-MD11 failed due to one of the leaves (90B) magnet and door contact compatibility issue (magnet not strong enough to pull the DC closed) PAD-D2-95A-MD32 failed due to one of the leaves (95A-B) magnet and door contact compatibility issue (magnet not strong enough to pull the DC closed)
| 03SR - Stations (RfL) | Cxxx-NCR-003507 | NCR | Damaged Telephones |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2020-09-04 | 2020-10-30 15:58 | 56 | 2020-08-21 07:56 | Communications and Control Systems - Telephony | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | No.14 Telephones were found damaged during a site survey for CRL Cxxx.
| 03SR - Stations (RfL) | Cxxx-NCR-003508 | NCR | Use of type B breakers in cotravention of the JY specification |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-10-01 | 2020-10-22 14:53 | 21 | 2020-08-20 12:39 | Electrical - Power Distribution | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Use of type B __ where the approved specification identifies type C __'s or higher indicating type D where required
| 03SR - Stations (RfL) | Cxxx-NCR-003509 | NCR | ECR V & VI Handrails - Incorrect Finish |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-09-09 | 2020-08-27 09:15 | -13 | 2020-08-26 13:41 | Architectural - Handrail | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | As per the __ F2 drawing ref.: Cxxx-SKC-Y-DDD-M171_Z-50118 Rev C03 approved by __, the colour of the handrails should have been PPC RAL 9005 (Jet Black). The handrails have in fact been delivered to site PPC RAL 1023 (traffic yellow).
| 03SR - Stations (RfL) | Cxxx-NCR-003510 | NCR | Incorrect Security Rating for Doors - D4-1019 and D2-700 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-12-05 | 2021-01-08 10:45 | 34 | 2020-08-27 07:40 | Architectural - Security | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Following a discussion with the CRL Lead Architect __ and through further investigation, it has been determined that the door schedule incorrectly states that doors D4-1019 and D2-700 are not required to have a security rating. These are FOH doors and until __ provide evidence on the contrary that they do not need to be security rated in accordance with the security statement for Cxxx, it is deemed to be a non-conformance. Please see attached zip folder with the information for the aforementioned doors.
| 03SR - Stations (RfL) | Cxxx-NCR-003511 | NCR | Incorrect Ironmongery to Doors on Escape Routes |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-10-17 | 2021-03-25 14:45 | 159 | 2020-08-28 13:35 | Architectural - Doors | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | It has come to light during an inspection by the fire engineers that some doors on escape routes have the facility to be locked and on some, lock upon shutting thereby preventing egress from one side. Following a RRM with __ the __ fire engineer confirmed that the ironmongery in fact is incorrect and free egress should be provided from both sides for evacuation purposes. Note this is a new issue and does not include any doors picked up in Cxxx-NCR-003144.
| 03SR - Stations (RfL) | Cxxx-NCR-003512 | NCR | Gridline 1 & 24 - overcrowded cable detail |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-10-30 | 2021-03-16 15:57 | 137 | 2020-09-22 16:09 | Fire - Compartmentation | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Along Gridline 1 & 24 on Intermediate & Concourse Levels there are a number of floor penetrations with overcrowded cable trunkings. Due to the limited space available within the trunking, we are not able to guarantee the internal firestopping has been completed to the approved detail. Total no. of affected details - 5no.: - INT west corridor - 1 x floor penetration - INT east corridor - 1 x floor penetration - CON west DR-WB I - 1 x floor penetration - CON east DR-WB II - 2 x floor penetration
| 03SR - Stations (RfL) | Cxxx-NCR-003513 | NCR | Scope Gap at BLKD-13 in the BLB - Cladding Interface with Fire Boarding and Doors - Trim Required |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-11-04 | 2020-11-25 06:29 | 21 | 2020-09-25 09:49 | Architectural - Finishes | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Following an inspection in the BLB, it was determined that there is a scope gap at BLKD-13 whereby the fire boarding behind is exposed. This is unacceptable with regards to the architectural finish and seems like the design has not been fully coordinated.
| 03SR - Stations (RfL) | Cxxx-NCR-003514 | NCR | Trip hazard at D2-697 threshold |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-10-09 | 2020-11-06 12:59 | 28 | 2020-09-25 13:25 | Architectural - Doors | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Interfacing problems | Completed |  | There was a trip hazard at the threshold of the D2-697 which would be unsafe for personal entering the corridor. There is a 30mm concrete lip protruding when enterning the BAT III corridor.
| 03SR - Stations (RfL) | Cxxx-NCR-003515 | NCR | Asset labelling - Alternative Asset IDs (approval of current label text line 3 content for L7172 - Valves ) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2021-03-12 | 2021-07-15 09:57 | 125 | 2020-09-30 17:58 | Information Management - Asset Information | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | Cxxx requesting approval of current label text line 3 content for L7172 - Valves (Absence of Design Alternative Asset ID) Leave all currently installed labels 'As Is' and produce all remaining labels consistently with previously installed labels for the L7172 -Valves Asset Class (No DAAID present on label). The Cxxx Asset Information Team has previously supplied L7172 - Valve labels to the installer (__) with the absence of a Design Alternative Asset ID (DAAID) on the third line of text on the label. This was due to there not being a finalised list of contractor IDs available at the time of ordering and installing the labels (from 2018 until now). As of recently, the finalised list of contractor IDs for all chilled water valves has been made available. It is also expected that similar IDs will be created for all Valves on other systems too with the exception of Fire Mains valves, which already have formal contractor IDs. In accordance with this updated Chilled Water Valve Schedule, which is contained on the same schedule as the Asset Tag Codes, the label installer has commenced installing their own separate ID labels on all valves alongside the asset labels (please see attached photos - green labels). Although it is expected that whenever a unique DAAID is available for an asset it should be contained on Line 3 of the Asset Label, this was not feasible for Cxxx, where labelling of valves began as early as 2018. We therefore propose that all existing valve labels that are installed without the DAAID on text line 3 of the label are deemed acceptable, furthermore all new valve labels requiring labelling in partial labelled systems are to be produced and installed consistently without the DAAID. There are currently 984 Asset Tags for valves that are in non-fire systems that are covered by the contents of this RFI. Of those 984 Asset Tags, 835 have already been labelled (without a DAAID present on the label), with a portion of these requiring re-labelling in the coming months due to changes to the CHW Valves Schedule.
| 03SR - Stations (RfL) | Cxxx-NCR-003516 | NCR | Issues with __ Doors (C10) - Remedial Works Required |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-10-31 | 2021-02-19 17:11 | 111 | 2020-10-01 10:08 | Architectural - Doors | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following inspections of the C10 doors manufactured and installed by __, there has been various items identified as requiring rectification such as bowing at the top of the doors, ironmongery requiring altering and caps missing over bolt holes. Please see attached list of items to be rectified.
| 03SR - Stations (RfL) | Cxxx-NCR-003517 | NCR | __ Doors - Ironmongery issues - Panic bar, espagnolet and door closers |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-10-31 | 2021-01-28 14:02 | 89 | 2020-10-01 10:20 | Architectural - Doors | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Following amendments to the __ doors on site to fit dampers and surrounding trims, ironmongery was required to be removed. This has been reinstated but is not performing as it should be and requires rectification. Also, the door closer on some of the doors is not closing the doors once opened due to the weight.
| 03SR - Stations (RfL) | Cxxx-NCR-003518 | NCR | Damaged Gate Hanger - West |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-11-10 | 2020-11-08 09:18 | -2 | 2020-10-01 10:31 | Architectural - Partitions | 5000 |  | Damaged | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | On the west gateline, a hanger has been damaged. This will require replacement.
| 03SR - Stations (RfL) | Cxxx-NCR-003519 | NCR | CIS Door Clashes - __ Gatelines |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-10-31 | 2020-11-12 09:01 | 12 | 2020-10-01 10:48 | Architectural - Partitions | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Upon installation of the CIS doors, clashes have been detected at both ends with the gateline. This will require rectification. The clashes are as follows: East: • Larger CIS door clashes with RSS hinge panel. Please see photo attached – See photo WA0002 for example. West: • Small Door Clashes with the top rail – Photo 0009 • Large Door Clashes with the RSS panel and hinges. This will also clash with the top of the track. Photo 111245. It is about 5mm discrepancy in the panels.
| 03SR - Stations (RfL) | Cxxx-NCR-003520 | NCR | Antenna Z4/ANT/002 has been broken |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-10-15 | 2020-11-16 16:49 | 32 | 2020-10-01 13:25 | Communications and Control Systems - Radio | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Antenna Z4/ANT/002 has already been handed over to Cxxx but has been damaged by the West folding gate.
| 03SR - Stations (RfL) | Cxxx-NCR-003522 | NCR | Discrepancy between stone cladding and EWS-117 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-10-15 | 2021-06-02 08:14 | 230 | 2020-10-01 16:07 | Architectural - Finishes | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Previous Construction - Other | Completed |  | There has been a lack of coordination between the EWS-117 & Stone cladding near GL 2 results in gaps in the façade.
| 03SR - Stations (RfL) | Cxxx-NCR-003523 | NCR | Cabling installed without a valid MCR |  | Contr | SKC | PAD - Paddington Station (West) |  | 2021-01-31 | 2021-03-16 20:22 | 44 | 2020-10-14 13:46 | Electrical - Power Distribution | 50000 |  | Material | Rework | 2 (6-60k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | During a site inspection an observation has been raised identifying potential different cable types that have been installed as part of the electrical install at Cxxx. An initial investigation has identified 3 different cable types installed without a valid MCR. The locations and systems affected are currently being tabulated and details of the cables installed are being collated also. The Contractor is working with their Subcontractor to identify any further material which may have been installed without a valid MCR.
| 03SR - Stations (RfL) | Cxxx-NCR-003525 | NCR | Canopy light fitting asset tags |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2020-11-06 | 2020-12-21 09:47 | 45 | 2020-10-23 14:36 | Architectural - Roofing & Exterior Treatment | 500 |  | Design | Reject | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Canopy downlights that are mounted on canopy structural beams have white asset tags applied to the dark grey light fitting. This is visually unacceptable and not compliant with CRL protocol which requires that asset labels in public facing areas shall be discretely located An alternative location on stainless steel CMS cover adjacent to each fitting, is available.
| 03SR - Stations (RfL) | Cxxx-NCR-003526 | NCR | __s Ltd. - Installation of DR EB Shaft Lanyard without Accepted ITP |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-11-23 | 2021-04-15 11:58 | 143 | 2020-10-24 07:55 | Architectural - General | 3000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The lanyard for the fall arrest/restraint system in the DR EB I & II shaft was designed and installed by __s and their certified installers. Pull tests were conducted, certificate of conformities have been issued and a report is forthcoming, but the works were installed without a code 1 accepted ITP.
| 03SR - Stations (RfL) | Cxxx-NCR-003528 | NCR | __ documentation - POM and PEW steelwork installation: Missing pull test results |  | Contr | SKC | PAD - Paddington Station (West) |  | 2021-05-11 | 2021-04-29 09:58 | -12 | 2021-04-27 13:32 | Structural Engineering - Structural Engineering - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the review of 5.12.24 Main Box – Items – POM and Pew machine steelwork and cladding installation pack, there were no evidence of pull test for installed anchor bolts
| 03SR - Stations (RfL) | Cxxx-NCR-003530 | NCR | Damaged telephones |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2020-11-13 | 2021-01-20 17:20 | 68 | 2020-10-30 10:48 | Communications and Control Systems - Telephony | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | No.3 phones were identified damaged on site. TEL 10103 TEL 10255 TEL 10326
| 03SR - Stations (RfL) | Cxxx-NCR-003531 | NCR | Intermediate Level Precast Planks - Lack of Fabrication Records (Ebor) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-11-29 | 2021-03-30 12:21 | 121 | 2020-10-30 14:09 | Civil - Civil Engineering General | 3000 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Through a review of the 1.27.2 SCC, it was determined that there is no fabrication ITP or records for the Ebor precast concrete planks to be installed at intermediate level.
| 03SR - Stations (RfL) | Cxxx-NCR-003533 | NCR | Intermediate West Skinny CSR - Incorrect Fabrication of Floor Grating |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-12-13 | 2020-11-20 15:40 | -23 | 2020-11-13 15:59 | Architectural - Flooring | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The skinny riser flooring was refabricated as part of PWK #1635 due to the changes in MEPH design leaving large empty BWIC's within the floor. The intermediate west skinny riser was incorrectly fabricated and as such will require alteration.
| 03SR - Stations (RfL) | Cxxx-NCR-003534 | NCR | slip resistance of flooring at platform level |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2021-01-02 | 2021-01-12 07:37 | 10 | 2020-11-15 15:57 | Architectural - Flooring | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | slip resistance testing has identified areas that do not meet the required value
| 03SR - Stations (RfL) | Cxxx-NCR-003535 | NCR | Incorrect Paint Application to Exposed CAT Ladders in VSHH |  | Contr | SKC | PAD - Paddington Station (West) |  | 2021-01-21 | 2020-12-21 13:32 | -31 | 2020-11-16 15:04 | Architectural - Finishes | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | It has been determined that the manufacturers guidelines on the paint install to the CAT ladders and exposed support steelwork at mezzanine level in the VSHH has not been followed with regards to preparation of the galvanised steel. This NCR has been linked to NCR #3457 to allow its closure once all other works are complete.
| 03SR - Stations (RfL) | Cxxx-NCR-003536 | NCR | Step Over Chiller Farms Pipes (Cxxx-NCR-003431 - PAC-36) Clash with Chiller Farm Hoods |  | Contr | SKC | PAD - Paddington Station (West) |  | 2021-03-23 | 2021-02-23 16:20 | -28 | 2020-11-16 15:10 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The chiller farm hoods are required to be replaced/altered due to the clash with the step over the pipework. The step over cannot be altered so hoods must change.
| 03SR - Stations (RfL) | Cxxx-NCR-003538 | NCR | No Coordination Between Stainless Steel PAE Covers & Services within the enclosure. |  | Contr | SKC | PAD - Paddington Station (West) |  | 2021-04-05 | 2021-04-28 07:14 | 23 | 2020-11-16 16:15 | Architectural - Finishes | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Following works were not coordinated: • Platform West; No Services and requires full hinged door with no cut-outs • Platform East; No Services and requires full hinged door with no cut-outs • Escalator 7 – New S/S Door Required to be detailed. • Escalator 11 – New S/S Door Required to be detailed. • BLB – 1No. Stainless steel door required.
| 03SR - Stations (RfL) | Cxxx-NCR-003540 | NCR | Installation of __ Doors without an approved ITP |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-12-03 | 2020-12-15 11:09 | 12 | 2020-11-19 16:04 | Architectural - Doors | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Installation of __ Doors without an approved ITP. D2-93 - Cxxx-SKC-Y-DDL-M171_2-32334 D2-94a - Cxxx-SKC-Y-DDL-M171_2-32333 D2-95a - Cxxx-SKC-Y-DDL-M171_2-32332 D2-90a - Cxxx-SKC-Y-DDL-M171_2-32337 D2-91 - Cxxx-SKC-Y-DDL-M171_2-32336 D2-92 - Cxxx-SKC-Y-DDL-M171_2-32335 The doors were installed by __ who have supplied the attached Installation Checksheets WD-43. Manufacture of the doors is covered in MCR Cxxx-SKC-O-TSC-B071_WS077-51768.
| 03SR - Stations (RfL) | Cxxx-NCR-003541 | NCR | Matwell Benchmarks sample |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-12-18 | 2021-01-20 15:05 | 33 | 2020-12-10 13:15 | Architectural - Flooring | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Matwell Bench mark sample not completed
| 03SR - Stations (RfL) | Cxxx-NCR-003542 | NCR | Use of Non-Fire cable for connection of PLC Field Devices |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-12-06 | 2021-02-19 16:34 | 75 | 2020-11-22 20:51 | Communications and Control Systems - General | 25000 |  | Design | Rework | 2 (6-60k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | A issue has been raised that the currently installed __ YE00381 data cable (CRL-MCR-003712) should not be used for life safety systems, as per the CEG review on the MCR. This cable has been installed between the 4 PLCs and life safety equipment such as smoke exhaust fans, air release fans and associated dampers. Control of hvac systems including cable requirements are outlined in CRL1-XRL-M-RSP-CR001-50110 - Rev 2.0 - Control of HVAC Services in a Fire Alarm Situation (STATIONS).
| 03SR - Stations (RfL) | Cxxx-NCR-003543 | NCR | Installation without ITP and checksheets – __ - Screeding (inc. Hatch Install), Tiling (FoH Only) and Vinyl Works |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-12-08 | 2021-01-04 10:24 | 27 | 2020-11-24 08:17 | Architectural - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Upon review of documentation for 5.8.20 - Main Box – Screeding (inc. Hatch Install), Tiling (FoH Only) and Vinyl Works – Site Wide It has been noted that __ didn’t produce checksheets and an updated ITP wasn’t created to cover the works (Cxxx-SKC-Z-ITP-B071_WS077-50007) These areas are: Tiling - Lift 8/9 – Intermediate Hatches in floor - Esc. 10/11 - Departures Road Vinyl flooring is in the following rooms: - SMK (intermediate) - STR II (intermediate) - GSM (intermediate) - __F I & II (intermediate & concourse) - SOR (intermediate) - SCR I & II (intermediate) - SLR-F & SLR-M (Intermediate) - Bakerloo box stairs - screed and tiling needed (PWK-01583) LER V __ hatches outside HFT1 Esc. 10/11 - Platform - missing documentation is covered under Cxxx-NCR-003329
| 03SR - Stations (RfL) | Cxxx-NCR-003544 | NCR | Use of undersized cable for connection of field device i/o |  | Contr | SKC | PAD - Paddington Station (West) |  | 2021-02-25 | 2021-02-19 16:37 | -6 | 2020-11-22 21:07 | Communications and Control Systems - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | A issue has been raised that no engineering calculations have been performed to verify the suitability of the size of the installed __ YE00381 data cables (CRL-MCR-003712). These data cables have been used throughout the 4 PLCS associated with MCC01-MCC04, as well as the portions of the BMS cabling.
| 03SR - Stations (RfL) | Cxxx-NCR-003545 | NCR | OHLE 1 Fire door FD rating not aligned with Fire strategy drawings |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2020-12-10 | 2021-01-27 10:48 | 48 | 2020-11-26 08:53 | Architectural - Doors | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Arch VAP inspection 25.11.20 noted D4-664 FD Certifire tag states FD60 which does not align with 120 mins fire compartment rating indicated on Fire Strategy drawing Cxxx-SKC-A-DDE-M171_4-32703
| 03SR - Stations (RfL) | Cxxx-NCR-003546 | NCR | OHLE II D4-668 FD60 does not align with 120 mins compartment indicated in Fire strategy |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2020-12-10 | 2021-01-27 10:45 | 48 | 2020-11-26 09:22 | Architectural - Doors | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | D4-668 doorset certifire tag FD60 noted on site inspection 25.11.20, does not align with 120mins compartment indicated on Fire Strategy drawing Cxxx-SKC-A-DDE-M171_4-42703. This door opens directly on to circulation corridor CIR-PL-IV.
| 03SR - Stations (RfL) | Cxxx-NCR-003547 | NCR | Bakerloo line level wall cladding Tethers not fitted. |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2021-02-12 | 2021-02-19 16:59 | 7 | 2020-12-03 14:35 | Architectural - Walls | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Security site inspection 02.12.20 noted 2no wall panels temporarily removed for MEP works. This revealed that required wall cladding tethers are missing. This is not acceptable .
| 03SR - Stations (RfL) | Cxxx-NCR-003548 | NCR | BLL GFRC panels top -recess metal inclined panels have insufficient slope to meet security reqmts |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2021-02-18 | 2021-02-03 09:17 | -15 | 2020-12-03 15:01 | Architectural - Walls | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following a security inspection of 2.12.20 Inclined metal panels to high level recess above BLL GFRC adit panels have insufficient gradient ( 30 degrees minimum to ensure that thrown items roll off.
| 03SR - Stations (RfL) | Cxxx-NCR-003549 | NCR | BLL adit ceiling panels Tethers missing |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2021-03-11 | 2021-02-23 13:55 | -16 | 2020-12-04 08:28 | Architectural - Ceilings & Soffits | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient work planning by the subcontractors | Completed |  | CRL Rfl site visit of 2.12.20 noted soffit panels, opened for MEP connection, did not have tethers fitted. Not acceptable ~
| 03SR - Stations (RfL) | Cxxx-NCR-003550 | NCR | Benchmark not provided as part of Suspended Signs Certification (W&W) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-12-23 | 2021-01-21 15:46 | 29 | 2020-12-09 11:34 | Architectural - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Upon review of documentation provided by __; benchmark for the following types of Suspended Signs wasn’t provided before the works where started. Horizontal Directional sign – SGN-209 USN 335 Platform Level, Grid C13 340a Platform Level, Grid D16 340b Platform Level, Grid B16 700 Level 7, Grid C12-13 352 Platform Level, between Grid Line 13 and BLL Lift 353 Platform Level, between Grid Line 13 and BLL Lift Horizontal Directional sign – SGN-222 701 Level 7, Tunnel Link Entrance, D13 707 Level 7, Tunnel Link Entrance, D13 Combined Fire Hydrant and Help Point Sign – SGN-223 - USN-605 Platform Level, Grid D10 Combined Illuminated Fire Hydrant and Help Point Sign with Integrated Luminaire SGN-223 - USN-608 - Platform Level, Grid B10 Benchmark for Sample inspection – First Fix Required Signage was produced and excepted
| 03SR - Stations (RfL) | Cxxx-NCR-003551 | NCR | __ Doors - Benchmark Outstanding |  | Contr | SKC | PAD - Paddington Station (West) |  | 2020-12-23 | 2021-01-07 09:54 | 15 | 2020-12-09 15:23 | Architectural - Doors | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Works for the __ doors on Departures Road were installed without an agreed and signed off Benchmark in place.
| 03SR - Stations (RfL) | Cxxx-NCR-003552 | NCR | Glass Damaged - Sign USN 617 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2021-02-18 | 2021-03-16 15:34 | 26 | 2020-12-10 12:02 | Architectural - Signage | 5000 |  | Damaged | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | One glass and carrier panel has been broken on projected hydrant signs USN 617 (Grid D 13-14). Projected bracket and Frame remain installed until the broken glass and Al runner replaced. This was found broken whilst stored on site.
| 03SR - Stations (RfL) | Cxxx-NCR-003553 | NCR | QA inconsistencies - IRn 175 & 176 |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2020-12-25 | 2020-12-21 13:05 | -4 | 2020-12-11 14:21 | Fire - Detection | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During CEG review of IRN 175 & 176 the following irregularities were observed IRN 175 Conceptual design statement was not listed - this is now listed in AC-07 Cxxx-SKC-O-CER-B071_WS077-50687 Design Certificate was listed as a placeholder - this is now listed in AC-07 Cxxx-SKC-O-CER-B071_WS077-50687 Installation Certificate was listed as a placeholder - this is now listed in AC-07 Cxxx-SKC-O-CER-B071_WS077-50687 The above weren't listed as COWLs IRN 176 Conceptual design statement was not listed - this is now listed in AC-07 Cxxx-SKC-O-CER-B071_WS077-50687 Design Certificate was listed as a placeholder - this is now listed in AC-07 Cxxx-SKC-O-CER-B071_WS077-50687 Installation Certificate was listed as a placeholder - this is now listed in AC-07 Cxxx-SKC-O-CER-B071_WS077-50687 The above weren't listed as COWLs
| 03SR - Stations (RfL) | Cxxx-NCR-003554 | NCR | Door, SID, Hydrant & Statutory Signage Installation Benchmark sample |  | Contr | SKC | PAD - Paddington Station (West) |  | 2021-01-08 | 2021-01-04 13:24 | -4 | 2020-12-17 11:44 | Architectural - Signage | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Door, SID, Hydrant & Statutory Signage Installation Benchmark sample not completed
| 03SR - Stations (RfL) | Cxxx-NCR-003555 | NCR | Urban Realm - Praed Street Junction Work Missing MCR Approval |  | Contr | SKC | PAD - Paddington Station (West) |  | 2021-01-08 | 2021-01-08 12:07 | 0 | 2021-01-08 10:42 | Civil - Civil Engineering General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | During the construction of the external works installation at the Praed Street junction upgrade, works progressed and material were used prior to MCR being raised and approval given. The following material used at listed below and have now been captured with the relevant MCR, noting that these MCR's are all now approved for use; Cxxx-SKC-O-TSC-B071_WS077-51807 - 750X600 ASP concrete slabs (WCC) Cxxx-SKC-O-TSC-B071_WS077-51789 - Marshalls 400x400x65 Tactile Paving Cxxx-SKC-O-TSC-B071_WS077-51774 - NAL Retention Sockets Cxxx-SKC-O-TSC-B071_WS077-51805 - Keep left bollards note that these are all approved Westminster City Council material.
| 03SR - Stations (RfL) | Cxxx-NCR-003557 | NCR | QA - Fire Detection and Alarms IRN reference incorrect certificate document number |  | Contr | SKC | PAD - Paddington Station (West) |  | 2021-01-28 | 2021-01-26 08:56 | -2 | 2021-01-14 12:42 | Fire - Fire Systems & General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | During CEG review of Fire Alarm and Detection System IRNs associated with Cxxx-XRL-O-XCS-B071_WS077-50021 Conceptual design statement was not listed - this is now listed in AC-07 Cxxx-SKC-O-CER-B071_WS077-50687 Design Certificate was listed as a placeholder - this is now listed in AC-07 Cxxx-SKC-O-CER-B071_WS077-50687 Installation Certificate was listed as a placeholder - this is now listed in AC-07 Cxxx-SKC-O-CER-B071_WS077-50687
| 03SR - Stations (RfL) | Cxxx-NCR-003558 | NCR | LFO VI water leak, VSHH east |  | Crossrail | PDP | PAD - Paddington Station (West) |  | 2021-02-28 | 2021-10-19 13:12 | 233 | 2021-01-15 14:21 | Architectural - Roofing & Exterior Treatment | 5000 |  | Damaged | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During a routine inspection by CRL on the 14.01.2021 a waterleak was found in the soffit of the Intervention Lift Lobby east, upon further investigation a serious waterleak was identified in the LFO VI which is directly above the intervention lobby. At the time no access was available to the area above LFO VI however water damage is noted to fire stopping, ductwork, lagging, MEP and boarding in the soffit of this room. This water leak was identified during a site visit between CRL and on the 18.11.2020 to view firestopping, an NCR was requested to be raised by but it has not hence CRL raising.
| 03SR - Stations (RfL) | Cxxx-NCR-003559 | NCR | Missing checksheet 5.23.2, BOH Suspended Ceiling AND Acoustic Ceilings |  | Contr | SKC | PAD - Paddington Station (West) |  | 2021-01-29 | 2021-03-31 13:01 | 61 | 2021-01-19 13:34 | Architectural - Ceilings & Soffits | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | • BOH Suspended Ceilings Location (GSM, SOR, __F, SMK, SLR-F, SLR-M, LB-W, SWC1, SWC2, SSR. Concourse __F1 Platform TEP, SWCIII) Works period form Feb 2018 to Sep 2018 • Acoustic Ceilings Location CIR PI Works period Apr- May 2018
| 03SR - Stations (RfL) | Cxxx-NCR-003560 | NCR | Internal fire stipping of conduits |  | Contr | SKC | PAD - Paddington Station (West) |  | 2021-05-12 | 2021-05-23 12:47 | 11 | 2021-01-19 14:54 | Fire - Compartmentation | 2500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Conduits not installed with sufficient gap to incorporate Fire Stopping
| 03SR - Stations (RfL) | Cxxx-NCR-003561 | NCR | Low level damper motor is not accessible in TR-II CWU (VAP 96) - AC-014 |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2021-02-04 | 2021-03-09 11:46 | 33 | 2021-01-21 11:45 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Location: TR-II CWU Ref.: VAP item 96 The corner of the room to the right of CCU is too congested - the low level shut off damper motor can not be safely accessed or maintained (ref. CCU01/TR II - supply shut off damper). Refer to attached photos.
| 03SR - Stations (RfL) | Cxxx-NCR-003562 | NCR | High level fire damper and fire damper interface panel is not accessible in TR-II CWU (VAP 96) |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2021-03-31 | 2021-05-23 12:50 | 53 | 2021-01-21 11:53 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Location: TR-II CWU Ref.: VAP item 96 The corner of the room to the right of CCU is too congested - the high level fire damper (ref. (FD30/AHU01/W) and interface panel can not be safely accessed or maintained. Refer to attached photos.
| 03SR - Stations (RfL) | Cxxx-NCR-003563 | NCR | Paddington - Insufficient Fire Detection coverage in 4/232 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2021-02-28 | 2021-02-15 11:27 | -13 | 2021-01-21 15:48 | Fire - Detection | 1500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | There is insufficient Fire Detection coverage in 4/232 due to high level duct work fitted tight to the slab. The ductwork is effectively acting as an obstruction and reducing the coverage between the 2 detectors, as the top of the duct is less than 300mm it should be treated as a wall under the recommendations of BS 5839-1.
| 03SR - Stations (RfL) | Cxxx-NCR-003564 | NCR | BLL stair safety - balustrade height & handrails |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2021-06-08 | 2021-12-08 17:44 | 183 | 2021-05-25 13:10 | Architectural - Handrail | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Refer also NCR 3276 now closed (included security issues.) now Safety issues have not been resolved .1 Handrail is not compliant at landings -BS 8300 5.10.2 (b) continuously graspable along its entire length 2. Height of balustrade at top landing/ top flight is installed with lower/ upper handrail combination that could be climbed by children. Ref BS 8300 5.10.1 For all buildings used by the general public and buildings designed principally for children, a second handrail should be installed with its top surface 600 mm from the ramp surface or pitch line. Where necessary, structural guarding should be provided of sufficient height to prevent a child falling if they climb on the handrail.
| 03SR - Stations (RfL) | Cxxx-NCR-003565 | NCR | BOH Suspended Ceilings being installed with incorrect brackets |  | Contr | SKC | PAD - Paddington Station (West) |  | 2021-04-01 | 2021-04-01 08:05 | 0 | 2021-01-25 10:29 | Architectural - Ceilings & Soffits | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | BOH Suspended Ceilings being installed with incorrect brackets according to C drawings (element 1 Emac Hanger) Cxxx-SKC-Y-DDF-M171_3-31001 Main Box - West Intermediate Level Reflected Ceiling Plan - BOH Cxxx-SKC-Y-DDF-M171_3-31002 Main Box - West Intermediate Level Reflected Ceiling Grid Plan - BOH Cxxx-SKC-Y-DDF-M171_4-31020 Main Box - West Concourse Level Reflected Ceiling Plan - BOH Cxxx-SKC-Y-DDF-M171_5-31020 Main Box - West Platform Level Reflected Ceiling Plan - BOH
| 03SR - Stations (RfL) | Cxxx-NCR-003566 | NCR | Concourse totems Cxxx PAVA speakers bracket clash |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2021-02-12 | 2021-06-15 15:43 | 123 | 2021-01-29 10:59 | Architectural - Signage | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | 4no concourse level totems each have 2no speakers concealed behind the totem grille enclosure, The internal totem brackets for mounting the speakers are not compatible with the required Cxxx speaker orientation. This also prevents installation of the grille. .
| 03SR - Stations (RfL) | Cxxx-NCR-003567 | NCR | STR1-Cxxx Comms space - projecting damper hazard |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2021-02-25 | 2021-05-11 14:02 | 75 | 2021-01-29 15:05 | Architectural - Walls | 500 |  | Design | Reject | 4 (0.5-3k) | Complete | Design Problem - Inadequate man -machine interface | Completed |  | The new fire rated enclosure for Cxxx equipment, located in the corner of concourse level STR I, has a low level ventilation damper installed which projects into the new space adjacent to the door opening. The projection may cause injury on entering the space or a trip hazard if maintaining the Cxxx equipment Cxxx have advised that it intrudes on the space necessary to access/ maintain their equipment.
| 03SR - Stations (RfL) | Cxxx-NCR-003569 | NCR | ESCR III Door / Tiling Clash |  | Contr | SKC | PAD - Paddington Station (West) |  | 2021-02-19 | 2021-03-12 14:19 | 21 | 2021-02-05 11:06 | Architectural - Doors | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The Tile level is incorrect causing the door leaf to hit the floor. The door was snagged but still a requirement to lift the doors as this is causing further issues with closing. The door will be required to be installed higher to avoid the floor.
| 03SR - Stations (RfL) | Cxxx-NCR-003570 | NCR | AC-024 - Faulty VFC Cable to Lift Emergency Distribution Board |  | Contr | SKC | PAD - Paddington Station (West) |  | 2021-03-31 | 2021-04-20 09:51 | 20 | 2021-02-16 11:40 | Mechanical - Lifts | 2500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During Form54 Testing of Lift 10 Firefighters Lift on 22.01.21 it was observed that during the emergency distribution board test (with both 'A' and 'B' ATS supplies isolated) the lift batteries failed to operate and return the lift to the next available floor.
| 03SR - Stations (RfL) | Cxxx-NCR-003571 | NCR | __ Inspection of site applied M24 coating system to site welded joints |  | Contr | COS | PAD - Paddington Station (West) |  | 2021-03-17 | 2021-07-08 08:32 | 113 | 2021-03-03 14:47 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A __ M24 corrosion protection paint system (M24/014) was applied off site at __ Surface Treatment. Joints to be site welded were masked after blast cleaning and prior to painting, stepped back at 50mm per coat. The same M24 system was applied to these areas on site after welding. At assurance stage of the project, no dry film thicknesses (DFTs) could be found. Specification/Contract Requirement: Surface preparation: ISO 8501:1 Sa 2.5 Paint system: a. Macropoxy M902 @ 100 microns b. Macropoxy M902 @ 100 microns c. Acrolon C137 @ 50 microns The contractor responsible for the works (__) consulted __'s qualified paint inspector to carry out DFTs for the onsite welded joint areas of the Paid, Unpaid and BLL lifts. 1. At the inspection, some localised areas were found to have reading below the required 250 microns. 2. Also to be noted were several chips in paint on the unpaid lift, in some cases exposing the steel substrate. As per to the issued report Cxxx-SKC-O-RGN-B071_WS077-50461, the paint inspector deems the works as acceptable as follows: "According to ISO 19840 individual readings of 80% of the specified thickness are deemed acceptable as long as these readings account for less than 20% of the readings taken within a sample area. Given that the site application itself represents only a small proportion of the surface area of the lift, this is certainly the case. Whilst there are very localised areas that fall well out of specification in terms of lowest readings obtained they represent a tiny proportion of the overall coated surface area".
| 03SR - Stations (RfL) | Cxxx-NCR-003573 | NCR | Departures Rd Bin store lack of impact protection to installed services |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2021-03-19 | 2021-05-04 13:44 | 46 | 2021-03-05 13:11 | Architectural - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Installed drainage and chilled water services are at risk of impact damage from loaded refuse bins when the bin store is operational. refer attached photo
| 03SR - Stations (RfL) | Cxxx-NCR-003574 | NCR | __ Escalator Skirt Lighting Faulty Drivers |  | Contr | SKC | PAD - Paddington Station (West) |  | 2021-05-26 | 2021-05-17 15:17 | -9 | 2021-05-12 08:15 | Electrical - Lighting | 5000 |  | Manufacturing Defect | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | A fault has been observed with the escalator skirt lighting, when __ attempts to change the state of the lights via the LCS, i.e. by switching, dimming or during addressing and commissioning works. Fault causes the system to “lock out” and isolate the supply from the driver to the DALI interfaces and in turn the LED outputs. It is then necessary to power cycle the mains supply voltage to the drivers in order to reset them. Issue to be resolved with framework contractor to allow the final T&C and interface with DALI/ __. (Fault is project wide.) Cxxx-PWK-01710 AC-018 - Escalator Lighting can be superseded by this NCR, due to prevention of final T&C and requirement to retest upon resolution or installation of new drivers.
| 03SR - Stations (RfL) | Cxxx-NCR-003575 | NCR | Single Point of Failure of station lighting systems |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2021-03-31 | 2021-05-17 15:18 | 47 | 2021-03-17 12:00 | Electrical - Lighting | 25000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | During a CEG review it was discovered that there were various areas across the station where the loss of a single circuit plunged the sopace into darkness. the station has A & B and emergency supplies and therefore there should always be an alternative circuit in a space.
| 03SR - Stations (RfL) | Cxxx-NCR-003576 | NCR | Lux level failures - Normal and Emergency |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2021-05-31 | 2021-05-28 08:29 | -3 | 2021-03-17 12:03 | Electrical - Lighting | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | During lux level testing various areas have shown to be substandard in terms of normal and emergency lux levels
| 03SR - Stations (RfL) | Cxxx-NCR-003577 | NCR | Lux level measurements during UPS discharge test |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2021-03-31 | 2021-08-05 11:02 | 127 | 2021-03-17 12:36 | Electrical - Lighting | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Cxxx-PMI-1661 required a test script to be followed to measure lux levels before and after UPS battery discharge testing. This script was followed in part but various omissions are apparent
| 03SR - Stations (RfL) | Cxxx-NCR-003578 | NCR | Camera 138 damaged Bracket and cam is offline |  | Contr | SKC | PAD - Paddington Station (West) |  | 2021-07-30 | 2021-07-09 12:37 | -21 | 2021-03-17 17:01 | Communications and Control Systems - CCTV | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | Cam 138 bracket has been damaged and CAM 138 is currently off line
| 03SR - Stations (RfL) | Cxxx-NCR-003579 | NCR | __ Conduit & fixing Incident |  | Contr | SKC | PAD - Paddington Station (West) |  | 2021-04-02 | 2021-06-15 15:46 | 74 | 2021-03-19 11:29 | Architectural - Walls | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | On the 17/02, there was an incident bought to the attention of the Subcontractor that there was a fixing that had damaged a conduit and a cable inside. This occurred on the east __ adjacent to D2-698. Further mitigation to stop this occurring again are being investigated.
| 03SR - Stations (RfL) | Cxxx-NCR-003580 | NCR | Cavity wall drainage channel debris / blocked downpipe |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2021-07-20 | 2021-07-20 22:48 | 0 | 2021-03-22 08:28 | Civil - Drainage | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | Arch VAP inspection of cavity wall access hatches, Friday 19 March TVF I intermediate level West wall grid 19 LH drainage outlet is blocked seepage water backed up. Hatch on Grid E debris in scupper with minor seepage water salts building on debris Comprehensive cleanout required / recorded and check made of all hatches all levels not accepted on Arch VAP
| 03SR - Stations (RfL) | Cxxx-NCR-003581 | NCR | Cast in drainage blockages - CCTV Survey |  | Contr | SKC | PAD - Paddington Station (West) |  | 2021-05-13 | 2021-04-30 09:56 | -13 | 2021-04-29 12:07 | Mechanical - Public Health Engineering | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Cast in Drainage pipe blockages have been located from the drainage CCTV Survey carried out under Cxxx-PMI-01740. Due to the types of the blockages, standard water jetting for clearing debris is not a sufficient method and will require further specialist intervention via cutting and rodding. Blockage 1: Concrete debris blockage has been located in 0.9m into the sub platform invert SPR I 6/781 cast in drainage, connected to west critical sump. Blockage is contained within the branched connection before the mainline, confirmed from surveys upstream down to the sump. Blockage 2: Pipe Blockage located 1.6m into the Sub platform invert 6/900. cast in drainage, connected to west critical sump. See attached cast in drainage layouts for location
| 03SR - Stations (RfL) | Cxxx-NCR-003582 | NCR | Concourse Access Hatch - Series 5000 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2021-06-29 | 2021-07-13 10:20 | 14 | 2021-05-06 14:22 | Architectural - Doors | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | The highway standard __e 5000 series hatches specified by Weston Williamson on the concourse at gate lines CON-P I and CON-P II were installed without an MCR being raised for the item. Hatches were required that could accommodate a 28mm floor tile and the __e 5000 series hatches could provide the required depth and structural integrity as outlined in -RFI-002959.
| 03SR - Stations (RfL) | Cxxx-NCR-003583 | NCR | Battery Failure |  | Contr | SKC | PAD - Paddington Station (West) |  | 2021-07-28 | 2021-08-10 13:46 | 13 | 2021-04-29 12:07 | Electrical - LV Equipment | 500 |  | Equipment Breakdown | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | During the UPS discharge test it was noted that the UPS system had failed during discharge and switched back into charging mode. after further investigation by __ it was identified the two batteries had failed within rack one 23/4/21 - During Drain test with __ Engineer it was identified that 2 Batteries on the East Lighting UPS Battery String 1 had failed and were recommended for replacement. 5/5/21 - __ attended site with and the 2 batteries identified were replaced and a drain down test commenced after charging the batteries for 120 minutes. A Drain down test was commenced which failed after 50 minutes, a check on the batteries was done which identified a further 18 with voltage levels below the recommended 4.9V. __ recommend complete battery change. 26/5/21 - __ returned to site with 3 batteries (all that were available) and replaced out for faulty ones, batteries left on charge ahead of performing a drain down test. 27/5/21- Drain Down test performed which failed after 120 minutes. All existing batteries on String 1 and 2 to be changed as well as the addition of a third battery string (Programmed to be fitted week commencing July 13 2021)
| 03SR - Stations (RfL) | Cxxx-NCR-003584 | NCR | Bronze cladding delaminating from 3No. Doors. |  | Contr | SKC | PAD - Paddington Station (West) |  | 2021-11-24 | 2021-11-24 16:23 | 0 | 2021-04-30 16:06 | Architectural - Doors | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | The bronze sheets on the doors are delaminating from the door. D5-101 - Bottom left corner D5-102 - Top Right Corner D4-72b - Right Lower leaf
| 03SR - Stations (RfL) | Cxxx-NCR-003586 | NCR | 5.6.17 - Works undertaken without an approved ITP |  | Contr | SKC | PAD - Paddington Station (West) |  | 2021-06-03 | 2021-05-28 08:45 | -6 | 2021-05-20 10:40 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The contractor (__/) undertook the Misc Installation Metalworks without an approved ITP in place including These are the areas: ECR V VI goalpost finishes - Departures Road 2x Flashing Concourse West Install Grillage over the Vent Shaft - VSHH Metal Modules (1no. Bench with Roundel) GL13 Platform Folded Aluminium Box Out - Concourse GL9 South __F I; Intermediate GL10.5 SMK, GL10 GSM, GL9.5 __F II Skirting - 2.5m Barrier - Skirting to Baseplates – Platform Handrail to Stairwell LER V BLL Mesh Infill to Large Opening within South Wall Handrail Around Pump in Corridor MNS III – Departures Ladder Install to GL 20 Raised Access Floor Area Lift 10 and 11 Grille Installation – Platform E__ - Chiller Farm Ladders E__ - Chiller West - External additional Flashing Installation E__ - Chiller West - Landing Grating to be Galvanised Entrance Gates - DR - __ Cladding above CIS Doors SI-041/045- CCTV Bracket for Totem SI-042 - Housing for Leading Edge Sensor (Column Cladding) Works have been steadily been inspected by / CRL and IRF have been signed accordingly
| 03SR - Stations (RfL) | Cxxx-NCR-003587 | NCR | Paddington - Water Mist nozzle obstruction in Bin Store 2/400 |  | Contr | SKC | PAD - Paddington Station (West) |  | 2021-06-15 | 2021-06-30 09:28 | 15 | 2021-06-01 10:40 | Fire - Suppression | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Not Defined | Completed |  | Following the installation of aluminium cladding around the chilled water pipe in Bin Store 2/400 it created an obstruction for a Water Mist nozzle within the room.
| 03SR - Stations (RfL) | Cxxx-NCR-003588 | NCR | Surge Protection not installed at Comms DBs |  | Contr | SKC | PAD - Paddington Station (West) |  | 2022-03-18 | 2022-03-07 09:21 | -11 | 2022-03-04 09:48 | Electrical - General | 2500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Surge protection has not been installed on Comms DBs and Comms Control to Cross passages in line with Cxxx-SKC-E-DDE-M171_Z-30514 and Cxxx-SKC-E-DDE-M171_Z-40517.
| 03SR - Stations (RfL) | Cxxx-NCR-003589 | NCR | Departures Road - Water Damaged CMS |  | Contr | SKC | PAD - Paddington Station (West) |  | 2021-07-07 | 2021-07-13 13:18 | 6 | 2021-06-23 11:55 | Electrical - Cable Management | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Weather or ambient condition | Completed |  | The CMS has been damaged by rainwater in two locations: East emergency staircase at Departures road level (PAVA Trunking) and Riser 1016 at Departures road West (radio tray, general comms & power / lighting) via opened access hatch to the west chiller farm.
| 03SR - Stations (RfL) | Cxxx-NCR-003592 | NCR | PXR02 4D Coffer lighting not tagged and labelled |  | Contr | COS | PAD - Paddington Station (West) |  | 2021-07-26 | 2021-09-03 10:06 | 39 | 2021-07-12 17:19 | Information Management - Asset Information | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Bespoke Coffer lighting manufactured by 4D Lighting Ltd has been installed at Paddington station and consists of 2no parts to the system; the architectural element being a Bespoke Circular LED Box/Flat Coffer luminaire - Type PXR01, and a concealed downlighter located above above the Circular LED Box/Flat Coffer luminaire - Type PXR02. The asset engineering team has listed both the PXR01 and the PXR02 elements as a singular asset: Bespoke Circular LED Box/Flat Coffer luminaire - PXR01. These have tagged and labelled as such. Type PXR02 should be identified, tagged and labelled as separate luminaires under L Class L74731 - Fixed luminaires for general lighting, but this exercise has not been carried out. It is accepted by that the Coffer Lighting by 4D Lighting Ltd comprises of two elements and should have been tagged and labelled as such. It is to be noted however that the PXR02 is concealed and therefore labelling of these assets would bring little benefit to the maintainer as they will have to remove the Type PXR01 to access the PXR02 for maintenance activities. It is ther3efore proposed that these PXR02 assets are detailed within AIMS information, but request a dispensation from having to label these assets due to the time and costs of undertaking the exercise of labelling 301no assets at high level by removal and reinstatement of the PXR01 luminaires beneath.
| 03SR - Stations (RfL) | Cxxx-NCR-003593 | NCR | Broken Glass - West Concourse PAE Enclosure box (Front Panel) |  | Contr | SKC | PAD - Paddington Station (West) |  | 2021-08-16 | 2021-09-09 06:37 | 24 | 2021-08-02 13:12 | Architectural - Finishes | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Whilst __ where snagging the West Concourse PAE Enclosure, the glass shown in the attached photos shattered.
| 03SR - Stations (RfL) | Cxxx-NCR-003596 | NCR | L7515 Air Handling Unit (AHU) breakdown not broken down into component parts on AIMS |  | Contr | COS | PAD - Paddington Station (West) |  | 2021-08-31 | 2021-09-16 16:45 | 16 | 2021-08-17 17:59 | Information Management - Asset Information | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The current AD4 description as set out in CRL1-XRL-Z3-ADDSD-CR001-50113 Rev 9 L7515 - Air Handling Unit (AHU) states that "Air Handling Unit (AHU) is a device used to condition and circulate air as part of a heating, ventilating, and air-conditioning (HVAC) system. They are either integral devices with all functions part of the core unit or are supplied as modular units attached to each other. They will typically provide more than one HVAC function e.g. air movement, heating, cooling, filtration and will have no sections of ducting between these functions. The maintainable items within the Air Handling Unit shall be tagged and labelled (as required) as separate items, these include the individual fans, filters etc.". The function of an AHU is to supply conditioned air. As detailed above, there are no sections of ducting between these components hence they are a single entity. The components within the AHUs are integral to the system as a whole not as individual components. If a maintainable component breaks within the AHU, the unit will not function and will switch to the standby unit. All components (fans, motors etc.,) are sourced or manufactured by the manufacturer of the AHU which is where the IM is able to procure replacement parts should they be required for either planned or reactive maintenance. The purpose and requirement for asset identification is to make the maintenance of the units simple. The IM should be directed to one source of information from one asset tag (not numerous ones). Please note that filters are considered consumables and are not asset identified. Cxxx originally created AHU assets in AIMS as individual systems (not broken down into components). Subsequently, additional L Classes have been added to try to conform with the AD4 requirements to include L7864 Control Panels, L75533 Variable Speed Drives, L71678 Variable Speed Drives, L75534 Actuators, & L755243 Temperature Sensors. All details for AHUs are captured within associated MCRs as detailed below which includes specifications and technical information from Fläkt Woods UK Ltd: EQ00003240 Cxxx-MCR-003337 Fläkt Woods UK Ltd - Air Handling Unit - VEKA 30 ACON-01874567 EQ00003241 CRL-MCR-004595 Fläkt Woods UK Ltd - Air Handling Unit - eQ 023-ACON-02068513 EQ00003242 CRL-MCR-004595 Fläkt Woods UK Ltd - Air Handling Unit - eQ 041-ACON-02068511 Cxxx are requesting for the asset identification requirement to be "Use as Is" with current L Classes remaining, but to direct the IM (in the O&M) to utilise L7515 Air Handling Unit (AHU) as the primary source for information so that there is only one identification for an individual Air Handling Unit when contacting the manufacturer to source replacement parts.
| 03SR - Stations (RfL) | Cxxx-NCR-003597 | NCR | Laminated Glazed Balustrades - In-Situ Load Testing - Inconsistencies in Loading Arrangements |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2021-11-10 | 2021-11-12 08:51 | 2 | 2021-08-25 12:48 | Architectural - Glazing | 5000 |  | Testing and Commissioning | Rework | 3 (3-6k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | During the in-situ load test of the laminated glazed balustrade panels conducted by __/__ LLP on 05/02/20 (see report 66890/M - Load Testing of a Laminated Glass Balustrade Panel), the horizontal imposed load of 3.0 kN/m was applied to only one individual panel without removing/accounting for the load distribution that would occur to adjacent panels through the continuous steel top channels. As a result of this, the measured deflections of the loaded panel are not representative of what would occur in a continuous crowd loading scenario where all panels could be loaded up to 3.0 kN/m. Due to this reason, this test also does not align with the Contractor's Balustrade Design Review Report produced by __ on behalf of __ (Calculation Number 23-02-TN-25), where an assessment was conducted of the individual panel without any load distribution through the steel top channel.
| 03SR - Stations (RfL) | Cxxx-NCR-003602 | NCR | CRL Redline Procedure |  | Contr | MRG | PAD - Paddington Station (West) |  | 2022-02-14 | 2022-02-25 15:26 | 11 | 2022-01-31 14:42 | Information Management - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | The current production of redline drawings at Cxxx Paddington is not fully compliant to CRL procedure CRL1-XRL-Z-GPD-CR001-50010 (Management of Redlines and As Builts Procedure) particularly sections 3.02, 3.04 and 3.10. The contractor is to demonstrate how the requirements are being achieved.
| 03SR - Stations (RfL) | Cxxx-NCR-003603 | NCR | Use of __ 1 DPM C |  | Contr | SKC | PAD - Paddington Station (West) |  | 2021-11-03 | 2022-03-25 09:12 | 142 | 2021-10-20 13:56 | Civil - Civil Engineering General | 3000 |  | Material | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | has installed __ 1 DPM C on the Departures Road Level (see attached location mark ups), which is a non LUL approved product. The material was essentially used as the top layer under the matwell to ensure there is a waterproof layer for the water to run down and drain.
| 03SR - Stations (RfL) | Cxxx-NCR-003604 | NCR | Fan frame buckling around anti vibration mount |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2021-12-13 | 2021-12-13 13:26 | 0 | 2021-10-21 13:12 | Mechanical - Heating Ventilation & Air Conditioning | 2000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Fan frame buckling around anti vibration mount. Observed on air release west fan frame (upper fan), and pressurisation fan frame east (lower fan). See attached photos. Contractor to check all fan frames for similar issue, identify root cause, and agree method of mitigation.
| 03SR - Stations (RfL) | Cxxx-NCR-003605 | NCR | Main Entrance Gates - Failure to achieve SR3 Rating |  | Contr | SKC | PAD - Paddington Station (West) |  | 2022-06-20 | 2022-06-07 12:33 | -13 | 2021-12-13 12:16 | Architectural - Security | 6000 |  | Manufacturing Defect | Repair | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Please see attached __ Global Report report for the East & West entrance gates which details the tests undertaken to achieve a security rating SR3, unfortunately the gate has not met the minimum requirements to be classified as SR3 and only reaches a security rating of SR2. Refer to page 21 for where attack test P199444-1 failed. The associated MCR also requires updating to ensure all open comments are closed to the satisfaction of the SR. Materials Compliance Record – Entrance Gates __ - Cxxx-SKC-O-TSC-B071_WS077-51663
| 03SR - Stations (RfL) | Cxxx-NCR-003606 | NCR | Departures Rd - In-road Fire Hydrant Signage |  | Contr | SKC | PAD - Paddington Station (West) |  | 2022-01-04 | 2022-02-21 15:59 | 48 | 2021-12-21 18:04 | Architectural - Signage | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Fire Hydrant identification signage is missing from Departures Rd. There is a requirement to provide signage which identifies the location and dimension of the fire hydrants within Departures rd. The Hydrants are located as per the below: East Hydrant - Opposite NR room 2/784 Central Hydrant - Opposite RFLi room 2/170 West Hydrant - In front of the first column for Paxton Canopy This signage is currently missing.
| 03SR - Stations (RfL) | Cxxx-NCR-003607 | NCR | Low door height to door D2-94b between stair INS II and lobby LB-S XIV |  | Contr | ATK | PAD - Paddington Station (West) |  | 2022-04-06 | 2022-04-11 11:09 | 5 | 2022-01-28 15:27 | Architectural - Doors | 10000 |  | Design | Repair | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The headroom provided by door D2-94b is too low for the functions it will serve.
| 03SR - Stations (RfL) | Cxxx-NCR-003608 | NCR | SOR Remote Release Access Doors - PSU Upgrades |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2022-03-08 | 2022-03-03 16:31 | -5 | 2022-02-08 09:59 | Electrical - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | It has been identified that the ongoing issues with the SOR Remote Release Access Doors is due to an issue with the capacity of the power supply to these units. PSU upgrades to be designed and installed.
| 03SR - Stations (RfL) | Cxxx-NCR-003609 | NCR | Fall Protection Gates in Maintenance Areas (TVS Area and Shafts) |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2022-07-01 | 2022-06-24 14:49 | -7 | 2022-02-17 12:48 | Architectural - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Further to the RfLI Civils Dilap (see Cxxx-PWK-01942), and following subsequent design checks (see attached) it has been noted that the current fall protection gates install in the BoH areas are not fit-for purpose and require modification/replacement. __ have proposed a number of modifications/improvements to the current install, however CRL/RfLI's preference is for these gates to be replaced with demountable 'Key Clamp' style barriers.
| 03SR - Stations (RfL) | Cxxx-NCR-003610 | NCR | Doors D2-95a and D2-90a Ironmongery |  | Contr | ATK | PAD - Paddington Station (West) |  | 2022-08-12 | 2022-07-30 11:13 | -13 | 2022-02-17 16:40 | Architectural - Doors | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Doors D2.95a and D2.90a should be provided with ironmongery to provide escape from inside at all times by depressing a lever handle or push-pad to open the door without the use of a key. The doors as fitted are only openable on the escape side by using keys, which is not acceptable.
| 03SR - Stations (RfL) | Cxxx-NCR-003611 | NCR | Missing Stamps/Kitemarks on Safety Glazing |  | Contr | ATK | PAD - Paddington Station (West) |  | 2022-08-12 | 2022-08-05 14:10 | -7 | 2022-02-17 18:08 | Architectural - Glazing | 6000 |  | Manufacturing Defect | Rework | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | Refer to the attached IRF 3286 - Missing Kite Marks. The panels noted below and on the IRF lack visible manufacturer's stamps/kitemarks, which are required under clause JZ25.1102 of the architectural specification. 1. One pane next to the column on the glass balustrade around the top of escalator 10/11 has its kite mark missing. 2. Lift 8/9 entrance at platform and concourse levels - architraves obscure view of kite marks- unable to verify. 3. Lift 6/7 – 2 panels on second level of glazing above concourse level are missing kite marks. The higher panels could not be accessed to verify. 4. __ East staircase- panel on mid-section missing a kite mark 5. __ glass balustrade sections with escalator screen vinyl have kite marks obscured- unable to verify 6. E__ balustrade: Numbering the panels from the east end the following panels are missing kite marks: 15, 17, 21, 42, 63. 7. Concourse and Platform PAE Enclosure Doors has kite marks that are not visible
| 03SR - Stations (RfL) | Cxxx-NCR-003612 | NCR | Platform Level TVP I & II Door Enhancements Required to meet Design / Specification |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2022-06-16 | 2022-06-07 12:48 | -9 | 2022-02-18 11:20 | Architectural - Doors | 6000 |  | Manufacturing Defect | Rework | 3 (3-6k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | It is understood that the refabricated TVP doors being procured by __ __ do not feature the enhancements required by the F2 designer (__) on the referenced DDCD document. Fabrication drawings suggest that the enhanced central stile sections (specified by PM&A to resist damper failure loads) have not been incorporated
| 03SR - Stations (RfL) | Cxxx-NCR-003613 | NCR | BoH Walkway Handrail - Multiple 90 Degree Bends - TSI Compliance |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2022-04-29 | 2022-05-03 05:55 | 4 | 2022-04-11 16:14 | Architectural - Balustrade | 3000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Further to Cxxx-PWK-02012, it has become apparent that the BoH handrail installation has been modified from the original design to accomodate driver's phones. The modification is also non compliant with TSI requirements as the The attached drawing and photos show several 90 degree bends around an obstacle along the BoH Tunnel Evacuation Walkway handrails, which is non-compliant to the SRT TSI: 4.2.1.6 (b) (2) Handrails shall be angled at 30° to 40° to the longitudinal axis of the tunnel at the entrance to and exit from an obstacle.
| 03SR - Stations (RfL) | Cxxx-NCR-003614 | NCR | Proximity of green button posts to gates |  | Contr | ATK | PAD - Paddington Station (West) |  | 2022-06-20 | 2022-05-27 08:06 | -24 | 2022-02-24 15:10 | Architectural - Security | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | At both the Paddington station entrance gates it is possible to reach through the bars of the gate, and the button post is close enough for the button to be pressed by someone outside the station using a hooked handle walking stick or similar. This negates the security function of the gates and needs to be rectified.
| 03SR - Stations (RfL) | Cxxx-NCR-003615 | NCR | Paddington Canopy Soffit Panels |  | Contr | ATK | PAD - Paddington Station (West) |  | 2022-07-19 | 2022-07-14 08:21 | -5 | 2022-03-03 13:02 | Architectural - Ceilings & Soffits | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Refer to the attached pdf. Soffit panels recently fitted to the station canopy are non-compliant for the following reasons: · Bad colour match of replacement panels with existing panels · Inconsistent fixing arrangements for replacement panels - should be in line with the existing installation · Inconsistent panel gaps · Inconsistent levels · Inconsistent holes in replacement panels - should be in line with the existing installation · Hinged panels being replaced with panels that do not appear to be hinged, compromising the finish and maintenance access provided by the originally installed system.
| 03SR - Stations (RfL) | Cxxx-NCR-003616 | NCR | Defective Escalator Skirt Lighting |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2022-04-27 | 2022-04-26 09:19 | -1 | 2022-03-03 13:22 | Electrical - Lighting | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Skirting lighting not illuminated on 2 banks of escalators (ESCs 1, 2 & 3 and ESCs 13, 14 & 15)
| 03SR - Stations (RfL) | Cxxx-NCR-003618 | NCR | Platform roundels on posts partially obscured by escalator newels |  | Contr | ATK | PAD - Paddington Station (West) |  | 2022-03-23 | 2022-04-26 15:44 | 34 | 2022-03-07 15:57 | Architectural - Signage | 3000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The roundels on posts at platform level between the escalators are partially obscured by the escalator newels, which detracts from the basic form and reduces the legibility of the roundel. An example is shown in the attached photograph. The locations of the roundels on posts are given on the "Platform Level Roundels Mark-up.pdf" attached to Cxxx-NCR-003601.
| 03SR - Stations (RfL) | Cxxx-NCR-003619 | NCR | Defective Mechanical (HVAC) Calculation Reports |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2022-03-29 | 2022-05-06 08:30 | 38 | 2022-03-15 05:18 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Revision 6.0 of Cxxx-SKC-M-XCL-B071_WS077-50001 (HVAC Calculations - Main Box East and West) was produced in 2016 and is not-up-to-date, and cannot be relied upon. Rev 6.0 required update to reflect the final as built design, and to incorporate more recent PMIs (e.g. PMI1226). Revision 7.0 of Cxxx-SKC-M-XCL-B071_WS077-50001 was issued in Nov 2021, however this update omits a significant amount of information (including key schedules and calculations). It is believed that this information is available, but requires compiling into an updated Rev 8.0 of the above report.
| 03SR - Stations (RfL) | Cxxx-NCR-003620 | NCR | Lack of protection to vertical waterproofing visible above ground on Departures Road |  | Contr | ATK | PAD - Paddington Station (West) |  | 2022-06-10 | 2022-06-17 13:22 | 7 | 2022-03-25 12:58 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | The vertical waterproofing visible above ground at the base of the wall on Departures Road has not been protected in accordance with the requirements of clause KW10.3226 of the waterproofing specification Cxxx-SWN-S-RSP-B071-00013. Please refer to the pdf attachments below, together with the reference document links to the waterproofing specification and product MCR.
| 03SR - Stations (RfL) | Cxxx-NCR-003621 | NCR | Canopy Cover Cap Failures following Storm Event |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2022-07-20 | 2022-07-11 09:56 | -9 | 2022-05-11 00:13 | Architectural - Roofing & Exterior Treatment | 5000 |  | Damaged | Rework | 3 (3-6k) | Complete | Design Problem - Other | Completed |  | Several (approx. 3 no.) canopy cover caps failed during a storm event in February 2022. Engineering assessment and root cause analysis of the canopy cover cap failures required to ensure this is not a concern. The cover caps also require replacing. Cxxx-SKC-O-RGN-B071_WS077-50428 - Canopy Cladding – Bullnose Report Rev 2.0 for a separate canopy cladding failure also remains under review. Comments raised following this review are to be resolved to the satisfaction of the SR by the Tier 1 Contractor.
| 03SR - Stations (RfL) | Cxxx-NCR-003622 | NCR | Cxxx - Paddington Station (Main Station Works, Fit Out & M&E) - Failed Rectifier to Battery Charger Unit at PAD 3/617 |  | Crossrail | XRL | PAD - Paddington Station (West) |  | 2023-01-27 | 2023-01-13 14:50 | -14 | 2023-01-13 14:43 | Electrical - LV Equipment | 5000 |  | Equipment Breakdown | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | PDX 3/617 E LV Swb-A, Closing Battery Charger Unit, Mains, Off. Has been attended and diagnosed as one rectifier faulty requires replacement. See below technician report: Today we attended a fault on LV-A east battery charger 006 at Paddington station. On arrival we found that Q01 20A input MCCB & Q06 10A rectifier __ had tripped out inside the battery charger. I then carried out safe isolation and isolated the supply to the battery charger so we could open the battery and check all the connections was sound and visually no burns or arching had been caused to trip these breakers out. After checking all battery charger connections, we put it back together and re-energised the circuit. We put both circuits back to the on position and found the rectifier T01-1 had failed and this is the cause it had tripped out the circuit breakers. I then carried out safe isolation again on the battery charger and removed the rectifier and gave it a clean down including the compartment and blew out dust from the inside of the rectifier and then re-installed the rectifier. I then went on to checking all the fuses in the battery charger that go to the rectifier had continuity which they did. I then re-energised the circuit, but the rectifier still did not work. New rectifier is required for this battery charger I will attach photos below of the make model and serial number so a like for like replacement can be ordered also included photos of the battery charger unit. The battery charger is now just operating on rectifier T01-2 but now has a mains supply. I will update the SR and close it down as the SR states there is no mains power which there is now. A new SR needs to be raised for the rectifier replacement for battery charger CR081-LVD-02935.
| 01CV - Civils | Cxxx-NCR-000110 | NCR | System By-Pass |  | Contr |  | BOS - Bond Street Station (West) |  | 2011-11-17 | 2011-11-22 | 5 | 2011-11-17 | Geotechnical Engineering - Compensation Grouting | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | The drilling team had issues with the constriction of the flush, which throttled the supply of flush preventing progress, this later resulted in a blockage. In order to solve the drilling issues and make sure the drilling method and system were functioning correctly the team by-passed the restriction, bypassing the pressure recording facility (M5). (see attached report)
| 01CV - Civils | Cxxx-NCR-000117 | NCR | Shift Review Group for 19/11/11 (BOS GS3 TaM Installation) |  | Contr |  | BOS - Bond Street Station (West) |  | 2011-11-25 | 2011-11-28 | 3 | 2011-11-24 | Geotechnical Engineering - Compensation Grouting | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | on the 19/11/11 (Saturday), as repairs were being carried out on the drill rig and no drilling occurred, the review group was not wholly attended by the required members.
| 01CV - Civils | Cxxx-NCR-000128 | NCR | Manual Survey at GS3 (Dering Street Area) - Surveying Point Temporary Bench Mark |  | Contr |  | BOS - Bond Street Station (West) |  | 2011-12-05 | 2011-12-06 | 1 | 2011-12-02 | Surveying - Instrumentation and Monitoring | 500 |  | System Defect | Repair |  | Complete |  | Completed |  | During the survey rounds, it was noticed that a heave of 3.5mm had occurred affecting C07LB115, C07LB114 and C07LB113. Upon investigation, it was identified that there are some works being carried out on the building very close to where the TBM is located, causing the bench mark to settle that much, and affecting all other survey points within its reference.
| 01CV - Civils | Cxxx-NCR-000138 | NCR | GS1 , Shaft Constaruction |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-01-20 | 2012-01-18 | -2 | 2012-01-16 | Shafts - Shafts General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Post pour inspection has confirmed that the concrete finshed (colar) level at varies place are out tolerance , notably at north east corner of jacking Gallow the holding down bolts are too far in the concrete which has compromised the base plate fixing.
| 01CV - Civils | Cxxx-NCR-000159 | NCR | NCR - PLPs BOS |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-01-27 | 2012-02-08 | 12 | 2012-01-27 | Surveying - Instrumentation and Monitoring | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | The Kerbs accommodating the PLPs have been damaged/loose and Point has not are not being reported/read.
| 01CV - Civils | Cxxx-NCR-000160 | NCR | NCR - __ Reading |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-01-29 | 2012-04-16 | 78 | 2012-01-27 | Surveying - Instrumentation and Monitoring | 500 |  | System Defect | Repair |  | Complete |  | Completed |  | A company plaque was making a __ on 74 New Bond Street inaccessible; the point has not been read thus backdated data lead to a trigger breach.
| 01CV - Civils | Cxxx-NCR-000170 | NCR | Shaft Excavation |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-03-05 | 2012-05-16 | 72 | 2012-03-05 | Shafts - Excavation | 500 |  | System Defect | Rework |  | Complete |  | Completed |  | During pre pour check a engineer noticed that there was a discrepancy between the design level and the level excavated by __ of the underside of the concrete plug within the shaft. This was discovered when checking the dowel bar levels. The drawing states that the underside of plug level should have been 110.350maod. The drawing shows that the distance beneath the final ring to underside of plug level is a minimum of 400mm. This measurement however is a typical detail, stating the minimum distance it should be from the underside of the last ring. Instead of using the 110.350 aod level __ set the dig level by measuring 400mm from the last ring. This resulted in the plug level being higher than the 110.350maod design level. __ should have set the dig level using the AOD level and not by measuring from the underside of the ring. The correct excavation level should have been 1.07m below the last ring. This is calculated by taking the bottom ring level of 111.420maod minus the underside of plug level of 110.350maod. Further checks carried out by a engineer confirmed this was the case. Hence instructed __ not carry out any further work until the issue was resolved. It should be noted that the shaft is within 20mm of the designed level. __ however proceeded to place the concrete. This NCR was raised for the following: • Non compliance of the Daily check sheet i.e. failure to check design level prior to pour • Concrete pour carried out without signing the pre pour check sheet approved (as per ITP) by the Engineer • Failure to comply with MS and ITP requirement • Not adhering to site instruction (clear instruction given to __ not to pour the concrete until the design level was resolved ) • Failure to manage activities on site in accordance with the ITP • instructed __ to immediately remove the concrete. • Concrete plug was then excavated to the correct level which was 1.07m below the last ring. obtained a further design check to ensure this could be excavated safely. • Concrete plug installed to correct level in accordance with drawing Cxxx--C-DDA-CRG03-50002
| 01CV - Civils | Cxxx-NCR-000206 | NCR | TCR WTH Panel 34 drilling |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-04-20 | 2012-08-20 | 122 | 2012-04-13 | Structural Engineering - Reinforcement | 500 |  | Damaged | Use As-Is |  | Complete |  | Completed |  | When drilllig one of the 14 holes, the reinforcement was drilled through to get to depth. This was due to miscommunication to stop drilling if re-bar was struck. The driller was instructed on future holes to stop if any re-bar was met whilst drilling. The drill recoils when re-bar is met. Please see attached drawing which shows the location of the affected hole: Panel 34 dowels (a)
| 01CV - Civils | Cxxx-NCR-000208 | NCR | Drilling of arrays at TCR CGS 7 |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-05-11 | 2012-05-22 | 11 | 2012-04-26 | Tunnelling - Grouting | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | A total number of 5 arrays were found to be out of tolerance (3, 8, 9, 11 & 14).
| 01CV - Civils | Cxxx-NCR-000220 | NCR | acceptance of grout testing |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-05-25 | 2012-05-22 | -3 | 2012-04-26 | Tunnelling - Grouting | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Site testing facility does not meet the above requirements
| 01CV - Civils | Cxxx-NCR-000221 | NCR | Testing standards |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-05-25 | 2012-07-18 | 54 | 2012-04-26 | Tunnelling - Grouting | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Grout testing acceptance criteria not made avaialbe during surveillance QS410-01. Grout compression test samples made previously were not provided protection form dehydration, there was no temperature control for storing the samples or set temperature environment for undertaking grout flow tests. The grout tray flow test was referred to as the Mash cone test, and no literature was made available to demonstrate that the tests were referenced to any national or Contract acceptable standards.
| 01CV - Civils | Cxxx-NCR-000222 | NCR | Maxibor Calibration Records |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-05-25 | 2012-07-18 | 54 | 2012-04-26 | Tunnelling - Grouting | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Calibration record provided during the surveillance for Maxibor number 021-241 was not traceable to national standards. Calibration record for Maxibor 020-044 was not made available
| 01CV - Civils | Cxxx-NCR-000227 | NCR | TCR Gantry Crane Rail Foundation |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-05-11 | 2012-05-16 | 5 | 2012-04-30 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | section of rail base was poured. Drawings were not signed or approved by Engineering Manager or accepted by CRL. In addition, No Inspection and Test Plan in place neither approved by or accepted by CRL.
| 01CV - Civils | Cxxx-NCR-000229 | NCR | TaMs installed Out of tolerance in BOS GS3 |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-05-07 | 2012-05-22 | 15 | 2012-04-30 | Geotechnical Engineering - Compensation Grouting | 500 |  | Design | Rework |  | Complete |  | Completed |  | "The following TaMs have been drilled short of design length/out of tolerance and have been corrected. B3/05: encountered Obstruction at 21m. B3/09: 547mm out of tolerance B3/21: drilled to 21m Obstruction encountered. B3/24: 263mm out of tolerance B3/25: 977mm out of tolerance B3/29: 724mm out of tolerance B3/30: 363mm out of tolerance B3/32: 390mm out of tolerance B3/33: 129mm out of tolerance B3/34: 615mm out of tolerance B3/35: 473mm out of tolerance B3/39: 1042mm out of tolerance B3/46: 211mm out of tolerance B3/49: 292mm out of tolerance B3/53: 451mm out of tolerance B3/54: 200mm out of tolerance B3/57: 176mm out of tolerance"
| 01CV - Civils | Cxxx-NCR-000231 | NCR | TCR WTH Crane Beam - cube tests no taken |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-05-11 | 2012-05-22 | 11 | 2012-05-01 | Structural Engineering - Concrete Member | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | The inspection test plan was not fully in place (See NCR-410-00227) and hence cube tests were not taken
| 01CV - Civils | Cxxx-NCR-000232 | NCR | TCR GS1 TaM Drilling Out-of-Tolerance |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-05-15 | 2012-05-22 | 7 | 2012-05-01 | Geotechnical Engineering - Compensation Grouting | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | TaM 12 (T1/12) encountered sand/gravel/water at 44m depth. Drilling stopped at this point and the TaM was installed to 42m (of a design drill length 66.8m). This has been surveyed and has shown that the borehole has deviated 440mm (upward) outside of the given tolerance (750mm).
| 01CV - Civils | Cxxx-NCR-000233 | NCR | TCR GS1 TaM Drilling Out-of-Tolerance |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-05-15 | 2012-05-22 | 7 | 2012-05-01 | Geotechnical Engineering - Compensation Grouting | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | TaM 92 (T1/92) encountered sand/gravel/water at 46m depth. Drilling stopped at this point and the TaM was installed to 44.85m (of a design drill length 56.85m). This has been surveyed and at a depth of 19.5m has shown that the borehole has deviated 400mm (upward).
| 01CV - Civils | Cxxx-NCR-000234 | NCR | TCR GS1 TaM Drilling Out-of-Tolerance |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-05-15 | 2012-05-22 | 7 | 2012-05-01 | Geotechnical Engineering - Compensation Grouting | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | TaM 96 (T1/96) encountered sand/gravel at 45m depth. Drilling stopped at this point and the TaM was installed to 44m (of a design drill length 58.85m). This has been surveyed and has shown that the borehole has deviated 1860mm (upward) outside of the given tolerance (500mm).
| 01CV - Civils | Cxxx-NCR-000237 | NCR | Access to deep pins 1002-1003-1004 |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-05-04 | 2012-08-13 | 101 | 2012-05-03 | Surveying - Instrumentation and Monitoring | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | deep pins inaccessible due to have being covered by a thin concrete layer, that was done to level the area.
| 01CV - Civils | Cxxx-NCR-000239 | NCR | Adherence to __ procedures |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-05-11 | 2012-05-16 | 5 | 2012-05-04 | Utilities Engineering - Water | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Operative undertaking works on TW main was found not to hold EUSR hygiene card when challenged by TW supervisor. and the operative had been told prior to the works commencing that they must have the EUSR card, despite this, the operative was found to be working on the TW assets.
| 01CV - Civils | Cxxx-NCR-000245 | NCR | Scabbling instead of grit blasting as per de ITP |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-11-05 | 2012-07-12 | -116 | 2012-05-10 | Civil - Civil Engineering General | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | Scabbling the D-Wall was the chosen method, instead of grit blasting as per ITP Cxxx--C-ITP-CRT00_ST005-5044 Rev 2.0, to create a rough surface for the concrete packing between the D-Wall and WTH P1 level waling beams. This was due to the fact that the grit blasters couldn't come on site on time just before the beginning of the propping installation. We had resources to scabble the D-Wall ourselves and did it not to delay the works.
| 01CV - Civils | Cxxx-NCR-000248 | NCR | TCR GS1 TaM Drilling Out-of-Tolerance |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-05-29 | 2012-05-22 | -7 | 2012-05-16 | Geotechnical Engineering - Compensation Grouting | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | TaM 97 (T1/97) encountered sand/gravel/water between 38-40m depth. Drilling stopped at this point and the TaM was installed to 38m (2.85m short of the design drill length). The hole has been Maxibore surveyed and the results are being processed to establish any deviation out-of-tolerance.
| 01CV - Civils | Cxxx-NCR-000249 | NCR | TCR - WTH Gaps between P1 propping end plates |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-05-29 | 2012-05-28 | -1 | 2012-05-22 | Structural Engineering - Bolted Connections | 500 |  | System Defect | Repair |  | Complete |  | Completed |  | After completion of P1 temporary propping installation, there are gaps up to 10mm between the props end plates at several locations.
| 01CV - Civils | Cxxx-NCR-000250 | NCR | TCR - WTH Fillet welds not passing the N__ test |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-05-29 | 2012-05-28 | -1 | 2012-05-22 | Structural Engineering - Welding | 500 |  | System Defect | Repair |  | Complete |  | Completed |  | After testing all welds connecting the P1 gallows brackets and waling beams, 10 of them haven't passed the N__ tests as per the ITP. All of them but one failed because they didn't reach the 8mm required, and one that cracked. See survey attached with the ones that failed.
| 01CV - Civils | Cxxx-NCR-000252 | NCR | TCR-WTH. Method statement for TW has no mention of TW drawings & calculations |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-05-24 | 2012-07-06 | 43 | 2012-05-17 | Civil - Geotechnical Engineering | 500 |  | Planning | Rework |  | Complete |  | Completed |  | The method statement “ Temporary Propping Installation Cxxx--C-GMS-CRT00_ST005-50240 Rev1, does not include the calculations and detail drawings for the temporary works.
| 01CV - Civils | Cxxx-NCR-000256 | NCR | Installation of Shape Arrays in WTH without accepted ITP |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-08-27 | 2012-08-13 | -14 | 2012-05-23 | Surveying - Instrumentation and Monitoring | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Carrying out installation with not accepted ITP. MS and SAP are not in place.
| 01CV - Civils | Cxxx-NCR-000257 | NCR | Carrying out installation with not accepted ITP |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-06-06 | 2012-06-13 | 7 | 2012-05-23 | Surveying - Instrumentation and Monitoring | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Magnetic Extensometers where installed without accepted ITP.
| 01CV - Civils | Cxxx-NCR-000258 | NCR | Carrying out installation with not accepted ITP |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-06-06 | 2012-06-13 | 7 | 2012-05-23 | Surveying - Instrumentation and Monitoring | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Installation of piezometers in WTH with not accepted ITP.
| 01CV - Civils | Cxxx-NCR-000259 | NCR | Carrying out installation with not accepted ITP |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-06-06 | 2012-07-12 | 36 | 2012-05-23 | Surveying - Instrumentation and Monitoring | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Carrying out installation of Crack meters in WTH with not accepted ITP.
| 01CV - Civils | Cxxx-NCR-000260 | NCR | Obstruction Encountered - TaM abandoned |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-08-01 | 2012-07-13 | -19 | 2012-05-23 | Geotechnical Engineering - Compensation Grouting | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | Due to encountering an obstruction, the drill could not progress beyond 17m. The TaM was installed to 17m.
| 01CV - Civils | Cxxx-NCR-000261 | NCR | Carrying out installation with not accepted ITP |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-06-06 | 2012-07-04 | 28 | 2012-05-23 | Surveying - Instrumentation and Monitoring | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Carrying out draw wire sensor installation with not accepted ITP.
| 01CV - Civils | Cxxx-NCR-000262 | NCR | Carrying out installation with not accepted ITP |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-08-27 | 2012-08-16 | -11 | 2012-05-23 | Surveying - Instrumentation and Monitoring | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Carrying out manual monitoring with not accepted ITP.
| 01CV - Civils | Cxxx-NCR-000263 | NCR | Carrying out Inclinometer installation with not accepted ITP |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-06-06 | 2012-06-13 | 7 | 2012-05-23 | Surveying - Instrumentation and Monitoring | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Carrying out inclinometer installation with not accepted ITP.
| 01CV - Civils | Cxxx-NCR-000264 | NCR | Watermain at TCR CGS 2 |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-05-31 | 2012-07-05 | 35 | 2012-05-24 | Utilities Engineering - Water | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Of the 5 electrofusion couplings undertaken 2 failed.
| 01CV - Civils | Cxxx-NCR-000268 | NCR | BOS GS4 TaM Drilling Out-of-Tolerance |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-06-08 | 2012-05-28 | -11 | 2012-05-25 | Geotechnical Engineering - Compensation Grouting | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | Hole B4/29 was drilled to full depth (46.75m). It was not possible to insert the TaM to the full depth of the hole, and the TaM was installed to 42m only (4.75m short). The hole will be Maxibore surveyed to establish any deviation out-of-tolerance.
| 01CV - Civils | Cxxx-NCR-000269 | NCR | TCR WTH - Alteration to hoarding kentledge |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-06-08 | 2012-07-02 | 24 | 2012-05-28 | Structural Engineering - Structural Engineering - General | 500 |  |  | Repair |  | Complete |  | Completed |  | On great Chapel Street, the road has become narrowed due to the position of the crane beam. To enable maximum width to allow vehicles to pass down Great Chapel Street, 12 no. u-bar's were cut flush with the kentledge (Photo 2 & Photo 3) This was done without prior agreement with Crossrail.
| 01CV - Civils | Cxxx-NCR-000273 | NCR | TCR CGS3 lateral replacement |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-06-13 | 2012-08-17 | 65 | 2012-06-06 | Utilities Engineering - Water | 500 |  |  | Rework |  | Complete |  | Completed |  | proceeded with replacement before __ had issued final requirements for the works. Upon completion TW informed that the lateral replacement was not acceptable.
| 01CV - Civils | Cxxx-NCR-000275 | NCR | Waling concrete gaps |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-06-21 | 2012-08-20 | 60 | 2012-06-07 | Civil - Structural Engineering | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The concrete packing behind the P1 walers was installed as follows. A leanmix haunch was installed beneath the walers to act as a seal / blinding. A narrow strip of polythene was placed down the back of the waler, to act as a debonding material between the blinding and the packing concrete. The packing concrete was then placed. Upon excavating beneath the P1 walers, it is clear that some of the lean mix is set at too high a level, ranging approx between 50mm and 100mm. Some has fallen out during the excavation. This presents itself as an technical problem - (leanmix not suitable as packing concrete as low grade and not compacted) and a H&S problem as the leanmix can fall off onto the waler / excavation beneath.
| 01CV - Civils | Cxxx-NCR-000276 | NCR | TCR Gantry Crane Rails |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-06-21 | 2012-07-04 | 13 | 2012-06-07 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Approx 60% of holding down bolts used are at limit of slot, as such should the wall deflect inwards, there is currently no possibility of adjusting the alignment. This is due to the slot being used to adjust for errors in aligment, i.e - Setting Out Failure.
| 01CV - Civils | Cxxx-NCR-000284 | NCR | TCR-WTH Gaps on Underside of Props |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-06-27 | 2012-07-06 | 9 | 2012-06-13 | Structural Engineering - Bolted Connections | 500 |  | System Defect | Repair |  | Complete |  | Completed |  | In attached reccomendation from TW designer it states that gaps greater than 2.5mm need to be packed. Observation carried out by A Spencer sent via email on 6/6/2012 attached shows that gap on prop underside of P1S12a, close to waling is approx. 4mm.
| 01CV - Civils | Cxxx-NCR-000287 | NCR | WTH - Strain gauges damaged at P1 propping level |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-06-22 | 2012-07-06 | 14 | 2012-06-15 | Civil - Civil Engineering General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | During the digging operations to level P2 two strain gauges, P1S2 and P1S5, were damaged by the minidiggers buckets. This occured the 30th of May and they were repaired as soon as it was possible and safe to do, being operative again the 8th of May (considering the Jubilee Bank holiday in between).
| 01CV - Civils | Cxxx-NCR-000288 | NCR | TCR WTH Shape Array 9 and 11 removal |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-06-29 | 2012-07-06 | 7 | 2012-06-18 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | Shape arrays 9 and 11, in the west wall of the South Box, were removed on 15th June 2012. CRL were alerted at the SRG meeting on the same day. This is due to their location clashing with the movement of the Gantry Crane. The Gantry Crane had to be moved to the south end of the box to allow for P2 props installation to commence using a mobile crane sitting on the northern box. It was known that the Array's location would need to be altered however a solution had not been determined prior to the Gantry Crane movement
| 01CV - Civils | Cxxx-NCR-000289 | NCR | NCR-s not closed out by the required date |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-07-02 | 2012-07-18 | 16 | 2012-06-18 | Geotechnical Engineering - Compensation Grouting | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | NCR-s opened during CRL audit on 10/04/12 should have been closed by 25/05/12.
| 01CV - Civils | Cxxx-NCR-000291 | NCR | WTH-TCR: Failue to issue IRF on time (non compliance to Part 20, Vol 2B) |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-06-25 | 2012-07-06 | 11 | 2012-06-18 | Civil - Civil Engineering General | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | IRF was issued at 19:00 on Friday 15/06/2012 for an activity planned to start on Saturday 16/06/2012.
| 01CV - Civils | Cxxx-NCR-000297 | NCR | Concrete cube error |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-06-22 | 2012-07-02 | 10 | 2012-06-21 | Structural Engineering - Structural Engineering - General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | A small amount of repair work was required to the underside of the concrete packing. A number of cube tests have been taken to ensure the concrete reaches the correct strength. Two of the cubes taken were placed in the emergency hut on Dean Street by an operative and left for an unkown period of time (see attached picture). On discovery, these cubes they were struck and stored in a make shift bath until __ were able to collect them for testing.
| 01CV - Civils | Cxxx-NCR-000298 | NCR | TCR WTH P2 Propping Frame, incorrect waler end plate |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-06-22 | 2012-07-05 | 13 | 2012-06-21 | Structural Engineering - Steel Member | 500 |  | Material | Repair |  | Complete |  | Completed |  | P2 Level: On waler P2W9, (DAM's reference WB20) it was found that the six holes on the waler end plate had been drilled incorrectly, approximately 100mm out from the horizontal position . See attached picture.
| 01CV - Civils | Cxxx-NCR-000301 | NCR | TCR WTH P2 Propping Frame, Waler stub error |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-06-29 | 2012-07-02 | 3 | 2012-06-21 | Structural Engineering - Steel Member | 500 |  | Material | Rework |  | Complete |  | Completed |  | When fitting the final prop P2S9 it became apparant that there was a fabrication error due to it not fitting in place as expected. DAM, the propping frame fabricators and installers, informed . On examination, it became apparent that there is a dimensional error on the stub connection coming from waler P2W6.
| 01CV - Civils | Cxxx-NCR-000311 | NCR | TCR-WTH- welding electrodes package found at the tally hut |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-07-02 | 2012-07-06 | 4 | 2012-06-30 | Structural Engineering - Welding | 500 |  | Material | Repair |  | Complete |  | Completed |  | A welding electrodes package was fount by the fridge at the tally hut, with the risk or being missuesd, damaged and used on site, or mixed up with live ones.
| 01CV - Civils | Cxxx-NCR-000314 | NCR | TCR WTH - Piezometer damaged |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-07-11 | 2012-07-06 | -5 | 2012-07-04 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | On 03/07/12, a staff member found a data logger in the south box area which was no longer attached to the piezometer, hence the piezometer had been damaged. A spoil heap was covering the piezometer location. It is not known when the damage occurred. As the piezometers readings are only taken weekly, the damage will have happened since the last reading on 27/06/12
| 01CV - Civils | Cxxx-NCR-000315 | NCR | SMM - Compensation Grouting - Cleaning out TaM Pipes |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-07-20 | 2012-07-13 | -7 | 2012-07-06 | Geotechnical Engineering - Compensation Grouting | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | A number of TaM's, most notably in BOS GS5 have not been cleaned sufficiently at the correct stage of the works, following grouting. As a result these TaM's have become blocked with solid grout, and have required additional internal drilling to clear the tubes and make the TaM's good.
| 01CV - Civils | Cxxx-NCR-000319 | NCR | Pull out test without correct operating instructions, passing criteria |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-07-30 | 2012-07-26 | -4 | 2012-07-09 | Structural Engineering - Testing | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | Instruction on site gave wrong information about the test stating that the fixing is likely to be insecure and should be investigated if the load is decreasing during 10-15 seconds loading time. Instructions from Hydrajaws Limited (testing equipment supplier) is saying – Apply load using the ratchet spanner and observe the reading on the gauge until the required test load is reached. This reading could decay due to first movement or creep on the anchor. Continue to apply the load to the required reading and observe that the loading remains steady*. Should a serious drop in the indicated load occur again, the fixing is likely to be insecure and should be investigated. * DIGITAL GAUGES ARE VERY ACCURATE AND THE SECOND DECIMAL FIGURE MAY NOT ALWAYS REMAIN STEADY As the digital gauge is very accurate a drop off will be noticeable but this should stabilise after a period of time. If the reading continues to drop off, further investigation of the fixing would be required. According to the Hydrajaws instructions the load is allowed to decrease.
| 01CV - Civils | Cxxx-NCR-000321 | NCR | GS3 Collar Construction |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-07-12 | 2012-07-27 | 15 | 2012-07-10 | Shafts - Shafts General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | __ uncovered pockets of honey comb in the top surface of the concrete finish at GS3. This was found during stripping off the shutter on Tuesday 10th July 2012
| 01CV - Civils | Cxxx-NCR-000324 | NCR | TCR WTH Pull out tests |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-08-03 | 2012-07-27 | -7 | 2012-07-26 | Structural Engineering - Structural Engineering - General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | When undertaking the pull out test the load appeared to gradually decrease. Although a small reduction in load can be expected according to the user manual, the specification of the amount of decline allowable was unclear. Hence the original testing regime could be considered ambiguous. Pull out test report and pictures attached. On the first five bolts, the load applied was slightly higher than required to allow for a small drop. The test was conducted for one minute. Despite achieving the test load required, the load appeared that it would still decline after one minute; hence there could be some uncertainty as to whether this would stabilise as expected or was leading to a failure.
| 01CV - Civils | Cxxx-NCR-000328 | NCR | TCR WTH Loss of Deep Pin levelling stub |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-07-27 | 2012-07-17 | -10 | 2012-07-13 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | It was recorded on 12/07/12 that Deep Pin 6 on Dean Street was indicating a settlement of 10mm. On investigation it was discovered that the dome levelling stub which sits on top of the pin was missing, accounting for the drop in level. It is not know what happened to the stub.
| 01CV - Civils | Cxxx-NCR-000333 | NCR | TCR WTH Piezo 1A damaged |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-07-31 | 2012-07-23 | -8 | 2012-07-17 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | Piezometer 1A (furthest north) was damaged between 2-3pm on 14th July - the cable had been snapped.
| 01CV - Civils | Cxxx-NCR-000334 | NCR | TCR WTH Strain Gauge Damage P2S2 |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-07-31 | 2012-07-19 | -12 | 2012-07-18 | Structural Engineering - Structural Engineering - General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | P2S2 strut's (Instrumetation plot attached) strain gauge ceased to give readings at 2pm on 07/07/12 (Saturday). On investigation, it was found there was an issue with the wiring in the data logger box.
| 01CV - Civils | Cxxx-NCR-000337 | NCR | TCR WTH Strain Gauge Damage P2S11 |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-07-31 | 2012-07-23 | -8 | 2012-07-18 | Structural Engineering - Structural Engineering - General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | P2S11 strut stopped giving readings at 8am on 7/7/12 (Saturday). On inspection the strain gauge was loose from the strut. It is unknown what caused this. (TCR WTH Instrumentation plot attached)
| 01CV - Civils | Cxxx-NCR-000338 | NCR | TCR WTH Broken prisms on Diaphragm wall |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-08-01 | 2012-07-23 | -9 | 2012-07-18 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | On 13/07/12 it was not possible to read Prism 2 (on the West side of the diaphragm wall); on inspection it appeared to be damaged. On 16/07/12 it was discovered that Prism 11 was also damaged.
| 01CV - Civils | Cxxx-NCR-000344 | NCR | TCR-WTH ATS (stable reference points) |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-08-06 | 2012-08-17 | 11 | 2012-07-23 | Surveying - Instrumentation and Monitoring | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Currently orientates to 5 reference prisms within the ZOI.
| 01CV - Civils | Cxxx-NCR-000356 | NCR | BOS GS4 TaM Drilling Out of Tolerance |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-08-15 | 2012-08-14 | -1 | 2012-08-01 | Geotechnical Engineering - Compensation Grouting | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | Hole B4/21 was drilled to a depth of 69m. When approaching this depth the drilling progress had been becoming increasingly more difficult and very slow due to the encountered ground conditions. As such, it was not possible to advance the augers beyond 69m. Attempts at drilling any further ceased and the TaM was installed to a depth of 67m (10.75m short of the design length). This hole will be maxibore surveyed to establish any deviation out-of-tolerance.
| 01CV - Civils | Cxxx-NCR-000357 | NCR | BOS GS4 TaM Drilling Out-of-Tolerance |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-08-15 | 2012-08-14 | -1 | 2012-08-01 | Geotechnical Engineering - Compensation Grouting | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | When drilling hole B4/58 an obstruction was encountered at a depth of 18.5m and it was not possible to progress the hole any further. As this TaM is close to the piles of 28 South Molton Lane it was decided to cease drilling. The TaM was installed to a depth of 18.5m (1.25m short of the design length). The TaM will be maxibore surveyed to establish any deviation out-of-tolerance.
| 01CV - Civils | Cxxx-NCR-000367 | NCR | Resin Anchor Pull Out Test Failure - P4 Level |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-08-14 | 2012-08-23 | 9 | 2012-08-13 | Structural Engineering - Testing | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | are currently undertaking testing on 100% of the bolts at this level. Four failures have been identifed to date (testing still in progress). It appears not enough __ Hit had been used on those that had failed (all on north wall and installed during the same shift)
| 01CV - Civils | Cxxx-NCR-000368 | NCR | TCR WTH Goliath Crane Monitoring Strategy and Test Lift Plan |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-08-20 | 2012-08-23 | 3 | 2012-08-13 | Structural Engineering - Testing | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | Site Team has not implemented the requirement as consider it to be an unneccesary requirement. Site team should have raised this with designer (KES) in a prompt fashion prior to submission to CRL. Site team also should have closed this out when raised by CRL also in a prompt fashion.
| 01CV - Civils | Cxxx-NCR-000369 | NCR | Weld Procedure Specification |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-08-19 | 2012-08-24 | 5 | 2012-08-13 | Structural Engineering - Welding | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Weld Procedure Specification describes pre-heating welding rods and a different type of rod to that used.
| 01CV - Civils | Cxxx-NCR-000370 | NCR | TaMs installed Out of tolerance in BOS GS1 |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-08-28 | 2012-08-30 | 2 | 2012-08-14 | Geotechnical Engineering - Compensation Grouting | 500 |  | Design | Rework |  | Complete |  | Completed |  | The following TaMs have been drilled short of design length/out of tolerance and have been corrected : B1/4a: 535mm out of tolerance B1/12a: Augers snapped in hole at 34.5m B1/14: not drilled B1/19: Augers snapped in hole at 18m B1/27: 886mm out of tolerance B1/29a: 623mm out of tolerance B1/40: 513mm out of tolerance B1/47: 462mm out of tolerance B1/50: 185mm out of tolerance B1/55: 189mm out of tolerance B1/59: 324mm out of tolerance
| 01CV - Civils | Cxxx-NCR-000373 | NCR | Disposal / Storage of Welding Rods |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-08-31 | 2012-08-23 | -8 | 2012-08-17 | Structural Engineering - Welding | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Despite efforts to better control / improve, the welding rods ( the type being used need to be used the same day the pack was opened for structural welding) have been found half open on site once more. (Note no structural welding happening on site at this time thus no concern that any welds have been compromised, it is more a question of establishing the use and disposal procedure properly.)
| 01CV - Civils | Cxxx-NCR-000377 | NCR | SMM_No SRG meeting on Sunday NIGHTSHIFT (TCR_WTH) |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-09-04 | 2012-09-04 | 0 | 2012-08-21 | Surveying - Instrumentation and Monitoring | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | On Sunday NIGHTSHIFT no SRG was held due to a misunderstanding between KGI operative and WTH construction team. However, the report was produced, analysed and distributed during Monday DAYSHIFT, after the issue was noticed.
| 01CV - Civils | Cxxx-NCR-000378 | NCR | TaMs installed Out of tolerance in BOS GS4 |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-09-11 | 2012-08-30 | -12 | 2012-08-28 | Geotechnical Engineering - Compensation Grouting | 500 |  | Design | Rework |  | Complete |  | Completed |  | The following TaMs have been drilled short of design length/out of tolerance and have been corrected/use as is : B4/5: 64mm out of vertical tolerance -Above 4.5m exclusion zone and with design band-Use as is B4/7: 275 mm out of horizontal tolerance – Within allowable horizontal spacing – Use as is 8mm out of vertical tolerance-Above 4.5m exclusion zone and with design band-Use as is B4/9: 43mm out of vertical tolerance-Above 4.5m exclusion zone and with design band-Use as is B4/12: 289 mm out of horizontal tolerance – Within allowable horizontal spacing – Use as is B4/13: 287 mm out of horizontal tolerance – Within allowable horizontal spacing – Use as is B4/14: 597 mm out of horizontal tolerance – Within allowable horizontal spacing – Use as is 102mm out of vertical tolerance- Above 4.5m exclusion zone and with design band-Use as is B4/15: 619 mm out of vertical tolerance and located outside design band -No tunnels located beneath TaM, therefore ok – Use as is B4/16: 1479 mm out of vertical tolerance and located outside design band -No tunnels located beneath TaM, therefore ok – Use as is B4/17: 619 mm out of vertical tolerance and located outside design band -No tunnels located beneath TaM, therefore ok – Use as is B4/20: 467 mm out of horizontal tolerance – Within allowable horizontal spacing – Use as is 1805 mm out of vertical tolerance and located outside design band –Accept as above exclusion zone, therefore ok – Use as is B4/23: 405 mm out of horizontal tolerance – Awaiting Maxibor of adjacent TaMs 1765 mm out of vertical tolerance, outside design band and within the 4.5m Exclusion zone – Ok to use TaM section clear of 4.5m exclusion zone – Extend TaM from BOS 2 ( tbc)- Use as is B4/25: 1674 mm out of vertical tolerance and outside design band- Above the 4.5m Exclusion zone – Use as is B4/26: 3167 mm out of horizontal tolerance- 833mm out of tolerance for horizontal spacing between adjacent TaMs – New re-drill B4/26A to achieve coverage B4/27: 488 mm out of horizontal tolerance- 1026mm out of tolerance for horizontal spacing between adjacent TaMs – New re-drill B4/27A to achieve coverage B4/28: 1128mm out of horizontal tolerance – Within allowable horizontal spacing – Use as is B4/29: 1309 mm out of horizontal tolerance- 524mm out of tolerance for horizontal spacing between adjacent TaMs – New re-drill B4/29A to achieve coverage B4/30: 310mm out of vertical tolerance -Above 4.5m exclusion zone and with design band-Use as is B4/31: 537 mm out of horizontal tolerance – Within allowable horizontal spacing – Use as is 418mm out of vertical tolerance- Above 4.5m exclusion zone and with design band-Use as is B4/33: 976 mm out of horizontal tolerance- 1650mm out of tolerance for horizontal spacing between adjacent TaMs – New re-drill B4/33A to achieve coverage B4/34: 1216 mm out of horizontal tolerance – Within allowable horizontal spacing – Use as is B4/35: 498 mm out of horizontal tolerance – Within allowable horizontal spacing – Use as is B4/37: 621mm out of vertical tolerance- Above 4.5m exclusion zone and with design band-Use as is B4/38: within allowable individual horizontal tolerance- 353mm out of tolerance for horizontal spacing between adjacent TaMs – New re-drill B4/38A to achieve coverage 429mm out of vertical tolerance- Above 4.5m exclusion zone and with design band-Use as is B4/39: 725 mm out of horizontal tolerance – Within allowable horizontal spacing – Use as is B4/40: 646 mm out of horizontal tolerance – Within allowable horizontal spacing – Use as is 262mm out of vertical tolerance- Above 4.5m exclusion zone and with design band-Use as is B4/41: 479 mm out of horizontal tolerance- 612mm out of tolerance for horizontal spacing between adjacent TaMs – New re-drill B4/41A to achieve coverage 777mm out of vertical tolerance- Above 4.5m exclusion zone and with design band-Use as is B4/42: 1062 mm out of horizontal tolerance – Within allowable horizontal spacing – Use as is B4/43: 1871 mm out of horizontal tolerance- 303mm out of tolerance for horizontal spacing between adjacent TaMs – New re-drill B4/43A to achieve coverage B4/45: 4mm out of vertical tolerance -Above 4.5m exclusion zone and with design band-Use as is B4/49: out of vertical tolerance -Above 4.5m exclusion zone and with design band-Use as is B4/52: out of vertical tolerance -Above 4.5m exclusion zone and with design band-Use as is B4/55: out of vertical tolerance -Above 4.5m exclusion zone and with design band-Use as is B4/56: out of vertical tolerance -Above 4.5m exclusion zone and with design band-Use as is B4/57: out of vertical tolerance -Above 4.5m exclusion zone and with design band-Use as is Awaiting Maxibor results for the following : B4/18,21,22,24,26A,27A,29A,33A,38A Please refer to DRAFT- BOS 4- Drill Deviation Assessment - 07.0812 and Cxxx--C-DWG-CRT00_ST005_Z-50084
| 01CV - Civils | Cxxx-NCR-000379 | NCR | SMM_TCR_Dean Street HLCs stopped working (20/08/12-21/08/12) |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-09-05 | 2012-09-04 | -1 | 2012-08-22 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Use As-Is |  | Complete |  | Completed |  | As of 20/08/12 the Hydrostatic Levelling Cells (HLC’s) installed along Dean Street stopped functioning correctly.
| 01CV - Civils | Cxxx-NCR-000380 | NCR | Access to deep pins 1003 |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-08-23 | 2012-08-23 | 0 | 2012-08-22 | Surveying - Instrumentation and Monitoring | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | On 200812 deep pin inaccessible due to muckskip covering it.
| 01CV - Civils | Cxxx-NCR-000383 | NCR | Failure to have an approved Inspection & Test Plan in place prior to starting works |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-09-13 | 2012-09-12 | -1 | 2012-08-23 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Works were started on the BOS ETH dry silo batching plant tank foundation prior to the ITP for the works being accepted by the Project Manager.
| 01CV - Civils | Cxxx-NCR-000393 | NCR | SMM_TCR_HLCs connectivity failure over the weekend |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-09-24 | 2012-09-13 | -11 | 2012-09-04 | Surveying - Instrumentation and Monitoring | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | HLCs connectivity (South and West of the WTH) was lost at the end of Friday's shift (24/08/12) and although no works have been taking place over the bank holiday, we agreed to present HLC data over the weekend and no readings from those blocks (South and West) could be presented.
| 01CV - Civils | Cxxx-NCR-000394 | NCR | SMM_TCR_ATS K not receiving data |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-09-21 | 2012-09-04 | -17 | 2012-09-04 | Surveying - Instrumentation and Monitoring | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | ATS K was not sending data since Friday evening (24/08/12) so we were missing some prisms in the area of Sheraton Street and Wardour Street and therefore not presenting their readings in the SRGs over that weekend.
| 01CV - Civils | Cxxx-NCR-000397 | NCR | Extensometer Readings |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-09-30 | 2012-09-20 | -10 | 2012-08-30 | Surveying - Instrumentation and Monitoring | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Blockage occurs at 9m depth from current level. Level of blockage is 92.138.
| 01CV - Civils | Cxxx-NCR-000401 | NCR | Grout Testing |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-09-14 | 2012-09-04 | -10 | 2012-08-31 | Geotechnical Engineering - Compensation Grouting | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Grout testing personal are not UKAS accredited or trained to an equivalent standard.
| 01CV - Civils | Cxxx-NCR-000402 | NCR | Sock Grout Testing does not follow design requirements |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-09-21 | 2012-10-08 | 17 | 2012-09-03 | Shafts - Grouting | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | gets test results on a weekly basis. 2 day strength results are not checked before drilling in the same segment. is testing at the moment only 7 and 28 day strength.
| 01CV - Civils | Cxxx-NCR-000403 | NCR | BOS 3 Sleeve Grout Testing Records |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-09-21 | 2012-10-02 | 11 | 2012-09-04 | Geotechnical Engineering - Compensation Grouting | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | There are no field grout test forms available that recorded the batching and testing of the sleeve grout during the drilling operations at BOS GS3. These forms record the results of flow & bleed tests and mud balance (specific gravity).
| 01CV - Civils | Cxxx-NCR-000431 | NCR | TCR 7 Sleeve Grout Testing Records |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-10-01 | 2012-10-02 | 1 | 2012-09-13 | Geotechnical Engineering - Compensation Grouting | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | There are no field grout test forms available that recorded the batching and testing of the sleeve grout during the drilling operations at TCR GS 7. These forms record the results of flow & bleed tests and mud balance (specific gravity).
| 01CV - Civils | Cxxx-NCR-000443 | NCR | TCR 7 Plug Grout Cube Results |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-10-02 | 2012-10-02 | 0 | 2012-09-18 | Geotechnical Engineering - Compensation Grouting | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | There are no plug grout cube results available for TCR 7. are unable to demonstrate that prior to drilling again in the same PCC segment the previous TàMs sock grout had reached the required strength.
| 01CV - Civils | Cxxx-NCR-000458 | NCR | TCR GS2 TaM Drilling Out-of-Tolerance |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-10-09 | 2012-10-01 | -8 | 2012-09-25 | Geotechnical Engineering - Compensation Grouting | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | When drilling hole T2/44 an obstruction was encountered at a depth of approximately 31m and it was not possible to progress the hole any further. The TaM was installed to a depth of 31m (1.75m short of the design length). The TaM will be maxibore surveyed to establish any deviation out-of-tolerance.
| 01CV - Civils | Cxxx-NCR-000459 | NCR | TaMs installed Out of tolerance in BOS GS4 |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-10-15 | 2012-10-01 | -14 | 2012-10-01 | Geotechnical Engineering - Compensation Grouting | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | Further to BOS-CRL NCR-Cxxx-00378 The following TaMs have been drilled short of design length/out of tolerance and have been corrected/use as is: B4/17: 604 mm out of horizontal tolerance- 1142mm out of tolerance for vertical deviation – New re-drill B4/17A to achieve coverage B4/17a: 171 mm out of horizontal tolerance – Within allowable horizontal spacing – Use as is 2148mm out of vertical tolerance- Above 4.5m exclusion zone and with design band-Use as is B4/18: Abandoned – New redrill B4/18A to achieve coverage B4/19: 1676 mm out of horizontal tolerance – Within allowable horizontal spacing – Use as is B4/21: 661 mm out of horizontal tolerance – Within allowable horizontal spacing – Use as is B4/22: 1236 mm out of horizontal tolerance- New re-drill B4/22A to achieve coverage-3822mm out of tolerance for vertical deviation and Ok to use TaM section clear of 4.5m tunnel exclusion zone and extend TaM from BOS 2 B4/23: 405 mm out of horizontal tolerance- – Within allowable horizontal spacing – Use as is -1765mm out of tolerance for vertical deviation and Ok to use TaM section clear of 4.5m tunnel exclusion zone and extend TaM from BOS 2 B4/24: 935mm out of vertical tolerance- Above 4.5m exclusion zone and within design band-Use as is B4/26A: 371mm out of vertical tolerance- Above 4.5m exclusion zone and within design band-Use as is B4/27A: 323mm out of vertical tolerance- Above 4.5m exclusion zone and within design band-Use as is Please refer to DRAFT- BOS 4- Drill Deviation Assessment -14.09.12 and Cxxx--C-DWG-CRT00_ST005_Z-50084
| 01CV - Civils | Cxxx-NCR-000460 | NCR | BOS GS 5 Sleeve Grout Testing Records |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-10-29 | 2012-10-24 | -5 | 2012-09-28 | Geotechnical Engineering - Compensation Grouting | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | There is only one field grout test form available that recorded the batching and testing of the sleeve grout during the drilling operations at BOS GS5 which doesn't sufficiently cover the all the sleeve grouting operations that were undertaken. These forms record the results of flow & bleed tests and mud balance (specific gravity).
| 01CV - Civils | Cxxx-NCR-000463 | NCR | Damaged Inclinometer |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-05-03 | 2013-01-23 | -100 | 2012-10-01 | Surveying - Instrumentation and Monitoring | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | This instrument is currently damaged and can not be read.
| 01CV - Civils | Cxxx-NCR-000467 | NCR | Layout of TCR WTH Earthing Mat System |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-10-14 | 2012-10-19 | 5 | 2012-10-01 | Electrical - Electrical Engineering General | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | Earthing Mat altered to suit attached drawing showing the layout due to sub-contractor not turning up with the materials required for the job.
| 01CV - Civils | Cxxx-NCR-000482 | NCR | TCR GS2 Grout Test Cubes |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-10-31 | 2012-11-23 | 23 | 2012-10-03 | Shafts - Excavation | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Cube samples were not taken at the time of mixing the grout
| 01CV - Civils | Cxxx-NCR-000483 | NCR | TaMs installed Out of tolerance in BOS GS2 |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-10-31 | 2012-10-04 | -27 | 2012-10-03 | Geotechnical Engineering - Compensation Grouting | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | The following TaMs have been drilled short of design length/out of tolerance and have been corrected/use as is(DRAFT): B2/1 – 219mm out of tolerance on plan – Propose acceptable, as slightly in excess of tolerance, and at outer boundary - Use as is B2/2- 320mm horizontal deviation – within allowable spacing in plan – Use as is - 560mm vertical deviation – above exclusion zone and within design band - Use as is B2/3- 345mm horizontal deviation – within allowable spacing in plan – use as is - 1030mm vertical deviation – above exclusion zone and outside design band. However, only 830mm below band - Use as is B2/4- 620mm vertical deviation – above exclusion zone and within design band - Use as is B2/7- 1220mm vertical deviation – above exclusion zone and within design band - Use as is B2/8- 421mm out of tolerance on plan-Propose acceptable, as slightly in excess of tolerance, and at outer boundary - Use as is - 410mm vertical deviation – above exclusion zone and within design band - Use as is B2/9- 1495mm horizontal deviation – within allowable spacing in plan – Use as is B2/11- 6mm horizontal deviation – within allowable spacing in plan – Use as is - 750mm vertical deviation – above exclusion zone and within design band - Use as is B2/12- 16mm horizontal deviation – within allowable spacing in plan – Use as is - 600mm vertical deviation – above exclusion zone and within design band - Use as is B2/13 – 611mm horizontal deviation-6mm out of tolerance on plan – Propose acceptable, as slightly in excess of tolerance, and at outer boundary - Use as is B2/15- 116mm horizontal deviation – within allowable spacing in plan – Use as is - 710mm vertical deviation – above exclusion zone and within design band - Use as is B2/16- 1230mm vertical deviation – above exclusion zone and within design band - Use as is B2/17- 110mm vertical deviation – above exclusion zone and within design band - Use as is B2/18- 709mm horizontal deviation – within allowable spacing in plan – Use as is - 240mm vertical deviation – above exclusion zone and within design band - Use as is B2/19- 1015mm horizontal deviation – within allowable spacing in plan – Use as is - 560mm vertical deviation – above exclusion zone and within design band - Use as is B2/20- 451mm horizontal deviation – within allowable spacing in plan – Use as is - 190mm vertical deviation – above exclusion zone and within design band - Use as is B2/21 – 1031mm horizontal deviation-859mm out of tolerance on plan –Propose Redrill B2/21A B2/22- 1300mm of vertical deviation – above exclusion zone and outside design band. However, only 660mm above band - Use as is B2/23- 358mm horizontal deviation – within allowable spacing in plan – Use as is - 1530mm vertical deviation – above exclusion zone and within design band - Use as is B2/24 –1145mm horizontal deviation-123mm out of tolerance on plan – Propose acceptable, as slightly in excess of tolerance - Use as is B2/25- Drilled short 47.7m – Propose Redrill B2/25A B2/25A –29mm horizontal deviation-178mm out of tolerance on plan – Propose acceptable, as slightly in excess of tolerance - Use as is B2/26- 198mm horizontal deviation – within allowable spacing in plan – Use as is B2/27- 990mm vertical deviation – above exclusion zone and outside design band. However, only 1440mm above band - Use as is B2/29- 340mm horizontal deviation – within allowable spacing in plan – Use as is B2/37 – 1055mm horizontal deviation-1009mm out of tolerance on plan –Propose Redrill B2/37A B2/41- 514mm horizontal deviation – within allowable spacing in plan – Use as is - 420mm vertical deviation – above exclusion zone and within design band - Use as is B2/45- 600mm vertical deviation – above exclusion zone and within design band - Use as is B2/46- 548mm horizontal deviation – within allowable spacing in plan – Use as is - 400mm vertical deviation – above exclusion zone and within design band - Use as is B2/49- 212mm horizontal deviation – within allowable spacing in plan – Use as is - 590mm vertical deviation – above exclusion zone and within design band - Use as is B2/53-270mm vertical deviation – above exclusion zone and within design band - Use as is B2/57-240mm vertical deviation – above exclusion zone and within design band - Use as is B2/59-920mm vertical deviation – above exclusion zone and within design band - Use as is B2/61-280mm vertical deviation – above exclusion zone and within design band - Use as is B2/64- 333mm horizontal deviation – within allowable spacing in plan – Use as is B2/65-340mm vertical deviation – above exclusion zone and within design band - Use as is B2/67-430mm vertical deviation – above exclusion zone and within design band - Use as is B2/68- 64mm horizontal deviation – within allowable spacing in plan – Use as is - 450mm vertical deviation – above exclusion zone and within design band - Use as is B2/69-260mm vertical deviation – above exclusion zone and within design band - Use as is B2/73-810mm vertical deviation – above exclusion zone and within design band - Use as is B2/78- 1484mm horizontal deviation – within allowable spacing in plan – Use as is - 100mm vertical deviation – above exclusion zone and within design band - Use as is B2/81-650mm vertical deviation – above exclusion zone and within design band - Use as is B2/82- 103mm horizontal deviation – within allowable spacing in plan – Use as is - 1300mm vertical deviation – above exclusion zone and within design band - Use as is B2/83- 367mm horizontal deviation – within allowable spacing in plan – Use as is - 600mm vertical deviation – above exclusion zone and within design band - Use as is B2/84- 489mm horizontal deviation – within allowable spacing in plan – Use as is - 100mm vertical deviation – above exclusion zone and within design band - Use as is B2/85-1160mm vertical deviation – above exclusion zone and within design band - Use as is B2/86-700mm vertical deviation – above exclusion zone and within design band - Use as is B2/89 – 285mm out of tolerance on plan – Propose acceptable, as slightly in excess of tolerance, and at outer boundary - Use as is - 2030mm vertical deviation – above exclusion zone and outside design band. However, only 680mm band - Use as is B2/93-1130mm vertical deviation – above exclusion zone and within design band - Use as is B2/94-560mm vertical deviation – above exclusion zone and within design band - Use as is B2/97-550mm vertical deviation – above exclusion zone and within design band - Use as is B2/100-110mm vertical deviation – above exclusion zone and within design band - Use as is B2/101- 83mm horizontal deviation – within allowable spacing in plan – Use as is - 20mm vertical deviation – above exclusion zone and within design band - Use as is B2/102- 34mm horizontal deviation – within allowable spacing in plan – Use as is B2/103- 176mm horizontal deviation – within allowable spacing in plan – Use as is The following TaMs are awaiting results of Maxibor/processing: B2/30- 36 , B2/37A-40, B2/43-44,B2/47-48,B2/50-51,B2/55-56, B2/62-63, B2/70-72,B2/74-B2/77, B2/79-80, B2/87-88,B2/90-92, B2/95-96, B2/98-99 Please refer to DRAFT- BOS 2- Drill Deviation Assessment -28.09.12 and Cxxx--C-DWG-CRT00_ST005_Z-50081
| 01CV - Civils | Cxxx-NCR-000490 | NCR | ITP Checksheets not filled in |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-10-19 | 2012-10-16 | -3 | 2012-10-05 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | During joint surveillance the following was highlighted: ITP Cxxx--C-ITP-CRT00_ST005-50104 (Inspection and Test Plan - TCR WTH Level - 5 RC Slab Works) Checksheets not being completed on site by . Checksheets checked a number of days after completion of works on site. No B3 044a checksheets (pre/post pour check sheets for blinding). works completed last week No B5 064 checksheets (Reinforcement check sheet upon delivery). Deliveries started early last week
| 01CV - Civils | Cxxx-NCR-000492 | NCR | TCR WTH SAA 9 and 11 Loss of Data |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-10-10 | 2012-10-11 | 1 | 2012-10-08 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | Data Cable between instrument and data logger damaged by Excavator in removing adjacent spoil heap resulting in loss of data over weekend 6th and 7th October.
| 01CV - Civils | Cxxx-NCR-000493 | NCR | Dowels drilled and installed in incorect position |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-10-19 | 2012-10-11 | -8 | 2012-10-10 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | The dowels for the central column (11no.) were drilled and fixed in incorrect positions in the column in plan, meaning dowels would not have penetrated the central column cage.
| 01CV - Civils | Cxxx-NCR-000514 | NCR | -5 RC slab (Pour 1) Pre-pour inspection check sheet procedure |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-10-19 | 2012-10-26 12:35 | 7 | 2012-10-12 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Reject |  | Complete |  | Completed |  | Inspection and Test Plan (Cxxx--C-ITP-CRT00_ST005-50104) Check sheet 044a was filled in and signed off by site Engineer before completion and inspection of works on site. Activities: B4 (Water Bar at Construction Joint), B7 (Reinforcement fixing check) and B14 (Install of Filler board)
| 01CV - Civils | Cxxx-NCR-000518 | NCR | TCR WTH Pour 1 incorrect reinforcement |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-10-30 | 2012-10-23 | -7 | 2012-10-16 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | To much cover.
| 01CV - Civils | Cxxx-NCR-000523 | NCR | TaMs installed out of tolerance in BOS GS5 |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-10-31 | 2012-10-29 15:26 | -2 | 2012-10-17 | Geotechnical Engineering - Compensation Grouting | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | The following TaMs are out of design tolerance: 1,2,3,10,14,1518,25,26,28,33,34,35,48,54. The following TaM is damaged: 19
| 01CV - Civils | Cxxx-NCR-000524 | NCR | Tottenham Court Road Western Ticker Hall - Principal Site Control |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-10-24 | 2012-11-15 12:30 | 22 | 2012-10-18 | Surveying - GIS Engineering & Land Surveying | 500 |  | System Defect | Rework |  | Complete |  | Completed |  | Above not done. Established during independent check of principal site control undertaken by Crossrail
| 01CV - Civils | Cxxx-NCR-000527 | NCR | TCR GS 7 TaMs out of tolerance |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-11-02 | 2012-10-24 14:48 | -9 | 2012-10-19 | Geotechnical Engineering - Compensation Grouting | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | After completing all required redrills for horizontal spacing TaMs 1, 3a, 5, 8a, 10, 13, 14a and 16 have been identified as out of vertical tolerance.
| 01CV - Civils | Cxxx-NCR-000531 | NCR | Pour 2 |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-11-02 | 2012-11-21 18:56 | 19 | 2012-10-22 | Structural Engineering - Structural Engineering - General | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | Drainage runs supported vertically from threaded bars attached to both top and bottom mat. Not all bottom threaded bars installed, despite agreement that this would be done during inspection with CRL. Drainage chamber shutter not completed in advance of pour, thus decision made on site to install an oversize box out in hy-rib and face up final size. At a later date.
| 01CV - Civils | Cxxx-NCR-000533 | NCR | NW Shaft Level -4 Core Bit Jam |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-10-26 | 2012-11-15 12:39 | 20 | 2012-10-23 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | During coring of the L-4 dowels and pouring holes for continuity through column 2 the core barrel became jammed in the hole.
| 01CV - Civils | Cxxx-NCR-000537 | NCR | Insufficient Concrete cover to reinforcement |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-11-07 | 2012-11-23 14:10 | 16 | 2012-10-24 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Insufficient concrete cover to reinforcement (measured 25mm)
| 01CV - Civils | Cxxx-NCR-000541 | NCR | TCR Western Ticket Hall Pour 2 - TOC Control |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-02-11 | 2012-11-01 13:05 | 264 | 2012-10-25 | Structural Engineering - Finishes | 500 |  | Planning | Rework |  | Complete |  | Completed |  | TOC for pour 2 is acceptable, with approx 10mm variation. However the couplers for the walls kicking off the slab have been buried beneath the 'fat' of the grout, requiring scabbling to uncover.
| 01CV - Civils | Cxxx-NCR-000554 | NCR | Rebate in Pour 2 B |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-11-13 | 2012-11-20 19:47 | 7 | 2012-10-31 | Structural Engineering - Concrete Member | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | The slab was cast with a 150x150mm rebate in the pour 2 area. Shown in red in the attached sketch. No 20x20mm fillet was cast in place.
| 01CV - Civils | Cxxx-NCR-000557 | NCR | BOS 1 Sleeve Grout Testing Records |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-11-15 | 2012-11-27 19:27 | 12 | 2012-11-01 | Geotechnical Engineering - Compensation Grouting | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | There are no field grout test forms available that recorded the batching and testing of the sleeve grout during the drilling operations at BOS GS 1. These forms record the results of flow & bleed tests and mud balance (specific gravity).
| 01CV - Civils | Cxxx-NCR-000558 | NCR | TCR 1 Sleeve Grout Testing Records |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-11-30 | 2012-11-27 20:13 | -3 | 2012-11-01 | Geotechnical Engineering - Compensation Grouting | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | There are no field grout test forms available that recorded the batching and testing of the sleeve grout during the drilling operations at TCR GS 1. These forms record the results of flow & bleed tests and mud balance (specific gravity).
| 01CV - Civils | Cxxx-NCR-000567 | NCR | Level -5 Slab Sump water ingress |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-02-28 | 2013-01-16 10:33 | -43 | 2012-11-08 | Structural Engineering - Concrete Member | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Joint in concrete allowing water ingress
| 01CV - Civils | Cxxx-NCR-000578 | NCR | Incomplete as-built information for TCO heading advance 1 |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-01-10 | 2012-12-17 18:08 | -24 | 2012-11-19 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | As-records for excavated profile were not taken for the complete profile of advance profile as required by clause KT20.3203 c). Readings were taken from shoulder to shoulder, rather than the full excavted profile (axis to axis)
| 01CV - Civils | Cxxx-NCR-000579 | NCR | Insufficient lining thickness of TCO heading advance 1 |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-01-12 | 2013-01-17 | 5 | 2012-11-19 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | Due to under excavation the primary lining was of insuffieint thickness
| 01CV - Civils | Cxxx-NCR-000580 | NCR | Incorrect bench advance sequence |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-11-23 | 2012-11-26 11:07 | 3 | 2012-11-19 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The bench was mucked and intially sealed after being advanced only 1m.
| 01CV - Civils | Cxxx-NCR-000581 | NCR | Heading / Bench located at incorrect level TCO advance 1 |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-11-23 | 2012-11-29 09:48 | 6 | 2012-11-19 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The heading to joint was installed at a level approximately 440mm above that shown on the drawing
| 01CV - Civils | Cxxx-NCR-000582 | NCR | Heading / Bench joint located at incorrect level TCO advance 2 |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-12-10 | 2012-12-17 | 7 | 2012-11-19 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The heading to joint was installed at a level approximately 440mm above that shown on the drawing
| 01CV - Civils | Cxxx-NCR-000583 | NCR | TCO heading advance 6 |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-11-30 | 2012-11-26 | -4 | 2012-11-21 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | 1) An attempt was made to lap reinforcement between advances, not a requirement of the design. 2) The advance was under excavated in several places. 3) The initial layer was of insufficient thickness. 4) The circle joint was of insufficient quality. 5) There was evidence of clay inclusion in the initial lining.
| 01CV - Civils | Cxxx-NCR-000591 | NCR | Cxxx-BFK-SCL-BOS-Reduced accelerator usage |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-12-07 | 2012-11-26 | -11 | 2012-11-23 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | The invert lining from chainage 2.75 - 4.75 in the TCO tunnel was accidently sprayed at a reduced accelerator percentage (2%) and therefore did not achieve the required strength gain. The invert concrete was removed and re-installed by the following day shift crew.
| 01CV - Civils | Cxxx-NCR-000592 | NCR | Testing and Commissioning of BOS Batching Plant ITP |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-12-07 | 2012-12-12 | 5 | 2012-11-27 | Tunnelling - Tunnelling General | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | ITP has not been issued to PM for acceptance. Batching plant now erected and trials being undertaken.
| 01CV - Civils | Cxxx-NCR-000594 | NCR | Temperature of Shotcrete |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-12-20 | 2013-01-31 | 42 | 2012-11-27 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | The temperatures of the concrete have been consistantly below 15 deg C when measured at the point of aplication.
| 01CV - Civils | Cxxx-NCR-000596 | NCR | Shotcrete |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-11-08 | 2012-12-07 | 29 | 2012-11-29 | Tunnelling - Linings - In-situ Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | There are record sheets which are incoplete and have been left blank. The flow tests are also blank.
| 01CV - Civils | Cxxx-NCR-000597 | NCR | Incorrect excavation in TCO Advance 13 Top Heading |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-12-20 | 2013-01-17 | 28 | 2012-11-29 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | During excavation for the Advance 13, the chainage was significantly overmucked in part of the face. The affected area is from the 11 o'clock to 10 o'clock position looking in-bye. The engineer was controlling the chainage using the specified profile system, and informed the excavator driver to muck a further "50". At this point the __ operator buried the breaking hammer into the face and arced the bucket towards the left knee (anti-clockwise). The engineer was talking in millimetres, the continental system is centimetres, hence the misunderstanding. Once the loose material was removed, the upper half of the face had been overmucked by around 600mm. The lower half was then mucked to the correct chainage, giving a sloped profile in the longitudinal section. The profile was trimmed and the excavation sealed.
| 01CV - Civils | Cxxx-NCR-000599 | NCR | Curing of test specimens |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-01-12 | 2013-01-17 14:10 | 5 | 2012-11-30 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Curing of core specimens taken form trail panels sprayed on the 27th November for strength tests was not taking place. The cores were seen stored at 10 a.m. on the 28th November in an open site hut in a dry condition. The ambient temperature at the time was 8ºC
| 01CV - Civils | Cxxx-NCR-000602 | NCR | Incorrect excavation in TCO Advance 13 Top Heading |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-12-17 | 2012-12-03 18:07 | -14 | 2012-12-03 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | During excavation for the Advance 13, the chainage was significantly overmucked in part of the face. The affected area is from the 11 o'clock to 10 o'clock position looking in-bye. The engineer was controlling the chainage using the specified profile system, and informed the excavator driver to muck a further "50". At this point the __ operator buried the breaking hammer into the face and arced the bucket towards the left knee (anti-clockwise). The engineer was talking in millimetres, the continental system is centimetres, hence the misunderstanding. Once the loose material was removed, the upper half of the face had been overmucked by around 600mm. The lower half was then mucked to the correct chainage, giving a sloped profile in the longitudinal section. The profile was trimmed and the excavation sealed.
| 01CV - Civils | Cxxx-NCR-000603 | NCR | BOS ETH TCO Advance 19 |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-12-17 | 2012-12-03 18:11 | -14 | 2012-12-03 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Concrete for the sealing layer of adv.19 was not at the required temperature of 15°C (given by 12 Section KT20 Materials and Workmanship Specification - Sprayed Concrete Linings). As a result the early age strength of the concrete was not at the necessary level. Additionally, the engineers record keeping was not up to standard.
| 01CV - Civils | Cxxx-NCR-000608 | NCR | Cxxx-BFK-SCL-BOS-Concrete below 15 degrees used in lining |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-12-20 | 2013-01-17 14:17 | 28 | 2012-12-06 | Tunnelling - Linings - Sprayed Concrete | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | On the advance of the top heading to chainage 12.1, concrete at a temperature below 15 degrees was allowed to be included in the works, going against the requirements in the ITP (and KT20 Specification). The construction of the TCO tunnel is currently on hold, and it is noted that this concrete has subsequently gained sufficient strength in line with the requirements of the specification, however the decision to allow the concrete outside specified temperature range to be included in the lining contradicts the ITP.
| 01CV - Civils | Cxxx-NCR-000610 | NCR | SCL Delivery, back up maintenance and thermometer calibration records. |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-01-03 | 2013-02-28 15:11 | 56 | 2012-12-06 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Records were not made available as agreed during surveillance SQ410-04 of 28th November with respect to the maintenance of the SCL pumps ,pipelines and Trolexc thermometer serial number 462 calibration The contractor therefore failed to demonstrate that he maintains contemporaneous records
| 01CV - Civils | Cxxx-NCR-000616 | NCR | BOS GS1 Plug Grout Records |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-12-21 | 2012-12-12 17:37 | -9 | 2012-12-07 | Geotechnical Engineering - Compensation Grouting | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | There a plug grout cube results only for 4 TaMs at BOS GS1. In addition to this results for TaM No 1 are below the expected strength for the 7,13 and 28 day tests.
| 01CV - Civils | Cxxx-NCR-000617 | NCR | BOS GS1 TaMs Drilled Out of Tolerance |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-12-21 | 2012-12-07 13:27 | -14 | 2012-12-07 | Geotechnical Engineering - Compensation Grouting | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The following TàMs are out of vertical design tolerance: 1,2,4,4a,5,6,7,8,9,14,14a,15,16,17,19a,20,21,23,24,25,26,27,29,29a,30,31,32,33,41,45,46,47,48,51,52,52A,53,55,56,58,59,60,61,62,63,65,67,69,70,72,73,75 The following TàMs are outside the design band: 2,9,14a,20,21,23,27,29a,46,55,56,70 See attached drill deviation assessment for full details.
| 01CV - Civils | Cxxx-NCR-000618 | NCR | Grout Jacking without accepted ITP |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-01-10 | 2013-02-07 | 28 | 2012-12-10 | Shafts - Grouting | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | Grout Jacking started without accepted ITP.
| 01CV - Civils | Cxxx-NCR-000619 | NCR | Cxxx-BFK-SCL-BOS-Insufficient frequency of 12 hour strength test |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-01-31 | 2013-01-21 | -10 | 2012-12-10 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | have not carried a sufficient number of tests up to 12 hours during the sprayed concrete works on the TCO tunnel
| 01CV - Civils | Cxxx-NCR-000620 | NCR | Cxxx-BFK-SCL-BOS-Convergence pins installed too high (TCO array 2) |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-12-24 | 2013-01-17 14:35 | 24 | 2012-12-10 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | The convergence pins (6 and 7) were installed much higher in the tunnel profile than agreed, and therefor do not provide the convergence information to correlate to the prescribed trigger levels.
| 01CV - Civils | Cxxx-NCR-000621 | NCR | On site batching plant QMS |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-03-29 | 2013-03-21 13:40 | -8 | 2012-12-11 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | There is no inspection and test plan / procedure in place for the on site batching plant
| 01CV - Civils | Cxxx-NCR-000625 | NCR | TCR GS1 Plug Grout Records |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-12-26 | 2012-12-12 18:10 | -14 | 2012-12-12 | Geotechnical Engineering - Compensation Grouting | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | There a plug grout cube results only for 21 out of 101 drilled TaMs at TCR GS1. Additionly no 2 day tests were carried out and the 7 day tests on some TaMs show an inffucient strength.
| 01CV - Civils | Cxxx-NCR-000630 | NCR | TCR GS1 TaMs Drilled out of Tolerance |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-01-17 | 2013-01-03 12:10 | -14 | 2012-12-14 | Geotechnical Engineering - Compensation Grouting | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | 59 TaMs are out of vertical tolerance. 20 TaMs are outside the design band. 11 TaM spacings are over 4m. Please see attached drill deviation spreadsheet for exact values.
| 01CV - Civils | Cxxx-NCR-000631 | NCR | Incorrect joint detail on Advance 15 of TCO |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-02-01 | 2013-02-15 13:58 | 14 | 2012-12-15 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Bars met the overlap requirement, however they were bent at the joint in order for the mesh to put into place. This resulted in a 'kink' in the bar.
| 01CV - Civils | Cxxx-NCR-000643 | NCR | BFK-SCL-BOS-Invert advance out of sequence |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-01-31 | 2013-01-31 13:41 | 0 | 2013-01-17 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | A short invert advance was complete to chainage 15.9 on the right hand side of the face and 16.6 on the left hand side to bring the face to the correct angle to follow the angle of the wedges which was different to the sequence agreed on the RESS and in the SRG.
| 01CV - Civils | Cxxx-NCR-000646 | NCR | TCR GS 7 - TaM drill lengths |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-02-04 | 2013-01-21 12:41 | -14 | 2013-01-21 | Geotechnical Engineering - Compensation Grouting | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | TaMs 3A, 8A and 9A deisn lengths were 54.75, 83.75 and 88.75 metres respectfully. However the asbuilt lengths are 57.75, 88.75 and 87.75 metres.
| 01CV - Civils | Cxxx-NCR-000657 | NCR | Cxxx-BFK-SCL-Pile 128 saw cut out of sequence |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-02-06 | 2013-01-31 14:57 | -6 | 2013-01-23 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Two wire saw cuts were made 3/4 of the way through the pile in the bottom half of the pile prior to the removal of the removal of the top half of the pile.
| 01CV - Civils | Cxxx-NCR-000660 | NCR | No invert profile control in advance 33 TCO |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-02-12 | 2013-02-08 14:05 | -4 | 2013-01-29 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Invert Advance number 33(Ch. 17 - 18) in the TCO was sprayed without the excavated profile control and the lining thickness could not be verified.
| 01CV - Civils | Cxxx-NCR-000662 | NCR | Unaproved mix used in AP3A advance 3 |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-02-12 | 2013-02-04 19:01 | -8 | 2013-01-29 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | On Sunday 27/1/13 unaproved mixed concrete was used in advance number 3 (Ch. 1 - 2) of the AP3A.
| 01CV - Civils | Cxxx-NCR-000663 | NCR | Over excavation of AP3A adavance Number 3 |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-02-12 | 2013-02-07 16:31 | -5 | 2013-01-29 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | During excavation of unaproved mix concrete from AP3A advance number 3 (Ch 1-2m) over excavation occured.
| 01CV - Civils | Cxxx-NCR-000665 | NCR | Temperature below 15 degrees |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-02-12 | 2013-02-04 19:04 | -8 | 2013-01-31 | Tunnelling - Linings - Sprayed Concrete | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | Shotcerete sprayed for Advance 5 (Ch 2 to 3m) in the AP3A was sprayed at 14.4 degrees celcius
| 01CV - Civils | Cxxx-NCR-000671 | NCR | BOS GS 3 - TaM drill deviations |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-02-17 | 2013-02-08 14:09 | -9 | 2013-02-02 | Geotechnical Engineering - Compensation Grouting | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | As an amendment to NCR 00229 please refer to attached drill deviation table summarising the TaMs that are our of tolerance. Specifically: 5 - installed at 19m after obstruction encountered. 21 - installed at 24m after obstruction encountered. Out of horizontal tolerance: 5A, 8, 8A, 9, 10, 22, 23, 26, 27, 28, 32, 34, 35, 38, 38A, 39, 40, 42, 44, 45, 46, 49, 50A, 51, 57. Out of vertical tolerance: 8A, 9, 21A, 23A, 24, 25, 29, 30, 32, 33A, 34, 35, 38A, 39, 41A, 43A, 46, 49, 50A, 53, 54, 57. Outside design band: 9, 23A, 33A, 39, 41A.
| 01CV - Civils | Cxxx-NCR-000674 | NCR | L Shaped bars for headwall reinforcement |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-02-25 | 2013-02-08 14:12 | -17 | 2013-02-04 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | In Invert Advance 8 & 9 of the AP3A, 5 no. 20mm L bars where replaced with 5 * 2 * 16mm bars (bent on site). As they ran out of the 20mm bars on site.
| 01CV - Civils | Cxxx-NCR-000675 | NCR | Advances 8&9 of the AP3A sprayed at once instead of Seperately |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-02-28 | 2013-02-08 14:26 | -20 | 2013-02-05 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Primary lining for Advances 8 and 9 wheres sprayed at once instead of seperately as was indicated on the RESS
| 01CV - Civils | Cxxx-NCR-000680 | NCR | Temperature Below 15 degrees |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-02-27 | 2013-02-08 14:28 | -19 | 2013-02-06 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Shotcerete sprayed for Advance 10 (Ch 3.94 to 4.94m) in the AP3A was sprayed at 14.6 degrees celcius
| 01CV - Civils | Cxxx-NCR-000681 | NCR | CPI mix used for sealing |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-02-27 | 2013-02-19 13:52 | -8 | 2013-02-06 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | In advance 10 (Ch 3.94 to 4.94m) CPI mix was used as a sealing coat as the mix concrete that arrived woulfd not pump.
| 01CV - Civils | Cxxx-NCR-000682 | NCR | Insufficent Thickness of Headwall |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-02-27 | 2013-02-07 15:28 | -20 | 2013-02-06 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | While spraying the heading headwall after advance 7 in AP3A insufficent thickness of shotcrete was applied.
| 01CV - Civils | Cxxx-NCR-000683 | NCR | Insufficnent Doming of Headwall |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-02-27 | 2013-02-12 12:49 | -15 | 2013-02-06 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Doming of the Headwall before advance 10 in AP3A is not as per the Drawings. Data could not be entered into the profile control system so the profile was sprayed inaccurately.
| 01CV - Civils | Cxxx-NCR-000684 | NCR | Late installation of Monitoring Sections |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-02-28 | 2013-02-26 13:10 | -2 | 2013-02-07 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Monitoring section in advance 5 of the AP3A according to RESS AP3A-028 was meant to be installed on the 30.01.13 but was not.
| 01CV - Civils | Cxxx-NCR-000688 | NCR | Kwikastrips installed at the wrong level |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-03-01 | 2013-02-12 12:55 | -17 | 2013-02-08 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Kwikastrips in advance 5 of the AP3A where installed at the incorrect level.
| 01CV - Civils | Cxxx-NCR-000691 | NCR | Spraying when ambient temperature is below 5°C |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-02-25 | 2013-02-21 15:31 | -4 | 2013-02-11 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Spraying of shot concrete for final part of soft eye when ambient temperature is below 5 degrees.
| 01CV - Civils | Cxxx-NCR-000692 | NCR | Temperatur below 15 degrees |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-03-04 | 2013-02-11 14:24 | -21 | 2013-02-11 | Tunnelling - Linings - Sprayed Concrete | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | Shotcerete sprayed for Advance 20 (Ch 13.94 to 14.94m) in the AP3A was sprayed at 14.1 degrees celcius
| 01CV - Civils | Cxxx-NCR-000693 | NCR | RESS not clarly displayed at excavatiom |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-03-04 | 2013-02-26 18:04 | -6 | 2013-02-11 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | During a surveilance on the 6/2/20134 it was observed that the current RESS was not displayed at the excavation. Although it was in the engineers posession.
| 01CV - Civils | Cxxx-NCR-000694 | NCR | Temperature Below 15 degrees |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-02-25 | 2013-02-12 12:57 | -13 | 2013-02-11 | Tunnelling - Linings - Sprayed Concrete | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | Shotcerete sprayed for Advance 21 (Ch 14.94 to 15.94m) in the AP3A was sprayed at 14.8 degrees celcius
| 01CV - Civils | Cxxx-NCR-000695 | NCR | Temperature below 15 degrees |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-02-25 | 2013-02-12 13:00 | -13 | 2013-02-11 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Shotcerete sprayed for Advance 17 (Ch 10.94 to 11.94m) in the AP3A was sprayed at 13 degrees celcius
| 01CV - Civils | Cxxx-NCR-000696 | NCR | Temperature below 15 degrees |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-02-25 | 2013-02-12 13:31 | -13 | 2013-02-11 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Shotcerete sprayed for Advance 22 (Ch 15.94 to 16.94m) in the AP3A was sprayed at 13.1 degrees celcius
| 01CV - Civils | Cxxx-NCR-000697 | NCR | No invert profile control in advance 4 AP3A |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-03-05 | 2013-02-12 16:42 | -21 | 2013-02-12 | Tunnelling - Linings - Sprayed Concrete | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | Invert Advance number 4 in the AP3A was sprayed without the excavated profile control and the lining thickness could not be verified.
| 01CV - Civils | Cxxx-NCR-000699 | NCR | Hot water thermostat calibration |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-04-12 | 2013-04-04 13:54 | -8 | 2013-02-13 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | No calibration records available for Batching plant hot water thermostat. Thermostat was confirmed during surveillance of 12 February 2013 to be set at 21ºC yet hot water tank thermometer was reading 29 ºC.
| 01CV - Civils | Cxxx-NCR-000700 | NCR | Storage temperature of concrete mix additives |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-06-26 | 2013-06-03 09:41 | -23 | 2013-02-13 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | During surveillance of 12/02/2013 the Contractor could not demonstrate compliance with the manufacturers recommendation for minimum storage temperatures of concrete mix additives in use.
| 01CV - Civils | Cxxx-NCR-000701 | NCR | Temperature of Shotcrete below 15 degrees |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-02-28 | 2013-02-18 13:56 | -10 | 2013-02-13 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Shotcerete sprayed for Advance 25 (Ch 18.94 to 19.94m) in the AP3A was sprayed at 13.4 degrees celcius
| 01CV - Civils | Cxxx-NCR-000702 | NCR | Temperature of Shotcrete below 15 degrees and air temp below 5 degrees |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-03-06 | 2013-02-14 16:41 | -20 | 2013-02-13 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Shotcrete sprayed for Advance 24 (Ch 17.94 to 18.94m) in the AP3A was sprayed at 13.5 degrees celcius when the air temperatur was 3 degrees.
| 01CV - Civils | Cxxx-NCR-000703 | NCR | Temperature of Shotcrete below 15 degrees |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-02-28 | 2013-02-14 16:43 | -14 | 2013-02-14 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Shotcerete sprayed for Advance 27 (Ch 20.94 to 21.94m) in the AP3A was sprayed at 13.8 degrees celcius
| 01CV - Civils | Cxxx-NCR-000707 | NCR | Early age testing procedures not being followed |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-03-01 | 2013-02-26 09:10 | -3 | 2013-02-15 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Some test results are unavailable for the advances that have been sprayed and the required testing has not happened.
| 01CV - Civils | Cxxx-NCR-000712 | NCR | Temperature below 15 degrees |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-03-04 | 2013-02-21 15:38 | -11 | 2013-02-18 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Temperature of sprayed concrete was 14 and 14.5 degrees at the point of spray (chainage from 1.14 to 2.14) on 14/02/13 night shift.
| 01CV - Civils | Cxxx-NCR-000716 | NCR | Temperature below 15 degrees |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-03-04 | 2013-02-21 15:42 | -11 | 2013-02-18 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Temperature of sprayed concrete was 13.7 degrees at the point of spray (chainage from 7.002 to 7.782) on 17/02/13 morning shift.
| 01CV - Civils | Cxxx-NCR-000718 | NCR | Primary lining out of tolerance |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-03-05 | 2013-03-05 14:38 | 0 | 2013-02-19 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Pilot tunnel CH1 Chainage 9.35 over sprayed 100 mm - 220 mm.
| 01CV - Civils | Cxxx-NCR-000722 | NCR | TCR conrete batching plant |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-05-30 | 2013-04-19 16:18 | -41 | 2013-02-22 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Objective evidence that the calibration was undertaken in a manner traceable to nationally recognised standards was not made avaialbe
| 01CV - Civils | Cxxx-NCR-000723 | NCR | TCR conrete batching plant QMS |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-05-30 | 2013-04-19 16:22 | -41 | 2013-02-22 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Contractors ISO 9001 certified quality management system is incomplete with respect to for operations associated with running the site concrete batching plant
| 01CV - Civils | Cxxx-NCR-000724 | NCR | TCR conrete batching plant cold weather working |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-04-11 | 2013-04-12 15:12 | 1 | 2013-02-22 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | There were no measures in place to demonstrate that the minimum temperature requirement was maintained.
| 01CV - Civils | Cxxx-NCR-000725 | NCR | TCR conrete batching plant aggregate MC |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-04-19 | 2013-04-08 13:29 | -11 | 2013-02-22 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Records to demonstrate that the concrete batching plant aggregate moisture sensors were checked were not made avaialble
| 01CV - Civils | Cxxx-NCR-000729 | NCR | Temperature Below 15 degrees |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-03-15 | 2013-02-28 15:43 | -15 | 2013-02-25 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Temperature of sprayed concrete was 13 degrees at advance 35 in AP3A (chainage from 5.6 to 6.6). Temperature of sprayed concrete was 14.5 degrees at advance 33 in AP3A (chainage from 3.8 to 4.6). Temperature of sprayed concrete was 14.8 degrees at advance 31 in AP3A (chainage from 24.94 to 25.94).
| 01CV - Civils | Cxxx-NCR-000730 | NCR | Temperature of air below 5 degrees |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-03-15 | 2013-02-28 15:54 | -15 | 2013-02-25 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Shotcrete sprayed for Initial advance 28 (CH 23 to 24) Shotcrete sprayed for primary lining advance 28 (CH 21.94 to 22.94) Shotcrete sprayed for primary lining advance 38 (CH 7.51 to 8.51)
| 01CV - Civils | Cxxx-NCR-000731 | NCR | Temperature of air below 5 degrees |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-03-15 | 2013-02-28 15:59 | -15 | 2013-02-25 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Shotcrete sprayed for Advance 13 (CH 12.22 to 13.22) Shotcrete sprayed for Advance 12 (CH 11.23 to 12.22)
| 01CV - Civils | Cxxx-NCR-000732 | NCR | Shotcrete Temperature below 15 degrees |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-03-15 | 2013-02-28 16:03 | -15 | 2013-02-25 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Sprayed concrete at LCE1 advance 5 (CH 4.6 to 5.6)
| 01CV - Civils | Cxxx-NCR-000746 | NCR | Temperature of Shotcrete below 15 degrees and air temp below 5 degrees |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-03-15 | 2013-03-05 15:13 | -10 | 2013-02-28 | Tunnelling - Linings - Sprayed Concrete | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | For AP3A: 1. Low air temperatures for advance 40 (CH 8.5 - 9.5m) and 39 (CH 5.55 - 7.51m) 2. Low concrete temperature for advance 41 (CH 9.5 - 10.5m) For LCE1: 3. Low air temperature for advance 19 (CH 17.71 - 18.71m), advance 20 (CH 18.71-20.07m) and advance 21 (20.07-20.98m) 4. Low air and concrete temperatures for advance 28 (CH 26.98 - 27.46), advance 25 (23.98 - 24.98m), advance 23 (CH 21.98-22.98m) and advance 22 (CH 20.98-21.98m)
| 01CV - Civils | Cxxx-NCR-000747 | NCR | Temperature of shotcrete below 15 degrees and air temp below 5 degrees |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-03-15 | 2013-03-05 15:21 | -10 | 2013-02-28 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Low air temperature for advance 43 (CH 10.51 - 11.51m)
| 01CV - Civils | Cxxx-NCR-000748 | NCR | Grout testing results are out of agreed limits |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-04-21 | 2013-04-15 14:31 | -6 | 2013-03-07 | Shafts - Grouting | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Field test results from 19/02/13 and 20/02/13 Flow 380, 320, 380, 440, 380, 140 mm Bleed not recorded on 19/02/13 during day shift Mud balance 1.35, 1.40, 1.35, 1.35, 1.34 and 1.40 kg/m3 Most of the cube results so far according to the Summary table after 28 days more than 10 N/mm2.
| 01CV - Civils | Cxxx-NCR-000749 | NCR | Cube storage - cubes not kept moist |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-03-14 | 2013-03-20 13:04 | 6 | 2013-03-07 | Shafts - Grouting | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | Cubes (BOS Shaft 3) are not covered with hessian and not kept moist.
| 01CV - Civils | Cxxx-NCR-000752 | NCR | Concrete cube curing at Bond St. |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-03-29 | 2013-03-28 17:18 | -1 | 2013-03-01 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Cubes stored at ambient temperature ( between 4 to 7 ºC )cubes in water tank stored at 14 ºC Cubes transported approximately 1 hour after making -no protection form vibration /shock
| 01CV - Civils | Cxxx-NCR-000753 | NCR | Insufficient thickness at Advance 7 |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-03-22 | 2013-03-20 13:43 | -2 | 2013-03-01 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | While spraying the wall of the tunnel at advance 7 in the LCE1 pilot, insufficient thickness of shotcrete was applied. Proof drilling was undertaken and results attached below.
| 01CV - Civils | Cxxx-NCR-000756 | NCR | Insufficient coverage of excavation profile |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-04-26 | 2013-04-15 16:15 | -11 | 2013-03-01 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | While spraying the wall of the tunnel at advance 22, 23 & 24 in the LCE pilot, insufficient thickness of shotcrete was applied.
| 01CV - Civils | Cxxx-NCR-000757 | NCR | Temperature of Shotcrete below 15 degrees |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-03-15 | 2013-03-08 14:43 | -7 | 2013-03-01 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Temperature of sprayed concrete was less than 15 degrees at the point of spray (all the dates, chainages and temperatures attached to NCR).
| 01CV - Civils | Cxxx-NCR-000760 | NCR | Temperature of shotcrete below 5 degrees |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-03-18 | 2013-03-07 14:17 | -11 | 2013-03-04 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Low air temperature (0 degrees) for advance 38 (CH 7.51 - 8.51m)
| 01CV - Civils | Cxxx-NCR-000761 | NCR | Ambient temperature is below 5 degrees |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-03-18 | 2013-03-08 15:01 | -10 | 2013-03-04 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Ambient temperature was less than 5 degrees during spraying (all the dates, chainages and temperatures attached to NCR).
| 01CV - Civils | Cxxx-NCR-000769 | NCR | Temperature of Shotcrete below 15 degrees and air temp below 5 degrees |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-03-19 | 2013-03-08 15:10 | -11 | 2013-03-05 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Low concrete and air temp for advance 50 (CH 15.5 - 16.5m) Low concrete and air temp for advance 48 (CH 11.51 - 13.51m) Low air temp for advance 47 (CH 13.5 to 14.5m) Low concrete and air temp for advance 46 (CH 12.5 - 13.5m)
| 01CV - Civils | Cxxx-NCR-000770 | NCR | AP3A Pilot: insufficient survey records at CH 9.85 |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-03-25 | 2013-03-15 12:55 | -10 | 2013-03-11 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | It was not possible to calculate the lining thickness from the small number of primary survey records.
| 01CV - Civils | Cxxx-NCR-000772 | NCR | Monitoring points not installed in CH1 enlargement |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-04-19 | 2013-04-04 13:28 | -15 | 2013-03-05 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Monitoring points not installed because they will be lower than the level of backfill.
| 01CV - Civils | Cxxx-NCR-000773 | NCR | Rebound incorporated into the Primary Lining of AP3A |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-03-21 | 2013-03-15 13:11 | -6 | 2013-03-07 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The lower LHS of the joint between the Initial Lining and the Primary Lining of Advance 40 was not adequately cleaned and therefore incorporated some rebound in the tunnel lining. During the excavation of Advance 42, the rebound in the tunnel lining in Advance 40 was identified and the sub-standard shotcrete was removed and subsequently replaced during the spray of Advance 42.
| 01CV - Civils | Cxxx-NCR-000775 | NCR | Temperature of Shotcrete below 15 degrees and air temp below 5 degrees AP3A adv 51, 52 |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-03-20 | 2013-03-08 15:22 | -12 | 2013-03-06 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Low air temp for advance 51 (CH 13.5 to 15.5m) Low concrete temp for advance 52 (CH 16.51 to 17.51m)
| 01CV - Civils | Cxxx-NCR-000776 | NCR | Failure to carry out complete set of early age strength tests as per ITP |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-03-21 | 2013-03-21 16:42 | 0 | 2013-03-07 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Some early age strength tests have not been carried out.
| 01CV - Civils | Cxxx-NCR-000777 | NCR | Lining thickness not achieved at chainage 16 of AP3A |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-03-21 | 2013-03-15 13:02 | -6 | 2013-03-07 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Survey records suggest a region at chainage 15.95 where the thickness of the lining does not reach the specified 300mm. Subsequent proof-drilling of the area of the lining identified by the survey data to be between 290mm and 400mm thick. (290mm being the single point of non-conformance).
| 01CV - Civils | Cxxx-NCR-000778 | NCR | Low air and concrete temperature for advance 53 and 54 of AP3A |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-03-21 | 2013-03-08 15:26 | -13 | 2013-03-07 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Low air and concrete temperature for advance 53 (CH 17.51 to 18.51m) Low air and concrete temperature for advance 54 (CH 15.51 to 17.51m)
| 01CV - Civils | Cxxx-NCR-000781 | NCR | Flow test under the specified limit |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-03-22 | 2013-03-26 14:37 | 4 | 2013-03-08 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Flow was less than specified minimum 02/03/13 450 and 460 mm (chainage 2.08 - 3.08) 03/03/13 460 mm (chainage 0.00 - 2.10) 07/03/13 460mm (chainage 2.08 - 4.08)
| 01CV - Civils | Cxxx-NCR-000784 | NCR | Clash of bore 2a of Pali Radice support system with TaM 27 from Grout Shaft 3 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-08-01 | 2013-07-25 10:08 | -7 | 2013-03-14 | Tunnelling - Grouting | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Late availability of IFC drawings resulted in a limited amount of time available for analysing the design and assessing potential constructability issues. This lack of design coordination failed to flag-up the potential for a clash.
| 01CV - Civils | Cxxx-NCR-000798 | NCR | Low air and concrete temperature for advance 64, 65, 66, 67 of AP3A |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-03-28 | 2013-03-18 16:55 | -10 | 2013-03-14 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Low concrete temp. for advance 64 (Headwall) Low concrete temp. for advance 65 (Headwall) Low concrete temp. for advance 66 (3.57 to 4.57m) Low air temp. for advance 67 (4.5 to 5.5m)
| 01CV - Civils | Cxxx-NCR-000799 | NCR | Joint preparation |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-03-28 | 2013-03-21 13:59 | -7 | 2013-03-14 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Instead of kwikastrip and L-bar straight bars where used.
| 01CV - Civils | Cxxx-NCR-000800 | NCR | distance between studs |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-04-12 | 2013-03-21 14:27 | -22 | 2013-03-15 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The distance between studs seen on the test panel for advance 67 of AP3A was less than 70mm for 5 number studs.
| 01CV - Civils | Cxxx-NCR-000805 | NCR | Dowel installation for SE2 & TCO tunnel portal support beam |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-04-03 | 2013-04-19 13:26 | 16 | 2013-03-20 | Tunnelling - Tunnelling General | 500 |  | System Defect | Rework |  | Complete |  | Completed |  | 35mm diameter holes were drilled into the existing 1200mm piles in readiness to receive the 32mm diameter dowel bars. The __ Specification & Procedures recommends a 40mm diameter hole for installing resin and a 32mm diameter bar. Upon attempting to install the bars, it was esablished that they would not fit.
| 01CV - Civils | Cxxx-NCR-000806 | NCR | Breach of amber trigger level at LCE1/2 pilot BOS - response by SRG/CTC |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-03-27 | 2013-03-21 16:15 | -6 | 2013-03-20 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | A amber trigger was suspected to have been breached but not all the relevant parties were notified within the prescribed timescales. Instead, the suspected breach was discussed at the subsequent SRG meeting. The procedure was not (strictly-speaking) followed. Debate between Cxxx site representatives, the Senior SCL Engineer and surveying department concluded: 1. There was confusion around which trigger levels apply to this situation (no specific triggers for LCE1/LCE2 pilot in the Cxxx I&M plan). Concluded that this should be from Figure 19 of Cxxx-MMD-C4-RAN-Cxxx-00016 Rev 7.0 which states "CH2 pilot" and "Pilot tunnels in unfaulted ground". Amber trigger level for Stage II is therefore 7mm (y) at CB1. 2. The measured deflection was 7.1mm. It was felt that this was due to surveying "noise", so a further survey was carried out to check. This was later confirmed to be <7mm so not a "real" breach of the amber trigger. However, the required notifications to the I&M team, grouting teams, etc (according to MPCoGM) were not made. The flowchart from MPCoGM should have been followed, and this should have included notifying the SRG and CTC within 4 hours. However, it is worth noting that the ultimate outcome would have been the same (survey noise, not a real breach). Mitigating actions / lessons learned: * Senior SCL Engineer and __ surveyors re-briefed about requirements of MPCoGM, and the importance of sharing data as quickly as possible (even if this turns out to be a "false alarm"). * Flowchart extracts from MPCoGM printed and displayed in office at TCR and BOS for ease of reference. * Better clarity from Cxxx for the trigger levels in their I&M plan.
| 01CV - Civils | Cxxx-NCR-000811 | NCR | Underthickness of lining of AP3A Invert chainage 12.85 |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-04-04 | 2013-03-28 14:28 | -7 | 2013-03-21 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Proof drilling was undertaken due to a lack of survey information in this area. Proof drilling identified one location which was just 285mm thick.
| 01CV - Civils | Cxxx-NCR-000812 | NCR | Lack of shotcrete on face of LCE1 Enlargement, Advance 5 |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-04-04 | 2013-04-04 13:02 | 0 | 2013-03-21 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | It was identified that the temporary face support of Advance 5 (invert) of the enlargement of LCE did not receive the required 75mm of shotcrete as specified.
| 01CV - Civils | Cxxx-NCR-000813 | NCR | In-tunnel monitoring not installed in line with KT21 Specification |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-04-04 | 2013-04-04 13:08 | 0 | 2013-03-21 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | At advance 3 of LCE enlargement, monitoring targets numbered 2 and 3 (located in the "shoulders") were installed at a lower level than specified.
| 01CV - Civils | Cxxx-NCR-000815 | NCR | Low air temperature advance LCE Adv 1, 4, 6 and AP3A adv 70, 73, 76 |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-04-05 | 2013-03-26 14:45 | -10 | 2013-03-22 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | AP3A Low air temp for advance 70 (CH 7.5 - 8.5m) Low air temp for advance 73 (CH 10.5 - 11.5m) Low air temp for advance 76 (CH 13.5 - 14.5m) LCE Low air temp for advance 1 (CH 0 -1.39m) Low air temp for advance 4 (CH 0 - 2.39m) Low air temp for advance 6 (CH 3.39 - 4.39m)
| 01CV - Civils | Cxxx-NCR-000817 | NCR | Pipe arch Pipes cut during excavation in LCE |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-04-15 | 2013-04-04 15:14 | -11 | 2013-03-27 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | Due to the transition at chainage 7.4m advances 10 and 11 8no pipes of the pipe arch in LCE1 were encountered and 5 had to be cut back.
| 01CV - Civils | Cxxx-NCR-000820 | NCR | Instrumentation and Monitoring |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-04-01 | 2013-04-04 14:11 | 3 | 2013-03-26 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | CH1 enlargement monitoring points at ch.22 not installed in time
| 01CV - Civils | Cxxx-NCR-000821 | NCR | SCL lining at CH1 |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-04-10 | 2013-03-28 15:16 | -13 | 2013-03-27 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | Upon inspection, it was dicovered that lose shotcrete and rebound has not been cleared from the invert proir to the instalation the the 25mm L-bars.
| 01CV - Civils | Cxxx-NCR-000822 | NCR | ATS UKAS Certificates |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-02-02 | 2014-01-29 11:35 | -4 | 2013-03-27 | Surveying - Instrumentation and Monitoring | 3000 |  | System Defect | Reject | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | are unable to source Certification by a testing company that is UKAS accredited for __ and __ ATSs being used in the Tottenham Court Road and Bond Street station areas. We can confirm that all ATS insturments are procured ‘new’ for the project and are provided with Certificates of Conformity to: EN61000-6-1: 20007 EN 61000-6-3: 2007 + A1:2011 EN 300 328-2: V1.7.1 EN 301 489-1: V1.9.1 EN 301 489-17: V2.1.1 EN 60950-1:20006, + A 11:2009, + 1:2010 Certificates of Conformity will be included within the installation reports provided to the Client as part of the Quality Assurance procedure for the project
| 01CV - Civils | Cxxx-NCR-000828 | NCR | Cxxx-BFK-SCL-BOS-Rebound in invert of AP3A advance 83 |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-04-17 | 2013-04-19 13:45 | 2 | 2013-04-03 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Rework |  | Complete |  | Completed |  | During excavation of advance 84 an area of rebound inclusion and sub-standard concrete was identified in the invert of advance 83.
| 01CV - Civils | Cxxx-NCR-000829 | NCR | Cxxx-BFK-SCL-BOS-Shadowing of cores taken in advance 69 |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-04-17 | 2013-04-19 13:48 | 2 | 2013-04-03 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Cores taken from advacne 69 exhibited some shadowing behind the steel.
| 01CV - Civils | Cxxx-NCR-000830 | NCR | Cxxx-BFK-SCL-BOS-Steel in LCE1 advance 5 |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-05-31 | 2013-05-09 14:17 | -22 | 2013-04-03 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | The steel was not installed for the first approx 600mm of the tunnel due to the skew on the tunnel opening, however the invert was substantially overexcavated. See attached photo for steel which was installed in advance 5.
| 01CV - Civils | Cxxx-NCR-000831 | NCR | Cxxx-BFK-SCL-BOS-Headwall Reinforcement |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-04-17 | 2013-04-19 13:57 | 2 | 2013-04-03 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Some shadowing has been identified on one of 3 cores taken in the headwall. The other two cores do not have any shadowing what so ever (see attached photo summary report).
| 01CV - Civils | Cxxx-NCR-000832 | NCR | Cxxx-BFK-SCL-BOS-LCE1 Advance 16 under excavation |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-04-18 | 2013-04-19 14:01 | 1 | 2013-04-04 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The excavation of advance 16 was completed using teh tollerances for LCE1 rather than for the transition. This means that the finished primary lining surface is approximately 60mm inside the planned profile, and that the lining is 30mm thinner than design (see attached profiles and thickness).
| 01CV - Civils | Cxxx-NCR-000833 | NCR | SMM TCR 6 Drilling - TaM 16 - Obstruction Encountered |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-04-18 | 2013-04-19 15:31 | 1 | 2013-04-04 | Geotechnical Engineering - Compensation Grouting | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | At TCR6 hole T6/16 hit an obstruction at 58m, cleared through and then auger progressed 2m with no resistance i.e. void indicated. After pulling out the augers nothing has been recovered to help us identify the nature of the obstruction and water was flowing from the hole, resulting in not achieving the full drill depth (61.75m). Tam pipe has been installed to only 56m due to obstruction/void and water.
| 01CV - Civils | Cxxx-NCR-000834 | NCR | Temperature of Shotcrete below 15 degrees |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-04-18 | 2013-04-10 11:17 | -8 | 2013-04-04 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Temperature of sprayed concrete was less than 15 degrees at the point of spray (all the dates, chainages and temperatures attached to NCR).
| 01CV - Civils | Cxxx-NCR-000835 | NCR | Flow test under the specified limit |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-04-18 | 2013-04-10 11:41 | -8 | 2013-04-04 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Flow was less than specified minimum (all the dates, chainages and temperatures attached to NCR).
| 01CV - Civils | Cxxx-NCR-000836 | NCR | Shadowing behind reinforcement at crown of CH1 Thickening at junction of AP1 |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-04-18 | 2013-04-23 13:23 | 5 | 2013-04-04 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | Slight shadowing behind 25mm reinforcement as seen from cores taken at the crown of CH1 thickening at the junction of AP1. (Report Attached)
| 01CV - Civils | Cxxx-NCR-000837 | NCR | Cores every 50m3 |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-04-30 | 2013-04-15 15:02 | -15 | 2013-04-04 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Instead of following the requirement, three 1 days, five 28 and five 90 day cores where taken on the 30/3/2013 in AP3A.
| 01CV - Civils | Cxxx-NCR-000841 | NCR | TCR Overspraying of Primary Layer to PTE Pilot Tunnel |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-04-20 | 2013-04-23 13:54 | 3 | 2013-04-06 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Chainages 1.61,2.16,3.03,3.63 all have some amount of overspray (see attached profiles)
| 01CV - Civils | Cxxx-NCR-000845 | NCR | Temperature of Shotcrete and Ambient temperature |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-05-01 | 2013-04-08 17:09 | -23 | 2013-04-08 | Tunnelling - Linings - Sprayed Concrete | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | AP3A Advance 14 concrete temperature was 13.4 and Air Temperature was 2.3. LCE Advance 24 concrete temperature was 36 AP3A Advance 86, 87 & 88 Air temperature was 0.5 AP3A Advance 85 Air temperature was 1.5 AP3A Advance 83 Air temperature was 4 LCE Advance 10 Air Temperature was 1.5 LCE Advance 12 Air Temperature was 3 LCE Advanve 16 Air Temperature was 3 LCE Advance 17 Air Temperature was 4 LCE Advance 18 Air Temperature was 4 LCE Advance 19 Air Temperature was 3 LCE Advance 21 Air Temperature was 4 LCE Advance 22 Air Temperature was 2
| 01CV - Civils | Cxxx-NCR-000849 | NCR | Rebound identified in tunnel lining |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-04-23 | 2013-04-16 17:43 | -7 | 2013-04-09 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Cores taken from tunnel lining of Advance 85 appear below the required thickness and have may have incorporated some rebound.
| 01CV - Civils | Cxxx-NCR-000850 | NCR | Overspray to PTE Pilot Tunnel Primary Linning |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-04-25 | 2013-04-26 11:39 | 1 | 2013-04-09 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Some overspray has taken place at ADV 11 and 13.
| 01CV - Civils | Cxxx-NCR-000851 | NCR | AP1 Temporary Headwall |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-04-25 | 2013-04-22 14:22 | -3 | 2013-04-09 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | Top heading of headwall constructed insufficiently domed by an average of 300mm.
| 01CV - Civils | Cxxx-NCR-000852 | NCR | Joint installation level varying between adjacent advances |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-04-23 | 2013-04-16 17:48 | -7 | 2013-04-09 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The level of the joint between the bench and invert is different for Advance 20 and Advance 24. The level of the joint between the bench and invert is also different between Advance 24 and Advance 28. (the level of the joint of Advance 20 and Advance 28 are the same) The levels of the joint are not clearly defined on drawing # Cxxx-MMD-C4-DDB-Cxxx_6-00203 The engineers responsible for setting the level of the kwikastrip have interpreted the drawing differently on different shifts.
| 01CV - Civils | Cxxx-NCR-000853 | NCR | Non-fibre shotcrete sprayed to Primary Lining |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-04-23 | 2013-04-16 17:51 | -7 | 2013-04-10 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | The first 3No. batches of shotcrete deliverd from 's off-site batching plant during the night of 8/9th April did contain the steel fibres as per the mix design. The 4th batch of shotcrete applied to Primary Lining of Advance 27 of LCE Enlargement was not adequately anaylsed prior to spray and did not contain the steel fibres. After approximately 15 minutes, this non-conformance was identified and shotcrete spray was stopped. Shotcrete that had been applied without the steel fibres was immediately removed and the substrate cleaned in readiness to receive the next batch of shotcrete which was delivered with steel fibres to specification.
| 01CV - Civils | Cxxx-NCR-000856 | NCR | Early Age compressive strength |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-04-24 | 2013-04-23 15:00 | -1 | 2013-04-10 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | In AP1 first 16 advances only 2 Early Strength tests where carried out (5 and 9 advance).
| 01CV - Civils | Cxxx-NCR-000857 | NCR | One day cores not taken |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-04-24 | 2013-04-23 15:16 | -1 | 2013-04-10 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | No one day cores taken out from AP1 first 16 advances.
| 01CV - Civils | Cxxx-NCR-000858 | NCR | BOS GS4 TaM drill deviations |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-04-25 | 2013-04-25 11:39 | 0 | 2013-04-11 | Geotechnical Engineering - Compensation Grouting | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Further to NCRs 00378, 00459 please find attached revised and complete drill deviation assessment for BOS GS 4. In summary 27 TaMs are out of horizontal tolerance, 30 out of vertical tolerance, 2 within the exclusion zone and 13 outside the deisgn band.
| 01CV - Civils | Cxxx-NCR-000859 | NCR | Face of Advance 30 of the enlargement did not get the required 75mm shotcrete support |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-04-25 | 2013-04-16 15:46 | -9 | 2013-04-11 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | It was identified that the temporary face support of Advance 30 (top heading) of the enlargement of LCE did not receive the required 75mm of shotcrete as specified.
| 01CV - Civils | Cxxx-NCR-000860 | NCR | Temperatures of Shotcrete exceeding 35 degrees |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-05-02 | 2013-04-16 16:16 | -16 | 2013-04-11 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Concrete batched from the Hanover Square batching plant on the 10/4/2013 was above 35 degrees C for the following mixes. Ticket number 860 batched at 11.39 was 37 degrees Ticket number 861 batched at 12.22 was 38 degrees Ticket number 863 batched at 14.35 was 36 degrees
| 01CV - Civils | Cxxx-NCR-000861 | NCR | BOS GS 4 - Sleeve Grout Testing Records |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-04-25 | 2013-04-15 15:24 | -10 | 2013-04-11 | Geotechnical Engineering - Compensation Grouting | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | There are only 3 on-site grout test forms available that recorded the batching and testing of the sleeve grout during the drilling operations at BOS grout shaft 4. This is an insufficient number as one should be produced per each shift where grouting occurs.
| 01CV - Civils | Cxxx-NCR-000865 | NCR | Slight amount of rebound found in cores taken from AP1 Flare section |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-04-29 | 2013-04-25 14:13 | -4 | 2013-04-12 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Slight amount of rebound found in cores taken from AP1 Flare section Adv 16 (Invert) Chainage 11.5m (See attachment image)
| 01CV - Civils | Cxxx-NCR-000871 | NCR | Tickness of SCL at temporary excavation face |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-04-30 | 2013-04-24 14:50 | -6 | 2013-04-15 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | During spraying of advance 34 on AP1 pilot tunnel, not enough shotcrete was applied at the face
| 01CV - Civils | Cxxx-NCR-000875 | NCR | Joint Continuity Reinforcement in LCE2 Enlargement |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-05-15 | 2013-05-07 14:56 | -8 | 2013-04-17 | Tunnelling - Linings - Sprayed Concrete | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | __ Eazistrip "EZ 160U 10/150" has been installed to the joint between advance 31 (top-heading) and advance 36 (bench). Subsequent joints have had 1200mm long L-bars installed to span the joint as per specification on the drawing.
| 01CV - Civils | Cxxx-NCR-000876 | NCR | TaM T6/25 not installed as per design at TCR Grout Shaft 6 |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-05-23 | 2013-05-16 12:15 | -7 | 2013-04-25 | Geotechnical Engineering - Compensation Grouting | 500 |  | System Defect | Rework |  | Complete |  | Completed |  | On completion of drilling TaM T6/25 at TCR GS6 - Goslett Yard, the augers were retracted but a continuous ingress of water was noticed. When fully removed, fragments of plastic, appearing to be ducting, were identified on the auger. As a result of the water ingress to the shaft it was not possible to install the TàM. Instead the hole was fully cased, and a valve was grouted into the end of the drill casing to stop/control the water flow into the shaft.
| 01CV - Civils | Cxxx-NCR-000881 | NCR | Joint between Advances 35, 38 & 40 of LCE Enlargement at BOS ETH |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-05-02 | 2013-04-22 13:45 | -10 | 2013-04-18 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The levels differed between Advance 35 and 38 by approximately 200mm. Furthermore, the area of reinforcement installed to Advance 38 was found to incorporate rebound towards the leading edge.
| 01CV - Civils | Cxxx-NCR-000883 | NCR | Missing Profiles of LCE Pilot at BOS ETH |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-05-02 | 2013-04-25 13:55 | -7 | 2013-04-18 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Advances 3, 4, 14, 15, 19 and 26 of the Pilot tunnel of LCE1/2 either do not have enough survey records, or did not get proof-drilled. These areas are now not accessible because the pilot tunnel has either been demolished or is not accessible due to the enlargement works advancing.
| 01CV - Civils | Cxxx-NCR-000884 | NCR | Temperatures of Shotcrete exceeding 35 degrees |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-05-23 | 2013-04-19 16:41 | -34 | 2013-04-18 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Concrete batched from the Hanover Square batching plant on the 16/4/2013 & 17/4/2013 was above 35 degrees C for the following mixes. Ticket number 960 batched at 12.18 was 35.6 degrees Ticket number 962 batched at 13.55 was 37.5 degrees Ticket number 971 batched at 00.56 was 35.4 degrees Ticket number 974 batched at 4.20 was 36 degrees Ticket number 977 batched at 6.57 was 35.2 degrees Ticket number 979 batched at 8.20 was 35.5 degrees Ticket number 980 batched at 8.48 was 35.5 degrees Ticket number 987 batched at 16.56 was 36.5 degrees Ticket number 988 batched at 17.34 was 36.5 degrees Ticket number 989 batched at 17.58 was 35.5 degrees
| 01CV - Civils | Cxxx-NCR-000886 | NCR | Rebound and Lamination in AP1 Temp Invert |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-05-03 | 2013-05-01 16:01 | -2 | 2013-04-19 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Temp invert AP1 Adv 41 when uncovered during adv 44 found to contain rebound and some lamination.
| 01CV - Civils | Cxxx-NCR-000888 | NCR | Early Age compressive strength |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-05-07 | 2013-05-02 11:23 | -5 | 2013-04-23 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | In AP1 Early Strength tests where missed in advances 44, 47 and 53.
| 01CV - Civils | Cxxx-NCR-000889 | NCR | BOS NW Shaft Portal Frame |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-05-22 | 2013-05-13 14:34 | -9 | 2013-04-23 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The pours to column B, column C, central plinth, and lower beam were poured using C32/40 concrete. have undertaken a review of the existing concrete strength through an analysis of the cubes strengths that have been attained from each pour, and taking cores from the columns B and C. These have been conveyed back to the designer and under original loading conditions did not achieved the required strength. After discussions between , and CRL, (__, __, __ ('s designer), __, __), have reduced the loading that is applied to the structure. This is through an assessment and practical assumptions regarding the as-built temporary slabs. The original design loads were provided from , and appeared to be of a preliminary design (ie not taking into account the thickness of the temporary slabs actually constructed, or the voids within it). With the same dead and live loading that has been been previously specified as UDLs and dead loads, applied to the now amended slab area, s designers have in turn reduced the loading that is applied to the portal frame. Please note, we have not reduced the live UDL that has been supplied to us as a constraint, just the area over which it acts.
| 01CV - Civils | Cxxx-NCR-000890 | NCR | SCL on site testing |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-06-20 | 2013-06-20 16:32 | 0 | 2013-04-24 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | Engineers and Technicians who are doing testing in TCR are not trained by a person from UKAS accredited testing house. Engineers and Technicians are briefed to carry out tests according to BS/EN standards and procedures by sub-agents. Quality Department has done surveillances to check that testing has been done as required by standards.
| 01CV - Civils | Cxxx-NCR-000891 | NCR | 1 day cores not taken |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-06-27 | 2013-06-26 16:38 | -1 | 2013-04-25 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | No cores taken from advance 17 to 61.
| 01CV - Civils | Cxxx-NCR-000892 | NCR | BOS GS2 - HOVY - TaM Drilling out of tolerences |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-05-10 | 2013-05-09 15:26 | -1 | 2013-04-25 | Geotechnical Engineering - Compensation Grouting | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | The following are out of design tolerance: Horizontal Tolerance - B2/... 2,3,9,11,12,13,15,18,19,20,21,21a,23,24,25,25a,26,29,30,32,33,33a,34,35,36,37,37a,38,39,40,40a,41,43,44,46,47,48,49,51,56,64,68,77,78,79,82,83,84,88,90,91,96,99, 101,102,103. Vertical Tolerance - B2/... 3,4,5,6,7,8,9,10,12,14,16,20,21a,22,25,28,31,36,37a,38,40a,41,44a,45,46,47,48,49, 50,51,52,53,55,56,57,58,59,60,61,62,63,64,65,66,69,70,73,74,75,76,76a,77,78,79,80,81,82,85,86,87,89,90,93,94,96,96a,97,98,99,101,102,103. Outside design band - B2/... 3,21a,22,37a,38,89. Obstructions encountered - B2/33 - Obstruction of unknown nature encountered at approx 27.5m; TaM pipe installed to 24m: 22m sleeve pipe + 2m plain; hole replaced by 33a. Miscellaneous - B2/25 - installed short at 47.75m. B2/25a replaced this TaM. See attached drill deviation spreadsheet for further information.
| 01CV - Civils | Cxxx-NCR-000894 | NCR | TCR GS2 - Soho Sq - TaM Drilling out of tolerance |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-07-04 | 2013-06-18 17:59 | -16 | 2013-04-25 | Geotechnical Engineering - Compensation Grouting | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | The following are out of design tolerance: Horizontal Tolerance - T2/... 1,3,4,5,8,10,11,12,14,17,18,19,20,31,32,33,36,38,39,41,41a,42,44,47,48,48a,49,50,50a,51,52,54,55,56,58,59,60,62,65,65a,67,68,71,71a,73,74,74a. Vertical Tolerance - T2/... 1a,2,4,7,9,11,12,16,19,22,25,26,28,33,34,35,39,40,41a,43,44,46,48,49,50a,52,53,54,60,63,64,65,67,68a,72,73,74,75. Horizontal Distance between TaM's - T2/... 18, 54, 70 Depth Overdrill (not a non-conformance but noted for information) T2/71a - drilled 20m too long Obstructions encountered - T2/44 - Obstruction of unknown nature encountered at 31m; TaM pipe installed to 2m short of design depth. See attached drill deviation spreadsheet for further information.
| 01CV - Civils | Cxxx-NCR-000896 | NCR | TCR GS3 - TaM Drilling Obstructions and Over Spaced TaM's |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-06-06 | 2013-06-06 10:23 | 0 | 2013-04-25 | Geotechnical Engineering - Compensation Grouting | 500 |  | Design | Rework |  | Complete |  | Completed |  | Obstructions encountered during installation of TaM's meaning full coverage not realised. TaM's affected: T3/56 - Concrete obstruction at 5.6m; hole abandoned. T3/32 - hole abandoned at 8.5. T3/31 - hole installed 9m short due to operative error. Additionally, the out of tolerance horizontal spacing deviations are as follows: TaM ref. 9 to 10 = 5121m gap TaM ref. 27 to 28 = 5008m gap TaM ref. 34 to 35 = 5026m gap TaM ref. 37 to 38 = 4313m gap TaM ref. 14 to 15 = 6.042m gap TaM ref. 30 to 31 = 5.325m gap TaM ref. 34 to 35 = 6.568m gap TaM ref. 37 to 38 = 4313m gap TaM ref. 54 to 55 = 4088 m gap TaM ref. 9 to 9A = 4478m gap TaM ref. 27 to 27A = 4408m gap TaM ref. 34A to 35 = 6.568m gap
| 01CV - Civils | Cxxx-NCR-000897 | NCR | Incorrect spacing of pull-out test nails on Early Age Strength Test Panel - BOS ETH LCE Adv 49 |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-09-05 | 2013-05-07 16:20 | -121 | 2013-04-25 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Pull-out test nails were being spaced closer together than the specified minimum 80mm.
| 01CV - Civils | Cxxx-NCR-000898 | NCR | Joint level differed by approx 400mm between adjacent advances of LCE Enlargement - BOS ETH |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-05-16 | 2013-05-09 14:21 | -7 | 2013-04-25 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | There is a difference in the specified level of the joint between LCE1 and LCE2 which was being phased-in over a number of advances. Through a break down in communication between shifts, the excavation and subsequent installation of the continuity reinforcement of Advance 48 was approx 300mm different to the level of the reinforcement to Advance 44.
| 01CV - Civils | Cxxx-NCR-000899 | NCR | Reinforcement mesh installed across the Bench Advance 48 did not adequately lap the continuity joint reinforcement bars - BOS ETH LCE |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-05-14 | 2013-05-09 11:55 | -5 | 2013-04-25 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The sheet of A393 mesh used to span the Bench Advance 48, did not extend high enough to pick up the full length of the L-bars. This situation has arisen because of the joint level change identified by NCR# 00898.
| 01CV - Civils | Cxxx-NCR-000903 | NCR | TCR GS4 - TaM coverage - Draft |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-06-20 | 2013-06-19 17:34 | -1 | 2013-05-08 | Geotechnical Engineering - Compensation Grouting | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Horizontal spacing between these TaM's are as follows: TaM ref. 18 to 18B = 4.617m gap TaM ref 23 to 25 = 7.753m gap. TaM ref. 27 to 27A = 7.766m gap TaM ref. 30 to 31A = 5.310m gap TaM ref. 33 to 33A = 4.833m gap TaM ref. 24B to 25 = 5.749m gap TaM's entering the Tunnel exclusion zone are: TaM ref. 23 – Tunnel crown to TaM pipe Vertical measurement 3.628m TaM ref. 26 – Tunnel crown to TaM pipe Vertical measurement 4.386m TaM ref. 27a – Tunnel crown to TaM pipe Vertical measurement 4.638m TaM ref. 28 – Tunnel crown to TaM pipe Vertical measurement 4.915m TaM ref. 31 – Tunnel crown to TaM pipe Vertical measurement 4.914m TaM ref. 31a – Tunnel crown to TaM pipe Vertical measurement 4.986m
| 01CV - Civils | Cxxx-NCR-000904 | NCR | Missing profiles of AP1 and PTE tunnels at TCR WTH |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-05-10 | 2013-04-29 12:43 | -11 | 2013-04-26 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Due to problems with processing the data from the 'as build', the information about the thickness wasn't presented at the SRG. In some of those advances the excavation profiles were missing and there were no evidences of the thickness.
| 01CV - Civils | Cxxx-NCR-000905 | NCR | RMS29 not installed to LCE Pilot - BOS ETH |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-05-10 | 2013-05-07 13:07 | -3 | 2013-04-26 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | RMS29 was not installed.
| 01CV - Civils | Cxxx-NCR-000911 | NCR | Missing Profiles and Proof Drilling Records - BOS ETH AP3A Enlargement |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-01-30 | 2014-01-06 10:13 | -24 | 2013-04-29 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Some of the records for the tunnel lining thickness checks or proof drilling of AP3A Enlargement are not available: Advance 47 - Thickness check not giving conclusive >300mm thickness of Top Heading ch.14 Advance 51 - Primary Lining Records of the LHS of Bench ch. 14 Advance 57 - Thickness check not giving conclusive >300mm thickness of Bench ch. 18 Advance 57 - Primary Lining Records of Bench ch. 19 Advance 59 - Thickness check not giving conclusive >300mm thickness of Top Heading ch. 22 Advance 63 - Thickness check not giving conclusive >300mm thickness of Bench ch. 22 Advance 64 - Excavation and Primary Lining records missing of Top Heading ch. 25 Advance 66 - Thickness check not giving conclusive >300mm thickness of Invert ch. 4 (transition makes survey records deceptive) Advance 67 - Thickness check not giving conclusive >300mm thickness of Bench ch. 5 Advance 75 - Thickness check not giving conclusive >300mm thickness of Bench ch. 13 Advance 87 & 88 - Thickness check not giving conclusive >300mm thickness of Bench ch. 25
| 01CV - Civils | Cxxx-NCR-000913 | NCR | Weekly accelerator pump calibration not done |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-05-14 | 2013-05-16 11:53 | 2 | 2013-04-30 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Weekly calibration not done. Manufacturer calibration was done in February.
| 01CV - Civils | Cxxx-NCR-000914 | NCR | TCR GS6 - T6/26 Installed short of design length |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-05-14 | 2013-05-13 14:24 | -1 | 2013-04-30 | Geotechnical Engineering - Compensation Grouting | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Whilst drilling TCR6 / 26, very sandy/sticky clay was encountered at 35m. This material jammed the augers and prevented drilling to continue to full depth (43.75), resulting in the TaM pipe being installed short, to 33.75m.
| 01CV - Civils | Cxxx-NCR-000915 | NCR | Incorrect loading of shotcrete fines into silo 2 at BOS ETH Batching Plant |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-05-22 | 2013-05-22 16:50 | 0 | 2013-05-08 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | On 28/04/13, silo 2 was incorrectly filled from the upper filling inlet. Owing to the pre-existing level of the fines, the material should have been loaded from the middle inlet.
| 01CV - Civils | Cxxx-NCR-000918 | NCR | Starter Bars in Pour 2 |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-05-30 | 2013-05-20 11:06 | -10 | 2013-05-02 | Structural Engineering - Reinforcement | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | The column in the South-East corner of the basement slab been cast with __ Taper Threaded Couplers rather than with the Griptec Parallel Thread coupler system.
| 01CV - Civils | Cxxx-NCR-000919 | NCR | Pour 4 Starter Bars |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-05-16 | 2013-05-17 16:09 | 1 | 2013-05-02 | Structural Engineering - Reinforcement | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | In the wall to the north of the trench in the basement slab there are 16No. starter bars which have a __ taper threaded coupler on rather than a Griptec parallel threaded coupler.
| 01CV - Civils | Cxxx-NCR-000921 | NCR | Shear Links in Crane Base |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-05-30 | 2013-05-24 14:15 | -6 | 2013-05-02 | Structural Engineering - Reinforcement | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | There are 14 shear links missing from the northern side of the outside ring around the tower crane base. See attached sketch.
| 01CV - Civils | Cxxx-NCR-000923 | NCR | TCR PTE Temporary Headwall |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-05-30 | 2013-05-16 12:54 | -14 | 2013-05-02 | Surveying - Instrumentation and Monitoring | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | __ system cannot adequately demonstate shotcrete thicknesses achieved when used on headwalls i.e - a relatively tight radius'd chainage.( Thickness demonstrated as achieved by proof drilling (see attached))
| 01CV - Civils | Cxxx-NCR-000926 | NCR | Early Age Strength Testing |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-05-23 | 2013-05-21 13:40 | -2 | 2013-05-02 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | 12hr testing result missing for advance 1 and 8, CH1 pilot tunnel (Feb 2013).
| 01CV - Civils | Cxxx-NCR-000927 | NCR | Invert excavation open face |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-06-20 | 2013-06-19 14:57 | -1 | 2013-05-03 | Tunnelling - Tunnelling General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Primary linning was being sprayed in the invert with the assistance of men on the lance blowing rebound forward without the face being sealed. ITP was not followed (NCR not following procedure) and the face was not sealed as per the ITP before ther next stage of works commenced.
| 01CV - Civils | Cxxx-NCR-000929 | NCR | As build records to prove lining thickeness |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-05-23 | 2013-05-20 10:56 | -3 | 2013-05-04 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | Not enough points recorded on the left side of the excavation profile on the chainages 25.20 and 26.15 of AP1 due to posiition of the instrument
| 01CV - Civils | Cxxx-NCR-000934 | NCR | TCR GS5 - Soho Square |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-06-20 | 2013-06-18 13:30 | -2 | 2013-05-09 | Geotechnical Engineering - Compensation Grouting | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | The followign are out of design tolerance: Horizontal Tolerance - T5/... 2a,4a,4,4b,5a,5,7a,8,9a,10,11,11a,12,13,17,19,21,22,23,24,25,26,x1a,x2,x3,x4,x5,x5,x8,x8a,x9, x12,x13,x14,x15,x16,x17,x18,x19,x20,x23,44,45,46,55,56,57,59,61,62,63,65,70,71,72,75,78,80,81,81a,82,83,84a,85,86a,87. Vertical tolerance - T5/... 2a,3,4b,5a,7a,8,12,12a,14,15,22,24,26,27,x1,x5,x6,x8a,x10,x11,x13,x14,x18,x23,44,48,49,52,53, 57,58,62,62a,64,66,72,75,76,77,79,80,81,81a,86. Outside design band - T5/... 2a,5,12,x6,x10,x11,x14,x18,77 Obstructions Encountered - Miscellaneous - T5/4 - TaM Installed short, supplemented with T5/4B T5/5A - TaM installed short, acceptable as is T5/5 - TaM installed short, supplemented with T5/5A T5/11 - TaM installed short, supplemented with T5/11A T5/12 - TaM installed short, supplemented with T5/12A See attached drill deviation spreadsheet and as built drawing for further information.
| 01CV - Civils | Cxxx-NCR-000938 | NCR | Incorrect construction sequencing to SE2 Soft Eye |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-05-22 | 2013-05-14 15:43 | -8 | 2013-05-08 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Horizontal cuts were made to the top half of pile#190 and pile#195. The RESS required that the top half of pile#195 could only be sawn once the bottom half of pile#190 was cut.
| 01CV - Civils | Cxxx-NCR-000939 | NCR | fibre content washout tests not being perfromed |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-06-17 | 2013-06-04 11:52 | -13 | 2013-05-09 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Fibre washout content tests currently not being undertaken
| 01CV - Civils | Cxxx-NCR-000940 | NCR | Fibre content of hardened specimens |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-06-28 | 2013-06-25 15:54 | -3 | 2013-05-09 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Currently fibre content taken from 100mmX100mm cores are displaying fibre content below the allowable limit.
| 01CV - Civils | Cxxx-NCR-000941 | NCR | Rebound testing |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-06-24 | 2013-06-25 15:57 | 1 | 2013-05-09 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Currently no fibre rebound tests have taken place
| 01CV - Civils | Cxxx-NCR-000942 | NCR | TCR GS6 - Goslett Yard - TaM Drilling Out of Tolerance |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-06-20 | 2013-06-21 10:03 | 1 | 2013-05-09 | Geotechnical Engineering - Compensation Grouting | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | The following are out of design tolerance: Horizontal Tolerance - T6/... 4,4a,7,8,9,10,12,14,15,16,19,21,22,23,25,27,29,30 Vertical Tolerence - T6/... 3,6,8,8a,9,13,15,16,17,18,19,23,25a,26 Miscellaneous - T6/26 - installed short. T6/25a covered the shortfall. See attached drill deviation spreadsheet and as built drawing for further information.
| 01CV - Civils | Cxxx-NCR-000943 | NCR | Concrete testing |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-05-30 | 2013-05-15 11:32 | -15 | 2013-05-09 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | Concrete was tested 2hours before the excavation started, when only muck was being removed. When tested again the excavation was already on going and the flow was 460mm (10mm out of spec). Concrete was rejected and fresh concrete was batched
| 01CV - Civils | Cxxx-NCR-000945 | NCR | Monthly tests - Beams Flexural Strength |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-06-17 | 2013-05-17 16:14 | -31 | 2013-05-13 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Panels damaged before beams had been cut. (Sample number 37, PTE adv 8)
| 01CV - Civils | Cxxx-NCR-000946 | NCR | 1 day Cores not taken |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-06-13 | 2013-06-10 12:48 | -3 | 2013-05-13 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | No 1 day cores taken from advances 58-80
| 01CV - Civils | Cxxx-NCR-000949 | NCR | REinforcement position on AP1 thickening layer |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-05-30 | 2013-05-21 15:37 | -9 | 2013-05-16 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Reinforcement installed 100mm inside (at aprox. 275mm) on the crown of the AP1 thickening layer
| 01CV - Civils | Cxxx-NCR-000951 | NCR | Over dig of invert advance |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-06-06 | 2013-06-04 11:47 | -2 | 2013-05-16 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Leading edge was left to far back on the right hand side of the advance and as the invert was excavated there was not enough of the shotcrete lining bearing on the bench.
| 01CV - Civils | Cxxx-NCR-000954 | NCR | Primary lining spraying |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-06-06 | 2013-05-28 09:49 | -9 | 2013-05-20 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Leading edge of advance 40 (invert) sprayed too far back and with an irregular shape. Due to a programed stop of CH1 excavation, a 150mm initial layer was sprayed on the invert. When spraying the primary lining on top of the extra thick initial the leading edge was sprayed to far back.
| 01CV - Civils | Cxxx-NCR-000956 | NCR | noncompliant flow test |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-06-20 | 2013-06-20 16:36 | 0 | 2013-05-20 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The specified 30 second wait from completing the mould strike off was omitted
| 01CV - Civils | Cxxx-NCR-000957 | NCR | Sampling procedures and records |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-06-20 | 2013-06-20 16:27 | 0 | 2013-05-20 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Sampling records do not record the sampling method reference procedure and who undertook the sampling as required by UKAS
| 01CV - Civils | Cxxx-NCR-000965 | NCR | LCE1 RESS Form not signed by Senior SCL Engineer |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-06-11 | 2013-06-03 09:44 | -8 | 2013-05-24 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | RESS not signed by Senior SCL Engineer.
| 01CV - Civils | Cxxx-NCR-000966 | NCR | Primary lining thickness |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-06-08 | 2013-05-28 16:24 | -11 | 2013-05-25 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | No as build were taken or profiles were lost during data transfer of excavation of Advance 57 (chainages 66.22 and 67.08). No evidences of primary lining shown in the SRG
| 01CV - Civils | Cxxx-NCR-000967 | NCR | Testing regime described in ITP not followed during the pour |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-06-13 | 2013-06-12 15:57 | -1 | 2013-05-28 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | It was impossible to test density before pumping and each load due to health and safety reasons. Out of 22 loads density was tested by __ 18 times.
| 01CV - Civils | Cxxx-NCR-000968 | NCR | LCE 1 Sprayed Concrete Lining Checksheets Form BFK-050 not signed in all locations for advances 2, 3, 4, 11, 13 & 17 |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-06-13 | 2013-06-12 16:10 | -1 | 2013-05-28 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | LCE 1 Sprayed Concrete Lining Checksheets Form -050 are not signed in all required locations for advances 2, 3, 4, 11, 13 & 17
| 01CV - Civils | Cxxx-NCR-000969 | NCR | Testing Requirements to KT20 |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-06-28 | 2013-06-04 11:55 | -24 | 2013-05-29 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Early Age Strength CH1 No 3, 2 or 4 hour tests were done on advance 36 enlargement and no 12 hour test was done on advance 79 enlargement. Gap of 4 advances between tests for Adv. 20 – 24, 48 – 52 & 52 – 56. PTE No 12 hour test result for advance 41. Greater than every 3rd advance gap in some of the advances between tests, gap of 7 Adv. 6 -13, gap of 4 Adv. 13-16 & a gap of 6 Adv. 35 – 41. AP1 No 12 hour test for advance 64 & 1 hour test for advance 41. Greater than every 3rd advance gap in some of the advances gap of 4 between 19-13, gap of 5 between 31-36, gap of 16 between 41 and 57 a NCR has been raised for this gap but does not fully cover it, it states that tests where missed in 44, 47 and 53 it does not cover the gap between 47 and 53 of 6 and the gap between 53 and 57 of 4. There is a gap of 4 between advance 69 and 73. CH1 Extension Greater than every 3rd advance in some of the advances gap of 5 advances between 3 and 8, gap of 4 between 9 and 13 and gap of 4 between 23 and 27. Compressive Strength Cores CH1 Requirements of tests every 50m3 has not been completely followed between the test on advance 30 and advance 31 there was 70m3 sprayed. Between advance 76 and the end of the tunnel there was 70m3 sprayed. PTE No cores where crushed at 1 day for the samples taken from advances 13 &20. AP1 No 1 day cores where crushed for samples taken from advances 41, 50, 53, 56 & 59. CH1 Extension Between advance 19 and advance 27 the volume of concrete sprayed was 60 and not 50m3. Fibre Content CH1 Requirements of fibre content from hard samples every 50m3 has not been completely followed between the test on advance 30 and advance 31 there was 70m3 sprayed and between advance 76 and the end of the tunnel there was 70m3 sprayed with no cores taken. CH1 Extension Between advance 19 and advance 27 the volume of concrete sprayed was 60 and not 50m3.
| 01CV - Civils | Cxxx-NCR-000970 | NCR | BOS GS2 - Blocked TaM's |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-07-01 | 2013-06-28 12:38 | -3 | 2013-05-29 | Geotechnical Engineering - Compensation Grouting | 500 |  | Damaged | Use As-Is |  | Complete |  | Completed |  | TaM’s in BOS GS2 have become blocked and sections of them are no longer serviceable. The following TaM’s and ports are identified as blocked: B2/24 Blocked at 70m of 85.75 – Sleeves 1 to 29 unavailable B2/25 Blocked at 55 of 86 – Sleeves 1 to 62 unavailable B2/26 Blocked at 84m of 87.75– Sleeves 1 to 6 unavailable B2/30 Blocked at 88m of 91.75– Sleeves 1 to 7 unavailable
| 01CV - Civils | Cxxx-NCR-000971 | NCR | Batching plant scale calibration |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-06-12 | 2013-06-11 11:17 | -1 | 2013-05-29 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Calibration is overdue. Calibration was done 14/01/13 - next calibration was planned April 2013.
| 01CV - Civils | Cxxx-NCR-000977 | NCR | Thickening layer behind reinforcement overspray AP2E/W |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-06-21 | 2013-06-18 13:53 | -3 | 2013-05-31 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | Sprayed 200mm thickening in the thought of installing reinforcement near face, whereas the drawing indicates the reinforcement to be installed far face.
| 01CV - Civils | Cxxx-NCR-000979 | NCR | Overspray of AP2E/W softeyes |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-06-28 | 2013-06-21 09:59 | -7 | 2013-05-31 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | Some areas of the softeye invert have been oversprayed by 200mm thinking it was part of CH1 thickening
| 01CV - Civils | Cxxx-NCR-000980 | NCR | Spraying of horizontal test panel |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-06-21 | 2013-06-20 11:34 | -1 | 2013-05-31 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Panel was sprayed when lying in a horizontal position
| 01CV - Civils | Cxxx-NCR-000981 | NCR | Insufficient Excavation Survey Records for Advances 2 & 3 of CH3 Pilot - BOS ETH |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-06-17 | 2013-06-10 13:08 | -7 | 2013-06-03 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Insufficient survey records of the excavation profile of Advance 2 and Advance 3 of CH3 Pilot meant that the lining thickness could not be verified. (Excavation Profiles attached)
| 01CV - Civils | Cxxx-NCR-000983 | NCR | Early strength testing on Advance 4 CH3 |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-07-04 | 2013-06-28 12:53 | -6 | 2013-06-03 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Early age compressive strength testing was not perfromed on Advance 4 of CH3 tunnel.
| 01CV - Civils | Cxxx-NCR-000988 | NCR | Early strength testing on Advance 19 CH3 |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-06-25 | 2013-06-25 15:59 | 0 | 2013-06-04 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Early age compressive strength testing was not perfromed on Advance 19 of CH3 tunnel.
| 01CV - Civils | Cxxx-NCR-000995 | NCR | Early age testing requirements |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-06-27 | 2013-06-18 16:38 | -9 | 2013-06-05 | Tunnelling - Linings - Sprayed Concrete | 500 |  |  | Use As-Is |  | Complete |  | Completed |  | In LCE tunnel between advances 31 & 34 no 12 hour testing occured this is greater than every third advance as required.
| 01CV - Civils | Cxxx-NCR-001000 | NCR | Penetrometer |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-06-24 | 2013-06-25 10:33 | 1 | 2013-06-10 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is |  | Complete |  | Completed |  | Some of the penetrometers were out of use for calibration, this meant sharing of equipment between sites, therefore not on site to do all face logs.
| 01CV - Civils | Cxxx-NCR-001001 | NCR | Delay in replacing damaged target to Chainage 5 in CH3 Pilot - BOS ETH |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-06-24 | 2013-06-14 17:23 | -10 | 2013-06-10 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Damaged | Use As-Is |  | Complete |  | Completed |  | The RMS target in the crown of chainage 5 of the CH3 Pilot Tunnel was broken off and not replaced for at least 2 days. This resulted in 3no. daily readings being missed from the monitoring of CH3 pilot.
| 01CV - Civils | Cxxx-NCR-001002 | NCR | Snapped and abandonnned drilling rod during CH3 Depressurisation Drilling - BOS ETH |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-06-11 | 2013-06-11 11:35 | 0 | 2013-06-11 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Equipment Breakdown | Use As-Is |  | Complete |  | Completed |  | Drilling rod snapped at approx 7.5m penetration during the augering of investigation hole "C2". Auger drill bit and 2no. 3m rods abandoned.
| 01CV - Civils | Cxxx-NCR-001005 | NCR | MCR for foam concrete not approved on eB before works started |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-07-05 | 2013-06-18 16:55 | -17 | 2013-06-11 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Approved copy of MCR for foam concrete is not available on eB and foam concrete works have occurred.
| 01CV - Civils | Cxxx-NCR-001006 | NCR | Insuffcient shotcrete testing AP3A |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-08-22 | 2013-08-22 10:41 | 0 | 2013-06-11 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Supervision/Management | Reject | 4 (0.5-3k) | Complete |  | Completed |  | Long term testing and flexural beam testing was only completed for the BOS batching plant. No testing took place for TCR batching plant
| 01CV - Civils | Cxxx-NCR-001008 | NCR | Amber trigger level breached due to false survey readings - BOS ETH CH3 RMS23 |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-06-27 | 2013-06-26 11:05 | -1 | 2013-06-11 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Amber trigger level falsely breached at RMS23 of CH3 pilot tunnel: The crown target was replaced after being damaged during the previous excavation. Shotcrete debris on the threaded section of the fixing stud prevented the adapter to the target being fully tightened thus resulting in the target sitting a few millimeters further into tunnel than the original base-lined target. The new target being in a different position to the original, resulted in an amber trigger level being breached.
| 01CV - Civils | Cxxx-NCR-001009 | NCR | Tight primary lining of crown of Adv 2, CH3, BOS ETH |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-07-25 | 2013-07-25 12:57 | 0 | 2013-06-12 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete |  | Completed |  | The crown area of Adv. 2 was sprayed up to 400mm tight: Because of the decline in the tunnel axis and the chainages being measured perpendicular to the axis rather than vertically, the profile didn't appear correctly in the survey system. The lining thickness in this area is more than sufficient.
| 01CV - Civils | Cxxx-NCR-001014 | NCR | Thickness of CH3 Pilot Headwall not recorded - BOS ETH CH3 |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-06-28 | 2013-06-18 18:10 | -10 | 2013-06-14 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Records of excavation of face of Advance 52 (headwall) not recorded.
| 01CV - Civils | Cxxx-NCR-001015 | NCR | Early Age Strength outside J2 for test panel from Adv 1 CH3 Enlargement - BOS ETH |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-06-28 | 2013-06-20 16:40 | -8 | 2013-06-14 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Panel sprayed at the end of Advance 1 of the CH3 Enlargement yielded results outside the modified J2 for the 2 hour and 3 hour tests carried out.
| 01CV - Civils | Cxxx-NCR-001017 | NCR | BOS-ETH Inground Instruments |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2013-08-22 | 2013-08-22 17:07 | 0 | 2013-06-17 | Surveying - Instrumentation and Monitoring | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | The in-ground instruments installed around the ETH by Contract 411 have not been installed according to the KX10.3200 spec, and the instruments are malfunctioning. inspected the instruments in April 2013 (see attached inspection report) carrying out maintenance works (i.e. draining the chambers and clearing it of dirt and replacing damaged batteries and logger boxes), this instruments have are now no longer reporting as a result of the poor chamber construction.
| 01CV - Civils | Cxxx-NCR-001019 | NCR | Delayed Monthly Geotechnical Reports |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-07-01 | 2013-06-28 12:31 | -3 | 2013-06-18 | Geotechnical Engineering - Geotechnical Engineering - General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | AP3A Tunnel Geotechnical Report and May Monthly Geotechnical Report outstanding for prolonged period of time.
| 01CV - Civils | Cxxx-NCR-001020 | NCR | Access to exclusion zone |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-07-04 | 2013-07-01 15:05 | -3 | 2013-06-18 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | In adv. 139 of CL1 after the initial lining sprayed - miners went in to work within 5 min without waiting for results of test panels
| 01CV - Civils | Cxxx-NCR-001021 | NCR | Over-excavation of Advance 7 of CH3 - BOS ETH |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-07-02 | 2013-06-26 11:41 | -6 | 2013-06-18 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Excavation of Advance 7 (Bench) of CH3 encroached into the adjacent invert advances (Advance 8 and Advance 12).
| 01CV - Civils | Cxxx-NCR-001022 | NCR | Monitoring targets in RMS 15 of CH3 Pilot not promptly replaced |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-07-02 | 2013-06-26 11:47 | -6 | 2013-06-18 | Surveying - Tunnels/Portal/Shafts surveys | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Broken, damaged and defaced targets in RMS 15 of CH3 Pilot were not replaced for 2+ days resulting in a shortage of monitoring data throughout this section of the tunnel.
| 01CV - Civils | Cxxx-NCR-001023 | NCR | Thickness of Advance 12 not presented to SRG - BOS ETH CH3 |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-07-02 | 2013-06-25 10:40 | 358 | 2013-06-18 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The thickness of the lining of Advance 12 of the CH3 Enlargement tunnel was not verified to the SRG by either survey records or by proof drilling.
| 01CV - Civils | Cxxx-NCR-001024 | NCR | Cores from Primary Lining - CH3 BOS ETH |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-07-02 | 2013-06-26 15:04 | -6 | 2013-06-18 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Cores taken from the LHS of Advance 7 (Bench) of CH3 did not penetrate the entire thickness of the lining of the tunnel.
| 01CV - Civils | Cxxx-NCR-001026 | NCR | Surveillance NCR reporting |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-07-17 | 2013-06-20 11:40 | -27 | 2013-06-19 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Deviations from the ITP testing frequency requirements recorded in the Contractor’s surveillance report Cxxx- -O4-RGN-CRT00_ST005-50090 not raised as NCRs
| 01CV - Civils | Cxxx-NCR-001028 | NCR | Allowable 5mm Jacking Exceeded in BOS 4 Post EB TBM Pass |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2013-07-25 | 2013-07-25 10:26 | 0 | 2013-06-19 | Geotechnical Engineering - Compensation Grouting | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete |  | Completed |  | While carrying out the Post EB TBM grouting from BOS GS4, exceeded the 5mm allowable heave.
| 01CV - Civils | Cxxx-NCR-001031 | NCR | Barcode Scales |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2013-07-21 | 2013-07-25 10:31 | 4 | 2013-06-21 | Surveying - Instrumentation and Monitoring | 20000 |  | Material | Rework | 2 (6-60k) | Complete |  | Completed |  | The rectangular foamed PVC base used are not eqivilant to invar mater and the lenght of barcodes installed are not 600mm long. This an issue across all area.
| 01CV - Civils | Cxxx-NCR-001035 | NCR | Thickness of Advance 18 not presented to SRG - BOS ETH CH3 |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-07-04 | 2013-06-26 13:39 | -8 | 2013-06-24 | Surveying - Tunnels/Portal/Shafts surveys | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The thickness of the lining of Advance 18 of the CH3 Enlargement tunnel was not verified to the SRG by either survey records or by proof drilling.
| 01CV - Civils | Cxxx-NCR-001043 | NCR | Kwikastrip not installed as per sketch attached to RESS |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-07-10 | 2013-07-04 17:26 | -6 | 2013-06-26 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Sketch accompanying RESS shows kwikastrip installed with hook facing extrados of tunnel lining. Following discussion with the SRG last week, kwikastrip has been installed through a number of advances with the hook of the kwikastrip facing the intrados of the lining.
| 01CV - Civils | Cxxx-NCR-001047 | NCR | Monthly Testing |  | Crossrail | PDP | BOS - Bond Street Station (West) |  | 2013-08-01 | 2013-07-25 11:18 | -7 | 2013-06-27 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | The monthly tests were not completed during the month of March. These records were not included the March Production Records folder.
| 01CV - Civils | Cxxx-NCR-001049 | NCR | CH3 Pilot Spraying Sequence on Advance 6 |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-07-12 | 2013-07-01 14:59 | -11 | 2013-06-28 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Alteration in spray sequence on advance 6 was not discussed in RESS meeting
| 01CV - Civils | Cxxx-NCR-001050 | NCR | Water tank at BOS3 out of tolerence |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-08-22 | 2013-07-30 17:24 | -23 | 2013-06-28 | Geotechnical Engineering - Compensation Grouting | 1000 |  | Equipment Breakdown | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | During a planned surveillance it was found that the tank at BOS3, a 50 litre tank that is filled twice per mix only held 48.5 litrees which equates to 97 litres per mix, this is 3% below the required volume and is out of spec.
| 01CV - Civils | Cxxx-NCR-001051 | NCR | Water tank BOS2 out of tolerence |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-07-25 | 2013-07-25 10:40 | 0 | 2013-06-28 | Geotechnical Engineering - Compensation Grouting | 500 |  |  | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | During a planned surveillance it was found that the Tank at BOS 2 which is is a 100 litre was found to hold 97litres which is 3% below the required volume and is out of spec.
| 01CV - Civils | Cxxx-NCR-001052 | NCR | Bench and Invert Advances of CH3 excavated to the incorrect chainage - BOS ETH |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-08-08 | 2013-07-25 14:35 | -14 | 2013-07-01 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Rework | 3 (3-6k) | Complete |  | Completed |  | Due to the setting-out difficulties throughout the "crank" (change of direction) of the CH3 Enlargement, the Bench and Invert Advances were not excavated to the correct chainage resulting in the Benchs and Inverts lagging behind the Top Headings.
| 01CV - Civils | Cxxx-NCR-001053 | NCR | Densities of concrete infill not recorded and not taken at the stated frequency |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-07-31 | 2013-07-25 10:52 | -6 | 2013-07-03 | Tunnelling - Linings - Sprayed Concrete | 0 |  |  | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | On the pour on the 17/6 night only one density has been recorded and this was after 70m3 had been pumped. No densities recorded for night pours on the 18th and the 20th. For the night pour on the 21st density was only recorded at the start and was not taken at the 100m3 stage.
| 01CV - Civils | Cxxx-NCR-001054 | NCR | Backfill of NW Shaft to incorrect level |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-08-01 | 2013-07-04 17:30 | -28 | 2013-07-04 | Tunnelling - Tunnelling General | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | Drawing Cxxx--C4-DWG-CRT00_ST005-50372 indicates level of 103.188mATD. This was taken as finished level of the pour but is in fact the finished level of the top of the crash-deck slab. Further heave of the surface of the low-strength concrete during the TBM transit has accentuated the problem.
| 01CV - Civils | Cxxx-NCR-001055 | NCR | 28-day compressive strength test results below specification - BOS ETH CH3 Pilot |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-08-22 | 2013-07-30 17:23 | -23 | 2013-07-04 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 5 our of 6 cores taken from test panel sprayed during Advance 16 of the Pilot Tunnel of CH3 yielded results of <28MPa.
| 01CV - Civils | Cxxx-NCR-001056 | NCR | Leading Edge |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-08-01 | 2013-07-25 10:55 | -7 | 2013-07-05 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | leading edge more than 300mm from face
| 01CV - Civils | Cxxx-NCR-001057 | NCR | Spraying Initial and Primary at the same time. |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-07-23 | 2013-07-25 10:57 | 2 | 2013-07-05 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Sprayed all at once.
| 01CV - Civils | Cxxx-NCR-001058 | NCR | Face support of Advance 58, CH3 Enl during >12hr stoppage. BOS ETH |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-08-22 | 2013-07-25 11:06 | -28 | 2013-07-08 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Equipment Breakdown | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Thickness of face support to Advance 58 (top heading) remained at 75mm for approx 24hrs.
| 01CV - Civils | Cxxx-NCR-001059 | NCR | Damaged Pipe in TCR WTH Base Slab Drainage System |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-08-22 | 2013-08-14 14:05 | -8 | 2013-07-09 | Civil - Drainage | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | During the CCTV as built survey a crack about 50-75mm long has been located in one of the runs in the base slab. See attached image.
| 01CV - Civils | Cxxx-NCR-001062 | NCR | Tunnel profile |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-08-29 | 2013-09-04 16:21 | 6 | 2013-07-11 18:08 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Over spray on CH3 enlargement chainages 144.5 to 145.5, of a maximum of 60mm on the crown area
| 01CV - Civils | Cxxx-NCR-001063 | NCR | Excavation started with concrete on stand by being out of spec. TCR SCL |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-08-16 | 2013-07-25 11:20 | -22 | 2013-07-17 13:39 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | On saturday 13/7/13 excavation started on advance 13 of the CH3 enlargement at TCR with the concrete on standby being out of spec. (very wet)
| 01CV - Civils | Cxxx-NCR-001065 | NCR | Calibration of testing equipment TCR |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-08-22 | 2013-07-26 15:03 | -27 | 2013-07-23 10:54 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | KT20.3301 General Equipment a) Any equipment supplied to the Project shall have a manufacturer declaration of conformity in accordance with BS EN 45014. Works Information Part 20 20.8 Inspection and testing The contractor shall maintain a schedule of all inspection measuring and test equipment used for the works that includes records of the calibration of such equipment to nationally recognised standards Calibration register in TCR does not include equipment used for early age strength testin. No calibration certificate available for penetrometer needle being used on site.
| 01CV - Civils | Cxxx-NCR-001066 | NCR | Training to do flow tests at TCR |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-08-22 | 2013-07-26 15:04 | -27 | 2013-07-23 11:45 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | KT20 20.8 Inspection and testing The contractor shall ensure that staff nominated for undertaking sampling, inspection and testing activities are appropriately trained and competent to carry out the particular activities to which they have been assigned. The contractor shall maintain records of training and competence and make such records available to the supervisor for inspection upon request. 20.8 Inspection and testing All on site testing and off site testing shall be carried out by laboratories accredited by UKAS or similar, acceptable body or by persons accredited to a similar standard. The samples shall be taken by staff appointed by the laboratory. The requirement for UKAS accreditation may be waived for the testing of systems and there components, subject to an alternative testing proposal by the contractor and the acceptance of the project manager. RFI000982 has been raised which asks for permission so that materials manager can train staff to do the flow tests amongst other things. This RFI was raised on the 3/6/2013 and only one shift of personnel has been trained so far at TCR. This means that for the other shifts tests are being performed by personnel that have not received the training. During surveillance on the 16/7/13 it was noticed that personnel carrying out flow test was not trained although competent to do the tests and had read and understood the instructions that had been clearly displayed on site. BS EN 12350-5 Flow Table Test 5. Sampling The Sample shall be re-mixed before carrying out the test using the remixing container and the square mouthed shovel. The training matrix does not include training for sampling and there is no remixing procedure taking place on site.
| 01CV - Civils | Cxxx-NCR-001067 | NCR | Joint preparation |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-08-19 | 2013-08-01 15:09 | -18 | 2013-07-27 12:14 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Excavation and Longitudinal joint advance 73 (bench) of CH3 tunnel were incorrectly prepared. Kwikastrip was not in level and wasn’t supported in firm ground, also the Left side was over excavated about 400mm to open an extra kwikastrip.
| 01CV - Civils | Cxxx-NCR-001068 | NCR | SFR concrete sprayed over 25mm rebar beneath CP9 & CP10 - BOS ETH CH3 Thickening |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-08-22 | 2013-08-01 12:13 | -21 | 2013-07-29 09:15 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Reject | 4 (0.5-3k) | Complete |  | Completed |  | SFR shotcrete was sprayed through he rebar installed beneath the invert of CP9 and CP10 within the CH3 thickening.
| 01CV - Civils | Cxxx-NCR-001069 | NCR | Calibration of Penetrometer at BOS SCL |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-09-19 | 2013-08-22 10:47 | -28 | 2013-08-05 14:57 | Civil - Tunnelling | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Penetrometer needles being used on site at Bond street have no calibration certificates available for review and have no unique identification number marked on them.
| 01CV - Civils | Cxxx-NCR-001070 | NCR | SMM_TCR WTH Deep Pin 8 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-08-20 | 2013-08-14 15:41 | -6 | 2013-08-06 15:38 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | TCR WTH Deep Pin 8 (DP1008) is obstructed by the cabin walkway (last reading on 31/3/13).
| 01CV - Civils | Cxxx-NCR-001072 | NCR | NCR's Regulating trial in AP3A |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-02-07 | 2014-01-31 15:45 | -7 | 2013-12-20 09:50 | Civil - Tunnelling | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | According to the method statement for the Waterproofing Membrane Trial: - The Regulating layer should be sprayed by hand and not with the potenza - The thickness check of the regulating layer should be done with a surveying system - Regulating layer soft in spots (Sprayed 02/08/2013) - Over sized aggregates within the regulating layer
| 01CV - Civils | Cxxx-NCR-001073 | NCR | Excavated advance length of adv 4 in CP7 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-01-30 | 2014-01-29 19:13 | -1 | 2013-12-20 09:54 | Tunnelling - Excavation - Hand | 1500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | In CP7, the excavation of sequence 4 (invert) is one metre too long. Invert finished with this length. Due to this mistake, a change of excavation sequence was implemented.
| 01CV - Civils | Cxxx-NCR-001074 | NCR | 600mm overexcavation for CH3 Enlargement Adv 73 (bench) on LHS |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-08-26 | 2013-08-15 13:53 | -11 | 2013-08-12 15:41 | Shafts -Sprayed Concrete | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 600mm was overexcavated on the left hand side (LHS) in the CH3 Enlargement tunnel at Adv 73 (bench)
| 01CV - Civils | Cxxx-NCR-001075 | NCR | Over excavation to 2.8m in CH3 Enlargement Adv 90 (Invert) |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-08-30 | 2013-08-22 10:49 | -8 | 2013-08-12 15:57 | Shafts -Sprayed Concrete | 1500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Adv 90 (invert) was over excavated to 2.8m. This is partially due to the under-spray of the previous invert.
| 01CV - Civils | Cxxx-NCR-001076 | NCR | Early age testing was not taken on Adv 139 CH3 therefore exceeded interval of 6 advs |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-09-04 | 2013-09-04 16:23 | 0 | 2013-08-14 09:53 | Shafts -Sprayed Concrete | 1000 |  | Supervision/Management | Reject | 4 (0.5-3k) | Complete |  | Completed |  | Early age testing was not taken on Adv 139 CH3 due to an operative removing concrete from panel. This resulted in an exceedance in the testing interval of 6 advs. Early age testing was carried out in Adv 140 in an attempt to rectify this.
| 01CV - Civils | Cxxx-NCR-001077 | NCR | Adv 127 CH3: Early strength at 2hrs lower than specified |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-08-31 | 2013-08-22 10:57 | -9 | 2013-08-15 11:36 | Shafts -Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Adv 127 CH3: Early strength at 2hrs was 0.74 whereas the J2 curve suggests it to be >1.0
| 01CV - Civils | Cxxx-NCR-001078 | NCR | SMM_TCR ATS calibration date |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-09-12 | 2013-08-22 11:03 | -21 | 2013-08-16 16:49 | Surveying - Instrumentation and Monitoring | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Calibration date for the ATSs in TCR clashed with the arrival of TBM2 and it has been decided (Survey meeting 9/7/13) to postpone it until the TBM is out of TCR area to avoid any unexpected problem with the network/readings.
| 01CV - Civils | Cxxx-NCR-001079 | NCR | 50mm underspray in primary lining at ch.223 on CH3 tunnel |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-08-30 | 2013-08-22 11:07 | -8 | 2013-08-16 18:02 | Shafts -Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Insufficient thickeness in the Primary lining at ch223 top heading.
| 01CV - Civils | Cxxx-NCR-001080 | NCR | SMM_TCR WTH Deep Pin 8 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-09-02 | 2013-08-30 09:47 | -3 | 2013-08-19 16:47 | Surveying - Instrumentation and Monitoring | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | The last reading for Deep Pin 8 in TCR WTHhas been taken at the end of March 2013 and since then the point is obstructed by site facilities. The point should be read once a month as per I&M PLan.
| 01CV - Civils | Cxxx-NCR-001082 | NCR | Spraying plain concrete in SFR area of the thickening layer |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-09-11 | 2013-09-17 11:15 | 6 | 2013-08-22 15:03 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | 2m3 of plain concrete were sprayed in an area where Steel fibre reinforced (SFR) concrete was required. As shown in the attached sketch, for an area of 30m2 the thickness of the sprayed layer should be around 70mm. This layer was sprayed in top of and SFR layer with 250mm.
| 01CV - Civils | Cxxx-NCR-001083 | NCR | Fibre content from washout 1/8/13 is below 80% of the design fibre content |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-09-27 | 2013-09-23 10:05 | -4 | 2013-08-28 16:32 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | Fibre content from washout 1/8/13 is below 80% of the design fibre content Fibre content from the washout gives an average of 22.9 which is below the specification requirement of 80% of the design fibre content, which would give a minimum value of 28.
| 01CV - Civils | Cxxx-NCR-001084 | NCR | TCR SCL Overspray in CH3 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-09-26 | 2013-09-03 10:22 | -23 | 2013-08-29 09:50 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Supervision/Management | Rework | 3 (3-6k) | Complete |  | Completed |  | When installing the reinforcement in the CH3 invert required for the AP3E/W junction thickening, it was found that there was overspray in the invert from the CH3 construction between the approximate chainages 159.000 - 161.000.
| 01CV - Civils | Cxxx-NCR-001085 | NCR | TCR SCL CH3 to AP3E/W junction thickening profiles |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-09-12 | 2013-09-12 14:57 | 0 | 2013-08-29 10:15 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Three sprayed profiles of thickening at junction CH3 to AP3E/W were found to have one point that was below the 750mm requirement. These chaianges were: 153.12 (1 point at 730mm) 155.11 (1 point at 743mm) 156.12 (1 point at 721mm) Theses were directly around the AP3E/W opening
| 01CV - Civils | Cxxx-NCR-001086 | NCR | Secondary Lining Regulating Layer Fire Protection Trials |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-09-12 | 2013-09-17 11:19 | 5 | 2013-08-29 16:22 | Materials - Approval | 3000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | Cubes were not taken for moisture content testing. Cubes taken for compressive strength testing were not cured in the same conditions as the test panels.
| 01CV - Civils | Cxxx-NCR-001088 | NCR | TCR SCL AP2W opening breakout |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-09-16 | 2013-09-12 15:07 | -4 | 2013-09-02 17:27 | Tunnelling - Linings - In-situ Concrete | 2000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | When breaking out the opening of AP2W, the excavation sequence was not followed as per the RESS (AP2W-001 see attached). See attached skecth for area broken out. This was a misunderstanding by the site team, in terms of the level as to which the opening should be broken out.
| 01CV - Civils | Cxxx-NCR-001089 | NCR | TCR SCL spraying invert without applying 75mm inital |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-09-20 | 2013-09-10 16:43 | -10 | 2013-09-06 08:13 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | Sprayed full invert advance 14 without applying 75mm initial - invert not sprayed as per RESS AP2W-003. No men entered the face prior to spraying.
| 01CV - Civils | Cxxx-NCR-001090 | NCR | Calibration check of spraying equipment accelerator dosage |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-09-27 | 2013-09-23 10:12 | -4 | 2013-09-06 08:32 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | Although regular accelerator dosage checks are carried out using Form -082 as per the ITP (Cxxx--C4-GMS-CRT00_ST005-50097), there has been no evidence to suggest recalibration of equipment if found to be outside the +-5% parameter.
| 01CV - Civils | Cxxx-NCR-001092 | NCR | Monthly Concrete Testing |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-09-30 | 2013-09-16 10:40 | -14 | 2013-09-11 11:25 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Long term testing and flexural beam testing was missed for batching plant for 12/2012, 01/2013, 04/2013 and 05/2013 (table attached).
| 01CV - Civils | Cxxx-NCR-001093 | NCR | TCR SCL Monitoring |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-09-26 | 2013-10-03 16:31 | 7 | 2013-09-12 17:24 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | A small number of monitoring points were found to not have been read for 1 day or a longer duration. This was raised in the SRG on 10/09/13. The cause of these points not being measured was either due to plant or ventilation blocking the view to the monitoring target, where a target had been damaged, or where the point had been relocated or removed as a result of SCL thickening and Cross Passage openings. A list of the monitoring points identified has been attached to the NCR.
| 01CV - Civils | Cxxx-NCR-001094 | NCR | AP4W Invert overdig |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-09-26 | 2013-09-25 11:28 | -1 | 2013-09-12 18:23 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | When excavating invert advance 4, due to the parent to child tunnel profile, to allow for bars to be drilled into the heading above to create a construction joint, some overdigging occured. Without this overdig, no bars could have been installed. However, as the leading heading (adv 3) was shorter in length at 850mm, this meant that the heading was bearing on a minimal distance on the invert below.
| 01CV - Civils | Cxxx-NCR-001095 | NCR | Inufficient face support AP4W |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-09-26 | 2013-09-27 12:41 | 1 | 2013-09-12 18:56 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Supervision/Management | Rework | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | When fixing steel at the tunnel junction at the start of day shift, it was advised that the face support be proof drilled as it appeared insufficient. The face had been sealed on the night shift and steel fixing had already been undertaken. Proof drilling showed face to be insufficeient as suspected. Additional face support was installed as per design and
| 01CV - Civils | Cxxx-NCR-001096 | NCR | Concrete was not tested at point of spray prior to spraying primary lining |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-11-01 | 2013-10-30 11:47 | -2 | 2013-09-13 16:45 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | ITP Cxxx--C4-ITP-CRT00_ST005-50050 states concrete's flow to be tested "prior to spraying" irrespective of when it was last tested. In this instance the flow was tested prior to spray of intial lining and left untested for 1hr before use in the primary lining.
| 01CV - Civils | Cxxx-NCR-001097 | NCR | AP2E overspray |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-10-31 | 2013-10-11 13:57 | -20 | 2013-09-16 19:38 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | On advances 28 and 30, there was a small amount of ove__ray in the crown which exceeded the tolerance available.
| 01CV - Civils | Cxxx-NCR-001098 | NCR | Poor 28 day core strengths at Bond Street |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-01-31 | 2013-12-15 19:10 | -47 | 2013-09-18 11:06 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Due to the workmanship of the panels being sprayed at the time in Bond street two sets of 28 day cores were of poor strength. sets of cores Numbers: 331 CH3 advance 16 and 360 CH3 Advance 34 both failed to meet the required 28 day strengths.
| 01CV - Civils | Cxxx-NCR-001099 | NCR | AP3W stitch drilling incomplete before breaking out invert |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-10-03 | 2013-09-26 14:06 | -7 | 2013-09-19 14:32 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | When commencing the breakout of AP3W advance 4, the opening from CH3, there was a 1.5m length of the circumference that had not been stitch drilled on the right hand side. Commencing the breakout without completing this length of stitch drilling or discussing it with Cxxx was against the RESS for AP3W.
| 01CV - Civils | Cxxx-NCR-001100 | NCR | AP3W over excavation of Advance 4 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-10-03 | 2013-09-24 16:10 | -9 | 2013-09-19 15:01 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The first invert of AP3W, advance 4, was over excavated which left a minimal bearing between the heading and invert. The over excavation was caused by the action of breaking out the shotcrete of the CH3 lining and, CH3 being constructed with an allowable tolerance greater than design profile.
| 01CV - Civils | Cxxx-NCR-001101 | NCR | ETH - Plunge Columns Splice plate fabrication error |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-10-18 | 2013-10-09 14:25 | -9 | 2013-09-23 11:42 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Error by manufacturer in shipping or marking | Completed |  | Splice plates bolt holes does not line up with holes on Plunge columns section. this is a fabrication error.
| 01CV - Civils | Cxxx-NCR-001102 | NCR | Break out of Adv 4 due to lamination and rebound encapsulation |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-10-14 | 2013-10-15 12:33 | 1 | 2013-09-23 15:29 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Invert (Adv 4) of AP4W required breaking out due to lamination and rebound encapsulation
| 01CV - Civils | Cxxx-NCR-001104 | NCR | AP4W Ad27 excavation |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-10-08 | 2013-09-24 16:15 | -14 | 2013-09-24 12:20 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | After commencing excavation on advance 27 on AP4W , it was found that the RESS sheet for that day had not been updated to include the chainage of advance 27.
| 01CV - Civils | Cxxx-NCR-001106 | NCR | Damage to Permanent Slab |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-10-31 | 2013-10-09 11:33 | -22 | 2013-09-24 15:08 | Civil - Civil Engineering General | 4500 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Cast in hold down bars damaged and bent during muckaway activities for handover.
| 01CV - Civils | Cxxx-NCR-001107 | NCR | Damage to corner of concrete permanent slab prior to CSJV handover |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-10-08 | 2013-10-09 11:34 | 1 | 2013-09-24 15:16 | Civil - Civil Engineering General | 4500 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Damage to corner of concrete permanent slab damage and concrete broken away prior to handover during muckaway
| 01CV - Civils | Cxxx-NCR-001108 | NCR | Edge of Slab damaged on permanent slab prior to CSJV |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-10-31 | 2013-10-09 11:39 | -22 | 2013-09-24 15:20 | Civil - Civil Engineering General | 4500 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Damage to edge of permanent slab and rebar exposed during muckaway of fill
| 01CV - Civils | Cxxx-NCR-001109 | NCR | Damage to column base and cast in couplers |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-10-29 | 2013-10-09 11:46 | -20 | 2013-09-24 15:28 | Civil - Civil Engineering General | 8000 |  | Damaged | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | Column corner damaged as well as cast in couplers on permanent slab during muckaway
| 01CV - Civils | Cxxx-NCR-001110 | NCR | Edge of permanent slab damaged during muckaway on surface |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-10-29 | 2013-10-09 11:51 | -20 | 2013-09-24 15:34 | Civil - Civil Engineering General | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Edge of permanent slab damaged and reinforcement exposed during muckaway
| 01CV - Civils | Cxxx-NCR-001111 | NCR | 2 cast in couplers exposed and bent along permanent slab |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-10-31 | 2013-10-09 11:28 | -22 | 2013-09-24 15:56 | Civil - Civil Engineering General | 4500 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Two cast in couplers exposed and bent along permanent slab
| 01CV - Civils | Cxxx-NCR-001112 | NCR | SMM - Damaged Piezometer and Extensometer in ETH |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2014-01-31 | 2014-01-28 14:52 | -3 | 2013-09-24 16:46 | Surveying - Instrumentation and Monitoring | 5000 |  | System Defect | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Peizometer 01 and Extensometer 02 are currently non-operational.
| 01CV - Civils | Cxxx-NCR-001113 | NCR | SMM - Damaged Extensometer Cxxx-XR700013 |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2014-01-31 | 2014-01-20 08:28 | -11 | 2013-09-25 10:42 | Surveying - Instrumentation and Monitoring | 5500 |  | Damaged | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | In preparation for ETH handover to Cxxx, the multiplexer for Cxxx-IE_Pile79 was damaged.
| 01CV - Civils | Cxxx-NCR-001114 | NCR | Aggregate grading less than required in March 2013 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-10-25 | 2013-09-30 14:29 | -25 | 2013-09-25 13:57 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | ITP for SCL concrete production calls for 2 gradings a month aggregates. In March 2013 only one grading occurred.
| 01CV - Civils | Cxxx-NCR-001115 | NCR | No cubes taken in March |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-10-25 | 2013-09-30 14:33 | -25 | 2013-09-25 16:23 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | AS per the ITP Cxxx--C4-ITP-CRT00_ST005-50012 line B2.1 cubes should be taken every month and in March they were not taken.
| 01CV - Civils | Cxxx-NCR-001117 | NCR | SCL re-test AP4W |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-10-11 | 2013-10-16 10:14 | 5 | 2013-09-27 14:51 | Tunnelling - Tunnelling General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | On re-testing the shotcrete prior to spraying advance 30 in AP4W, the temperature was not re-checked.
| 01CV - Civils | Cxxx-NCR-001118 | NCR | Depressurisation for platform tunnels in AP4W |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-10-11 | 2013-10-08 15:20 | -3 | 2013-09-27 15:57 | Tunnelling - Tunnelling General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | Depressurisation at the headwall for the furture PTW works was undertaken in AP4W during the nightshift on 26/09/13. These works were not specifically mentioned in the day's RESS sheet. As the tunnel was completed, with linings all to full thickness, and with no open excavation, there was some confusion as to whether this was required to be covered in the RESS.
| 01CV - Civils | Cxxx-NCR-001119 | NCR | AP2E & AP4W, Profile Control - Leading edge not Square with Face |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-11-15 | 2013-11-13 17:13 | -2 | 2013-09-30 14:55 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The leading edge in AP4W and AP2E were found to not be consistent with the designed tolerances, with the actual edge being out side of design parameters in some areas.
| 01CV - Civils | Cxxx-NCR-001120 | NCR | AP4W, Adv. 15 miners entering face before early age test |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-11-08 | 2013-11-12 09:41 | 4 | 2013-09-30 15:10 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Early age test panel was not tested before miners entered the face of heading AP4W Adv.15, only minutes after the panel had been sprayed.
| 01CV - Civils | Cxxx-NCR-001121 | NCR | AP3E Overdig |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-10-16 | 2013-10-04 15:55 | -12 | 2013-10-02 11:56 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | When breaking out the first advance on AP3E, the chainage showed approximataly 500mm of overdig.
| 01CV - Civils | Cxxx-NCR-001122 | NCR | TCR SCL In tunnel monitoring |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-10-16 | 2013-10-07 13:04 | -9 | 2013-10-02 13:11 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | On the week of the 23rd Sept, one monitoring point on chainage 161 and 199 were not read on one day.
| 01CV - Civils | Cxxx-NCR-001123 | NCR | Early age stength testing not as per the ITP |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-10-24 | 2013-10-04 16:22 | -20 | 2013-10-03 09:34 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | AP2E First early age testing done on advance 7 not 6 meaning it was on the 7th advance and between 36 and 43 the testing was also done on the 7th advance. No 2 or 4 hour test was done for advance 13. AP2W Between advance 5 and 12 the testing took place on the 7th advance and the same occurred between advance 12 and 20. AP3W Between advance 5 and 12 the testing took place on the 7th advance and the same occurred between advance 18 and 25. AP4W Between advance 20 and 29 the testing took place on the 9th advance.
| 01CV - Civils | Cxxx-NCR-001124 | NCR | Long term compressive strength testing not as per the ITP in TCR AP2E, AP3W & AP4W |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-10-24 | 2013-10-08 15:25 | -16 | 2013-10-03 10:00 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | AP2E Between advance 13 and 29 a gap of 92m3 was left between testing. AP3W Between advance 11 and 18 a gap of 70m3 was left between testing and between 18 and 25 there was a gap of 63m3 between testing. AP4W Between advance 16 and 23 a gap of 70m3 was left and between advance 26 and 33 a gap 63m3 was left. No one day cores where taken for advance 12 with the 28day cores coming from the lining.
| 01CV - Civils | Cxxx-NCR-001125 | NCR | TC Tunnel Junction Steel Repair |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-10-17 | 2013-10-08 16:40 | -9 | 2013-10-03 11:38 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | When breaking the second advance on AP3E, one bar of tunnel junction steel was damaged.
| 01CV - Civils | Cxxx-NCR-001126 | NCR | Monthly Testing Beams TCR SCL August 28 & 90 day results |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-01-17 | 2014-01-06 13:09 | -11 | 2013-10-04 14:07 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Out of the 3 Beams tested in the month of August at 28 days. One passed One failed on the D3 value One failed on both D1 and D3 And this brings the average value of the set below specification on the D3 value Out of the 3 Beams tested in the month of August at 90 days. Two passed One failed on the D3 value
| 01CV - Civils | Cxxx-NCR-001128 | NCR | BOS - AP3B/LCE2 removal of thickening mesh reinforcement |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-05-30 | 2014-05-22 17:24 | -8 | 2013-10-07 15:12 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | During the break out of the foam concrete from AP3B through LCE2 to reach the TBM segments the mesh which was left exposed to form the connection between LCE and AP3B was ripped out. See attached photographs.
| 01CV - Civils | Cxxx-NCR-001129 | NCR | TCR GS3 TaM Drilling out of Tolerance and TaMs have encountered obstructions |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-11-11 | 2013-11-07 18:05 | -4 | 2013-10-21 12:30 | Geotechnical Engineering - Compensation Grouting | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | The TaM ref 27 to 27a is out of H deviation tolerance (>4m to the adjacent TaMs) T3/ 27A =4478m gap The following holes have encountered obstructions: T3/46 between 4 and 5 meters T3/49 at 4.5 meters T3/53 at 5 meters T3/56 at 5.6 meters In TaMs 46,49,53 investigation has been carried out by a camara survey and found to be concrete The nature of obstruction is unknown for TaM 56
| 01CV - Civils | Cxxx-NCR-001130 | NCR | Over Excavation AP4E Advance 22 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-11-08 | 2013-11-12 09:42 | 4 | 2013-10-07 16:27 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During construction of Access Passage 4 East, advance 22 (heading) was over excavated. This meant that the excavated profile did not match that outlined in the RESS.
| 01CV - Civils | Cxxx-NCR-001131 | NCR | Engineers signatures missing on form 50 for CH3 advances |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2013-11-21 | 2013-11-12 17:09 | -9 | 2013-10-08 15:23 | Civil - Tunnelling | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | It was noted during pre-submission reveiw of the CH3 primary lining construction records that the engineers signature was missing from the form 50 on a number of advances.
| 01CV - Civils | Cxxx-NCR-001132 | NCR | Early age stength testing not as per the ITP TCR AP3E & AP4E |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-11-04 | 2013-10-14 15:41 | -21 | 2013-10-14 14:01 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | AP3E Between advances 6 & advance 20 testing took place on the 14th advance. AP4E Between advance 12 and 19 the testing took place on the 7th advance and the same occurred between advance 19 and 26. On these advances testing should have taken place on the 6th advance so they are not per the ITP.
| 01CV - Civils | Cxxx-NCR-001134 | NCR | Long term compressive strength testing not as per the ITP in TCR AP3E & AP4E |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-11-04 | 2013-11-04 12:16 | 0 | 2013-10-14 14:58 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | AP3E Between advance 8 and advance 18 there was a gap of 73m^3 between testing and between advance 18 and advance 28 there was a gap of 71m^3 between testing. AP4E Between advance 12 and 21 there was a gap of 71.5m^3 between testing and between advance 26 and advance 35 there was a gap of 66m^3 between testing. These are all above the 50m^3 spacing stated in the ITP.
| 01CV - Civils | Cxxx-NCR-001135 | NCR | TCR CH1 Flare Stitch drilling |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-10-28 | 2013-10-15 13:59 | -13 | 2013-10-14 18:15 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | On advance 4 for the CH1 Flare, the bench area stitch drilling was undertaken, which will be required as part of the works. However, this extent of stitch drilling in the bench area was not defined as to be done on the current RESS sheet.
| 01CV - Civils | Cxxx-NCR-001136 | NCR | Monthly Testing Beams BOS SCL August Mix 17.2 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-12-20 | 2013-12-19 14:23 | -1 | 2013-10-23 14:13 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Out of the 3 Beams tested in the month of August at 28 days. Average D1 value came back as 1.4 which is below the 1.8 requirement. Average D3 value after recaluation ignoring the drop zone failure (squigilly line) came back as 1.2 which is below the 1.4 requirement.
| 01CV - Civils | Cxxx-NCR-001137 | NCR | Kwikastrip Installation |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-11-19 | 2013-11-04 12:47 | -15 | 2013-10-29 08:32 | Surveying - Tunnels/Portal/Shafts surveys | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | Kwikastrip installed in thickening layer as oppose to primary lining in AP7a ch 8.5-11. This error is due to a lack of communication regarding the change in surveying reference lines to the engineers.
| 01CV - Civils | Cxxx-NCR-001138 | NCR | Incorrect spraying method on AP7a invert |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-12-10 | 2013-12-04 16:33 | -6 | 2013-10-29 08:41 | Tunnelling - Linings - Sprayed Concrete | 3500 |  | Workmanship | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During Adv 14 (invert) of AP7a, the initial was applied after excavation. Following the removal of rebound the primary lining was applied, however, only half of the invert was sprayed to full profile leaving the other half with the initial only. This is the incorrect method of spraying the primary lining of an invert and could lead to rebound encapsulation.
| 01CV - Civils | Cxxx-NCR-001139 | NCR | 28 day comprssive strength tests in AP4W |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-11-20 | 2013-11-04 13:03 | -16 | 2013-10-30 08:42 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate resources | Completed |  | Sample 230 from advance 6 in AP4W was not tested at 28 days Sample 247 from advance 36 in AP4W was not tested at 28 days
| 01CV - Civils | Cxxx-NCR-001140 | NCR | TCR 1-3 day cores |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-11-20 | 2013-11-04 13:13 | -16 | 2013-10-30 08:56 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | AP7A Advance 9 Sample 282 A set of 6 cores to be tested between 1-3 days were tested at 4 days.
| 01CV - Civils | Cxxx-NCR-001141 | NCR | Monthly Testing September - Beams |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-02-13 | 2014-01-30 14:36 | -14 | 2013-11-08 13:10 | Tunnelling - Linings - Sprayed Concrete | 8000 |  | Material | Rework | 2 (6-60k) | Complete | Material/Preservation Problems - Other | Completed |  | Out of the 3 Beams tested in the month of September at 28 days. One passed Two failed on both D1 and D3
| 01CV - Civils | Cxxx-NCR-001142 | NCR | Aggregate grading less than required in August 2013 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-11-29 | 2013-11-13 17:11 | -16 | 2013-11-08 14:37 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | ITP for SCL concrete production calls for 2 gradings a month aggregates. In August 2013 only one grading occurred. Sample was taken but sample certificate was missing information.
| 01CV - Civils | Cxxx-NCR-001143 | NCR | Insufficient thickness in primary lining of Adv 23 in AP7a |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-12-06 | 2013-11-30 11:15 | -6 | 2013-11-11 19:18 | Tunnelling - Linings - Sprayed Concrete | 3500 |  | Supervision/Management | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Upon excavation of Adv 4 of AP7b, it was noticed that there was insufficient thickness at the joint (ch4.5). This therefore meant that when excavating Adv23 on AP7a, this area was under mucked by 170mm i.e. 80mm shotcrete in lining.
| 01CV - Civils | Cxxx-NCR-001146 | NCR | TCR WTH Base Slab Manhole Construction |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-11-27 | 2013-11-27 14:55 | 0 | 2013-11-13 12:36 | Civil - Drainage | 2500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | On drawing Cxxx-OVE-P-DDD-N105_Z-30110 it shaows a Manhole section in Detail No.06. It shows boared pipelines through the manhole chamber. The actual construction that took place was a half pipe placed through it and then grouted up to suit. See attached sketch.
| 01CV - Civils | Cxxx-NCR-001147 | NCR | Presentation of complete profile information to SRG for PTW enlargement advances 6-10 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-12-05 | 2013-11-28 14:13 | -7 | 2013-11-14 17:36 | Tunnelling - Linings - Sprayed Concrete | 2000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Not Defined | Completed |  | Incomplete profile information has been presented to the SRG for PTW enlargement. This has occurred over a period of 5 separate advances (temporary SCL flare).
| 01CV - Civils | Cxxx-NCR-001148 | NCR | Plunge Column P19t Bracing |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-12-19 | 2013-12-03 16:30 | -16 | 2013-11-19 17:22 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After raised issues with the plunge column installation it was agreed to do a joint inspection. This happened on 18/11/13 in presence of __ (Agent ) and __ (Sub-Agent ), no CRL present. See inspected items on plunge column P19t bracings on attached list, with items that are not built according to the design marked in orange or red, items built to design marked in green. Items marked in purple were not visible at time of inspection. Also see photos of inspected works attached.
| 01CV - Civils | Cxxx-NCR-001149 | NCR | Plunge Column P12t Bracing |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-12-19 | 2013-12-03 17:58 | -16 | 2013-11-19 17:27 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After raised issues with the plunge column installation it was agreed to do a joint inspection. This happened on 18/11/13 in presence of __ (Agent ) and __ (Sub-Agent ), no CRL present. See inspected items on plunge column P12t bracings on attached list, with items that are not built according to the design marked in orange or red, items built to design marked in green. Items marked in purple were not visible at time of inspection. Also see photos of inspected works attached.
| 01CV - Civils | Cxxx-NCR-001150 | NCR | Plunge Column P15t Bracing |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-12-19 | 2013-12-03 18:01 | -16 | 2013-11-19 17:29 | Tunnelling - Linings - Sprayed Concrete | 2500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After raised issues with the plunge column installation it was agreed to do a joint inspection. This happened on 18/11/13 in presence of __ (Agent ) and __ (Sub-Agent ), no CRL present. See inspected items on plunge column P15t bracings on attached list, with items that are not built according to the design marked in orange or red, items built to design marked in green. Items marked in purple were not visible at time of inspection. Also see photos of inspected works attached.
| 01CV - Civils | Cxxx-NCR-001152 | NCR | Plunge Column P16t Bracing |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-12-19 | 2013-12-03 18:04 | -16 | 2013-11-19 17:33 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After raised issues with the plunge column installation it was agreed to do a joint inspection. This happened on 18/11/13 in presence of __ (Agent ) and __ (Sub-Agent ), no CRL present. See inspected items on plunge column P16t bracings on attached list, with items that are not built according to the design marked in orange or red, items built to design marked in green. Items marked in purple were not visible at time of inspection. Also see photos of inspected works attached.
| 01CV - Civils | Cxxx-NCR-001153 | NCR | Plunge Column P20t Bracing |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-12-19 | 2013-12-03 18:05 | -16 | 2013-11-19 17:34 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After raised issues with the plunge column installation it was agreed to do a joint inspection. This happened on 18/11/13 in presence of __ (Agent ) and __ (Sub-Agent ), no CRL present. See inspected items on plunge column P20t bracings on attached list, with items that are not built according to the design marked in orange or red, items built to design marked in green. Items marked in purple were not visible at time of inspection. Also see photos of inspected works attached.
| 01CV - Civils | Cxxx-NCR-001154 | NCR | Plunge Column P23t Bracing |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-12-19 | 2013-12-03 17:04 | -16 | 2013-11-19 17:36 | Tunnelling - Linings - Sprayed Concrete | 2000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After raised issues with the plunge column installation it was agreed to do a joint inspection. This happened on 18/11/13 in presence of __ (Agent ) and __ (Sub-Agent ), no CRL present. See inspected items on plunge column P23t bracings on attached list, with items that are not built according to the design marked in orange or red, items built to design marked in green. Items marked in purple were not visible at time of inspection. Also see photos of inspected works attached.
| 01CV - Civils | Cxxx-NCR-001155 | NCR | Failure of early strength @1 and 2 hours for advance 28 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-12-12 | 2013-12-03 16:41 | -9 | 2013-11-21 13:51 | Tunnelling - Linings - Sprayed Concrete | 4000 |  | Material | Use As-Is | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | 1 and 2 hour results were below the J2 curve
| 01CV - Civils | Cxxx-NCR-001156 | NCR | Initial lining not sprayed on invert face before primary lining bulk out |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-12-05 | 2013-11-27 08:32 | -8 | 2013-11-21 17:02 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | When spraying the invert of advance 25, the initial lining of 75mm was not sprayed on the face before the bulking out of the primary lining on the profile
| 01CV - Civils | Cxxx-NCR-001157 | NCR | Monitoring points no 6 and 7 placed to high for RMS9 and RMS18. Invert points missing |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-12-02 | 2013-11-28 14:22 | -4 | 2013-11-25 05:05 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Monitoring points no. 6 and 7 for RMS9 and RMS18 were placed to high. They should have been placed lower towards the invert of the tunnel.
| 01CV - Civils | Cxxx-NCR-001158 | NCR | Damage to permanent works - Partial hand-over of the ETH |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2014-01-30 | 2014-01-28 14:54 | -2 | 2013-11-25 11:09 | Civil - Civil Engineering General | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Damage to permanent works between gridlines 1-2 and E-F of Cxxx-__-S-DDL-Cxxx-52100 not covered in NCR's Cxxx-NCR-001106, 001107, 001108, 001109, 001110, 001111. 1. Bolt sets bent. 2. Slab surface gouging / bucket tooth marks and abrasion.
| 01CV - Civils | Cxxx-NCR-001159 | NCR | Damage to permanent works - Partial hand-over of the ETH - Section 2 |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2014-01-30 | 2013-12-09 08:16 | -52 | 2013-11-25 12:02 | Civil - Civil Engineering General | 50000 |  | Damaged | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Damage to permanent work between gridlines 2-4 and D-F of drawing Cxxx-__-S-DDL-Cxxx-52100 not covered by NCR's Cxxx-NCR-001106, 001107, 001108, 001109, 001110, 001111. 1. Damage along the edge of slab in 7 locations. See attached images: 026, 032, 034, 035, 059, 060, 061. 2. Slab surface gouging / bucket tooth marks in 7 location. See attached images: 033, 039, 042, 043, 049, 051, 064.
| 01CV - Civils | Cxxx-NCR-001160 | NCR | Damage to permanent works - Partial hand-over of the ETH - Section 3 |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2014-01-30 | 2013-12-09 08:17 | -52 | 2013-11-25 12:36 | Civil - Civil Engineering General | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Damage to permanent works between gridlines 3-4 and C-D of drawing Cxxx-__-S-DDL-Cxxx-52100 not covered in Cxxx-NCR-001106, 001107, 001108, 001109, 001110, 001111. 1. Damaged couplers (6 no.). See image 070. 2. Damage to slab edge, 1 location. See image 071. 3. Damage to the edge of the capping beam. See image 075.
| 01CV - Civils | Cxxx-NCR-001161 | NCR | 1 day cores in CH3 TCR |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-12-17 | 2013-12-03 16:52 | -14 | 2013-11-26 17:06 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | 1-3 day cores were tested late at 4 days from Advance 94 Ch186.64-188.64, Invert. Sample 186 1-3 days cores were missed at CH3/AP7 thickening (Invert). Sample 214 1-3 day cores were tested late at 12 days for thickening CH3/AP4 (Heading) Sample 214A 28 day cores were crushed early at 4 and 5 days to enable breakthrough, unfortunately no further cores were taken to make up for this.
| 01CV - Civils | Cxxx-NCR-001162 | NCR | TCR A3E Overspray |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-12-13 | 2013-12-02 11:22 | -11 | 2013-11-29 15:32 | Tunnelling - Linings - Sprayed Concrete | 12000 |  | Supervision/Management | Rework | 2 (6-60k) | Complete | Supervision - Insufficient supervision | Completed |  | In accordance with drawing Cxxx-MMD-C4-DDD-N105_Z-00035, the calculated tolerance is 100mm +/- 20mm. On reviewing the as-built profiles and onsite checks prior to spraying the regulating, it was found that there were a small number of points that were below the required tolerance (0-80mm). This means that there is no allowance for deformation tolerance where the points are less than 50mm as required on the above drawing.
| 01CV - Civils | Cxxx-NCR-001163 | NCR | TCR AP3W Overspray |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-12-13 | 2013-12-02 11:29 | -11 | 2013-11-29 14:54 | Tunnelling - Linings - Sprayed Concrete | 12000 |  | Supervision/Management | Rework | 2 (6-60k) | Complete | Management Problem - Inadequate supervision | Completed |  | In accordance with drawing Cxxx-MMD-C4-DDD-N105_Z-00035, the calculated tolerance is 100mm +/- 20mm. On reviewing the as-built profiles and onsite checks prior to spraying the regulating, it was found that there were a small number of points that were below the required tolerance (0-80mm). This means that there is no allowance for deformation tolerance where the points are less than 50mm as required on the above drawing.
| 01CV - Civils | Cxxx-NCR-001164 | NCR | AP7A Timber heading |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-12-10 | 2013-12-03 16:39 | -7 | 2013-11-26 19:55 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Work commenced on AP7a two hours before the Inspection Test Plan had been signed off by Crossrail. A method statement was in place for the works.
| 01CV - Civils | Cxxx-NCR-001165 | NCR | Early age strength @2 hours failed |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-12-12 | 2013-12-03 16:54 | -9 | 2013-11-28 09:02 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | 25/11/2013 early age strength test failed @2 hours for mix 17.2
| 01CV - Civils | Cxxx-NCR-001166 | NCR | Plunge Column P16t out of verticality |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-12-12 | 2013-12-04 11:19 | -8 | 2013-11-28 09:17 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Plunge Column P16twas found to be out-of-verticality by 28mm between the baseplate and the first (lowest) splice position ~13m above. This corresponds to an out-of-verticality of 0.22%.
| 01CV - Civils | Cxxx-NCR-001167 | NCR | Incorrect profile on TRC AP3E |  | Crossrail | PDP | BOS - Bond Street Station (West) |  | 2013-12-12 | 2013-12-05 15:45 | -7 | 2013-11-28 11:47 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Supervision/Management | Use As-Is | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | In order to rectify defect identified in NCR 001162: The primary lining of the AP3E tunnel had over-sprayed locations that needed to be profiled back to the acceptable primary lining profile. When milling these locations the road-header over milled them and took away excess primary lining. These locations are to be provided by . It was also noted there was a lack of supervision during these operations.
| 01CV - Civils | Cxxx-NCR-001168 | NCR | Incorrect profile on TRC AP3W |  | Crossrail | PDP | BOS - Bond Street Station (West) |  | 2013-12-12 | 2013-12-04 11:00 | -8 | 2013-11-28 11:53 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Supervision/Management | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | In order to rectify defect identified in NCR 001163: The primary lining of the AP3E tunnel had over-sprayed locations that needed to be profiled back to the acceptable primary lining profile. When milling these locations the road-header over milled them and took away excess primary lining. These locations are to be provided by . It was also noted there was a lack of supervision during these operations.
| 01CV - Civils | Cxxx-NCR-001169 | NCR | Concrete Temperature below 15degree |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-12-15 | 2013-12-04 16:28 | -11 | 2013-12-01 15:26 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Concrete which arrived at Hanover Sq was initially tested at 15degree. After one hour the batch was tested again at 14.6degree. This 3m3 was delivered to the pit bottm and used to spray top heading 62.
| 01CV - Civils | Cxxx-NCR-001170 | NCR | Monitoring Targets missed in PTW |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-12-15 | 2013-12-04 16:34 | -11 | 2013-12-01 15:37 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | RMS were not placed after Top Heading Advance 62 was sprayed (chainage 45.25)
| 01CV - Civils | Cxxx-NCR-001171 | NCR | Overspraying concrete to advance 58 in PTW |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-12-16 | 2013-12-15 19:08 | -1 | 2013-12-02 15:36 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Rework | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | The RHS to advance 58 at chainage 40.30m was oversprayed by approximately 100-120mm.
| 01CV - Civils | Cxxx-NCR-001172 | NCR | Flow & specific gravity results fail to comply with the specification limits GS BOS1 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-01-31 | 2014-01-08 16:16 | -23 | 2013-12-03 16:22 | Geotechnical Engineering - Compensation Grouting | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | As per the attached field grout testing results for Pre-treatment works in BOS 1 shaft, its noted that flow & specific gravity test results fail to comply the specification limits and also lack of cube results recorded as per the ITP & material approval reference Cxxx--C-LRC-CRT00_ST005-50074 Rev.2
| 01CV - Civils | Cxxx-NCR-001175 | NCR | Tunnel face not sealed with 150mm of shotcrete after 12hr |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-12-18 | 2013-12-19 14:25 | 1 | 2013-12-04 14:36 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During a 24hr stoppage in the tunnel works the face of top heading 75 and invert 76 was required to have 150mm of shotcrete to ensure a safe stop procedure. However some areas of the face had a maximum of 100mm, 50mm less than required.
| 01CV - Civils | Cxxx-NCR-001176 | NCR | Rebound washout below required spec defined in KT20 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-04-29 | 2014-04-15 14:18 | -14 | 2013-12-10 12:42 | Tunnelling - Linings - Sprayed Concrete | 3500 |  | Material | Use As-Is | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | The 3 washout conducted for the rebound test were all below the 35 kg design requirement KT20.2201 c) ix) The average fibre content from the set of three samples should reflect the design fibre content and no individual sample shall have a fibre content less than 80% of th design fibre content.
| 01CV - Civils | Cxxx-NCR-001177 | NCR | Compressive Results taken outside the accepted window of 1-3days |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2013-12-20 | 2013-12-10 10:51 | -10 | 2013-12-06 09:48 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Compressive strength cores tested 4-9 day age (certificates attached) outside the accepted window of 1-3 days
| 01CV - Civils | Cxxx-NCR-001178 | NCR | BOS ETH - Installation of Inclinometer 113 |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2014-01-31 | 2014-01-10 15:19 | -21 | 2013-12-09 11:39 | Surveying - Instrumentation and Monitoring | 15000 |  | Supervision/Management | Use As-Is | 2 (6-60k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Under PMI 814 BOS ETH Handover of Deep Instruments was instructed to install inclinometer 113. This has not been undertaken to date.
| 01CV - Civils | Cxxx-NCR-001179 | NCR | Low concrete temperature for AP3A Ch 12.5-17.5 thickening April 2013 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-02-28 | 2014-02-19 10:52 | -9 | 2013-12-12 14:14 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Low concrete temperature for AP3A Ch 12.5-17.5 thickening April 2013
| 01CV - Civils | Cxxx-NCR-001181 | NCR | 90 day beam test low for Adv 37 LCE (April 2013) and 69B LCE (May 2013) |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-03-12 | 2014-01-23 17:56 | -48 | 2013-12-12 13:41 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | 28 day beam test passed but 90 day low for Adv 37 LCE (April 2013) and 69B LCE (May 2013)
| 01CV - Civils | Cxxx-NCR-001182 | NCR | Fibre Washout result below specification |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-02-28 | 2014-02-25 14:46 | -3 | 2013-12-11 13:11 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | KT20.2201 c) ix) The average fibre content from the set of three samples should reflect the design fibre content and no individual sample shall have a fibre content less than 80% of the design fibre content. Two of the individual results were below 80% and the average was less than the design fibre content of 35.
| 01CV - Civils | Cxxx-NCR-001183 | NCR | Stored accelerator (TamShot 80AF) temperature below the minimum required |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-01-30 | 2014-01-21 12:42 | -9 | 2013-12-12 11:31 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper storage of material | Completed |  | TamShot 80AF was stored at less than 10C. This is less than that detailed on the TamShot 80AF storage guidelines.
| 01CV - Civils | Cxxx-NCR-001184 | NCR | SCL Nozzleman Competencies (AP7a Advance 23) |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2014-02-10 | 2014-02-11 10:13 | 1 | 2013-12-13 03:18 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Worker not qualified | Completed |  | On 29/10/2013, a trainee Nozzleman was observed spraying Advance 23 (invert) of AP7a without any supervision. Following the issue to CRL (on 04/12/2013) of the list of TCR Nozzleman, it was confirmed that the trainee Nozzleman should have been supervised whilst he was spraying the advance [KT20.2107 (b) (i)].
| 01CV - Civils | Cxxx-NCR-001185 | NCR | PTW Advance 30 commenced without sufficient shotcrete available on-site |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2014-01-31 | 2014-01-24 15:35 | -7 | 2013-12-14 01:02 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | PTW Advance 30 (Top Heading) excavation was started yet there was an insufficient amount of wet mix concrete available to immediate support the excavated face/profile [KT20.3207 (k)]. There was approximately 1.0m3 of shotcrete that was available when the excavation commenced. On completion of the excavation, the standby load was sprayed to seal the excavated face. However, this was insufficient to safely seal the exposed faces. It took approximately 1.50 hours after this load was used for the remainder of the shotcrete to arrive on site after which the excavation was fully sealed.
| 01CV - Civils | Cxxx-NCR-001187 | NCR | Accelerator dosing pump calibration checksheets for CH1 Enlargement TCR |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-01-31 | 2014-01-20 15:54 | -11 | 2013-12-17 10:57 | Tunnelling - Tunnelling General | 1500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not trained for the work being performed | Completed |  | __ checks were incorrectly recorded by the engineers.
| 01CV - Civils | Cxxx-NCR-001188 | NCR | NCR – BOS Exceeding the maximum heave for a grout jacking episode |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2014-02-04 | 2014-02-04 16:24 | 0 | 2013-12-18 17:50 | Surveying - Instrumentation and Monitoring | 1500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | It was has been identified in the CTC minutes on 13.11.26 @ 1100hrs and CTC 13.12.03 @ 1100hrs that the heave as a result of grouting has been ~9mm. Cxxx-OVE-C2-RSP-Cxxx-00001 “SCOGM” Section 3.2.5.13 states that “The maximum heave generated during a grout jacking episode shall be 5mm”. The grouting in the area noted on the 13.11.26 & 13.12.03 have exceeded this maximum limit.
| 01CV - Civils | Cxxx-NCR-001189 | NCR | NCR – BOS Notification of a Red Trigger the Incident Response Desk (IRD) |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2014-01-24 | 2014-01-15 19:11 | -9 | 2013-12-18 17:53 | Surveying - Instrumentation and Monitoring | 4500 |  | Supervision/Management | Use As-Is | 3 (3-6k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | In the Bond Street SRG on 13.12.02 @ 1600hrs a red trigger had been identified. Cxxx--C4-STP-CRT00_ST005-51801 Rev 2.0 - MANAGEMENT PLAN FOR THE CONTROL OF GROUND MOVEMENTS~ ADDENDUM 40~ BOND STREET STATION ~SCL Phase 2 Works state in section 5 Alert & Trigger levels and Action Plans that “RED and BLACK TRIGGERS (not ALERTS) have to be reported to the CRL Incident Reporting Desk (IRD) under the RIVO system. As of the 13.12.17 (15days) after the trigger the IRD had not been notified.
| 01CV - Civils | Cxxx-NCR-001191 | NCR | Low Concrete and Air Temp LCE Adv 14 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-01-24 | 2014-01-20 15:58 | -4 | 2014-01-10 11:49 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Low Concrete temp (13.3 C) and Air Temp (2.3 C) LCE Adv 14
| 01CV - Civils | Cxxx-NCR-001193 | NCR | Concrete re-testing at point of spray for PTW Adv 98 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-02-04 | 2014-02-04 15:59 | 0 | 2014-01-14 10:57 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | As stated in KT20 [KT20.3206 b)] and ’s ITP (Cxxx--C4-ITP-CRT00_ST005-50011 Rev 3.0 – B4.5 & B4.6), every shotcrete load that is to be sprayed needs to be tested at all times during batching, delivery and at the point of spray application. It was recorded that the loads used to spray PTW Adv 98 Primary Lining were tested at 11:02 & 11:15 respectively. However, spraying commenced at 12:00 and there is no record of tests carried out prior to spray.
| 01CV - Civils | Cxxx-NCR-001194 | NCR | NCR- Flow & specific gravity results fail to comply with the specification limits GS BOS3,TCR1&7 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-01-28 | 2014-01-14 15:36 | -14 | 2014-01-14 11:31 | Geotechnical Engineering - Compensation Grouting | 1000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | As per the attached field grout testing results for Pre-treatment works in BOS 3, TCR1& TCR7 shaft, its noted that flow & specific gravity test results fail to comply the specification limits and also lack of cube results recorded as per the ITP & material approval reference Cxxx--C-LRCCRT00_ST005-50074 Rev.2
| 01CV - Civils | Cxxx-NCR-001195 | NCR | Insufficient survey points taken on PTW Adv 68 & 69 TH excavation profile |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-02-04 | 2014-01-21 17:04 | -14 | 2014-01-14 13:21 | Surveying - Tunnels/Portal/Shafts surveys | 1500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Not enough points were taken on the excavation profiles of PTW Adv 68 & 69 Shift Engineers are to keep a minimum spacing of 1m between points.
| 01CV - Civils | Cxxx-NCR-001196 | NCR | Temperatures of Regulating layer during trial below 15 degrees |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-02-28 | 2014-02-14 15:18 | -14 | 2014-01-14 14:59 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | During Regulating trails in TCR AP3E on the 5/1/14 the temperature of the Regulating mix was recoreded below 15 degrees at 6.45 in mixer number 2 fresh sample temperature was 12.6 degrees at 9.05 in mixer number 2 fresh sample temperature was 14.4 degrees at 6.15 in mixer number 3 fresh sample temperature was 14.9 degrees
| 01CV - Civils | Cxxx-NCR-001197 | NCR | Low Fresh Fibre Content |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-02-14 | 2014-02-13 17:39 | -1 | 2014-01-17 16:47 | Tunnelling - Linings - Sprayed Concrete | 2500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Low Fresh fibre content on 15/12/2013 (Thickening 52-65), 09/01/2014 (PTW 116), 11/01/2014 (PTW 126). Results attached to the NCR
| 01CV - Civils | Cxxx-NCR-001198 | NCR | Damage to ETH permanent slab in the south-east corner |  | Crossrail | PDP | BOS - Bond Street Station (West) |  | 2014-03-27 | 2014-02-18 17:32 | -37 | 2014-01-22 13:20 | Tunnelling - Tunnelling General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | are exposed the permanent slab in the south-east corner (not exposed during handover). It seems the slab in this area was not protected, uncovering has revealed that damage is present (photo attached). Concrete damage to mole hole opening at SE corner of East Ticket Hall site. This affects all four edges of the mole hole, typically concrete has broken off leaving poor finish standard. However in some locations rebar has also been exposed, the exposed rebar is not damaged
| 01CV - Civils | Cxxx-NCR-001202 | NCR | Engineers not carrying out 10 and 30 minutes penetrometer early age strength test |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-02-12 | 2014-01-31 16:45 | -12 | 2014-01-29 16:59 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Engineers not carrying out 10 and 30 minutes penetrometer early age strength test
| 01CV - Civils | Cxxx-NCR-001203 | NCR | Oversized aggregate in shotcrete |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-02-20 | 2014-02-18 17:00 | -2 | 2014-01-30 09:37 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | On 14/01/14 oversized aggregate was found within the shotcrete delivrered to site from s, not to specification.
| 01CV - Civils | Cxxx-NCR-001204 | NCR | Geological Mapping of Adv 141 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-02-13 | 2014-02-14 15:26 | 1 | 2014-01-30 09:41 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Shear Strength in logs missing due to miscommunication in adv 141 (top heading) in PTW
| 01CV - Civils | Cxxx-NCR-001206 | NCR | Fibre washout for CH3 in June being low |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-02-13 | 2014-02-10 16:32 | -3 | 2014-01-30 17:11 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Lack or improper material identification and traceability | Completed |  | Fibre washout done in the Month of June were low and the figures were as follows: 23.2kg/m3,29.9kg/m3 and 30.7kg/m3.
| 01CV - Civils | Cxxx-NCR-001207 | NCR | Fibres still protruding after regulating layer sprayed in AP3 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-02-28 | 2014-03-05 17:41 | 5 | 2014-01-31 14:02 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After completing the Regulating trials in TCR AP3W between the dates of 19/12/2013 and 04/1/2014, it was found through a visual inspection that fibres were still protruding out.
| 01CV - Civils | Cxxx-NCR-001208 | NCR | 1 day cores taken outside the acceptable window of 1 to 3 days for advances 201a,193 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-02-14 | 2014-02-12 15:46 | -2 | 2014-01-31 12:46 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | 1day cores for PTW taken outside accepted window of 1-3 days because the panel was sprayed in front of the spraying machine and due to the miners still working in that vicinity and the potenza being in the way i was unable to move the panels. I also was unable to core the panel where it stood because it was unsafe.
| 01CV - Civils | Cxxx-NCR-001209 | NCR | Low Fibre washouts in January |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-03-07 | 2014-03-06 13:13 | -1 | 2014-01-31 13:38 | Tunnelling - Linings - Sprayed Concrete | 2500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Lack or improper material identification and traceability | Completed |  | Low Fresh fibre content on 17/01/2014,@ advance 157 PTW, 21/01/2014 @ advance 179 PTW, 22/01/2014 @advance 184 PTW and 26/01/2014 @ PTW thickening. Results attached to the NCR
| 01CV - Civils | Cxxx-NCR-001210 | NCR | Not enough cores taken taken @ 28 days & in a few instances cores taken outside the required 28 day window |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-03-28 | 2014-02-11 10:35 | -45 | 2014-02-03 18:21 | Tunnelling - Linings - Sprayed Concrete | 2500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | During the month of November in some instances rather than six 28 day core results only 3 was taken ie: Advances 13,33,39,48,55, also in two instances compressive results were outside the 28 day window ie: Advance 13 and 25 Advance of PTW .
| 01CV - Civils | Cxxx-NCR-001211 | NCR | Fibres stored at Silvertown and Vic Deep not stored under cover |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-03-06 | 2014-02-04 17:04 | -30 | 2014-02-04 11:38 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper storage of material | Completed |  | During a surveillance at Silvertown on the 17/1/14 it was observed that large bags of fibres where being stored in the open against manufacturers guidelines. This was alos observed during a surveillance by crossrail on the 22/1/14 at victoria deep.
| 01CV - Civils | Cxxx-NCR-001212 | NCR | Monitoring of temperatures of admixtures at Silvertown and Vic deep not taking place |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-03-06 | 2014-03-04 13:10 | -2 | 2014-02-04 12:06 | Tunnelling - Linings - Sprayed Concrete | 2500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | During a surveillance at Silvertown on the 17/1/14 it was observed that s do not monitor the temperature of the admixtures. This was also observed during a surveillance by crossrail on the 22/1/14 at victoria deep.
| 01CV - Civils | Cxxx-NCR-001213 | NCR | Long Term Compressive Strength 28 Day Cores |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-02-25 | 2014-02-14 15:34 | -11 | 2014-02-04 12:31 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Verbal communication problem | Completed |  | AP7B Advance 11 we had planned to take sets of cores for routine 50m3 testing. The 1 day cores were tested but the original 28 day cores have been lost.
| 01CV - Civils | Cxxx-NCR-001214 | NCR | SGI Segments BOS Vent Tunnel Diverson |  | Crossrail | PDP | BOS - Bond Street Station (West) |  | 2014-02-19 | 2014-02-18 16:18 | -1 | 2014-02-05 15:43 | Tunnelling - Linings - SGI Rings | 5000 |  | Design | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Casting of SGI segments for the Vent Tunnel Diversion is out of Specification Cxxx-PMI-00158 issued Cxxx - M&W Specification KN20 Cxxx -OVE-Z4-RSP-CR001-00006 Clause KN20.3102 Marking of Castings Marks as indicated on the Drawings shall be distinct and shall be cast on the inner surface of the skin of each casting as follows: a) Internal diameter. b) Crossrail. c) Date of casting. d) Type of ring and type of segment: i) O ordinary; ii) T top. The T shall be at the key end of the segment; iii) X special or taper. e) Maker's name and mark. The following errors are noted: a)Is not marked on some, b) Is incorrect as it states " / Cxxx", c) Date of casting is not shown. Any deviation from the above should be approved by the PM, this as far as we are aware has not been done.
| 01CV - Civils | Cxxx-NCR-001215 | NCR | SMM - Amber Level Trigger Breach Along South Molton Street |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-02-21 | 2014-02-14 15:38 | -7 | 2014-02-07 12:45 | Geotechnical Engineering - Settlement | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other management problem | Completed |  | Two Amber Trigger on slopes have been breached in South Molton Street (west) between B07LB044-B07LB045 / B07LB047-B07LB048. The breach has been communicated to the BOS.CTC.internal group as per management plan. (see attached email). Action: - Point has be resurveyed - continue with PTW excavation and grout over when area is out of exclusion zone.
| 01CV - Civils | Cxxx-NCR-001216 | NCR | SMM - Amber Level Trigger Breach Along South Molton Street 07/02/2014 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-02-21 | 2014-02-24 08:23 | 3 | 2014-02-07 17:27 | Geotechnical Engineering - Settlement | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | New Amber Breach on __ slopes: B07LB044 – B0LB043 Green Trigger breach on __s slope: B07LB042 – B07LB043 The breach has been communicated to the BOS.CTC.internal group as per management plan. (see attached email) Actions: Points will be re-surveyed Continue with PTW excavation and grout over when area is out of exclusion zone.
| 01CV - Civils | Cxxx-NCR-001217 | NCR | Drainage in WTH base slab |  | Crossrail | PDP | BOS - Bond Street Station (West) |  | 2014-12-19 | 2014-12-18 11:33 | -1 | 2014-05-22 14:12 | Civil - Drainage | 15000 |  | Incorrect Installation | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | During the CCTV survey, it was identified that a 3 m (aprox) section of the drainage has a backfall with standing water in the pipe (aprox 5-10%). This is located in the NE corner of the southern box from the gully to the main pipe drainge run.
| 01CV - Civils | Cxxx-NCR-001218 | NCR | TCR fresh steel fibre content below KT20 requirements - Aug 2013 |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2014-02-24 | 2014-02-25 14:43 | 1 | 2014-02-10 16:53 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Average steel fibre content from washout tests undertaken in August 2013 is 34.1kg/m3 this is below the KT20 requirement of 35kg/m3.
| 01CV - Civils | Cxxx-NCR-001219 | NCR | TCR SCL Stitch Drilling AP2W |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-02-24 | 2014-02-18 17:08 | -6 | 2014-02-10 18:24 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | When undertaking the tie-in between PTW and AP2W, the invert on the AP2W headwall was stitch drilled along the incorrect line which was not discovered until after breaking had commenced. Lining broken out to correct profile under shift engineers supervision with small excavator mounted breaker and cleaned by hand breaking. The joint was inspected and there was no indication of damage to the permanent lining
| 01CV - Civils | Cxxx-NCR-001220 | NCR | TCR SCL AP8 primary lining |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-02-24 | 2014-02-18 17:13 | -6 | 2014-02-10 18:54 | Tunnelling - Linings - Sprayed Concrete | 2000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | When commencing advance 17 excavation at the change of shift, it was discovered that the kwikastrip had not been fully sprayed in on invert 16 in the strut location on the left hand side.
| 01CV - Civils | Cxxx-NCR-001221 | NCR | TCR SCL AP8 Invert Chainage |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-02-24 | 2014-02-18 17:18 | -6 | 2014-02-10 18:42 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Due to the 1m step between the heading and invert, the shift engineer left the invert chainage shorter than appeared on the RESS to ensure a suitable length of primary lining was bearing on the clay bench below. On the following advance, to ensure that no more than 2m invert was dug, the chainage was once again left short. By advance 11, this meant that an 800mm shortage of the chainage was present which deviated against what was shown in the RESS.
| 01CV - Civils | Cxxx-NCR-001222 | NCR | SMM-Amber Level Trigger Breach Along Davies Street |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-06-03 | 2014-06-03 15:53 | 0 | 2014-03-04 12:58 | Geotechnical Engineering - Settlement | 1500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Two new amber triggers breached in Davies Street (East) on building monitoring between: B07LB346-B07LB347 and B07LB349-350 Action: - continue with PTW excavation and grout over when area is out of exclusion zone The breach has been communicated to the BOS.CTC.internal group as per management plan. (see attached email). And NGG has been notified.
| 01CV - Civils | Cxxx-NCR-001223 | NCR | SMM-Amber Level Trigger Breach Along South Molton Lane (East) |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-02-25 | 2014-02-18 17:21 | -7 | 2014-02-11 10:15 | Geotechnical Engineering - Settlement | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Two Amber Triggers on slopes have been breached in South Molton Lane (East) between B07LB318-B07LB319 / B07LB315-B07LB316. Actions: -Emergency CTC Meeting -Points have been resurveyed -Increase grout volume over the central line of the tunnel -Target grouting over the area -Proposal of reduction the Exclusion Zone -NGG and __ have been notified (see attached email)
| 01CV - Civils | Cxxx-NCR-001224 | NCR | TCR 1-3 day cores - Oct 2013 |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2014-03-14 | 2014-02-25 14:57 | -17 | 2014-02-11 12:35 | Tunnelling - Linings - Sprayed Concrete | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Sample 278 from CH1 Thickening A set of 6 cores to be tested between 1-3 days were tested at 4 days.
| 01CV - Civils | Cxxx-NCR-001225 | NCR | Fresh fibre washout tests do not meet specification - TCR - Nov 2013 |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2014-02-25 | 2014-02-25 14:51 | 0 | 2014-02-11 14:20 | Tunnelling - Linings - Sprayed Concrete | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Fresh fibre washout tests done on sample 306 produced an average of 31.3 kg/m3. This is below the required 35kg/m3
| 01CV - Civils | Cxxx-NCR-001227 | NCR | Fresh fibre washout tests - TCR - Sept 2013 |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2014-02-25 | 2014-02-25 14:54 | 0 | 2014-02-11 16:59 | Tunnelling - Linings - Sprayed Concrete | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Fibre washout tests undertaken for samples 223 and 237 do not meet KT20 as the average fibre content of three 10 litre samples is below 35kg/m3. In addition two individual samples are below 28kg/m3. See attached results
| 01CV - Civils | Cxxx-NCR-001228 | NCR | BOS - Insufficient readings taken of in tunnel monitoring points |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2014-03-05 | 2014-02-27 13:27 | -6 | 2014-02-13 14:14 | Tunnelling - Linings - Sprayed Concrete | 2500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | In tunnel monitoring data presented in SRG on 6/2/2014 at 16:00 had points missing on the following RMS: 36, 46, 53, 58, 71, 130, 137. See attached SRG minutes from 6/2/2014.
| 01CV - Civils | Cxxx-NCR-001229 | NCR | BOS - Advance Rate |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-03-03 | 2014-03-03 10:21 | 0 | 2014-02-17 17:01 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Exceeding Advance Rate - more than 4m/24hrs as stated in the RESS - 065 PTW Advance 233A - 239A - 6no advances/4m - see attached sketch PTW Advance 233A started @ 1535 on 13/02/2014 - CH158.75 PTW Advance 239A started @ 1320 on 14/02/2014 - CH162.75 - as detailed above advance 239A started 2hrs 15min before the advance 233A the previous day But at BOS ETH the EAS result have always been good - see attached results page from SRG minutes 14/02/14 Ground was considered to be stable No significant tunnel settlement effects Early Age Strength Test as per SRG minutes 14/02/2014
| 01CV - Civils | Cxxx-NCR-001230 | NCR | Compressive results taken outside the acceptable window os 1-3 days |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-03-04 | 2014-02-21 16:10 | -11 | 2014-02-18 14:39 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Compressive cores tested @ 7 days for PTW advance 7 ( Thus outside acceptable window of 1-3 days)
| 01CV - Civils | Cxxx-NCR-001231 | NCR | Rebound Testing |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-03-06 | 2014-03-05 17:35 | -1 | 2014-02-20 16:14 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | No Rebound test carried out in January ( last rebound test was carried out in November 25/11/2013)
| 01CV - Civils | Cxxx-NCR-001232 | NCR | Sprayed panels for monthly |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-03-06 | 2014-02-26 13:29 | -8 | 2014-02-20 17:31 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper storage of material | Completed |  | Monthly panels for February were left unprotected/uncovered for 19hours, before being picked up by lab.
| 01CV - Civils | Cxxx-NCR-001234 | NCR | Insufficient number of cores tested per set |  | Contr | BFK |  |  | 2014-03-14 | 2014-03-03 10:23 | -11 | 2014-02-21 14:18 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Each of the following sets consisted of 5 cores: Sample 280 CH1 Thickening 28 day cores, Sample 267, AP4E Adv35.
| 01CV - Civils | Cxxx-NCR-001235 | NCR | Cores testing outside of ITP Requirements |  | Contr | BFK |  |  | 2014-03-14 | 2014-03-03 10:25 | -11 | 2014-02-21 14:15 | Tunnelling - Linings - Sprayed Concrete | 1115 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Sample 214, CH3/AP7A Thickening, No one day cores tested Sample 214A, CH3/AP4 Thickening, 1-3 days cores tested late Sample 215, CH3/AP4 Thickening, 1-3 days cores tested late Sample 217, CH3/AP2 Thickening, 28 day cores tested early at 4/5 days Sample 226A, AP2E Adv.12, 1-3 days cores tested late Sample 230, AP4W Adv.6, 28 days cores tested late Sample 232, AP4W Adv.12, no 1-3 days cores tested
| 01CV - Civils | Cxxx-NCR-001236 | NCR | January 2014 Flexural strength beams |  | Contr | BFK |  |  | 2014-04-30 | 2014-04-29 15:09 | -1 | 2014-02-21 17:25 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Out of the 3 Beams tested in the month of January 2014 at 28 days. Two passed on both D1 and D3 One failed on D3 The average of the D1 value was 2.7 which was well above the 1.8 requirement. The average of the D3 value was 1.56 which is still above the 1.4 requirement.
| 01CV - Civils | Cxxx-NCR-001239 | NCR | 28 Day Cores Tested Late |  | Contr | BFK |  |  | 2014-03-19 | 2014-03-03 10:27 | -16 | 2014-02-26 11:34 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | Sample 218, CH3 / AP2 Thickening. 28 day cores tested late at 62 days
| 01CV - Civils | Cxxx-NCR-001240 | NCR | a set of 1 day cores taken outside acceptable window |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-03-12 | 2014-02-28 10:06 | -12 | 2014-02-26 15:48 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | PTW thickening in December 2013, a set of 1 day cores was crushed at 6 days.
| 01CV - Civils | Cxxx-NCR-001241 | NCR | TCR SCL Installation and Base Readings of Monitoring Points |  | Contr | BFK |  |  | 2014-03-13 | 2014-03-05 17:38 | -8 | 2014-02-27 19:48 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | At the following chainages, the installation/base readings of monitoring points was excessively delayed in relation to the completion of the excavation and primary lining works: 1) ch55 installed 8/1/14. Excavation completed at 07:10, base readings not taken until 20:30 2) ch81 installed 16/1/14. Excavation completed 21:40, monitoring installed 17/1 at 07:15.
| 01CV - Civils | Cxxx-NCR-001242 | NCR | Fibre Washout Tests Jan + Feb 2014 |  | Contr | BFK |  |  | 2014-05-02 | 2014-03-26 09:16 | -37 | 2014-03-21 12:00 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Cxxx--C4-ITP-CRT00_ST005-50013 states Fresh fibre washout (average of 3 samples) to be done once per month. A number of tests were below specification. Sample 336 Average of 31.9 less than 35 Sample 345 Average of 30.4 less than 35 Sample 374 Average of 32.3 less than 35 Sample 379 Average of 33.2 less than 35 Sample 383 Two indivual results less than 80% and average (27.3) below 35 Sample 393A Average of 31.3 less than 35 Sample 426 average of 33.6 less than 35
| 01CV - Civils | Cxxx-NCR-001243 | NCR | 1 core from Advance 7 of PTW in November not meeting 90 day requirements |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-03-17 | 2014-03-10 16:15 | -7 | 2014-03-03 17:36 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | From a set of six cores taken from advance 7 of PTW 1 core does not meet requirements of 90 days.
| 01CV - Civils | Cxxx-NCR-001244 | NCR | B32 bar removed from AP8 invert during break-out of AP7b tie-in |  | Contr | BFK |  |  | 2014-03-25 | 2014-03-07 16:43 | -18 | 2014-03-04 09:45 | Tunnelling - Tunnelling General | 1500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | ~1m section of B32 bar removed from AP8 invert during break out of Adv 4 of AP7b tie-in.
| 01CV - Civils | Cxxx-NCR-001245 | NCR | TCR SCL AP8-AP7b tie-in |  | Contr | BFK |  |  | 2014-03-18 | 2014-03-26 09:04 | 8 | 2014-03-04 10:37 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Verbal communication problem | Completed |  | Breaking commenced on the AP7b headwall before the primary lining had been sprayed on heading 5 (see attached RESS). It was unclear whether the works could occur in this sequence and caused a health and safety concern (RIVO to be raised).
| 01CV - Civils | Cxxx-NCR-001246 | NCR | TCR SCL CH1 monitoring data February 2014 |  | Contr | BFK |  |  | 2014-03-18 | 2014-03-26 09:05 | 8 | 2014-03-04 19:27 | Tunnelling - Linings - Sprayed Concrete | 2500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | The monthly monitoring data in CH1 at RMS 04 - RMS 12, RMS 23 - RMS 75 was presented 1 week late.
| 01CV - Civils | Cxxx-NCR-001247 | NCR | SMM-Amber Level Trigger Breach Along Davies Mews between B07LB067-B07LB068 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-06-12 | 2014-06-03 15:54 | -9 | 2014-04-03 18:02 | Geotechnical Engineering - Compensation Grouting | 1500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | New slope trigger on Building monitoring reported along Davies Street 50 Davies street. Slope has exceeded the 1/1000 specification.
| 01CV - Civils | Cxxx-NCR-001248 | NCR | SMM-Amber Level Trigger Breach Along Davies Street Between B07LP279-B07LP282 and B07LP278-127 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-06-04 | 2014-06-03 15:55 | -1 | 2014-03-04 18:37 | Geotechnical Engineering - Settlement | 1500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | All, Two new amber triggers breached in Davies Street (East): between: B07LP279-B07LP282 and B07LP278-127 (Picture below). Both have been verified by the resurvey. ACTION: No further action required this area is within the current tunnel exclusion zone – it is expected that the rear injections will improve the slopes when the area comes out of the exclusion zone. NGG have been notified.
| 01CV - Civils | Cxxx-NCR-001249 | NCR | Late baseline readings/ installation for RMS in AP7b/AP8 final tie-in at Adv 3 |  | Contr | BFK |  |  | 2014-03-27 | 2014-03-07 16:45 | -20 | 2014-03-06 11:50 | Tunnelling - Tunnelling General | 1500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | RMS were due to be installed in the AP7b/ AP8 final-tie in ADV 3 as soon as practicable in the excavation cycle and application of ground support. This did not happen, but were instead installed about 2days later.
| 01CV - Civils | Cxxx-NCR-001251 | NCR | SMM-Amber Level triggers breach along Davies Street between B07LB350-351/B07LP277-281/B07LP127-286 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-06-08 | 2014-06-03 15:56 | -5 | 2014-03-06 14:13 | Geotechnical Engineering - Settlement | 1500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | All, New Amber trigger breach in Davies Street (East) __ between: B07LB350-351 New Amber trigger breach in Davies Street (East) PLP between: B07LP277-281 New Amber trigger breach in Davies Street (East) PLP between: B07LP127-286 Actions: • Re-survey of the area was carried out and the data checked. The Amber triggers have been verified. • A visual inspection of the area of the triggers breach has been undertaken today. Nothing unusual to report. • No further action required this area is within the current tunnel exclusion zone – it is expected that the rear injections will improve the slopes when the area comes out of the exclusion zone. • For more monitoring details please refer to today’s SRG Minutes. • Location (current SCL Advance 354a (Invert). NGG have been notified.
| 01CV - Civils | Cxxx-NCR-001252 | NCR | SMM-Amber Level trigger breach along Davies Street (East) PLP between: B07LP283-288 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-06-08 | 2014-06-03 15:58 | -5 | 2014-03-07 10:37 | Geotechnical Engineering - Settlement | 1500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | All, New Amber trigger breach in Davies Street (East) PLP between: B07LP283-288 Actions: • Re-survey of the area was carried out and the data checked. The Amber trigger has been verified. • A visual inspection of the area of the triggers breach has been undertaken. Nothing unusual to report. • For more monitoring details please refer to today’s SRG Minutes. • Location (current SCL Advance 360a (Invert). NGG have been informed.
| 01CV - Civils | Cxxx-NCR-001253 | NCR | Incident Management of Property Damage |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2014-05-30 | 2014-05-30 14:56 | 0 | 2014-03-07 14:48 | Surveying - Instrumentation and Monitoring | 1500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Not Defined | Completed |  | The contractor is not complying with Incident Management requirements outlined in the works information relating to “damage to or loss of, property” with respect to damage reported as a result of tunnelling works.
| 01CV - Civils | Cxxx-NCR-001255 | NCR | Non-Conformance of 88-89 Dean St + 12-16 Southampton Row Tiltmeters |  | Contr | BFK |  |  | 2014-03-25 | 2014-03-27 13:04 | 2 | 2014-03-11 11:14 | Surveying - Instrumentation and Monitoring | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following a recent review of the installed Tiltmeters at the above locations, it was noted that the measuring range for the installed instruments is out of spec. Technical Requirements KX10.3219 c) Tiltmeter (Remotely read) i) The tiltmeter shall have the following requirements: • measuring range: ±10 degrees or greater; • operating temperature: 0°C to +50°C; • accuracy: ±0.05% full scale ; • resolution: 0.01% full scale; • repeatability: ±0.01% full scale. Existing Condition/ Non conformance This instruments installed as part of this PMI are: • measuring range: ±5 degrees or greater;
| 01CV - Civils | Cxxx-NCR-001256 | NCR | Failure of 2 out of 6 beams for February Flexural Strength. |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-07-30 | 2014-07-10 16:10 | -20 | 2014-03-20 12:58 | Tunnelling - Linings - Sprayed Concrete | 3500 |  | Material | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Failure of 2 out of 6 beams for Flexural Strength Test carried out in February.
| 01CV - Civils | Cxxx-NCR-001257 | NCR | Moistures at TCR Batching Plant April 2013 |  | Contr | BFK |  |  | 2014-04-04 | 2014-03-21 17:04 | -14 | 2014-03-21 12:35 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Only 3 moisture comparisons taken during the month, all in the first week.
| 01CV - Civils | Cxxx-NCR-001258 | NCR | SMM- Amber Level trigger breach in St Anselm's Place |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-04-14 | 2014-04-25 11:45 | 11 | 2014-03-25 13:32 | Geotechnical Engineering - Settlement | 1500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | New Amber triggers breached in: • Davies Street (East) __ between: B07LB362-A07LB011 • St. Anselm’s Place PLP between: A07LP001-B07LP131 • St. Anselm’s Place PLP between: A07LP004- A07LP002 • St. Anselm’s Place PLP between: A07LP002- B07LP132 • St. Anselm’s Place PLP between: A07LP003- A07LP001 • St. Anselm’s Place PLP between: A07LP005- A07LP003 Actions: • Re-survey of the area was carried out and the data checked. The Amber triggers have been verified. • A visual inspection of the area of the triggers breach has been undertaken. Nothing unusual to report. • For more monitoring details please refer to SRG Minutes (days 22-23-24/03/2014)
| 01CV - Civils | Cxxx-NCR-001259 | NCR | TCR SCL Incomplete Geotechnical Logs |  | Contr | BFK |  |  | 2014-04-09 | 2014-03-28 09:18 | -12 | 2014-03-26 16:17 | Geotechnical Engineering - Geotechnical Monitoring | 1500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Verbal communication problem | Completed |  | Adv 2 Top Heading Geotechnical Log no shear strength reading was taken due to no suitable material to test Adv 3 Top Heading Geotechnical Log, no photograph taken due to communication error
| 01CV - Civils | Cxxx-NCR-001260 | NCR | Fire Testing |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-07-11 | 2014-07-11 15:08 | 0 | 2014-03-28 09:03 | Tunnelling - Linings - Sprayed Concrete | 30000 |  | Supervision/Management | Rework | 2 (6-60k) | Complete | Material/Preservation Problems - Other | Completed |  | Method Statment was not followed when preparing/spraying test panels for fire testing. Main things not followed: 1) Segregation of the panels whilst spraying. Rebound contaminated the neighbouring panels 2) Not covered once the secondary was sprayed and not jet washed sufficiently before the regulating layer spray. 3) There was no sufficient depth/profile control measures in place. A few nails hammered in at various intervals because impossible to see once spraying commenced. 4) The depth control boards were fabricated but were not used. 5) The panels were sprayed on their backs, whereas this time we will sprayed them standing up (at a slight angle to the vertical)
| 01CV - Civils | Cxxx-NCR-001261 | NCR | February Monthly Testing - Beams |  | Contr | BFK |  |  | 2014-06-30 | 2014-07-07 11:42 | 7 | 2014-04-03 11:03 | Tunnelling - Linings - Sprayed Concrete | 5500 |  | Workmanship | Use As-Is | 3 (3-6k) | Complete | Verification Problems - Not Defined | Completed |  | The set of monthly beam for February failed. A transducer fell out during the first test which makes that test void. One of the beams failed abrubtly meaning the test was not completed to give a result. The third beam passed with results exceeding the 90 day specification. Therefore the average of the three was below specification.
| 01CV - Civils | Cxxx-NCR-001262 | NCR | Incomplete F50 Forms |  | Contr | BFK |  |  | 2014-05-29 | 2014-05-08 15:41 | -21 | 2014-04-02 12:20 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Supervision/Management | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | A number of the F50 forms for the PTW pt 2 section have not been fully completed This includes advances: 12 - Incomplete ticket number recorded for stand by load prior to excavation (last three digits were recorded, as below) 13 - Incomplete ticket number pre-excavation and nozzleman signature for initial lining 14 - Primary lining ticket information incomplete 19 - Pre-spray primary lining names recorded but no signature 20 - Post primary lining completion signature missing 21 - Initial lining signature missing
| 01CV - Civils | Cxxx-NCR-001263 | NCR | BOS VD1B Soft eye construction - uncontrolled stop of construction/not following the RESS or approved temporary works design |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-04-21 | 2014-04-09 09:45 | -12 | 2014-04-07 15:41 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | During construction of soft eye VD1B full stitch drilling of the d-wall has taken place but then works have been stopped. From SRG minutes, it appears that works stopped on 17 March but the next prescribed stages in the construction have NOT taken place. have introduced a non-approved stoppage of the works at that stage, part-way through the excavation sequence. The approved sequence is shown on the Donaldsons drawings and, in essence, require stitch drilling of the d-wall, removal of the blocks, excavation (doming) of the face and then application of the shotcrete for the soft eye. We then have up to 90 days to commence the break-out of the tunnel VD1B. Upon inspection there were no signs of instability of the d-wall blocks, and no indication that these blocks had moved since the core-drilling had originally been done. As a precaution, 4 monitoring points were established last night on the face of the partially-removed d-wall elements, baseline readings were completed 20:30 last night (2.4.14). First readings today 04.00 (3.4.14) don't show any movement.
| 01CV - Civils | Cxxx-NCR-001264 | NCR | Batching Plant Moistures May 2013 |  | Contr | BFK |  |  | 2014-04-17 | 2014-04-09 09:48 | -8 | 2014-04-03 11:17 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Violation of requirement or procedure | Completed |  | Silo 2 moisture comparisons with batching plant were greater than 2% difference.
| 01CV - Civils | Cxxx-NCR-001265 | NCR | Sprayed concrete on piles at Bond Street NW Shaft |  | Crossrail | PDP | BOS - Bond Street Station (West) |  | 2014-05-30 | 2014-05-16 15:39 | -14 | 2014-04-03 15:20 | Civil - Tunnelling | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Cxxx-PMI-00692 required to install temporary works necessary in order to encapsulate loose clay between the piles in the NW Shaft. Irrespective of receiving no formal Temporary Works design, we note that Cxxx-CQT-00691 identified that 100mm SCL would be sprayed between the piles only. The asbuilt not only didn’t pick this up it has now been identified that the front face of the piles were sprayed, not only this wasn’t envisaged from the PMI or the CQT wording the temporary works installed on the face of the piles did not appear to be part of your temporary works solution. If this was considered unavoidable then these temporary works should have been removed prior to handover or identified in the as built. The Current Principle Contractor Cxxx will now have to break out the shotcrete that has potential to damage the couplers.
| 01CV - Civils | Cxxx-NCR-001266 | NCR | Out-of-spec concrete not promptly replaced |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-04-18 | 2014-04-07 14:12 | -11 | 2014-04-04 15:42 | Civil - Tunnelling | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | When the result of the hourly flow test dropped below the specified 480mm, a fresh batch of concrete was not ordered.
| 01CV - Civils | Cxxx-NCR-001267 | NCR | No Core results (dry fibre content) taken from SilverTown flexual beams in January |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-05-06 | 2014-04-28 14:15 | -8 | 2014-04-06 13:32 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | No core results (dry fibre content) taken from the flexual beams from Silvertown for the month of January.
| 01CV - Civils | Cxxx-NCR-001269 | NCR | Concrete testing equipment availability |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-04-21 | 2014-04-07 14:41 | -14 | 2014-04-07 08:22 | Civil - Tunnelling | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | No flow test table available on site.
| 01CV - Civils | Cxxx-NCR-001270 | NCR | TCR AP4W over excavation |  | Contr | BFK |  |  | 2014-04-21 | 2014-04-22 13:42 | 1 | 2014-04-07 11:49 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During Excavation of advance 4 invert, the muncher was used to remove concrete in order to reduce noise impacts to any stakeholders. After excavating removing approximately up to the first 500mm in height on concrete, it became clear that using the muncher was leading to an over excavation of the invert due to the side of the muncher, leaving very minimal bench between the heading and invert (see attached photo) Works stopped and the face sealed in order for a revised RESS to be agreed to.
| 01CV - Civils | Cxxx-NCR-001271 | NCR | BOS - Band layers in cores |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-10-10 | 2014-10-01 10:55 | -9 | 2014-04-08 20:36 | Tunnelling - Linings - Sprayed Concrete | 4500 |  | Workmanship | Use As-Is | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | Band layers are present in some cores taken from the primary lining and panels sprayed at Bond Street.
| 01CV - Civils | Cxxx-NCR-001272 | NCR | BOS - PTW Protection of monitoring points |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-04-24 | 2014-04-29 16:20 | 5 | 2014-04-08 20:51 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Damage to monitoring points in PTW. Monitoring points should be sufficiently protected and replaced as soon as possible if they are accidentally damaged. PTW chainage 252 point 3 above AP2A and chainage 258 point 7. AP2A chainage 8 point 6 and 7.
| 01CV - Civils | Cxxx-NCR-001274 | NCR | LU Trackshoe Monitoring (VD1) |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-04-24 | 2014-04-23 17:19 | -1 | 2014-04-10 10:58 | Geotechnical Engineering - Grouting Instrumentation | 500 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate resources | Completed |  | As it is specified in the MPCoGM: “In the Jubilee line tunnels the primary, automated monitoring is reviewed on a daily with the secondary, manual monitoring undertaken weekly.” A LU trackshoe survey was scheduled for 05-06/04/2014. No data presented due to unavailability of the surveyors.
| 01CV - Civils | Cxxx-NCR-001277 | NCR | SMM_TCR_PTW East missing manual readings |  | Contr | BFK |  |  | 2014-05-23 | 2014-05-19 15:28 | -4 | 2014-04-11 08:52 | Surveying - Instrumentation and Monitoring | 500 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | PTW (East) Adv 317-319 has been started on 9/4/14. Due to miscommunication it was not possible to take a set of manual readings (PLPs and __s) on the 9/4/14. Daily manual monitoring started on 10/4/14. Automated instrumentation (HLC) were correctly working and has been used to monitor the area.
| 01CV - Civils | Cxxx-NCR-001278 | NCR | Missing Form 50 for AP2W (Initial-drive) Adv 12 |  | Contr | BFK |  |  | 2014-05-19 | 2014-04-23 18:07 | -26 | 2014-04-14 14:24 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Missing form 50 for Adv 12 from the AP2W initial drive.
| 01CV - Civils | Cxxx-NCR-001279 | NCR | Cement standard test not done for week 6 in February 2013 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-04-29 | 2014-04-23 16:53 | -6 | 2014-04-15 13:22 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Cement standard test not done for week 6 in February 2013. SCL production ITP states that standard strength test should be done twice a week, however no 28 day test was carried out for week 6 in February 2013 by Cement.
| 01CV - Civils | Cxxx-NCR-001280 | NCR | TCO Form 50 missing information |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-05-15 | 2014-04-22 13:39 | -23 | 2014-04-17 09:53 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Missing information on Form 50-s Please see attached document discribing where and what is missing.
| 01CV - Civils | Cxxx-NCR-001281 | NCR | Non Conformance in carrying out all the requirements of Early Age Strength Test and the filling of Form BFK057 For TCO Tunnel |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-05-08 | 2014-04-22 14:27 | -16 | 2014-04-17 10:42 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Not Defined | Completed |  | Non Conformance in carrying out all the requirements of Early Age Strength Test and the filling of Form 057 For TCO Tunnel
| 01CV - Civils | Cxxx-NCR-001282 | NCR | 28 Day Cores |  | Contr | BFK |  |  | 2014-05-17 | 2014-04-29 16:31 | -18 | 2014-04-17 16:35 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The following sets of cores each had one set of cores below specification: Sample 394, AP8 Adv 22, result of 30.1 Sample 417, PTW Adv 254, result of 22.6 Sample 419, PTW Adv 262, result of 33.2 Sample 424, PTW Adv 271, result of 22.7 Sample 433, PTW Adv 291, result of 28.6 These results have had a negative effect on the average meaning its lower when compared to the 28 day SD target.
| 01CV - Civils | Cxxx-NCR-001283 | NCR | 28 day cores Tested late |  | Contr | BFK |  |  | 2014-05-17 | 2014-04-25 11:42 | -22 | 2014-04-17 16:55 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Verbal communication problem | Completed |  | Sample 400, AP8 Adv 28, 28 day cores tested at 34 days
| 01CV - Civils | Cxxx-NCR-001284 | NCR | 1 Day Cores |  | Contr | BFK |  |  | 2014-05-02 | 2014-04-23 18:11 | -9 | 2014-04-18 14:05 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Sample 349, PTW Adv 108 Only 5 cores tested at 1 day
| 01CV - Civils | Cxxx-NCR-001285 | NCR | Early Age Testing |  | Contr | BFK |  |  | 2014-05-21 | 2014-04-23 18:13 | -28 | 2014-04-21 10:24 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Gaps between early age testing greater than 6 advances: PTW Adv. 312-320, gap of 8 advances, test missed 318, returned to original programme on 330, gap of 4 advances between 326-330 PTW Adv. 330-339, gap of 9 advances, test missed at 336 so additional test on 339 PTW .2 Adv 48-55, gap of 7 advances, test missed at 54 but additional test on 55, some results for this advance were below modified J2 curve.
| 01CV - Civils | Cxxx-NCR-001286 | NCR | Inadequately Weather Proofed Steel Fibre Dosing System – Vic Deep Batching Plant |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2014-06-04 | 2014-06-04 16:55 | 0 | 2014-04-23 08:39 | Civil - Tunnelling | 3000 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | There is an open access at the top of the conveyor system (Vic Deep) dosing the steel fibres into the concrete truck, which has the potential to allow rain water to run down the conveyor and over the steel fibres when batching in periods of bad weather. A header or covering should be put over this access to ensure the fibres are free from any environmental conditions such as rain. This will remove any potential issues with steel fibres rusting and/or clumping (see Surveillance Report Cxxx-XRL-O4-RGN-CR001-50020 for associated figure). Quality System Ready Mix Concrete (QSRMC) Quality and Product Conformity Regulations part 7.5.1, 3.9 states “All plant, equipment and delivery vehicles shall be subject to a planned and preventive maintenance system and shall be maintained in a clean and efficient working condition so that the quality and quantity of concrete is not adversely affected”.
| 01CV - Civils | Cxxx-NCR-001287 | NCR | In Bond Street June 2013 Tunnel CH3 for advances 2,6 and 23 no 1 day cores was taken , also 90 day cores during that same month and for CH3 in a few instances only 3 to 5 cores were taken |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-05-29 | 2014-05-20 18:22 | -9 | 2014-04-24 12:56 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the month of June 2013 for CH3 tunnel no 1 day cores were taken @ advances 2,6 and 23 and in a few instances @ other advances 4 to 5 cores only was taken for 90 days.
| 01CV - Civils | Cxxx-NCR-001288 | NCR | In July 2013 Tunnel CH3 for advance 63, no 1 day cores was taken, also during this same month in a few instances we received compressive results for 3 to 5 cores for certain advances rather than our required 6. |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-05-31 | 2014-05-20 18:31 | -11 | 2014-04-24 13:56 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | During month of July 2013 for CH3, no 1 day cores was taken for advance 63, also in a few instances during that month we received compressive results for 3 to 5 cores rather than the required 6.
| 01CV - Civils | Cxxx-NCR-001289 | NCR | Missing Form 50 for PTW (East) Advs 314 & 315 |  | Contr | BFK |  |  | 2014-05-19 | 2014-05-19 15:26 | 0 | 2014-04-24 14:12 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | F50 for PTW Advs 314 & 315 have been misplaced
| 01CV - Civils | Cxxx-NCR-001290 | NCR | Inadequate spraying of Waterproofing Membrane in AP3E |  | Contr | BFK |  |  | 2014-07-04 | 2014-07-02 13:50 | -2 | 2014-04-24 15:56 | Tunnelling - Tunnelling General | 6000 |  | Workmanship | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following a joint inspection of the AP3E cross passage, post waterproofing trials, the thickness and the bonding of the waterproofing substrate to the regulating layer did not meet the required specification. Numerous pit holes, along with insufficient thickness, was found in the connection between the crown/side and the invert. When spraying the invert, excess water accumulated in parts stopping the waterproofing to cure fully. A thin film occurred on top, trapping the water underneath, and preventing the substrate to bond fully with the regulating layer.
| 01CV - Civils | Cxxx-NCR-001291 | NCR | AP3E waterproofing contamination |  | Contr | BFK |  |  | 2014-06-09 | 2014-06-12 11:10 | 3 | 2014-05-19 08:48 | Tunnelling - Tunnelling General | 1500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Shallow puddle of oil-substance was found sitting on the hardened waterproofing in AP3E. No evidence of damage to waterproofing.
| 01CV - Civils | Cxxx-NCR-001292 | NCR | TCR CL1 Excavation and Primary Lining Handover Package Overdue |  | Contr | BFK |  |  | 2014-05-23 | 2014-05-23 15:56 | 0 | 2014-04-25 10:07 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate resources | Completed |  | CL1 Excavation and Primary Lining sub-construction listing, ITP records and redline drawings were due for submission in August 2013 and is overdue.
| 01CV - Civils | Cxxx-NCR-001293 | NCR | Residual strength for D3 S1.4 @ 28 days for 1 beam out of the 3 tested does not conform with the criteria of EN 14487,clause7.5.2.4 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-08-07 | 2014-07-11 15:29 | -27 | 2014-04-25 17:19 | Tunnelling - Linings - Sprayed Concrete | 2500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Residual strength for D3 S1.4 @ 28 days does not comply with the criteria of EN 14487-1, clause 7.5.2.4 for 1 beam out of the 3 tested for the month of July 2013 (CH3, Advance 87).
| 01CV - Civils | Cxxx-NCR-001294 | NCR | Form 50 for AP7b Adv 9C partially complete |  | Contr | BFK |  |  | 2014-05-29 | 2014-05-14 10:55 | -15 | 2014-05-08 19:14 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Form 50 for AP7b Adv 9C missing initial lining section.
| 01CV - Civils | Cxxx-NCR-001295 | NCR | Fault within Diaphragm Wall Panel P16 |  | Contr | BFK |  |  | 2014-05-12 | 2014-05-16 15:35 | 4 | 2014-04-28 19:19 | Structural Engineering - Diaphragm Walls | 500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | have identified a non-conformance in construction works carried out by a previous contractor. On excavation of the North Box we have uncovered a fault within diaphragm wall panel P16, in the form of an arched crack above the raft slab keying-in recess (see attached photograph). have been unable to progress with the raft slab steel fixing works today whilst awaiting confirmation from CRL that reworking of this panel is not necessary.
| 01CV - Civils | Cxxx-NCR-001296 | NCR | Omitted Coupled Starters/Void Former in Panels P22 and P57 |  | Contr | BFK |  |  | 2014-05-12 | 2014-05-09 15:08 | -3 | 2014-04-28 19:12 | Structural Engineering - Diaphragm Walls | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | has identified a non-conformance in construction works carried out by a previous contractor. Following excavation of the North Box we are required to remove void formers to expose the coupled starters within the diaphragm wall for connection to the raft slab. Panels P22 and P57 do not contain the void formers shown on drawings C421-__M-S-RGN-N105_WS089-50051 & 50065 respectively for the Level -2 raft. are therefore unable to expose the couplers and install the raft slab starter bars at these locations. Given the omission of the void formers, it is not certain that the coupled starters were installed at these locations by the previous contractor. We do not propose to carry out destructive investigation works to the diaphragm wall to determine this.
| 01CV - Civils | Cxxx-NCR-001297 | NCR | Dimensions of Recesses within North Box Diaphragm Wall Panels |  | Contr | BFK |  |  | 2014-05-13 | 2014-05-09 15:11 | -4 | 2014-04-29 11:16 | Structural Engineering - Diaphragm Walls | 2500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On removing the void formers in the North Box diaphragm walls to expose the Level -2 raft slab couplers, have encountered non-conformances in construction works by a previous contractor. Drawing Cxxx-OVE-S-DDD-N105_Z-24010 states the depth of the recess to be 200mm, whereas depths measured on site vary between 120-190mm. Refer to attached survey. On 28/04/2014 has been unable to progress with steel fixing whilst awaiting confirmation from CRL & Cxxx that no remedial works are required to these recesses. We have also observed that width of the recesses is in some panels less than those stated on the reinforcement detail drawings for the diaphragm wall cages; drawings C421-__M-S-RGN-N105_WS089-50021, 50024, 50027, 50057. P7: 1720mm (should be 2000mm) P15: 1100mm (should be 1150mm) P19: 2460mm (should be 2525mm) P21: 2840mm (should be 2925mm)
| 01CV - Civils | Cxxx-NCR-001299 | NCR | At BOS PTW Tunnel (CP05), early age strength development was not carried out every third advance. |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-05-29 | 2014-05-09 13:47 | -20 | 2014-04-29 16:19 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | For PTW (CP05) in BOS the frequency of carrying out early age strength development every third or fourth advance was not adhered to. Instead at advance 3 of CP5 the next advance was 10. However from then on the test was carried out @ every third, sometimes fouth advance as required.
| 01CV - Civils | Cxxx-NCR-001300 | NCR | Tight spots in AP7b following a re-survey 8-weeks after construction |  | Contr | BFK |  |  | 2014-05-13 | 2014-05-12 13:37 | -1 | 2014-04-29 17:26 | Tunnelling - Linings - Sprayed Concrete | 2500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following a re-survey of the AP7b primary lining, some profiles (attached) were found to exceed the primary lining design line.
| 01CV - Civils | Cxxx-NCR-001301 | NCR | North Box Level -2 Raft Slab Recesses Out of Vertical Tolerance |  | Contr | BFK |  |  | 2014-05-27 | 2014-05-09 15:14 | -18 | 2014-04-29 18:58 | Structural Engineering - Diaphragm Walls | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | have surveyed the levels of the Level -2 raft slab recesses within the diaphragm walls and have identified a non-conformance in the works of a previous contractor. KP10.3207(e) (Cxxx-OVE-C2-RSP-N105-00002) states a vertical tolerance of the reinforcement of +/- 50mm. have identified panels where the level of the coupled starters exceeds this tolerance. This could affect the fixing of the raft slab reinforcement, in that the B40 starters may clash with the top mat. Panel P9: 70mm high Panel P11: 120mm high Panel P15 (north wall): 60mm high Panel P21: 230mm high Refer to attached sketch.
| 01CV - Civils | Cxxx-NCR-001302 | NCR | Early Age Testing PTW Adv 75 |  | Contr | BFK |  |  | 2014-09-23 | 2014-09-17 16:22 | -6 | 2014-05-01 19:34 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Early age strength results have been below the modified J2 curve: PTW, Adv 75, Below J2 at 30min, and 1hr
| 01CV - Civils | Cxxx-NCR-001303 | NCR | Early Age Testing Adv 78 PTW .2 |  | Contr | BFK |  |  | 2014-09-23 | 2014-09-17 16:24 | -6 | 2014-05-01 19:42 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Early age strength results have been below the modified J2 curve: PTW, Adv 78, Below J2 at 10min, 30min, and 1hr
| 01CV - Civils | Cxxx-NCR-001304 | NCR | There are no cube results available for pass1 and 2 of pre-treatment works in TCR 1, resulted in failing to show grout compressive strengths in line with specification |  | Contr | BFK |  |  | 2014-06-12 | 2014-06-09 15:03 | -3 | 2014-04-30 16:37 | Geotechnical Engineering - Compensation Grouting | 1500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Cube results are important that the pre-treatment grout has some strength property to achieve & sustain the heave (i.e. should not remain fluid!), but should not be excessively strong otherwise during subsequent injections might prove problematic and is therefore grout strength is one key indicator. Considering any subsequent grouting will have rectified any non-conformance with regards to grout compressibility. Since pre-treatment grouting works pass 3 and concurrent grouting carried-out without any problem to date and successfully achieved the heave, are content that the performances of the TaM pipes are as intended. It is therefore considered that the lack of reporting of cube results is unlikely to have had any detrimental effect on the permanent works, and remedial works are not required.
| 01CV - Civils | Cxxx-NCR-001305 | NCR | BOS - Geotechnical face log for Advance 12 of CP5 not done |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2014-05-15 | 2014-05-15 13:37 | 0 | 2014-05-01 08:05 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | No geotechnical face log was undertaken for Advance 12 of CP5.
| 01CV - Civils | Cxxx-NCR-001307 | NCR | BOS - No excavation profile presented for CP5 Adv 13. |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2014-05-15 | 2014-05-15 09:23 | 0 | 2014-05-01 08:17 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | No excavation profile was presented for Adv 13 of CP5
| 01CV - Civils | Cxxx-NCR-001308 | NCR | BOS WTH VD1B 75mm Face Support |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-05-29 | 2014-05-19 17:43 | -10 | 2014-05-01 09:04 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Supervision - Supervisor not familiar with the work | Completed |  | Face support of Advance 1 was not sprayed to the specified 75mm thickness.
| 01CV - Civils | Cxxx-NCR-001309 | NCR | PTE backfilling of invert |  | Contr | BFK |  |  | 2014-05-15 | 2014-05-08 15:24 | -7 | 2014-05-01 17:01 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Tha invert of Adv14 in PTE was backfilled without Eearly Age strength testing in-situ on the profile. The panel was tested after 45 minutes and had reached the 0.5MPa requirement but the egnieer failed to test the profile.
| 01CV - Civils | Cxxx-NCR-001310 | NCR | Early Age Testing PTW .2 Adv 82 |  | Contr | BFK |  |  | 2014-06-06 | 2014-05-08 15:34 | -29 | 2014-05-07 16:13 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Early age strength results have been below the modified J2 curve: PTW .2, Adv 82, Below J2 at 30min, and 1hr
| 01CV - Civils | Cxxx-NCR-001311 | NCR | Senior surveyor not present to calculate profiles for SRG |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-05-18 | 2014-05-20 18:14 | 2 | 2014-05-04 14:14 | Tunnelling - Tunnelling General | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Senior surveyor not present to calculate profiles in a timely manner for SRG
| 01CV - Civils | Cxxx-NCR-001312 | NCR | Protection of monitoring targets |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-05-18 | 2014-05-19 15:24 | 1 | 2014-05-04 14:18 | Surveying - Tunnels/Portal/Shafts surveys | 2500 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Some monitoring targets in CP5 were damaged and were unable to be read
| 01CV - Civils | Cxxx-NCR-001313 | NCR | Missing monitoring point Adv 31 of CP5 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-05-18 | 2014-05-19 15:25 | 1 | 2014-05-04 14:26 | Surveying - Tunnels/Portal/Shafts surveys | 2500 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Monitoring point was missing from Adv 31 of CP5
| 01CV - Civils | Cxxx-NCR-001314 | NCR | Insufficient thickness of shotcrete applied to the face of PTE Adv 33 for a 12hr stand-down |  | Contr | BFK |  |  | 2014-05-27 | 2014-05-08 15:44 | -19 | 2014-05-06 10:50 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | As per KT20.3218: a) If excavation is halted for more than twelve hours, the excavation face shall be protected by the application of additional sprayed concrete to the minimum initial layer of 75mm. Adv33 face was sealed with 75mm shotcrete, however an unplanned stoppage had caused Adv 33 to stop works for approximately 17hrs without applying additional concrete.
| 01CV - Civils | Cxxx-NCR-001316 | NCR | Form 50s are incomplete for CP08 & CP10 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-05-20 | 2014-05-08 15:30 | -12 | 2014-05-06 10:50 | Tunnelling - Linings - Sprayed Concrete | 2500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The following Form 50s are incomplete for CP08 - Jan Adv 1 not signed by nozzleman - Jan Adv 4 not signed by nozzleman - Feb Adv 8 initial lining not signed by nozzleman - July Adv 1 primary no name and signature from nozzleman. Post spray check not signed by engineer. Pre spray information missing. - July Adv 2, pre spray information missing. - July Adv 3, pre spray information missing. - July Adv 4 initial and primary has no named nozzleman or signature. No Engineer named or signature on post spray check. Pre spray information missing - July Adv 5 no engineer name or signature on pre excavation check. No nozzleman signature. Pre spray information missing - July Adv 6 no nozzleman signature on primary lining and pre spray information missing. July Adv 7, shotcrete information incomplete. The following Form 50s are incomplete for CP10: - Adv 1 Feb 14 not signed by nozzleman for primary lining - Adv 4 Feb not signed by either sprayer for initial or primary - Adv 3 Aug 13 No concrete info for pre excavation check - Adv 4 Aug 13 No concrete info for pre excavation check and primary lining not signed off by sprayer. - Adv 5 Aug 13 Initial layer not signed off by sprayer - Adv 7 Aug 13 No concrete info for pre excavation check and initial not signed off by sprayer.
| 01CV - Civils | Cxxx-NCR-001317 | NCR | Exposure of Reinforcement in Piles P2 & P6 |  | Contr | BFK |  |  | 2014-05-13 | 2014-05-16 15:36 | 3 | 2014-05-06 16:59 | Structural Engineering - Reinforcement | 4000 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During breakdown of the bored piles within the TCR WTH North Box, some of the vertical reinforcement bars in 2 No. piles were severed. Pile P2: 4 No. bars damaged (500mm, 470mm, 740mm, 520mm of bar remains intact) Pile P6: 1 No. bar damaged (220mm of bar remains intact)
| 01CV - Civils | Cxxx-NCR-001318 | NCR | PTW CP05 Adv 34 Low Early Age Strength b/w 0.5hr to 4hrs |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-06-05 | 2014-05-20 18:28 | -16 | 2014-05-06 17:47 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Low early age strength PTW Adv 34 b/w 0.5hr to 4hrs BOS
| 01CV - Civils | Cxxx-NCR-001320 | NCR | Adv 11 Ch 3.56 to 5.56 invert low early age strength for 2hrs PTE BOS ETH |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-06-05 | 2014-05-15 09:37 | -21 | 2014-05-06 18:15 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | low early age strength for 2hrs test (below J2 curve)
| 01CV - Civils | Cxxx-NCR-001321 | NCR | 2hrs/4hrs Early age strength test missing PTE Adv 02 Ch1.44 to 2.56 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-06-06 | 2014-06-05 18:21 | -1 | 2014-05-07 10:50 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | 2 hrs and 4 hrs early age strength test missed for PTE Adv 02 BOS ETH.
| 01CV - Civils | Cxxx-NCR-001322 | NCR | Only 5 cores tested at 1-3 days |  | Contr | BFK |  |  | 2014-06-06 | 2014-05-22 11:00 | -15 | 2014-05-07 16:47 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | For the following set of cores only 5 cores were tested between 1-3 days PTW.2 Adv 85 Sample 503 PTE Adv 18 Sample 504 Cores damaged in transit on route to laboratory.
| 01CV - Civils | Cxxx-NCR-001324 | NCR | SMM - Amber Level Trigger Breach: Along NBS (C07LB0084- C07LB0085 ) |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-06-27 | 2014-06-27 16:58 | 0 | 2014-05-09 12:18 | Geotechnical Engineering - Settlement | 1500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | An Amber trigger breach has been reported in front of 74 New Bond street (C07LB0084- C07LB0085). The façade has been inspected and no visible cracks sighted..
| 01CV - Civils | Cxxx-NCR-001325 | NCR | Early Age Testing PTE Adv 45 |  | Contr | BFK |  |  | 2014-09-23 | 2014-09-15 11:04 | -8 | 2014-05-09 14:26 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Early Age Testing PTE Adv 45 failed to acheive modified J2 strength at 4hrs
| 01CV - Civils | Cxxx-NCR-001326 | NCR | 10-20mm overspray of regulating layer in AP7b at chng. 14.04m & 13.55m at 1o'clock |  | Contr | BFK |  |  | 2014-06-03 | 2014-05-14 10:57 | -20 | 2014-05-09 14:24 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | 10-20mm overspray at 1o'clock chaiange 14.04m of AP7b (Profiles attached) 10mm overspray at 1o'clock chainage 13.55m of AP7b (Profiles attached)
| 01CV - Civils | Cxxx-NCR-001327 | NCR | Testing Frequenices - Early Age Testing August 2013 |  | Contr | BFK |  |  | 2014-10-01 | 2014-09-15 11:05 | -16 | 2014-09-10 14:28 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Early age testing frequency of every 6 advances not followed between: Adv 133-140 - gap of 7, gap of 5 between 147-171 to return to intial schedule Adv 158-167 - gap of 9, gap of 3 between 167-170 to return to intial schedule
| 01CV - Civils | Cxxx-NCR-001330 | NCR | Voids in cores CP08 Adv 10 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-06-08 | 2014-05-29 14:53 | -10 | 2014-05-09 17:38 | Tunnelling - Linings - Sprayed Concrete | 3500 |  | Material | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Voids in cores for CP08 invert PTW Adv 10 Ch 8.4
| 01CV - Civils | Cxxx-NCR-001331 | NCR | Cores Crushed at 4 Days PTE Adv 8 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-06-08 | 2014-05-30 15:07 | -9 | 2014-05-09 18:04 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Cores Crushed at 4 days for compressive strength PTE Adv 08
| 01CV - Civils | Cxxx-NCR-001333 | NCR | Cores tested at 4 days |  | Contr | BFK |  |  | 2014-06-06 | 2014-05-22 11:29 | -15 | 2014-05-16 11:39 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Sample 499 PTE Adv 6 and Sample 508 PTE Adv 26. The 1-3 day cores were tested at 4 days.
| 01CV - Civils | Cxxx-NCR-001334 | NCR | 28 day Cores |  | Contr | BFK |  |  | 2014-06-03 | 2014-05-16 17:08 | -18 | 2014-05-13 09:20 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Not Defined | Completed |  | Sample 475 PTW Advance 334 Invert 28 day cores were tested at 26 days
| 01CV - Civils | Cxxx-NCR-001335 | NCR | Out of spec concrete during Adv 7, S4 |  | Contr | BFK |  |  | 2014-06-04 | 2014-06-04 16:56 | 0 | 2014-05-14 08:37 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | During Adv 7 at S4, standby concrete was tested at 20:50 (flow 510mm). The excavation finished at 21:30 and standby concrete was tested again at approx. 21:50 prior to use, however it was found to be out of spec. As it was out of spec the concrete was not fit for use and was not sprayed, instead it was dumped. A fresh load of concrete was delivered onto site, tested at the face by 22:15 and used to seal the open excavation.
| 01CV - Civils | Cxxx-NCR-001337 | NCR | Damage to soffit of lvl -3 in Goslett Yard Box |  | Contr | BFK |  |  | 2014-12-19 | 2015-01-08 17:10 | 20 | 2014-05-15 09:50 | Tunnelling - Tunnelling General | 15000 |  | Damaged | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Other | Completed |  | Damage to the soffit of lvl -3 in Goslett Yard Box around the pit bottom muck bin. Photos of damage attached.
| 01CV - Civils | Cxxx-NCR-001338 | NCR | BOS WTH VD1C Adv 6 mesh installed with in excess of 35mm cover |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-08-14 | 2014-08-04 11:42 | -10 | 2014-05-19 17:33 | Tunnelling - Linings - Sprayed Concrete | 2500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A393 mesh was installed with in excess of 35mm cover to the intrados of the primary lining.
| 01CV - Civils | Cxxx-NCR-001339 | NCR | BOS WTH VD1C Adv |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-08-14 | 2014-08-04 11:43 | -10 | 2014-05-19 17:46 | Tunnelling - Linings - Sprayed Concrete | 3500 |  | Documentation and Records | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Reinforcmeent checksheet has not been completed and countersigned by Cxxx/CRL inspectors for Advances 1 - 5 of VD1C.
| 01CV - Civils | Cxxx-NCR-001340 | NCR | Voids in Base of Lift Pit in Level -2 Raft |  | Contr | BFK |  |  | 2014-08-15 | 2014-08-16 15:07 | 1 | 2014-05-20 12:59 | Structural Engineering - Concrete Member | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Two voids are present in the concrete forming the base of the lift pit. These are approximately 1200x200 and 500x500 in size and 100mm deep. See attached photo showing voids and exposed reinforcement.
| 01CV - Civils | Cxxx-NCR-001341 | NCR | Missing F50 forms for AP4W Adv 5 & 8 |  | Contr | BFK |  |  | 2014-06-30 | 2014-06-27 15:55 | -3 | 2014-05-21 17:25 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Missing F50 forms for AP4W Adv 5 & AP4W Adv 8
| 01CV - Civils | Cxxx-NCR-001342 | NCR | Leak sealing in AP7B done with ITP and MS which was code 2'd for AP2E & W only |  | Contr | BFK |  |  | 2014-07-18 | 2014-07-02 18:15 | -16 | 2014-05-22 09:20 | Tunnelling - Linings - Sprayed Concrete | 5500 |  | Supervision/Management | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | The ITP and method statement used for leak sealing works in AP7B was code 2 and had the note added to them when reviewed that they where to be used for AP3 E & W only.
| 01CV - Civils | Cxxx-NCR-001343 | NCR | TCR Batching Plant Moistures June 2013 |  | Contr | BFK |  |  | 2014-08-02 | 2014-07-15 12:47 | -18 | 2014-07-12 17:49 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Silo 1 moisture comparisons with batching plant, one results of six was greater than 2% difference
| 01CV - Civils | Cxxx-NCR-001345 | NCR | No field grout test records available for Pre-treatment grout injections at BOS4 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-06-19 | 2014-06-16 12:14 | -3 | 2014-05-29 13:02 | Geotechnical Engineering - Compensation Grouting | 1500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | There are no field grout test records available for the following passes as mentioned below in relation to grout volumes injected towards pre-treatment works in BOS 4, resulted in failing to show grout characteristics in line with specification. Pass 1( Sep’12): volume injected 6364 litres Pass 2( Sep’12): volume injected 9220 litres Pass 3(Sep’12): volume injected 9469 litres Pass 4(Sep’12): volume injected 2996 litres Pass 5(Sep’12): volume injected 1472 litres
| 01CV - Civils | Cxxx-NCR-001346 | NCR | Over and under dosing of Microsillica of Shotcrete produce and delivered by Hanson to BFK |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-07-28 | 2014-07-11 15:26 | -17 | 2014-05-29 13:48 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Material | Use As-Is | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | The over and under dosing of microsillica in the shotcrete produce by on behalf of from January February, March, May, June, July, August, November and December 2013. (the dosing of microsillica should be within + or - 3%)
| 01CV - Civils | Cxxx-NCR-001347 | NCR | Primary lining defects at the S4 bend (chg. 23.15 - 29.78) |  | Contr | BFK |  |  | 2014-07-11 | 2014-06-24 16:05 | -17 | 2014-05-30 10:36 | Tunnelling - Linings - Sprayed Concrete | 3500 |  | Workmanship | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following a visual inspection of the primary lining at the S4 bend (chg. 23.15 - 29.78), loose, uncompacted material was noticed along the leading edge of a few invert advances. Cores in this area have indicated a clean cold joint between advances.
| 01CV - Civils | Cxxx-NCR-001348 | NCR | Primary lining defects at the S4 straight section (chg. 13.15 - 23.15) |  | Contr | BFK |  |  | 2014-06-27 | 2014-06-27 16:01 | 0 | 2014-05-30 10:43 | Tunnelling - Linings - Sprayed Concrete | 5500 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following a visual inspection of the primary lining at the S4 bend (chg. 13.15 - 23.15), loose, uncompacted material was noticed along the leading edge of a few invert advances. Cores in this area have indicated a clean cold joint between advances.
| 01CV - Civils | Cxxx-NCR-001349 | NCR | Primary lining defects on S4 straight section (chg. 5.15 - 13.15) |  | Contr | BFK |  |  | 2014-06-27 | 2014-06-24 16:06 | -3 | 2014-05-30 10:48 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following a visual inspection of the primary lining at the S4 bend (chg. 5.15 - 13.15), loose, uncompacted material was noticed along the leading edge of a few invert advances. Additionally, two cracks within this section have shown signs of leakage.
| 01CV - Civils | Cxxx-NCR-001350 | NCR | Incorrect backfilling of cores |  | Contr | BFK |  |  | 2014-06-27 | 2014-06-19 18:22 | -8 | 2014-05-30 11:53 | Tunnelling - Linings - Sprayed Concrete | 3500 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Three core holes in AP2E (1no.) and AP4W (2no.) were backfilled with incorrect material using shotcrete rather than non shrink grout.
| 01CV - Civils | Cxxx-NCR-001351 | NCR | Core Hole filled in with wrong material/grout |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-07-29 | 2014-06-30 13:11 | -29 | 2014-05-30 12:07 | Tunnelling - Linings - Sprayed Concrete | 4000 |  | Material | Rework | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | Core hole backfilling in PTE with grout not as per specification/MCR
| 01CV - Civils | Cxxx-NCR-001352 | NCR | Geotehcnical log missing PTE adv 54 |  | Contr | BFK |  |  | 2014-06-13 | 2014-06-09 08:36 | -4 | 2014-05-30 12:01 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Verbal communication problem | Completed |  | Geotehcnical log for adv54 mssing on PTE
| 01CV - Civils | Cxxx-NCR-001353 | NCR | S4 DWall Opening to TCR WTH |  | Contr | BFK |  |  | 2014-07-31 | 2014-07-08 16:48 | -23 | 2014-05-30 18:52 | Tunnelling - Linings - Sprayed Concrete | 2500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Drawing Cxxx-MMD-C4-DDD-N105_Z-00068 shows the vertical offset off the S4 horizontal tunnel axis as 1190mm to the top of the Diaphragm Wall Opening. After surveying the opening and checking this against the level of the -4 slab and other drawings there was found to be inconsistencies between the levels. Initially it was believed that the tunnel axis level on drawing Cxxx-OVE-S-DDD-N105_Z-24316 and Cxxx-MMD-C4-DDD-N105_Z-00068 was incorrect, shown as +100.430 when on the tunnel longitudinal section, Cxxx-MMD-C4-DDB-N105_5-00228, the tunnel axis is +100.570. However after further investigation by Cxxx, it was confirmed that the level of SOP .401 is incorrect on the longitudinal section; this should be +100.430 hence causing an error on site. From the as-built survey of the opening, this means the opening of S4 is between 100-140mm too high on the top cut. The sides are to be checked in accordance with the confirmed revised level at SOP .401.
| 01CV - Civils | Cxxx-NCR-001354 | NCR | SMM - Amber Slope trigger breach in Davies Street (West) __ between: B07LB395-384 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-06-16 | 2014-06-12 13:07 | -4 | 2014-06-02 11:52 | Geotechnical Engineering - Settlement | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | New Amber Slope trigger breach in Davies Street (West) __ between: B07LB395-384 Actions: • Re-survey of the area was carried out and the data checked. The Amber trigger has been verified. • A visual inspection of the area of the trigger breach has been undertaken. Nothing unusual to report. • For more monitoring details please refer to the SRG Minutes for Thursday 29 May 2014. • The value of the Amber is just in the limit between Amber and Green: 1/1000 • SCL Progress: PTE, current Adv 145A (Invert)/VD1C, excavation completed 22/05/2014
| 01CV - Civils | Cxxx-NCR-001355 | NCR | Grade 5 Core PTE Advance 43/47 BOS ETH |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-07-02 | 2014-06-25 09:11 | -7 | 2014-06-02 12:30 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Core contains more than 3 sandy areas exceeding 0.5cm thikck. A number of voids are present exceeding 1cm in width.(Grade 5)
| 01CV - Civils | Cxxx-NCR-001356 | NCR | Form 83 Reinforcement Check Sheets Missing BOS ETH CH3 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-08-15 | 2014-08-01 12:19 | -14 | 2014-06-02 16:57 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | The following reinforcement check sheets are missing for BOS ETH CH3 Handover pack 3 No check sheets missing for CP10 (Crown and axis/mesh/parent child bars) 2 No check sheets missing for CP09 (Crown and axis/mesh) 2 No check sheets missing for CP08 (Invert/parent child bars) 2 No check sheets missing for CP07 (Invert bars/parent child bars)
| 01CV - Civils | Cxxx-NCR-001357 | NCR | No field grout test records/ cube results available for some Pre-treatment passes at GS BOS5 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-06-18 | 2014-06-18 10:47 | 0 | 2014-06-04 14:23 | Geotechnical Engineering - Compensation Grouting | 1500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | There are no field grout test records/ cube results available for the following passes as mentioned below towards pre-treatment works in BOS 5, resulted in failing to show grout characteristics and compressive strengths in line with specification. Pass 1: Total Volume injected – 1141 litres on 01/3/2012 – No field grout testing record and cube results Pass 3: Total volume injected – 10382 litres No field grout testing record and cube result for volume injected 600 litres on 9/3/2012 Pass 4: Total volume injected – 10382 litres No field grout testing record for volume injected 2190 litres on 04/4/2012 No field grout testing record for volume injected 2040 litres on 05/4/2012 Pass 7: Total volume injected – 15473 litres No field grout testing record for volume injected 8052 litres on 18/4/2012
| 01CV - Civils | Cxxx-NCR-001358 | NCR | No geotechnical face log for PTE Adv 99 |  | Contr | BFK |  |  | 2014-06-25 | 2014-06-23 11:17 | -2 | 2014-06-04 17:02 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | No geotechnical face log was taken for PTE Adv 99 top heading
| 01CV - Civils | Cxxx-NCR-001359 | NCR | PTW Sump |  | Contr | BFK |  |  | 2014-06-19 | 2014-06-05 20:03 | -14 | 2014-06-05 08:44 | Tunnelling - Linings - Sprayed Concrete | 4500 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Prior to installed primary lining thickening steel, it was discovered that a box out to de-bond the tunnel primary lining from where breakout for a sump is to be undertaken in PTW (east end) was installed in the wrong position. Additionally, a section of thickening already sprayed had encroached on the area where steel needed to be installed for the sump in the primary lining thickening.
| 01CV - Civils | Cxxx-NCR-001360 | NCR | Omitted Starter Bars on Level -2 Step Wall |  | Contr | BFK |  |  | 2014-08-21 | 2014-08-04 11:46 | -17 | 2014-06-05 09:16 | Structural Engineering - Reinforcement | 8000 |  | Incorrect Installation | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On the south face of the Level -2 step wall, some of the starter bars for the outstand (bar marks 99 and 100) have been omitted. Refer to attached survey showing the affected locations.
| 01CV - Civils | Cxxx-NCR-001361 | NCR | Bond Street WTH - NE Corner works |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-12-05 | 2014-07-15 12:12 | -143 | 2014-06-05 13:05 | Structural Engineering - Finishes | 1500 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Whilst pouring the reinforced concrete wall in the NE corner Level -6 BOS WTH we experienced a break in the flow of concrete to the pour of 2 hours. This may have meant a cold joint occurred in the pour. This occurred due to a non-compliant concrete truck being refused access to site
| 01CV - Civils | Cxxx-NCR-001362 | NCR | Low Flexual Beam in November 2013 @ BOS |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-10-30 | 2014-09-29 15:29 | -31 | 2014-06-05 14:15 | Tunnelling - Linings - Sprayed Concrete | 40000 |  | Material | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | From 3 beams tested @ 28 days for November 2013, 1 beam failed at D3 with a value 1.03 (Specification is 1.4).
| 01CV - Civils | Cxxx-NCR-001363 | NCR | Rebound Testing TCR |  | Contr | BFK |  |  | 2014-07-21 | 2014-07-02 17:48 | -19 | 2014-06-30 16:12 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Correct frequency of 1 every 2 months not adhered too between January and June in 2014. Jan - Test missed Feb - Test Done Sample 426 Mar - Test Not req Apr - Test Missed May - Test Done Sample 558 June - Test Done Sample 598
| 01CV - Civils | Cxxx-NCR-001365 | NCR | Method Statement/ Safe Systems of Work documentation not updated prior to casting in-situ invert or fixing steel for the AP7b secondary lining trials |  | Contr | BFK |  |  | 2014-06-27 | 2014-06-09 13:51 | -18 | 2014-06-06 18:08 | Tunnelling - Tunnelling General | 4000 |  | Documentation and Records | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Secondary Lining cast in-situ invert & 1st layer of secondary lining mesh installed without updated and approved documentation.
| 01CV - Civils | Cxxx-NCR-001366 | NCR | New amber slopes reported along Woodstock Street PLPs between C07LP229-C07LP227 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-06-30 | 2014-06-27 16:22 | -3 | 2014-06-09 11:51 | Geotechnical Engineering - Settlement | 2000 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | All, 1 New amber slopes reported along Woodstock Street PLPs between B07LB373-B07LB374 and C07LP230-C07LP228, is a result of post excavation settlement over PTE centre line. A visual inspection was carried out, nothing unusual to report. Please refer to the SRG for Thursday 05f06/2014 for further details.
| 01CV - Civils | Cxxx-NCR-001370 | NCR | Two new amber slopes reported along Woodstock Street __s and PLPs between B07LB373-B07LB374 and C07LP230-C07LP228 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-06-23 | 2014-06-27 16:32 | 4 | 2014-06-09 11:10 | Geotechnical Engineering - Settlement | 1500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | All, 2 New amber slopes reported along Woodstock Street __s and PLPs between B07LB373-B07LB374 and C07LP230-C07LP228. The survey has been verified and reported in today’s (03/06/2014) CTC and so no requirement for CTC to convene.
| 01CV - Civils | Cxxx-NCR-001371 | NCR | BOS PTW Advance 219 Early Age Strength below J2 requirement after 1 hour |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2014-07-14 | 2014-07-01 12:30 | -13 | 2014-06-09 12:33 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | The early strength test at 1 hour yielded a results of 0.488MPa which is below the J2 requirement (0.52MPa)
| 01CV - Civils | Cxxx-NCR-001372 | NCR | 22 Great Chapel – Missing Calibration Certificate for Crackmeter Installed |  | Contr | BFK |  |  | 2014-06-26 | 2014-06-18 10:50 | -8 | 2014-06-12 10:11 | Surveying - Instrumentation and Monitoring | 1500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | The crackmeter installed in 22 Great Chapel requires a calibration certificate, although the calibration certificate was used with data set up, it is not provided within the installation report. This is due to the certificate being misplaced.
| 01CV - Civils | Cxxx-NCR-001373 | NCR | Non complient material used in AP7B |  | Crossrail | PDP | BOS - Bond Street Station (West) |  | 2014-09-30 | 2014-08-29 15:56 | -32 | 2014-06-12 16:02 | Materials - Approval | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | The final smoothing layer used at AP7B does not have an accepted Materials Compliance Report demonstrating compliance with the specifications.
| 01CV - Civils | Cxxx-NCR-001374 | NCR | Non compliant material used in cast invert secondary lining AP7B |  | Crossrail | PDP |  |  | 2014-09-30 | 2014-09-19 11:25 | -11 | 2014-06-12 16:24 | Materials - Approval | 3500 |  | Supervision/Management | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | The cast invert for the secondary lining in AP7B was placed without an accepted Materials Compliance Report in place.
| 01CV - Civils | Cxxx-NCR-001375 | NCR | Missing details and incorrect filling of F50 forms for AP2W |  | Contr | BFK |  |  | 2014-07-11 | 2014-07-02 17:52 | -9 | 2014-06-16 10:36 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | A number of F50 forms for AP2W are missing details and have not been correctly filed i.e missing signatures, volumes, filed names and providing incorrect details about the profiles.
| 01CV - Civils | Cxxx-NCR-001376 | NCR | Monthly Testing - October Beams 2013 |  | Contr | BFK |  |  | 2014-07-18 | 2014-07-02 17:55 | -16 | 2014-06-18 17:31 | Tunnelling - Linings - Sprayed Concrete | 4000 |  | Software | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Set of 3no. 28 day beam, one of the D3 values is below specification by more than 10%. Sample 290.17, D3 = 1.2, Specification = 1.4
| 01CV - Civils | Cxxx-NCR-001377 | NCR | PTE Advance 193A, compressive results given @ 5 days and for PTE advance 205A only results for 5 cores received at BOS |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-07-17 | 2014-06-19 18:21 | -28 | 2014-06-17 16:01 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | PTE advance 193a, compressive results was at 5 days rather than our ITP requirements of 1-3 days, also for PTE advance 205a, only 5 cores received compressive results for.
| 01CV - Civils | Cxxx-NCR-001379 | NCR | Concrete Early Age Strength below J2 Curve Adv 23 CP4 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-07-18 | 2014-06-23 12:38 | -25 | 2014-06-18 14:02 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Early age strength at 2hrs and 3hrs below J2 curve (form 57 attached)
| 01CV - Civils | Cxxx-NCR-001381 | NCR | PTW @ BOS advances 398a and CP2&CP4,early age strength not carried out at .10 and .30 minutes |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-07-19 | 2014-06-23 15:38 | -26 | 2014-06-19 14:13 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | PTW @ BOS early age strength test was missed @ 10 and 30 minutes for advances 398a and CP2&4, thus this is a non compliance against s own ITP.
| 01CV - Civils | Cxxx-NCR-001382 | NCR | PTW Advance 68 @ BOS BFK received results for 4 cores rather than the ITP requirements of 6 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-07-19 | 2014-06-23 16:00 | -26 | 2014-06-19 16:10 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | PTW advance 68, only 4 twentyeight day compressive cores was received from laboratory
| 01CV - Civils | Cxxx-NCR-001383 | NCR | Missing form 50 for AP3W advances 21 and 23 |  | Contr | BFK |  |  | 2014-07-25 | 2014-07-10 11:13 | -15 | 2014-06-20 15:11 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Missing form 50 for AP3W advances 21 and 23
| 01CV - Civils | Cxxx-NCR-001384 | NCR | Hammer Testing Not Performed in PTE East as per KT 20 Requirements |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-08-21 | 2014-07-31 12:43 | -21 | 2014-06-20 15:36 | Tunnelling - Linings - Sprayed Concrete | 3500 |  | Testing and Commissioning | Rework | 3 (3-6k) | Complete | Supervision - Insufficient supervision | Completed |  | Hammer Testing Not Performed within time as per KT20 Requirements
| 01CV - Civils | Cxxx-NCR-001385 | NCR | New Amber Triggers breach in South Molton Street |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-07-07 | 2014-07-07 17:07 | 0 | 2014-06-23 10:52 | Geotechnical Engineering - Settlement | 1500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Three new Amber Triggers breached between: • BO7LP087 -089 South Molton Street East PLP • BO7LP088 -090 South Molton Street East PLP • BO7LB187 -186 South Molton Street East __
| 01CV - Civils | Cxxx-NCR-001386 | NCR | AP8 Permanent Headwall Primary Lining Reinforcement |  | Contr | BFK |  |  | 2014-07-07 | 2014-07-04 16:36 | -3 | 2014-06-23 17:57 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Steel was installed as per drawing Cxxx-MMD-C4-DDD-N105_5-00373. CRL inspector came to inspect FF steel on headwall advance 48 in AP8 and found a difference between the schedule (Cxxx-MMD-C4-DDJ-N105_5-00373) and the drawing. The A* component on the left hand side appeared to denote the length of the steel on the face which contradicted what appeared on the right hand side. The inspector instructed the engineer to turn the steel from 12 o'clock to 3 o'clock around. The steel was then signed off and sprayed. Afterwards, it was found that the drawing was correct and the schedule is wrong, therefore the steel is installed incorrectly. This concerns BM08 only in the area described above.
| 01CV - Civils | Cxxx-NCR-001387 | NCR | Incorrect filling of form 50 for AP4W initial drive |  | Contr | BFK |  |  | 2014-07-14 | 2014-06-27 16:35 | -17 | 2014-06-23 12:47 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Incorrectly filled out F50 forms for AP4W initial drive. These forms are missing information such as nozzleman names, nozzleman signatures and spray commence/finish times.
| 01CV - Civils | Cxxx-NCR-001388 | NCR | 2 No Monitoring Points Missing/ 2 No moitoring points installed late RMS161 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-07-31 | 2014-07-07 17:37 | -24 | 2014-06-24 09:23 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 2 No Monitoring Points Missing/ 2 No moitoring points installed late in RMS161
| 01CV - Civils | Cxxx-NCR-001389 | NCR | TCR - Lack of fire proofing layer thickness over the near face mesh at AP7B |  | Contr | BFK |  |  | 2014-08-29 | 2014-08-29 16:46 | 0 | 2014-06-26 09:52 | Tunnelling - Linings - Sprayed Concrete | 10000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following completion of secondary lining fire proofing layer in AP7B trial, it became apparent that in some areas, the required thickness for fire proofing layer (50mm theoretical) over the near face mesh has not been achieved.
| 01CV - Civils | Cxxx-NCR-001390 | NCR | Missing Form 50 For AP3W Tie-in advance 7 |  | Contr | BFK |  |  | 2014-07-17 | 2014-07-08 11:36 | -9 | 2014-06-26 09:49 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Lack or improper material identification and traceability | Completed |  | Missing form 50 for AP3W tie-in advance 7
| 01CV - Civils | Cxxx-NCR-001391 | NCR | During the Month of June 2013 for CH3 BFK failed to carryout .10 and .30 minutes Early Age Strength Development throught the month including the 1 hour test for advance 16. |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-07-26 | 2014-07-04 16:46 | -22 | 2014-06-26 15:07 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | During Month of June 2013, engineers on a few occassions fail to carryout 10 and 30 minutes penetrometer test which is not compliant with their ITP, also missed the 1 hour test for advance 16 of CH3.
| 01CV - Civils | Cxxx-NCR-001392 | NCR | Miling proposal AP4W |  | Contr | BFK |  |  | 2014-07-10 | 2014-07-07 16:58 | -3 | 2014-06-26 18:49 | Tunnelling - Linings - Sprayed Concrete | 6500 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Oversprayed areas in AP4W between ch 19 to 27. propose remove oversprayed concrete. These areas will be taken back to 5 green or 50 mm larger than the primary lining design line. (See attached signed proposal)
| 01CV - Civils | Cxxx-NCR-001393 | NCR | 2 No Piles Damaged in AP3A ETH |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-08-27 | 2014-08-08 12:56 | -19 | 2014-06-27 17:20 | Tunnelling - Linings - Sprayed Concrete | 5500 |  | Material | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 2 No piles were damaged when packer was used to remove excess shotcrete from soft eye/lining AP3A area to put in the dowel bars
| 01CV - Civils | Cxxx-NCR-001394 | NCR | TCR WTH −5 Raft Slab Couplers : Missing Caps |  | Contr | BFK |  |  | 2014-08-15 | 2014-08-15 16:07 | 0 | 2014-06-30 07:27 | Structural Engineering - Concrete Member | 10000 |  | Incomplete Works | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | Breaking out the protection slab on top of the -5 raft slab has revealed a number of couplers that are missing their protective caps, in various locations around the slab. These couplers have started to fill up with muck and dust.
| 01CV - Civils | Cxxx-NCR-001395 | NCR | TCR WTH −5 Raft Slab Couplers : Bent Bars |  | Contr | BFK |  |  | 2014-08-15 | 2014-08-15 16:10 | 0 | 2014-06-30 07:32 | Structural Engineering - Concrete Member | 10000 |  | Damaged | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During break out of the protection slab on top of the -5 raft slab, some couplers have been bent over up to an angle of 75° from the vertical. This applies predominantly to the two walls just south of the eastbound running tunnel, but also in other isolated locations around the slab.
| 01CV - Civils | Cxxx-NCR-001396 | NCR | TCR WTH −5 Raft Slab Couplers : Couplers Not Visible |  | Contr | BFK |  |  | 2014-08-15 | 2014-08-15 16:11 | 0 | 2014-06-30 11:17 | Structural Engineering - Concrete Member | 10000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In various locations around the −5 raft slab, couplers that should be in place for connection to the walls and columns are not visible at the surface.
| 01CV - Civils | Cxxx-NCR-001397 | NCR | TCR WTH −5 Raft Slab Couplers : Couplers Damaged |  | Contr | BFK |  |  | 2014-08-15 | 2014-08-15 17:14 | 0 | 2014-06-30 09:45 | Structural Engineering - Concrete Member | 10000 |  | Damaged | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During break out of the protection slab on top of the -5 raft slab, some of the couplers have been found to be damaged to varying degrees. These range from small deformities to complete crushing. The scale of the damage is in clusters spread out over the whole base slab.
| 01CV - Civils | Cxxx-NCR-001398 | NCR | TCR WTH −5 Raft Slab Couplers : Couplers Out of Position (Reduced Cover) |  | Contr | BFK |  |  | 2014-08-15 | 2014-08-16 14:54 | 1 | 2014-07-01 15:31 | Structural Engineering - Concrete Member | 10000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During steel fixing for the -5 raft slab, there was not space to fit the vertical coupled bars through the top mat at precise locations, particularly at lap joints. As a result, some of the coupled bars have less than the minimum cover for the walls and columns above. This predominantly applies to the curved and diagonal walls on either side of the eastbound running tunnel, which cross the grid of steel in the top mat at an angle, although there are other isolated cases in the rest of the box. See attached survey of coupler locations relative to the faces of the structural walls and columns. In the survey, couplers in orange have less than the minimum cover stated on the Cxxx drawings. The worst-case (least) cover is annotated for each wall and column.
| 01CV - Civils | Cxxx-NCR-001399 | NCR | TCR WTH −5 Raft Slab Couplers : Missing __ Couplers |  | Contr | BFK |  |  | 2014-08-15 | 2014-08-15 16:21 | 0 | 2014-06-30 10:02 | Structural Engineering - Reinforcement | 10000 |  | Incomplete Works | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | The structural wall just south of the eastbound running tunnel alignment contains a series of __ taper threaded couplers for B16 bars in the centre (just north of the trench) — see Cxxx-OVE-S-DDL-N105_6-25162 rev. X02. Breaking out the protection slab on top of the -5 raft slab has revealed that a small number of these couplers themselves are missing.
| 01CV - Civils | Cxxx-NCR-001400 | NCR | TCR WTH −5 Raft Slab : Damage Outside S4 |  | Contr | BFK |  |  | 2014-08-15 | 2014-08-15 16:22 | 0 | 2014-06-30 11:18 | Structural Engineering - Concrete Member | 10000 |  | Damaged | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | Breaking out the protection slab has damaged an area of the −5 raft slab outside the opening to S4, approx. 4.6m long × 1.8m wide × 0.120m deep. One rebar sticks out by approx. 0.150m and has been bent upwards.
| 01CV - Civils | Cxxx-NCR-001401 | NCR | TCR WTH −5 Raft Slab : Poorly Compacted Concrete around Catchpit 5 |  | Contr | BFK |  |  | 2014-12-19 | 2014-12-09 13:23 | -10 | 2014-07-14 07:57 | Structural Engineering - Concrete Member | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Voids in the -5 raft slab concrete have been found after lifting the lid on catchpit 5 (following break out of the protection slab). The concrete on the lip on the north edge has broken away; there is a void on the left hand side of the north face of the catchpit; and there are voids around the two drainage pipes that enter the catchpit on the north face. There are also some areas of honeycombing. See attached pictures. A repair has previously been attempted on the lip and void on the left hand side, using shotcrete.
| 01CV - Civils | Cxxx-NCR-001402 | NCR | Hammer testing in PTW ch 123 prior to regulating application |  | Contr | BFK |  |  | 2014-07-21 | 2014-07-08 12:26 | -13 | 2014-06-30 18:02 | Tunnelling - Linings - Sprayed Concrete | 2500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Hammer testing was carried out at chn 123 prior to regulating application. Hammer testing around a crack revealed a hollow sound and this area was consequently removed as per Cxxx's request (refer to attached photograph - IMG_1473). Upon completion of the concrete removal, this area was proof-drilled and found the lining in this local area to be of 300-340mm (required lining thickness = 350mm).
| 01CV - Civils | Cxxx-NCR-001403 | NCR | TCR WTH −5 Raft Slab : Spalling Concrete (Central Trench) |  | Contr | BFK |  |  | 2014-09-29 | 2014-09-09 13:06 | -20 | 2014-07-14 07:50 | Structural Engineering - Concrete Member | 10000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Concrete on the horizontal top edges and on the vertical edges of the trench in the -5 raft slab is spalling away in places. Furthermore, concrete that forms the construction joint / kicker with the pour underneath the trench is also spalling away. See attached picture.
| 01CV - Civils | Cxxx-NCR-001404 | NCR | SMM - un-read manual points around BOS area |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-07-21 | 2014-07-21 11:37 | 0 | 2014-07-01 18:36 | Surveying - Instrumentation and Monitoring | 2500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | A number of ground and building points outside of the compensation grouting zone have not been read to the agreed monthly frequency. The agreed monitoring frequency for these points are; All BOS points outside of the compensation grouting zone: 1x monthly All points within Compensation grouting zone: 1x weekly All points within concurrent jacking/excavation zone (1.5D): Daily (otherwise agreed in the SRG/CTC group)
| 01CV - Civils | Cxxx-NCR-001405 | NCR | TCR WTH −5 Raft Slab Couplers : Out of Vertical Alignment |  | Contr | BFK |  |  | 2014-08-15 | 2014-08-15 16:45 | 0 | 2014-07-02 13:06 | Structural Engineering - Reinforcement | 10000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A number of couplers in the -5 raft slab are vertically out-of-plumb, such that when male threaded starter bars are screwed in they either clash with other bars or extend outside the minimum cover zone of the wall/column. This occurs in clusters spread out over the whole slab; one example is the central buttress wall of the three on the north side of the box.
| 01CV - Civils | Cxxx-NCR-001406 | NCR | AP8 Missing Geological logs |  | Contr | BFK |  |  | 2014-07-16 | 2014-07-02 18:53 | -14 | 2014-07-02 07:36 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | No photos taken for geological logs in advance 45 and 47 top headings approaching TBM tunnel. Logs in advance 44 and 48 as expected.
| 01CV - Civils | Cxxx-NCR-001408 | NCR | Missing details in AP7b Initial drive and tie-in form 50s |  | Contr | BFK |  |  | 2014-07-29 | 2014-07-14 10:13 | -15 | 2014-07-08 08:38 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Most of the form 50s in AP7b Intial drive and Tie-in are missing details such as signatures, spray time, file name, etc
| 01CV - Civils | Cxxx-NCR-001409 | NCR | Missing details in AP2E Initial drive form 50s |  | Contr | BFK |  |  | 2014-07-29 | 2014-07-15 14:53 | -14 | 2014-07-08 08:39 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Almost all of the form 50s in AP2E initial drive are incorrectly filled out or incomplete. Forms do not have details such as signature, spray time, file name and initials.
| 01CV - Civils | Cxxx-NCR-001410 | NCR | TCR WTH −5 Raft Slab Couplers : Repairing Broken Out Concrete |  | Contr | BFK |  |  | 2014-08-15 | 2014-08-15 16:47 | 0 | 2014-07-08 11:24 | Structural Engineering - Concrete Member | 10000 |  | Damaged | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | This NCR covers two issues relating to the reinstatement of concrete following remedial works to the couplers (see attached pictures): 1. The remedial works involved drilling and fixing a number of bars into the slab (Cxxx-NCR-001395, 1396, 1397 and 1398). In many cases, due to congestion of steel in the top mat, several attempts were needed to find a way through the rebar — leaving several shallow, abandoned holes in the slab. 2. Some sets of bars, for example the 4No 32mm bars on the west face of the south lining wall, could not be found at all and drilling was repeatedly hitting rebar. For these bars, the concrete was locally broken out (within the footprint of the wall/column) to expose the top mat to assist drilling. Concrete has also been locally broken out to expose buried couplers in various locations, as described in Cxxx-NCR-001396.
| 01CV - Civils | Cxxx-NCR-001411 | NCR | During the month of December .10minutes early age strength test was not carried out in a few instances |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-07-22 | 2014-07-11 10:33 | -11 | 2014-07-08 12:19 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate resources | Completed |  | During the month of December, engineers on a few occassions fail to carryout .10 minute test, thus not adhering to the own ITP.Location are PTW advance 65, 103 and thickening works @ chainage 52-65 from the dates of 13/12/2013 and 15/12/2013.
| 01CV - Civils | Cxxx-NCR-001412 | NCR | July 2013 cores crushed outside 1-3 day windows in CH3 thickening works |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-07-22 | 2014-07-10 11:08 | -12 | 2014-07-08 13:47 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate resources | Completed |  | For the month of July 2013 cores were cushed outside 1-3 days,@ CH3 thickening works on 22/07/2013 and 25/07/2013. (sample number is as follows 384 and 386)
| 01CV - Civils | Cxxx-NCR-001415 | NCR | Certificates of analysis for shotcrete admixture namely; Tamcem60, HCA. missing from ITP Records from BOS January 2013 to April 2014 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-07-23 | 2014-07-10 11:57 | -13 | 2014-07-09 13:55 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Lack or improper material identification and traceability | Completed |  | Certficates of analysis for admixtures used in shotcrete supplied by is currently missing from ITP records. This is a deliverable record as stated by ITP.
| 01CV - Civils | Cxxx-NCR-001417 | NCR | For the Month of January and February 2014 Microsillica was over and underdosed on a few occasions by maximum of 2.7% |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-09-08 | 2014-07-11 12:52 | -59 | 2014-07-10 15:00 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Error by manufacturer in shipping or marking | Completed |  | For the Month of January and February 2014 Microsillica was over and underdosed on a few occasions by maximum of 2.7%. Thus a few wagons were batched at 5.7% whilst ITP states that Microsilica bactching has a tolerance of +/- 3%. See Attached batch tolerance summary sheets
| 01CV - Civils | Cxxx-NCR-001418 | NCR | AP2W Remedia Action |  | Contr | BFK |  |  | 2014-07-24 | 2014-07-31 13:15 | 7 | 2014-07-10 21:40 | Civil - Tunnelling | 4500 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Oversprayed areas in AP2W between ch 11 to 15. propose remove oversprayed concrete. These areas will be taken back to 5 green or 50 mm larger than the primary lining design line. (See attached signed proposal) Proof drilling will be attached for close NCR.
| 01CV - Civils | Cxxx-NCR-001419 | NCR | Residual flexural beam strength test result - anomaly (TCR sample 144 June 2013) |  | Contr | BFK |  |  | 2014-07-25 | 2014-07-15 12:49 | -10 | 2014-07-11 16:30 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Residual flexural beam test result for SA 3397 (sprayed 26/6/13) indicates slightly low reading between 3.6 to 4.0 CMOD (1.1MPa), but then recovers to exhibit compliant residual flexural strength at higher CMOD. Test result for SA3395 passes 90 day criteria at 28 days (both D1S1.8 and D3S1.4) Test result for SA3396 passes 90 day criteria at 28 days (both D1S1.8 and D3S1.4) Test result for SA3397 passes 90 day criteria at 28 days for D1S1.8, but marginal fail on D3S1.4 criteria due to anomalous reading (sample recovered to exhibit compliant residual flexural strength). Recommend that this should be treated as a "pass". Location: TCR CH3 PILOT TUNNEL ADVANCE 25 (NOW ALREADY DEMOLISHED)
| 01CV - Civils | Cxxx-NCR-001420 | NCR | The initial and primary lining were sprayed as one layer CP09 Adv 02 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-08-10 | 2014-07-28 12:08 | -13 | 2014-07-11 16:49 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The initial and primay lining were sprayed as one layer in Adv 2 CP09. RESS not followed
| 01CV - Civils | Cxxx-NCR-001421 | NCR | 5 One day cores tested |  | Contr | BFK |  |  | 2014-08-03 | 2014-07-15 17:35 | -19 | 2014-07-13 17:20 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | 5 cores tested at 1 day ITP states 6
| 01CV - Civils | Cxxx-NCR-001422 | NCR | PTE Adv 249 Face sealing only 75mm while next invert started after more than 12hrs |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-08-13 | 2014-08-01 12:21 | -12 | 2014-07-14 13:01 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | The face of advance 249 PTE was covered with only 75mm shotcrete. More than 12 hrs elapsed before the start of next invert.
| 01CV - Civils | Cxxx-NCR-001423 | NCR | PTE - Incomplete F50s |  | Contr | BFK |  |  | 2014-07-28 | 2014-07-15 18:34 | -13 | 2014-07-14 17:43 | Tunnelling - Linings - Sprayed Concrete | 2000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Some F50s were left incomplete by new engineers being trained on shift: adv 252 - excavation time adjusted according to CRLs request adv 253 - excavation time adjusted according to CRLs request adv 254 - missing accelerator dosage adv 257 - missing accelerator dosage adv 265 - missing completed ticket number for excavation adv 266 - missing completed ticket number for excavation and as-built file name adv 267 - missing completed ticket number adv 268 - missing batch time of shotcrete and engineers signature on permit to enter (lead miners present)
| 01CV - Civils | Cxxx-NCR-001424 | NCR | S3 - Incomplete F50 form |  | Contr | BFK |  |  | 2014-07-28 | 2014-07-15 18:38 | -13 | 2014-07-14 18:03 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | On adv 2, at completion of primary lining, Engineer carried out early age strength testing at 45 minutes to determine that it was safe to enter the exclusion zone. The test was completed and determined it was safe to enter, which the lead miner signed the F50 form and verified. On this occasion the engineer forgot to add her own signature to the form. Once this was identified, the form was then completed by the shift engineer.
| 01CV - Civils | Cxxx-NCR-001425 | NCR | Materials Proposal Schedule not being used and managed as required by WI vol 2B 20.7 |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2014-10-31 | 2014-10-14 16:38 | -17 | 2014-07-15 08:39 | Civil - Tunnelling | 1500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | During the CE Marking and Materials Compliance Surveillance dated 8th July 2014 stated that the responsibility of raising Materials Compliance Record’s (MCR’s) for Crossrail acceptance lies with both the Construction team and Materials team. On review of the Materials Proposal Schedule (MPS), Cxxx--C-TSC-CRT00_ST005-50004 Rev 18 Code 2, it was identified that this document was not being used for the forward planning of materials for approval to allow for timely submission and review before the incorporation date. The requirements of the Works Information vol 2B clause 20.7 state “The Contractor shall develop a Materials Proposal Schedule (MPS) listing all proposed permanent works materials and products and indicating any variances from the specified materials ... The MPS shall identify .,target dates(approval, delivery, over dues)”. It was further confirmed that there was no process in place for forward planning of required materials, such as a look a-head programme, with the MPS being used as a ‘tracker’ of MCR’s only. Within the MPS there is a box requirement which details a ‘required incorporation in the works date’, however this requirement is not being managed and completed. Additionally the Crossrail site team have recently raised two NCR’s for materials used in the works without an accepted MCR in place; Cxxx-NCR-1373 and Cxxx-NCR-1374 refer. To ensure the MPS is used for proposing and managing material compliance as required by the Works Information parts 13 and 20 this NCR was raised.
| 01CV - Civils | Cxxx-NCR-001426 | NCR | Material Compliance Records had not undergone internal update as required by PMI 1297 |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2015-01-23 | 2015-01-22 17:03 | -1 | 2014-07-15 08:44 | Civil - Tunnelling | 6000 |  | Documentation and Records | Use As-Is | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | The Construction Products Regulations 2011 came into force in the UK in July 2013 which requires Manufacturers to draw up a Declaration of Performance (DoP) for all products that are covered by a harmonised European Standard or European Technical Assessment. This is a mandatory requirement and is law under the regulations. To ensure materials being used on Crossrail conform to these CE Marking requirements, a Project Managers Instruction was sent to all Crossrail contracts for issue; PMI 1297 was instructed to the Contractor at Cxxx in December 2013. The PMI stated: ‘It is the Contractors responsibility to ensure that all documentation is in place to support the new regulations. Any MCR’s which have been submitted to date, including those submitted pre July 2013 still being sourced post July 2013 are not required to be re-submitted at this time, but supporting documentation must be obtained by the Contractor and kept on record and available upon CRL’s request or for auditing purposes’. During the CE Marking and Material Compliance Surveillance dated 8th July 2014 it was confirmed that MCR’s previously accepted before July 2013 which are still in use post July 2013 had not undergone internal update. Additionally it was confirmed that materials submitted between the period of July 2013 and Nov 2013 had also not undergone internal update as required.
| 01CV - Civils | Cxxx-NCR-001427 | NCR | Revised MCR template not incorperated in works when instructed by PMI 1297 in Dec 2013, as such MCR's submitted do not include CE marking requirements |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2015-01-16 | 2015-01-16 14:16 | 0 | 2014-07-15 08:51 | Civil - Tunnelling | 1500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | To ensure materials being used on Crossrail conform to these CE Marking requirements, a Project Managers Instruction was sent to all Crossrail contracts for issue; PMI 1297 was instructed to the Contractor at Cxxx in December 2013. The PMI stated: “The existing Materials Compliance Form – Appendix 13J has been revised to accommodate the aforementioned supplier decal and also the necessary Declaration of Performance and requirements for CE marking” During the CE Marking and Materials Compliance Surveillance dated 8th July 2014 it was confirmed that this form was not incorporated in the works until 10th April 2014 and as such all MCR’s submitted between the issue of PMI 01297 and the 10th April 2014 had no information submitted demonstrating compliance with the CE marking requirements as required by the instructed PMI. This was further demonstrated on review of three MCR’s for their respective CE marking compliance, see below. NCR raised to ensure MCR’s between the period mentioned are updated as required by the PMI. • Cxxx--C-LRC-CRT00_ST005-50277 Dec 2013 No CE marking information • Cxxx--C-LRC-CRT00_ST005-50321 Jan 2014 No CE marking information • Cxxx--C-LRC-CRT00_ST005-50328 May 2014 CE marking information submitted
| 01CV - Civils | Cxxx-NCR-001428 | NCR | Works carried out without signing MCR as Code 1 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-08-14 | 2014-07-15 17:27 | -30 | 2014-07-15 13:35 | Civil - Tunnelling | 1500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | BOS WTH hall team caried out the civil works for RC slab and RC wall north east corner level -5 to -6 without Code 1 MCRs for the following 1. Cxxx--C-LRC-CRT00_ST005-50340 (Chemcure R90) 2. Cxxx--C-LRC-CRT00_ST005-50342 (Servitite Waterstop) 3. Cxxx--C-LRC-CRT00_ST005-50347 (Aquatard Topface)
| 01CV - Civils | Cxxx-NCR-001429 | NCR | Cubes not taken for NE corner slab pour on 06/06/14 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-08-14 | 2014-07-15 17:29 | -30 | 2014-07-15 13:45 | Civil - Tunnelling | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | did not take any cubes for the 3m3 pour on 06/06/14
| 01CV - Civils | Cxxx-NCR-001430 | NCR | SMM -Amber trigger breach between HS2007M – HS2008M (rear 20 Hanover Square) |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-11-28 | 2014-11-05 13:34 | -23 | 2014-07-15 16:59 | Surveying - Instrumentation and Monitoring | 1500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | An amber slope breach between HS2007M – HS2008M 20 Hanover Square HLCs the point at the time of report just exceeded the amber level at 1:839. Currently this area is within the compensation grouting exclusion zone for PTW (back excavation). No action is required until the SCL excavation exits the affected area. It is expected that as excavation works progresses out of the affected zone, the differential settlements will improve with the rear injections from concurrent grouting. have also reduced the grout efficiency for areas outside of the foam concrete area.
| 01CV - Civils | Cxxx-NCR-001431 | NCR | April 2014 Microsillica overdosed in 3 loads by .8%, .5% and .4%. (tolerance is 3% plus or minus) |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-07-29 | 2014-07-16 08:35 | -13 | 2014-07-15 17:13 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Insufficient quantity of material to do the job | Completed |  | For the month of April 2014 3 loads were over dosed by a maximum of .8%. ITP states that there is a tolerance of 3% plus or minus.
| 01CV - Civils | Cxxx-NCR-001434 | NCR | Missing geo-logs in PTE |  | Contr | BFK |  |  | 2014-08-14 | 2014-07-23 17:08 | -22 | 2014-07-17 18:46 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | No photos taken for geological logs in PTE advance 264, 282 and 286. All logs in between show as expected ground conditions. No photos from inspectors available.
| 01CV - Civils | Cxxx-NCR-001435 | NCR | PTE Adv 258A Face Sealing only 75mm for over 12hrs BOS ETH |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-08-17 | 2014-07-28 12:10 | -20 | 2014-07-18 09:57 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Equipment Breakdown | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Sealing of the face of PTE ADV 258A Top Heading was sprayed with 75mm thickness but due to delays on the following invert advance the face was left with 75mm sealing for over 12 hours. Additional 75mm were subsequently sprayed on 18 hours after face was sealed initially. The delay was caused due to insufficient concrete transport capacity available underground (mechanical problems with remixers).
| 01CV - Civils | Cxxx-NCR-001436 | NCR | Insufficient Profile control records presented in SRG PTW BOS |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-08-17 | 2014-07-28 12:26 | -20 | 2014-07-18 14:18 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Insufficient profile control records were presented in SRG on 15/07/14 for some advances where there were noticeably less than 1 point per meter on the perimeter. The profiles showed less than 1 point per one meter perimeter and threrefore didn’t comply with the specified 1 point per 1m2. (Sheets attached)
| 01CV - Civils | Cxxx-NCR-001437 | NCR | BOS PTW Crack Repairs |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-08-30 | 2014-08-26 09:51 | -4 | 2014-07-18 14:29 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | BOS PTW: Crack drilling and injection process on going for 2 days with no engineer present and no check sheet (form 98) being filled
| 01CV - Civils | Cxxx-NCR-001438 | NCR | Leak Sealing PTW Records Being Filled in Office |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-08-30 | 2014-08-27 17:34 | -3 | 2014-07-18 14:35 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | CRL Observed engineer filling out leak sealig record sheets several days after the resin had been injected into the lining.
| 01CV - Civils | Cxxx-NCR-001439 | NCR | TCR WTH −5 Raft Slab Couplers : Horizontal Alignment |  | Contr | BFK |  |  | 2014-09-05 | 2014-08-29 16:43 | -7 | 2014-08-14 18:49 | Structural Engineering - Concrete Member | 10000 |  | Incorrect Installation | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Similar to Cxxx-NCR-001398, this NCR applies to couplers that are far inside the concrete member, such that they are not in the same plane as the rest of the bars on that face and have excessive cover. See attached picture for an example, where a 32mm bar has been drilled and fixed to replace a damaged coupler in the lining wall outside PTE.
| 01CV - Civils | Cxxx-NCR-001440 | NCR | Cores tested at 4 days |  | Contr | BFK |  |  | 2014-09-07 | 2014-08-28 14:13 | -10 | 2014-08-17 11:13 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Equipment Breakdown | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Samples 645 and 647, PTE Adv 283 and 287. 1 day cores were tested late at at 4 days
| 01CV - Civils | Cxxx-NCR-001441 | NCR | BOS LCE2 Sump Reinforcement Repairs |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-08-08 | 2014-08-05 16:49 | -3 | 2014-07-18 17:48 | Tunnelling - Linings - Sprayed Concrete | 30000 |  | Damaged | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The LCE2 sump reinforcement was installed during the thickening works in 2013 and would be constructed at a later date. The tunnel was then backfilled with foam concrete for the TBM to pass though Bond Street Station. During the removal of the foam concrete it has been discovered that the top mat of reinforcement was not completely covered with the thickening layer and bars have been left exposed. The reinforcement remains intact however further exposure and cleaning will be required to create a good bond with the sump lining.
| 01CV - Civils | Cxxx-NCR-001442 | NCR | Remedial Action S3 |  | Contr | BFK |  |  | 2014-10-31 | 2014-10-08 17:33 | -23 | 2014-07-20 12:18 | Civil - Tunnelling | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | From chainage 0 – 2 m the over sprayed areas have to be removed by handbreaking or milling (crown and sidewall area). Between chainage 4 – 8 the invert area overspray has to be removed. These areas will be taken back up to 30mm larger than the primary lining design line.(See attached signed proposal) Proof drilling will be attached for close NCR.
| 01CV - Civils | Cxxx-NCR-001443 | NCR | PTE Adv 260A face not sealed for two hours |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-08-20 | 2014-07-28 12:28 | -23 | 2014-07-21 10:25 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Equipment Breakdown | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | PTE Adv 260A no shotcrete availaible for two hours to seal the face and spray the initial
| 01CV - Civils | Cxxx-NCR-001444 | NCR | PTE - Incomplete F50s |  | Contr | BFK |  |  | 2014-08-04 | 2014-07-23 17:09 | -12 | 2014-07-21 10:38 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Additional to Cxxx-NCR-001423, and not recorded at the time, two additional F50 forms were left incomplete by new engineers being trained on shift: - adv 270 permit to excavate not signed by lead miner (test checked by engineer and signed) - adv 274 permit to excavate not signed by lead miner (test checked by engineer and signed)
| 01CV - Civils | Cxxx-NCR-001445 | NCR | Hanson Aggregate Supplier Test - Flakiness |  | Contr | BFK |  |  | 2014-08-11 | 2014-07-23 10:50 | -19 | 2014-07-21 15:16 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | On coarse aggregate Flakiness test is to be performed by supplier once in a month. During January to November 2013 no tests were carried out in the following months: May August September
| 01CV - Civils | Cxxx-NCR-001446 | NCR | PTE, CP9, Advance 7; only 5 core results for compressive strength @ 1 day wasr received rather than 6 core results as stipulated by BKF ITP. |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-08-04 | 2014-07-22 18:14 | -13 | 2014-07-21 15:24 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | PTE, CP9, advance 7, only 5 cores were tested, KT20 stipulates 6 core results.
| 01CV - Civils | Cxxx-NCR-001447 | NCR | ETH , PTE Advance 229A cores were cushed @ 31 days rather than 28 days. |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-08-18 | 2014-07-22 18:15 | -27 | 2014-07-21 15:46 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | ETH, PTE advance 229A, cores were crushed @ 31 days rather than 28 days as stated by KT20.
| 01CV - Civils | Cxxx-NCR-001448 | NCR | Hanson Aggregate Supplier Tests - Limestone Summary |  | Contr | BFK |  |  | 2014-09-07 | 2014-08-29 12:53 | -9 | 2014-08-17 15:06 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Particle Density and Water Absorption test to be performed once per year. For 2/6mm Limestone from __ Quarry, the time difference between tests is greater than one year. Tests were performed in August 2012 and then again in October 2013.
| 01CV - Civils | Cxxx-NCR-001451 | NCR | Construction of LCE2 Sump - Platform Tunnel Enlargement (East) |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2014-09-02 | 2014-08-28 10:38 | -5 | 2014-07-22 15:06 | Tunnelling - Linings - Sprayed Concrete | 59000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The construction of the LCE2 Sump in PTE (East) has been constructed outside the requirements stated within the Required Excavation Support Sheet, RESS No. LCE2-003 (Sump) dated 21st July 2014. The primary lining for the sump which was constructed during the nightshift of 21st July 2014, has been constructed using placed concrete, which is not in accordance with the RESS for the works which states ‘sprayed 200mm sump primary lining’. In addition, Crossrail recorded at the time of the works, that the construction of the base for the sump was not compacted using an emersion vibrator, despite Crossrail requesting that compact the concrete to the base sump using an immersion vibrator. Crossrail recorded that undertook the compaction of the placed concrete by a ‘tamped’ method by using an excavator shovel bucket. Crossrail also note from post concrete pour inspection of the sump that the temporary works strutting used internally to form the shape of the sump is of a poor standard and workmanship, where the shape of the sump has deformed as a result of the weight of concrete applied to the sides of the sump during the construction of the sump’s primary lining.
| 01CV - Civils | Cxxx-NCR-001452 | NCR | AP3E Cast Invert U1 finish out of specification |  | Contr | BFK |  |  | 2015-01-16 | 2014-12-19 17:45 | -28 | 2014-07-23 12:28 | Civil - Tunnelling | 10000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | AP3E cast invert U1 finish is out of specifications due to an inappropriate leveled.
| 01CV - Civils | Cxxx-NCR-001453 | NCR | Incorrect filling of form 50 for AP3W initial drive |  | Contr | BFK |  |  | 2014-08-08 | 2014-07-28 17:20 | -11 | 2014-07-25 13:56 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Incorrect filled out F50 forms for AP3W Initial drive. These forms are missing information such as nozzleman names and signatures, spray start and finish times, and file names.
| 01CV - Civils | Cxxx-NCR-001454 | NCR | PTE Advance 259A not Sprayed Pass by Pass |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-08-23 | 2014-08-07 12:07 | -16 | 2014-07-24 11:04 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Adv 259A was not sprayed pass by pass
| 01CV - Civils | Cxxx-NCR-001455 | NCR | BOS LU vent tunnel - Structural Steel out of tolerance |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-08-21 | 2014-08-11 11:13 | -10 | 2014-07-24 15:22 | Civil - Tunnelling | 1500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Cill Beams overall fabricated lengths are 6 & 7mm short respectively. Tolerance is 2mm
| 01CV - Civils | Cxxx-NCR-001456 | NCR | In March 2014 one wagon was underdosed by 1.8 extra% from Hanson with Microsillica |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-09-19 | 2014-08-21 15:02 | -29 | 2014-07-25 15:38 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | In Macrh 2014,1 wagon from was underdosed by 1.8% with microsillica whilst BFI ITP states that the dosing of micosillica must be 3% plus or minus where as that 1 was was 4.8%
| 01CV - Civils | Cxxx-NCR-001457 | NCR | IN May 2014 Shotcrete supplied by Hanson was under and over dosed with Microsillica on a few occasions. |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-08-09 | 2014-07-30 15:40 | -10 | 2014-07-26 12:39 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | In May 2014 shotcrete supplied by was under and overdosed, ITP states that the dosing of Microsillica should be within tolerance of plus or minus 3%.
| 01CV - Civils | Cxxx-NCR-001458 | NCR | SMM - Amber trigger breach between B07LB008-B07LB184 (52 South Molton Street) |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-08-17 | 2014-08-14 15:15 | -3 | 2014-07-28 18:17 | Tunnelling - Tunnelling General | 1000 |  | System Defect | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | A new amber trigger breached at 52 South Molton Street (__s) has been recorded between points B07LB008-B07LB184.
| 01CV - Civils | Cxxx-NCR-001459 | NCR | Milling LCE1 and LCE2 without agreed procedure |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-08-12 | 2014-07-30 15:39 | -13 | 2014-07-29 15:19 | Tunnelling - Linings - Sprayed Concrete | 2000 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Commenced milling of tight areas of primary lining in preparation for regulating without an agreed procedure and agreement with all parties.
| 01CV - Civils | Cxxx-NCR-001460 | NCR | TCR S2 Adit Misalignment |  | Contr | BFK |  |  | 2014-08-13 | 2014-07-31 11:49 | -13 | 2014-07-30 08:45 | Tunnelling - Tunnelling General | 5000 |  | Design | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The SGI segments within the running tunnel are to coincide with the planned position of the S2 adit opening in the Tottenham Court Road Eastern Ticket Hall. The allowable tolerance for the tunnel position was specified in drawing Cxxx-OVE-C4-DDL-CR001_Z-21160 as being + 300mm. Based on the existing tunnel ring positions and the As Built position of the TCR ETH box they are out by 321mm. The western SGI opening’s centre is roughly at chainage 5013.185m which corresponds to the first opening Ch. 5013.013 (172mm difference, within tolerance). However, it should be noted that elevation ‘A’ on drawing Cxxx-OVE-C4-DDL-CR001_Z-21160 is incorrect. It appears to assume the SGI rings are tapered which they are not. The drawing shows: The start of SGI segments is shown as chainage 5013.013 – dimension 1.600 = 5011.413m The end of SGI segments is shown as chainage 5019.132 + dimension 1.600 = 5020.732m Therefore, length of SGI (5020.732-5011.413) = 9.319m As SGI rings are 1.6m long, the nearest number of complete rings would be 6 (or 9.6m). Error in design = 281mm. This would account for the difference in position.
| 01CV - Civils | Cxxx-NCR-001461 | NCR | BOS WTH S2 adit timber heading under-excavation |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-08-18 | 2014-08-15 16:55 | -3 | 2014-08-04 17:12 | Tunnelling - Excavation - Hand | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Under-excavation of the timber heading opening adjacent to the 1315mm adit pier will lead to a reduction in the extent of the concrete pier. As can be seen in the attached sketch, the area of concrete missing is away from the adit opening and therefore shall not be used in composite action to support the ground. This leads us to propose that the area of adit in question can be left out, avoiding the need for additional heading work, which would increase the risk.
| 01CV - Civils | Cxxx-NCR-001463 | NCR | AP7B and AP3E BFK 22 Cast Invert |  | Contr | BFK |  |  | 2014-08-29 | 2014-08-20 09:43 | -9 | 2014-08-01 17:09 | Tunnelling - Linings - In-situ Concrete | 5500 |  | Material | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | The compressive strength at 28 days from the cast in situ invert (mix 22) in AP7B and AP3E was below specification. (See attached Laboratory Test Results)
| 01CV - Civils | Cxxx-NCR-001464 | NCR | PTE AP3E thickening cold joint |  | Contr | BFK |  |  | 2014-08-19 | 2014-08-13 17:11 | -6 | 2014-08-05 01:07 | Tunnelling - Linings - Sprayed Concrete | 4500 |  | Workmanship | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | Prior to spraying the invert thickening on AP3E, a cold joint was identified longtidinally within the crown thickening at the horizontal joint between crown and invert.
| 01CV - Civils | Cxxx-NCR-001465 | NCR | BOS WTH - S2 Timber Heading Propping Frame Fixing Detail |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-08-29 | 2014-08-21 14:41 | -8 | 2014-08-07 13:15 | Tunnelling - Excavation - Hand | 1500 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A number of the steel props installed between the waler beams to support the timber headings were fixed with fillet welds instead of the end plate and bolt detail that was specified.
| 01CV - Civils | Cxxx-NCR-001466 | NCR | Compressive Strength Test Carried out after 6 days instead of 1 & 3 days at WTH CP1. |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-09-05 | 2014-08-29 13:24 | -7 | 2014-08-06 11:21 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Compressive Strength Test Carried out after 6 days instead of 1 & 3 days at WTH CP1. Test reports presented in 31/07/14 SRG meeting.
| 01CV - Civils | Cxxx-NCR-001467 | NCR | BOS No Engineer Present to supervise the leak sealing injections works |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-09-06 | 2014-08-27 17:40 | -10 | 2014-08-07 11:31 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | 28/07/14 BOS Crack Leak sealing- No engineer supervising the leak sealing injection works. Holes were drilled, packers installed and resin injectted into lining in PTE between CP07 & CP05 without a form 98 being filled in at the time
| 01CV - Civils | Cxxx-NCR-001468 | NCR | PTW 1 Crown Waterproofing Pinholes |  | Contr | BFK |  |  | 2015-01-16 | 2015-01-07 09:43 | -9 | 2014-08-07 18:11 | Tunnelling - Tunnelling General | 4500 |  | Material | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | PTW 1 from chainages 195 to 150 has been sprayed with 3 layer of masterseal and inspected by , Cxxx and CRL reps. Collectively we are unable to confirm a good coverage of the end of the holes as we are unable to see inside.
| 01CV - Civils | Cxxx-NCR-001469 | NCR | TaM T1-11 installed out of design deviation tolerance (Permeation Grouting) |  | Contr | BFK |  |  | 2014-08-28 | 2014-08-18 13:53 | -10 | 2014-08-07 16:12 | Geotechnical Engineering - Compensation Grouting | 4500 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | External Phenomenon - Other | Completed |  | TaM T1-11 was setup to the correct drilling angle of -7.14° but due to the drilling rigs shaft platform not maintaining its set level. This caused the shaft platform to creep downwards and the drilling angle of -7.14° increased to +1.1°. The TaM was installed out of design deviation tolerance and does not reach its design location to the treatment area.
| 01CV - Civils | Cxxx-NCR-001470 | NCR | TaM Pipe (T1-12) disconnected During installation works (Permeation Grouting) |  | Contr | BFK |  |  | 2014-08-28 | 2014-08-18 13:54 | -10 | 2014-08-07 16:18 | Geotechnical Engineering - Compensation Grouting | 4500 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | External Phenomenon - Other | Completed |  | TaM T1-12 separated at 8m inside the casing on 23.07.14 dayshift. This occurred whilst extracting the casings from the hole. The casings are installed by anticlockwise rotation or left hand and the TaM pipe is installed by clockwise rotation or right hand. When extracting the casings with Left hand rotation this caused the TaM to unscrew and become separated in the casing. All casings have been removed and the separated TaM at 8m remains in the ground.
| 01CV - Civils | Cxxx-NCR-001471 | NCR | TaMs T1-01 & T1-05 Pipes disconnected during installation works (Permeation Grouting) |  | Contr | BFK |  |  | 2014-08-28 | 2014-08-18 13:55 | -10 | 2014-08-07 16:31 | Geotechnical Engineering - Compensation Grouting | 4000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | TaMs T1-01 & T1-05 separated at 8m inside the casing during nightshift works. This occurred whilst extracting the casings from the hole. The casings are installed by anticlockwise rotation or left hand and the TaM pipe is installed by clockwise rotation or right hand. When extracting the casings with Left hand rotation this caused the TaM to unscrew and become separated in the casing. All casings have been removed and the separated TaM at 8m remains in the ground.
| 01CV - Civils | Cxxx-NCR-001472 | NCR | Badly Repaired Regulating Layer in 2a (LCE2) Secondary Lining |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-10-24 | 2014-10-14 12:57 | -10 | 2014-08-07 17:38 | Tunnelling - Linings - Sprayed Concrete | 2000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Bad patch repairs to regulating layer at CH:30 to 35 4 o clock to 11 o clock
| 01CV - Civils | Cxxx-NCR-001473 | NCR | Failure to spray test panels during regulating works in section 3B(CH3) Secondary Lining Works |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-09-06 | 2014-09-01 11:47 | -5 | 2014-08-07 17:44 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Failure to spray test panels during regulating works in section 3B(CH3) Secondary Lining Works This panel was to check the early age strength for safe access
| 01CV - Civils | Cxxx-NCR-001474 | NCR | PTE Adv 292A Not Sprayed Pass by Pass |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-09-19 | 2014-09-16 16:24 | -3 | 2014-08-08 16:32 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | PTE Adv 292A Not Sprayed Pass by Pass
| 01CV - Civils | Cxxx-NCR-001475 | NCR | PTW-Resin spillage over the waterproofing |  | Contr | BFK |  |  | 2014-08-23 | 2014-08-21 14:38 | -2 | 2014-08-09 12:00 | Tunnelling - Tunnelling General | 1500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | In PTW ch 102 there was a spillage of resin over the waterproofing while the corkers where injecting. ( See attached photo)
| 01CV - Civils | Cxxx-NCR-001476 | NCR | Monitoring points sprayed with Masterseal in PTE |  | Contr | BFK |  |  | 2014-08-25 | 2014-08-21 12:49 | -4 | 2014-08-11 13:36 | Tunnelling - Tunnelling General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | NCR raised as Masterseal was sprayed with monitoring points in place in PTE.
| 01CV - Civils | Cxxx-NCR-001477 | NCR | Insufficient number of readings taken for the AP3W chng. 17-18m As-built |  | Contr | BFK |  |  | 2014-08-29 | 2014-08-22 14:33 | -7 | 2014-08-12 13:47 | Tunnelling - Tunnelling General | 1500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | As per the minimum requirement of 1 as-built reading per m2 of tunnel, a minimum of 22 points ought to have been taken for the attached profile. However, only 20 have been taken.
| 01CV - Civils | Cxxx-NCR-001480 | NCR | PTW Invert Adv 98/107 Sprayed inadequately/Not sprayed Pass by Pass |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-09-30 | 2014-09-23 16:22 | -7 | 2014-08-12 12:07 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | PTW Invert Adv 98/107 Sprayed inadequately/Not sprayed Pass by Pass
| 01CV - Civils | Cxxx-NCR-001481 | NCR | PTW Profiles at Ch 63.32/66.37/69.33/68.43 not completed with a minimum of 1shot per m2 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-09-30 | 2014-09-17 16:39 | -13 | 2014-08-12 12:21 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | PTW Profiles at Ch 63.32/66.37/69.33/68.43 not completed with a minimum of 1shot per m2 (Profiles attached)
| 01CV - Civils | Cxxx-NCR-001482 | NCR | Proceeding with Masterseal Waterproofing without NCR closure for regulating layer - CH:30 to 35 4 o clock to 11 o clock |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2014-10-31 | 2014-10-14 12:59 | -17 | 2014-08-12 17:29 | Tunnelling - Linings - Sprayed Concrete | 2000 |  | System Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Masterseal was sprayed without closure of non-conformances relating to the regulating layer substrate, refer to Cxxx-NCR-001472
| 01CV - Civils | Cxxx-NCR-001483 | NCR | Dry Crack in CH3 CH1.5 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-09-12 | 2014-09-01 09:49 | -11 | 2014-08-13 16:13 | Tunnelling - Linings - Sprayed Concrete | 4000 |  | Damaged | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | The crown of CH3 at CH1.5 has a crack between 10 to 30mm wide. The length is from 11 o clock to 2 o clock
| 01CV - Civils | Cxxx-NCR-001484 | NCR | PTW Adv 110 Sprayed inadequately/Not sprayed Pass by Pass |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-09-26 | 2014-09-12 15:14 | -14 | 2014-08-14 14:47 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | PTW Adv 110 Sprayed inadequately/Not sprayed Pass by Pass
| 01CV - Civils | Cxxx-NCR-001485 | NCR | Incorrect Red Trigger Level Alert |  | Crossrail | PDP | BOS - Bond Street Station (West) |  | 2014-09-19 | 2014-09-08 11:09 | -11 | 2014-08-14 15:42 | Surveying - Instrumentation and Monitoring | 2500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | A red trigger was reported between D07LB021 and D07LB022 in front of 21 Hanover Square (Brook Street Façade). The Prism point on the wall did not correspond with the __ likewise the closest HLC (HS2103M). re-surveying the points (and its surrounding points) and the same result was obtained. Cxxx were contacted as per the relevant procedures and asked to confirm if their system was reporting the same. Cxxx reported that they had not had an alert, resurveyed again and found that the survey team had made a mistake and their was no alert.
| 01CV - Civils | Cxxx-NCR-001487 | NCR | BOS SCL Milling works in AP3B has exposed the pile infill reinforcement Waterproofing/secondary lining works |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-09-14 | 2014-08-29 16:15 | -16 | 2014-08-15 08:51 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | BOS SCL Milling works in AP3B has exposed the pile infill reinforcement (photos attached)
| 01CV - Civils | Cxxx-NCR-001488 | NCR | PTE Insufficient profile points taken at Adv 295A/298A |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-09-25 | 2014-09-17 16:40 | -8 | 2014-08-15 09:12 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | PTW Profiles at Adv 295A/298A not completed with a minimum of 1shot per m2 (Profiles attached)
| 01CV - Civils | Cxxx-NCR-001489 | NCR | Cores tested at 4 days |  | Contr | BFK |  |  | 2014-08-31 | 2014-08-27 17:41 | -4 | 2014-08-17 12:13 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Samples 661 and 662, PTE Adv 312 and 314. 1 day cores were tested late at at 4 days
| 01CV - Civils | Cxxx-NCR-001490 | NCR | 28 Day Cores |  | Contr | BFK |  |  | 2014-09-20 | 2014-09-12 15:32 | -8 | 2014-09-06 12:03 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Sample 574, Thickening PTW/VEW Invert, Only 3 cores were tested at 28 days, ITP states 6
| 01CV - Civils | Cxxx-NCR-001491 | NCR | 28 day Cores tested late |  | Contr | BFK |  |  | 2014-09-07 | 2014-08-28 14:17 | -10 | 2014-08-17 14:24 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Sample 593, PTE Adv 170, tested 30 days Sample 600, PTE Adv 183, tested at 31 days
| 01CV - Civils | Cxxx-NCR-001492 | NCR | Cores tested at 4 days |  | Contr | BFK |  |  | 2014-09-07 | 2014-08-28 14:19 | -10 | 2014-08-17 15:03 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Sample 613, PTE Adv. 209. Cores were taken on weekend but not collected until monday (4days).
| 01CV - Civils | Cxxx-NCR-001493 | NCR | Non-Conformance of Tiltmeters - TCR & BOS General |  | Contr | BFK |  |  | 2014-09-02 | 2014-08-29 16:37 | -4 | 2014-08-19 13:04 | Surveying - Instrumentation and Monitoring | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Following a recent review of the installed Tiltmeters at the above locations, it was noted that the measuring range for the installed instruments is out of spec. Technical Requirements KX10.3219 c) Tiltmeter (Remotely read) i) The tiltmeter shall have the following requirements: • measuring range: ±10 degrees or greater; • operating temperature: 0°C to +50°C; • accuracy: ±0.05% full scale ; • resolution: 0.01% full scale; • repeatability: ±0.01% full scale. Existing Condition/ Non conformance as the measuring range for the Instruments installed is +/-5 degrees.
| 01CV - Civils | Cxxx-NCR-001494 | NCR | AP2W Cast in situ curing |  | Contr | BFK |  |  | 2014-10-31 | 2014-10-17 13:19 | -14 | 2014-08-21 13:52 | Tunnelling - Tunnelling General | 1500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | There was lack of evidence of curing the invert in AP2W although it has been cured.See attached Secondary Lining ITP section B7.2 state curing of secondary lining at 4,6,8,12 hours as per KT20.3225. To demonstrate that the cast in situ concrete has the correct strength see attached EX 0637-28 compressive strength report complying with what is required in the section B.2.4 of the Concrete Testing ITP also attached. See attached result from AP2W invert. Please note that there is a mistake with the date and site (from the lab)
| 01CV - Civils | Cxxx-NCR-001495 | NCR | Milling works for secondary linining had been carried out by BFK at PTE (Ch 70 to 80) AP3A area |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-09-19 | 2014-09-11 16:14 | -8 | 2014-08-20 13:52 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | milling works had been carried out by at PTE (Ch 70 to 80) AP3A area without following procedures and without informing Senior SCL Engineers.
| 01CV - Civils | Cxxx-NCR-001496 | NCR | Failure to spray test panel immediately after regulating is finished |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-09-04 | 2014-08-21 17:18 | -14 | 2014-08-21 08:43 | Tunnelling - Tunnelling General | 750 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | After completion of spraying regulating layer in crown, the lead miner did not instruct the nozzleman to immediately spray the panel after request from the engineer.
| 01CV - Civils | Cxxx-NCR-001497 | NCR | BOS Secondary Lining Masterseal has been sprayed over monitoring targets |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-10-31 | 2014-10-20 18:12 | -11 | 2014-08-22 09:46 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Contamination | Completed |  | It has been observed that masterseal has been sprayed over monitoring targets. raised this NCR on CRL observation report (see attached). Please also find some pictures for before and after making good of that area. propose to close this NCR. The location of the effected area is also attached on the sketch see attached. Robert I have re-checked and the pictures attach to this NCR are the right ones
| 01CV - Civils | Cxxx-NCR-001498 | NCR | PTW Advance 68 @ BOS only 5 core compressive results received at 28 days. |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-10-21 | 2014-09-03 18:18 | -48 | 2014-08-22 13:53 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | For PTW advance 68, test house issued results of only 5 cores rather than ITP stipulation of 6 cores.
| 01CV - Civils | Cxxx-NCR-001499 | NCR | VD3 Advance 5 not Sprayed Pass by Pass BOS ETH |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-09-21 | 2014-09-15 17:13 | -6 | 2014-08-22 14:23 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | VD3 Adv 5 Not Sprayed Pass by Pass
| 01CV - Civils | Cxxx-NCR-001500 | NCR | Masterseal sprayed without waiting for 24hrs after regulating/grout in LCE2 Sump secondary lining works |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-11-29 | 2014-11-25 15:14 | -4 | 2014-08-22 16:31 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Masterseal sprayed without waiting for 24hrs after regulating/grout in LCE2 Sump secondary lining works
| 01CV - Civils | Cxxx-NCR-001502 | NCR | TCR AP3E undersprayed profiles |  | Contr | BFK |  |  | 2014-09-05 | 2014-08-28 14:25 | -8 | 2014-08-22 18:10 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Advances 1 to 3 of the PTE to AP3E tie-in appear to be undersprayed in compared to the tolerance value of 150mm (between 200-300mm) targetted for the AP3E tunnel. Due to over excavation, there is still sufficient thickeness in the primary lining. (see attached profiles)
| 01CV - Civils | Cxxx-NCR-001503 | NCR | LP9 ITP not approved |  | Contr | BFK |  |  | 2014-09-05 | 2014-08-29 14:23 | -7 | 2014-08-22 18:14 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Verbal communication problem | Completed |  | Works commenced to install the LP9 steel to be sprayed within the AP8 thickening prior to the ITP being signed off. The ITP had been reviwed by CRL but comments were being addressed and final sign off hadn't taken place before works commenced. An activity plan was in place.
| 01CV - Civils | Cxxx-NCR-001504 | NCR | VEW advance length over excavation |  | Contr | BFK |  |  | 2014-09-06 | 2014-08-29 14:25 | -8 | 2014-08-23 12:27 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Due to a short leading edge on the previous advance, on advance 21 the excavation appeared to be approximtaly 1.75m in the crown section between the region of approximately 11-1 o'clock where the allowable for the lining thickness of 250mm should be 1.3m. The shoulder to axis section was within tolerance.
| 01CV - Civils | Cxxx-NCR-001505 | NCR | Hollow areas around LCE Sump BOS ETH |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-09-21 | 2014-09-12 16:17 | -9 | 2014-08-22 18:39 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Hollow areas were detected during hammer testing around LCE sump
| 01CV - Civils | Cxxx-NCR-001506 | NCR | PTE Milling prior to secondary lining works |  | Contr | BFK |  |  | 2014-09-08 | 2014-08-29 14:28 | -10 | 2014-08-25 08:51 | Tunnelling - Linings - Sprayed Concrete | 2500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Milling undertaken in PTE ch.66 to remove up to 100mm prior to approval to mill signed off. Works supervised by shift engineer to control. Proof drilling undertaken and sufficient thickness remains.
| 01CV - Civils | Cxxx-NCR-001508 | NCR | AP2W Monitoring Targets |  | Contr | BFK |  |  | 2014-09-09 | 2014-08-29 14:32 | -11 | 2014-08-26 17:58 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Targets removed without prior approval of SRG.
| 01CV - Civils | Cxxx-NCR-001509 | NCR | PTW Pump Rate Secondary Lining |  | Contr | BFK |  |  | 2014-09-22 | 2014-09-09 16:11 | -13 | 2014-08-25 13:54 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | While spraying Secondary Lining in PTW it was observed 17 %pump rate. Above the value stated in RAMS Cxxx--C4-GMS-CRT00_ST005-50274
| 01CV - Civils | Cxxx-NCR-001510 | NCR | Cast Invert Cleaning |  | Contr | BFK |  |  | 2014-09-23 | 2014-09-10 16:09 | -13 | 2014-08-25 14:00 | Tunnelling - Tunnelling General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | NCR raised due to using airlines rather than water to clean cast in situ invert sides as described in RAMS Cxxx--C4-GMS-CRT00_ST005-50274 section C.1.3.
| 01CV - Civils | Cxxx-NCR-001511 | NCR | Curing Secondary Lining 148-145 |  | Contr | BFK |  |  | 2014-10-24 | 2014-10-09 12:43 | -15 | 2014-08-26 10:41 | Tunnelling - Tunnelling General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | The Secondary Lining bay 148-145 wasn't cured with water at 8 hours
| 01CV - Civils | Cxxx-NCR-001512 | NCR | BOS PTW RMS070 not read at required time interval |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-09-23 | 2014-09-09 16:20 | -14 | 2014-08-25 15:32 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | BOS PTW RMS070 monitoring was not carried out at 24hrs but at 36hrs (23/08/2014).
| 01CV - Civils | Cxxx-NCR-001513 | NCR | PTE Adv 325 invert not sprayed Pass by Pass |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-09-19 | 2014-09-17 16:42 | -2 | 2014-08-26 09:51 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | PTE Adv 325 invert not sprayed Pass by Pass
| 01CV - Civils | Cxxx-NCR-001514 | NCR | Early Age Testing Frequency - VEW |  | Contr | BFK |  |  | 2014-09-16 | 2014-08-29 14:37 | -18 | 2014-08-26 16:51 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Correct frequency of early age testing not maintained during construction of VEW tunnel, gap greater than 6 advances between ad 17 and 24.
| 01CV - Civils | Cxxx-NCR-001515 | NCR | VEW Installation of Monitoring Points |  | Contr | BFK |  |  | 2014-10-06 | 2014-09-29 16:33 | -7 | 2014-09-22 08:40 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Targets not installed in advance 32 of VEW as defined by RESS.
| 01CV - Civils | Cxxx-NCR-001516 | NCR | VEW standby by shotcrete |  | Contr | BFK |  |  | 2014-09-30 | 2014-09-23 16:23 | -7 | 2014-08-27 09:11 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | It was found that not enough shotcrete was held on site to seal the face for advance 37 (invert). Next batch arrived on site as excavation was completed. Dry shotcrete and hand spraying equipment was available in the vicinty of the VEW works required.
| 01CV - Civils | Cxxx-NCR-001518 | NCR | PTW 3 Waterproof Leaks |  | Contr | BFK |  |  | 2014-09-19 | 2014-09-17 16:48 | -2 | 2014-08-27 17:23 | Tunnelling - Linings - Sprayed Concrete | 3500 |  | Workmanship | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Pin hole leaks in waterproofing in PTW3 at chainages: - ch36.6 - ch39.9 - ch42.4 - ch43.2
| 01CV - Civils | Cxxx-NCR-001519 | NCR | PTW Invert Core Holes |  | Contr | BFK |  |  | 2014-12-31 | 2014-12-17 16:18 | -14 | 2014-09-08 09:01 | Tunnelling - Linings - In-situ Concrete | 3500 |  | Workmanship | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | Cores taken in the cast insitu invert in PTW, ch.118 were backfilled with SFR concrete rather than grout.
| 01CV - Civils | Cxxx-NCR-001520 | NCR | PTE crack register |  | Contr | BFK |  |  | 2014-09-24 | 2014-09-10 16:08 | -14 | 2014-08-27 17:30 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | PTE crack regsiter was not updated monthly as agreed (frequency a local agreement and not defined by KT20). However, all reviews of the crack register, additions as required and subsequent approvals for secondary lining have been signed off by CRL and Cxxx.
| 01CV - Civils | Cxxx-NCR-001521 | NCR | PTE 2 Waterproofing Leak |  | Contr | BFK |  |  | 2014-09-30 | 2014-09-26 16:04 | -4 | 2014-08-27 17:33 | Tunnelling - Linings - Sprayed Concrete | 2500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Pin hole leak at chainage 76 in PTE 2.
| 01CV - Civils | Cxxx-NCR-001522 | NCR | PTE 2 Hammer Testing (Invert) |  | Contr | BFK |  |  | 2014-09-17 | 2014-09-03 18:11 | -14 | 2014-08-27 17:36 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Hammer Testing undertaken by at PTE 2 Invert chainage 82-86, however this was not witnessed by CRL/Cxxx.
| 01CV - Civils | Cxxx-NCR-001523 | NCR | Filling LP9 steel gap with grout |  | Contr | BFK |  |  | 2014-11-14 | 2014-11-11 23:23 | -3 | 2014-08-27 19:52 | Tunnelling - Tunnelling General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | To guarantee that there was no gap between the LP9 jamb frame and the primary lining of AP8, a shutter was erected after the installation of the jamb frame to grout the gap. The gap was 120 mm on a localized area at the top of the jamb frame. According to the specifications of Five Star Grout, the maximum thickness allowed to apply is 100mm. See sketch below showing extent of area with more than 100 mm thickness.
| 01CV - Civils | Cxxx-NCR-001524 | NCR | Early Age Testing Frequency - VEW |  | Contr | BFK |  |  | 2014-09-18 | 2014-08-29 14:39 | -20 | 2014-08-28 10:55 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Gap of 7 advances between tests at adv 29 and adv 36.
| 01CV - Civils | Cxxx-NCR-001526 | NCR | Spraying of tunnel junction cast invert at AP3B and LCE1/2 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-09-12 | 2014-09-08 11:21 | -4 | 2014-08-29 00:15 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | The cast invert at the tunnel junction from LCE to AP3B has been sprayed using mix 17.2 leaving 50mm shy for Mix 21
| 01CV - Civils | Cxxx-NCR-001527 | NCR | Shape of lining joint at LCE2 CH11m not correct on LHS while building shotcrete out for secondary lining |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-10-31 | 2014-10-20 16:35 | -11 | 2014-08-29 01:03 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | It was observed the secondary lining joint was not being built out correctly during the dayshift continuing onto the nightshift handover. When the nightshift took over, they completed the lining while the shotcrete was still "green" and rectified the joint. This was done without any damage to waterproofing. The joint was sprayed in and the secondary lining completed. The lining has been completed without issue and the area handed over, no cores required.
| 01CV - Civils | Cxxx-NCR-001528 | NCR | LCE2 Panel Sprayed against Water proofing CH23 2a area |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-11-07 | 2014-10-27 12:11 | -11 | 2014-08-29 14:22 | Tunnelling - Linings - Sprayed Concrete | 4500 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A test panel was sprayed for secondary lining works in LCE2 (2a) area. The panel was leaning against fully cured masterseal at CH23 knee level RHS adjacent to the spraying activity.
| 01CV - Civils | Cxxx-NCR-001529 | NCR | SMM - Amber Trigger breach in 24, South Molton Street (West) between B07LB334-333. |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-09-12 | 2014-08-29 16:44 | -14 | 2014-08-29 14:55 | Surveying - Instrumentation and Monitoring | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Previous Construction - Other | Completed |  | A new Amber Trigger breached between B07LB334-B07LB333, 24 South Molton Lane __s.
| 01CV - Civils | Cxxx-NCR-001531 | NCR | TCR - AP3E - damage to waterproofing at invert |  | Contr | BFK |  |  | 2014-10-31 | 2014-10-14 13:04 | -17 | 2014-09-03 15:05 | Tunnelling - Tunnelling General | 9000 |  | Damaged | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The AP3E tunnel was used for secondary lining trials. As a result the tunnel was regulated and waterproofed and invert was cast prior to the breakthrough. Following completion of the breakthrough, have cleaned the invert and found out that the waterproofing in the invert was damaged close to the cast invert concrete. in the worst case scenario, there was only 10mm of previously applied Masterseal was available to lap onto. The damage was photographed (see attached).
| 01CV - Civils | Cxxx-NCR-001532 | NCR | Overlapping of waterproofing with regulating layer at PTE ch. 122 |  | Contr | BFK |  |  | 2014-09-22 | 2014-09-09 13:29 | -13 | 2014-09-01 15:54 | Tunnelling - Linings - Sprayed Concrete | 2500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Overlapping waterproofing with regulating layer at PTE ch.122
| 01CV - Civils | Cxxx-NCR-001533 | NCR | PTE Thickening Works Ch 205 sprayed with PP fibres instead of steel fibres |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-10-01 | 2014-09-12 15:39 | -19 | 2014-09-01 17:43 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | PTE Thickening Works Ch 205 sprayed with PP fibres instead of steel fibres
| 01CV - Civils | Cxxx-NCR-001534 | NCR | Missing Form 50 for AP3E Primary Lining Advance 1-4 and Advance 9 |  | Contr | BFK |  |  | 2014-10-03 | 2014-09-26 12:49 | -7 | 2014-09-04 13:28 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | AP3E tie-in missing form 50 for spraying of primary lining advance 1-4 and advance 9
| 01CV - Civils | Cxxx-NCR-001535 | NCR | TCR-AP7B-Addendum to NCR Cxxx-NCR-001389 - Lack of Fire proofing thickness |  | Contr | BFK |  |  | 2015-04-27 | 2015-04-21 11:17 | -6 | 2014-09-04 16:17 | Tunnelling - Linings - Sprayed Concrete | 25000 |  | Incorrect Installation | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Further to the close out of Non conformance report Cxxx-NCR-001389, it became apparent that adequate information was not attached in this NCR report. The original NCR cannot be reopened hence it was decided to raise this NCR and complete the required records to close out this defect.
| 01CV - Civils | Cxxx-NCR-001536 | NCR | PTE Advance 322A, only 4 core results submitted @ 1 days and advance 324A results were outside window of 1 to 3 days in the month of August @ BondStreet. |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-09-18 | 2014-09-12 16:04 | -6 | 2014-09-04 17:49 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | At PTE advances 322a only 4 cores results @ 1 day and 324a core result was outside 1 to 3 day window. ITP requires 6 cores and compressive results to be within 1 to 3 days @ 1 day.
| 01CV - Civils | Cxxx-NCR-001537 | NCR | Apprentice nozzleman spraying permanent works unsupervised |  | Crossrail | XRL |  |  | 2014-10-24 | 2014-10-15 16:57 | -9 | 2014-09-05 09:22 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not trained for the work being performed | Completed |  | Nozzleman spraying permanent works (primary lining) in VEW. At the time of receiving the latest SCL TCR Compentecy Matrix (attached) the Nozzleman had sprayed 10no advances according to the F50 forms provided (attached). This does not comply with KT20.2107 Site Personnel Requirements b) and c), and also does not comply with the SCL Nozzleman Assessment and Training Plan which states "Trainee Nozzleman (Apprentice) is not allowed to spray permanent works."
| 01CV - Civils | Cxxx-NCR-001538 | NCR | Cuiring not marked on checksheet for 8 & 12hrs for secondary lining PTW Ch. 83 to 80 |  | Contr | BFK |  |  | 2014-10-03 | 2014-10-02 10:33 | -1 | 2014-09-05 14:38 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | During a surveillance on the 20/8/14 it was observed that on form 88 for PTW Ch. 83 to 80 the curing has not been marked as done for 8 & 12hrs.
| 01CV - Civils | Cxxx-NCR-001539 | NCR | Invert slab in PTE (Ch.100-112) poured without completing remedial works to waterproofing |  | Crossrail | XRL |  |  | 2014-09-26 | 2014-10-20 16:13 | 24 | 2014-09-05 15:55 | Tunnelling - Linings - In-situ Concrete | 10000 |  | Supervision/Management | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Pre-pour witness check carried out by CRL and Cxxx identified areas of waterproofing within the pour area which had several holes / areas of damage, and two areas with suspected insufficient thickness. The holes would have required patch repairing and a Shore A hardness of 30 confirmed prior to pouring. The two sections with suspected insufficient thickness were approx. 150mm x 1.25m in size, and had previously been repaired (hardness was not a concern). The lap to the adjacent waterproofing was insufficient and there was a concern that the repair thickness was insufficient (<3mm) as the 'grey' of the underlying concrete could be seen. Observations were discussed with the Shift Manager however the decision was made by to pour the bay.
| 01CV - Civils | Cxxx-NCR-001540 | NCR | Curing Not Done properly 2A area as per Cast in Situ Checksheets |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-02-23 | 2015-02-13 10:55 | -10 | 2014-09-05 17:23 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Curing Not Done properly 2A area as per Cast in Situ Checksheets. Check sheets attached Cores have been taken for testing awaiting results from lab
| 01CV - Civils | Cxxx-NCR-001541 | NCR | PTE invert slab ch.141-153 poured without sufficient curing of waterproofing |  | Crossrail | XRL |  |  | 2014-11-14 | 2014-10-13 09:16 | -32 | 2014-09-08 09:31 | Tunnelling - Linings - In-situ Concrete | 8000 |  | Supervision/Management | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | PTE invert waterproofing ch.141-153 was shore tested at ~21:00 (avg. 21.5) and ~04:00 (avg. 35). At this point CRL and Cxxx advised that proceeding with pouring the invert slab is not in accordance with approved documentation and may result in significant re-work. made the decision to commence the pour which was complete ~06:30. Masterseal waterproofing requires a Shore A hardness test value of 50 prior to secondary lining application (in accordance with RAMS Cxxx--C4-GMS-CRT00_ST005-50267 and ITP Cxxx--C4-ITP-CRT00_ST005-50112).
| 01CV - Civils | Cxxx-NCR-001542 | NCR | VWW - Adv 16, Early Age Strength panel data misplaced |  | Contr | BFK |  |  | 2014-09-29 | 2014-09-19 13:08 | -10 | 2014-09-08 11:34 | Tunnelling - Tunnelling General | 1500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | As discussed in the SRG, an EAS panel was sprayed for Adv 16 and tested accordingly. The records for this data has been misplaced and as a consequence, an EAS panel ought to have been sprayed for Adv 17 however this did not happen. It has since been agreed in the SRG that a panel be sprayed for Adv 22.
| 01CV - Civils | Cxxx-NCR-001543 | NCR | Monthly Tests |  | Contr | BFK |  |  | 2014-11-13 | 2014-10-27 10:33 | -17 | 2014-10-23 17:01 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | KT20 table KT20-06 states that monthly test are required for each source of concrete used is the works. RFI 1080 has since been raised which now states that monthly tests are required when over 75m3 is used from the second source. In December 2013, our main source was -Silvertown, towards the end of the month the MCR for Vic Deep2 was approved and began using this plant as the source for concrete. No monthly tests were carried out for -Vic Deep2 during December 2013.
| 01CV - Civils | Cxxx-NCR-001544 | NCR | No approval to spray PTE Ch 82-88 |  | Contr | BFK |  |  | 2014-09-30 | 2014-09-12 16:37 | -18 | 2014-09-09 11:40 | Tunnelling - Tunnelling General | 1500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | In PTE Invert from Ch 82 to 88 it has been sprayed with out an approval to spray in place. The required information was gathered but wasn't presented to Cxxx and CRL.
| 01CV - Civils | Cxxx-NCR-001545 | NCR | SMM - unsurveyed manual points |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-10-17 | 2014-10-01 11:07 | -16 | 2014-09-09 13:05 | Surveying - Instrumentation and Monitoring | 1500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | A number of points along South Molton street area have not been read as per agreed monitoring frequency; the area was last read on 30/08/2014 and due 05/09/2014. It was planned and discussed in the SRG 05/09/2014 as a reminder and noted that the area in particular is to be picked up ahead of grout jacking pass for CP1&3 excavations.
| 01CV - Civils | Cxxx-NCR-001546 | NCR | PTE Thickening cores crushed @ 5 days in September rather than within 1-3 day window. |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-09-23 | 2014-09-12 16:45 | -11 | 2014-09-09 13:01 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | PTE Thickening cores crushed @ 5 days rather than ITP required 1 to 3 days.
| 01CV - Civils | Cxxx-NCR-001547 | NCR | TCR WTH North Box — Blinding to Base Slab |  | Contr | BFK |  |  | 2014-09-23 | 2014-09-25 17:09 | 2 | 2014-09-09 16:22 | Structural Engineering - Concrete Member | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | As-built survey (attached) of blinding underneath raft slab is out of tolerance. Item B22b of ITP (referenced) specifies 112.820 +0 / −20mm, while as-built survey shows maximum +13mm and minimum −19mm compared to design.
| 01CV - Civils | Cxxx-NCR-001548 | NCR | TCR WTH North Box — Wire Saw Cutting of Partition Dwall |  | Contr | BFK |  |  | 2014-09-23 | 2014-09-11 11:33 | -12 | 2014-09-09 19:33 | Structural Engineering - Reinforcement | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | As-built survey (attached) of wire saw cutting of partition Dwall is out of tolerance. Item B23b of the ITP (referenced) specifies 114.270 +/- 20mm, while as-built survey varies from a maximum of +76mm to a minimum of -7mm. All Dwall concrete in this area was removed by hydro-demolition or drill and burst, leaving the Dwall rebar protruding into the raft slab. Even at its highest point of 114.346, this rebar is well within the slab and does not encroach on the minimum cover zone (top of slab 114.620).
| 01CV - Civils | Cxxx-NCR-001550 | NCR | TCR WTH North Box — Slump of Concrete in Base Slab |  | Contr | BFK |  |  | 2014-09-24 | 2014-09-25 17:23 | 1 | 2014-09-10 15:29 | Structural Engineering - Concrete Member | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | ITP for the base slab specifies S3 slump, which it states to be 100–150mm; however, according to the MCR the concrete mix is designed for an S4 slump (150–230mm according to BS 8500-1:2006+A1:2012 Table B.1) on the basis of it being pumped. The actual slump test results are attached, both as a table and histogram, and do not 100% comply with either class. They vary from 100 to 240mm with the majority lying between 150 and 200mm.
| 01CV - Civils | Cxxx-NCR-001551 | NCR | BACKFILLING OF PERMEATION GROUTING TaM |  | Contr | BFK |  |  | 2014-10-31 | 2014-11-27 16:06 | 27 | 2014-09-10 12:47 | Geotechnical Engineering - Supported Excavations | 4000 |  | Damaged | Use As-Is | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | Upon completion of Permeation grouting, the following TaM’s will not be able to backfill with grout over the full length as below 1. TaM ref. T1-1 (01) installed to 20m and separated after 8m approx. from shaft – TaM Abandoned. 2. TaM ref. T1-5 (03) installed to 24.8m and separated after 5m approx. from shaft – TaM Abandoned. 3. TaM ref. T1-12 (12) installed to 25.6m and separated after 8m approx. from shaft – TaM Abandoned. 4. TaM ref. T3-4 (38) installed to 18m and separated after 8m approx. from shaft – TaM Abandoned. 5. TaM ref. T3-6 (32) installed to 24.2m and Tam blocked with packer & grout at 4m approx. from the shaft
| 01CV - Civils | Cxxx-NCR-001552 | NCR | Damaged to Invert Masterseal in PTE Ch30 (2A) |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-10-31 | 2014-10-15 13:37 | -16 | 2014-09-10 15:12 | Tunnelling - Linings - Sprayed Concrete | 7500 |  | Supervision/Management | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Damaged to Invert Masterseal in PTE Ch30 (2A). Pictures attached for the damaged area Please receive approved MCR __ 550MI. propose to close this NCR
| 01CV - Civils | Cxxx-NCR-001553 | NCR | TCR WTH North Box — Hydro-Demolition of Partition Dwall |  | Contr | BFK |  |  | 2014-10-10 | 2014-10-03 16:29 | -7 | 2014-09-10 15:59 | Structural Engineering - Concrete Member | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | After the final wire saw cut of the partition Dwall, the remaining concrete was removed by hydro-demolition, and drill and burst to expose the Dwall rebar. The as-built survey of the Dwall concrete after hydro-demolition / drill and burst is out of tolerance. The ITP states 112.82 +/- 75mm, however the as-built survey varies between +80 and -13mm.
| 01CV - Civils | Cxxx-NCR-001555 | NCR | Sample Number SCL 602 (Tunnel LCE 1/2 Fire proofing; CH 12-21) Given wrong mix number on result certificate. |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-09-25 | 2014-09-12 16:48 | -13 | 2014-09-11 10:05 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | LCE Tunnel 1/2 Ch 12 to 21 fire proof spraying results @ 1 day given wrong mix number on results certificate of C17.2 rather than 21. despite the correct mix of 21 being used.
| 01CV - Civils | Cxxx-NCR-001556 | NCR | GS TCR5 Pretreatment records. Flow test fail to comply the specification limits as per ITP |  | Contr | BFK |  |  | 2014-09-25 | 2014-09-25 17:29 | 0 | 2014-09-11 11:06 | Geotechnical Engineering - Compensation Grouting | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | As per the attached field grout testing results for Pre-treatment works in TCR 5 shaft, it’s noted that Flow tests fail to comply the specification limits as per ITP.
| 01CV - Civils | Cxxx-NCR-001557 | NCR | Early Age Testing - PTE |  | Contr | BFK |  |  | 2014-11-12 | 2014-10-21 17:16 | -22 | 2014-10-15 09:50 | Tunnelling - Linings - Sprayed Concrete | 4500 |  | Workmanship | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | ITP states early age testing every 6th advance. During July 2014, there was a gap of 7 advances between, Adv 237 - 244 and gap of 11 between adv 291-303, due to a test being missed at 297.
| 01CV - Civils | Cxxx-NCR-001558 | NCR | CG-GS TCR2 Pre-treatment flow test& cube results fail to comply the specification limits |  | Contr | BFK |  |  | 2014-09-25 | 2014-09-23 16:29 | -2 | 2014-09-11 16:44 | Geotechnical Engineering - Compensation Grouting | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | As per the attached field grout testing results for Pre-treatment works in TCR 2 shaft, its noted that Flow test & cube results fail to comply the specification limits as per material approval reference Cxxx--CLRC-CRT00_ST005-50074 Rev.2
| 01CV - Civils | Cxxx-NCR-001560 | NCR | Insufficient profile points for CH1 Englargement Ch. 6.29 |  | Contr | BFK |  |  | 2014-10-03 | 2014-09-16 16:43 | -17 | 2014-09-12 10:45 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Excavation profile for CH1 enlargement ch. 6.29 has missing profile points between 3 o'clock and 5 o'clock.
| 01CV - Civils | Cxxx-NCR-001561 | NCR | Mistake on ITP BOS Secondary Lining |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-10-12 | 2014-10-09 18:26 | -3 | 2014-09-12 14:29 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Not Defined | Completed |  | Due to a mistake on ITP form 091/098 has not got CRL signature
| 01CV - Civils | Cxxx-NCR-001562 | NCR | Regulating layer sprayed over masterseal in section 2b Ch 6 to Ch 37 secondary lining |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-11-28 | 2014-11-13 20:50 | -15 | 2014-09-12 14:35 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Whilst spraying regulating layer to invert from 4 o clock to 7 o clock position (invert). Regulating layer was oversprayed onto masterseal by 300mm to 600mm in places.
| 01CV - Civils | Cxxx-NCR-001564 | NCR | Simultaneous excavation of CP1 & CP3 and not following RESS BOS Station Cross Passages |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-10-15 | 2014-09-24 13:59 | -21 | 2014-09-15 10:22 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Simultaneous excavation was carried out at CP1 & CP3 BOS station cross passages and RESS was not followed. Specification KT20.3207(g) states "Where two tunnels are simultaneously under construction there shall be at least 25m between the ring closure point of each tunnel". In this instance did not follow this clause and hence this NCR was raised. Also the RESS attached does not say to carry the construction activities simultaneously. In this instance did not follow the RESS as well.Excavation of Advance 1 was started simiultaneously for both CP1/CP3 PTE side which is against specification as both tunnels are not 25m apart. Please find attach briefing sheet. propose to close this NCR as a briefing has been carried out. Also find attach KT20 specifications as well
| 01CV - Civils | Cxxx-NCR-001565 | NCR | Improper preparation of invert substrate in section 2c, prior Waterproofing Layer. |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2014-11-14 | 2014-11-14 09:23 | 0 | 2014-09-18 09:43 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | CRL is raising NCR for improper preparation of the substrate at axis level of the tunnel (at approx 3 and 9 o'clock location - see last attached photo) in section 2c (PTE), that took place on 14-09-2014 DS. Loosen parts from previously sprayed WP layer on crown area (down to the axis level) weren't removed/cleaned prior to the waterproofing application in the invert area (from 3 to 9 o'clock). Photos attached.
| 01CV - Civils | Cxxx-NCR-001566 | NCR | BOS June 2013 - Compressive strength cores do not meet specification requirements |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-10-01 | 2014-10-01 12:30 | 0 | 2014-09-17 14:25 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | During the month of June 2013, 28 day compressive strength cores did not meet the 90 day strength criteria (refer to criterion 1 from Table 13 in BS EN 14487). 90 day cores were not taken for all advances as required. propose to use-as-is as the small number of 90 day (+) cores that were taken in June 2013 were compliant. See attached summary table for compressive strength and test results for 90 day core.
| 01CV - Civils | Cxxx-NCR-001567 | NCR | Damaged to water proofing in CH3 Secondary lining Ch15 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-11-28 | 2014-11-07 11:47 | -21 | 2014-09-19 16:13 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please find attached some pictures where the dowel bar shows damage/leak in invert. Chainage of the effected area under investigation
| 01CV - Civils | Cxxx-NCR-001568 | NCR | Lack of curing in PTE |  | Contr | BFK |  |  | 2014-11-14 | 2014-11-04 15:57 | -10 | 2014-09-20 12:06 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | During days 13-16th of September there was lack of curing on the secondary lining bays. is confident that those bays were cured although we don't have any evidence. The lack of curing does not comply with the Section B7.2 of the ITP of Secondary Lining (attached) and KT20.3225. PTE ch.39-42m 13/09/2014 NS PTE ch.46-49m 14/09/2014 DS PTE ch.42-46m 14/09/2014 NS PTE ch.70-73m 15/09/2014 DS PTE ch.73-76m 15/09/2014 NS PTE ch.76-80m15/09/2014 NS PTE ch.80-83m 16/09/2014 DS PTE ch.119-122m 16/09/2014 NS PTE ch.122-125m 16/09/2014 NS
| 01CV - Civils | Cxxx-NCR-001569 | NCR | Excessive Trimming to SCL Primary Lining in CP4 - between chainage 6.1 & 6.6 |  | Contr | BFK |  |  | 2014-10-31 | 2014-11-03 09:20 | 3 | 2014-09-20 16:26 | Tunnelling - Tunnelling General | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | As a result of the milling works in preparation for the regulating layer, a very localized area (500mm by 500mm) was over trimmed at CP4a & clay was exposed in one spot (see picture attached). Proof drilling works were carried out to establish the area requiring remedial works (see proof drilling records attached). Remedial actions were carried out on the following area: * CP4a - Chainage - between 6.1 & 6.6; - Crown - between 10 o'clock & 11 o'clock; - Remedial actions - break out primary lining, excavate to right profile, install bars to ensure good connection between joints & spray up to the right profile (see RESS attached)
| 01CV - Civils | Cxxx-NCR-001570 | NCR | Insufficient lining thickness in VWW ~ch.18-19 (top heading) |  | Crossrail | XRL |  |  | 2014-11-07 | 2014-10-21 17:21 | -17 | 2014-09-21 10:10 | Tunnelling - Linings - Sprayed Concrete | 4500 |  | Supervision/Management | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As-built profiles for VWW ~ch.18-19 (attached) presented in the SRG had missing sections and areas of underspray. These areas were proof drilled and the results showed insufficient lining thickness (attached). The proof drilling results gave 4no localised areas of insufficient thickness (3no @ 150mm and 1no @ 180mm). The design lining thickness is 250mm.
| 01CV - Civils | Cxxx-NCR-001572 | NCR | Missing details in AP4E Form50s |  | Contr | BFK |  |  | 2014-10-14 | 2014-09-26 12:57 | -18 | 2014-09-23 12:45 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Incomplete F50 forms for AP4E Initial drive. These forms are missing information such as nozzleman names and signatures, spray start and finish times and file names.
| 01CV - Civils | Cxxx-NCR-001573 | NCR | Breakdown of Concrete Pump 2a/2b area Ch 0-26.5 PTE Secondary Lining |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-10-31 | 2014-10-17 13:22 | -14 | 2014-09-22 19:13 | Tunnelling - Linings - Sprayed Concrete | 2500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Break down of concrete pump 2a/2b area.
| 01CV - Civils | Cxxx-NCR-001574 | NCR | BOS PTE Secondary Lining Cast Invert : Crack Inducers Not Installed Every 6m Ch. 0 to 68.5 (2A/2B/2C Areas) |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-01-23 | 2015-01-14 16:29 | -9 | 2014-09-22 18:55 | Tunnelling - Linings - Sprayed Concrete | 6000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Crack inducers were not installed at every 6m in the secondary lining cast invert, PTE Ch. 0 to 68.5, as required by KF10.3207(i).
| 01CV - Civils | Cxxx-NCR-001575 | NCR | Cp9 Timber between the Master Seal and secondary lining Ch 5 to 6 3b area |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-10-31 | 2014-10-27 13:34 | -4 | 2014-09-22 19:17 | Tunnelling - Linings - Sprayed Concrete | 15000 |  | Supervision/Management | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Contamination | Completed |  | Cp9 Timber between the Master Seal and secondary lining Ch 5 to 6 3b area please find attach the pictures before/after the works was made good. propose to close this NCR as the works have been rectified. Specification Ref :KF10.3200 A plan view sketch is also attached
| 01CV - Civils | Cxxx-NCR-001576 | NCR | Concrete temperature not controlled for pour depth greater than 500mm 2a/2b area |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-10-31 | 2014-10-27 13:35 | -4 | 2014-09-22 19:23 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Concrete temperature not controlled for pour depth greater than 500mm in pour 2a/2b area Please find attached graph showing variation of temperature in the third lift of the PTW west headwall. These results are for 2m pour depth with the same concrete mix 27 and under the same conditions as the orignal pour. The maximum temperature reached at the centre of the pour was 69.1°C, less than the limit of 70°C in the specification KF10.3206(j). All cast inverts have shallower depth than this so will not reach a higher temperature.
| 01CV - Civils | Cxxx-NCR-001577 | NCR | Area not washed and cleaned before pour 2a/2b area |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-01-31 | 2015-01-21 12:19 | -10 | 2014-09-22 19:29 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | Area not damp before pour LCE1/2 ch. 2-30 (area 2a/b) as per ITP
| 01CV - Civils | Cxxx-NCR-001578 | NCR | use of hyrib in CH3 No MCR in place secondary lining |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-11-28 | 2014-11-03 09:25 | -25 | 2014-09-22 19:36 | Tunnelling - Linings - Sprayed Concrete | 10000 |  | Documentation and Records | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Contamination | Completed |  | use of hyrib in CH3 No MCR in place secondary lining
| 01CV - Civils | Cxxx-NCR-001580 | NCR | BOS Secondary Lining : Cherry Picker Loading on Slab |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-10-31 | 2014-10-17 13:23 | -14 | 2014-09-23 08:02 | Tunnelling - Linings - In-situ Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | In PTE (chainages approx. 20–80) a cherry picker was found on the cast invert slab, 2 days after pouring but before obtaining cube strength results. No damage to the slab was sustained.
| 01CV - Civils | Cxxx-NCR-001581 | NCR | PTE to AP2E Secondary Lining Junction Steel |  | Contr | BFK |  |  | 2014-10-09 | 2014-09-26 09:32 | -13 | 2014-09-25 18:55 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Supervision/Management | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On the nightshift 21/09/14 during the Secondary Lining steel fixing inspection in AP2E, CRL Field Engineer and Cxxx representative instructed to modify the radial steel position before it could be signed off (a hold point on the ITP). Following these modifications Cxxx, and CRL Field Engineer signed the Sprayed/Poured Concrete Reinforcement Checksheet as “steel OK to spray”. sprayed over the steel in AP2E junction during the nightshift. On the dayshift of the 22/09/14 CRL site manager and Cxxx representative informed that the steel that they were dissatisfied with the steel installation, specifically the lap between the radial steel and crown steel and the changes requested by the CRL field Engineer which left a large gap in the radial bars around the shoulders (see attached pictures). Despite the steel being signed off by the night shift representatives it was stated that the steel could not be accepted as it would be inadequate in performing the structural function required in the way it was fixed. CRL/Cxxx verbally instructed that the steel would have to be modified. Please find attached the original sign off sheet for Sprayed/Poured Concrete Reinforcement Check sheet and the secondary lining meeting minutes.
| 01CV - Civils | Cxxx-NCR-001582 | NCR | PTE East Headwall Masterseal |  | Contr | BFK |  |  | 2014-10-07 | 2014-10-02 13:07 | -5 | 2014-09-23 12:02 | Tunnelling - Linings - Sprayed Concrete | 40000 |  | Workmanship | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Face dowels were installed in the PTE East headwall as part of the formwork design. When spraying the crescent section on the right hand side of the headwall, this lead to overspray on the cast insitu section of the headwall. Where is was not possible to temove overspray without damaging the original masterseal, some of the face dowels in both the heading and invert section of the headwall had to be drilled through the oversprayed section for installation. (See attached picture) Although masterseal was then painted around the dowels and on the oversprayed concrete, it is not possible to overlap fully with the masterseal applied originally applied to the headwall.
| 01CV - Civils | Cxxx-NCR-001583 | NCR | Missing Form50 for AP4E initial drive advance 15 |  | Contr | BFK |  |  | 2014-10-14 | 2014-10-09 15:15 | -5 | 2014-09-23 15:31 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Missing Form50 for AP4E initial drive advance 15
| 01CV - Civils | Cxxx-NCR-001584 | NCR | Drill through to install packers invert 2a Ch20 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-11-28 | 2014-11-14 09:30 | -14 | 2014-09-23 17:12 | Tunnelling - Linings - Sprayed Concrete | 4500 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 2 no steel packers were installed by drilling through secondary lining & waterproofing membrane in invert 2a Ch20. Picture attached for the said area
| 01CV - Civils | Cxxx-NCR-001585 | NCR | Masterseal Thickness at CP7/CP8/CP9/CP10 Junctions |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-12-19 | 2014-12-08 17:05 | -11 | 2014-09-24 09:01 | Tunnelling - Linings - Sprayed Concrete | 15000 |  | Supervision/Management | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Thickness of masterseal at CP7/CP8/CP9/CP10 Junctions is not as per specification (Double layer) Patch test was carried out in the effected area. It was found the thickness in the junctions was less than required 6mm (double thickness) as shown on drawing Cxxx-MMD-C4-DDD-Cxxx_6-00031 Rev C03. This NCR was caused due to engineering error and poor engineering control of spraying operation. has removed all steal that was installed in the affected area. has re-sprayed the area to the required thickness. The rebar has been reinstalled. propose to close this NCR using signed check sheets (will be atatched later). In future propose to maintain engineering presence at all times. A re-briefing/tool box talk will be carried out in this regard(will be attached later). Please also find a plan view showing the location of the area
| 01CV - Civils | Cxxx-NCR-001586 | NCR | TCR WTH -5 and -2 Raft Slab Damaged Earthing Cables |  | Crossrail | PDP |  |  | 2015-02-27 | 2015-02-03 09:44 | -24 | 2014-09-24 08:57 | Civil - Civil Engineering General | 25000 |  | Damaged | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the removal of the protection slab to the -5 and -2 levels the Earthing Cables which protrude from the base slab for extension by Cxxx were damaged. Handover records and photos included within Cxxx--C-RGN-CRT00_ST005-50964 records the fact they were damaged however no NCR was raised. Refer to pages 46, 130 and 196 of the document Cxxx--C-RGN-CRT00_ST005-50964.
| 01CV - Civils | Cxxx-NCR-001587 | NCR | AP8 thickening invert steel |  | Contr | BFK |  |  | 2014-10-09 | 2014-10-09 16:02 | 0 | 2014-09-25 14:08 | Tunnelling - Linings - Sprayed Concrete | 7000 |  | Supervision/Management | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | AP8 primary lining thickening has been installed in two stages. Stage 1 was completed up to chainage 22 in February 2014. On constructiong the stage 2 primary lining thickening, it was realised that some near face invert steel for LP9, which extends into where the stage 1 primary lining thickening was constructed, was not installed. As per Cxxx-MMD-C4-DDD-N105_5-00395, Bar Mark 10, 82no. B12 bars were to be installed at 150mm spacing. Approximately 20no. bars should have been installed during the stage 1 thickening.
| 01CV - Civils | Cxxx-NCR-001588 | NCR | SMM - 20 Hanover Square Draw Wire Data |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-10-31 | 2014-10-13 08:23 | -18 | 2014-09-26 18:04 | Surveying - Instrumentation and Monitoring | 2500 |  | Software | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Not Defined | Completed |  | The draw wire located on the fourth floor balcony of 20 Hanover Square have been presented to the SRG and CTC groups as raw data.
| 01CV - Civils | Cxxx-NCR-001589 | NCR | PTE Crack |  | Contr | BFK |  |  | 2014-10-31 | 2014-10-24 10:33 | -7 | 2014-09-30 15:00 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A longitudinal crack in the secondary lining in PTE at TCR has been identified from chainage 20-45 approximately no more than 1mm in width. It is located between the 1 and 2 o'clock position looking west to east. (see attached pictures from Cxxx inspector)
| 01CV - Civils | Cxxx-NCR-001590 | NCR | Incomplete F50s for AP3E Initial Drive. |  | Contr | BFK |  |  | 2014-10-31 | 2014-10-09 15:38 | -22 | 2014-09-30 09:52 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Incomplete F50 forms for AP3E Initial drive. These forms are missing information such as nozzleman names and signatures, spray start and finish times and file names.
| 01CV - Civils | Cxxx-NCR-001591 | NCR | CH3 Invert concrete at headwall poured without FCD in place |  | Crossrail | PDP | BOS - Bond Street Station (West) |  | 2014-11-14 | 2014-10-24 14:31 | -21 | 2014-09-30 17:11 | Tunnelling - Linings - In-situ Concrete | 1500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | Due to the CH3 headwall drawing being unavalable. Its was discussed and agreed with __ (CRL Engineering Manager) and __ ( SCL Engineer) that could pour the invert concrete up to the headwall. This was on the proviso by __ that a FCD and Sketch were issued for acceptance to CRL. The pour proceeded without the FCD or sketch being raised for subsequent acceptance.
| 01CV - Civils | Cxxx-NCR-001592 | NCR | Missing inforamtion from the Sprayed Secondary lining checksheet form BFK 088 PTE Ch. 52 to 55 |  | Contr | BFK |  |  | 2014-12-02 | 2014-11-26 16:09 | -6 | 2014-10-01 14:05 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | During a surveillance o f PTE Ch. 52 to 55 secondary lining it has been noticed that several important bits of information has not been filled in. Type of concrete has not been recorded/checked. Flow & temperature on arrival to site has not been recorded. Secondary lining within tolerence has not been checked.
| 01CV - Civils | Cxxx-NCR-001593 | NCR | AP3E BFK 22 Cast in-situ Invert |  | Contr | BFK |  |  | 2014-10-24 | 2014-10-09 15:13 | -15 | 2014-10-01 14:27 | Tunnelling - Linings - In-situ Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | raised the NCR 001463 due to compressive strength at 28 days from the cast insitu invert (mix 22) in AP3E was below specification. Based on the data submitted with the NCR -001463 the data provided for AP3E secondary lining was insufficient, therefore was requested to provide data for AP3E related to the compressive strength.
| 01CV - Civils | Cxxx-NCR-001594 | NCR | AP8/LP9 thickening NF steel |  | Contr | BFK |  |  | 2014-10-23 | 2014-10-14 12:37 | -9 | 2014-10-09 11:49 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Further to Cxxx-NCR-001587, the NF invert steel was installed in AP8 correctly, however it was sprayed incorrectly with not enough concrete cover.
| 01CV - Civils | Cxxx-NCR-001595 | NCR | Summary sheets from Hanson missing some tickets throught 2013 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-11-14 | 2014-11-07 11:41 | -7 | 2014-10-02 08:21 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Summary sheets received from do not match up with the tickets supplied in some instances in 2013
| 01CV - Civils | Cxxx-NCR-001596 | NCR | Hardened Fibre Content |  | Contr | BFK |  |  | 2014-11-13 | 2014-10-27 10:39 | -17 | 2014-10-23 17:00 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Hardened fibre content test not carried on sample 600, PTE Adv 183, Heading.
| 01CV - Civils | Cxxx-NCR-001597 | NCR | For the Month of June 2013, Handover package contains Batch summary provided by Hanson of all shotcrete provided for that month which includes the individual constituencies of the mix but no wagon delivery dockets. |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-11-13 | 2014-11-07 11:42 | -6 | 2014-10-02 11:05 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | For the month of June 2013, has failed to provide wagon delivery dockets for shotcrete delivered. ( However a batch summary was provided by of shotcrete delivered in that month which also depicts its constituences and populates a register of all wagons delivered and To BOS and the area sprayed)
| 01CV - Civils | Cxxx-NCR-001598 | NCR | 1 Day Cores tested late |  | Contr | BFK |  |  | 2014-12-14 | 2014-11-17 17:15 | -27 | 2014-11-16 18:01 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Cores from thickening zones were tested outside of 1-3 days: Sample 662A PTE/S1 Thickening Cores tested at 12 days Sample 666, PTE/AP4E Thickening Heading, cores tested at 4 days Sample 667, PTE/AP4E Thickening Invert, cores tested at 4 days
| 01CV - Civils | Cxxx-NCR-001602 | NCR | Flexural beam test results - TCR July 2013 |  | Contr | BFK |  |  | 2014-10-31 | 2014-11-03 19:03 | 3 | 2014-10-03 11:05 | Tunnelling - Linings - Sprayed Concrete | 40000 |  | Workmanship | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Flexural beam test results for July 2013 at TCR were reported to be below the specified requirement (one beam had a D3S1.4 of only 0.4MPa). On review of the detailed load/displacement graph, it appears that this low result was erroneous due to an "unload/reload" loop, with the specimen recovering to exhibit compliant residual flexural strength. On this basis, all three beams exceeded the 90 day specification requirements and no further testing should have been necessary. Investigation into the insitu lining demonstrates a consistently compliant lining with compliant quality cores, very few band layers, good fibre counts and high compressive strengths. On this basis, it is proposed to "leave as is". Full report attached to support this approach.
| 01CV - Civils | Cxxx-NCR-001603 | NCR | PTE Secondary Lining Hammer Testing |  | Contr | BFK |  |  | 2014-11-28 | 2014-11-18 14:57 | -10 | 2014-10-03 11:54 | Tunnelling - Tunnelling General | 1500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | As per KT20.2205, the sprayed secondary linings for platform tunnels must be tested for voids in the crown every 10m. This test was unintentionally omitted prior to application of the fireproofing layer between chainages 20 - 130.
| 01CV - Civils | Cxxx-NCR-001604 | NCR | Under thickness and overspray of secondary lining in PTE CH. 20 - 130 |  | Contr | BFK |  |  | 2014-10-31 | 2014-10-09 17:37 | -22 | 2014-10-03 18:44 | Tunnelling - Linings - Sprayed Concrete | 25000 |  | Workmanship | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After spraying the secondary lining in PTE between ch. 20 - 130, the profiles have been assessed by __ (), __ (Cxxx) & __ (CRL). It was concluded that there is concern with possible under thickness at ch. 65 - 66 and overspray at 42.0, 51.5, 57.0, 74.0, 96.5, 98.5, 99.5, 105.0, 109.0, 110.0 and 117.0.
| 01CV - Civils | Cxxx-NCR-001605 | NCR | Under thickness of secondary lining in PTE ch. 130 - 165 |  | Contr | BFK |  |  | 2015-02-06 | 2015-02-03 09:57 | -3 | 2014-10-09 16:53 | Tunnelling - Linings - Sprayed Concrete | 15500 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After spraying the secondary lining in PTE between ch. 130 - 165, the profiles have been assessed by M. Velupillai (), __ (Cxxx) & __ (CRL). It was concluded that there is concern with possible under thickness at ch. 137.5, 142.5, 152 - 153.5, 157-157.5 and 159.5.
| 01CV - Civils | Cxxx-NCR-001606 | NCR | Incorrect Reinforcement Lap Length to CP9 - Secondary Lining |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2014-11-01 | 2014-10-22 17:00 | -10 | 2014-10-04 03:51 | Tunnelling - Linings - Sprayed Concrete | 8000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As part of the Crossrail and Cxxx inspection of the installed reinforcement bars to CP9 and CP10 to Concourse Junction (CH3) as detailed as a hold point in the ITP for Secondary Lining works document number Cxxx--C4-ITP-CRT00_ST005-50144 Rev 3.0, Crossrail and Cxxx identified during the planned inspection of the Far Face reinforcement to CP9 that the installed reinforcement bars (2 no. sets of bars) to the invert had the incorrect lap length. Crossrail and Cxxx stated on site to that as per detailed in the reinforcement details, drawing no. Cxxx-MMD-C4-DDD-Cxxx_5-00021 Rev C05, the lap length to reinforcement bars B16-BM23 and B10-BM24 is required to be 570mm, where what been installed on site to the two sets of bars was a lap length of 460mm. Crossrail and Cxxx were unable to sign off the ITP Hold Point intervention for the installed reinforcement to CP9 and CP10 until the defect was corrected.
| 01CV - Civils | Cxxx-NCR-001607 | NCR | Spraying Secondary Lining High Pump Rate |  | Contr | BFK |  |  | 2014-11-19 | 2014-11-05 16:56 | -14 | 2014-10-29 18:39 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | In PTW at AP3W junction while spraying secondary lining between ch. 129.5-132.5 (checksheet attached) it was observed that the __ pump rate reached 17.8m3/h. This is not compliant with the method statement Cxxx--C4-GMS-CRT00_ST005-50274 which caps he maximum spray to 15m3/h. has provided evidence that spraying at a pump rate up to 22m3/h does not compromise the quality of the lining. This is reflected in the short change notice Cxxx--C4-CCN-CRT00_ST005-50696 - signed Code 1.
| 01CV - Civils | Cxxx-NCR-001608 | NCR | AP7a hollow section |  | Contr | BFK |  |  | 2014-10-28 | 2014-10-23 10:44 | -5 | 2014-10-14 19:07 | Tunnelling - Linings - Sprayed Concrete | 4500 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | When hammer testing the AP7a crown lining, a hollow section was identified above the tunnel junction to AP7b approximately 2x1m in area. Following coring it was found that the primary lining thickening appeared to have 'sagged' leaving a void between the primary lining and primary lining thickening. At worst this void was approximately 25mm in the centre.
| 01CV - Civils | Cxxx-NCR-001609 | NCR | Lack of curing secondary lining AP3E |  | Contr | BFK |  |  | 2014-11-07 | 2014-11-05 19:02 | -2 | 2014-10-08 20:02 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | In AP3E missed two curing's of secondary lining in bay 20-17 and one in bay 23 -20. As agreed, is supposed to: - Three curing passes within 12 hours after spraying - First curing to be done minimum of 3 hours after spray finish - Curing to be done at a minimum spacing of every two hours - Minimum of three curing passes to be undertaken - Curing to consist of spraying the entire profile of the bay sprayed with water
| 01CV - Civils | Cxxx-NCR-001610 | NCR | VEW primary lining headwall lamination |  | Contr | BFK |  |  | 2014-11-06 | 2014-10-24 15:12 | -13 | 2014-10-23 16:10 | Tunnelling - Linings - Sprayed Concrete | 4500 |  | Workmanship | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Hollow spots where identified in VEW Headwall Primary Lining thickening when undertaking hammer testing prior to secondary lining. On taking cores, it was identified that there was a gap between the primary lining and primary lining thickening
| 01CV - Civils | Cxxx-NCR-001611 | NCR | Under thickness and overspray secondary lining in PTW ch. 25- 148 |  | Contr | BFK |  |  | 2015-03-26 | 2015-03-30 18:02 | 4 | 2014-10-07 14:45 | Tunnelling - Linings - Sprayed Concrete | 55000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After spraying the secondary lining in PTE between ch. 25 - 135, the profiles have been assessed by __, __ () and presented to __ (Cxxx).It was concluded that there is concern with under thickness and overspray at chainages detailed in the snag list attached.
| 01CV - Civils | Cxxx-NCR-001613 | NCR | Outstanding CV for Walter Foeger Nozzleman |  | Crossrail | PDP |  |  | 2015-03-31 | 2015-01-14 16:33 | -76 | 2014-10-08 02:19 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Not Defined | Completed |  | Following a number of requests for __ CV since he was first observed by CRL supervising a Trainee Nozzleman on 07/08/14 in VEW his CV submittal is still outstanding. As per KT20 2107 b) it is stated that... "the trainee will be supervised by a nozzleman with a minimum five years robotic application in SCL tunnelling experience, or satisfies options ii) and iii) ii) Nozzlemen shall have five years robotic application in SCL tunnelling experience and hold relevant certificates of competence and training issued by the Contractor or written evidence of previous satisfactory work indicating compliance with EFNARC Nozzleman Certification Scheme, ACI 506R-03 (USA) or similar national standards to the acceptance of the Project Manager. iii) Subject to the Project Manager's agreement, tests and acceptance for nozzleman proficiency may be combined with trial mix tests. The Contractor shall be responsible for establishing the acceptance criteria for the test, and gain acceptance from the Project Manager prior to the nozzlemen assessment. To be considered for this route, the nozzleman shall have two years relevant experience.
| 01CV - Civils | Cxxx-NCR-001615 | NCR | Non compacted concrete poured in the AP3A slab invert (small additional bay). |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2014-11-21 | 2014-11-21 16:37 | 0 | 2014-10-08 17:48 | Tunnelling - Linings - In-situ Concrete | 4500 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The additional part of AP3A slab invert (next to the Vandex) that was poured on 07-10-2014 NS had a pour finish which indicates from the texture of the surface (as well as it was coming out easily crumbled) that has not been vibrated at that area. Also, it shows that the poured invert section was not protected efficiently, as finger prints were obvious on the surface.
| 01CV - Civils | Cxxx-NCR-001617 | NCR | Allowing AP3W secondary lining invert concrete pour to commence on Masterseal with insufficient Shore A strength. |  | Crossrail | PDP |  |  | 2014-11-14 | 2014-11-04 15:42 | -10 | 2014-10-09 00:49 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | AP3W invert waterproofing ch. 6.1-22.1 was shore tested at ~16:30 (avg. 34) on day shift and ~22:30 (avg. 38) on night shift. Following the night shift inspection CRL and Cxxx advised that proceeding with pouring the invert slab is not in accordance with approved documentation and may result in significant re-work. When it became apparent had made the decision to commence the pour at ~23:30, CRL advised the Cxxx Shift Engineer and the Shift Manager to do a joint witness test together. When they arrived on site the Pit Boss had already allowed the pumping of the concrete to commence but in doing so a blockage in the line had occurred, the subsequent hold up allowed Cxxx / to do a joint inspectionwithin the invert bay where no concrete had been poured which had an average of avg. Shore A strength of 40 at ~00:00. The Cxxx Shift Engineer once again advised the site management team not to commence with the pour until the required Shore A 50 strength had been reached. The Shore A testing for this pour relates to both the sprayed lining and small patch repairs within the invert. Masterseal waterproofing requires a Shore A hardness test value of 50 prior to secondary lining application (in accordance with RAMS Cxxx--C4-GMS-CRT00_ST005-50267 and ITP Cxxx--C4-ITP-CRT00_ST005-50112).
| 01CV - Civils | Cxxx-NCR-001618 | NCR | TCR CP2 RMS |  | Contr | BFK |  |  | 2014-10-23 | 2014-10-14 13:06 | -9 | 2014-10-09 11:37 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | A RMS was not installed in CP2 as specified on Cxxx-MMD-C4-DDD-N105_Z-00032.
| 01CV - Civils | Cxxx-NCR-001619 | NCR | Missing Excavation and Primary Lining As-builts Profiles for AP1 |  | Contr | BFK |  |  | 2014-11-06 | 2014-10-09 16:30 | -28 | 2014-10-09 14:29 | Tunnelling - Linings - Sprayed Concrete | 4000 |  | Documentation and Records | Rework | 3 (3-6k) | Complete | Management Problem - Other | Completed |  | AP1 excavation and primary lining has as-builts profiles missing for the following chainages below; Ch. 3.03- Has no primary lining and thickness profiles for invert Ch. 4.56- Has no excavtion profile for invert Ch. 4.56- The primary lining thickness profile shows the thickness is less than required. Ch. 5.42- Has no primary lining profile for invert Ch. 5.42- The profile for thickness shows is less than required. Ch. 6.01- Has missing excavtion points between 12 o'clock to 2 o'clock and between 3 o'clock to 6 o'clock.
| 01CV - Civils | Cxxx-NCR-001620 | NCR | Monitoring point holes were not grouted prior waterproofing layer sprayed |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2014-12-19 | 2014-12-09 09:40 | -10 | 2014-10-09 22:01 | Tunnelling - Tunnelling General | 1500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In CP5 - section 5a, monitoring point holes were not grouted with 5* prior aplying the waterproofing layer which was sprayed on 28-09-2014 DS, with result these areas not to have at all or the apropriate thickness of masterseal.
| 01CV - Civils | Cxxx-NCR-001621 | NCR | Oil spillage in Cast Invert PTW 3 |  | Contr | BFK |  |  | 2014-10-30 | 2014-10-15 17:56 | -15 | 2014-10-09 22:25 | Tunnelling - Tunnelling General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | Oil spillage of 200x200 mm in Cast Invert in PTW 3 ch 35 . Potential damage to the cast invert slab.
| 01CV - Civils | Cxxx-NCR-001622 | NCR | AP2W Waterproofing patches A&B |  | Contr | BFK |  |  | 2014-10-30 | 2014-10-17 13:28 | -13 | 2014-10-09 22:37 | Tunnelling - Linings - Sprayed Concrete | 20000 |  | Supervision/Management | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In AP2W patches A&B from waterproofing weren't Shore A hardness check prior to spray secondary lining. Both patches were smaller than 3x3 cm. See attached checksheet
| 01CV - Civils | Cxxx-NCR-001623 | NCR | Crack Injection - resin pump used with no pressure gauge on in S3 tunnel - Ch. 5.34 4 o'clock Invert |  | Contr | BFK |  |  | 2014-11-28 | 2014-11-21 13:54 | -7 | 2014-10-10 11:03 | Tunnelling - Tunnelling General | 15000 |  | Equipment Breakdown | Use As-Is | 2 (6-60k) | Complete | Material/Preservation Problems - Other | Completed |  | After hammer testing S3 tunnel, when undertaking crack injections - Chainage 5.34 4 o' clock Invert, a resin pump was used with no pressure gauge on - so it was not possible to know what the pump pressure was.
| 01CV - Civils | Cxxx-NCR-001624 | NCR | Sprayed Concrete Secondary Lining Check Sheet Not filled for curing works Ch29 to 35.5 CH3 area (3b) |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-02-27 | 2015-02-11 14:22 | -16 | 2014-10-15 12:39 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please find attach a check sheet which believes was filled in improperly/incorrectly. The check sheet shows that curing was not done. believes curing was done in the said area. propose to provide pictures for the said area showing curing was done at the time. also propose to do a briefing to Engineers so that the check sheets are filled in correctly. propose to close this NCR by attaching photos + briefing sheet. Specification Ref: KF10.3206 Curing and Protection
| 01CV - Civils | Cxxx-NCR-001627 | NCR | The spraying of master seal over unclean areas |  | Crossrail | PDP | BOS - Bond Street Station (West) |  | 2014-11-21 | 2014-11-14 09:34 | -7 | 2014-10-13 11:27 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Spraying Master Seal over an area at the junction of PTW and VD3 which was not cleaned correctly which has lead to no bonding between the master seal and the regulating layer.
| 01CV - Civils | Cxxx-NCR-001628 | NCR | VWW - Less than 6 cores tested at 28 Days |  | Contr | BFK |  |  | 2014-11-28 | 2014-11-21 13:57 | -7 | 2014-10-15 10:04 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | VWW Advance 16, 4 cores tested at 28 days VWW Advance 28, 5 cores tested at 28 days
| 01CV - Civils | Cxxx-NCR-001629 | NCR | Incorrect Application of Masterseal Waterproofing to CP9 |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2014-12-19 | 2014-12-17 10:58 | -2 | 2014-10-13 17:38 | Tunnelling - Linings - Sprayed Concrete | 6000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | Crossrail raising NCR for the incorrect application of Masterseal waterproofing for a repair area within CP9, as witnessed by Crossrail during the nightshift of 11 October 2014. Crossrail observed the Masterseal being applied by hand which does not meet the requirements of Section KW20 Materials and Workmanship Specification Spray Applied Waterproofing Membrane System for SCL Works. In addition, the repair does not meet the requirements of ITP Regulating and Sprayed Waterproof Application.
| 01CV - Civils | Cxxx-NCR-001630 | NCR | 28 Day Cores - AP8 |  | Contr | BFK |  |  | 2014-12-14 | 2014-12-08 16:54 | -6 | 2014-11-16 12:04 | Tunnelling - Linings - In-situ Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Sample 701, AP8 Thickening, Heading, CH27-3228 day cores results from mix 17.2 below specification. Average of results below 34N and two results less than 30N.
| 01CV - Civils | Cxxx-NCR-001631 | NCR | Over scrapping of fireproofing |  | Crossrail | PDP | BOS - Bond Street Station (West) |  | 2014-12-23 | 2014-12-19 13:28 | -4 | 2014-10-14 12:29 | Tunnelling - Linings - Sprayed Concrete | 7000 |  | Workmanship | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After completion of the spraying of fireproofing in VD4, work force scraped back an area of freshly sprayed fireproofing which had been over sprayed. The area was then over scraped.
| 01CV - Civils | Cxxx-NCR-001634 | NCR | Spraying of Secondary Lining to CP7 with Monitoring Points Remaining in Tunnel Lining |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2014-12-19 | 2014-12-16 14:43 | -3 | 2014-10-14 14:09 | Tunnelling - Linings - Sprayed Concrete | 4500 |  | Supervision/Management | Use As-Is | 3 (3-6k) | Complete | Procedure Problem - Other | Completed |  | Crossrail observed the spraying of secondary lining to CP7 on the dayshift of Monday 13th October 2014 and noted that two monitoring points had been left in the tunnel lining. Crossrail raised the issue with the Shift Engineer at the time, highlighting that the monitoring points were required to be removed and the penetrations to be filled and also made good with Masterseal repair. Crossrail raising this NCR as the spraying to the regulating layer, the waterproofing layer and the secondary lining layer to CP7 had proceeded without undertaking required checks and preparation of the substrate before spraying. Crossrail note that the works do not meet the requirements of KW20 Materials and Workmanship Specification and also do not meet the requirements of the ITP for Regulating and Sprayed Waterproof Application. Update: 12/12/14 - Crossrail inspected the repairs at the time of being completed and accepted the form and completion of the repairs. Crossrail note that the NCR is to be closed out on this basis and to ensure site teams are briefed on the procedure for the removal of monitoring points and penetrations and making good those areas prior to spraying Secondary Lining, which was the main purpose of the NCR. attached briefing sheet. NCR to be closed.
| 01CV - Civils | Cxxx-NCR-001635 | NCR | Damaged Masterseal to CP8 invert |  | Crossrail | PDP | BOS - Bond Street Station (West) |  | 2014-12-19 | 2014-12-15 16:49 | -4 | 2014-10-14 13:30 | Tunnelling - Linings - Sprayed Concrete | 6000 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Masterseal was damaged in the area around the shutter at CH3. The secondry lining sprayed in CH 3 has resulted in not enough overlap 300mm availible for the repair of the Masterseal in CP8. (See attached photo)
| 01CV - Civils | Cxxx-NCR-001636 | NCR | Damage to Masterseal at the invert location of the 1st stage concrete pourin CH 3 |  | Crossrail | PDP | BOS - Bond Street Station (West) |  | 2014-10-28 | 2014-11-21 17:13 | 24 | 2014-10-14 16:28 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | Damaged waterproofing in CH3 invert slab at the headwall. The invert slab was poured short to allow for the reinforcement to be installed but the erection and then dismantling of the stop end has damaged the Masterseal. There is now not enough room for the masterseal to be repaired with the correct overlap of 300mm.
| 01CV - Civils | Cxxx-NCR-001637 | NCR | Secondary lining early age strength |  | Contr | BFK |  |  | 2014-11-28 | 2014-11-25 15:08 | -3 | 2014-10-15 09:08 | Tunnelling - Linings - Sprayed Concrete | 7000 |  | Supervision/Management | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Out of all the secondary lining sprayed so far in TCR starting mid August a total of one complete early age test has been completed. The requirement as per FCD 1141 is that an early age stregth panel should be sprayed every 24hrs.
| 01CV - Civils | Cxxx-NCR-001638 | NCR | 28 Day Cores - CP4A |  | Contr | BFK |  |  | 2015-02-02 | 2015-01-21 15:25 | -12 | 2014-11-16 17:49 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Sample 716 CP4A Thickening Invert CH 12.7-19, 28 day cores less than specification. Extra cores were tested at 59 days.
| 01CV - Civils | Cxxx-NCR-001639 | NCR | 28 Day Cores - PTW CH.145-148 |  | Contr | BFK |  |  | 2014-12-07 | 2014-11-20 12:33 | -17 | 2014-11-16 17:50 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Sample 675, PTW Secondary Lining,CH.145-148, 28 Day cores from Mix 17.2 below specification, average below 34N, some indivual results less than 30N. Only 4 cores tested at 90 days but this due to some of the samples being too short to create viable test piece.
| 01CV - Civils | Cxxx-NCR-001640 | NCR | 1-3 Day cores |  | Contr | BFK |  |  | 2014-11-12 | 2014-10-23 10:34 | -20 | 2014-10-15 10:48 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | During August 2014 the following sets of cores were tested late outside of th 1-3 day reuirement. Sample 674, S1, Adv5, tested at 5 days Sample 690, PTW Secondary, CH71-74, tested at 5 days Sample 692, PTW Secondary, CH65-68, tested at 4 days Sample 693, VEW, Adv 22, tested at 6 days Sample 698, VEW Adv 31, tested at 4 days Sample 701, AP8 Thickening, tested at 7 days Sample 702, VEW Adv42, tested at 6 days Sample 703, VEW Adv 46, tested at 4 days
| 01CV - Civils | Cxxx-NCR-001641 | NCR | The requirment of Cxxx-NCR-001539 has not been followed |  | Contr | BFK |  |  | 2014-10-31 | 2014-10-23 10:41 | -8 | 2014-10-14 17:25 | Tunnelling - Linings - In-situ Concrete | 15000 |  | Supervision/Management | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | According to CRL reply to Non-conformance report “Cxxx-NCR-001539”, were required to install reinjectable grout hose along the longitudinal joint of PTE invert at CH 100 to 112 and the sprayed secondary lining. This requirement was missed by team and this section of PTE was sprayed with secondary lining and fireproofing without installing the reinjectable grout pipe.
| 01CV - Civils | Cxxx-NCR-001642 | NCR | Early age testing of the fireproofing layer |  | Contr | BFK |  |  | 2014-11-28 | 2014-11-06 11:30 | -22 | 2014-10-15 10:50 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Line B9.8 of Cxxx--C4-ITP-CRT00_ST005-50144 ITP for cast in situ and sprayed secondary lining states that a full set of early age strength test should be one every 3 bays a tunnel for the fireproofing layer. This is not being done at TCR and is not a requirement of the specification.
| 01CV - Civils | Cxxx-NCR-001643 | NCR | Insufficient compressive strength testing PTE sprayed secondary lining. |  | Contr | BFK |  |  | 2014-12-23 | 2014-12-19 13:23 | -4 | 2014-10-15 11:56 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | In PTE so far a total of 1100m^3 of secondary lining has been sprayed. This being the case 20 every 50m^3 comppressive strengh should have been taken. A total of 9 compressive strength tests have actually been taken.
| 01CV - Civils | Cxxx-NCR-001644 | NCR | 28 day cores - PTE CH28-32 |  | Contr | BFK |  |  | 2015-02-10 | 2015-01-23 11:58 | -18 | 2015-01-05 15:55 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Sample 714, PTE Secondary Ch 28-32, 4 of 6 results below 34N
| 01CV - Civils | Cxxx-NCR-001646 | NCR | Insufficient amount of waterproofing overlap in the AP2E/ PTE junction |  | Contr | BFK |  |  | 2014-11-05 | 2014-11-05 11:11 | 0 | 2014-10-22 09:01 | Tunnelling - Tunnelling General | 5000 |  | Workmanship | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Whilst spraying the PTE/AP2e junction, the nozzleman accidentally over-sprayed into the AP2e tunnel and reduced the waterproofing lap between 11 and 12o'clock to less than 300mm. This is a non-conformance against the 300mm overlap minimum of existing membranes as per Cxxx-MMD-C4-DDD-N105_Z-00042 Typical Waterproofing and Connection Details.
| 01CV - Civils | Cxxx-NCR-001647 | NCR | Insufficient amount of waterproofing overlap in the CH1/ AP2W junction |  | Contr | BFK |  |  | 2014-11-05 | 2014-11-06 17:06 | 1 | 2014-10-22 09:06 | Tunnelling - Tunnelling General | 4500 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Whilst spraying the AP2W/CH1 junction, the nozzleman accidentally over-sprayed into the CH1 tunnel and reduced the waterproofing lap between 8 and 10o'clock to less than 300mm. This is a non-conformance against the 300mm overlap minimum of existing membranes as per Cxxx-MMD-C4-DDD-N105_Z-00042 Typical Waterproofing and Connection Details.
| 01CV - Civils | Cxxx-NCR-001648 | NCR | S4 in-situ invert cast at incorrect level |  | Contr | BFK |  |  | 2014-11-05 | 2014-11-18 09:39 | 13 | 2014-10-22 09:32 | Tunnelling - Linings - In-situ Concrete | 4500 |  | Documentation and Records | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Due to an error with the surveying information given to the shift engineer, the in-situ concrete invert level has been cast 120mm greater than design level between the chainages of 9 to 19.5m. Once noticed, as agreed in the daily secondary lining meeting the level was reduced to the correct level (-20m than design) by chainage 23.1. This gives a declined slope of ~40mm every 1m.
| 01CV - Civils | Cxxx-NCR-001649 | NCR | Waterproofing sprayed over 12hr old regulating layer in AP7a invert |  | Contr | BFK |  |  | 2014-11-05 | 2014-11-04 16:13 | -1 | 2014-10-22 09:50 | Tunnelling - Tunnelling General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Waterproofing was sprayed over a 12hr old regulating layer in the AP7a invert between chainages 1.5m - 23.0m. This is a non-conformance against: KW20.3201: b) Waterproofing membrane shall be sprayed on primary lining which is dry for at least 24 hours, and KW20.3202: "The system shall provide a suitable dry substrate for 24 hours before the membrane is installed."
| 01CV - Civils | Cxxx-NCR-001650 | NCR | CH3 Head Wall 3b Area |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-11-14 | 2014-11-07 16:05 | -7 | 2014-10-15 16:28 | Tunnelling - Linings - Sprayed Concrete | 4500 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Through Cxxx-PMI-01562, was provided with drawings that detailed reinforcement in the headwall at the end of CH3. At this stage, the entire area of CH3 (including the headwall) had been sprayed with Masterseal. During spraying of the secondary lining to the junctions CP7/CH3 and CP8/CH3, the headwall area was not protected and shotcrete was oversprayed onto the Masterseal. Operatives then drilled and fixed GRP dowels (for supporting the headwall rebar) through the layer of shotcrete and through the Masterseal. It is now impossible to repair the Masterseal by painting around the dowels, because the required lap of 200mm cannot be achieved. The secondary lining to the junctions has not yet been sprayed to full thickness.
| 01CV - Civils | Cxxx-NCR-001651 | NCR | VD4: Fireproof Thickness insufficient |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-01-16 | 2015-01-08 15:25 | -8 | 2014-10-16 15:15 | Tunnelling - Linings - Sprayed Concrete | 40000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the spraying of the fireproofing layer to the VD4 tunnel the required thickness of a minimum of 50mm was not achieved. One of the principle causes to this lack of thickness was the spraying robot (Logica) as it didn't apply a uniform thickness. The Logica failed due to two reasons: - when there is a transition or slight bent in the tunnels scanning of the Logica is difficult to achieve - due to the advanced techology with the Logica, inexperience in the setup of the scanning may have been incorrect
| 01CV - Civils | Cxxx-NCR-001652 | NCR | VD3: Fireproof Thickness insufficient |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-01-09 | 2015-01-08 14:52 | -1 | 2014-10-16 15:19 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the spraying of the fireproofing layer to the VD3 tunnel the required thickness of a minimum of 50mm was not achieved. One of the principle causes to this lack of thickness was the spraying robot (Logica) as it didn't apply a uniform thickness. The Logica failed due to two reasons: - when there is a transition or slight bent in the tunnels scanning of the Logica is difficult to achieve - due to the advanced techology with the Logica, inexperience in the setup of the scanning may have been incorrect
| 01CV - Civils | Cxxx-NCR-001653 | NCR | Spraying of SL over monitoriing target. |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2014-11-21 | 2014-11-13 22:07 | -8 | 2014-10-17 14:19 | Civil - Tunnelling | 5000 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The spraying of secondary lining in CH3 occured with a monitoring target still in place. The target subsequently remains in the lining, at approximately 9 o'clock in between CP10 and CP8.
| 01CV - Civils | Cxxx-NCR-001654 | NCR | Injecting through secondary lining South face of invert slab in CP9 Ch6 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-12-19 | 2014-12-12 16:37 | -7 | 2014-10-30 18:30 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | A leak was found on the south side of invert slab CP9. Part of the sprayed secondary lining was broken out and packers drilled through into the primary lining. The area was injected with __ 150 (approx 15ltrs), as per the approved method statement for crack injection, of which 10ltrs came out through the contraction joint. However this was not agreed with CRL/Cxxx prior to carrying out the works.
| 01CV - Civils | Cxxx-NCR-001656 | NCR | AP4E / PTE Junction - Installation of rebar dowels though Masterseal to hold Secondary Lining Reinforcement in place. |  | Crossrail | PDP |  |  | 2014-11-21 | 2014-11-05 19:13 | -16 | 2014-10-20 12:02 | Tunnelling - Linings - Sprayed Concrete | 5500 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Within the AP4E / PTE Junction 5 x 25mm rebar dowels were drilled through the secondary lining (first 100mm layer) and Masterseal with embedment into the primary lining by approx 400mm. GRP dowels were already in place within the junction but someone had taken the decision to use these additional dowels to hold the invert link bars in place for the NF secondary lining reinforcement which completely compromises the water proofing membranes ability to control water ingress. This non compliance can be referenced against the KW20.3203 (c) for Substrate Preparation.
| 01CV - Civils | Cxxx-NCR-001657 | NCR | AP4E / PTE Junction Masterseal Damage |  | Crossrail | PDP |  |  | 2014-11-07 | 2014-11-07 11:48 | 0 | 2014-10-20 12:54 | Tunnelling - Linings - Sprayed Concrete | 15000 |  | Damaged | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A hammer test was undertaken by a CRL inspector in the AP4E / PTE Junction (12:00 19/10/14) after locating laminations and rebound in front and around the stop-end shutter from the invert poured on the 18/10/14 DS which had been recently struck at Ch 34 in the AP4E / PTE Junction. Hollows / rebound was then marked up by the CRL Inspector, Masterseal damage was also observed in and around this shutter location. Upon removal of the rebound and hollows extensive damage and de-bonding of Masterseal was observed in front of the stop end at Ch. 34-35 from 5-7 o’clock and above the invert between Ch 33-34 (LHS / RHS). Poor surface preparation was evident prior to Masterseal application which appears to have contributed to the waterproofing de-bonding to such an extent achieving the required 300m lap for the Masterseal will not be possible at this location now. Evidence of poor surface preparation includes; - Cleanliness of the regulating was unsatisfactory - Masterseal has been sprayed directly on top of fibres on the RHS looking towards the PTE around Ch 33-35 approx - 3 pieces of rebar appear to have not been removed from the primary lining a little bit further back from junction damage on the RHS looking towards the PTE and have had Masterseal sprayed over the top. TheMasterseal encapsulation on top of one of the bars was easily removed. Following a joint inspection involving CRL / / Cxxx a decision was taken to put the work face on hold at 17:00 on the 19/10/14 so the Cxxx Senior Engineer could undertake an inspection the following morning to assess the damage due to the extent of the quality issues which were evident. These Workmanship non compliances can be referenced against KW20.3203 (Substrate Preparation) & KW20.3204 (Spray Applied Waterproofing Membrane).
| 01CV - Civils | Cxxx-NCR-001658 | NCR | Insufficient thickness to Masterseal in AP4E / PTE Junction |  | Crossrail | PDP |  |  | 2014-11-14 | 2014-11-07 16:57 | -7 | 2014-10-20 14:44 | Tunnelling - Linings - Sprayed Concrete | 6000 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following the AP4E / PTE Junction Masterseal damage samples retrieved have revealed insufficient thickness (less than 6mm for a junction). Some samples retrieved were approx 2-3mm in thickness which is non compliant with with the detail on found on Dwg Cxxx-MMD-C4-DDD-N105_5-00150 for Generic Junction Details for Sprayed Concrete Linings
| 01CV - Civils | Cxxx-NCR-001659 | NCR | Spraying secondary lining CP7 Junction and not folowing BFK procedures |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-11-21 | 2014-11-13 21:01 | -8 | 2014-10-20 16:33 | Tunnelling - Linings - Sprayed Concrete | 4500 |  | Workmanship | Use As-Is | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | Nozel man sparayed CP7 Junction in one go and not sprayed pass by pass. He did not folow procedure. had fall out on the same location.
| 01CV - Civils | Cxxx-NCR-001660 | NCR | Crack inducer not installed in CP8 in invert top |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-11-19 | 2014-11-03 09:43 | -16 | 2014-10-20 16:41 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Supervision/Management | Rework | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | invert slab has two crack inducers one at the bottom and the other at the top. In this instance the top Crack inducer was not installed in CP8 invert.
| 01CV - Civils | Cxxx-NCR-001661 | NCR | Insufficient number of readings taken for the AP3E chng. 21 As-built |  | Contr | BFK |  |  | 2014-11-12 | 2014-10-27 10:46 | -16 | 2014-10-22 14:23 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | As per the minimum requirement of 1 as-built reading per m2 of tunnel, a minimum of 23 points ought to have been taken for the attached Excavation profile. However, only 20 have been taken.
| 01CV - Civils | Cxxx-NCR-001662 | NCR | PTW West Headwall: Lack of Masterseal overlap |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-11-21 | 2014-11-14 09:37 | -7 | 2014-10-22 14:48 | Tunnelling - Linings - Sprayed Concrete | 15000 |  | Damaged | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the pouring of the mass concrete infill to the the headwall at PTW west, some damage has occurred to the waterproofing and the required lap will not be achieved.
| 01CV - Civils | Cxxx-NCR-001663 | NCR | BOS CH3 secondary lining water ingress. |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2014-11-21 | 2014-11-14 09:40 | -7 | 2014-10-23 11:03 | Civil - Tunnelling | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Proceeding the Near face secondary lining spraying in the CP9/CP10 area of CH3, water ingress occured along the joint between the poured invert slab and the Sprayed secondary lining on the CP9 side of CH3 and at the right hand entend of the FF reinforcment. The leak area was subsequently injected with resin prior to being sprayed over with the far face layer of secondary lining. (Photo's taken on 14/10/14).
| 01CV - Civils | Cxxx-NCR-001665 | NCR | 28 day compressive results not attained in some instances from all six cores @ SCL 596 in August 2014 and SCL 607 and 579 in September 2014 at BOS. |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-12-30 | 2014-12-12 17:05 | -18 | 2014-10-23 11:53 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | 28 day compressive results were not attained from all cores taken @ SCL 596, 607 and 579. In a set of six cores taken per sample between 3 to 4 cores gained 28 day required strength.
| 01CV - Civils | Cxxx-NCR-001666 | NCR | AP4E cast invert U1 finsih out of specifications |  | Contr | BFK |  |  | 2014-11-28 | 2014-11-27 12:32 | -1 | 2014-10-23 17:33 | Tunnelling - Tunnelling General | 5000 |  | Workmanship | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | AP4E ch 12- 34 cast invert U1 finish (0-20mm) is out of specifications due to an inappropriate leveled. This NCR it is not complaint with the ITP Cxxx--C4-ITP-CRT00_ST005-50144 - BOS TCR CP Cast-in situ and Sprayed Secondary Lining section B4.10 and the general note G36 from the drawing Cxxx-MMD-C4-DDJ-N105-00001 reference below. See attached the scans showing the profile of the cast invert from ch.12- 34 and briefing to engineers.
| 01CV - Civils | Cxxx-NCR-001667 | NCR | TCR - AP7a/AP7b - damage to waterproofing at invert |  | Contr | BFK |  |  | 2014-11-06 | 2014-10-27 18:04 | -10 | 2014-10-23 17:26 | Tunnelling - Tunnelling General | 6000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following completion of the cast invert in the junction between ap7a/ap7b, have cleaned the invert and found out that the waterproofing in the invert was damaged close to the cast invert concrete and de-bonded due to a leak. As the waterproofing was de- bonded there was no a proper overlap.
| 01CV - Civils | Cxxx-NCR-001668 | NCR | 1 Day Cores - September |  | Contr | BFK |  |  | 2014-12-05 | 2014-11-10 12:16 | -25 | 2014-11-07 19:47 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | During September the following sets of cores were outside of 1-3 days: Sample 719, PTE Secondary Ch 114-117, tested at 7 days Sample 720, PTE Secondary Ch 89-92, tested at 4 days Sample 721, PTE Secondary Ch 98-100, tested at 4 days Sample 722, AP2E Secondary Ch35-36, tested at 4 days
| 01CV - Civils | Cxxx-NCR-001669 | NCR | Unsatisfactory Masterseal remediation works / painting TaM hoses with Masterseal to AP4E / PTE JUNCTION |  | Crossrail | PDP |  |  | 2014-11-06 | 2014-11-07 12:02 | 1 | 2014-10-23 16:27 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Supervision/Management | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | With reference to NCR 1656 & 57 it was observed that the Masterseal repairs undertaken at AP4E / PTE JUNCTION were unsatisfactory. It was observed by Cxxx/CRL at various locations along the joints from the saw cut and intersections of the invert where TaM grout hoses were fixed to shortcrete was still visible through the Masterseal indicating the waterproofingl thickness for the rework was insufficient. Further investigations therefore was requested to by CRL as Masterseal thickness within junction areas is required to be 6mm (Dwg Cxxx-MMD-C4-DDD-N105_5-5-00150). Destructive Testing was done at 3 locations and all 3 samples proved the Masterseal tapered away to the extents from 6mm to approx. 2mm. It was then agreed that Masterseal would need to be reapplied along the joints which formed the extents where the TaM Hoses were installed by /CRL. The CRL Inspector observing the repairs did advise the TaM hoses were first removed before the Masterseal was reapplied due to the risk of covering the perforated TaM injection hoses in Masterseal. Following the reapplication of Masterseal without removing the TaM Hoses were covered in Masterseal which meant that futher rework was required to install new TaM hoses with clips as per the manufacturers instructions. Masterseal has also been painted above the top TaM hose on top of shotcrete in localised areas.
| 01CV - Civils | Cxxx-NCR-001670 | NCR | VWW primary lining chainage 22.5 |  | Contr | BFK |  |  | 2014-11-06 | 2014-11-04 16:03 | -2 | 2014-10-23 18:01 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Proof drilling after milling at chainage 22.5 showed very isolated areas of under thickness as per attached proof drilling sheet
| 01CV - Civils | Cxxx-NCR-001671 | NCR | AP4E- Application of Waterproofing over secondary lining |  | Contr | BFK |  |  | 2014-11-21 | 2014-11-13 21:07 | -8 | 2014-10-23 20:08 | Tunnelling - Tunnelling General | 10000 |  | Workmanship | Use As-Is | 2 (6-60k) | Complete | Material/Preservation Problems - Other | Completed |  | During an inspection with CRL present at AP4E ch 21-24. It was identified that there was a leak in the lining requiring repair. The team were instructed to undertake a the repair but due to a misunderstanding, the repair also covered part of the secondary lining ( photo attached and sketch with dimensions) the required 300mm overlap of the repairs were achieved. A further joint inspection of the repair was undertaken with CRL/Cxxx present and the approval to spray was signed (attached). Cxxx/CRL advised to remove the excessive masterseal but secondary lining was sprayed over it. This is not compliant because a sandwich was introduced to the lining.
| 01CV - Civils | Cxxx-NCR-001672 | NCR | AP4W Longitudinal crack |  | Contr | BFK |  |  | 2014-11-21 | 2014-11-11 23:28 | -10 | 2014-10-23 20:14 | Tunnelling - Tunnelling General | 5000 |  | Supervision/Management | Use As-Is | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | The longitudinal crack in AP4W/CH3 between ch 5-7 was injected with __ 150 instead of micro fine cement as agreed.
| 01CV - Civils | Cxxx-NCR-001673 | NCR | Commencement of leak repair to CP9 with ITP & RAMS in place |  | Crossrail | PDP | BOS - Bond Street Station (West) |  | 2014-11-28 | 2014-11-26 16:07 | -2 | 2014-10-24 15:51 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | A leak identified in CP9 needed sealing. The issue was discussed in the secondary lining meeting in which it was stated that the works would not commence until the documentation had been provided and accepted by CRL/ Cxxx. The following nighshift undertook the repair without prior notifcation and the documenation not in place. The check sheets have also not been provided.
| 01CV - Civils | Cxxx-NCR-001674 | NCR | Fireproofing compressive strenghts tests not being done at required frequency TCR SCL |  | Contr | BFK |  |  | 2015-01-23 | 2015-01-15 16:32 | -8 | 2014-10-24 16:48 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Over 50 m^3 of fireproofing layer have been sprayed so far at TCR and no compressive strength tests have been completed.
| 01CV - Civils | Cxxx-NCR-001675 | NCR | Concrete Temperature below 15 Deg C AP3A |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-11-26 | 2014-10-29 16:31 | -28 | 2014-10-27 12:18 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Please find attached some form 50s which shows concrete below 15 deg C.
| 01CV - Civils | Cxxx-NCR-001676 | NCR | Secondary Lining Thickness |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-02-16 | 2015-02-13 18:40 | -3 | 2014-10-27 18:09 | Tunnelling - Linings - Sprayed Concrete | 25000 |  | Incomplete Works | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In CH3 there are localised areas where the secondary lining thickness does not meet the design requirement of 250mm (300mm including fireproofing layer). At chainage 0 there are two spots (clock position 11 & 12) where the thickness is 35mm and 30mm less than required. Additionally at chainage 13.5 there is a localised patch (clock position 1 - 3) where the thickness is less than required, ranging from 232mm down to 192mm. Thickness scans for these areas have been attached.
| 01CV - Civils | Cxxx-NCR-001677 | NCR | For the Month of July 2014, 1 wagon was over dosed with Microsilica by 9.10% |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-11-11 | 2014-11-04 16:07 | -7 | 2014-10-28 10:54 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | During the month of July 2014, one delivery wagon of shotcrete by was over dosed with microsillica by 9.10%
| 01CV - Civils | Cxxx-NCR-001678 | NCR | Milling Secondary Lining CH 3 |  | Crossrail | PDP | BOS - Bond Street Station (West) |  | 2014-11-21 | 2014-11-13 21:46 | -8 | 2014-10-30 13:31 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Due to over spray milling took place of the secondry lining in CH 3 at the 9 O'clock location looking inbye. It was discovered that the jiont was feathered not stepped. This type of joint is not aceptable and is not in the design.
| 01CV - Civils | Cxxx-NCR-001680 | NCR | PTE: Insufficient Lining Thickness to areas of 2B/2C |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-12-19 | 2014-12-09 16:39 | -10 | 2014-10-29 12:00 | Tunnelling - Linings - Sprayed Concrete | 7500 |  | Incomplete Works | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In PTE there are localised areas where the secondary lining thickness does not meet the design requirement of 250mm (300mm including fireproofing layer). Areas include: Chainage 48m - 25mm shy of 250mm thickness Chainage 58m - 13mm shy of 250mm thickness See attached scans for PTE Sections 2
| 01CV - Civils | Cxxx-NCR-001681 | NCR | TCR WTH Level -5 Drainage installed in incorrect location |  | Crossrail | PDP |  |  | 2014-11-12 | 2014-11-04 12:55 | -8 | 2014-10-29 14:13 | Civil - Sewage/Water services | 50000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The surface water drain which rises from the -5 level base slab has been installed out of position to am unacceptable position. The Surface Water Drain (SWD) which rises near to grid line A9 (refer to drawing Cxxx-OVE-P-DDA-N105_6-31182) has been installed out of poisition from the IFC drawings by delta E = 103mm, delta N = 22mm. This out of tolerance results in the pipe rising within the walls of the WTH which are currently being constructed by Cxxx, see attached photo showing a blue line which indicates the wall line which is to be poured. Drawing Cxxx-OVE-P-DDA-N105_6-31183 issued under Cxxx-PMI-00729 indicated that the co-ordinates should be X = 79901.360mE, Y = 36023.49mN. The surveyed as built coordinates are actually 79901.257mE, 36023.468mN resulting in delta E = 103mm, delta N = 22mm. This out of tolerance did not get presented on the As Built drawings, the as-built co-ordinates are stated as being 79901.314mE, 36023.474mN (delta E = 46mm, delta N = 16mm) this is also incorrect and did not get highlighted as being a non conformance. In addition there is no spigot on the pipe for Cxxx to connect on to, or is there sufficient length of pipe protruding above the base slab to allow a pipe collar to connect to the pipe to allow it's continuation. see attached photo. need to propose a solution.
| 01CV - Civils | Cxxx-NCR-001682 | NCR | In August 2014 in a few instances Hanson delivered shotcrete which was over dosed with microsillica outside ITP limit of 3%. |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-11-12 | 2014-11-04 16:14 | -8 | 2014-10-29 14:18 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | In August 2014 in a few instances over dosed its shotcrete delivered to Bondstreet outside the batching tolerance of 3%.
| 01CV - Civils | Cxxx-NCR-001683 | NCR | Milling/Scrapping of CH 3 Headwall |  | Crossrail | PDP | BOS - Bond Street Station (West) |  | 2014-11-13 | 2014-11-18 14:58 | 5 | 2014-10-30 13:47 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | A few hours after the completion of spraying the headwall in CH 3 either milled or scraped the area. This was visable from the crown down passed axis towards invert.
| 01CV - Civils | Cxxx-NCR-001684 | NCR | AP4E Potential Cold Joint Secondary Lining |  | Contr | BFK |  |  | 2014-11-28 | 2014-11-28 17:04 | 0 | 2014-10-30 15:52 | Tunnelling - Linings - Sprayed Concrete | 2500 |  | Equipment Breakdown | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Potential cold joint in AP4E ch.26.5-30 not compliant with KT20.1301. While spraying secondary lining there was a 5.30 hour delay in spraying the last 1.5 m3 in the crown around 11- 1 o'clock due to a breakdown of the concrete pump. The area was perfectly clean prior to the application of the last 1.5 m3. (See attached check sheet)
| 01CV - Civils | Cxxx-NCR-001685 | NCR | AP4E-PTE junction potential cold joint |  | Contr | BFK |  |  | 2014-11-21 | 2014-11-10 15:45 | -11 | 2014-10-30 18:02 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In AP4E junction with PTE there is a potential cold joint not compliant with an homogeneous layer required in KT20. 1301.The two potential cold joints are from the end of the cast invert of both sides to 1m higher by 0.5m (as per sketch attached) break out the area, clean and installed dowels as agreed with Cxxx. (Photo attached of both areas).Afterwards it was sprayed to profile.
| 01CV - Civils | Cxxx-NCR-001686 | NCR | Potential cold joint in AP7a:AP7b Secondary Lining junction |  | Contr | BFK |  |  | 2014-12-19 | 2014-12-10 18:18 | -9 | 2014-11-02 17:16 | Tunnelling - Linings - Sprayed Concrete | 6000 |  | Incomplete Works | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Having finished spraying the secondary lining junction between AP7a:AP7b, it was made clear that there was insufficient thickness, approx. 150mm, towards the invert level (this is indicated on the attached photographs) at 7 - 9o'clock. This is a non-conformance since the required thickness of the secondary lining in this area is 200mm.
| 01CV - Civils | Cxxx-NCR-001687 | NCR | Potential cold joint in AP7a secondary lining reinforcement area |  | Contr | BFK |  |  | 2014-11-23 | 2014-11-14 14:52 | -9 | 2014-11-02 17:30 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | When spraying the last 2m of the AP7a junction reinforcement, spraying operations were stopped mid-spray leaving a portion of the 2m bay un-sprayed (see attached photographs). This could cause a potential cold joint within the reinforced area.
| 01CV - Civils | Cxxx-NCR-001688 | NCR | Form 50 with missing details/information AP3a |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-11-29 | 2014-11-21 13:58 | -8 | 2014-10-30 18:07 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Please find attached some form 50 with missing information/incomplete information
| 01CV - Civils | Cxxx-NCR-001689 | NCR | Concrete & Air temperature low AP3A |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-11-29 | 2014-11-04 11:17 | -25 | 2014-10-30 18:25 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Please find atatched some check shets which show air temperature & SCL temperature low below the required limit of 5 deg/15 deg
| 01CV - Civils | Cxxx-NCR-001690 | NCR | Sprayed over monitoring points |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2014-11-28 | 2014-11-21 16:38 | -7 | 2014-10-31 15:15 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Monitoring point has been sprayed over in CP3 (PTE) at 10 o'clock. A further two points have been sprayed in the area directly adjacent to CP3 in the PTE tunnel during the regulating process.
| 01CV - Civils | Cxxx-NCR-001691 | NCR | The Viscosity Test on Micosillica in week 13 25/03/2013 and week 29 15/07/2013 was @ 142 and 111 mPas respectively whilst the maximum should be 100mPas. |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-11-21 | 2014-11-06 12:06 | -15 | 2014-10-31 16:07 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | In weel 13 and week 29 of 2013 micosillica viscosity was 141 and 111 mPas which is outside specification requirement which stares that the viscosity should be less than 100mPas.
| 01CV - Civils | Cxxx-NCR-001692 | NCR | VWW ch 13-15 not following AP |  | Contr | BFK |  |  | 2014-11-26 | 2014-11-17 17:17 | -9 | 2014-11-05 13:52 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During inspection of works it was noted that the spraying team at VWW ch.13-15 were not following the requirement of creating a flat longitudinal joint.(See photo attached) This NCR is not compliant with the method statement Cxxx--C4-GMS-CRT00_ST005-50274 (linked below)
| 01CV - Civils | Cxxx-NCR-001694 | NCR | VWW ch.8 Damage to Waterproofing |  | Contr | BFK |  |  | 2014-12-23 | 2014-12-10 11:21 | -13 | 2014-11-05 14:38 | Tunnelling - Tunnelling General | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | Whilst removing the rebound from VWW ch.8 invert the sprayed protective layer came away and brought some Masterseal with it. Consequently the 300mm overlap required in KW20.3204 was not achieved.
| 01CV - Civils | Cxxx-NCR-001695 | NCR | Potential cold joint in the VEW secondary lining due to a delay in concrete supply |  | Contr | BFK |  |  | 2014-12-12 | 2014-12-01 13:08 | -11 | 2014-11-02 19:08 | Tunnelling - Linings - Sprayed Concrete | 3500 |  | Equipment Breakdown | Use As-Is | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | Whilst spraying the secondary lining in VEW between chainages 12 to 9 there was a delay of 3hrs due to a delay in concrete supply. This delay could cause a potential cold joint within the lining and is a non-conformance against KT20.1301.
| 01CV - Civils | Cxxx-NCR-001696 | NCR | BOS PTW incorrect spraying sequence CH 165 - 180 |  | Crossrail | PDP | BOS - Bond Street Station (West) |  | 2015-03-13 | 2015-03-02 15:12 | -11 | 2014-11-03 11:29 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The current Metrhod Statement Cxxx--C4-GMS-CRT00_ST005-500274 (Rev 04) for secondary lining defines the following for Secondary Lining: 1. Apply secondary lining (fibre SCL) from invert to 9 o' clock and from invert to 3 o' clock at full structural thickness. 2. Apply first 50 - 75 mm of upper arch (9 o' clock to 3 o' clock) 3. Complete the remaining thickness in passes of not more than 50mm. It is also understood that the bays will not excede 4m in length. During the nightshft of 02/11/14 a total length of 8m were sprayed and then went back to complete the crown section (Photo attached). There is a considerable risk of a cold joint which will need to be investigated.
| 01CV - Civils | Cxxx-NCR-001697 | NCR | VWW Secondary Lining Overspray |  | Contr | BFK |  |  | 2014-11-28 | 2014-11-19 16:51 | -9 | 2014-11-03 18:47 | Tunnelling - Linings - Sprayed Concrete | 7000 |  | Design | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After spraying the secondary lining in VWW between ch. 10 - 25, the profiles have been assessed by __ () and presented to CRL /Cxxx.It was concluded that there is overspray at chainages detailed in the approval of remedial action attached. See attached also profiles. Please note the tolerances for this tunnel was set tighter to eliminate the risk of under spray due to the following factors: - The geometry of the tunnel (inclined) - It was impossible to survey the profile while spraying as there was no place where engineer can set up. GRP dowels were installed and cut to 60 mm. The decision was made to spray this tunnel with a risk of overspray as it is far easier to remove tight spots than to remediate any under spray
| 01CV - Civils | Cxxx-NCR-001700 | NCR | BOS CH3 - Milling without agreed procedure in place |  | Crossrail | PDP | BOS - Bond Street Station (West) |  | 2014-12-19 | 2014-12-08 17:22 | -11 | 2014-11-05 10:57 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Procedure Problem - Lack of procedure | Completed |  | In the Secondary Lining Meeting at BOS on 04/11/14, referred to Cxxx-NCR-001676 and stated that at CH3 they took approx. 50mm of the compliant lining off and subsequently sprayed a full circle with new 50mm secondary lining all around (invert to invert joint). did refer to the an e-mail from the Project Manager. At the meeting the Designers Representitive stated that this has the caveat on it that Cxxx calculation and discussion with CRL / LUL are accepting the way of ‘re-working’ the defect. should wait with this work rather than go ahead and mill part of the lining away and apply a new 50mm thick lining on top (there is definitely a cold joint, is the 50mm a structural relevant part to carry / transfer load, etc). There was no formal agreement in place ie. response to Cxxx-NCR-001676 to allow works to proceed.
| 01CV - Civils | Cxxx-NCR-001702 | NCR | No adequate overlap of 200mm and not clean surface prior masterseal 345 application on repair area. |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2014-12-19 | 2014-12-17 15:16 | -2 | 2014-11-07 06:17 | Tunnelling - Tunnelling General | 4500 |  | Workmanship | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | NCR to be raised for the repair patch that was done next to CP4 lining (LHS), with no adequate overlap of 200mm at least, due to the size of it. Additionaly, the substrate was not cleaned properly the MS 345 application on the area.
| 01CV - Civils | Cxxx-NCR-001703 | NCR | 1d crown water ingress |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2014-12-05 | 2014-11-26 13:06 | -9 | 2014-11-07 09:20 | Tunnelling - Tunnelling General | 1500 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | An area of 1d tunnel profile was presented for sign off to commence secondary lining spraying. Upon inspection is was observed that a leak through the masterseal layer existed at approx 10 o'clock, chainage 75. Repair works required and SL spraying held up for 6 hours.
| 01CV - Civils | Cxxx-NCR-001704 | NCR | 1 Day Cores tested late |  | Contr | BFK |  |  | 2014-11-28 | 2014-11-13 21:51 | -15 | 2014-11-07 19:39 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Sample 745A, AP4E Secondary Lining Ch27-30. 1 day cores tested at 7days.
| 01CV - Civils | Cxxx-NCR-001705 | NCR | Missing Post Installation Photos on HLC Installation Reports |  | Contr | BFK |  |  | 2015-02-27 | 2015-01-30 17:17 | -28 | 2014-11-07 12:20 | Surveying - Instrumentation and Monitoring | 2500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | The works specification, KX10.3203 (f) (i), requires that "the records shall include (but not be limited to) the following information:...• a location sketch and photograph" to be included within installation reports. However, Photographs for the installation of some HLC instruments, have not been undertakenin accordance with the specification.
| 01CV - Civils | Cxxx-NCR-001706 | NCR | 28 day Cores - PTW |  | Contr | BFK |  |  | 2014-11-28 | 2014-11-10 13:29 | -18 | 2014-11-07 19:51 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Sample 691, PTW Secondary CH.65-68. No samples were tested at 28 days and only 4 tested. 6 Lining cores have been taken but only 4 could produce a viable test piece due to length.
| 01CV - Civils | Cxxx-NCR-001707 | NCR | 4a secondary lining cold joint |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2014-11-28 | 2014-11-24 13:46 | -4 | 2014-11-07 11:56 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the spraying of secondary lining in 4a a 6 meter bay was sprayed up to 3 and 9 o'clock (approx chainage 160-170) , followed by the next 6 meter bay being sprayed up to 3 and 9 o'clock prior to the first bay crown area being sprayed, allowing the shotcrete to cure before the crown layer was applied.
| 01CV - Civils | Cxxx-NCR-001708 | NCR | Cores - AP3E |  | Contr | BFK |  |  | 2015-01-23 | 2015-01-15 15:38 | -8 | 2014-11-16 11:39 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Sample 740 AP3E Secondary Ch. No cores tested at 1-3 days and only 4 tested at 28 days Sample 741 AP3E Secondary Ch. No cores tested at 1-3 days and only 3 tested at 28 days
| 01CV - Civils | Cxxx-NCR-001709 | NCR | BOS CH3 headwall box out reinforcement |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-11-21 | 2014-11-21 17:16 | 0 | 2014-11-07 14:27 | Tunnelling - Linings - Sprayed Concrete | 4500 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A box out was left to the left hand side of the CH3 headwall prior to spraying due to water ingress. This area was to be repaired post spray. During the night shift of the 06/11/2014 it was noticed that some of the reinforcement in the box out had been cut. BM11 from the CH3 headwall steel and BM23 from CP7 steel. These bars were then spliced by post drilling and fixing bars into the CH3 invert/lining and lapping them with the cut bars. Please see attachments for more details.
| 01CV - Civils | Cxxx-NCR-001710 | NCR | Low early age strength of secondary lining at CH3 headwall |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-11-21 | 2014-11-13 21:55 | -8 | 2014-11-07 13:45 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Whilst spraying near face steel (Second layer of secondary lining) in CH3 a fallout occured. Note that there was already an initial layer of sprayed concrete that covered far face steel and was not removed in the fallout. Area was approximately 1.50 x 0.80 x 0.12m in size. Concrete fallout was at approximately 12-1 o'clock (clock position). This was raised on RIVO (ID 3785422). Cores were taken from the lining to investigate poor early age strength given from a small panel.
| 01CV - Civils | Cxxx-NCR-001711 | NCR | BOS 4b invert slab box out reinforcement PTW chainage 200.5 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-12-19 | 2014-12-17 13:47 | -2 | 2014-11-07 14:45 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the pour of 4b a box out section was left due to water ingress. This area was to be repaired and poured at a later date. It was found on day shift 07/11/14 that the 2No 8mm bars of the B1131 mesh have been cut. PTW chainage 200.5. Location of box out at chainage 200.5m (RHS looking west). propose to drill and fix 10mm bars at the locations of the cut bars each side to provide connection. These will have 250mm embedment and use __ HIT-HY 200 Resin. Please see attachment.
| 01CV - Civils | Cxxx-NCR-001712 | NCR | BOS CH3 exposed reinforcement |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-11-21 | 2014-11-21 17:18 | 0 | 2014-11-07 18:28 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | During milling works of the secondary lining in CH3 steel has been exposed by CP9 and CP10.
| 01CV - Civils | Cxxx-NCR-001713 | NCR | CH3 Milling Works |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-12-19 | 2014-11-26 13:10 | -23 | 2014-11-10 11:53 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | undertook milling works at BOS in CH3 without prior approval from CRL/Cxxx. have never had an 'official' permit to mill for secondary lining which is why the works were done in this manner, however for all future works will agree milling extents in the secondary lining meeting with CRL & Cxxx. In addition have produced a milling procedure document by which all milling works must follow.
| 01CV - Civils | Cxxx-NCR-001714 | NCR | Missing survey information for primary lining thickness AP3A |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2014-12-08 | 2014-11-26 13:12 | -12 | 2014-11-10 17:21 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | There is a lack of profile information for the invert section at chainage 6.00 for AP3A. Between the profiles produced and the proof drilling taken in AP3A, the section between chainage 5.50 and 6.50 has no information relating to the thickeness of the primary lining in the invert. As such it is impossible to determine whether sufficient thickness in the primary lining has been achieved.
| 01CV - Civils | Cxxx-NCR-001715 | NCR | Insufficient overlap of Masterseal in section 1D |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-12-05 | 2014-12-03 17:14 | -2 | 2014-11-14 08:53 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Material | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | There is insufficient overlap of Masterseal in section 1d in PTW chaninage 100 on the north side of the cast invert slab.
| 01CV - Civils | Cxxx-NCR-001716 | NCR | Insufficient overlap of Masterseal in section 4A |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-12-05 | 2014-12-03 16:59 | -2 | 2014-11-14 08:54 | Tunnelling - Linings - Sprayed Concrete | 10000 |  | Material | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Other | Completed |  | Insufficient overlap of Masterseal in section 4A invert in PTW chainage 150-152
| 01CV - Civils | Cxxx-NCR-001717 | NCR | CH3 headwall box out |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-11-25 | 2014-11-24 14:00 | -1 | 2014-11-11 15:11 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | Due to an area of water ingress to the RHS of the CH3 Headwall a box out was created prior to the spray. This box out was then repaired, including the installation of Hydrotite and __. propose to pour Mix 27 to the secondary lining profile and then spray fire proofing over this with the rest of CH3.
| 01CV - Civils | Cxxx-NCR-001718 | NCR | Secondary lining cores @ 1 day crushed @ 5 and 6 days for the Month of November rather than within 3 days as stipulated in BFK ITP. |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-12-29 | 2014-12-03 15:49 | -26 | 2014-11-11 10:48 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | One day cores for PTW 4A/CP8 secondary lining was crushed at 5 and 6 days rather than stipulated 1 to 3 days.
| 01CV - Civils | Cxxx-NCR-001720 | NCR | Exposed steel on junction of VD4/PTW Section 1c |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-12-23 | 2014-12-10 18:24 | -13 | 2014-11-13 11:36 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 2no reinforcement bars were exposed on the invert junction of VD4 and PTW (section 1c)
| 01CV - Civils | Cxxx-NCR-001721 | NCR | No Strength tests taken |  | Crossrail | PDP | BOS - Bond Street Station (West) |  | 2014-12-19 | 2014-12-03 15:57 | -16 | 2014-11-13 12:40 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | No compressive strength test and srinkage test taken for the mixes 20 and 21 for the months of Aug, Sept and Oct 2014
| 01CV - Civils | Cxxx-NCR-001723 | NCR | BOS Hammer imprint in cast invert 4b |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-03-13 | 2015-02-24 12:24 | -17 | 2014-11-20 07:35 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | A hammer was placed on the recently cast invert slab in 4b chainage 257 PTW leaving an imprint.
| 01CV - Civils | Cxxx-NCR-001724 | NCR | 28 Day cores tested late |  | Contr | BFK |  |  | 2014-12-07 | 2014-11-18 15:16 | -19 | 2014-11-16 17:47 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Sample 723, 28 day cores tested late at 50 days 6 @ 1-3 days 6 @ 28 days 6 @ 90 days RFI 895
| 01CV - Civils | Cxxx-NCR-001725 | NCR | During the Monthly test for Secondary Lining (Mix 17.2) @ BOS Water Penetration was not carried out. |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-11-28 | 2014-11-18 15:20 | -10 | 2014-11-14 15:15 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | For the month of September 2014, water Penetration was not carried out by BOS, despite it being required as stated by ITP.
| 01CV - Civils | Cxxx-NCR-001726 | NCR | 1 day Cores tested late |  | Contr | BFK |  |  | 2014-12-23 | 2014-11-27 17:20 | -26 | 2014-11-25 08:29 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Sample 734, AP3W, Secondary CH.23-23, tested at 4 days Sample 746, VWW, Secondary CH.15-17, tested at 4 days Sample 747, VWW, Secondary CH.13-15, tested at 4 days Sample 748, VEW, Secondary CH.9-12, tested at 11 days, only 5 cores tested Sample 750, VEW, Secondary CH.3.5-2, tested at 10 days, only 4 cores tested
| 01CV - Civils | Cxxx-NCR-001727 | NCR | BOS CH3 : Contraction Joints Not Cut |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-12-09 | 2014-12-01 17:48 | -8 | 2014-11-25 19:32 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The contraction joints in the secondary lining in CH3, as detailed on drawing Cxxx-MMD-C4-DDA-Cxxx_6-00100, were not cut before the secondary lining reached a strength of 20MPa. As yet no significant cracks have been observed in the lining.
| 01CV - Civils | Cxxx-NCR-001728 | NCR | BOS PTW : Lack of Masterseal Overlap Ch 220 and 180 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-12-23 | 2014-12-17 15:20 | -6 | 2014-12-11 09:10 | Tunnelling - Linings - In-situ Concrete | 5500 |  | Damaged | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | After striking the shutter on the secondary lining cast invert around chainage 220 in PTW, it was discovered that there are areas of damage to the Masterseal on the North and South side. At chainage 180 it was damaged on the South side of the invert slab, which when repaired will not have the required 200mm overlap — see attached pictures.
| 01CV - Civils | Cxxx-NCR-001729 | NCR | Heated Masterseal PTW ch 179-192 |  | Contr | BFK |  |  | 2014-12-23 | 2014-12-16 13:07 | -7 | 2014-11-17 19:49 | Tunnelling - Tunnelling General | 4500 |  | Damaged | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Generator had been placed in invert, and exhaust had been directed at tunnel wall above. This had produced the following -Heat generated had "baked" the Masterseal 345 by indirect heat. -Masterseal 345 was not cracked at all -MS345 bond to regulating layer was still very good - (could not cut out section ) -MS345 discoloured by fumes from diesel generator ( see attached ) Areas inspected - 1/ Approx 25 sq m from shoulder to crown on one side of tunnel - main affected area ch.181-183 2/ Estimate 100 - 200 sq m of discoloured MS345 - coincided with area of very rough regulating layer ch 179-192 ( dirt retention )
| 01CV - Civils | Cxxx-NCR-001730 | NCR | Foreign object sprayed into secondary lining |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-12-19 | 2014-12-15 16:30 | -4 | 2014-11-18 16:24 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | Crossrail and Cxxx along with undertook observation of completed secondary lining as at 04/11/14 to Section 4a in PTW from Ch 180.00 to Ch 154.6, where it was noted that at a 'foreign item/material' was embedded within the secondary lining at invert level. Crossrail raised the item with on site at the time of the observation and also at the Secondary Lining meeting of 04/11/14 and requested that investigate further to determine how and why the unknown material had been embedded within the secondary lining. removed the embedded material in the same shift.
| 01CV - Civils | Cxxx-NCR-001731 | NCR | AP7a Cast Invert U1 finish out of specifications |  | Contr | BFK |  |  | 2015-03-13 | 2015-03-02 15:00 | -11 | 2014-12-07 16:09 | Tunnelling - Tunnelling General | 25000 |  | Design | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | AP7a ch 6.50- 24 cast invert U1 finish (0-20mm) is out of specifications due to an inappropriate leveled. This NCR it is not complaint with the ITP Cxxx--C4-ITP-CRT00_ST005-50144 - BOS TCR CP Cast-in situ and Sprayed Secondary Lining section B4.10 and the general note G36 from the drawing Cxxx-MMD-C4-DDJ-N105-00001 reference below. See attached the scans showing the profile of the cast invert from ch.6.50- 24 and the thickness profiles
| 01CV - Civils | Cxxx-NCR-001732 | NCR | Oil leak onto invert slab PTW |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2014-12-02 | 2014-11-26 13:15 | -6 | 2014-11-18 14:50 | Tunnelling - Linings - In-situ Concrete | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | Oil has leaked onto the invert slab in PTW at approximately chainage 70.
| 01CV - Civils | Cxxx-NCR-001733 | NCR | Secondary lining early age strength BOS |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-12-23 | 2014-12-19 15:08 | -4 | 2014-11-19 09:59 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Out of all the secondary lining sprayed so far in BOS starting at the end of August a total of 22 tests have been completed where 40 should have been completed. The requirement as per FCD 1141 is that an early age stregth panel should be sprayed every 24hrs.
| 01CV - Civils | Cxxx-NCR-001734 | NCR | Insufficient compressive strength testing BOS sprayed secondary lining |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-01-09 | 2015-01-12 15:38 | 3 | 2014-11-19 10:43 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | In BOs so far a total of 3475m^3 of secondary lining has been sprayed. This being the case 69 every 50m^3 comppressive strengh should have been taken. A total of 31 compressive strength tests have actually been taken.
| 01CV - Civils | Cxxx-NCR-001735 | NCR | Washouts of cast invert mix not being done at required frequency BOS |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-01-16 | 2014-12-22 13:21 | -25 | 2014-11-19 11:32 | Tunnelling - Linings - In-situ Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Washouts from cast invert concrete should have been carried out once in a week when inverts are being poured. Out of 10 weeks where testing should have taken place 4 tests have been done.
| 01CV - Civils | Cxxx-NCR-001736 | NCR | Hydraulic oil spill to invert slab PTW/CP4 |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2014-12-19 | 2014-12-09 13:53 | -10 | 2014-11-19 17:30 | Tunnelling - Linings - In-situ Concrete | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Hydraulic oil spill to the invert slab in PTW at approximatly chaiange 220. Photo attached showing extent of spill.
| 01CV - Civils | Cxxx-NCR-001737 | NCR | In September 2014 @ BOS with regards to the Regulating Layer, on two occassions BFK where short of ITP stipulated 6 cores for compressive strength @28 days, also in October 2014 @ BOS no testing of the Regulating layer was carried out ie: compressive stre |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-12-19 | 2014-12-05 14:19 | -14 | 2014-11-20 15:23 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | In September 2014 @ BOS with regards to the Regulating Layer, on two occassions where short of ITP stipulated 6 cores for compressive strength @28 days, also in October 2014 @ BOS no testing of the Regulating layer was carried out ie: compressive strength and Drying Shrinkage.
| 01CV - Civils | Cxxx-NCR-001738 | NCR | CH3 Sprayed Concrete Checklist Form 50 sheets are missing information |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2014-12-22 | 2014-11-27 16:10 | -25 | 2014-11-24 10:58 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Sprayed Concrete Lining Checksheet form 50 are missing the follwing information: Chaiange Valid - Advance no: 97, 1 Pre spray check - before spray flow - Advance No: 90, 71, 69, 44A, 40, 31, 17, 16, 11, 3 Pre spray check - after batching flow - Advance No: 71, 69, 44A, 40, 31, 16,11 Post spray check signature - Advance No. 94,93,91,90,43, 20, 11 Spaying times - Advance No. 98,85, 71, 58, 44A, SCL Temp after batching - Advance No: 78, 71, 69, 44A, 40, 31, 16, 11, 3 SCL Temp before spraying- Advance No: 71, 69, 48B, 44A, 40, 31, 17 , 16, 11 Air Temp at face - Advance No: 75, 71, 69, 48B, 44A, 40, 31, 24, 18, 17, 16, 11
| 01CV - Civils | Cxxx-NCR-001739 | NCR | In AP3a polythene black sheet sprayed in secondary lining |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-12-08 | 2014-12-01 13:15 | -7 | 2014-11-24 12:51 | Tunnelling - Linings - Sprayed Concrete | 2500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | A section of the polythene curtain, hung between AP3a and PTW, was sprayed/cast into the secondary lining at ch.00 (PTW side). It was located a the bottom of the invert slab at approximately 5 o'clock whilst looking toward the Masterplan shaft. Photos have been attached.
| 01CV - Civils | Cxxx-NCR-001740 | NCR | BOS PTW 1A Area : Damage to Masterseal Close to Invert Slab, Approx. Ch. −50 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-12-23 | 2014-12-16 14:49 | -7 | 2014-12-10 08:56 | Tunnelling - Linings - In-situ Concrete | 4500 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There is potential damage to the Masterseal close to the slab in PTW at the end of the slab (approx. Ch. −50), close to the eastern headwall. It will not be possible to achieve the required overlap for a repair. Refer to attached picture <1a Invert for headwall Ch.JPG>.
| 01CV - Civils | Cxxx-NCR-001741 | NCR | BOS PTW : Injecting Tunnel Lining Close to East Headwall |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-12-23 | 2014-12-17 15:13 | -6 | 2014-12-09 14:59 | Tunnelling - Linings - In-situ Concrete | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Due to injecting close to the eastern headwall, we are unable to achieve sufficient lap of Masterseal.
| 01CV - Civils | Cxxx-NCR-001743 | NCR | AP2W - Under thickness Secondary Lining ch 7-21 |  | Contr | BFK |  |  | 2015-02-06 | 2015-02-03 11:05 | -3 | 2014-11-25 18:52 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | After spraying the secondary lining in AP4E between ch. 7 - 21, the profiles have been assessed by __ () and presented to __ (Cxxx).It was concluded that there is concern with under thickness at chainages detailed in the snag list attached as the 200mm thickness was not achieved.
| 01CV - Civils | Cxxx-NCR-001744 | NCR | GS BOS5 field grout testing results for Pre-Treatment missed |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-12-09 | 2014-11-25 18:31 | -14 | 2014-11-25 10:16 | Geotechnical Engineering - Compensation Grouting | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | As per the attached field grout testing results for Pre-treatment works in BOS 5 shaft, it’s noted that 4no. bleed test results are missing for passes carried-out on 2/4/2012, 3/4/2012, 12/4/2012 & 31/5/12, resulting fail to comply with the specification as per ITP
| 01CV - Civils | Cxxx-NCR-001745 | NCR | Polythene curtain sprayed into fire proofing in CP8 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-12-17 | 2014-12-10 10:05 | -7 | 2014-11-26 08:28 | Tunnelling - Linings - Sprayed Concrete | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Whilst spraying fire proofing layer in section 3b, part of the polythene curtain was sprayed into the lining between 10 and 2 o'clock.
| 01CV - Civils | Cxxx-NCR-001746 | NCR | AP3W - Under thickness secondary lining ch. 7.50-30 |  | Contr | BFK |  |  | 2015-02-23 | 2015-02-09 18:07 | -14 | 2014-11-25 18:53 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After spraying the secondary lining in AP3W between ch. 7.5 - 30, the profiles have been assessed by __ () and presented to __ (Cxxx).It was concluded that there is concern with under thickness at chainages detailed in the snag list attached as the 200mm thickness was not achieved.
| 01CV - Civils | Cxxx-NCR-001748 | NCR | Box out of invert leak in section 4b PTW ch. 228 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-02-27 | 2015-02-24 13:44 | -3 | 2014-11-25 16:57 | Tunnelling - Linings - Sprayed Concrete | 9500 |  | Workmanship | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Other | Completed |  | A leak has been found by the invert slab in section 4b chainage 228 in PTW. It is on the left hand side of the slab, looking westbound. wish to proceed with spraying secondary lining and therefore will box out this area.
| 01CV - Civils | Cxxx-NCR-001749 | NCR | TCR Regulating layer Testing - June - September |  | Contr | BFK |  |  | 2015-02-09 | 2015-01-15 16:54 | -25 | 2015-01-12 14:31 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | There was a lack of compressive strength testing and drying shrinkage testing during June - September. June - Compressive Testing but no shrinkage (Sample 619), July - no testing August - Compressive testing but no shrinkage (sample 676) September - No testing
| 01CV - Civils | Cxxx-NCR-001750 | NCR | AP3E Under thickness Secodnary Lining ch. 10- 33 |  | Contr | BFK |  |  | 2014-12-23 | 2014-12-19 16:50 | -4 | 2014-11-25 20:15 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After spraying the secondary lining in AP3E between ch. 10 - 33, the profiles have been assessed by __ () and presented to __ (Cxxx).It was concluded that there is concern with under thickness at chainages detailed in the snag list attached as the 200mm thickness was not achieved.
| 01CV - Civils | Cxxx-NCR-001751 | NCR | Damage to Masterseal PTW section 1C |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-01-16 | 2015-01-12 16:04 | -4 | 2014-11-26 08:23 | Tunnelling - Linings - Sprayed Concrete | 4500 |  | Damaged | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | Upon inspection of section 1c in PTW, it was noticed that there was damage to the Masterseal. It was located by the invert slab and was apparent on both sides at ch20 and 33.5.
| 01CV - Civils | Cxxx-NCR-001752 | NCR | PTW- Incomplete F50s |  | Contr | BFK |  |  | 2014-12-17 | 2014-12-16 14:35 | -1 | 2014-11-26 13:58 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Some PTW F50 forms for excavation and primary lining and primary lining thickness has missing details such as Nozzleman name and signature, Excavation start and finish time spray start and finish time.
| 01CV - Civils | Cxxx-NCR-001753 | NCR | PTW (ch181 to 217) slab level out of design tolerence. |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-02-10 | 2015-02-03 17:41 | 358 | 2014-11-26 13:18 | Tunnelling - Linings - In-situ Concrete | 8500 |  | Incorrect Installation | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In PTW between chainage 181 and 217, survey indicates reduced level of invert slab is lower than the minimum (95.027mod).
| 01CV - Civils | Cxxx-NCR-001754 | NCR | BOS Oil spillage on cast invert in 3B |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-12-10 | 2014-12-01 13:25 | -9 | 2014-11-26 14:03 | Tunnelling - Linings - In-situ Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | It was noticed on the 24/11/2014 that there was an oil spillage on the cast invert along 3B. This is against KF10.3231 Protection of Finished Concrete - The finished concrete surfaces shall be protected from damage and from rust or oil staining, and any necessary protective measures shall be adopted. have ordered a number of large 'nappies' to place underneath plant to prevent oil from damaging permanent works. These were not in place.
| 01CV - Civils | Cxxx-NCR-001755 | NCR | BOS Oil leak from Merlo in 3B |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-12-10 | 2014-12-01 13:37 | -9 | 2014-11-26 14:07 | Tunnelling - Linings - In-situ Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | It was noticed on the 25/11/2014 that there was an oil spillage on the cast invert in 3B where the Merlo was parked. There was no protection to the cast invert in place. This is against KF10.3231 Protection of Finished Concrete - The finished concrete surfaces shall be protected from damage and from rust or oil staining, and any necessary protective measures shall be adopted.
| 01CV - Civils | Cxxx-NCR-001756 | NCR | 4 No. Re-Bar missing from AP1 CH1 Junction Invert Slab Pour. |  | Contr | BFK |  |  | 2015-01-16 | 2015-01-08 16:28 | -8 | 2014-11-26 17:45 | Tunnelling - Linings - In-situ Concrete | 4500 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Lateral Rebar Barmark 01 and 13 were not completely installed as per drawing Cxxx-MMD-C4-DDD-N105-5-00485 Section A-A. 2 No. of each barmark were not installed prior to pouring the invert of the CH1 and AP1 Junction. The requirement of installing the bars was noted on a Concrete Reinforcement Checklist dated 12/11/14, this was however missed. If these are not installed barmark 05 will have noting to lap.
| 01CV - Civils | Cxxx-NCR-001757 | NCR | BOS 4a Secondary Lining Sprayed beyond cast insitu invert |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-12-19 | 2014-12-10 10:06 | -9 | 2014-12-01 16:02 | Tunnelling - Linings - Sprayed Concrete | 2500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The secondary lining crown was sprayed approximately 0.5m ahead of the cast invert at chainage 145-. This area of extended spray was not included in the pre spray checksheet.
| 01CV - Civils | Cxxx-NCR-001758 | NCR | PTW- Missing F50 Forms |  | Contr | BFK |  |  | 2014-12-17 | 2014-12-16 15:38 | -1 | 2014-11-26 17:07 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Missing form 050 for PTW advance 210 and advance 315
| 01CV - Civils | Cxxx-NCR-001759 | NCR | Missing Re-injectable injection tube in secondary lining at face of Adit S1 to Goslett Yard Box. |  | Contr | BFK |  |  | 2014-12-11 | 2014-12-10 11:22 | -1 | 2014-11-27 09:25 | Tunnelling - Grouting | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Re-injectable Grout tube within the secondary lining at the face of the S1 Adit/Goslett was missed when spraying occured.
| 01CV - Civils | Cxxx-NCR-001761 | NCR | Insufficient thickness of Masterseal at final inspection to pour the VEW to GYB connection's sill |  | Crossrail | XRL |  |  | 2014-12-12 | 2014-12-08 18:08 | -4 | 2014-11-28 01:01 | Tunnelling - Linings - In-situ Concrete | 5000 |  | Incomplete Works | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Masterseal applied to the D-Wall was clearly under thickness over a week before the sill's final inspection and this was pointed out to Shift Engineers & Shift Managers to rectify before going on with reinforcement installation. With the reinforcement finally fixed over the Masterseal, it did not look like any additional layers had been applied. So an in informal thickness test on the 25/11/2014 night shift revealed there to be only 1-1.5mm of Masterseal thickness in a location that appeared representative of the rest of the water-proofing. As a result it was agreed more Masterseal needed to be added. On the 26/11/2014 night shift Crossrail was invited to witness the final inspection before pouring the sill. There were locations that did not look to have been re-painted. After debate about whether any thickness tests post the re-application had been carried out during the day shift (there were no available signed check-sheets), it was agreed to undertake a thickness test. This initial location thickness looked to be less than 1mm, further tests showed there were numerous areas that needed more thickness.
| 01CV - Civils | Cxxx-NCR-001762 | NCR | Diesel spillage on slab invert in PTW |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-01-16 | 2014-12-03 16:08 | -44 | 2014-11-29 07:50 | Tunnelling - Linings - In-situ Concrete | 500 |  | Equipment Breakdown | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Diesel spillage occurred onto top of slab of PTW in the vicinity of AP3A when refuelling plant last night on the 28/11/14. A similar incident also occurred with the Merlo on the 26/11 NS
| 01CV - Civils | Cxxx-NCR-001763 | NCR | PTW - Ch 153 - Damage to waterproofing at Invert |  | Contr | BFK |  |  | 2014-12-19 | 2014-12-15 16:40 | -4 | 2014-12-01 11:51 | Tunnelling - Tunnelling General | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | Following completion of the cast invert at ch .153, have cleaned the invert and found out that the waterproofing in the invert was damaged close to the cast invert concrete and de-bonded due to a leak. As the waterproofing was de- bonded there was no a proper overlap.(See attached photos) This NCR is not compliant with KW20.3204
| 01CV - Civils | Cxxx-NCR-001764 | NCR | TCR - AP4W - Cast invert - Mesh installation |  | Contr | BFK |  |  | 2014-12-15 | 2015-01-05 14:09 | 21 | 2014-12-01 16:58 | Tunnelling - Linings - In-situ Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During construction of Cast in situ invert in AP4W the requirement of installing B283 mesh (Drawing Cxxx-MMD-C4-DDD-N105_5-00407 to was missed. The invert was checked by and all parties without noticing the mesh requirement.
| 01CV - Civils | Cxxx-NCR-001765 | NCR | BOS 4a delay in rebound removal at chainage 145 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-01-10 | 2014-12-19 15:26 | 343 | 2014-12-01 16:41 | Tunnelling - Linings - Sprayed Concrete | 4500 |  | Workmanship | Rework | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | After spraying up to chainage 145 in 4a there was a delay in removing the rebound along the leading edge, this caused it to gain strength and become harder to remove.
| 01CV - Civils | Cxxx-NCR-001766 | NCR | BOS VD3 : Damage to Masterseal in front of invert slab (approx. Ch. 6) |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-12-23 | 2015-01-05 14:33 | 13 | 2014-12-11 09:15 | Tunnelling - Linings - In-situ Concrete | 6500 |  | Damaged | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | At the south side of the VD3 invert slab, concrete appears to have leaked out from the underside of the invert shutter, and there appears to be damage to the Masterseal adjacent to the slab. It will not be possible to achieve the required overlap of Masterseal in this area.
| 01CV - Civils | Cxxx-NCR-001767 | NCR | BOS 1c box out PTW chainage 15 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-01-10 | 2015-01-08 15:52 | -2 | 2014-12-01 17:49 | Tunnelling - Linings - Sprayed Concrete | 7500 |  | Workmanship | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Other | Completed |  | During the pour of 1c a box out section was left due to water ingress. This area is to be repaired and poured at a later date. BOS 1c box out PTW chainage 15.
| 01CV - Civils | Cxxx-NCR-001768 | NCR | BOS 1c box out chainage PTW -5 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-01-09 | 2015-01-05 14:42 | -4 | 2014-12-02 09:07 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | During the pour of 1c a box out section was left due to water ingress. This area is to be repaired and poured at a later date. BOS 1c box out chainage PTW -5.
| 01CV - Civils | Cxxx-NCR-001769 | NCR | BOS PTE/LCE2 : Cracks in Crown of Secondary Lining Around PTE Ch. 0 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-01-24 | 2015-01-19 17:06 | -5 | 2014-12-12 09:18 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Use As-Is | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | After spraying secondary lining to LCE2 and PTE, a randomly oriented map pattern of hairline cracks have been observed in the crown of the tunnel. The most likely explanation for this is plastic shrinkage cracking, as described in Section 5.3 of Concrete Society Technical Report 22: Non-structural cracks in concrete (4th Ed.)
| 01CV - Civils | Cxxx-NCR-001770 | NCR | CP4 Primary Lining Underthickness |  | Crossrail | XRL |  |  | 2014-12-19 | 2014-12-08 18:18 | -11 | 2014-12-03 08:52 | Tunnelling - Linings - Sprayed Concrete | 10000 |  | Incorrect Installation | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | It was stated in the RESS (attached) and FCD-001183 (attached) for CP4, as a result of the clash with LP9 lobby, that the primary lining thickness of 250mm must be maintained. Profile comparisons for the thickness check (attached) showed underthickness of up to 107mm. The Non-Conformance was discussed and minuted (attached) by the SRG on 24/11/2014. The profile was re-sprayed and thickness checks (attached) were presented to the SRG on 27/11/2014. Underthickness of up to 9mm deemed acceptable by the SRG.
| 01CV - Civils | Cxxx-NCR-001771 | NCR | Wrong forms used for thickening works PTE Primary Lining BOS |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-01-09 | 2014-12-05 14:46 | -35 | 2014-12-03 10:31 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Wrong forms (-050) have been used for thickening works PTE primary lining instead of using form -050a. This might have occured due to the following two reasons. 1. Human error 2. Printer broke down Effected chainage is from 6.3 to 27.3. Also shown on the check sheets attached
| 01CV - Civils | Cxxx-NCR-001772 | NCR | Damaged Masterseal PTW invert ch. 196 |  | Contr | BFK |  |  | 2014-12-17 | 2014-12-17 10:54 | 0 | 2014-12-03 11:19 | Tunnelling - Tunnelling General | 3500 |  | Damaged | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | Debonded / damaged MS at edge of cast invert in PTW at CH 196 due to leak. It was noticed a blister was formed in the Masterseal at this area. Area is within 300mm of cast invert therefore insufficient MS lap for remedial patch.
| 01CV - Civils | Cxxx-NCR-001773 | NCR | 1 Day Cores tested late |  | Contr | BFK |  |  | 2015-02-06 | 2015-01-16 13:41 | -21 | 2015-01-10 17:27 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The following sets of 1-3 days cores were tested late: Sample 762, AP4W Secondary, CH27-30, tested at 7days Sample 763, AP4W Secondary, CH21-19, tested at 6 days Sample 765, AP4W Secondary, CH19-16, tested at 6 days Sample 766, S3 Secondary, CH3.5 7.3, tested 5 days Sample 768, PTW Regulating, CH -10 to -38
| 01CV - Civils | Cxxx-NCR-001774 | NCR | Exposed mesh im AP1 -PTW junction |  | Contr | BFK |  |  | 2014-12-19 | 2015-01-07 16:28 | 19 | 2014-12-03 15:04 | Tunnelling - Linings - Sprayed Concrete | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | When milling in the crown some mesh in the RHS of the AP1 opening in PTW in the crown was exposed and damaged. Also, while removing a hollow section the rebar was exposed. Attached Regulating Approval after remedials done.
| 01CV - Civils | Cxxx-NCR-001775 | NCR | Pressure gauge illegible and faulty |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2014-12-23 | 2014-12-17 16:30 | -6 | 2014-12-05 15:14 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Pressure gauge used in section 5b of PTE was observed to be faulty and the pessure dial was not readable.
| 01CV - Civils | Cxxx-NCR-001776 | NCR | In the month of August 2014 on 2 occassions no dry fibre content was carried out on the one day cores, also on many occassions within that same month no dry fibre content was carried out on 28 day cores. Also sample number SCL 656 was crushed @ 5 days rat |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-12-23 | 2014-12-15 14:04 | -8 | 2014-12-05 12:07 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | In the month of August 2014 on 2 occassions no dry fibre content was carried out on the one day cores, also on many occassions within that same month no dry fibre content was carried out on 28 day cores. Also sample number SCL 656 was crushed @ 5 days rather than 1-3 days. (On all three instances above ITP stipulates that dry fibre content should be done on 2 one day and twentyeight days cores and also cores should be crushed with 1 -3 days and at 28 days)
| 01CV - Civils | Cxxx-NCR-001777 | NCR | ES1 Stitch Drilling: Deviation from RESS |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-02-20 | 2015-02-03 09:53 | -17 | 2014-12-06 15:52 | Tunnelling - Linings - In-situ Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Stitch drilling to ES1 softeye was not undertaken in the correct sequence as stated in the RESS. Vertical drillings were not fully finished before the perimeter line was commenced.
| 01CV - Civils | Cxxx-NCR-001778 | NCR | PTE ch 24- 128 Under thickness Fireproofing |  | Contr | BFK |  |  | 2015-02-06 | 2015-02-03 09:55 | -3 | 2014-12-10 20:13 | Tunnelling - Linings - Sprayed Concrete | 17500 |  | Workmanship | Use As-Is | 2 (6-60k) | Complete | Material/Preservation Problems - Other | Completed |  | After spraying the fireproofing layer in PTE between ch. 24 - 128, the profiles have been assessed by __ () and presented to __ (Cxxx).It was concluded that there is concern with under thickness at chainages detailed in the snag list attached as the 50mm thickness was not achieved.
| 01CV - Civils | Cxxx-NCR-001780 | NCR | Two new Amber Trigger breached in Davies Street PLPs |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-12-19 | 2014-12-16 10:53 | -3 | 2014-12-08 18:26 | Geotechnical Engineering - Settlement | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Two New Amber Triggers breached in Davies Street PLPs between: • B07LP255-259 • B07LP254-258 Actions: • Re-survey of the area was carried out and the data checked. The Amber triggers have been verified. • For more monitoring details please refer to yesterday’s SRG Minutes. • Issue will be discussed in tomorrow’s CTC meeting (09/12/2014 11:00 hrs) • SCL Progress: AP1 Adv 6 excavation on-going
| 01CV - Civils | Cxxx-NCR-001781 | NCR | Lack of Masterseal overlap CP5/PTW |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-01-30 | 2015-01-30 13:19 | 0 | 2014-12-09 10:10 | Tunnelling - Linings - Sprayed Concrete | 8500 |  | Damaged | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | on 06/12/2014 and 07/12/2014 it was noticed that the Masterseal was damaged at the end of the invert slab in CP5/PTW junction in section 1D. . There is not enough masterseal protruding from under the slab in order to achieve a 200mm lap.
| 01CV - Civils | Cxxx-NCR-001782 | NCR | Insufficient thickness smoothing layer AP3A |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-02-16 | 2015-02-11 15:48 | -5 | 2014-12-09 12:36 | Tunnelling - Linings - Sprayed Concrete | 25000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Scans of the AP3a smoothing layer indicate multiple areas of insufficient thickness (<50mm). Although relatively localized, in the worst case up to three square meters of tunnel does not meet the design specification. To clarify this issues the following has been attached to this NCR. Attachment 1 : A plot of applied smoothing layer thickness between AP3A chainage 11.5m and 19.5m. Attachment 2: A plot of smoothing layer profile between AP3A chainage 11.5m and 19.5m. When comparing the areas of insufficient thickness with the design profile it is clear that there is enough tolerance remaining to effectively bulk out with smoothing mix 21 such that a total thickness >50mm is achieved throughout the tunnel. The annotation of attachment 1 provides this information. In these circumstances feel the most appropriate method of repair is the following: 1. Identify the areas with insufficient in the field. This will be acheived using __ Easychecker survey software. The areas will be marked up clearly. 2. Prepare each area for reapplication of smoothing layer. Surface roughness will assessed. If descaling is required will proceed to remove loose material with pneumatic hand tools. Each area with then be jetwashed. 3.Spray additional smoothing layer mix, by hand, on the areas of insufficient thickness. The applied thickness will be controlled by the Engineer using __ Easychecker survey software. 4.The tunnel will be rescanned to confirm the total thickness of smoothing layer meets the design specification. 5.If required by Cxxx/CRL, will proceed to take cores in the areas to confirm the quality of bonding between the cured and freshly sprayed layer. feel that the quality of bonding between a cured and additional layer of Mix 21 is sufficient to carry out the repair work in such a manner. Evidence to support this can be found in the report titled Cxxx--C4-RGN-CRT00_ST005-51144-Investigation into bonding of subsequent layers of smoothing layer mix 21 at Crossrail Bond Street (also attached). 10.2.15 - Using guidance provided by the CEG in PMC10179, the areas of under thickness have been categorised. All areas within AP3A are not subject to a train fire and meet the guidance as stated below (see attached marked up scans with file name 10.2.15 scans): A.2 Areas not subject to a train fire In passenger areas (cross-passages / concourses) larger patches of fire-proofing less than 50mm, but more than 30mm, are accepted, on the basis that the EUREKA fire curve does not apply. In practice the largest of these areas are: 1m long x 4m measured around the circumference of the tunnel. 3m long x 1m measured around the circumference of the tunnel. therefore propose to use as is
| 01CV - Civils | Cxxx-NCR-001783 | NCR | TCR - VWW tunnel fireproofing lining |  | Contr | BFK |  |  | 2015-08-24 | 2015-08-18 23:44 | -6 | 2014-12-09 13:00 | Tunnelling - Linings - Sprayed Concrete | 15000 |  | Workmanship | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The VWW tunnel fireproofing has been oversprayed in some areas as per profiles document attached. Also, in small areas the thickness is slightly below the 50mm to be achieved.
| 01CV - Civils | Cxxx-NCR-001784 | NCR | BOS PTW : Plywood placed over damp patches before spraying over with Masterseal |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-01-09 | 2014-12-22 13:25 | -18 | 2014-12-10 08:39 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Supervision/Management | Use As-Is | 3 (3-6k) | Complete | Procedure Problem - Other | Completed |  | In PTW approx. Ch. -50, plywood was placed over damp patches on the regulating layer and sprayed over with Masterseal. Once the surrounding Masterseal had cured, the plywood was removed and the primary lining injected with resin. After sealing the leaks, all packers were removed, the resin was cleaned off and Masterseal painted over. While there is no effect on the permanent works since the damp areas were remediated, the use of plywood is not in accordance with ’s method statement for spray-applied waterproofing.
| 01CV - Civils | Cxxx-NCR-001785 | NCR | AP8 Primary Lining Milling at CP2 Junction |  | Contr | BFK |  |  | 2015-01-16 | 2015-01-07 16:26 | -9 | 2014-12-10 16:34 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | During milling of the primary lining in AP8 with CP2 junction (in preparation of secondary lining works), 3 no. bars have been exposed with of the tunnel junction steel, two of which have been damaged (as seen in the attached picture). These include: - x2 no. 10mm BM20 tunnel junction bar, 1 exposed only, 1 exposed and damaged - x1 no. 25mm BM72 longitudinal bar at approximately axis level, exposed and damaged
| 01CV - Civils | Cxxx-NCR-001786 | NCR | BOS WTH AP1 Advance 3 Spraying Sequence |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-12-24 | 2014-12-15 16:44 | -9 | 2014-12-10 10:56 | Tunnelling - Linings - Sprayed Concrete | 2500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The sequence detailed in the approved RAMS document was not followed during the construction of Advance 3 of the AP1 tunnel: The invert was sprayed to full profile prior to sealing the crown profile and face. The RAMS states that the full profile and face should be supported first. Rebound should then cleaned out of the invert to ensure Primary Lining achieves full thickness. Full Primary Lining then sprayed starting with the invert working up to the crown
| 01CV - Civils | Cxxx-NCR-001787 | NCR | BOS WTH AP1 Advance 9/10 Spraying Sequence |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-01-16 | 2015-01-05 11:36 | -11 | 2014-12-10 10:59 | Tunnelling - Linings - Sprayed Concrete | 2500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The sequence detailed in the approved RAMS document was not followed during the construction of Advance 9 & 10 of the AP1 tunnel.
| 01CV - Civils | Cxxx-NCR-001788 | NCR | BOS WTH AP1 Advance 2a Profiles |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-12-23 | 2014-12-17 16:16 | -6 | 2014-12-10 11:22 | Tunnelling - Linings - Sprayed Concrete | 2500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | A breakdown of communication lead to the Excavation and Primary Lining Profiles of Advance 2a not being delivered promptly to the SRG.
| 01CV - Civils | Cxxx-NCR-001789 | NCR | PTW Sump - Rebar exposed |  | Contr | BFK |  |  | 2015-01-23 | 2015-01-23 13:34 | 0 | 2014-12-10 18:08 | Tunnelling - Tunnelling General | 6500 |  | Workmanship | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | During removal of the protective layer on the PTW sump (in preparation of secondary lining works), 1 no. bar has been exposed and bent. The bar in question is: - BM 02 - B16 See relevant drawings attached.
| 01CV - Civils | Cxxx-NCR-001791 | NCR | Leak Injection Through Secondary Lining - PTW Chainage 101m |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-01-26 | 2015-01-19 16:31 | -7 | 2015-01-12 23:10 | Tunnelling - Linings - Sprayed Concrete | 4500 |  | Supervision/Management | Use As-Is | 3 (3-6k) | Complete | Procedure Problem - Lack of procedure | Completed |  | Packers were found in the secondary lining of PTW at chainage 101m. It has been assumed that this area has been injected. Injection through secondary lining is currently not approved.
| 01CV - Civils | Cxxx-NCR-001792 | NCR | Pitting In Smoothing Layer - PTE Chainage 20 - 40m |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-12-25 | 2014-12-19 17:08 | -6 | 2014-12-11 11:22 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | It has been identified that there are a number of areas of localized pitting in the recently sprayed fireproofing layer between PTE CH 20m & 40m. The photos attached illustrate the localized pitting. From inspection it has been found that the diameter of the indentations range from 20 to 60mm. The depth of the indentations range from 10 to 30mm feel the following are the possible causes of this pitting: 1.Balling of aggregate in mix 21. 2.Accumulation of aggregate in the nozzle resulting in build up in pressure then blowout.
| 01CV - Civils | Cxxx-NCR-001793 | NCR | Pitting In Smoothing Layer - CH3 Chainage 15m |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-01-09 | 2015-01-05 11:38 | -4 | 2014-12-19 14:00 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | It has been identified that there is an of of localised pitting in the recently sprayed fireproofing layer in CH3 Chainage 15. The diameter of the indentations range from 20 to 50mm. The depth of the indentations range from 10 to 25mm feel the following are the possible causes of this pitting: 1.Balling of aggregate in mix 21. 2.Accumulation of aggregate in the nozzle resulting in build up in pressure then blowout.
| 01CV - Civils | Cxxx-NCR-001794 | NCR | Mistake in Secondary Lining ITP |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-12-23 | 2014-12-17 15:24 | -6 | 2014-12-11 14:41 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | ITP Cxxx--C4-ITP-CRT00_ST005-50112 Rev 1 has mistake on row B3.5 Plant check stating that "Daily plant inspection check sheet" is deliverable record to CRL.
| 01CV - Civils | Cxxx-NCR-001795 | NCR | Slab level in CP7 out of tolerence |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-12-23 | 2015-01-05 11:43 | 13 | 2014-12-11 15:09 | Tunnelling - Linings - In-situ Concrete | 1500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | In section 3b between chainage 8 -16, survey indicates reduced level of invert slab is lower than the minimum (96.832).
| 01CV - Civils | Cxxx-NCR-001796 | NCR | Leak through the Masterseal in PTW Ch. -57 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-12-23 | 2015-01-05 17:58 | 13 | 2014-12-12 12:41 | Tunnelling - Linings - Sprayed Concrete | 4500 |  | Material | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | It was observed by that there was a leak through the Masterseal in PTW chainage -57 (Section 1a), after the area had been signed off by CRL/Cxxx.
| 01CV - Civils | Cxxx-NCR-001797 | NCR | BOS 1a PTW chainage -10 to -57 invert slab damage |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-01-23 | 2015-01-20 15:19 | -3 | 2014-12-12 14:42 | Tunnelling - Linings - In-situ Concrete | 7500 |  | Damaged | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During cleaning rebound from the invert slab in 1a PTW chainage -10 to -57 the slab has been damaged. A bucket with teeth was used to clean the area and this has resulted in indents approximately 5mm deep in the slab.
| 01CV - Civils | Cxxx-NCR-001798 | NCR | BOS 4b box out PTW chainage 200 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-12-23 | 2014-12-18 12:33 | -5 | 2014-12-12 18:17 | Tunnelling - Linings - Sprayed Concrete | 5500 |  | Workmanship | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | During the pour of 4ba box out section was left due to water ingress. This area is to be repaired and poured at a later date. BOS 4b box out PTW chainage 200.
| 01CV - Civils | Cxxx-NCR-001799 | NCR | BOS 4b box out PTW chainage 202 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-12-23 | 2014-12-18 13:15 | -5 | 2014-12-12 18:20 | Tunnelling - Linings - Sprayed Concrete | 6500 |  | Workmanship | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Other | Completed |  | During the pour of 4b box out section was left due to water ingress. This area is to be repaired and poured at a later date. BOS 4b box out PTW chainage 202.
| 01CV - Civils | Cxxx-NCR-001800 | NCR | BOS 4a box out PTW chainage 145 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-01-09 | 2015-01-07 16:42 | -2 | 2014-12-12 18:25 | Tunnelling - Linings - In-situ Concrete | 6500 |  | Workmanship | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Other | Completed |  | During the pour of 4a box out section was left due to water ingress. This area is to be repaired and poured at a later date. BOS 4a box out PTW chainage 145.
| 01CV - Civils | Cxxx-NCR-001801 | NCR | Failure in ATS 5 at Bond Street area above AP1 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-12-26 | 2015-01-08 16:36 | 13 | 2014-12-12 18:48 | Geotechnical Engineering - Compensation Grouting | 8500 |  | Equipment Breakdown | Repair | 2 (6-60k) | Complete | Personnel Error - Inattention to detail | Completed |  | A failure in the ATS5 at BOS area was noticed on the 8/12/14 and minuted in the SRG meeting on the 9/12/14. Daily Manual monitoring (__s / PLPs), HLCs and SAAs monitoring installed above the AP1 excavation area are showing stable data. It was planned to replace the ATS5 on the 18th December 2014 but was working to replace it as before that date. The excavation of the AP1 was stopped in the SRG taken the 11/12/2014 due to this issue. A replacement of the ATS was carried out the evening on the 11/12/2014. The ATS5 was working from that night but due to a network issue the data could not be processed. As part of the actions discussed in the SRG taken the 11/12/2014, a SRG Meeting was called on the 12/12/2014 at 8:00am. In this meeting was agreed to send the data without being processing to all the Attendees for review. Following this action the RESS was signed and the excavation of AP1 re-started.
| 01CV - Civils | Cxxx-NCR-001802 | NCR | PTW Slab Level - Out of Tolerance |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-02-27 | 2015-02-06 13:24 | -21 | 2014-12-15 11:16 | Tunnelling - Linings - Sprayed Concrete | 18500 |  | Incorrect Installation | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | invert level survey in PTW between chainages -22m & 217m indicate multiple locations that are out of tolerance. The design level of PTW slab is 95.047mAod. The minimum level is 95.027mAod. In summary: CH0 to -22: High: maximum 19mm (95.066mAod) CH36 - 50m: High: maximum 15mm (95.062mAod) CH57 - 73m: High maximum 19mm (95.066mAod) CH111 - 115: Low maximum 17mm (95.010mAod) CH121 - 131: High maximum 11mm (95.058mAod) CH150 - 161: Low maximum 22mm (95.005mAod) CH215: Low maximum 33mm (94.994mAod) Level surveys attached for clarification.
| 01CV - Civils | Cxxx-NCR-001803 | NCR | PTE Slab Level - Out of Tolerance |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-02-27 | 2015-02-11 18:09 | -16 | 2014-12-15 11:12 | Tunnelling - Linings - Sprayed Concrete | 18500 |  | Incorrect Installation | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | invert level survey in PTE between chainages 0m & 60m indicate multiple locations that are low and out of tolerance. The design level of PTE slab is 95.047mAod. The minimum permissible level is 95.027mAod. As the level survey attached shows, multiple locations along the slab are lower than the minimum permissible level of 95.027mAod. The worst effected area is chainage 63m with a reduced level of 94.994mAod (30mm out of tolerance).
| 01CV - Civils | Cxxx-NCR-001804 | NCR | Ap3a Slab Level - Out of Tolerance |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-12-23 | 2014-12-16 16:04 | -7 | 2014-12-15 11:08 | Tunnelling - Linings - Sprayed Concrete | 8500 |  | Incorrect Installation | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | invert level survey in AP3a between chainages 7 & 15m indicate multiple locations that the level is low and out of tolerance. The design level of PTW slab is 96.666mAod. The minimum permissible level is 96.646mAod. The worst effected area is chainage 14m (13mm low, RL 96.633mAod). Level surveys attached for clarification.
| 01CV - Civils | Cxxx-NCR-001805 | NCR | VD4 Slab Level - Out of Tolerance |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-12-23 | 2015-01-23 12:56 | 31 | 2014-12-15 11:07 | Tunnelling - Linings - Sprayed Concrete | 11000 |  | Incorrect Installation | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | invert level survey in VD4 between chainages 7 & 17m indicate one location that the level is low and out of tolerance. The design level of VD4 slab is 96.478mAod. The minimum permissible level is 96.458mAod. The effected area is chainage 10m (21mm low, RL 96.437mAod). Level surveys attached for clarification.
| 01CV - Civils | Cxxx-NCR-001806 | NCR | CP5 Slab Level - Out of Tolerance |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-12-29 | 2014-12-17 16:42 | -12 | 2014-12-15 11:22 | Tunnelling - Linings - Sprayed Concrete | 8500 |  | Incorrect Installation | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | invert level survey in CP5 between chainages 8 & 38m indicate multiple locations that the level is low and out of tolerance. The design level of CP5 slab is 96.852mAod. The minimum permissible level is 96.832mAod. The worst effected area is chainage 25m (9mm low, RL 96.823mAod). Level surveys attached for clarification. 96.823
| 01CV - Civils | Cxxx-NCR-001807 | NCR | CP9 Slab Level - Out of Tolerance |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-12-29 | 2014-12-18 13:09 | -11 | 2014-12-15 11:34 | Tunnelling - Linings - Sprayed Concrete | 8500 |  | Incorrect Installation | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | invert level survey in CP9 between chainages 7 & 17m indicate multiple locations that the level is low and out of tolerance. The design level of CP9 slab is 96.852mAod. The minimum permissible level is 96.832mAod. The worst effected area is chainage 9m (10mm low, RL 96.822mAod). Level surveys attached for clarification.
| 01CV - Civils | Cxxx-NCR-001808 | NCR | CP10 Slab Levels - Out of Tolerance |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-12-23 | 2014-12-18 12:13 | -5 | 2014-12-15 11:37 | Tunnelling - Linings - Sprayed Concrete | 8500 |  | Incorrect Installation | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | invert level survey in CP10 between chainages 7 & 13m indicate multiple locations that the level is low and out of tolerance. The design level of CP10 slab is 96.852mAod. The minimum permissible level is 96.832mAod. The worst effected area is chainage 10m (5mm low, RL 96.827mAod). Level surveys attached for clarification.
| 01CV - Civils | Cxxx-NCR-001809 | NCR | CH3 Slab Levels - Out of Tolerance |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-12-23 | 2014-12-18 13:23 | -5 | 2014-12-15 11:41 | Tunnelling - Linings - Sprayed Concrete | 8500 |  | Incorrect Installation | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | invert level survey in CH3 between chainages 1 & 47m indicate multiple locations that the level is low and out of tolerance. The design level of CH3 slab is 95.645mAod. The minimum permissible level is 95.625mAod. The worst effected area is chainage 25m (17mm low, RL 96.608mAod). Level surveys attached for clarification.
| 01CV - Civils | Cxxx-NCR-001810 | NCR | BOS PTE : Circumferential Crack Approx. Ch. 55 (2C Area) |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-12-23 | 2014-12-19 17:22 | -4 | 2014-12-15 17:48 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | In October 2014, a long section of secondary lining was sprayed (in bays of 3m) in BOS PTE, approx. Chainages 40–70 (2C area). Spraying and curing was carried out to ’s accepted method statement, and the shotcrete was in spec. (see attached 2SL checksheets). Drying shrinkage results for October were well within the specification at 0.001–0.002% (see attached monthly results). The contraction joints detailed on drawing Cxxx-MMD-C4-DDA-Cxxx_6-00100 [C02] (issued via PMI 1556) outside CP7 and CP9 were cut before the shotcrete reached a strength of 20MPa, as required by Cxxx-MMD-C4-DDD-Cxxx_Z-00053 [C06] (issued via PMI 1537). The area was sprayed on 05/10/2014 nightshift and the joints were cut on 06/10/2014 dayshift (see attached shift reports). However, several weeks later, a crack up to 3mm thick has been observed running circumferentially around the tunnel. The crack runs slightly diagonally, in the region of Chainages 52–59. This is in the middle of the approx. 30m long section between the contraction joint outside CP7 (around Ch. 40) and the end of the secondary lining sprayed in this period (around Ch. 70). Tell tales have been installed and the crack was monitored. The crack was not opening at any significant rate (see attached crack logs, where the crack width has been measured at 5No locations around the perimeter).
| 01CV - Civils | Cxxx-NCR-001811 | NCR | PTW - Invert Slab - Excessive Scabbling |  | Contr | BFK |  |  | 2015-02-13 | 2015-02-12 10:33 | -1 | 2014-12-15 18:38 | Tunnelling - Tunnelling General | 10500 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The invert slab on PTW was poured on 13/12/14 , between chainages 196 and 210. After removal of the formwork, a rough surface of the radial joint on the slab was created to form an adequate surface for the secondary lining layer. However, on the RHS of the invert these works were carried out in an excessive manner as shown in the picture attached.
| 01CV - Civils | Cxxx-NCR-001812 | NCR | Damage to Masterseal PTW Ch. -57 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-12-30 | 2014-12-19 17:23 | -11 | 2014-12-16 17:04 | Tunnelling - Linings - Sprayed Concrete | 3500 |  | Material | Use As-Is | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | It was observed by CRL/Cxxx that when they were asked to come down to inspect Section 1a Ch. -57, there was a small leak through the Masterseal.
| 01CV - Civils | Cxxx-NCR-001813 | NCR | BOS PTW : Secondary Lining Contraction Joint Not Cut Ch. −45 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-01-24 | 2015-01-19 17:20 | 360 | 2014-12-17 14:55 | Tunnelling - Linings - Sprayed Concrete | 4500 |  | Incomplete Works | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The contraction joint CJ.0316 in PTW (approx. Ch. -45, outside VD3) was cut on 17/12/2014 nightshift, whereas this area of secondary lining was sprayed on 09/12/2014 dayshift. The strength of this shotcrete will already have exceeded the 20N/mm² specified on Cxxx-MMD-C4-DDD-Cxxx_Z-00053 [C06].
| 01CV - Civils | Cxxx-NCR-001816 | NCR | BFK Form 89a not completed for PTW 1A Invert -62m to -44m as required by the documented ITP (CRL Surveillance) |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2015-01-30 | 2015-01-20 15:14 | -10 | 2014-12-17 11:43 | Tunnelling - Tunnelling General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | During a planned Crossrail surveillance (18th November 2014) at Bond Street covering SCL spray waterproofing a post surveillance request was made for Form 89a as it was not available during the site visit. Following three requests and clarification from the construction team, it was detailed that the form was not completed for the aforementioned location. Inspection and Test Plan – Regulating Layer and Sprayed Waterproofing Application, Cxxx--C4-ITP-CRT00_ST005-50112 details a requirement for Form 89a to be completed which details cured patch testing and remedial works such as repairs.
| 01CV - Civils | Cxxx-NCR-001817 | NCR | The secondary lining has been installed in tunnel S3 some six weeks after the installation of the spray waterproof membrane (CRL Surveillance) |  | Crossrail | XRL |  |  | 2015-01-28 | 2015-01-20 16:09 | -8 | 2014-12-17 12:05 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | During a planned Crossrail surveillance (25th November 2014) at TCR looking at SCL secondary lining installation, a review was carried out on the documentation associated to tunnel S3 to detail the time lapse between sprayed waterproof installation and secondary lining installation. KT20.3220.Q; states “the secondary lining shall be installed in any area within 3 weeks of the installation of the sprayed membrane in this area. If the Contractor wishes to delay installation this shall be agreed with the PM at least 2 weeks before installation”. On review it was highlighted that the final layer of sprayed waterproofing was completed on 09/10/2014 with the secondary lining was installed on 25/11/2014, some 6 weeks after. Cxxx-PMI-01568 was provided which states “Whilst unconditional relaxation of KT20.3220.Q. constraint cannot be granted, such change may be accepted on an individual basis. A review based on site conditions can be discussed for each location with the lead resident technical engineer (Cxxx representative) who may accept a relaxation of the KT20.3220.Q. 3 week constraint”. A request was made post surveillance to detail whether the time lapse between spraying was discussed with the Cxxx engineer, and if a relaxation had been granted to provide documented evidence of this; however following two requests no information was provided, as such this NCR was raised.
| 01CV - Civils | Cxxx-NCR-001818 | NCR | BOS PTW: Lack of Masterseal overlap CH 100 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-01-16 | 2015-01-15 15:46 | -1 | 2014-12-17 15:35 | Tunnelling - Linings - In-situ Concrete | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | After striking the shutter on the secondary lining cast invert around chainage 100 in PTW, it was discovered that there is a potential area of damage to the Masterseal on the right hand side. Although it has been repaired, it will not have the required 200mm overlap — see attached picture. The area is dry.
| 01CV - Civils | Cxxx-NCR-001820 | NCR | PTW Chainage 16 to 31 (Area 1C) secondary lining under thickness |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-02-16 | 2015-02-11 15:34 | -5 | 2014-12-17 17:45 | Tunnelling - Linings - Sprayed Concrete | 25000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Under thickness of profiles for secondary lining (see attached ) PTW Chainage 16 to 31 (Area 1C). This happened due to poor engineering control during spraying of secondary lining 9.02.15 - Checksheet and photos were attached to NCR1826(now closed) which was for same issue (duplicate) as this NCR. please see attached signed checksheets.
| 01CV - Civils | Cxxx-NCR-001821 | NCR | Slab not a U1 finish in PTW Ch 145 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-03-12 | 2015-03-02 15:13 | -10 | 2014-12-18 14:37 | Tunnelling - Linings - In-situ Concrete | 25000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | inspected the slab in PTW Ch 145 (Section 4a) and observed that the slab was not U1 finish as specified in KF10 - In Situ Specification, section KF10.3230.
| 01CV - Civils | Cxxx-NCR-001822 | NCR | BOS-Unapproved nozzleman spraying permanent works |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2014-12-23 | 2014-12-19 17:31 | -4 | 2014-12-18 15:27 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not qualified | Completed |  | On the 7/12/2014, it was observed by Crossrail that there was a nozzleman spraying permanent works, who was not on the official matrix document . He was operating the logica in automatic mode and did have a supervisor present at the time.
| 01CV - Civils | Cxxx-NCR-001823 | NCR | The following sample numbers (SCL 652,667,671) did't meet ITP requirements of six cores @ 1 day for compressive strength instead the lab produce results for 4 to 5 cores per sample also SCL 664 was crushed @ 6 days rather than within 1-3 days |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-01-09 | 2015-01-07 15:24 | -2 | 2014-12-18 18:21 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | The following sample numbers at BOS (SCL 652,667,671) did't meet ITP requirements of six cores @ 1 day for compressive strength instead the lab produce results for 4 to 5 cores per sample rather than 6 cores as stipulated by ITP also SCL 664 was crushed @ 6 days rather than within 1-3 days
| 01CV - Civils | Cxxx-NCR-001824 | NCR | Lamination in AP2E Secondary Lining ch 18-20 |  | Contr | BFK |  |  | 2015-01-12 | 2015-01-19 09:29 | 7 | 2014-12-22 15:26 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Use As-Is | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | After milling secondary lining tight spots it was notice there was a lamination present in the secondary lining between ch 18-20. Cores were taken,revised and accepted by Cxxx/CRL. This NCR is not compliant with an homogeneous layer specified in KT20.2202
| 01CV - Civils | Cxxx-NCR-001825 | NCR | TCR - PTE - CH 20 to 50 Fireproofing hollow sections |  | Contr | BFK |  |  | 2015-02-27 | 2015-02-03 13:10 | -24 | 2015-01-13 10:57 | Tunnelling - Linings - Sprayed Concrete | 17500 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Hammer testing below the axis level of PTE over fireproofing layer showed a number of hollow spots in the joints areas. The location and coordinates of the spots are marked on the attached drawing.
| 01CV - Civils | Cxxx-NCR-001826 | NCR | BOS WTH PTW Secondary Lining thickness being increased to full profile |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-01-20 | 2015-01-16 16:51 | -4 | 2015-01-06 09:30 | Tunnelling - Linings - Sprayed Concrete | 5500 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | B283 mesh was to be installed to areas that required additional thickness of secondary lining in PTW (see NCR 1820). Some of the mesh was installed in an incorrect orientation (by 90 degrees). All of the mesh was fixed at 400mm centres.
| 01CV - Civils | Cxxx-NCR-001827 | NCR | Secondary Lining Spraying Methodology Not Followed - PTW CH107 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-01-20 | 2015-01-20 17:15 | 0 | 2015-01-06 11:26 | Tunnelling - Linings - Sprayed Concrete | 6500 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Other | Completed |  | During the spraying of a secondary lining bay at PTW CH107, disruption in concrete delivery resulted in the halting of the works for a prolonged period. This has in turn resulted in the following: 1.A section of the profile sprayed to full thickness between 7 and 8 O'Clock positions. No sprayed concrete has been applied to the remainder of the profile. 2.A Joint feathering from full thickness to no thickness at the 8 O'Clock position. are aware that due to the prolonged delay in the completion of the bay, the spraying procedure set out in Cxxx--C4-GMS-CRT00-ST005-50274 has not been satisfied.
| 01CV - Civils | Cxxx-NCR-001828 | NCR | Grout Applied Over Secondary Lining To Seal Leak - PTW CH145 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-03-13 | 2015-02-26 13:20 | -15 | 2015-01-06 11:58 | Tunnelling - Linings - Sprayed Concrete | 4000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | At PTW CH145 it has been observed that operatives applied grout to the surface of the secondary lining in an attempt to seal a leak. This transgression deviates from any current accepted form of leak repair.
| 01CV - Civils | Cxxx-NCR-001829 | NCR | In October 2014 in a few instances, Hanson delivered shotcrete which was overdosed with microsillica outside ITP limit ok 3%. |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-01-20 | 2015-01-15 16:28 | -5 | 2015-01-06 14:39 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | In October 2014 at BOS, in a few instances overdosed its shotcrete with microsillica delivered to site outside the batching tolerance of 3%
| 01CV - Civils | Cxxx-NCR-001830 | NCR | In October 2014 one sample set of cores (6 cores) during that month was crushed @ 4 days rather than ITP stipulated 1-3 days |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-01-20 | 2015-01-15 16:29 | -5 | 2015-01-06 16:19 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | In October 2014 one sample set of cores (6 cores) during that month was crushed @ 4 days rather than ITP stipulated 1-3 days
| 01CV - Civils | Cxxx-NCR-001831 | NCR | AP7A Regulating - 4 cores tested at 28 days |  | Contr | BFK |  |  | 2015-02-03 | 2015-01-16 16:54 | -18 | 2015-01-06 18:25 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Sample 732, AP7A Regulating, CH9-26. Only 4 cores tested at 28 days.
| 01CV - Civils | Cxxx-NCR-001832 | NCR | Damage to masterseal through secondary lining - PTW CH107m |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-01-21 | 2015-01-14 16:28 | -7 | 2015-01-07 09:27 | Tunnelling - Linings - Sprayed Concrete | 5500 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Whilst reworking the secondary lining PTW CH 107m an operative equipped with hand tool accidentally punctured through the sprayed concrete secondary lining and into the masterseal. A small area of the waterproofing was damaged approximately 25mm x 25mm in size. propose the following repair method.
| 01CV - Civils | Cxxx-NCR-001833 | NCR | Invert alignment out of place due to formwork deflection |  | Contr | BFK |  |  | 2015-01-23 | 2015-01-19 14:13 | -4 | 2015-01-07 16:54 | Tunnelling - Linings - In-situ Concrete | 6000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Cast in situ invert is slightly out of position (by 50mm approx) due to deflection of formwork when loaded. This happens in approximately 4m around chainage -20 of PTW and it would affect (reduce) the surface in contact with the fireproofing. agreed with D.H. (Cxxx) and C.B. (CRL) to cut and break the top of the area to provide enough contact surface for the fireproofing. Please see picture attached.
| 01CV - Civils | Cxxx-NCR-001834 | NCR | BOS 2b/2c contraction joints not cut into fireproofing in timely manner |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2015-02-20 | 2015-02-16 10:16 | -4 | 2015-01-07 18:28 | Tunnelling - Linings - Sprayed Concrete | 3500 |  | Workmanship | Use As-Is | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | It has been observed that the contraction joints have not been cut into the fireproofing layer of section 2b/2c of the PTE tunnel in a timely manner.
| 01CV - Civils | Cxxx-NCR-001836 | NCR | BOS PTE Masterseal damage next to invert slab chainage 68 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-01-30 | 2015-01-20 17:18 | -10 | 2015-01-08 10:55 | Tunnelling - Linings - Sprayed Concrete | 5500 |  | Workmanship | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | During the removal of the ramp between the lining invert and the cast invert at chainage 68 the masterseal lap at the connection has been damaged.
| 01CV - Civils | Cxxx-NCR-001837 | NCR | BOS VD3 slab level out of tolerance |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-02-16 | 2015-02-13 12:01 | -3 | 2015-01-10 12:12 | Tunnelling - Linings - Sprayed Concrete | 15000 |  | Incorrect Installation | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | invert level survey in VD3 between chainages 7 & 23m indicate multiple locations that the level is low and out of tolerance. The design level of VD3 slab is 96.008mAod. The minimum permissible level is 95.988mAod. The worst effected area is chainage 10m (25mm low, RL 95.963mAod). From the regulating layer scans the minimum offset from the primary lining design line is +28mm at chainage 7.5. The regulating design line is -50mm. Therefore there is a remaining tolerance of 78mm to ensure the correct slab thickness. The lowest slab level is 25mm out of tolerance at chainage 10. Using the two worst cases there would still be 53mm of tolerance remaining. Thus the cast invert thickness is in excess of the design thickness. Level surveys and regulating layer scans attached for clarification.
| 01CV - Civils | Cxxx-NCR-001839 | NCR | AP3B Slab Level - Out of Tolerance |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-02-27 | 2015-02-06 13:10 | -21 | 2015-01-08 14:42 | Tunnelling - Linings - Sprayed Concrete | 25000 |  | Incorrect Installation | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | invert level survey in AP3B between chainages 0 & 2m indicate that the level is high and out of tolerance. The design level of AP3B slab is 96.768mAod. Level surveys attached for clarification.
| 01CV - Civils | Cxxx-NCR-001841 | NCR | De-Bonding of Fireproofing Layer - PTW CH 0 to -60m |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-01-23 | 2015-01-20 16:25 | -3 | 2015-01-08 23:19 | Tunnelling - Linings - Sprayed Concrete | 4500 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the hammer testing of applied fireproofing layer PTE 0 to -60m, 3 localised de-bonded areas were identified. De-bonded Area 1: The centre line of this area is located at PTE chainage -28.0m. The area is 1040mm in height and 660mm in width.The centre of the area is located approximately 1.5m above the cast invert slab. The entirety of the area lays below the finish level of mass concrete invert fill which will be carried out in the next stage of the works. See photographs 1, 2 & 3 for clarification. Scans produced following the completion of the application of 17.2 in this area indicate the secondary lining thickness prior to the application of smoothing mix ranges between 290 and 310mm. See Profile 1 for clarification. De-bonded area 2: After further investigation, it has been concluded that de-bonded area 2 was identified as a result of a thin layer of rebounded material in the area. This loose material (approximately 10mm) has now been removed. Although further investigation suggests the identified de-bonding in this area was superficial, calculations of secondary lining thickness prior to the application of smoothing mix ranges between 330 and 350mm. See Profile 2 for clarification. De-bonded area 3: The centre line of this area is located at PTE chainage -46.5m. The area is 470mm in height and 460mm in width. The centre of the area is located approximately 300mm above the cast invert slab. The entirety of the area lays below the finish level of mass concrete invert fill which will be carried out in the next stage of the works. See photographs 4, 5 & 6 for clarification. Scans produced following the completion of the application of 17.2 in this area indicate the secondary lining thickness prior to the application of smoothing mix ranges between 360 and 420mm. See Profile 3 for clarification.
| 01CV - Civils | Cxxx-NCR-001842 | NCR | Overspray Fireproofing AP4E ch 8-34 |  | Contr | BFK |  |  | 2015-03-27 | 2015-03-16 13:34 | -11 | 2015-01-09 20:00 | Tunnelling - Linings - Sprayed Concrete | 25500 |  | Workmanship | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Having reviewed the final as-built profile for AP4E ch 0-37; one tight areas was identified as below: 1) Approx CH 37 - 38 and 12 o'clock . Approx 1m2 patch.
| 01CV - Civils | Cxxx-NCR-001843 | NCR | AP2E- Final as-built profile out of tolerance (specific area) |  | Contr | BFK |  |  | 2015-03-13 | 2015-03-02 16:42 | -11 | 2015-01-09 20:28 | Tunnelling - Linings - Sprayed Concrete | 15500 |  | Workmanship | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Having reviewed the final as-built profile for AP2E; some tight areas were identified as below: 1) Approx CH 3.5 - 12 o'clock . Approx 0.5m2 patch. 2) Approx CH 30.5-31 -4 o'clock . Approx 0.5m2 patch. 3) Approx CH 35-36.5 -12 to 4 o'clock. Approx 4m2 patch. Find attached the approval of the remedial action. Further information will be added once 3d model is prepared
| 01CV - Civils | Cxxx-NCR-001845 | NCR | Overspray Fireproofing AP3E ch 10-33 |  | Contr | BFK |  |  | 2015-02-27 | 2015-01-30 16:39 | -28 | 2015-01-09 20:46 | Tunnelling - Linings - Sprayed Concrete | 15500 |  | Workmanship | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After spraying fireproofing in AP3E between ch. 10-33 the profiles have been assesse by __ () it was concluded that there are oversprayed areas between 10mm up to 20 mm. Please find attached the profiles.
| 01CV - Civils | Cxxx-NCR-001846 | NCR | Under Thickness Fireproofing PTE 179-195 |  | Contr | BFK |  |  | 2015-02-10 | 2015-02-17 14:24 | 7 | 2015-01-09 21:27 | Tunnelling - Linings - Sprayed Concrete | 15500 |  | Workmanship | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | After spraying the fireproofing layer in PTE between ch. 179-195, the profiles have been assessed by __ ().It was concluded that there is concern with under thickness between those chainages as the 50mm thickness was not achieved. Please note that the eye was not sprayed.
| 01CV - Civils | Cxxx-NCR-001847 | NCR | BOS 1c Oil leak on invert slab PTW chainage 20-25 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-01-25 | 2015-01-21 15:10 | -4 | 2015-01-11 08:19 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | It was noticed there was an oil spillage on the cast invert in PTW chainage 20-25. This is against KF10.3231 Protection of Finished Concrete - The finished concrete surfaces shall be protected from damage and from rust or oil staining, and any necessary protective measures shall be adopted. Removal of oil spill by jet washing to ensure that the slab has adequate bonding with subsequent concrete works.
| 01CV - Civils | Cxxx-NCR-001848 | NCR | Hardened Fibre Content - September 2014 |  | Contr | BFK |  |  | 2015-02-02 | 2015-01-19 10:15 | -14 | 2015-01-12 14:32 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Lack or improper material identification and traceability | Completed |  | During September 2014, the following samples are missing hardened Fibre Content tests: Sample 709, VWW, Adv 22 CH14.43-16.34 - no 28 day Sample 713, VWW, Adv 28 CH17.74-19.38 - no 1 day Sample 717, PTE, Secondary CH126-129 - no 1 day Sample 720, PTE, Secondary CH89-92 - no 1 or 28 day Sample 722, AP2E, Secondary CH35-36 - no 1 or 28 day Sample 725, PTE, Secondary CH70-67 - no 1 or 28 day Sample 726, PTE, SEcondary CH64-61 - no 1 or 28 day
| 01CV - Civils | Cxxx-NCR-001849 | NCR | BOS CP8 Slab Level - Out of tolerance |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-01-31 | 2015-01-19 14:20 | -12 | 2015-01-17 13:17 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | invert level survey in CP8 between chainages 7 & 13m indicate 3 locations that the level is low and out of tolerance. The design level of CP8 slab is 96.852mAod. The minimum permissible level is 96.827mAod. The worst effected area is chainage (5mm low, RL 96.827mAod). From the regulating layer scans the minimum offset from the primary lining design line is 0mm at chainage 12.5. The regulating design line is -50mm. Therefore there is a remaining tolerance of 50mm to ensure the correct slab thickness. The lowest slab level is 5mm out of tolerance at chainage 9. Using the two worst cases there would still be 45mm of tolerance remaining. Thus the cast invert thickness is in excess of the design thickness. Level surveys and regulating layer scans attached for clarification.
| 01CV - Civils | Cxxx-NCR-001850 | NCR | BOS alignment of secondary lining and fireproofing contraction joints |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-01-26 | 2015-01-20 17:19 | -6 | 2015-01-12 14:23 | Tunnelling - Linings - Sprayed Concrete | 4500 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On 09/01/15 it was raised by CRL that s current method of aligning secondary lining and fireproofing contraction joints at BOS is being deemed unsatisfactory. To date the method employed at Bond Street has involved surveying the secondary lining saw cut at 2m centres. Following the application of sprayed fireproofing staking out this survey has dictated the position of the subsequent cut. accept there there may be some minor variation between the position of first and second cuts between stakeout points.
| 01CV - Civils | Cxxx-NCR-001851 | NCR | Hollow spots at PTE CH 130 to 185 |  | Contr | BFK |  |  | 2015-02-20 | 2015-02-03 09:01 | -17 | 2015-01-13 11:09 | Tunnelling - Linings - Sprayed Concrete | 7500 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Hammer testing below the axis level of PTE over fireproofing layer showed a number of hollow spots in the joints areas. The location and coordinates of the spots are marked on the attached drawing.
| 01CV - Civils | Cxxx-NCR-001852 | NCR | Testing outside of ITP requirements |  | Contr | BFK |  |  | 2015-02-02 | 2015-01-15 16:30 | -18 | 2015-01-12 14:30 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The following were tested outside of ITP requirements: Sample 708, VWW ADV16 - Cores tested at 5 days Sample 709, VWW ADV22 - 28 days tested at 38 days Sample 724, PTE Secondary AP3E jct - only 5 cores tested at 3 days Sample 726, PTE Secondary CH64-61 - Only 5 cores tested at 28 days
| 01CV - Civils | Cxxx-NCR-001854 | NCR | BOS 1a Chainage -55 to -45 spraying procedure not followed |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-01-26 | 2015-01-20 16:28 | -6 | 2015-01-12 21:34 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the spraying of the far face steel at VD3 (04/12/14) in PTW the opposite side of the eye was sprayed to full thickness while the area of secondary lining around the eye was sprayed shy to enable the installation of the near face steel. The area was jet washed prior to spraying the remaining thickness above axis.
| 01CV - Civils | Cxxx-NCR-001855 | NCR | BOS PTW Ch. 240–260 : Lack of Masterseal Overlap (4B Area) |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-03-13 | 2015-03-02 15:56 | -11 | 2015-01-12 23:33 | Tunnelling - Linings - Sprayed Concrete | 19500 |  | Damaged | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | On removing the temporary ramp from the Western Ticket Hall through AP2A down to PTW, a number of areas of Masterseal damage were found, some of which are leaking and some of which are close to the invert slab (so that the lap in KW20 for patch repairs will not be achieved). Patches are located adjacent to the invert slab on the right-hand side at chainages 242, 249, 252, 256 and 258. Please find attached pictures of the affected areas.
| 01CV - Civils | Cxxx-NCR-001856 | NCR | BOS CH3 Cover to reinforcement in invert slab |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-01-29 | 2015-01-21 15:20 | -8 | 2015-01-15 09:03 | Tunnelling - Linings - Sprayed Concrete | 3500 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Investigation into the cover to B785 structural mesh cast into the secondary lining slab of CH3 has confirmed an earlier CRL observation that the mesh was set low during the pour. Three 100mm cores were taken by to confirm actual cover. Core 1 was taken from E:79100.480, N:35836.736. The core was taken to a depth of 325mm. The cover to the top of steel in this location is approximately 150mm, 90mm too low. Core 2 was taken from E:79104.389, N:35837.709. The core was taken to a depth of 380mm. The cover to the top of steel in this location is approximately 120mm, 60mm too low. Core 3 was taken from E79108.579, N: 35840.014. The core was taken to a depth of 300mm. The cover to the top of steel in this location is approximately 150mm, 90mm too low. See attached core reports for clarification. The cast insitu invert is thicker than the design requirement of 350mm, see attached scans showing the thickness. On average the slab is a minimum 100mm thicker than the design requirement. Thus the effective depth is equivalent to the design.
| 01CV - Civils | Cxxx-NCR-001857 | NCR | BOS PTW Ch 190-200 4b spraying procedure not followed |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-02-03 | 2015-01-21 15:27 | -13 | 2015-01-20 17:20 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | It had been discussed in the secondary lining meeting that the invert mesh opposite could be sprayed in to full thickness opposite the CP4 eye to reduce the risk of rebound inclusion. An activity plan was produced for this change to the spraying sequence but was not approved prior to carrying out the works.
| 01CV - Civils | Cxxx-NCR-001858 | NCR | CH3- Incomplete F50s |  | Contr | BFK |  |  | 2015-01-30 | 2015-01-26 12:49 | -4 | 2015-01-16 13:07 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Some CH3 F50 forms for excavation and primary lining and primary lining thickness has missing details such as Nozzleman name and signature, Excavation start and finish time spray start and finish time.
| 01CV - Civils | Cxxx-NCR-001859 | NCR | Fireproofing checksheet Form 128 being used on site at TCR but is not on the ITP |  | Contr | BFK |  |  | 2015-02-03 | 2015-01-13 16:37 | -21 | 2015-01-13 14:12 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | During a surveillance on the 11/12/14 it was observed that on site at TCR they use a seperate checksheet for fireproofing works than they are meant to according to the Cast in situ & sprayed secondary lining ITP : Cxxx--C4-ITP-CRT00_ST005-50144. The ITP they where using on site is 128 where according to the ITP they should be using the form 088. This new form 128 covered all the ITP requirements that 088 did.
| 01CV - Civils | Cxxx-NCR-001860 | NCR | Lack of lap lenght of Masterseal at PTW between CH 10 to -38 |  | Contr | BFK |  |  | 2015-01-27 | 2015-01-19 08:19 | -8 | 2015-01-13 16:24 | Tunnelling - Tunnelling General | 5500 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During inspection of waterproofing, it became apparent the waterproofing in some areas at PTW between ch 10 and -38 has been damaged close to the cast invert and minimum lap length of waterproofing cannot be achieved. (photos and check sheet attached)
| 01CV - Civils | Cxxx-NCR-001861 | NCR | TCR S2 Adit - __ Lock Couplers - Bolt Shearing |  | Contr | BFK |  |  | 2015-01-27 | 2015-02-26 16:51 | 30 | 2015-01-13 16:00 | Civil - Tunnelling | 4500 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During construction of S2, in installing the __ __ B-Series Couplers at the top of each column it has not been possible to shear all the bolt heads off. The attached sketch shows the proportion of the bolts which have been sheared off. The soffit slab is due to be cast on the 14th or 15th of January 2015.
| 01CV - Civils | Cxxx-NCR-001862 | NCR | Overspray Fireproofing PTE 129-165 |  | Contr | BFK |  |  | 2015-02-27 | 2015-02-03 11:15 | -24 | 2015-01-13 16:49 | Tunnelling - Linings - Sprayed Concrete | 17500 |  | Workmanship | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | After spraying fireproofing in PTE between ch.129-165 the profiles have been assesse by __ () and presented to __ (Cxxx) and __ (CRL) it was concluded that there are oversprayed areas between 10mm up to 30 mm. Please find attached profiles.
| 01CV - Civils | Cxxx-NCR-001863 | NCR | Lack of lap lenght of Masterseal at PTW junction with AP7A |  | Contr | BFK |  |  | 2015-02-26 | 2015-02-26 13:23 | 0 | 2015-01-13 16:40 | Tunnelling - Tunnelling General | 5500 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During inspection of waterproofing, it became apparent the waterproofing in some areas at PTW junction with AP7a has been damaged close to the cast invert and minimum lap length of waterproofing cannot be achieved. (photos attached)
| 01CV - Civils | Cxxx-NCR-001864 | NCR | Lack of lap lenght of Masterseal at AP4W CH 9 |  | Contr | BFK |  |  | 2015-01-27 | 2015-01-16 17:20 | -11 | 2015-01-13 16:59 | Tunnelling - Tunnelling General | 7500 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During inspection of waterproofing, it became apparent the waterproofing in AP4W at ch 9 invert been damaged close to the previously cast invert and minimum lap length of waterproofing cannot be achieved.
| 01CV - Civils | Cxxx-NCR-001865 | NCR | In December 2014 SCL 668, BFK received compressive results @ 28 days of only 4 cores rather than ITP stipulated 6 cores |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-01-28 | 2015-01-16 17:12 | -12 | 2015-01-14 11:50 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | In december 2014 4 cores with reference to compressive results were received by rather than ITP stipulated 6 cores.
| 01CV - Civils | Cxxx-NCR-001866 | NCR | BOS PTW crack - chainage 98 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-01-30 | 2015-01-19 10:23 | -11 | 2015-01-16 09:35 | Tunnelling - Linings - Sprayed Concrete | 6500 |  | Design | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Other | Completed |  | During an inspection prior to the spraying of secondary lining in PTW a circumferential crack was noticed propagating through the masterseal at chainage 98. This crack was further investigated and found to have been in the primary lining. Following discussions with Cxxx and Crossrail, this crack was repaired using an agreed / approved repair method, the area sealed and signed off to enable the secondary lining to be sprayed. These works are now complete. Please find checksheets of the repair attached.
| 01CV - Civils | Cxxx-NCR-001868 | NCR | TCR - Hollow spots at AP2E fireproofing |  | Contr | BFK |  |  | 2015-02-06 | 2015-02-03 11:08 | -3 | 2015-01-23 17:57 | Tunnelling - Linings - Sprayed Concrete | 17500 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Hammer testing below the axis level of AP2E over fireproofing layer showed two hollow spots. The location of the spots are marked on the attached hammer testing sheet.
| 01CV - Civils | Cxxx-NCR-001869 | NCR | TCR - Hollow spots at AP4E fireproofing |  | Contr | BFK |  |  | 2015-02-10 | 2015-02-03 11:19 | -7 | 2015-01-27 11:05 | Tunnelling - Linings - Sprayed Concrete | 8500 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Other | Completed |  | Hammer testing below the axis level of AP4E over fireproofing layer showed two hollow spots. The location of the spots are marked on the attached hammer testing sheet.
| 01CV - Civils | Cxxx-NCR-001870 | NCR | No Flexual Beam Test test carriedout in December 2014 @ BOS. on Mix 17.2 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-02-27 | 2015-02-09 15:05 | -18 | 2015-01-16 12:20 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | No flexural beam test done in December.
| 01CV - Civils | Cxxx-NCR-001871 | NCR | CH3 - Final as-built profile out of tolerance (specific area) |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-02-16 | 2015-02-11 15:53 | -5 | 2015-01-17 09:19 | Tunnelling - Linings - Sprayed Concrete | 25500 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Having reviewed the final as-built profile for CH3; some tight areas were identified as below: 1) Approx CH1016 - 1017.5 at angle 70 - 120degree. Approx 3m2 patch. 2) Approx CH1016 - 1017 at angle 30 - 65degree. Approx 2m2 patch. 3) Approx CH1020.5 - 1023.5 at angle 310 - 350degree. Approx 2m2 patch. 4) Approx CH1018.5 - 1019.5 at angle 5 - 45degree. Approx 1m2 patch.
| 01CV - Civils | Cxxx-NCR-001872 | NCR | Under Thickness Secondary Lining VEW ch 9-10 |  | Contr | BFK |  |  | 2015-02-13 | 2015-02-04 08:51 | -9 | 2015-01-16 14:21 | Tunnelling - Tunnelling General | 13500 |  | Workmanship | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Other | Completed |  | After spraying the secondary lining in VEW between ch. 9 - 10, the profiles have been assessed by __ (), __ (Cxxx) & __ (CRL). It was concluded that there is concern with under thickness at chainages detailed before as the 200mm thickness was not achieved.
| 01CV - Civils | Cxxx-NCR-001873 | NCR | BOS SCL : Cores Backfilled with Loose Material |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-02-04 | 2015-02-06 14:32 | 2 | 2015-01-21 14:39 | Tunnelling - Linings - Sprayed Concrete | 5500 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On 14/01/15 nightshift, it was observed that cores taken through the secondary lining were being backfilled with a loose mixture of sand and cement.
| 01CV - Civils | Cxxx-NCR-001874 | NCR | BOS PTW Ch. 132–135 : Radial joint not formed at correct level (1D/4A) |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-02-02 | 2015-01-20 16:42 | -13 | 2015-01-19 16:03 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | ’s accepted method statement for secondary lining involves spraying the invert to axis level to full thickness, forming a radial joint, followed by spraying the crown in layers. While spraying secondary lining to the bay at PTW chainage 132–135, the radial joint was formed at approx. 1m below axis level — see attached picture.
| 01CV - Civils | Cxxx-NCR-001875 | NCR | VEW overspray profile secondary lining |  | Contr | BFK |  |  | 2015-01-30 | 2015-01-20 16:50 | -10 | 2015-01-16 16:09 | Tunnelling - Linings - Sprayed Concrete | 5500 |  | Workmanship | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | After spraying the secondary lining in VEW between ch. 0 - 29.50, the profiles have been assessed by __ () and presented to __ (Cxxx) and __ (CRL).It was concluded that there is concern of overspray.
| 01CV - Civils | Cxxx-NCR-001876 | NCR | CP7 - Final as-built profile out of tolerance (specific area) |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-02-06 | 2015-02-10 17:58 | 4 | 2015-01-17 09:21 | Tunnelling - Linings - Sprayed Concrete | 17500 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Having reviewed the final as-built profile for CP7; some tight areas were identified as below: 1) Approx CH5.5 - 6.0 at angle 25 - 60degree. Approx 1m2 patch. 2) Approx CH6.8, lip at construction joint.
| 01CV - Civils | Cxxx-NCR-001877 | NCR | CP8 - Final as-built profile out of tolerance (specific area) |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-02-06 | 2015-02-11 16:29 | 5 | 2015-01-17 09:22 | Tunnelling - Linings - Sprayed Concrete | 25000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Having reviewed the final as-built profile for CP8; some tight areas were identified as below: 1) Approx CH5.35 at knee level below SSC. 2) Approx CH5.0 - 6.5 at angle 80 - 100degree. Approx 1m2 patch.
| 01CV - Civils | Cxxx-NCR-001878 | NCR | Sleeve grout cube test results for ES1 pipe arch TaM pipes installation did not achieve the required strength in line with specification (4N/mm2) |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-01-30 | 2015-01-21 12:44 | -9 | 2015-01-16 17:30 | Geotechnical Engineering - Supported Excavations | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | As per the attached grout cube results for ES1 pipe arch Tam Pipes installation, its noted that 28 day results didn't achieve the required strenght in line with specification (4N/mm2) ( As per MCR Cxxx--C4-LRC-CRT00_ST005-50443)
| 01CV - Civils | Cxxx-NCR-001879 | NCR | CP9 - Final as-built profile out of tolerance (specific area) |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-02-06 | 2015-02-11 16:43 | 5 | 2015-01-17 09:23 | Tunnelling - Linings - Sprayed Concrete | 25000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Having reviewed the final as-built profile for CP9; a tight area were identified at approx CH5.5 - 7.5 at angle 30 - 45degree, approx 1m2 area.
| 01CV - Civils | Cxxx-NCR-001880 | NCR | PTE CH0 - 50 - Final as-built profile out of tolerance (specific area) |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-02-16 | 2015-02-10 11:49 | -6 | 2015-01-17 09:25 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Having reviewed the final as-built profile for PTE; some tight areas were identified as below: 1) Approx CH15.0 - 16.0 at angle 10 - 25degree. Approx 1m2 patch. 2) Approx CH38.5 - 39.5 at angle 95 - 115degree. Approx 1m2 patch.
| 01CV - Civils | Cxxx-NCR-001881 | NCR | BOS PTW/VD4 Masterseal damage |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-01-31 | 2015-01-20 17:23 | -11 | 2015-01-17 16:37 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | During works the masterseal in front of VD4 was damaged. This was then repaired. See attached pre spray approval of waterproofing checksheet.
| 01CV - Civils | Cxxx-NCR-001882 | NCR | Late testing of 1-3 days |  | Contr | BFK |  |  | 2015-02-10 | 2015-01-23 14:29 | -18 | 2015-01-20 11:27 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The following sets of cores were tested later than 3 days: Sample 775, CH1 Secondary Ch.58-61, tested at 5 days Sample 776, CH1 Secondary Ch.64-67, tested at 4 days Sample 777, AP1 Secondary Ch.6.5-9, tested at 4 days Sample 778, S1 Fireproofing Ch.0-6, tested at 4 days
| 01CV - Civils | Cxxx-NCR-001883 | NCR | Cores tested outside of 1-3 days |  | Contr | BFK |  |  | 2015-02-10 | 2015-01-23 14:50 | -18 | 2015-01-20 11:30 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Equipment Breakdown | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The following set of cores were tested outside of 1-3 days: Sample 782, PTW Secondary, Ch.61-64, tested at 5 days Sample 783, PTW, Secondary, Ch.163, tested at 4 days Sample 785, CH1, Secondary, Ch.3-6, tested at 5 days Sample 786, AP8, Regulating, tested at 5 days Sample 787, PTE, Secondary, Ch.3-6, tested at 4 days Sample 788, CH1, Secondary, Ch8-10, tested at 4 days
| 01CV - Civils | Cxxx-NCR-001884 | NCR | BOS - PTW Ch98 leak through masterseal |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-02-02 | 2015-02-03 11:41 | 1 | 2015-01-19 14:17 | Tunnelling - Tunnelling General | 5500 |  | Damaged | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | Leak was observed close to secondary lining leading edge at chainage 98 after area had been signed off for application of secondary lining.
| 01CV - Civils | Cxxx-NCR-001885 | NCR | Hollow spots at CH1 CH 10 and 35 |  | Contr | BFK |  |  | 2015-02-06 | 2015-02-03 12:40 | -3 | 2015-01-19 15:45 | Tunnelling - Linings - Sprayed Concrete | 8500 |  | Workmanship | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Other | Completed |  | Hammer testing below the axis level of CH1 over fireproofing layer showed 3 number of hollow spots below axis. The location and coordinates of the spots are showed in attached hammer testing check sheet.
| 01CV - Civils | Cxxx-NCR-001886 | NCR | Longitudinal construction joint in PTW CH -21 to -24 (S4 side) |  | Contr | BFK |  |  | 2015-02-03 | 2015-01-23 15:07 | -11 | 2015-01-20 16:46 | Tunnelling - Linings - Sprayed Concrete | 6500 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During spraying of secondary lining in PTW between CH -21 to -24 (close to S4 eye) the sequencing of works have resulted in creating a longitudinal construction joint around 1.5m above the invert level (see attached picture).
| 01CV - Civils | Cxxx-NCR-001887 | NCR | Localised Fireproofing Under thickness - PTW CH -60 to 0m |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-02-13 | 2015-02-11 17:20 | -2 | 2015-01-20 00:57 | Tunnelling - Linings - Sprayed Concrete | 19500 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | A review of fireproofing thickness plots for PTW between chainages -60 & 0m has identified a number of underthick areas (less than the required 50mm). Using guidance provided by the CEG the areas of under thickness have been categorised. All areas within PTW have the potential to be subject to train fire and therefore the rules relevant for these areas have been applied for the proposed solution to these under thick areas. PTW -61m to 31m: See annotated sketch 'PTW -61 to 31m'. Under thickness displayed around opening, but assumed to be due to unreliable calculation stemming from junction complexity. Location 1 identified within the tunnel drive, approx. chainage -56.3m. Area of location 1 is 0.3m2. Longitudinal length is 0.7m. Location 1 is less than 1m2 in size. Single isolated area with no other significant under thickness within 5m distance measured longitudinally. propose 'use as is' for this section of the tunnel. PTW -31m to 0m See annotated sketch 'PTW -31 to 0m' page 1. Under thickness displayed around opening, but assumed to be due to unreliable calculation stemming from junction complexity. Location 1 identified within the tunnel drive, approx. chainage -29m. Area of location 1 is 1m2. Longnitudional length is 0.75m. Location 2 identified within the tunnel drive, approx. chainage -25.9m. Area of location 2 is 0.6m2. Longnitudional length is 1.2m. Location 3 identified within the tunnel drive, approx. chainage -15.3m. Area of location 3 is 1.75m2. Longnitudional length is 0.7m. Location 4 identified within the tunnel drive, approx. chainage -10.3m. Area of location 4 is 0.7m2. Longnitudional length = 1m. Given rules, locations 1 & 2 are unacceptable. Under sprayed areas are greater than 0.5m in length longitudinally and are spaced within 3m centre to centre longitudinally. Area 3 is unacceptable. Area is greater than 1m2. Area 4 is unacceptable; area is less than 1m2 but is within 5m spacing longitudinally of area 3. propose the following remedial works in PTW CH -31m to 0m to bring within acceptance. After the remedial works propose to leave as is for CH -31 to 0m. propose as follows (see sketch attached): Location 1: leave as is – Reason: rework to area 2 will make this area isolated with no under thickness within 5m longitudinally. Location 2: Wash the area to remove and loose particles and dust, reapply additional 50mm of fireproofing layer at affected cross section. Location 3: Wash the area to remove and loose particles and dust, reapply additional 50mm of fireproofing layer at affected cross section. Location 4: leave as is – Reason: rework to area 3 will make this area isolated with no under thickness area with 5m longitudinally.
| 01CV - Civils | Cxxx-NCR-001888 | NCR | Generic NCR - Fire proofing as-built profile out of tolerance |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-03-16 | 2015-02-11 17:29 | -33 | 2015-02-10 15:04 | Tunnelling - Linings - Sprayed Concrete | 25000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Fire proofing as-built profile out of designed tolerance - CH3, CP7, 8, 9 & 10, PTE CH0-50, LCE1 & 2, AP3A, VD4 and PTW CH-29 - CH70.
| 01CV - Civils | Cxxx-NCR-001889 | NCR | BOS PTW Ch 190-200 4b spraying procedure not followed - not sprayed bay by bay |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-02-03 | 2015-01-21 15:30 | -13 | 2015-01-20 18:02 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During spraying the heavily reinforced area outside the CP4 eye in BOS PTW the lining was not sprayed bay by bay as stipulated in the method statement. This was done to reduce the risk of reboun inclusion in the area. Further to this a Short Change Notice was produced, see attached
| 01CV - Civils | Cxxx-NCR-001890 | NCR | BOS PTW Ch 186 4b leakage |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-02-03 | 2015-01-29 14:31 | -5 | 2015-01-20 21:26 | Tunnelling - Linings - Sprayed Concrete | 8500 |  | Supervision/Management | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | BOS PTW Ch 186 4b a leakage was found during an inspection. This was repaired but it was noted on the checksheet that this should be checked by the DS Cxxx/CRL inspectors prior to spraying (see attached). There is no evidence that this was witnessed.
| 01CV - Civils | Cxxx-NCR-001891 | NCR | As part of concurrent grouting works in TCR1 along AP1 tunnel section, out of 1 to 66 grout passes carried |  | Contr | BFK |  |  | 2015-02-04 | 2015-02-05 16:17 | 1 | 2015-01-21 08:34 | Geotechnical Engineering - Compensation Grouting | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | As part of concurrent grouting works in TCR1 along AP1 tunnel section, out of 1 to 66 grout passes carried out there are two passes as mentioned below doesn’t have field grout test record/ cube result. This result in failing to show grout characteristics and compressive strengths in line with the specification for the two passes below. Pass 1-3: Total Volume injected – 2528 litres on 2/4/2013 NS – No field grout testing record and cube results Pass 4-6: Total volume injected – 1962 litres on 04/04/13 NS - No cube result
| 01CV - Civils | Cxxx-NCR-001892 | NCR | CH1- Final as-built profile out of tolerance (specific area) |  | Contr | BFK |  |  | 2015-02-10 | 2015-02-03 13:12 | -7 | 2015-01-27 13:23 | Tunnelling - Linings - Sprayed Concrete | 12500 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Having reviewed the final as-built profile for CH1; some tight areas were identified as below: 1) Approx CH 45 - at angle 10 - 70degree. Approx 1m2 patch. 2) Approx CH 50- 50.5 - at angle 20 - 50degree. Approx 1m2 patch. Find attached the 3d model of the are showing the tight areas and new asbuilts of the area.
| 01CV - Civils | Cxxx-NCR-001893 | NCR | CH1 Cast Invert out of tolerances ch 0-55 |  | Contr | BFK |  |  | 2015-02-04 | 2015-01-23 15:05 | -12 | 2015-01-21 16:29 | Tunnelling - Linings - Sprayed Concrete | 25500 |  | Workmanship | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | CH1 ch 0 - 55 cast invert U1 finish (0-20mm tolerance) is out of specifications due to an inappropriate leveled. This NCR it is not complaint with the ITP Cxxx--C4-ITP-CRT00_ST005-50144 - BOS TCR CP Cast-in situ and Sprayed Secondary Lining section B4.10 and the general note G36 from the drawing Cxxx-MMD-C4-DDJ-N105-00001 reference below. See attached the spreadsheet with all the invert levels and thickness detailed.
| 01CV - Civils | Cxxx-NCR-001894 | NCR | CH1- Final As Built Profiles 0-83 |  | Contr | BFK |  |  | 2015-02-04 | 2015-02-03 13:17 | -1 | 2015-01-21 20:18 | Tunnelling - Linings - Sprayed Concrete | 10500 |  | Workmanship | Use As-Is | 2 (6-60k) | Complete | Material/Preservation Problems - Other | Completed |  | Fire proofing as-built profile out of designed tolerance for CH1- chainages 0-83
| 01CV - Civils | Cxxx-NCR-001895 | NCR | PTW CH-29 - Ch70 - Final as-built profile out of tolerance (specific area) |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-02-20 | 2015-02-12 10:35 | -8 | 2015-01-21 18:28 | Tunnelling - Linings - Sprayed Concrete | 45000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Having reviewed the final as-built profile for PTW CH-32.5 - CH117; some tight areas were identified as below: 1) Approx CH-0.50 - 0.0 at angle 20 - 35degree. 2) Approx CH3.0 - 3.5 at angle 20 - 35degree. 3) Approx CH18.5 - 19.0 at angle 55 - 75degree. 4) Approx CH70.0 - 71.0 at angle 0 - 30degree. 5) Approx CH81.5 - 83.0 at angle 110 - 130degree. 6) Approx CH83.5 - 84.0 at angle 125 - 145degree. 7) Approx CH88.0 - 89.0 at angle 120 - 140degree. 8) Approx CH106.0 - 106.5 at angle 60 - 70degree. 9) Approx CH110.5 - 111.0 at angle 65 - 85degree. 10) Approx CH112.0 - 113.0 at angle 345 - 10degree. 11) Approx CH111.5 - 112.5 at angle 325 - 5degree. 12) Approx CH81.5 - 84.0 at angle 330 - 0degree. 13) Approx CH19.0 - 20.0 at angle 255 - 265degree
| 01CV - Civils | Cxxx-NCR-001896 | NCR | As part of concurrent grouting works in TCR along CH1 tunnel section, out of 1 to 80 grout passes carried |  | Contr | BFK |  |  | 2015-04-06 | 2015-02-19 10:38 | -46 | 2015-01-21 17:52 | Geotechnical Engineering - Compensation Grouting | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As part of concurrent grouting works in TCR along CH1 tunnel section, out of 1 to 80 grout passes carried out there are few passes as mentioned below are missing with field grout test records. This result in failing to show grout characteristics in line with the specification. Pass 21-22: Total Volume injected – 1178 litres on 22/2/2013 - No field grout testing record Pass 23-24: Total Volume injected – 1095 litres on 23/2/2013 - No field grout testing record Pass 25-26: Total Volume injected – 1298 litres on 24/2/2013 - No field grout testing record Pass 27-28: Total Volume injected – 1189 litres on 24/2/2013 - No field grout testing record Pass 41-43: Total Volume injected – 599 litres on 5/3/2013 - No field grout testing record Pass 44-46: Total Volume injected – 726 litres on 7/3/2013 - No field grout testing record Pass 56-58: Total Volume injected – 1187 litres on 14/3/2013 - No field grout testing record Pass 62-64: Total Volume injected – 1578 litres on 16/3/2013 - No field grout testing record
| 01CV - Civils | Cxxx-NCR-001897 | NCR | BOS PTW East Headwall : Scaffold Tube Cast in Crown |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-02-27 | 2015-02-16 11:18 | -11 | 2015-02-03 14:59 | Tunnelling - Linings - In-situ Concrete | 6500 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Contamination | Completed |  | The method statement for constructing the cast in-situ headwalls in PTW detailed a scaffold tube that would be used both as a relief pipe and for future grouting of the crown, if necessary. This was intended to be removed when the concrete had reached initial set, to form an opening in the crown. However, the tube was not removed — see attached picture.
| 01CV - Civils | Cxxx-NCR-001898 | NCR | BOS CH3/CP8 footprint in fireproofing layer |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2015-02-02 | 2015-01-26 13:11 | -7 | 2015-01-22 11:31 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | A footprint is present in the fireproofing lining to the junction of CH3 and CP8.
| 01CV - Civils | Cxxx-NCR-001900 | NCR | BOS CH3 damage to the fireproofing layer of the crown |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2015-02-02 | 2015-01-26 17:10 | -7 | 2015-01-22 11:17 | Tunnelling - Linings - Sprayed Concrete | 3500 |  | Workmanship | Use As-Is | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | Scrape marks to the firperoofing layer of 3B in the crown were observed between Cp7 and CP9 at approximately 1-2 o c'clock.
| 01CV - Civils | Cxxx-NCR-001901 | NCR | PTW Cast Invert Ch.-20 to 20 - Compressive cube Results |  | Contr | BFK |  |  | 2015-03-23 | 2015-03-26 13:11 | 3 | 2015-01-22 17:53 | Tunnelling - Linings - Sprayed Concrete | 59999 |  | Material | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Strengths of compressive cube results for cast invert PTW, Ch. -20 to 20 are below specification. Two sets of compressive cubes were taken, the average results of each set at 28 days was 18.6N and 20.9N, this is below the specification target of 40N. The density was also below the required 2300kg/m3 with results between 2110 -2190kg/m3.
| 01CV - Civils | Cxxx-NCR-001903 | NCR | BOS PTE Slab Level - Out of Tolerance Chainage 66 to 97 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-02-05 | 2015-01-23 15:48 | -13 | 2015-01-22 14:36 | Tunnelling - Linings - In-situ Concrete | 10500 |  | Incorrect Installation | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | invert level survey in PTE between chainages 66m & 97m indicate multiple locations that are low and out of tolerance. The design level of PTE slab is 95.047mAod. The minimum permissible level is 95.027mAod. As the level survey attached shows, multiple locations along the slab are lower than the minimum permissible level of 95.027mAod. The worst effected area is chainage 67m with a reduced level of 95.014mAod (13mm out of tolerance).
| 01CV - Civils | Cxxx-NCR-001904 | NCR | BOS - PTW - 1D incorrect spraying procedure |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2015-03-09 | 2015-02-24 13:01 | -13 | 2015-01-22 15:02 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the spraying of secondary lining to section 1D of PTW ch.97-103 incorrect start up procedure for spaying was obsered. 13/01/15 1445 . The nozzleman was observed starting the spray procedure with the nozzle at axis facing the lining and starting the flow of air, accelerator and then shotcrete. The nozzelman then poceeded to spray up an area to the LHS of the lining looking west. This is not in accordance with Cxxx--C4-GMS-CRT00_ST005-50274.
| 01CV - Civils | Cxxx-NCR-001905 | NCR | BOS PTW East Headwall : Leak at Joint with TBM Segments |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-02-16 | 2015-02-13 18:37 | -3 | 2015-01-22 22:21 | Tunnelling - Tunnelling General | 10500 |  | Workmanship | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Other | Completed |  | A minor seepage has been observed between the cast in-situ headwall and TBM segments at the east end of PTW. The leak is at the joint between pours 1 and 2 of the headwall, on the RHS looking towards positive chainage. The area around the TBM segments was problematic during construction of the headwalls, but all leaks through the Masterseal were sealed before casting concrete — see attached records of inspection for pours 1 and 2.
| 01CV - Civils | Cxxx-NCR-001906 | NCR | BOS PTW East Headwall : Additional Grout Tube Injection Point in Crown |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-02-16 | 2015-02-16 11:40 | 0 | 2015-02-03 15:48 | Tunnelling - Grouting | 8500 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Drawing 90801 details re-injectable grout tubes around the circumference of the platform tunnel PTW, on the face of the cast in-situ east headwall. 2No terminal boxes are shown indicatively at axis level, and this is confirmed in the response to Cxxx-RFI-001419. However, when the secondary lining was sprayed up to the headwall, an additional set of grout tubes were left protruding from the lining in the crown of the platform tunnel. There are currently 4No tubes visible: 2No for LHS crown, 2No for RHS crown (near face and far face).
| 01CV - Civils | Cxxx-NCR-001907 | NCR | De-bonded Fireproofing Layer PTE -30m to 65m |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-02-06 | 2015-02-13 15:16 | 7 | 2015-01-23 14:22 | Tunnelling - Linings - Sprayed Concrete | 25000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Systematic hammer testing of PTE fireproofing has detected multiple de-bonded areas between SFR and fireproofing layers. Initial, planned hammer testing was carried out on 12/12/14. (See attachment 'Hammer Testing - PTE - Smoothing Layer - CH-30 to 55m - 121214'). The areas identified were broken out and resprayed as agreed in the secondary lining meeting. (See attachment 'Form 88 - Fireproofing Repairs 2b). Further hammer testing was carried out on 13/01/15. Additional de-bonded areas and propagation of the initial de-bonded areas was detected. (See attachment 'Hammer Testing - PTE - Smoothing Layer - CH-30 to 55m - 130115'). 46 patches have been identified positioned between horizontal axis and invert at both northern and southern side of the tunnel, identified as PTE 1 to PTE45. Details of patch chainage, size and position can be found in attachment 'PTE de-bonding tracker general'.
| 01CV - Civils | Cxxx-NCR-001909 | NCR | Waterproofing AP7b/AP8 Junction |  | Contr | BFK |  |  | 2015-03-16 | 2015-03-04 10:41 | -12 | 2015-03-02 13:05 | Tunnelling - Tunnelling General | 10500 |  | Incomplete Works | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After inspection of waterproofing in Ap7b/Ap8 Junction it was observed that the waterproofing was brittle and 6mm thickness wasn't achieve as it was spray in May as a Trial. The area was re-spray. Please find attached the approval of the waterproofing before pouring.
| 01CV - Civils | Cxxx-NCR-001911 | NCR | BOS PTW Ch. -28 LHS: Radial joint not formed |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-02-16 | 2015-02-16 11:56 | 0 | 2015-01-23 13:03 | Tunnelling - Tunnelling General | 5000 |  | Supervision/Management | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | ’s accepted method statement for secondary lining involves spraying the invert to axis level to full thickness, forming a radial joint, followed by spraying the crown in layers. While spraying secondary lining to the bay at PTW chainage -28, the radial joint was NOT formed — see attached picture. Work at affected cross section was sprayed and completed in same shift, hence cold joint is unlikely. As part of the works, quality core are to be taken at this location. Note: The text has been edited to address Cxxx comment. now reads ''the radial joint was NOT formed'' 09.02.15 - Briefing sheet attached
| 01CV - Civils | Cxxx-NCR-001912 | NCR | AP3A - Final as-built profile out of tolerance (specific area) |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-02-22 | 2015-02-11 18:03 | -11 | 2015-01-23 17:07 | Tunnelling - Linings - Sprayed Concrete | 22500 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Having reviewed the final as-built profile for AP3A; a tight area were identified at approx CH6.0 - 8.5 at angle 40 - 75degree.
| 01CV - Civils | Cxxx-NCR-001913 | NCR | De-bonded Fireproofing Layer PTW - 7m to 62m |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-02-06 | 2015-02-12 10:38 | 6 | 2015-01-23 17:20 | Tunnelling - Linings - Sprayed Concrete | 55000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Other | Completed |  | Systematic hammer testing of PTW fireproofing has detected multiple de-bonded areas between SFR and Regulating layers. Hammer testing was carried out on 13/01/14. (See attachment 'Hammer Testing - PTE - Smoothing Layer - CH0 to 79m - 130115'). The extents of these hollow areas were marked out on 18/01/15. (See attachment 'Hammer Testing - PTE - Smoothing Layer - CH -7 to 62m - 180115). 14 patches have been identified positioned between horizontal axis and invert at both northern and southern side of the tunnel, , identified as PTW 1 to PTW11 & PTW A to PTW C. Details of patch chainage, size and position can be found in attachment 'PTW de-bonding tracker general'.
| 01CV - Civils | Cxxx-NCR-001914 | NCR | TCR - Hollow spots at AP2W fireproofing |  | Contr | BFK |  |  | 2015-02-06 | 2015-02-03 09:18 | -3 | 2015-01-23 17:50 | Tunnelling - Linings - Sprayed Concrete | 17500 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Other | Completed |  | Hammer testing below the axis level of AP2W over fireproofing layer showed two hollow spots. The location of the spots are marked on the attached hammer testing sheet.
| 01CV - Civils | Cxxx-NCR-001915 | NCR | TCR - Hollow spots at CH1 fireproofing |  | Contr | BFK |  |  | 2015-02-06 | 2015-02-03 14:56 | -3 | 2015-01-23 18:04 | Tunnelling - Linings - Sprayed Concrete | 17500 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Other | Completed |  | Hammer testing below the axis level of CH1 over fireproofing layer showed two hollow spots. The location of the spots are marked on the attached hammer testing sheet.
| 01CV - Civils | Cxxx-NCR-001916 | NCR | PTW - Secondary lining underthickness - Mesh installation |  | Contr | BFK |  |  | 2015-02-11 | 2015-02-03 14:18 | -8 | 2015-01-28 12:01 | Tunnelling - Linings - Sprayed Concrete | 8500 |  | Incorrect Installation | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Further to installation of the mesh in the area of under thickness of secondary lining and following inspection, it became apparent that in two locations, the mesh was installed in wrong orientation. This issue was raised with Cxxx representative and was agreed to leave the mesh as is. The location of the mesh is noted on the attached check sheets.
| 01CV - Civils | Cxxx-NCR-001917 | NCR | BOS WTH AP1 Advance 53 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-02-06 | 2015-01-28 10:42 | -9 | 2015-01-23 18:19 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | 75mm on face of Advance 53 for >12 hours.
| 01CV - Civils | Cxxx-NCR-001920 | NCR | Incorrect temporary headwall built in AP1 (CH50) for safe stop 23rd January 2015 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-02-27 | 2015-02-11 17:13 | -16 | 2015-01-24 16:57 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The exacavation and primary lining profiles for the temporary headwall for safe stop (23rd January 2015 NS) do not match the design or the requirements defined on the RESS
| 01CV - Civils | Cxxx-NCR-001921 | NCR | Hollow spots below axis in PTW tunnel CH -38 to 190 SL lining |  | Contr | BFK |  |  | 2015-03-03 | 2015-03-03 11:32 | 0 | 2015-01-25 17:35 | Tunnelling - Linings - Sprayed Concrete | 17500 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Hollow spots found under axis of PTW tunnel from CH -38 to 190. This areas are found on the SL lining, location as per hammertest sheets attached
| 01CV - Civils | Cxxx-NCR-001922 | NCR | PTE ch 0-64 Final as-built out of tolerance (specific area) |  | Contr | BFK |  |  | 2015-02-27 | 2015-02-20 12:59 | -7 | 2015-01-26 09:46 | Tunnelling - Tunnelling General | 15500 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Having reviewed the final as-built profile for PTE ch 0-64; some tight areas were identified as below: 1) Approx CH 24.5 - 12 and 5 o'clock . Approx 1m2 patch. 2) Approx CH 35 - 9 o'clock . Approx 0.5m2 patch. 3) Approx CH 39.5 -11 o'clock. Approx 0.5m2 patch. 4) Approx CH 44.5 -11 o'clock. Approx 0.5m2 patch. 5) Approx CH 53.5-56 - 4 o'clock. Approx 1m2 patch. 6) Approx CH 56- 58 - 1 o'clock. Approx 0.5m2 patch. Find attached the approval of the remedial action. Further information will be added once tight areas removed.
| 01CV - Civils | Cxxx-NCR-001923 | NCR | PTE ch 0-218 - Cast Invert out of tolerance |  | Contr | BFK |  |  | 2015-02-27 | 2015-02-04 13:38 | -23 | 2015-01-26 12:51 | Tunnelling - Tunnelling General | 18500 |  | Workmanship | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | PTE ch 0 - 218 cast invert U1 finish (0-20mm tolerance) is out of specifications due to an inappropriate leveled. This NCR it is not complaint with the ITP Cxxx--C4-ITP-CRT00_ST005-50144 - BOS TCR CP Cast-in situ and Sprayed Secondary Lining section B4.10 and the general note G36 from the drawing Cxxx-MMD-C4-DDJ-N105-00001 reference below. See attached the profiles out of tolerance and thickness.
| 01CV - Civils | Cxxx-NCR-001924 | NCR | CH1 ch 55-84 - Cast Invert Out of tolerance |  | Contr | BFK |  |  | 2015-02-10 | 2015-02-03 14:22 | -7 | 2015-01-27 14:19 | Tunnelling - Tunnelling General | 10500 |  | Workmanship | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | CH1 ch 55-84 cast invert U1 finish (0-20mm tolerance) is out of specifications due to an inappropriate leveled. This NCR it is not complaint with the ITP Cxxx--C4-ITP-CRT00_ST005-50144 - BOS TCR CP Cast-in situ and Sprayed Secondary Lining section B4.10 and the general note G36 from the drawing Cxxx-MMD-C4-DDJ-N105-00001 reference below. See attached the spreadsheet with all the invert levels and thickness detailed.
| 01CV - Civils | Cxxx-NCR-001925 | NCR | AP2E - Cast Invert out of tolerance |  | Contr | BFK |  |  | 2015-02-09 | 2015-02-03 08:47 | -6 | 2015-01-26 17:56 | Tunnelling - Tunnelling General | 8500 |  | Workmanship | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | AP2E ch 0 - 36 cast invert U1 finish (0-20mm tolerance) is out of specifications due to an inappropriate leveled. This NCR it is not complaint with the ITP Cxxx--C4-ITP-CRT00_ST005-50144 - BOS TCR CP Cast-in situ and Sprayed Secondary Lining section B4.10 and the general note G36 from the drawing Cxxx-MMD-C4-DDJ-N105-00001 reference below. See attached the profiles out of tolerance and thickness.
| 01CV - Civils | Cxxx-NCR-001926 | NCR | AP2W - Cast Invert out of tolerance |  | Contr | BFK |  |  | 2015-02-10 | 2015-02-03 14:28 | -7 | 2015-01-27 14:13 | Tunnelling - Tunnelling General | 8500 |  | Workmanship | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | AP2W ch 4-21 cast invert U1 finish (0-20mm tolerance) is out of specifications due to an inappropriate leveled. This NCR it is not complaint with the ITP Cxxx--C4-ITP-CRT00_ST005-50144 - BOS TCR CP Cast-in situ and Sprayed Secondary Lining section B4.10 and the general note G36 from the drawing Cxxx-MMD-C4-DDJ-N105-00001 reference below. See attached the spreadsheet with all the invert levels and thickness detailed.
| 01CV - Civils | Cxxx-NCR-001928 | NCR | BOS PTW - Oil Spill to invert slab ch 190 |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2015-03-13 | 2015-02-25 17:09 | -16 | 2015-01-28 11:41 | Tunnelling - Linings - In-situ Concrete | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Oil spill on invert slab to chaiange 190 of PTW tunnel.
| 01CV - Civils | Cxxx-NCR-001929 | NCR | BOS - PTE 5A - Outstanding repairs prior to invert pour |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2015-03-13 | 2015-02-24 17:42 | -17 | 2015-01-28 11:43 | Tunnelling - Linings - In-situ Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During requested inspection of section 5a for the invert pour on NS 17/01/15 it was identified that there were masterseal repairs and No. 4 leaks.
| 01CV - Civils | Cxxx-NCR-001930 | NCR | BOS PTW ch 238 - 246 leaks through masterseal |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2015-02-25 | 2015-02-24 14:54 | -1 | 2015-01-28 11:45 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | CRL/Cxxx were requested on NS 17/01/14 to carry out an inspection for approval of spraying the seocndary lining. During the investigation it was identified that there were 2 areas where leaks were present.
| 01CV - Civils | Cxxx-NCR-001931 | NCR | LCE 1 & 2 - Final as-built profile out of tolerance (specific area) |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-02-16 | 2015-02-13 14:50 | -3 | 2015-01-27 16:45 | Tunnelling - Linings - Sprayed Concrete | 19500 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Having reviewed the final as-built profile for LCE 1 & 2; some tight areas were identified as below: 1) Approx CH1030 - 1031 at angle 30 - 35degree. 2) Approx CH1013 - 1014 at angle 325 - 335degree. 3) Approx CH1009 - 1011 at angle 315 - 335degree.
| 01CV - Civils | Cxxx-NCR-001932 | NCR | BOS PTE 2B - Possible Lamination in secondary lining |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2015-02-16 | 2015-02-10 13:18 | -6 | 2015-01-28 11:46 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | It is beleived that a lamination is present between the far face and near face steel within the secondary lining of PTE Ch. 10 - Ch. 38. Details from the seocndary lining minutes: 02/12/14 - lamination in cores taken from the lining 10/12/14 - to be investigated further as no cores were taken in areas steel is presnt 16/12/14 - cores taken on 16/12/14 remedial action to follow ch 10 to ch 38 16/01/15 - 3no cores were taken, presented and discussed with Cxxx. 1 no shows possible evidence of lamination. Prior to this, cores were taken but the logs were not presented. A furhter 3no cores to be taken (250mm deep) in this area. Cores and holes to be witnessed by Cxxx.
| 01CV - Civils | Cxxx-NCR-001933 | NCR | PTE - Final as-builts out of tolerance (specific area) ch 64-216.5 |  | Contr | BFK |  |  | 2015-02-20 | 2015-02-06 13:34 | -14 | 2015-01-27 18:12 | Tunnelling - Linings - Sprayed Concrete | 18500 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Having reviewed the final as-built profile for PTE ch 200-218; some tight areas were identified as below: 1) Approx CH 215-216 - 8 to 12 o'clock . Approx 5m2 patch. Use as is as it is in the flare and is outside the train envelope. 2) Approx CH 216-216.5 - 12 to 3 o'clock. Approx 2m2 patch. Use as is as it is in the flare and is outside the train envelope. 3) Approx CH 86-88.5 - 9 to 11 o'clock. Approx 3m2 patch. 4) Approx CH 184-186 - 1 o'clock. Approx 2m2 patch. 5) Approx CH 196.5 -11 o'clock.Approx 0.5m2 patch. Find attached the approval of the remedial action. Further information will be added once tight areas removed.
| 01CV - Civils | Cxxx-NCR-001934 | NCR | Jack grouting works from TCR5 Grout Shaft, grout pass 5A is missing with field grout test record and cube results. |  | Contr | BFK |  |  | 2015-02-11 | 2015-02-04 13:12 | -7 | 2015-01-28 04:04 | Geotechnical Engineering - Compensation Grouting | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | As part of Jack grouting works from TCR5 Grout shaft, grout pass 5A carried-out between 16/4/2014 NS to 17/4/2014 NS it’s noted that partial of the pass done on 16/4/2014 NS is missing with field grout test record & cube results. This results in failing to show grout characteristics in line with the specification for particular shift.
| 01CV - Civils | Cxxx-NCR-001935 | NCR | Jack grouting works from TCR5 Grout shaft, grout pass 3B is missing with field grout test record. |  | Contr | BFK |  |  | 2015-02-11 | 2015-02-04 13:32 | -7 | 2015-01-28 04:10 | Geotechnical Engineering - Compensation Grouting | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | As part of Jack grouting works from TCR5 Grout shaft, grout pass 3B carried-out between 29/3/2014 DS to 29/3/2014 NS it’s noted that partial of the pass done on 29/3/14 DS is missing with field grout test record. This results in failing to show grout characteristics in line with the specification for particular shift.
| 01CV - Civils | Cxxx-NCR-001936 | NCR | Jack grouting works from TCR5 Grout shaft, grout pass Post CH3 pass 1 is missing with field grout testing record. |  | Contr | BFK |  |  | 2015-03-27 | 2015-02-27 11:56 | -28 | 2015-01-28 04:15 | Geotechnical Engineering - Compensation Grouting | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | As part of Jack grouting works from TCR5 Grout shaft, grout pass Post CH3 pass 1 carried-out between 4/9/2013 DS to 6/9/2013 DS it’s noted that partial of the pass done on 4/9/2013 DS is missing with field grout test record. This results in failing to show grout characteristics in line with the specification for particular shift.
| 01CV - Civils | Cxxx-NCR-001937 | NCR | Jack grouting works from TCR3 Grout shaft, grout pass Post CH1 extension pass1 is missing with field grout test record. |  | Contr | BFK |  |  | 2015-02-27 | 2015-02-17 14:30 | -10 | 2015-01-28 04:20 | Geotechnical Engineering - Compensation Grouting | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | As part of Jack grouting works from TCR3 Grout shaft, grout pass Post CH1 extension pass1 carried-out between 30/8/2013 DS to 31/8/2013 NS its noted that partial of the pass done on 30/8/2013 NS is missing with field grout test record. This results in failing to show grout characteristics in line with the specification for particular shift.
| 01CV - Civils | Cxxx-NCR-001938 | NCR | Concurrent grouting works in TCR along PTE tunnel, some grout passes missing with field grout test records |  | Contr | BFK |  |  | 2015-03-27 | 2015-02-20 17:00 | -35 | 2015-01-28 04:34 | Geotechnical Engineering - Compensation Grouting | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | As part of concurrent grouting works in TCR along PTE tunnel (first section up to end chainage approx. 12m between pilot & enlargement tunnel), out of 1 to 39 grout passes carried out there are few passes as mentioned below are missing with field grout test records. This results in failing to show grout characteristics in line with the specification for the passes below. PTE Pilot Adv Pass 1-4: Total Volume injected – 764 litres on 31/03/2013- No field grout testing record PTE Enlargement Adv Pass 28-31: Total Volume injected – 1144 litres on 21/04/2013 - No field grout testing record
| 01CV - Civils | Cxxx-NCR-001939 | NCR | Concurrent grouting works in TCR along AP7B tunnel section, pass 18-20 is missing with field grout test records. |  | Contr | BFK |  |  | 2015-03-27 | 2015-02-27 11:10 | -28 | 2015-01-28 04:39 | Geotechnical Engineering - Compensation Grouting | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | As part of concurrent grouting works in TCR along AP7B tunnel section, out of 1 to 33 grout passes carried out there is pass 18-20 as mentioned below is missing with field grout test records. This results in failing to show grout characteristics in line with the specification for the pass below. Pass 18-20: Total Volume injected – 568 litres on 13/11/2013- No field grout testing record
| 01CV - Civils | Cxxx-NCR-001940 | NCR | Concurrent grouting works in TCR along PTW Part 3 tunnel section, a few passes are missing with field grout test records. |  | Contr | BFK |  |  | 2015-04-23 | 2015-02-27 14:53 | -55 | 2015-01-28 04:56 | Geotechnical Engineering - Compensation Grouting | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | As part of concurrent grouting works in TCR along PTW Part 3 tunnel section, out of 1 to 343 grout passes carried out there are few passes as mentioned below are missing with field grout test records. This results in failing to show grout characteristics in line with the specification for the passes below. Pass 8-10: Total Volume injected – 992 litres on 7/12/2013- No field grout testing record Pass 209-211: Total Volume injected – 3469 litres on 11/2/2014 - No field grout testing record Pass 215-217: Total Volume injected – 2620 litres on 12/2/2014, 13/2/2014 - No field grout testing record Pass 341-343: Total Volume injected – 1502 litres on 18/4/2014- No field grout testing record
| 01CV - Civils | Cxxx-NCR-001941 | NCR | Concurrent grouting works in TCR along AP4W tunnel section, pass 27-29 is missing with field grout test record. |  | Contr | BFK |  |  | 2015-03-27 | 2015-02-27 11:43 | -28 | 2015-01-28 05:00 | Geotechnical Engineering - Compensation Grouting | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | As part of concurrent grouting works in TCR along AP4W tunnel section, out of 1 to 37 grout passes carried out, the pass as mentioned below is missing with field grout test record. This results in failing to show grout characteristics in line with the specification for the below pass. Pass 27-29: Total Volume injected – 2546 litres on 20/9/2013 - No field grout testing record
| 01CV - Civils | Cxxx-NCR-001942 | NCR | Concurrent grouting works in TCR along AP4E tunnel section, pass 18 - 20 is missing with field grout test record. |  | Contr | BFK |  |  | 2015-03-27 | 2015-02-27 14:56 | -28 | 2015-01-28 05:03 | Geotechnical Engineering - Compensation Grouting | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | As part of concurrent grouting works in TCR along AP4E tunnel section, out of 1 to 39 grout passes carried out, the pass as mentioned below is missing with field grout test record. This results in failing to show grout characteristics in line with the specification for the below pass. Pass 18-20: Total Volume injected – 2584 litres on 3/10/2013 - No field grout testing record
| 01CV - Civils | Cxxx-NCR-001943 | NCR | Concurrent grouting works in TCR along AP3W tunnel section, pass 9-11 is missing with field grout test record. |  | Contr | BFK |  |  | 2015-03-27 | 2015-02-27 15:17 | -28 | 2015-01-28 05:07 | Geotechnical Engineering - Compensation Grouting | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | As part of concurrent grouting works in TCR along AP3W tunnel section, out of 1 to 36 grout passes carried out, the pass as mentioned below is missing with field grout test record. This result in failing to show grout characteristics in line with the specification for the below pass. Pass 9-11: Total Volume injected – 2475 litres on 20/9/2013 - No field grout testing record
| 01CV - Civils | Cxxx-NCR-001944 | NCR | Concurrent grouting works in TCR along CH3 Enlargements tunnel section, there are a few passes missing field grout test record. |  | Contr | BFK |  |  | 2015-03-27 | 2015-02-27 15:22 | -28 | 2015-01-28 05:11 | Geotechnical Engineering - Compensation Grouting | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | As part of concurrent grouting works in TCR along CH3 Enlargements tunnel section, out of 1 to 102 grout passes carried out there are few passes as mentioned below are missing with field grout test records. This result in failing to show grout characteristics in line with the specification for the passes below. Pass 95-98: Total Volume injected – 2147 litres on 1/8/2013- No field grout testing record Pass 99-102: Total Volume injected – 2262 litres on 2/8/2013 - No field grout testing record Pass 147-150: Total Volume injected – 1296 litres on 12/8/2013 - No field grout testing record Pass 163-166: Total Volume injected – 1105 litres on 15/8/2013 - No field grout testing record
| 01CV - Civils | Cxxx-NCR-001945 | NCR | Concurrent grouting works in TCR along AP3E tunnel section, pass 9-11 is missing with field grout test record. |  | Contr | BFK |  |  | 2015-04-21 | 2015-04-24 07:32 | 3 | 2015-01-28 05:16 | Geotechnical Engineering - Compensation Grouting | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | As part of concurrent grouting works in TCR along AP3E tunnel section, out of 1 to 40 grout passes carried out, the pass as mentioned below is missing with field grout test records. This result in failing to show grout characteristics in line with the specification. Pass 9-11: Total Volume injected – 2146 litres on 03/10/2013 - No field grout testing record
| 01CV - Civils | Cxxx-NCR-001946 | NCR | Concurrent grouting works in TCR along CH1 Extension tunnel section, a few passes missing with field grout test records. |  | Contr | BFK |  |  | 2015-03-27 | 2015-02-27 15:25 | -28 | 2015-01-28 05:20 | Geotechnical Engineering - Compensation Grouting | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | As part of concurrent grouting works in TCR along CH1 Extension tunnel section, out of 1 to 82 grout passes carried out there are few passes as mentioned below are missing with field grout test records. This result in failing to show grout characteristics in line with the specification. Extension pass 44-46: Total Volume injected – 1926 litres on 20/5/2013 - No field grout testing record Extension pass 80-82: Total Volume injected – 1300 litres on 29/5/2013 - No field grout testing record
| 01CV - Civils | Cxxx-NCR-001948 | NCR | PTW / AP2W junction - Exposed secondary lining rebar |  | Contr | BFK |  |  | 2015-02-23 | 2015-02-24 15:08 | 1 | 2015-01-28 12:25 | Tunnelling - Linings - Sprayed Concrete | 9500 |  | Damaged | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Other | Completed |  | Following hammer testing hollow spots where identified in secondary lining below axis level in PTW/AP2W junction. During the operation of removing the hollow spots, two number of secondary lining reinforcement was exposed. See attached picture.
| 01CV - Civils | Cxxx-NCR-001949 | NCR | De-bonded Fireproofing Layer Section 3a & 3b. (CH3 + CP7 to CP10). |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-02-27 | 2015-02-16 11:45 | -11 | 2015-02-11 01:16 | Tunnelling - Linings - Sprayed Concrete | 25500 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Systematic hammer testing of 3a & 3b fireproofing has detected multiple de-bonded areas between SFR and fireproofing layers. Hammer testing was carried out on 09/12/14 (See attachment 'Hammer Testing CH3 091214) & 090115 (See attachments 'Hammer Test CH3 090115', Hammer Testing CP7 to CP10 090115). A number of the patches in CH3 were broken out and re-sprayed in December 2014. Of these patches patch: 3,5,6,7,13,20,21,26 & 28 were signed off as ok by Cxxx/ following the spray. Remaining patches 1a,1b,1c,2,4,9,10a,10b,11,12,14,15a,15b, 16a,16b,16c,17,18a,18b,19,24,27a,27b,29a,29b,29c and 30 remained. See patch overview 3a/3b attached for patch location. has divided these patches into two categories. Category 1 is use as is. These patches are a minimum of 200mm below the finish level of the 1st stage concrete and in positions that have equal to or in excess of the required design thickness before the fireproofing layer was applied. The dimensions of each patch, its RL as associated thickness of SFR behind the fireproofing can be found in attachment 'De-Bonding 3a3b - Use as is summary' Patches that propose to use as is are patches 1a,1b,1c,2,4,9,10a,10b,18a,18b,19,22,23, 24 & 30. For each of these patches see associated PDF attachment. This PDF provides information of the position of the patch in relation to the 1st stage concrete and the associated lining thickness in the area. Category 2 is break out and re-apply. These patches are either above the finish level of 1st stage concrete or the required thickness of SFR prior to application of fireproofing is not there. Patches that propose to break out are patches 11,12,14,15(a+b),16(a+b+c),17,27(a+b) & 29(a+b+c). See 'De-Bonding 3a3b - Break out summary' for information of patch location and size.
| 01CV - Civils | Cxxx-NCR-001950 | NCR | Missing Bars in AP8 Cast In-Situ Secondary Lining |  | Contr | BFK |  |  | 2015-02-27 | 2015-02-13 17:17 | -14 | 2015-02-02 12:27 | Tunnelling - Linings - In-situ Concrete | 8500 |  | Incorrect Installation | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The cast in situ concrete shown in drawing Cxxx-MMD-C4-DDD-N105_5-00496 has been poured from the headwall back to the inside face of the right hand side of the opening into LP9 from AP8. 6 no. FF1 & SF bar mark 116, 6 no. NF1 and SF bar mark 113 and 1 no. SF bar mark 111 should have been cast into this pour and have been omitted. These are shown highlighted on the attached sketch and the pour is shown in the attached photograph.
| 01CV - Civils | Cxxx-NCR-001951 | NCR | BOS WTH AP1 RMS040 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-02-20 | 2015-02-03 17:12 | -17 | 2015-01-29 12:26 | Tunnelling - Linings - Sprayed Concrete | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Crown target (01) of RMS040 in AP1 breached amber trigger (showed ~10mm settlement) between first initial and second readings (<24hrs).
| 01CV - Civils | Cxxx-NCR-001952 | NCR | Localised Fireproofing Under thickness - PTW ch0 to 97 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-03-12 | 2015-03-11 09:56 | -1 | 2015-01-29 14:40 | Tunnelling - Tunnelling General | 35000 |  | Supervision/Management | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A review of fireproofing thickness plots for PTW between chainages 0 & 97m has identified a number of underthick areas (less than the required 50mm). Using guidance provided by the CEG the areas of under thickness have been categorised. All areas within PTW have the potential to be subject to train fire and therefore the rules relevant for these areas have been applied for the proposed solution to these under thick areas. 1. PTW 69: Depth: 40mm Longitudinal length: 500mm Area: 0.5m^2 Comment: The area is isolated with no under thickness area within 5m longitudinally. proposes to leave as is. 2. PTW ch80 to ch97 Applying the guidance provided by the CEG, this area is deemed as unacceptable hence proposes to mill the inclusive area between ch 80 and ch97 and re-spray a minimum thickness of 50mm fireproofing. 4/03/15: The area of under thickness is less than 250mm x 250mm, below axis (9 o'clock position) and on non passenger side of the tunnel. propose to 'use as is' for the following reasons: 1). over 50mm of fire proofing all around the patch 2). Patch repair could have long term durability issues. 03/03/15: PTW 69 - propose 'use as is' due to the area's length and thickness, 40-45mm. As per PMC 10179 Guidance. PTW 85 - rescanned the area, these new scans are attached. These show that no area is less than 40mm. propose 'use as is' .
| 01CV - Civils | Cxxx-NCR-001953 | NCR | BOS PTE 5A/2C - Damage to masterseal from cable removed post spraying |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2015-03-09 | 2015-02-24 15:07 | -13 | 2015-01-29 16:33 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | A cable had been sprayed into the masterseal layer of the PTE tunnel LHS facing east. Between Ch. 120 -Ch.85 there are several areas where it is visible. The cable was removed and has left behind an imprint in areas with dirt embedded in the masterseal.
| 01CV - Civils | Cxxx-NCR-001954 | NCR | Missing profile information for Adv 54, 55 and 56 invert of AP1 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-03-02 | 2015-02-09 18:25 | -21 | 2015-02-02 11:44 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The invert primary thickness for Adv 54 55 and 56 was not presented immediately within the 24 hour period after the advance was completed.
| 01CV - Civils | Cxxx-NCR-001955 | NCR | BOS PTE ch0 to ch74 Low Density results for BFK027 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-02-27 | 2015-02-06 16:37 | -21 | 2015-02-03 11:45 | Tunnelling - Linings - In-situ Concrete | 10500 |  | Material | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | have experienced drop in density in cubes results for mix 027 in PTE ch0 to ch74. The drop does not meet the required 2300kg/m3 as specified in KF10. Even with the drop in density, the 28-day compressive strengths that are achieved are still exceeding the specification laid out by KF10. have done the calculation as below showing that the asbuilt mass with actual density is greater than the designed requirement due to 1.unconsumed 100mm protective layer. 2. Scans showing additional depth prior to secondary lining 1.Unconsumed 100mm protective concrete calculation for mass (per linear metre of tunnel): Design mass of slab = 1.9074m² × 2300kg/m³ = 4387kg/m Actual with protective concrete poured as structural = (1.9074m² + 0.1601m²) × 2200kg/m³ = 4549kg/m So as built mass > design mass. 2. In addition to the above, the affected inclusive chainages shows additional average depth prior to secondary lining to be above 100mm which has not been considered in the as built calculation above. (see attached scans) Note: Also find attached screen prints from AutoCAD calculating the cross sectional area of the invert and protective concrete in the platform tunnels Key for low density at BOS attached as per discussion between Ben Darkwa and Robert Wallner. 6.02.15
| 01CV - Civils | Cxxx-NCR-001956 | NCR | PTW 4 - Reinjectable grout tube |  | Contr | BFK |  |  | 2015-02-27 | 2015-03-11 11:05 | 12 | 2015-02-03 17:31 | Tunnelling - Tunnelling General | 8500 |  | Supervision/Management | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After getting approval of waterproofing from CH 198 to CH220, have started spraying 100mm thickness of Secondary Lining to cover the FF Steel of the junctions in that area. When spraying the second bay it was noticed that there were two issues: • The brackets of the reinjectable grout tubes were not painted with Masterseal; • The Reinjectable grout tube and hydrophilic stripes were missing on the sides of the invert. These two items were agreed to be installed to close out NCR’s 1863 & 1811. The spraying activities were put on hold to carry out these works (around chainage 214). The brackets of the reinjectable grout pipe at CH210 were touched up with Masterseal 865, the hydrophilic strips and the reinjectable grout pipes were installed as per NCR’s mentioned above. These works have taken approximately two hours given enough time to ensure the required Shore A strength.
| 01CV - Civils | Cxxx-NCR-001957 | NCR | BOS CH3 : Damage to __ at Headwall |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-02-27 | 2015-02-05 16:59 | -22 | 2015-02-04 08:38 | Tunnelling - Linings - Sprayed Concrete | 15500 |  | Damaged | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Cxxx-NCR-001650 detailed a proposal for mitigating the effects of overspray onto Masterseal at the CH3 headwall, which included the installation of __ 550MI injectable water bar around the circumference of the joint between the headwall and CP7/8 sprayed secondary lining. However, this __ was not sufficiently protected during spraying so was coated in concrete, and may also have been damaged during subsequent milling of the headwall.
| 01CV - Civils | Cxxx-NCR-001958 | NCR | BOS-CH3 LHS box out close to headwall |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-02-16 | 2015-02-11 18:13 | -5 | 2015-02-04 12:52 | Tunnelling - Tunnelling General | 19500 |  | Damaged | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Box out formed close to CH3 headwall due to damage to masterseal at time of spraying secondary lining. Boxed out area was repaired at later date but minimum 200mm overlap could not be achieved hence adcor 550mi was installed to perimeter as mitigation. See checksheet attached showing completion of repair 10.02.15- Location for box out was chainage ch45.5(LHS) at 7 o'clock position. size of box out was 500mm square.
| 01CV - Civils | Cxxx-NCR-001959 | NCR | BOS PTW 4b Secondary lining water ingress |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2015-03-13 | 2015-03-09 11:01 | -4 | 2015-02-04 13:38 | Tunnelling - Linings - Sprayed Concrete | 8500 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Underneath the PTW junction with AP2A in the sprayed secondary invert lining there are a number (at least 8) of locations where water is leaking through the secondary lining. The locations are mostly associated with the still protruding dowell bars.
| 01CV - Civils | Cxxx-NCR-001960 | NCR | BOS VD3 ch5.5 to ch24 Low Density results for BFK027 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-02-16 | 2015-02-09 15:00 | -7 | 2015-02-04 18:42 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | have experienced drop in density in cubes results for mix 027 VD3. The drop does not meet the required 2300kg/m3 as specified in KF10.
| 01CV - Civils | Cxxx-NCR-001961 | NCR | BOS VD4 ch4.5 to ch17.5 Low Density results for BFK027 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-02-16 | 2015-02-09 15:55 | -7 | 2015-02-04 18:44 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | have experienced drop in density in cubes results for mix 027 in VD4. The drop does not meet the required 2300kg/m3 as specified in KF10.
| 01CV - Civils | Cxxx-NCR-001962 | NCR | BOS PTW ch-61 to ch263.5 Low Density results for BFK027 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-02-16 | 2015-02-10 10:59 | -6 | 2015-02-07 10:07 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | have experienced drop in density in cubes results for mix 027 in PTW ch-61 to ch263.5. The drop does not meet the required 2300kg/m3 as specified in KF10.
| 01CV - Civils | Cxxx-NCR-001963 | NCR | BOS LCE2 ch20 to ch36 Low Density results for BFK027 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-02-16 | 2015-02-09 16:01 | -7 | 2015-02-04 18:47 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | have experienced drop in density in cubes results for mix 027 in LCE. The drop does not meet the required 2300kg/m3 as specified in KF10.
| 01CV - Civils | Cxxx-NCR-001964 | NCR | BOS-PTW ch62 oil leak |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-02-18 | 2015-02-09 11:45 | -9 | 2015-02-04 13:13 | Tunnelling - Tunnelling General | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Oil leak was found at chainage 62 in the PTW. Source of leakage was not identified so all plant checked for defect. Plant nappies are on site and are being used to stop future reoccurrences See photo attached
| 01CV - Civils | Cxxx-NCR-001965 | NCR | BOS AP3A ch-0.5 to ch10 Low Density results for BFK027 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-02-16 | 2015-02-09 16:07 | -7 | 2015-02-04 19:15 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | have experienced drop in density in cubes results for mix 027 in AP3A. The drop does not meet the required 2300kg/m3 as specified in KF10.
| 01CV - Civils | Cxxx-NCR-001966 | NCR | BOS CH3/CP7/CP8/CP9/CP10 Low Density results for BFK027 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-02-16 | 2015-02-09 16:14 | -7 | 2015-02-04 19:09 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | have experienced drop in density in cubes results for mix 027 in the above locations. The drop does not meet the required 2300kg/m3 as specified in KF10.
| 01CV - Civils | Cxxx-NCR-001967 | NCR | Fibre Rebound not carried out in October 2014 @ BOS. |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-02-18 | 2015-02-05 17:27 | -13 | 2015-02-04 14:41 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | ITP sates that Fibre Rebound Test is to be carried out every two months, however at BOS fibre rebiund was carried out in August 2014, the next test was done in November 2014; this should have been done in October 2014.
| 01CV - Civils | Cxxx-NCR-001970 | NCR | Secondary lining early age strength BOS |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-02-16 | 2015-02-16 18:12 | 0 | 2015-02-05 12:23 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Out of all the secondary lining sprayed since thew 19/11/14 in BOS a total of 17 tests have been completed where 42 should have been done. The requirement as per FCD 1141 is that an early age stregth panel should be sprayed every 24hrs. Please find attached BOS compressive summary from the 19/11/2014 to present of all available core compressive strengths, This shows that all test done are all above the J2 curve and KT20 requirements. propose to use as is based on all data collected within the said period.
| 01CV - Civils | Cxxx-NCR-001971 | NCR | PTW Lamination Secondary Lining |  | Contr | BFK |  |  | 2015-02-23 | 2015-02-16 12:02 | -7 | 2015-02-09 09:43 | Tunnelling - Linings - Sprayed Concrete | 9500 |  | Workmanship | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After milling secondary lining tight spots it was notice there was a lamination present in the secondary lining between ch 160 - 190. Cores were taken,revised and accepted by Cxxx/CRL. This NCR is not compliant with an homogeneous layer specified in KT20.2202
| 01CV - Civils | Cxxx-NCR-001973 | NCR | BOS WTH ES1 Primary Lining - Concrete Early Strength Test Panels |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-02-20 | 2015-02-09 18:18 | -11 | 2015-02-06 15:02 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Not all strength tests completed for Early Age Strength test panel for Advance 2 Early Age Strength test results not available until Advance 4. Test results should be submitted every 3no. advances.
| 01CV - Civils | Cxxx-NCR-001974 | NCR | BOS PTE 2C - Crack at chainage 70 |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2015-03-11 | 2015-02-24 17:47 | -15 | 2015-02-09 10:36 | Tunnelling - Linings - Sprayed Concrete | 9500 |  | Damaged | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Other | Completed |  | It was observed on 02/02/15 that a circumferential crack was present and propogating through the masterseal at approx. chainage 70 of PTE.
| 01CV - Civils | Cxxx-NCR-001975 | NCR | TCR Monthly Tests (Mix17.2) - January |  | Contr | BFK |  |  | 2015-05-12 | 2015-04-21 11:41 | -21 | 2015-04-14 15:28 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Planning | Use As-Is | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | The monthly test panels for mix 17.2 were not sprayed during January to allow testing for beams and drying shrinkage.
| 01CV - Civils | Cxxx-NCR-001977 | NCR | Damaged concrete in PTW5 cast in situ slab |  | Contr | BFK |  |  | 2015-02-23 | 2015-02-13 11:27 | -10 | 2015-02-09 15:51 | Tunnelling - Linings - In-situ Concrete | 5500 |  | Damaged | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | When breaking the invert in PTW5 that didn't achieve the expected strength, a bit of concrete that was not meant to be broken (chainage +3) was damaged. See picture attached. It was agreed with CRL (C.Barron) and Cxxx (D.Harris) to square it off creating a 50mm key in the bottom, and pour it with the following bay.
| 01CV - Civils | Cxxx-NCR-001978 | NCR | De-Bonded Fireproofing Layer VD3 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-02-17 | 2015-02-16 11:50 | -1 | 2015-02-16 08:43 | Tunnelling - Linings - Sprayed Concrete | 35500 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Systematic hammer testing of VD3 fireproofing detected a number of de-bonded areas between the two fireproofing layers. Hammer testing was carried out on 02/01/15 (below axis) and 08/01/15 (crown), see attached hammer test sheets. The patches were broken out and resprayed with fireproofing. The patches were re-tested on 10/02/15. Please find attached checksheet. 2 hollow areas were identified. Area 1 was 1.5m x 0.3m in size, positioned at CH 19m (LHS-8 O'clock). Area 2 was 0.200m x 0.300m is size, positioned at CH11 (RHS-5 O'clock). On 10/02/15, it was agreed between R.Wallner (Cxxx), C.Barron (CRL) & E Batty () to remove hollow area 1 and remediate. Due to the small size of area 2 it was agreed to leave as is. See 'VD3 Hammer Test 100215'. Following the completion of the works area 1 was retested. See 'VD3 Hammer Test 150215'.
| 01CV - Civils | Cxxx-NCR-001979 | NCR | De-Bonded Fireproofing Layer VD4 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-02-17 | 2015-02-16 12:06 | -1 | 2015-02-16 01:01 | Tunnelling - Linings - Sprayed Concrete | 11500 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Systematic hammer testing of VD4 fireproofing detected 2No de-bonded areas between the two fireproofing layers. Hammer testing was carried out on 08/01/15, see attached hammer test sheet. 2 No patches were broken out and rendered with fireproofing. These were found to be hollow when re hammer tested and were subsequently broken out creating one patch. This was then re sprayed with fireproofing. These areas were hammer tested on the 15/02/15 and found to be sound. Please find attached checksheets.
| 01CV - Civils | Cxxx-NCR-001980 | NCR | BOS WTH ES1 Primary Lining - Concrete Early Strength - compressive strength cores |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-02-24 | 2015-02-18 15:26 | -6 | 2015-02-10 10:18 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Compressive strength cores were not taken from panels sprayed for advance 4, 5 or 7. Panels were disposed of before the cores had been taken.
| 01CV - Civils | Cxxx-NCR-001981 | NCR | TCR - Hollow spots at AP3W fireproofing |  | Contr | BFK |  |  | 2015-03-20 | 2015-03-16 14:04 | -4 | 2015-02-12 14:51 | Tunnelling - Linings - Sprayed Concrete | 10500 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Hammer testing below the axis level of AP3W over fireproofing layer showed two hollow spots. The location of the spots are marked on the attached hammer testing sheet.
| 01CV - Civils | Cxxx-NCR-001982 | NCR | Missing details in AP8 F50s |  | Contr | BFK |  |  | 2015-02-25 | 2015-02-13 18:46 | -12 | 2015-02-11 15:50 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Some AP8 F50 forms for excavation and primary lining and primary lining thickness has missing details such as Nozzleman name and signature, Flow, Excavation start and finish time spray start and finish time.
| 01CV - Civils | Cxxx-NCR-001983 | NCR | Missing Form50 for AP8 advance 20 |  | Contr | BFK |  |  | 2015-02-27 | 2015-02-13 15:25 | -14 | 2015-02-11 14:00 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Missing Form50 for AP8 advance 15
| 01CV - Civils | Cxxx-NCR-001984 | NCR | CP4 - Cast in situ invert level |  | Contr | BFK |  |  | 2015-03-02 | 2015-02-17 14:35 | -13 | 2015-02-16 18:01 | Tunnelling - Tunnelling General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | According to RFI Cxxx-RFI-001332 attached below, the CP4 tunnel axis level on drawing Cxxx-MMD-C4-DDD-N105_Z-00067 was changed from 103.231 to 103.290. have not taken this into account when casting the invert slab of CP4. This has caused a difference of level of 59mm to the design level.
| 01CV - Civils | Cxxx-NCR-001985 | NCR | TCR - PTW East Headwall - Reinjectable grout tubes |  | Contr | BFK |  |  | 2015-03-02 | 2015-03-09 16:59 | 7 | 2015-02-16 17:09 | Tunnelling - Tunnelling General | 10500 |  | Incorrect Installation | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The works at PTW East headwall have been carried out according to the following sequence: 1 - cast invert slab up to headwall; 2 - install reinjectable grout tubes at the construction joint between face of invert slab and face of headwall; 3 - pour 1st lift of headwall. As per drawing Cxxx-MMD-C4-DDD-N105_Z-00071, the construction joint between the cast in-situ headwall and the sprayed secondary lining should have two reinjectable grout tubes around the full profile of the tunnel. During Activity 2 described above, it was only installed one reinjectable grout tube instead of two as per design. Having said that, it is now impossible to install the reinjectable grout tube that is missing between the invert slab and the headwall. See pic attached.
| 01CV - Civils | Cxxx-NCR-001986 | NCR | BOS WTH ES1 Advance 11 face support |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-02-26 | 2015-02-18 15:56 | -8 | 2015-02-12 13:13 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Calculations of thickness of SCL sprayed to face of Advance 11 show some areas <150mm.
| 01CV - Civils | Cxxx-NCR-001987 | NCR | BOS PTE ch0 to 50 Localised Fireproofing under thickness excluding junctions |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-02-26 | 2015-02-16 16:54 | -10 | 2015-02-12 14:29 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Supervision/Management | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A review of fireproofing thickness plots for PTE between chainages 0 & 50m has identified one number area of underthickness (less than the required 50mm). Using guidance provided by the CEG the areas of under thickness have been categorised. All areas within PTE have the potential to be subject to train fire and therefore the rules relevant for these areas have been applied for the proposed solution to these under thick areas. 1. PTE CH 24: Depth: 40mm Longitudinal length: 400mm Area: 0.08m^2 Comment: The area is isolated with no under thickness area within 5m longitudinally. proposes to leave as is.
| 01CV - Civils | Cxxx-NCR-001988 | NCR | Localised Fireproofing Under thickness in CH3,CP7,CP8,CP9,CP10 excluding junctions |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-02-26 | 2015-02-16 18:09 | -10 | 2015-02-12 17:20 | Tunnelling - Linings - Sprayed Concrete | 15500 |  | Supervision/Management | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Using guidance provided by the CEG in PMC10179, the areas of under thickness have been categorised. All areas within CH3,CP7,CP8,CP9 and CP10 are not subject to a train fire and meet the guidance as stated below (see attached marked up scans): A.2 Areas not subject to a train fire In passenger areas (cross-passages / concourses) larger patches of fire-proofing less than 50mm, but more than 30mm, are accepted, on the basis that the EUREKA fire curve does not apply. In practice the largest of these areas are: 1m long x 4m measured around the circumference of the tunnel. 3m long x 1m measured around the circumference of the tunnel. The largest area identified is 1m^2 therefore meets the above guidance hence propose to use as is
| 01CV - Civils | Cxxx-NCR-001990 | NCR | Localised Fireproofing Under thickness - LCE Ch 0 to 36.5 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-02-27 | 2015-02-16 18:20 | -11 | 2015-02-13 01:00 | Tunnelling - Linings - Sprayed Concrete | 15500 |  | Workmanship | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A review of fireproofing thickness profiles, chainage 0 to 36.5 m, has identified 6 number area of underthickness (less than the required 50mm). The scanning process was in the early stages of its use and the complex geometry of LCE means that the interpolation of manual survey of the secondary lining and the and final scanned profile has been used to present the results. This means that the longitudinal length of an under thickness area cannot be defined. From chainage 22 the Easychecker and scanning system was fully operational and there are no underthickness areas. The areas of under thickness are as follows: - Chainage 6 - 3 o'clock, 40-45mm thickness. Profiles 0.5m before and after this area have sufficient thickness. Therefore the length of this area is less than 1m however is undefinable. - Chainage 8 - 2 o'clock, 40-45mm thickness. Profiles 0.5m before and after this area have sufficient thickness. Therefore the length of this area is less than 1m however is undefinable. - Chainage 9 - 12 o'clock, 40-45mm thickness. Profiles 0.5m before and after this area have sufficient thickness. Therefore the length of this area is less than 1m however is undefinable. - Chainage 10 - 5 o'clock, 40-45mm thickness. Profiles 0.5m before and after this area have sufficient thickness. Therefore the length of this area is less than 1m however is undefinable. This area is below the mass infill of the LCE tunnel. - Chainage 11 - 7 o'clock, 40-45mm thickness. Profiles 0.5m before and after this area have sufficient thickness. Therefore the length of this area is less than 1m however is undefinable. This area is below the mass infill of the LCE tunnel. - Chainage 15 - 1 o'clock, 40-45mm thickness. Profiles 0.5m before and after this area have sufficient thickness. Therefore the length of this area is less than 1m however is undefinable. - Chainage 20.5 - 1 o'clock, 40-45mm thickness. Profiles 0.5m before and after this area have sufficient thickness. Therefore the length of this area is less than 1m however is undefinable. See attachment for profiles. propose these areas to be 'Use as is' due to their size and 40-45mm thickness.
| 01CV - Civils | Cxxx-NCR-001991 | NCR | TCR Fireproofing - Drying Shrinkage - November 2014 |  | Contr | BFK |  |  | 2015-04-01 | 2015-03-06 14:28 | -26 | 2015-03-04 08:55 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | No drying shrinkage tests were carried out during November 2014 on Fireproofing Mix 21.
| 01CV - Civils | Cxxx-NCR-001992 | NCR | BOS AP1 Vent Tunnel : Breaking Out Small Part of Primary Lining without RESS |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-03-02 | 2015-02-24 17:52 | -6 | 2015-02-16 09:18 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | On 10/11/15, works to fill the existing LU Vent Tunnel with foamed concrete were ongoing. In order to close up the opening created from AP1, a radial timber shutter was fabricated by the carpenters, which was to be drilled and fixed into the cast iron segments. On 10/11/15 nightshift, it was found that a small part of the sprayed concrete primary lining of AP1 would obstruct the shutter, and this was broken out so that the shutter could be fixed. However, the SRG was not consulted and there was no RESS for the breaking out.
| 01CV - Civils | Cxxx-NCR-001993 | NCR | 5 cores tested at 28 days |  | Contr | BFK |  |  | 2015-03-11 | 2015-02-24 15:19 | -15 | 2015-02-18 08:55 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | ITP states 6no. cores to be tested at each age, for sample 767, AP4E Fireproofing Ch. 25-20, only 5no. cores were tested at 28 days.
| 01CV - Civils | Cxxx-NCR-001994 | NCR | BOS PTW Ch. 135 : Damp Patches on Secondary Lining |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-03-13 | 2015-02-27 15:07 | -14 | 2015-02-20 12:29 | Tunnelling - Linings - Sprayed Concrete | 9500 |  | Incomplete Works | Repair | 2 (6-60k) | Complete | Material/Preservation Problems - Other | Completed |  | Two damp patches have been observed on the secondary lining in PTW at chainage 135, at the joint between two bays, at approx. 7–8 o’clock on the profile.
| 01CV - Civils | Cxxx-NCR-001995 | NCR | In February 2015, SCL 708, only 4 core tested @ 1 day rather than 6 cores. |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-03-03 | 2015-02-20 17:10 | -11 | 2015-02-17 13:46 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | In February 2015 for Sample Number SCL 708, only four cores were tested rather than 6 as stipulated by ITP.
| 01CV - Civils | Cxxx-NCR-001997 | NCR | BOS PTW 4B : 2SL Contraction Joints CJ.0301 and CJ.0302 Not Cut Prior to 20MPa Strength |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-03-09 | 2015-03-10 18:34 | 1 | 2015-02-17 18:20 | Tunnelling - Linings - Sprayed Concrete | 8000 |  | Incomplete Works | Rework | 2 (6-60k) | Complete | Management Problem - Inadequate supervision | Completed |  | The secondary lining contraction joints CJ.0301 and CJ.0302, in PTW 4B around chainages 250–260 outside AP2A, were not cut before the concrete reached 20MPa strength, as per drawing Cxxx-MMD-C4-DDD-Cxxx_Z-00053.
| 01CV - Civils | Cxxx-NCR-001998 | NCR | TCR - Hollow spots at S1 fireproofing |  | Contr | BFK |  |  | 2015-03-04 | 2015-02-24 15:23 | -8 | 2015-02-18 16:08 | Tunnelling - Linings - Sprayed Concrete | 15500 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Hammer testing below the axis level of S1 over fireproofing layer showed three hollow spots. The location of the spots are marked on the attached hammer testing sheet.
| 01CV - Civils | Cxxx-NCR-001999 | NCR | BOS PTE 5A/5B - Potential masterseal contamination |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2015-03-13 | 2015-03-02 15:57 | -11 | 2015-02-19 10:34 | Tunnelling - Linings - Sprayed Concrete | 15500 |  | Workmanship | Repair | 2 (6-60k) | Complete | Procedure Problem - Other | Completed |  | Crossrail observed on 09/02/15 high dust levels in PTE Section 2c/5a as a result of spraying secondary lining at Ch 68 to Ch 92 and spraying masterseal at Ch 126 to Ch 182 simultaneously without a curtain separating the two areas. This has the potential for the masterseal to be contaminated with the dust from the secondary lining spraying. The ongoing dust generating activity of spraying secondary lining continued during the curing period of the masterseal. During general inspection of the masterseal on 18/02/15 the masterseal was discoloured, soft to the touch in many areas of the invert and crumbled when you ran your finger over the surface (without any applied pressure).
| 01CV - Civils | Cxxx-NCR-002000 | NCR | De-Bonded Fireproofing CP5 CH0 to 34m |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-03-11 | 2015-03-02 10:20 | -9 | 2015-02-20 11:59 | Tunnelling - Linings - Sprayed Concrete | 17500 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Systematic hammer testing of CP5 fireproofing has detected multiple de-bonded areas between SFR and fireproofing layers. Initial, planned hammer testing was carried out on 08/01/15. See attachment: ' Form 116 - Smoothing Layer Hammer Testing - CP5 080115.pdf' . As a result of the breakout a number of the areas propagated. This was identified through hammer testing carried out on 10/01/15. See attachment: ' Form 116 - Smoothing Layer Hammer Testing - CP5 100115.pdf '. Further breaking was carried out; a number of smaller patches jointed together. The final size and location of the de-bonded areas prior to respray is as follows. Patches 1 to 3 (merged). Area of patch 3.8m x 2.8m. Chainage of cl of patch 25.1m. 7 O'Clock. Patches 4 & 6 (merged). Area of patch 4m x 3m. Chainage of cl of patch 27.5m. 4 O'Clock. Patch 7. Area of patc 1.5m x 1.5m. Chainage of cl of patch 20. 4 O'Clock. Following the respray of the hollow areas the patches were re-tested. See attachment: Form 116 - Smoothing Layer Hammer Testing - CP5 Final 180215.pdf
| 01CV - Civils | Cxxx-NCR-002001 | NCR | Missng F50 for CP4 advance 1 and 2 |  | Contr | BFK |  |  | 2015-03-06 | 2015-02-24 15:34 | -10 | 2015-02-20 15:23 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Missng Excavation and primary lining F50 for CP4 advance 1 and 2
| 01CV - Civils | Cxxx-NCR-002003 | NCR | De-Bonded Fireproofing PTW CH97 to 110m |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-03-18 | 2015-03-09 11:14 | -9 | 2015-03-04 08:09 | Tunnelling - Linings - Sprayed Concrete | 12500 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Systematic hammer testing of PTW fireproofing has detected multiple de-bonded areas between SFR and Regulating layers. 6 patches were identified positioned between horizontal axis and invert at both northern and southern side of the tunnel, identified as PTW 7, 12, 13, 14, 16, 18, 19. These were marked out and cut out. Joint hammer testing of the hollow areas was carried out on 22/02/15.The extents of these hollow areas were tested to ensure a sound bond before respraying. The patches were resprayed on the 23/02/15. These patches were then jointly retested on the 26/02/15 confirming a sound bond has been achieved. Please see attached hammer test records and spray checksheets.
| 01CV - Civils | Cxxx-NCR-002004 | NCR | PTW 225-230 Underthickness Secondary Lining |  | Contr | BFK |  |  | 2015-03-13 | 2015-02-24 18:02 | -17 | 2015-02-22 21:26 | Tunnelling - Linings - Sprayed Concrete | 15500 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After spraying the secondary lining in PTW between ch. 225 - 230, the profiles have been assessed by __ () and presented to __(Cxxx).It was concluded that there is concern with under thickness as the 250mm thickness was not achieved as required in PMI 1689.
| 01CV - Civils | Cxxx-NCR-002005 | NCR | TCR - Hollow spots at PTW fireproofing |  | Contr | BFK |  |  | 2015-03-31 | 2015-03-26 13:24 | -5 | 2015-03-17 16:23 | Tunnelling - Linings - Sprayed Concrete | 25000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Hammer testing below the axis level of PTW over fireproofing layer showed various hollow spots. The location of the spots are marked on the attached hammer testing sheets.
| 01CV - Civils | Cxxx-NCR-002006 | NCR | AP3E - Final as built profiles ch 9 -33.5 |  | Contr | BFK |  |  | 2016-11-03 | 2017-03-10 16:20 | 127 | 2015-02-19 12:58 | Tunnelling - Linings - Sprayed Concrete | 15500 |  | Workmanship | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Fire proofing as-built profile out of designed tolerance for AP3E- chainages 9 - 33.5
| 01CV - Civils | Cxxx-NCR-002007 | NCR | AP1 - Final As Builts Profiles |  | Contr | BFK |  |  | 2015-03-06 | 2015-03-10 09:45 | 4 | 2015-02-20 07:51 | Tunnelling - Linings - Sprayed Concrete | 35500 |  | Workmanship | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Fire proofing as-built profile out of designed tolerance for AP1- chainages 0-9
| 01CV - Civils | Cxxx-NCR-002008 | NCR | 6F2 grading failure |  | Contr | BFK |  |  | 2015-03-21 | 2015-02-20 13:55 | -29 | 2015-02-19 17:57 | Geotechnical Engineering - Compensation Grouting | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | has placed 6F2 material for the backfill of groutshaft TCR2. In accordance with the ITP, has tested the grading of the material, and it has proven non-compliant, containing too many large particles (93% passing for the sieve size 125mm instead of 100% and 38% passing for the 37.5mm sieve size instead of 45%). See attached grading anlysis.
| 01CV - Civils | Cxxx-NCR-002009 | NCR | AP3W - Cast Invert out of tolerance |  | Contr | BFK |  |  | 2015-03-13 | 2015-02-24 15:53 | -17 | 2015-02-20 11:22 | Tunnelling - Tunnelling General | 15500 |  | Workmanship | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | AP3W ch 8-31 cast invert U1 finish (0-20mm tolerance) is out of specifications due to an inappropriate leveled. This NCR it is not complaint with the ITP Cxxx--C4-ITP-CRT00_ST005-50144 - BOS TCR CP Cast-in situ and Sprayed Secondary Lining section B4.10 and the general note G36 from the drawing Cxxx-MMD-C4-DDJ-N105-00001 reference below. See attached the profiles.
| 01CV - Civils | Cxxx-NCR-002010 | NCR | In November 2014 BOS were 2 sets of sample short in terms of testing for the FireProof Lining. |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-03-10 | 2015-02-27 15:30 | -11 | 2015-02-24 11:14 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | In November 2014 with a total of 260m of Mix 21 being delivered to site, only 3 sets of test was performed, which represents 150m of Mix 21. ITP stipulates that a test needs to be carriede out every 50m.
| 01CV - Civils | Cxxx-NCR-002011 | NCR | PTW- Cast Invert out of tolerance |  | Contr | BFK |  |  | 2015-03-16 | 2015-03-10 10:11 | -6 | 2015-03-02 10:45 | Tunnelling - Tunnelling General | 25000 |  | Workmanship | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | PTW ch -38 TO 230 cast invert U1 finish (0-20mm tolerance) is out of specifications due to an inappropriate leveled. This NCR it is not complaint with the ITP Cxxx--C4-ITP-CRT00_ST005-50144 - BOS TCR CP Cast-in situ and Sprayed Secondary Lining section B4.10 and the general note G36 from the drawing Cxxx-MMD-C4-DDJ-N105-00001 reference below. See attached the profiles.
| 01CV - Civils | Cxxx-NCR-002012 | NCR | Backfall in rocker pipe at Sheraton Street sewer |  | Crossrail | PDP |  |  | 2015-03-30 | 2015-03-26 13:55 | -4 | 2015-02-20 14:08 | Civil - Sewage/Water services | 15500 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On removal of the 150mm flume pipe from the existing 300DN rocker pipe stub at Manhole ref - MH1 (Westbound Heading Connection) at Sheraton Street sewer, a backfall of approximately 40mm was identified over the length of the 600mm rocker pipe. This is likely to result in a minimum ponding and ultimately result in a minimum sediment build up sewer. It is also likely that it will affect any potential air test as the joint to the defective pipe is likely to be compromised. Taking into account that the issue described above is only encountered in the 600mm rocker pipe and the reduction in the hydraulic capacity with the backfall of 40mm would be minimum, suggest to Re-invert the pipe with a polyurethane line. It is noted that the defective works were constructed by during the establishment of the grout shafts and was not identified previously.
| 01CV - Civils | Cxxx-NCR-002013 | NCR | Backfall in the rocker pipe installed in TCR1 sewer |  | Contr | BFK |  |  | 2015-04-10 | 2015-03-20 16:05 | -21 | 2015-02-20 18:39 | Geotechnical Engineering - Compensation Grouting | 10500 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the reinstatement of the sewer at Sheraton Street it was found that there was a backfall in the rocker pipe installed in the Manhole 1 (downstream). Please find attached a copy of the survey sketch for your review : (For the purposes of the survey – all levels are arbitrary levels assigned at Cover Level of Manhole TQ29815203 (In Great Chapel Street) where the Bench Mark was set at +100.000. The subsequent level survey and values recorded are referenced from this hypothetical datum. Levels taken within the downstream sewer (MH1) are approximate, this particular part of the sewer would benefit from a serious jetting to free up the abundance of ragging and allow for a more decisive survey to be undertaken)
| 01CV - Civils | Cxxx-NCR-002014 | NCR | Concurrent grouting works in BOS along AP3A tunnel, there are few passes missing with field grout test records. |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-04-09 | 2015-04-24 07:05 | 15 | 2015-02-23 17:43 | Geotechnical Engineering - Compensation Grouting | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | As part of concurrent grouting works in BOS along AP3A tunnel, out of 1 to 65 grout passes carried out there are few passes as mentioned below are missing with field grout test records. This results in failing to show grout characteristics in line with the specification for the passes below. AP3A Pilot pass 16 to 17: Total Volume injected – 903 litres on 8/2/2013 - No field grout testing record AP3A Pilot pass 28 to 29: Total Volume injected – 710 litres on 13/2/2013 - No field grout testing record AP3A Pilot pass 30 to 31: Total Volume injected - 1404 litres on 14/2/2013 - No field grout testing record AP3A Enlargement 52 to 54: Total Volume injected - 1499 litres on 4/3/2013 - No field grout testing record
| 01CV - Civils | Cxxx-NCR-002015 | NCR | Calibration of spraying equipment |  | Crossrail | XRL |  |  | 2015-04-17 | 2015-03-30 17:21 | -18 | 2015-02-23 08:06 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | No evidence of accelerator dosing calibration for two __s (07/02/15-18/02/2015, 4 days overdue) and Logica (05/02/2015-18/02/2015, 6 days overdue). Documented in S&QS report sent to Shift Manager from CRL Field Engineer since 12/02/2015. These durations exceed that stated in SCL Excavation and Primary Lining ITP (Cxxx--C4-ITP-CRT00_ST005-50050) Inspection Number B4.1 for weekly accelerator pump calibration.
| 01CV - Civils | Cxxx-NCR-002016 | NCR | S4- Profiles discrepancies |  | Contr | BFK |  |  | 2015-03-09 | 2015-03-02 11:49 | -7 | 2015-02-23 08:31 | Tunnelling - Linings - Sprayed Concrete | 25500 |  | Design | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following fireproofing layer as built survey of the S4 tunnel it became apparent that the final layer is encroaching the design line in some areas. This out of tolerance is as a result of change to the tunnel axis level recorded on the NCR 1353 and 1648
| 01CV - Civils | Cxxx-NCR-002017 | NCR | Formation of radial joints in AP8 |  | Crossrail | XRL |  |  | 2015-04-17 | 2015-03-30 17:24 | -18 | 2015-02-23 08:26 | Tunnelling - Linings - In-situ Concrete | 10500 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Horizontal joint formed by haunch pour between CP2 and LP9, radial joint required between cast and sprayed secondary lining. Radial joint formed by haunch pour between AP7b and headwall, poor quality concrete (due to forming by hand in green concrete) requires removal retaining radial joint between cast and sprayed secondary lining. Issue identified by CRL / Cxxx on 19/02/2015 and minuted in daily secondary lining meeting. proceeded with spraying in FF steel with secondary lining 21/02/2015 without carrying out remedial works to joints. Potential for damaging waterproofing requiring installation of TAM injection tubes.
| 01CV - Civils | Cxxx-NCR-002018 | NCR | Concurrent grouting works in BOS along CH3 Enlargement tunnel, there are a few passes missing with field grout test records. |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-04-09 | 2015-04-24 07:09 | 15 | 2015-02-23 17:44 | Geotechnical Engineering - Compensation Grouting | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | As part of concurrent grouting works in BOS along CH3 Enlargement tunnel, out of 1 to 99 grout passes carried out there are few passes as mentioned below are missing with field grout test records. This results in failing to show grout characteristics in line with specification for the passes below. CH3 Enlg pass 17 to 20: Total Volume injected – 1191 litres on 16/6/2013 - No field grout testing record. CH3 Enlg pass 25 to 28 repeat: Total Volume injected – 480 litres on 27/6/2013 - No field grout testing record CH3 Enlg pass 45 to 48 rev 2: Total Volume injected - 2059 litres on 29/6/2013 - No field grout testing record
| 01CV - Civils | Cxxx-NCR-002019 | NCR | Concurrent grouting works in BOS along CP5 tunnel, one pass is missing with field grout test records. |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-04-09 | 2015-04-24 07:12 | 15 | 2015-02-23 17:45 | Geotechnical Engineering - Compensation Grouting | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | As part of concurrent grouting works in BOS along CP5 tunnel, out of 1 to 42 grout passes carried out the pass as mentioned below is missing with field grout test records. This results in failing to show grout characteristics in line with specification for the passes below. CP5 pass 29 to 31 rev 2: Total Volume injected – 2453 litres on 27/4/2014 - No field grout testing record.
| 01CV - Civils | Cxxx-NCR-002020 | NCR | Concurrent grouting works in BOS along LCE1 Enlargement tunnel, there are few passes missing with field grout test records |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-04-09 | 2015-04-15 22:05 | 6 | 2015-02-23 17:46 | Geotechnical Engineering - Compensation Grouting | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | As part of concurrent grouting works in BOS along LCE1 Enlargement tunnel, out of 1 to 77 grout passes carried out there are few passes as mentioned below are missing with field grout test records. This results in failing to show grout characteristics in line with specification for the passes below. LCE1 Enlg pass 10 to 13: Total Volume injected – 650 litres on 23/3/2013 - No field grout testing record. LCE1 Enlg pass 14 to 17 rev2: Total Volume injected – 1076 litres on 25/3/2013 - No field grout testing record LCE1 Enlg pass 46 to 49 rear only repeat: Total Volume injected – 1099 litres on 28/4/2013 - No field grout testing record
| 01CV - Civils | Cxxx-NCR-002021 | NCR | Concurrent grouting works in BOS along LCE1 Pilot tunnel, there are few passes missing with field grout test records. |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-04-09 | 2015-04-15 21:51 | 6 | 2015-02-23 17:48 | Geotechnical Engineering - Compensation Grouting | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | As part of concurrent grouting works in BOS along LCE1 Pilot tunnel, out of 1 to 40 grout passes carried out there are few passes as mentioned below are missing with field grout test records. This results in failing to show grout characteristics in line with specification for the passes below. LCE1 Pilot pass 7 to 8: Total Volume injected – 389 litres on 16/2/2013 - No field grout testing record. LCE1 Pilot pass 23 to 24: Total Volume injected – 1079 litres on 23/2/2013 - No field grout testing record
| 01CV - Civils | Cxxx-NCR-002022 | NCR | Concurrent grouting works in BOS along PTE tunnel, one pass is missing with field grout test records |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-04-09 | 2015-04-15 21:53 | 6 | 2015-02-23 17:51 | Geotechnical Engineering - Compensation Grouting | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | As part of concurrent grouting works in BOS along PTE tunnel, out of 1 to 184 grout passes carried out the pass as mentioned below is missing with field grout test records. This results in failing to show grout characteristics in line with specification for the passes below. PTE pass 95A to 97A: Total Volume injected – 2528 litres on 21/5/2014 - No field grout testing record.
| 01CV - Civils | Cxxx-NCR-002023 | NCR | Concurrent grouting works in BOS along PTW tunnel section, there are few passes missing with field grout test records. |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-05-01 | 2015-05-01 16:19 | 0 | 2015-02-23 17:52 | Geotechnical Engineering - Compensation Grouting | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | As part of concurrent grouting works in BOS along PTW tunnel section, out of 1 to 401 grout passes carried out there are few passes as mentioned below are missing with field grout test records. This results in failing to show grout characteristics in line with specification for the passes below. PTW pass 1 to 3 rev3: Total Volume injected – 1918 litres on 10/11/2013 - No field grout testing record. PTW pass 244A to 246A option 2 rev2: Total Volume injected – 4061 litres on 14/2/2014 - No field grout testing record PTW pass 352A to 354A option 2: Total Volume injected – 3220 litres on 05/3/2014 - No field grout testing record PTW pass 373A to 375A option 2: Total Volume injected – 4161 litres on 23/3/2014 - No field grout testing record PTW pass 385A to 387A option 2 rev4: Total Volume injected – 3801litres on 26/3/2014 - No field grout testing record PTW pass 391A to 393A option 2 rev4: Total Volume injected – 3814 litres on 28/3/2014 - No field grout testing record
| 01CV - Civils | Cxxx-NCR-002024 | NCR | BOS De-Bonded Fireproofing PTW CH140m |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-03-13 | 2015-03-06 17:15 | -7 | 2015-02-23 17:30 | Tunnelling - Linings - Sprayed Concrete | 4500 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Systematic hammer testing of PTW fireproofing CH133 - 158 detected one area of de-bonded fireproofing. Hammer testing was carried out on 22/02/2015 see attached hammer test sheet. Area is 1m x 1m in size, positioned at CH 140m (LHS-8 O'clock).
| 01CV - Civils | Cxxx-NCR-002025 | NCR | BOS PTW 5A - Outstanding masterseal repairs |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2015-03-24 | 2015-03-02 10:21 | -22 | 2015-02-24 09:46 | Tunnelling - Linings - In-situ Concrete | 8500 |  | Supervision/Management | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | During requested inspection for the signoff of 5A invert Ch. 127 to Ch.156 for the invert pour outstanding masterseal repairs were required and several areas were still to reach Shore A 50 and required further curing. All repairs were made and the area properly cured and signed off on DS 19/02/15.
| 01CV - Civils | Cxxx-NCR-002026 | NCR | BOS PTE 5A - Damage to masterseal by invert slab |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2015-03-19 | 2015-03-06 17:17 | -13 | 2015-02-24 10:04 | Tunnelling - Linings - Sprayed Concrete | 9500 |  | Damaged | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following the stripping of the shutters used to cast the invert slab in 5A up to CH. 126 several patches of masterseal were damaged on the RHS west facing. One of these patches (aprox. 300 x 300mm ) between Ch.110-115 was located about 50mm from the edge of the cast invert slab. Due to the damaged area's proximity to the invert slab the minimum overlap (200mm) could not be achieved.
| 01CV - Civils | Cxxx-NCR-002027 | NCR | TaM’s fail to achieve required design depth & 4no. TaM’s abandoned. (Permeation Grouting) |  | Contr | BFK |  |  | 2015-04-10 | 2015-04-15 22:00 | 5 | 2015-02-24 14:01 | Geotechnical Engineering - Compensation Grouting | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | As per the attached as-built records of TCR1 Drilling & TaM installation (Permeation grouting works), there are several TaM’s fail to achieve required design depth & 4no. TaM’s abandoned.
| 01CV - Civils | Cxxx-NCR-002028 | NCR | BOS PTE Fallout Chainage 90 to 93 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-03-13 | 2015-03-09 10:39 | -4 | 2015-02-26 20:11 | Tunnelling - Linings - Sprayed Concrete | 5500 |  | Material | Repair | 3 (3-6k) | Complete | Material/Preservation Problems - Other | Completed |  | During spraying of the far face secondary lining a fall out occured in BOS PTE between chainage 90 and 93. The position of the fall out was 12 o'clock, 3m x 3.5m x 200mm. The area was then blown with air to remove all loose material and washed down prior to re application. A small area of masterseal was exposed after the fall out, there was no visible damage to the area exposed. The attached photograph shows that the initial layer is still visible in most part. The panel which was sprayed from this bay of secondary lining did not reach the J2 curve for the 1 hour and 4 hour tests. A test on the lining was carred out at 24 hours which passed. Hammer testing has been under taken around the permiter of the fall out to ensure that no hollow areas are present. As a precaution for future fixings in this area B283 mesh is to be installed as per sketch attached from the 10 o'clock to 2 o'clock postion and 600mm outside the fall out area. Please find attached checksheet for mesh installation.
| 01CV - Civils | Cxxx-NCR-002029 | NCR | TCR - Hollow spot at VWW fireproofing |  | Contr | BFK |  |  | 2015-03-10 | 2015-02-26 16:04 | -12 | 2015-02-24 17:36 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Hammer testing below the axis level of VWW over fireproofing layer showed one hollow spots. The location of the spot is marked on the attached hammer testing sheet.
| 01CV - Civils | Cxxx-NCR-002030 | NCR | Missing Bars in AP8 to LP9 RHS column - Cast In-Situ Secondary Lining |  | Contr | BFK |  |  | 2015-03-12 | 2015-03-04 17:53 | -8 | 2015-02-26 15:46 | Tunnelling - Linings - In-situ Concrete | 9500 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The cast in situ concrete column to the RHS of LP9 has been poured to level 105.125, the 3 no. bar mark 86 bars (NF) shown in drawing Cxxx-MMD-C4-DDD-N105_5-00496 were not installed prior to pouring this element of the works.
| 01CV - Civils | Cxxx-NCR-002032 | NCR | PTW CH70 - Ch180 - Final as-built profile out of tolerance (specific area) |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-03-13 | 2015-03-09 12:37 | -4 | 2015-03-02 20:13 | Tunnelling - Linings - Sprayed Concrete | 35500 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Having reviewed the final as-built profile for PTW CH70 - CH180; some tight areas were identified as below: 1) CH82 between 1 and 2 o'clock position. (minimum FP thickness before rework 140mm. 20mm to be removed). 2) CH82 at 8 o'clock position. (minimum FP thickness before rework 150mm. 20mm to be removed). 3) CH82.5 between 4 and 5 o'clock position. (minimum FP thickness before rework 140mm. 20mm to be removed). 4) CH92 between 2 and 3 o'clock position. (minimum FP thickness before rework 190mm. 20mm to be removed). 5) CH92.5 at 5 o'clock position. (minimum FP thickness before rework 130mm. 10mm to be removed). 6) CH92.5 at 8 o'clock position. (minimum FP thickness before rework 140mm. 10mm to be removed). 7) CH94 at 8 o'clock position. (minimum FP thickness before rework 120mm. 10mm to be removed). 8) CH102 at 5 o'clock position. (minimum FP thickness before rework 160mm. 10mm to be removed). 9) CH102.5 at 5 o'clock position. (minimum FP thickness before rework 180mm. 20mm to be removed). 10) CH103 at 5 o'clock position. (minimum FP thickness before rework 170mm. 10mm to be removed). 11) CH119 at 8 o'clock position. (minimum FP thickness before rework 130mm. 10mm to be removed). 12) CH142.5 at 1 o'clock position. (minimum FP thickness before rework 180mm. 10mm to be removed). 13) CH143.5 to CH144 at 1 o'clock position. (minimum FP thickness before rework 170mm. 40mm to be removed). 14) CH160.5 at 9 o'clock position. (minimum FP thickness before rework 140mm. 10mm to be removed). As per PMC 10179, areas between 0-50mm tight are to remain as-is . Areas which are greater than 50mm tight (listed above) are to be trimmed back.
| 01CV - Civils | Cxxx-NCR-002033 | NCR | BOS AP2A - Masterseal overlap |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-04-27 | 2015-04-09 19:49 | -18 | 2015-03-30 11:35 | Tunnelling - Linings - Sprayed Concrete | 15500 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In order to spray the secondary lining to the junction of AP2A/PTE a sweep was installed with the bolts drilled through the masterseal lining of AP2A. 2 No. of these bolts were located in close proximity to the invert slab and as such the minimum overlap for the masterseal repair cannot be achieved.
| 01CV - Civils | Cxxx-NCR-002034 | NCR | BOS PTW 4B - Oil spill Ch. 235 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-03-15 | 2015-03-03 17:15 | -12 | 2015-03-03 11:28 | Tunnelling - Linings - In-situ Concrete | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | An oil spill to the invert slab in 4B of PTW occured at Ch. 235.
| 01CV - Civils | Cxxx-NCR-002035 | NCR | BOS PTE 5A - Masterseal Damage Ch.117 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-04-17 | 2015-04-01 15:43 | -16 | 2015-03-30 10:18 | Tunnelling - Linings - Sprayed Concrete | 15500 |  | Damaged | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A small localised area of masterseal has been damaged in PTE @CH 117. The damaged masterseal is located LHS (west facing) close to the invert slab and the leading edge. Due to the close proximity to the leading edge the minimum overlap for patch repair to the masterseal cannot be achieved.
| 01CV - Civils | Cxxx-NCR-002036 | NCR | BOS PTE : Damage to Masterseal Outside CP5 Secondary Lining |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-03-14 | 2015-03-04 13:45 | -10 | 2015-02-28 18:32 | Tunnelling - Linings - Sprayed Concrete | 10500 |  | Damaged | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | At the junction PTE/CP5, the Masterseal appears to have been damaged close the invert slab / sprayed secondary lining of CP5, such that the minimum overlap in KW20.3301 cannot be met. Patch repairs have been carried out on both the left and right hand sides, close to the joint between the cast invert and sprayed secondary lining of CP5.
| 01CV - Civils | Cxxx-NCR-002038 | NCR | PTE CH90.5-91 - Final as-built profile out of tolerance |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-03-12 | 2015-03-11 10:41 | -1 | 2015-03-10 11:57 | Tunnelling - Linings - Sprayed Concrete | 18500 |  | Incorrect Installation | Use As-Is | 2 (6-60k) | Complete | Material/Preservation Problems - Other | Completed |  | During spraying of the far face secondary lining a fall out occured in BOS PTE between chainage 90 and 93. The position of the fall out was 12 o'clock, 3m x 3.5m x 200mm. As a precaution for future fixings Cxxx suggested that in this area B283 mesh was installed as per sketch attached from the 10 o'clock to 2 o'clock position and 600mm outside the fall out area. Prior to the installation of this steel the area was not milled due to the fall out. The steel was then installed. The installation of this steel and subsequent spray did not leave room for 50mm of fire proofing without encroaching the design line. Thus this area is showing as -50mm on the scans. Please find attached scans of the area.
| 01CV - Civils | Cxxx-NCR-002039 | NCR | PTW CH180 - Ch240 - Final as-built profile out of tolerance (specific area) |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-03-12 | 2015-03-11 10:35 | -1 | 2015-03-10 15:55 | Tunnelling - Linings - Sprayed Concrete | 10500 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | have reviewed the as built profiles for PTW CH180 - CH240. As per PMC 10179, areas between 0-50mm tight are to remain as is. Areas which are greater than 50mm tight are to be trimmed back, see attached scans showing areas which were greater than 50mm tight. Also attached permit to mill from chainage 175-221 and 215 to 240.
| 01CV - Civils | Cxxx-NCR-002040 | NCR | CP5 CH7.5 - Ch35 - Final as-built profile out of tolerance (specific area) |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-03-13 | 2015-03-04 13:50 | -9 | 2015-03-02 20:34 | Tunnelling - Linings - Sprayed Concrete | 25500 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Having reviewed the final as-built profile for CP5 CH7 - CH35; some tight areas were identified with worse case being 27mm tight. In line with PMC 10179, propose to use as-is as none of the areas covered under this NCR are more than 50mm tight.
| 01CV - Civils | Cxxx-NCR-002041 | NCR | PTE- Final As Built Profiles 0-218 |  | Contr | BFK |  |  | 2015-05-26 | 2015-05-26 14:45 | 0 | 2015-03-02 12:51 | Tunnelling - Linings - Sprayed Concrete | 25000 |  | Workmanship | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Fire proofing as-built profile out of designed tolerance for PTE- chainages 0-218
| 01CV - Civils | Cxxx-NCR-002042 | NCR | Damage to Master Seal Ch117 PTE Invert LHS Secondary Lining |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-04-01 | 2015-03-04 13:51 | -28 | 2015-03-02 14:45 | Tunnelling - Linings - Sprayed Concrete | 10500 |  | Damaged | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Damage to Master Seal at Ch117 PTE Invert. On the left hand side(Secondary Lining)
| 01CV - Civils | Cxxx-NCR-002043 | NCR | Lack of Masterseal lap PTE ch123-135 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-03-17 | 2015-03-04 17:54 | -13 | 2015-03-03 15:02 | Tunnelling - Linings - Sprayed Concrete | 25500 |  | Damaged | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In PTW between chainage 123 and 138 there was extensive damage of the masterseal, close to the invert slab. This means it was not possible to achieve sufficient overlap. Damage to the masterseal was observed to be on both sides of the cast slab.
| 01CV - Civils | Cxxx-NCR-002044 | NCR | Lack of Masterseal lap PTE ch 185 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-03-17 | 2015-03-04 17:55 | -13 | 2015-03-03 16:26 | Tunnelling - Linings - Sprayed Concrete | 8500 |  | Damaged | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Masterseal was damaged at the end of the invert slab in PTE approximately chainage 185.
| 01CV - Civils | Cxxx-NCR-002045 | NCR | BOS PTW CH197-231 Hollow areas in secondary lining |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-03-13 | 2015-03-06 16:37 | -7 | 2015-03-04 08:31 | Tunnelling - Linings - Sprayed Concrete | 10500 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Systematic hammer testing of PTW secondary lining detected de-bonded areas between SFR and SFR layers. This occurred between the near face and far face steel. This area of PTW is heavily reinforced with NF and FF mesh. 5 hollow areas were identified. These areas were milled/broken out until no hollow areas could be identified around their perimeter/internally and then re sprayed with SFR concrete. Prior to the application of fireproofing the patches were then re hammer tested to ensure a sound bond. Please see attached hammer test records and spray checksheets.
| 01CV - Civils | Cxxx-NCR-002046 | NCR | In December 2014 Multiple batches of Hanson Shotcrete was underdosed with Microsillica. |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-03-18 | 2015-03-06 16:36 | -12 | 2015-03-04 11:34 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | In December 2014 multiple batches of shotcrete from was underdosed with Microsillica. ITP has a tolerance with reference to microsillica of 3% plus or minus.
| 01CV - Civils | Cxxx-NCR-002047 | NCR | AP1: Reinforcement Installation |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-03-18 | 2015-03-09 11:13 | -9 | 2015-03-04 16:24 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the installation of the reinforcement to the AP1 thickened section it was discovered that some reinforcement was missing from the original order. On discovery of this substitute reinforcement was located and "made to suit" the requirements of the tunnel. This was agreed between ,Cxxx and CRl. Once the reinforcement was complete all existing and new reinforcement was checked and signed off by all parties. Prior to handover this change will be documented in the red-line drawings.
| 01CV - Civils | Cxxx-NCR-002048 | NCR | BOS_CH2-pilot tunnel_lining thickness |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-03-18 | 2015-03-23 10:31 | 5 | 2015-03-04 16:49 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The lining thickness of CH2 Pilot consists of 75mm initial lining with 225mm of primary lining giving a combined thickness of 300mm for the tunnel. However with the recent excavation of the permanent tunnel AP1 (where we had 250mm PL) it was naturally assumed the CH2 pilot with a smaller radius would follow suit and also have a combined thickness of 250mm. As a result the initial 12 advances were sprayed to a thickness of +250mm instead of the design 300mm
| 01CV - Civils | Cxxx-NCR-002049 | NCR | Monthly Washout performed Incorrectly - February |  | Contr | BFK |  |  | 2015-03-18 | 2015-03-06 17:19 | -12 | 2015-03-04 16:50 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The monthly washout test in February was only performed using 3 samples instead of 6.
| 01CV - Civils | Cxxx-NCR-002050 | NCR | BOS De-Bonded Fireproofing PTW CH203, 205 and 207m |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-03-10 | 2015-03-09 12:59 | -1 | 2015-03-04 19:33 | Tunnelling - Linings - Sprayed Concrete | 15900 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Systematic hammer testing of PTW fireproofing CH182-206 (02/03/2015) and 208-220 (03/03/2015) detected one area of de-bonded fireproofing. See attached hammer test sheets. Area 1: Ch 203, 4 o'clock, 0.35m x 0.35m Area 2: Ch 205, 5 o'clock, 0.5 x 0.5m Area 3: Ch 207, 5 o'clock 0.5 x 1m The three areas are below axis level on the northern side of the platform. During break out patches 1 and 2 merged into one patch 2m x 2m. Please find attached final hammer test records showing sound bond.
| 01CV - Civils | Cxxx-NCR-002051 | NCR | BOS Localised Fireproofing Under thickness - PTW CH 98 to 204 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-03-12 | 2015-03-10 16:15 | -2 | 2015-03-04 20:42 | Tunnelling - Linings - Sprayed Concrete | 35500 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After spraying the fireproofing layer in PTW between chainage 98-204, the profiles have been assessed by (EK, PPL), Cxxx (RW) and CRL (PA) on the 04/03/15. It was concluded that there are 2 areas of concern with under thickness of the fireproofing layer. See attachment "BOS PTW Ch 100 - 200 Fire proofing under thickness - Agreed remedial works" for tunnel bends highlighting the 2 areas of concern and also the relevant profiles. Area 1 - Saw cut around perimeter between CH 111.5 and 112.5 and axis to axis - Mill out to a minimum of 60 green - Create an elephants foot at axis i.e. at axis mill to 100 green and then 1m up feather to 60 green. - Re scan - Re spray ensuring a minimum 50mm layer is applied Area 2 - Take a core in the location showing 30mm thickness – CH 182 - Core to be witnessed by Cxxx or CRL. Log core stating the thickness for fireproofing. Refer to report referenced - Investigation into bonding of subsequent layers of smoothing layer mix 21 at Crossrail Bond Street.
| 01CV - Civils | Cxxx-NCR-002052 | NCR | calibration certification has expired for steel rules at testing areas |  | Contr | BFK |  |  | 2015-05-06 | 2015-05-07 15:15 | 1 | 2015-03-05 11:41 | Civil - Tunnelling | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | During surveillance of testing equipment at TCR it was noted that steel rules used for concrete testing are out of calibration (certification has expired).
| 01CV - Civils | Cxxx-NCR-002053 | NCR | 1 day cores tested late |  | Contr | BFK |  |  | 2015-05-05 | 2015-04-16 00:32 | -19 | 2015-04-14 15:31 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The following sets of cores were tested outside of 3 days during January: Sample 796, PTE, Fireproofing, Ch.130, tested at 4 days Sample 801, CH1, FIreproofing, tested at 4 days Sample 802, PTW, Secondary, CH. -4 to -7, tested at 4 days Sample 806, VEW, Secondary, CH. 0.2 to 2.2, tested at 9 days Sample 807, VEW, Secondary, CH. 20 to 26, tested at 7 days
| 01CV - Civils | Cxxx-NCR-002054 | NCR | BOS PTE CP5 - Hollows identified in Secondary lining |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-03-12 | 2015-03-09 12:52 | -3 | 2015-03-06 08:01 | Tunnelling - Linings - Sprayed Concrete | 10500 |  | Design | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Joint (CRL/) hammer testing to the secondary lining on 04/03/2015 identified 3 no. possible hollows to the CP5 eye with PTE. These areas were marked up. 1 no. area was a lamination from overspray and was cleaned. 2 no. areas were cut back and the hollows removed. On 05/03/2015 these areas were jointly re-inspected and found to be solid. These areas are approx. 1m2 and are to be filled in using mix 21. Find attached hammer testing checksheets and permit to fireproof.
| 01CV - Civils | Cxxx-NCR-002055 | NCR | Lack of lap lenght of Masterseal at AP3E CH 7 |  | Contr | BFK |  |  | 2015-03-31 | 2015-03-13 09:39 | -18 | 2015-03-05 18:24 | Tunnelling - Linings - Sprayed Concrete | 15500 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During inspection of waterproofing, it became apparent the waterproofing in AP3E at ch 7 invert been damaged close to the previously cast invert and minimum lap length of waterproofing cannot be achieved.
| 01CV - Civils | Cxxx-NCR-002056 | NCR | S3 - Overspray fireproofing layer |  | Contr | BFK |  |  | 2015-03-19 | 2015-03-10 15:17 | -9 | 2015-03-05 18:21 | Tunnelling - Tunnelling General | 25000 |  | Workmanship | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Having reviewed the final as-built profile for S3 ch 0-7; some tight areas were identified as shown in the profiles attached.
| 01CV - Civils | Cxxx-NCR-002057 | NCR | BOS PTW Steel reinforcement damage |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2015-03-13 | 2015-03-09 12:40 | -4 | 2015-03-06 05:04 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | During milling of a hollow patch on the secondary lining in PTW (approx chainage 210), steel reinforcement was exposed and damaged.
| 01CV - Civils | Cxxx-NCR-002058 | NCR | BOS PTE Slab Level - Out of Tolerance Chainage 98 to 179 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-03-13 | 2015-03-10 16:03 | -3 | 2015-03-07 19:27 | Tunnelling - Linings - Sprayed Concrete | 15500 |  | Incorrect Installation | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | invert level survey in PTE between chainages 97m & 179m indicate multiple locations that are out of tolerance. The design level of PTE slab is 95.047mAod. The minimum permissible level is 95.027mAod. As the level survey attached shows, multiple locations along the slab are lower and higher than the permissible level of 95.027mAod and 95.047mAod. The worst effected area is chainage 107m with a reduced level of 95.057mAod (10mm out of tolerance) and chainage 169/170 with a reduced level of 95.008mAod (19mm out of tolerance).
| 01CV - Civils | Cxxx-NCR-002059 | NCR | BOS PTW Slab Level - Out of Tolerance Chainage 218 to 264 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-03-13 | 2015-03-10 15:39 | -3 | 2015-03-08 19:20 | Tunnelling - Linings - Sprayed Concrete | 15500 |  | Incorrect Installation | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | invert level survey in PTW between chainages 218m & 264m indicates locations that are out of tolerance. The design level of PTE slab is 95.047mAod. The minimum permissible level is 95.027mAod. As the level survey attached shows, locations along the slab are higher than the permissible level of 95.047mAod. The worst effected area is chainage 239m with a reduced level of 95.065mAod (18mm out of tolerance).
| 01CV - Civils | Cxxx-NCR-002060 | NCR | BOS PTW 4A 4B - Oil Spill to invert slab |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-03-13 | 2015-03-10 09:50 | -3 | 2015-03-09 10:59 | Tunnelling - Linings - In-situ Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | 3 no. small oil spills were identified to the invert slab in the 4a-4b section of the PTW tunnel. They are located at Ch.170 next to a lighting tower, at Ch.175 under a potenza and at Ch.220.
| 01CV - Civils | Cxxx-NCR-002061 | NCR | BOS PTW 1d - Contraction Joint to FP lining CJ.0308 not re cut through patch |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-03-12 | 2015-03-10 11:33 | -2 | 2015-03-07 16:38 | Tunnelling - Linings - Sprayed Concrete | 8500 |  | Incomplete Works | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Patch repair to the fireproofing in 1d of PTW was carried out in area where CJ.0308 passes through the lining. As such the contraction joint has not been fully cut as detailed on drawing Cxxx-MMD-C4-DDA-Cxxx_6-00100, before the lining reached a strength of 20MPa. No cracks have been observed in the lining.
| 01CV - Civils | Cxxx-NCR-002062 | NCR | Advances 15 to 17 were not sprayed to the correct thickness according to design in CH2 Pilot tunnel |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-03-13 | 2015-03-12 08:45 | -1 | 2015-03-07 07:23 | Tunnelling - Linings - Sprayed Concrete | 9500 |  | Workmanship | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Advances 15 to 17 (Ch14.08 To 17.08) were not sprayed to the correct thickness according to design in CH2 Pilot tunnel.
| 01CV - Civils | Cxxx-NCR-002063 | NCR | BOS PTW Secondary Lining under thickness ch 251 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-03-12 | 2015-03-10 11:40 | -2 | 2015-03-07 13:12 | Tunnelling - Linings - Sprayed Concrete | 10500 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A hollow area was found in the secondary lining at chainage 251 in PTW. This was removed, this resulted in the secondary lining thickness being less than required, see attached scan.
| 01CV - Civils | Cxxx-NCR-002064 | NCR | BOS PTE 50-110 Generic NCR - Fire proofing as-built profile out of tolerance |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-03-12 | 2015-03-10 15:24 | -2 | 2015-03-09 22:03 | Tunnelling - Linings - Sprayed Concrete | 55500 |  | Incorrect Installation | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Fire proofing as-built profile out of design tolerance PTE 50-110, excluding chainage 90.5-91 which is covered by Cxxx-NCR-002038.
| 01CV - Civils | Cxxx-NCR-002065 | NCR | BOS PTW 70-264 Generic NCR - Fire proofing as-built profile out of tolerance |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-03-12 | 2015-03-10 17:20 | -2 | 2015-03-10 15:33 | Tunnelling - Linings - Sprayed Concrete | 25500 |  | Incorrect Installation | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Fire proofing as-built profile out of design tolerance PTW 70-264.
| 01CV - Civils | Cxxx-NCR-002066 | NCR | BOS PTE 5A - Masterseal damage overlap unachievable |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-04-17 | 2015-04-24 07:40 | 7 | 2015-03-30 10:30 | Tunnelling - Linings - Sprayed Concrete | 10500 |  | Damaged | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Several areas of masterseal in PTE section 5A have been damaged and minimum masterseal overlap cannot be achieved during the repair works. These areas are: 1) LHS CH117 - small tear to the leading edge 2) LHS CH125 - patch (~100 x 100mm ) adjacent to the invert slab 3) LHS CH137 - patch (~ 300 x 700mm ) adjacent to the invert slab 4) RHS CH121 - patch (~ 150 x 150mm ) adjacent to the invert slab 5) RHS CH134 - patch (~ 500 x 200 mm ) adjacent to the invert slab 6) RHS CH135 -CH140 - patch (~5000 x 250mm) adjacent to the invert slab
| 01CV - Civils | Cxxx-NCR-002068 | NCR | CH2 advance 9, only 5 one day core results attained plus CH2 davance 30, the 1 hour Early Age Strength Test was below ITP requirements. |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-03-27 | 2015-03-12 10:15 | -15 | 2015-03-10 17:37 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | CH2 ADV 9, lab issued only results of 5 one day copessive results rather than ITP stipulation of 6 cores, plus advance 30 was below ITP requirements @ 1 hour with reference to Early Age Strength Testing.
| 01CV - Civils | Cxxx-NCR-002069 | NCR | AP7B- Cast Invert out of tolerance |  | Contr | BFK |  |  | 2015-03-25 | 2015-03-20 12:24 | -5 | 2015-03-11 11:03 | Tunnelling - Tunnelling General | 23500 |  | Workmanship | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | AP7B ch 0- 32 cast invert U1 finish (0-20mm tolerance) is out of specifications due to an inappropriate leveled. This NCR it is not complaint with the ITP Cxxx--C4-ITP-CRT00_ST005-50144 - BOS TCR CP Cast-in situ and Sprayed Secondary Lining section B4.10 and the general note G36 from the drawing Cxxx-MMD-C4-DDJ-N105-00001 reference below. See attached the profiles. Cast invert is lower than construction tolerance allows but the design secondary lining thickness is achieved.
| 01CV - Civils | Cxxx-NCR-002070 | NCR | AP4W- Cast Invert out of tolerance |  | Contr | BFK |  |  | 2015-03-25 | 2015-03-11 15:58 | -14 | 2015-03-11 12:13 | Tunnelling - Tunnelling General | 35500 |  | Workmanship | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | AP4W cast invert U1 finish (0-20mm tolerance) is out of specifications due to an inappropriate leveled. This NCR it is not complaint with the ITP Cxxx--C4-ITP-CRT00_ST005-50144 - BOS TCR CP Cast-in situ and Sprayed Secondary Lining section B4.10 and the general note G36 from the drawing Cxxx-MMD-C4-DDJ-N105-00001 reference below. See attached the profiles. The results indicate some of the inverts are 10-20 mm lower than construction tolerance allows but the design secondary lining thickness is achieved.
| 01CV - Civils | Cxxx-NCR-002071 | NCR | SMM - Amber trigger breach on 16 South Molton Lane __ |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-03-25 | 2015-03-12 10:08 | -13 | 2015-03-11 17:24 | Geotechnical Engineering - Compensation Grouting | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | An Amber trigger has been exceeded between B07LB303-B07LB305. This occurred during the daily survey of CH2 pilot excavation (11/03/15). This was discussed in the 1600hrs SRG and notification sent out. NO action is required as it is expected for the Slopes to improve when the area comes out of the excavation exclusion zone (refer to SRG notes (11.03.15 1600hrs)
| 01CV - Civils | Cxxx-NCR-002073 | NCR | BOS PTE Chainage 131 - 134 perpendicular joint |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-04-27 | 2015-04-16 00:14 | -11 | 2015-03-30 10:54 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the spraying of secondary lining in 5a a bay was sprayed up to 3 and 9 o'clock (chainage 133-136), a perpendicular joint was not properly prepared in this area. The joint at axis was left at too small an angle before moving onto spraying the crown. The spray was completed within 3 hours.
| 01CV - Civils | Cxxx-NCR-002074 | NCR | Lack of lap lenght of Masterseal at AP4E |  | Contr | BFK |  |  | 2015-04-17 | 2015-03-30 17:57 | -18 | 2015-03-23 17:07 | Tunnelling - Tunnelling General | 15500 |  | Workmanship | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During inspection of waterproofing, it became apparent the waterproofing in AP4E at ch 7 invert been damaged close to the previously cast invert and minimum lap length of waterproofing cannot be achieved.
| 01CV - Civils | Cxxx-NCR-002075 | NCR | Lack of lap lenght of Masterseal at AP4W |  | Contr | BFK |  |  | 2015-04-17 | 2015-03-30 18:03 | -18 | 2015-03-23 17:06 | Tunnelling - Tunnelling General | 15500 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During inspection of waterproofing, it became apparent the waterproofing in AP4W at ch 7 invert been damaged close to the previously cast invert and minimum lap length of waterproofing cannot be achieved.
| 01CV - Civils | Cxxx-NCR-002076 | NCR | TCR - AP7b - Under thicknes of secondary lining |  | Contr | BFK |  |  | 2015-03-31 | 2015-03-26 14:08 | -5 | 2015-03-17 17:12 | Tunnelling - Linings - Sprayed Concrete | 35500 |  | Incomplete Works | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following completion of AP7b tunnel and during final review of profile it was noted that some areas within this tunnel do not achieve the minimum combine thickness of fireproofing and secondary lining. This defect was not noted previously. The tunnel was the first tunnel being sprayed with secondary lining and fire proofing as trial.
| 01CV - Civils | Cxxx-NCR-002077 | NCR | PTW- Final As Built Profiles -38 to 230 |  | Contr | BFK |  |  | 2015-06-30 | 2015-06-29 12:36 | -1 | 2015-03-17 18:07 | Tunnelling - Tunnelling General | 35500 |  | Workmanship | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Fire proofing as-built profile out of designed tolerance for PTW- chainages -38 to 230
| 01CV - Civils | Cxxx-NCR-002078 | NCR | BOS PTE–WTH Connection : −5/−6 Slab Downstand |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-06-02 | 2015-05-29 09:25 | -4 | 2015-04-03 21:02 | Structural Engineering - Reinforcement | 10500 |  | Damaged | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Drawing Cxxx-__-S-DDL-Cxxx-11153 [C05] et al shows the -6 level slab and downstand in the WTH as being cast against the eastern Dwall. However, the Dwall behind needs to be broken out to accommodate the Cxxx cast collar to PTE in drawing Cxxx-MMD-C4-DDL-Cxxx_Z-000620 [C02]. During break out of the Dwall, part of the back of the Cxxx slab/downstand has been damaged, exposing some of the reinforcement (around grid reference M2 — see attached sketch Cxxx-NCR-002078-SK01). Please find attached pictures. Depth of damage is approximately 50–60mm. Note that the original bar mark E01 couplers were burned off, because they are not required in the Cxxx cast collar (compare Cxxx-__-S-DDA-Cxxx-81550 [C01] with Cxxx-MMD-C4-DDD-Cxxx_Z-00620 [C03]).
| 01CV - Civils | Cxxx-NCR-002079 | NCR | Insufficient Testing of cast insitu mix 22 during July 2014 |  | Contr | BFK |  |  | 2015-04-22 | 2015-04-15 23:17 | -7 | 2015-03-20 14:57 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Insufficient testing was carried out for cast insitu invert Mix 22 during July, no flexural strength, drying shrinkage or washouts.
| 01CV - Civils | Cxxx-NCR-002080 | NCR | Fibre Washout Test - Invert Mix - August 2014 |  | Contr | BFK |  |  | 2015-04-24 | 2015-03-25 14:17 | -30 | 2015-03-20 11:11 | Tunnelling - Linings - In-situ Concrete | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Fibre washout test sample EX637-W, no poly fibre only steel fibre was counted.
| 01CV - Civils | Cxxx-NCR-002081 | NCR | AP2E- Final As Built Profiles 0-36 |  | Contr | BFK |  |  | 2015-10-15 | 2017-07-02 19:55 | 626 | 2015-03-21 13:05 | Tunnelling - Tunnelling General | 25500 |  | Workmanship | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Fire proofing as-built profile out of designed tolerance for AP2E- chainages 0-36
| 01CV - Civils | Cxxx-NCR-002082 | NCR | CH3- Cast Invert Out of Tolerance |  | Contr | BFK |  |  | 2015-04-22 | 2015-04-15 23:32 | -7 | 2015-04-08 11:58 | Tunnelling - Tunnelling General | 25500 |  | Workmanship | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | CH3 ch 127-230 cast invert U1 finish (0-20mm tolerance) is out of specifications due to an inappropriate leveled. This NCR it is not complaint with the ITP Cxxx--C4-ITP-CRT00_ST005-50144 - BOS TCR CP Cast-in situ and Sprayed Secondary Lining section B4.10 and the general note G36 from the drawing Cxxx-MMD-C4-DDJ-N105-00001 reference below.
| 01CV - Civils | Cxxx-NCR-002083 | NCR | Spraying VD1A regulating invert without approval |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-04-27 | 2015-04-21 11:50 | -6 | 2015-03-23 11:02 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Cracks were repaired in VD1A on 16/03/2015. The invert was then sprayed with regulating layer on 17/03/15 without recieving approval from CRL/Cxxx. In our ITP this is listed as a 'hold point'.
| 01CV - Civils | Cxxx-NCR-002084 | NCR | BOS WTH: CH2 Enlargement over excavation to advance 3 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-04-17 | 2015-03-31 13:22 | -17 | 2015-03-21 02:15 | Tunnelling - Linings - Sprayed Concrete | 5500 |  | Workmanship | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the excavation of advance 3 invert to the CH2 enlargement over excavation occurred at both corners of the advance where the kwikastrip was placed. Over excavation was in the region of 400-500mm.
| 01CV - Civils | Cxxx-NCR-002085 | NCR | Spraying VD1C regulating layer without approval |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-04-24 | 2015-04-21 14:54 | -3 | 2015-03-23 11:27 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Cracks were repaired in VD1C on 19/03/2015. The invert was then sprayed with regulating layer on 20/03/15 without recieving approval from CRL/Cxxx. In our ITP this is listed as a 'hold point'.
| 01CV - Civils | Cxxx-NCR-002086 | NCR | BOS WTH: CH2 Advance 6 & 7 - Underthickness of shotcrete layer |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-04-17 | 2015-04-21 16:21 | 4 | 2015-03-26 14:46 | Tunnelling - Linings - Sprayed Concrete | 5500 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Advance 6 & 7 resulted in an under thickness shotcrete layer during the spraying of the primary lining.
| 01CV - Civils | Cxxx-NCR-002087 | NCR | Cores tested outside of 1-3 days |  | Contr | BFK |  |  | 2015-05-08 | 2015-04-21 15:18 | -17 | 2015-04-17 15:24 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Sample 827, PTW Fireproofing, Ch.7-18, cores tested at 5 days
| 01CV - Civils | Cxxx-NCR-002088 | NCR | Less than 6 cores tested per set |  | Contr | BFK |  |  | 2015-05-08 | 2015-04-21 15:30 | -17 | 2015-04-17 15:32 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Sample 822, CH3 Regulating CH. 160-190, only 5 cores tested at 3 days Sample 829, PTW Fireproofing CH. 12-38, Only 5 cores tested at 5 days Sample 830, PTW Fireproofing CH. 230-221, only 4 cores tested at 28 days
| 01CV - Civils | Cxxx-NCR-002089 | NCR | VD1C Masterseal Damage - Overlap not possible |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-04-09 | 2015-03-30 11:30 | -10 | 2015-03-26 17:29 | Tunnelling - Linings - Sprayed Concrete | 15500 |  | Damaged | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In VD1C invert adjacent to the cast invert of the __ collar there is masterseal damage as shown in the attached photos. One of these areas is close (155mm) to the already cast slab so an overlap of 200mm cannot be achieved (see attached photo).
| 01CV - Civils | Cxxx-NCR-002090 | NCR | Hollow spots in PTE invert CH192 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-04-17 | 2015-04-09 19:47 | -8 | 2015-03-30 13:47 | Tunnelling - Linings - Sprayed Concrete | 10000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After hammertest of primary lining in PTE invert, hollow spots were found in chainage 192 approximatelly (see sheet attached). The area was removed and repaired and found to be ready for spraying of regulating layer. Find approval to spray also attached.
| 01CV - Civils | Cxxx-NCR-002091 | NCR | AP2A damage to masterseal invert area in front of an invert |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-04-23 | 2015-04-24 08:20 | 1 | 2015-04-07 19:26 | Tunnelling - Linings - Sprayed Concrete | 10500 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Invert area was exposed in AP2A tunnel and found damages to the masterseal next to a cast invert. An __ 550 pipe was installed following the invert section and the injecting tubes taken out of the pour as agreed with CRL/Cxxx. Please find attached approval for that waterproofing layer.
| 01CV - Civils | Cxxx-NCR-002092 | NCR | SMM - Amber trigger breach between B07LP219 - B07LP217, along South Molton Lane |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-06-25 | 2015-06-23 17:35 | -2 | 2015-06-11 10:51 | Surveying - Surveying General | 10000 |  | Design | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | An Amber breach was reported between B07LP219 and B07LP217 (along South Molton Lane). The points have been resurveyed and verified as an amber breach. The street have been inspected and no noticeable/visible cracks observed.
| 01CV - Civils | Cxxx-NCR-002093 | NCR | S4- Underthickness Secondary Lining ch 24-31 |  | Contr | BFK |  |  | 2015-04-30 | 2015-04-28 11:26 | -2 | 2015-04-07 11:00 | Tunnelling - Linings - Sprayed Concrete | 25500 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After spraying the secondary lining in S4 between ch. 24 - 31, the profiles have been assessed by __ () and presented to __(Cxxx) and __ (CRL).It was concluded that there is concern with under thickness as the 250mm thickness was not achieved as required in PMI 1689.
| 01CV - Civils | Cxxx-NCR-002094 | NCR | LP9 Void |  | Contr | BFK |  |  | 2015-04-27 | 2015-04-21 16:26 | -6 | 2015-04-13 11:49 | Tunnelling - Tunnelling General | 25000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During an inspection in LP9 it was observed a void in the soffit. In the secondary lining meeting it was agreed to be repaired and suitable repair mortar to be applied. After the completion of the
| 01CV - Civils | Cxxx-NCR-002095 | NCR | BOS PTE Chainage 124 under thick secondary lining |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-04-20 | 2015-04-01 16:07 | -19 | 2015-03-30 14:35 | Tunnelling - Linings - Sprayed Concrete | 15500 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In BOS PTE secondary lining there is an underthickness area showing 140mm of secondary lining. The area is 1m x 0.25m This is due to a hollow sounding are that was broken out on a leading edge of sprayed secondary lining. This has been discussed with Cxxx and agreed that will fill this with Fireproofing Mix 21 due to its small size. Find attached scans showing this area.
| 01CV - Civils | Cxxx-NCR-002096 | NCR | BOS - PTE hollow spots in the primary lining invert CH200-220 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-04-30 | 2015-04-22 11:51 | -8 | 2015-04-14 11:54 | Tunnelling - Linings - Sprayed Concrete | 25500 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After hammertest of primary lining in PTE invert, hollow spots were found in several chainages (see sheet attached). The area was removed and repaired so it would be ready for spraying of the regulating layer. Find approval attached also.
| 01CV - Civils | Cxxx-NCR-002097 | NCR | TCR S2 Adit - Altered Spacing of Steel Lintel Beams |  | Contr | BFK |  |  | 2015-04-20 | 2015-04-01 15:25 | -19 | 2015-03-31 09:08 | Tunnelling - Linings - In-situ Concrete | 5000 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In installing the beams to the soffit of S2, the spacing of the steel lintel beams has been altered from that shown on drawing Cxxx-OVE-C4-DDB-CR001_Z-22160 rev C03. The beam positions have been adjusted to suit the reinforcement steel attached to the __ __ Couplers at the top of each column. The actual spacings achieved are shown in the drawings attached. Please confirm acceptable. This has been agreed over email with __ of Cxxx, this email is also attached.
| 01CV - Civils | Cxxx-NCR-002098 | NCR | VD1C Masterseal Damage - Overlap not possible |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-04-30 | 2015-04-30 20:54 | 0 | 2015-04-01 14:40 | Tunnelling - Linings - Sprayed Concrete | 9500 |  | Damaged | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In VD1C invert adjacent to the cast invert of the Cxxx invert there is masterseal damage as shown in the attached photos. One of these areas is close to the already cast slab so an overlap of 200mm cannot be achieved (see attached photo).
| 01CV - Civils | Cxxx-NCR-002099 | NCR | Cast In-Situ Invert Damage |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-07-29 | 2015-07-29 09:18 | 0 | 2015-04-09 14:28 | Tunnelling - Linings - In-situ Concrete | 9500 |  | Damaged | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In placing the formwork for the __-__ collar walls (RT) in VD1A discovered that due to the slope of the invert the shutter would not fit. As the side wall dimension could not be changed jiggered out a small section (200mm wide by 50-70mm deep by 1800mm in length) of the cast invert collar and an even smaller section (200mm wide by 70mm deep by 100mm in length).
| 01CV - Civils | Cxxx-NCR-002100 | NCR | BOS PTE Masterseal Chainage 176 and 178 - lights placed face down |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-04-15 | 2015-04-24 07:20 | 9 | 2015-04-01 14:59 | Tunnelling - Linings - Sprayed Concrete | 8500 |  | Supervision/Management | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On the 31/03/15 lights were placed 0.5 to 1m away from curing masterseal so that the light shone onto these areas. The warmth from the light will have aided curing these areas. Cxxx/CRL are concered that this may have a deterimental effect on the masterseal. The lights were removed and the areas re painted. The form -089b was signed off by Cxxx and CRL prior to pouring the invert. See attached photos and checksheets.
| 01CV - Civils | Cxxx-NCR-002101 | NCR | Damage to the overlap of the masterseal in PTE invert chainage 125.5 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-04-28 | 2015-04-28 11:28 | 0 | 2015-04-14 18:18 | Tunnelling - Linings - Sprayed Concrete | 20500 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During inspection of waterproofing, it became apparent the waterproofing in PTE at ch 125.5 invert have been damaged close to the previously cast invert and minimum lap length of waterproofing cannot be achieved.
| 01CV - Civils | Cxxx-NCR-002102 | NCR | BOS S2 Adits : 32mm Rebar in Column 1 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-05-26 | 2015-05-18 21:52 | -8 | 2015-05-12 22:39 | Tunnelling - Linings - In-situ Concrete | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In the invert pour of the Cxxx BOS S2 adits, one of the vertical BM38 bars for column 1 (westernmost column) was located approximately 100mm out of position — refer to attached sketch Cxxx-NCR-002102.
| 01CV - Civils | Cxxx-NCR-002103 | NCR | Masterseal Damage in PTE invert - Overlap not achieved |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2015-05-05 | 2015-04-22 10:02 | -13 | 2015-04-07 03:31 | Tunnelling - Linings - Sprayed Concrete | 30500 |  | Damaged | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In PTE invert area (approx at ch 200) there is a damage on masterseal (see attahced photos), adjacent to the stop end of the invert slab. The required overlap of 200mm according the workmanship specification (KW20.3301) was not achieved.
| 01CV - Civils | Cxxx-NCR-002104 | NCR | CH2 Enlargement Advance 25, low 1 and 2 hour early age strength result |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-04-23 | 2015-04-21 15:01 | -2 | 2015-04-07 14:34 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Low Early age Strength Results @ 1 and 2 hours for CH2 Advance 25. With reference to ITP required strength should be .52MPa @ 1 hour and .78MPa @ 2 hours.
| 01CV - Civils | Cxxx-NCR-002105 | NCR | BOS PTE 5b Ch 184 - Masterseal overlap |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-04-30 | 2015-04-29 12:01 | -1 | 2015-04-08 13:02 | Tunnelling - Linings - Sprayed Concrete | 20500 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During repair works of the masterseal outside CP1 a repair was undertaken next to the invert slab. The required 200mm overlap will not be achieved in this area. will install adcor as a mitigation in this area. The patched area is at chainage 184 and the area was 150mm in length along the slab and 50mm wide.
| 01CV - Civils | Cxxx-NCR-002106 | NCR | VD1A Masterseal Overlap not Achieved |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-04-29 | 2015-04-30 20:06 | 1 | 2015-04-15 09:41 | Tunnelling - Linings - Sprayed Concrete | 20500 |  | Damaged | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Overlap not achieved on VD1A masterseal in various places following minor tears. The location of these tears are in the WTH connection close to the SCL interface.
| 01CV - Civils | Cxxx-NCR-002107 | NCR | CH3 - Overspray and Underthickness Fireproofing ch 226-230 |  | Contr | BFK |  |  | 2015-04-27 | 2015-04-21 16:29 | -6 | 2015-04-13 11:52 | Tunnelling - Tunnelling General | 25500 |  | Workmanship | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After spraying the fireproofing in CH3 between ch. 226 - 230, the profiles have been assessed by __ () and presented to __(Cxxx) and __ (CRL). It was concluded that there is concern with under thickness as the 50mm thickness was not achieved. The thickness of the area is at least 40 mm(As per cross sections attached), compliant with the fire testing reports submitted in the FCD 1218. Also tight areas were identified (no more than 54 mm tight)
| 01CV - Civils | Cxxx-NCR-002108 | NCR | BOS - AP2A overspray on waterproofing |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-05-20 | 2015-05-26 11:06 | 6 | 2015-04-13 13:24 | Tunnelling - Linings - Sprayed Concrete | 15500 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A length of 1m of masterseal in AP2A tunnel was accidentally oversprayed with SL / FP being sprayed in the area next to it. As a result the area might not have the required overlap. cleaned thoughly the area, reapplied a new MS layer and __ will be installed in the joint.
| 01CV - Civils | Cxxx-NCR-002109 | NCR | At BOS SCL 770 was crushed @ 4 days whilst SCL 658,659,763 the required 6 cores were not crushed at 1 day including SCL 682 where only 5 cores were crushed at 28 days. |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-04-27 | 2015-04-16 12:03 | -11 | 2015-04-10 09:48 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | At BOS on one occassion cores were not crushed within the 1-3 day window (SCL 770), also on 3 occassions 4 to 5 cores were cushed to represent 1 day rather than ITP stipulated 6 cores (SCL 658,659,763) whilst @ 28 days 5 cores were crushed (SCL 682).
| 01CV - Civils | Cxxx-NCR-002110 | NCR | Damages to the masterseal on the invert chainage 218 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-04-28 | 2015-04-28 11:51 | 0 | 2015-04-14 11:09 | Tunnelling - Linings - Sprayed Concrete | 25500 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During inspection of waterproofing, it became apparent the waterproofing in PTE at ch 218 invert been damaged close to the previously cast invert and minimum lap length of waterproofing cannot be achieved.
| 01CV - Civils | Cxxx-NCR-002111 | NCR | From 19 November 2014 to the present 10/04/2015; 5977 metesr cube of shotcrete was delivered to BOS; thus 119 sets of compressive samples if ITP is followed; however only 83 sets of samples was actually performed. |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-04-27 | 2015-04-21 15:23 | -6 | 2015-04-10 16:43 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | From 19/11/2014 to the present 10/04/2015 5977m3 of shotcrete was delivered to BOS, thus 119 sets of compressive samples; however only 83 sets was actually taken within that period.
| 01CV - Civils | Cxxx-NCR-002112 | NCR | BOS PTE Chainage 112 to 135 hollow sounding areas |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-04-27 | 2015-04-28 11:55 | 1 | 2015-04-13 13:02 | Tunnelling - Linings - Sprayed Concrete | 20500 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Systematic hammer testing of PTE fireproofing CH112-135 (08/04/2015) detected 6 hollow sounding areas. See attached hammer test sheet. All areas are below axis, three areas are on the platform side and three are on the trackside.
| 01CV - Civils | Cxxx-NCR-002113 | NCR | BOS PTE Chainage 156 to 171 Hollow sounding areas |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-04-27 | 2015-04-30 09:18 | 3 | 2015-04-13 13:57 | Tunnelling - Linings - Sprayed Concrete | 10500 |  | Incorrect Installation | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Systematic hammer testing of PTE fireproofing CH156-171 (09/04/2015) detected 5 hollow sounding areas. See attached hammer test sheet. All areas are below axis, one area is on the platform side (are 11) and four are on the trackside(areas 7-10). These areas have been surveyed and fall below the next stage of concrete works, see reference drawings. See attached hammer test sheet and also the patch survey showing the area and level (summarised below). Area 7: 0.8 x 1.2 m - 96.75m - CH 169.58 - 170.38 Area 8: 0.8 x 1.4 m - 96.80m - CH 165.58 - 166.38 Area 9: 0.7 x 1.5m - 96.13m - CH 164.50 - 165.2 Area 10: 0.5 x 1.3m - 96.07m - CH 160.65 - 161.15 Area 11: 1.5 x 1.3m - 95.67m - CH 160.50 - 162.00 See attached secondary lining thickness scan cross sections marked up with the location of the hollow sounding areas.
| 01CV - Civils | Cxxx-NCR-002114 | NCR | Damages to the Masterseal in VD1C tunnel near connection to WTH |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-04-28 | 2015-04-21 16:54 | -7 | 2015-04-14 11:45 | Tunnelling - Linings - Sprayed Concrete | 35500 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Small damages were found in the area next to the invert in VD1C tunnel, on both sides. As a result the overlap required would not be achieved. The area was re-sprayed and it was areed with CRL and Cxxx to install __ along the cast in situ invert.
| 01CV - Civils | Cxxx-NCR-002115 | NCR | 7no reinforcement bars bent in PTE invert |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-04-30 | 2015-04-22 09:47 | -8 | 2015-04-14 12:56 | Tunnelling - Linings - Sprayed Concrete | 4500 |  | Workmanship | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Some bars in the PTE invert were bent in order to clean / repair the masterseal behind.
| 01CV - Civils | Cxxx-NCR-002116 | NCR | Invert Mix washout - No polyfibre result |  | Contr | BFK |  |  | 2015-05-12 | 2015-04-28 13:33 | -14 | 2015-04-14 17:15 | Tunnelling - Linings - In-situ Concrete | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | A washout test was performed on mix 30 (EX-1129) where no polyfibre result was recorded and steel washout was tested 6 times not the 3 as required
| 01CV - Civils | Cxxx-NCR-002117 | NCR | VD1C Shotcrete Overspray onto Masterseal |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-04-29 | 2015-04-21 16:15 | -8 | 2015-04-15 17:38 | Tunnelling - Linings - Sprayed Concrete | 25500 |  | Damaged | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In VD1C at the interface between the SCL and the WTH collar connections, oversprayed fireproofing onto the masterseal despite it being protected with a polythene sheet. cannot now repair the bolt holes from the timber sweep with the minimum 200mm overlap as per the manufactures guidance.
| 01CV - Civils | Cxxx-NCR-002118 | NCR | BOS PTE Chainage 192 Overspray onto waterproofing prior to inspection |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-05-01 | 2015-04-28 11:37 | -3 | 2015-04-17 13:24 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the spraying of the secondary lining in PTE before chainage 192 there has been some over spray on the un inspected masterseal. This area at chainage 192 on the right hand side facing west at the 3 o'clock position was therefore un able to be inspected prior to spraying secondary lining. Prior to spraying however the area was looked at and it was dry. See attached approval of masterseal checksheet and also signed sheet showing the area was dry.
| 01CV - Civils | Cxxx-NCR-002119 | NCR | PTW Headwall Tam Tubes |  | Contr | BFK |  |  | 2015-06-19 | 2015-06-20 11:47 | 1 | 2015-04-17 18:18 | Tunnelling - Tunnelling General | 10000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Although PTW was handed over to __ on the 23 March 2015. It has become apparent that the tam tubes at the PTW east Headwall are exposed. This issue wasn’t noticed by ,CRL / Cxxx or __ before handing over.
| 01CV - Civils | Cxxx-NCR-002120 | NCR | BOS PTE Overspray onto Waterproofing ch 210 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-05-05 | 2015-04-29 12:43 | -6 | 2015-04-21 14:26 | Tunnelling - Tunnelling General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the spraying of the secondary lining in PTE before chainage 210 there has been some over spray on the un inspected masterseal. Prior to spraying however the area was looked at and it was dry. See attached approval of masterseal checksheet and also signed sheet showing the area was dry.
| 01CV - Civils | Cxxx-NCR-002121 | NCR | PTE- Sprayed Secondary lining over patch shutter repairs |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-04-30 | 2015-04-29 12:42 | -1 | 2015-04-26 16:22 | Tunnelling - Tunnelling General | 2000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | After pouring shutters from 210 to 213 the stop end was removed and four patches each side were repaired. Although they were repaired it was not witness by CRL. Please find check sheet showing that the holes were grouted, waterproofed and tested before spraying secondary lining.
| 01CV - Civils | Cxxx-NCR-002122 | NCR | BOS PTE Connection - invert reinforcement bar cover |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-05-19 | 2015-05-13 17:28 | -6 | 2015-05-05 13:00 | Tunnelling - Linings - In-situ Concrete | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Due to the lack of couplers in the D wall of PTE bar mark 47 had to be drilled and fixed. For the invert pour for the collar these bars were drilled and fixed. After drilling and fixing these bars it was noted that the cover would be 40mm (min) rather than the 60mm noted on the design.
| 01CV - Civils | Cxxx-NCR-002123 | NCR | TCR ETH - Damaged couplers around moling hole in -4 slab |  | Contr | BFK |  |  | 2015-06-22 | 2015-06-23 17:56 | 1 | 2015-04-20 14:46 | Civil - Civil Engineering General | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During a pre-handover condition survey of the Goslett Yard Box on 15th of April 2015 it was noted that some of the couplers around the moling hole opening in the -4 floor slab have been damaged. These are shown annotated in the attached photographs and it can be seen that 5 no. have threads damaged, 3 no. are bent greater than 30 degrees from the correct position and 8 are bent less than 30 degrees from the correct position.
| 01CV - Civils | Cxxx-NCR-002124 | NCR | TCR S2 - Omission of section of cast concrete at each opening |  | Contr | BFK |  |  | 2015-05-11 | 2015-05-18 14:51 | 7 | 2015-04-20 17:44 | Tunnelling - Linings - In-situ Concrete | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The soffit of the S2 adit concrete was poured before the removal of the SGI ring infill panels, meaning that the concrete does not extend into the opening as shown in section B of drawing Cxxx-OVE-C4-DDB-CR001_Z-22160. This has resulted in a v-shaped notch in the crown where the concrete should be flat. This is shown in the attached photograph and sketch.
| 01CV - Civils | Cxxx-NCR-002125 | NCR | CL1 - Lack of radial joint |  | Contr | BFK |  |  | 2015-06-19 | 2015-06-20 11:51 | 1 | 2015-04-21 10:39 | Tunnelling - Tunnelling General | 15000 |  | Incorrect Installation | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In CL1 it has been noticed that has built a leading edge instead of a radial joint. This is not compliant with the Drawing Cxxx-MMD-C4-DDB-N105_5-00505.
| 01CV - Civils | Cxxx-NCR-002126 | NCR | CH3- Final As built Profile ch 130 -229 |  | Contr | BFK |  |  | 2015-08-24 | 2015-09-01 16:38 | 8 | 2015-04-21 17:57 | Tunnelling - Tunnelling General | 20000 |  | Workmanship | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Fire proofing as-built profile out of designed tolerance for CH3- chainages 130 to 229
| 01CV - Civils | Cxxx-NCR-002127 | NCR | AP4W- Final As Built Profiles |  | Contr | BFK |  |  | 2015-05-12 | 2015-05-18 14:59 | 6 | 2015-04-21 17:50 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Fire proofing as-built profile out of designed tolerance for AP4W
| 01CV - Civils | Cxxx-NCR-002128 | NCR | BOS PTE Slab Level - Out of Tolerance Chainage 180 to 218 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-04-29 | 2015-04-28 13:44 | -1 | 2015-04-22 10:09 | Tunnelling - Linings - Sprayed Concrete | 20000 |  | Incorrect Installation | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | invert level survey in PTE between chainages 180m & 218m indicate multiple locations that are out of tolerance. The design level of PTE slab is 95.047mAod. The minimum permissible level is 95.027mAod. As the level survey attached shows, multiple locations along the slab are lower and higher than the permissible level of 95.027mAod and 95.047mAod. The lowest area of the slab has a reduced level of 95.0005mAod (22mm out of tolerance) and the highest area of the slab has a reduced level of 95.055mAod (8mm out of tolerance).
| 01CV - Civils | Cxxx-NCR-002129 | NCR | At BOS from January 2015 to the end of April 2015 BFK didnt comply fully with reference to Longterm Compressive Strength, in terms of a set every 50m3. |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-06-11 | 2015-06-12 23:08 | 1 | 2015-04-23 13:29 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | At BOS Street from January 2015 to the end of April 2015, didnt comply fully with their ITP of a set every 50m3 with reference to Mix 21 where 1755.5m3 of shotcrete was delivered to site thus 35 sets required but carried out only 20 sets while Mix 20, 114m3 was delivered (thus 2 sets needed) but only 1 set was taken.
| 01CV - Civils | Cxxx-NCR-002130 | NCR | PTE Low Density results for BFK027 |  | Contr | BFK |  |  | 2015-05-23 | 2015-05-05 18:30 | -18 | 2015-04-23 17:57 | Tunnelling - Linings - Sprayed Concrete | 2500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | have experienced drop in density in cubes results for mix 027 in PTE ch87.9 to ch141.5(TCR). The drop does not meet the required 2300kg/m3 as specified in KF10.
| 01CV - Civils | Cxxx-NCR-002131 | NCR | LP9 Low Density results for BFK027 |  | Contr | BFK |  |  | 2015-05-23 | 2015-05-05 18:33 | -18 | 2015-04-23 18:08 | Tunnelling - Linings - Sprayed Concrete | 2500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | have experienced drop in density in cubes results for mix 027 in LP9(TCR). The drop does not meet the required 2300kg/m3 as specified in KF10.
| 01CV - Civils | Cxxx-NCR-002132 | NCR | CH1 Low Density results for BFK027 |  | Contr | BFK |  |  | 2015-05-23 | 2015-05-05 18:35 | -18 | 2015-04-23 18:12 | Tunnelling - Linings - Sprayed Concrete | 2500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | have experienced drop in density in cubes results for mix 027 in CH1 Ch0 to Ch15(TCR) including Ch1 to AP1 junction. The drop does not meet the required 2300kg/m3 as specified in KF10.
| 01CV - Civils | Cxxx-NCR-002133 | NCR | S2 Low Density results for BFK027 |  | Contr | BFK |  |  | 2015-05-23 | 2015-05-05 18:36 | -18 | 2015-04-23 18:17 | Tunnelling - Linings - Sprayed Concrete | 2500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | have experienced drop in density in cubes results for mix 027 in S2(TCR). The drop does not meet the required 2300kg/m3 as specified in KF10.
| 01CV - Civils | Cxxx-NCR-002134 | NCR | VEW Columns Low Density results for BFK027 |  | Contr | BFK |  |  | 2015-05-23 | 2015-05-05 18:39 | -18 | 2015-04-23 18:21 | Tunnelling - Linings - Sprayed Concrete | 2500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | have experienced drop in density in cubes results for mix 027 in VEW Columns(TCR). The drop does not meet the required 2300kg/m3 as specified in KF10.
| 01CV - Civils | Cxxx-NCR-002135 | NCR | PTW Low Density results for BFK027 |  | Contr | BFK |  |  | 2015-05-23 | 2015-05-05 18:40 | -18 | 2015-04-23 18:25 | Tunnelling - Linings - Sprayed Concrete | 2500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | have experienced drop in density in cubes results for mix 027 in PTW Ch-38 to Ch20 including PTW sump(TCR). The drop does not meet the required 2300kg/m3 as specified in KF10.
| 01CV - Civils | Cxxx-NCR-002136 | NCR | AP4W Low Density results for BFK027 |  | Contr | BFK |  |  | 2015-05-23 | 2015-05-05 18:42 | -18 | 2015-04-23 18:29 | Tunnelling - Linings - Sprayed Concrete | 2500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | have experienced drop in density in cubes results for mix 027 in AP4W(TCR). The drop does not meet the required 2300kg/m3 as specified in KF10.
| 01CV - Civils | Cxxx-NCR-002137 | NCR | S4 Low Density results for BFK027 |  | Contr | BFK |  |  | 2015-05-23 | 2015-05-05 18:43 | -18 | 2015-04-23 18:33 | Tunnelling - Linings - Sprayed Concrete | 2500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | have experienced drop in density in cubes results for mix 027 in S4(TCR). The drop does not meet the required 2300kg/m3 as specified in KF10.
| 01CV - Civils | Cxxx-NCR-002138 | NCR | ITP Item 3.9 not fulfilled completely for PTW 1C Secondary Lining BOS |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-05-24 | 2015-04-29 12:00 | -25 | 2015-04-24 16:34 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Use As-Is | 3 (3-6k) | Complete | Procedure Problem - Other | Completed |  | form-089a shows only 10 patches have been taken which is not enough as per the requirement of the approved ITP Item B3.9. The approved ITP and filled in form 089a are attached
| 01CV - Civils | Cxxx-NCR-002139 | NCR | BOS PTE Chainage 171 hollow sounding area |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-04-30 | 2015-04-29 13:19 | -1 | 2015-04-24 17:48 | Tunnelling - Linings - Sprayed Concrete | 20500 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Systematic hammer testing of PTE fireproofing CH1171-190 (23/04/2015) detected 1 hollow sounding areas. See attached hammer test sheet. One hollow sounding are was identified at chainage 171. This is below axis.
| 01CV - Civils | Cxxx-NCR-002140 | NCR | BOS PTE Chainage 135 to 156 hollow sounding areas |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-04-30 | 2015-04-29 13:22 | -1 | 2015-04-27 18:52 | Tunnelling - Linings - Sprayed Concrete | 20500 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Systematic hammer testing of PTE fireproofing CH135-156 (27/04/2015) detected 2 hollow sounding areas. See attached hammer test sheet. These area appear to be along the leading edge between bays. Both areas are below axis, one trackside and one platform side.
| 01CV - Civils | Cxxx-NCR-002141 | NCR | AP7A - Final As Built Profiles |  | Contr | BFK |  |  | 2015-05-12 | 2015-05-18 15:01 | 6 | 2015-04-28 12:19 | Tunnelling - Tunnelling General | 10000 |  | Workmanship | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Fire proofing as-built profile out of designed tolerance for AP7A.
| 01CV - Civils | Cxxx-NCR-002142 | NCR | HLC Computer in Mayfair Exchange, 34 Brook Street |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-05-12 | 2015-05-13 14:34 | 1 | 2015-04-28 13:30 | Surveying - Instrumentation and Monitoring | 70000 |  | Software | Use As-Is | 1 (>60k) | Complete | External Phenomenon - Not Defined | Completed |  | There have been reported power outage in 34 Brook Street (Mayfair Exchange) which trips off the computer and router that transmit HLC data to GTC visual. This incident occurred twice night of 18/04/2015 and night of 25/04/2015. At this period in time were carrying critical activities that required real time monitoring. (18/04/15 - grouting of the well in CH2 and 25/04/2015 - concurrent grouting works for CH2). These activities could not be done at those times as access was not available to reboot the system.
| 01CV - Civils | Cxxx-NCR-002143 | NCR | Less than 6 cores tested per set |  | Contr | BFK |  |  | 2015-05-14 | 2015-05-05 18:17 | -9 | 2015-04-30 11:31 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Sample 842, CH3, Fireproofing CH.169-180. Only 5 cores tested at 3 days
| 01CV - Civils | Cxxx-NCR-002144 | NCR | TCR - Cores tested outside of 1-3 days |  | Contr | BFK |  |  | 2015-05-21 | 2015-05-05 18:25 | -16 | 2015-04-30 11:34 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Sample 836, Fireproofing, AP7b, CH.3-8 tested at 6 days Sample 837, Fireproofing, AP8, CH, 6-12 tested at 5 days Sample 838, Secondary, CH3, CH176-179 tested at 4 days Sample 839, Fireproofing, AP8, CH 25-21 tested at 4 days
| 01CV - Civils | Cxxx-NCR-002145 | NCR | Bond St CH2 Enlargement works - Delayed installation of monitoring points |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-05-12 | 2015-05-07 20:38 | -5 | 2015-04-28 18:03 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | The installation of the monitoring points to advance 31a was delayed and as a result the 2hr installation period to obtain the zero base readings was missed. Monitoring points were installed once advance 31b was complete and the exclusion zone lifted.
| 01CV - Civils | Cxxx-NCR-002146 | NCR | BOS PTE Chainage 130 Oil Spill on Lining |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-05-01 | 2015-04-30 09:21 | -1 | 2015-04-29 11:05 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Equipment Breakdown | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Oil leakage from excavator hose at chainage 130 in PTE. A small area of the lining just above axis level has been covered in oil. See attached Photograph.
| 01CV - Civils | Cxxx-NCR-002147 | NCR | BOS S2 Adits : Cover to Rebar in Cxxx Piers 2 and 4 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-05-13 | 2015-05-18 15:03 | 5 | 2015-04-29 23:35 | Tunnelling - Linings - In-situ Concrete | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The main structural reinforcement to piers 2 and 4 of the S2 adits has variable cover to the SGI segments and is generally sufficient, but at its closest point (approx. axis level of the SGI) the cover is a minimum of 50mm. Note 2 of drawing Cxxx-OVE-S-DDD-CR001_Z-43100 specifies 75mm cover.
| 01CV - Civils | Cxxx-NCR-002148 | NCR | BOS PTE- Final As Built Profiles out of tolerances ch 110-218 |  | Contr | BFK |  |  | 2015-05-13 | 2015-04-30 09:26 | -13 | 2015-04-29 13:46 | Tunnelling - Tunnelling General | 20500 |  | Workmanship | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Fire proofing as-built profile out of designed tolerance for PTE- chainages 110 to 218
| 01CV - Civils | Cxxx-NCR-002149 | NCR | BOS S2 Adits : Cover to Rebar in Cxxx Piers 1 and 5 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-09-30 | 2015-08-23 23:04 | -38 | 2015-04-29 23:40 | Tunnelling - Linings - In-situ Concrete | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The main structural reinforcement to piers 1 and 5 of the S2 adits has variable cover to the SGI segments and is generally sufficient, but at its closest point (approx. axis level of the SGI) the cover is a minimum of 50mm. Note 2 of drawing Cxxx-OVE-S-DDD-CR001_Z-43100 specifies 75mm cover.
| 01CV - Civils | Cxxx-NCR-002150 | NCR | St. Patrick's Church in Soho Square - fallen crackmeter |  | Contr | BFK |  |  | 2015-05-20 | 2015-05-21 11:50 | 1 | 2015-04-29 14:29 | Surveying - Instrumentation and Monitoring | 500 |  | Equipment Breakdown | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Not Defined | Completed |  | On 28.08.2015 wre informed that the datalogger of the crackmeter at the at the back of St. Patrick's Church in Soho Square - by the picture - was pulled off from the wall where it was installed. The datalogger didn’t look like it was damaged, so it was re-attached it to the wall (see attached pictures). As for the causes, it’s not possible to determine if it was deliberate vandalism or accidental collision. However it is evident that someone/something definitely interfered with the instrumentation.
| 01CV - Civils | Cxxx-NCR-002151 | NCR | TCR - 1 day cores tested late |  | Contr | BFK |  |  | 2015-05-21 | 2015-05-05 18:27 | -16 | 2015-04-30 11:35 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Sample 848, CH3, Secondary, CH 210-207 tested at 5 days Sample 849, CH3, Secondary, CH 230-226.5 tested at 4 days
| 01CV - Civils | Cxxx-NCR-002152 | NCR | ITP Item B3.9 not fulfilled completely for PTE 2A Secondary Lining BOS |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-06-29 | 2015-06-13 00:28 | -16 | 2015-04-29 16:57 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | form-089a shows only few patches have been taken which is not enough as per the requirement of the approved ITP Item B3.9. The approved ITP and filled in form 089a are attached
| 01CV - Civils | Cxxx-NCR-002153 | NCR | BFK Cas Insitu mixes are supposed to use 50mm long fibres, but only 35mm fibres have been used. |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-05-14 | 2015-05-07 15:52 | -7 | 2015-04-30 11:27 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | across the three sites of BondStreet, Tottenham Court Road and Fisher Street were suppose to have used cast insitu mixes with 50mm long steel fibre (in accordance with KF10.1409), however only 35mm long steel fibres is being used in their mixes
| 01CV - Civils | Cxxx-NCR-002154 | NCR | BOS S2 Adits : Water Bar Not Installed in Invert Pour |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-09-30 | 2015-09-01 22:33 | -29 | 2015-04-30 20:44 | Tunnelling - Linings - In-situ Concrete | 5000 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Drawing Cxxx-OVE-C4-DDL-CR001_Z-21116 [C01] indicates water bars between certain construction joints in the S2 adit piers. The water bars between the invert and columns, on the outermost piers (1 and 5), were not installed (1No water bar missing on each of piers 1 and 5).
| 01CV - Civils | Cxxx-NCR-002155 | NCR | BOS AP2A Leaks close to cast invert |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-05-18 | 2015-05-13 15:42 | -5 | 2015-05-04 16:14 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Damaged | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 2 leaks were found close to the previously cast invert. These areas were repaired and __ installed along the invert. __ has also been installed around the stop end and re injectable tubes have been installed around the collar. See attached approval and repair checksheets.
| 01CV - Civils | Cxxx-NCR-002156 | NCR | BOS AP2A leak close to cast connection |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-05-18 | 2015-05-13 15:53 | -5 | 2015-05-04 16:20 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Damaged | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 1 leak was found in the crown close to the previously cast connection. This areas was repaired. The cast connection has 2 rows of re injectable tubes between the connection at the sprayed lining. __ has also been installed around the stop end from the last sprayed section and along the invert. See attached approval and repair checksheets.
| 01CV - Civils | Cxxx-NCR-002157 | NCR | ITP Item 3.9 not fulfilled completely for PTE 2B Secondary Lining BOS |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-06-04 | 2015-05-14 21:50 | -21 | 2015-05-05 14:21 | Tunnelling - Linings - In-situ Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | form-089a shows some patches have been taken which is not enough as per the requirement of the approved ITP Item B3.9. The approved ITP and filled in form 089a are attached
| 01CV - Civils | Cxxx-NCR-002158 | NCR | ITP Item 3.9 not fulfilled completely for CH3 3B Secondary Lining BOS |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-06-04 | 2015-05-14 21:52 | -21 | 2015-05-05 14:53 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | form-089a shows a few patches have been taken which is not enough as per the requirement of the approved ITP Item B3.9. The approved ITP and filled in form 089a are attached
| 01CV - Civils | Cxxx-NCR-002159 | NCR | AP4E - Final As Builts Profile |  | Contr | BFK |  |  | 2015-10-15 | 2017-03-12 14:57 | 514 | 2015-05-14 11:47 | Tunnelling - Tunnelling General | 5000 |  | Workmanship | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As agreed on the meetings of the 30/03/15 and 2/02/15 (Find sign off attached) this NCR cover the fireproofing as-built profile out of designed tolerance for AP4E. Please find attached the spreadsheet and profile showing that all the areas tighter than 50mm have been removed, except from one tight spot covered in the already closed NCR 1842
| 01CV - Civils | Cxxx-NCR-002160 | NCR | CP2 - Final As Built Profile |  | Contr | BFK |  |  | 2015-06-11 | 2015-06-12 21:36 | 1 | 2015-05-12 18:09 | Tunnelling - Tunnelling General | 5000 |  | Workmanship | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As agreed on the meeting of the 11/03/15 (Find sign off attached) this NCR cover the fireproofing as-built profile out of designed tolerance for CP2. Please find attached the spreadsheet and profile showing that all the areas tighter than 50mm have been removed.
| 01CV - Civils | Cxxx-NCR-002162 | NCR | Lack of overlap PTE to WTH connection |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-05-25 | 2015-05-26 11:15 | 1 | 2015-05-11 19:41 | Tunnelling - Tunnelling General | 10000 |  | Workmanship | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | While spraying regulating on the Dwall in the PTE - WTH connection the plastic sheet protecting the waterproofing was damaged and as a result the Masterseal was oversprayed. immediately cleaned the surface and re-sprayed the whole area and not only the holes in the masterseaal due to the bolts to fix the stopend in chainage 217.5. CRL showed later some concerns about the area not being sufficiently clean to re-spray the masterseal and agreed to install a re-injectable pipe around the perimeter of the tunnel to avoid any doubts about the quality of the works. Please find attached photos of the area before and after jet-washing. Another damage was found in the area above the previously cast lining in the RHS of the tunnel. Since the overlap could not be achieved, it was again agreed the installatiion of a reinjectable pipe along the joint.
| 01CV - Civils | Cxxx-NCR-002163 | NCR | BOS PTE Collar - outsanding masterseal repairs on inspection |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2015-06-08 | 2015-05-29 09:32 | -10 | 2015-05-11 17:41 | Tunnelling - Linings - Sprayed Concrete | 2000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | During requested inspection of PTE collar for the 2nd stage collar pour RHS ( looking upchainage)on DS 06-05-15 CRL/Cxxx identified several further areas where masterseal repairs were required and identified during a pre-inspection by CRL a day earlier and conveyed to were found to be unaddressed during the formal inspection.
| 01CV - Civils | Cxxx-NCR-002164 | NCR | CH2 Enlargement: Missing Profiles Advance 54 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-05-25 | 2015-05-26 15:19 | 1 | 2015-05-11 12:25 | Tunnelling - Linings - Sprayed Concrete | 1000 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the excavation of advance 54 Invert to CH2 the second profile record was not taken.
| 01CV - Civils | Cxxx-NCR-002165 | NCR | BOS AP2A - Timber embedded during 3rd stage collar pour |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2015-06-11 | 2015-06-12 21:39 | 1 | 2015-05-11 17:43 | Tunnelling - Linings - In-situ Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | CRL post inspection of the 3rd stage pour of AP2A collar RHS (facing platform) on the 26/04/15 identified that a timber length and ply panel affixed to the end of the timber had not been removed and found to be partially cast in. shift manager was notified of the issue and asked to resolve. The final stage of concrete pour has been completed but no evidence has been provided to CRL showing that the timber has been removed.
| 01CV - Civils | Cxxx-NCR-002166 | NCR | Amber Breach between B07LB307 – B07LB305 (__s front of 15 South Molton Lane |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-06-11 | 2015-06-12 21:44 | 1 | 2015-05-11 17:28 | Geotechnical Engineering - Settlement | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | An Amber breach was reported between B07LB307 – B07LB305 (location, façade of 15 South Molton Lane). This point has been resurveyed and verified as amber. (see attachment for location and monitoring plot) The façade of 15 South Molton Lane has been inspected and no visible cracks observed.
| 01CV - Civils | Cxxx-NCR-002167 | NCR | S4 - Final As Built Profile |  | Contr | BFK |  |  | 2015-08-14 | 2015-09-01 15:58 | 18 | 2015-05-12 13:02 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Fire proofing as-built profile out of designed tolerance for S4.This NCR is to cover the percentages out of tolerance. All the profiles discrepancies was covered in the NCR 2016 already closed
| 01CV - Civils | Cxxx-NCR-002168 | NCR | Overspray in CP4(RT) BOS |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-06-11 | 2015-05-26 18:14 | -16 | 2015-05-12 16:13 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After spraying fireproofing in CP4(RT) have noticed some areas that have been oversprayed between Ch5 to Ch25, the scans from __ have been attached to this NCR. The tight areas have been highlighted in red. The worst case being 40mm at Ch25
| 01CV - Civils | Cxxx-NCR-002169 | NCR | BOS WTH: S2 Timber Heading |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-06-18 | 2015-06-17 22:34 | -1 | 2015-05-12 19:30 | Tunnelling - Excavation - Hand | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the construction of the timber heading to S2 Adit handworks, the front of the heading was insufficiently covered with timber boards. No face boards were installed at the end of the shift and the face was left without support for 6-8hrs. The issue was identified by CRL inspector on night shift and a sheet of ply with wedges were installed as face support which is not suitable for the support.
| 01CV - Civils | Cxxx-NCR-002170 | NCR | CP4 - Final As Built Profile |  | Contr | BFK |  |  | 2015-06-11 | 2015-06-12 21:52 | 1 | 2015-05-14 13:28 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As agreed on the meetings of the 20/3/15 (Find sign off attached) this NCR cover the fireproofing as-built profile out of designed tolerance for CP4. Please find attached the percentage spreadsheet and profiles showing that all the areas tighter than 50mm have been removed, except from the right hand side area from ch 5.5 to 8 due to design issues covered in the RFI 1511.
| 01CV - Civils | Cxxx-NCR-002171 | NCR | BOS PTE Connection to WTH |  | Contr | BFK |  |  | 2015-05-30 | 2015-05-29 12:57 | -1 | 2015-05-26 16:56 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | A joint inspection was carried out by /CRL/Cxxx in order to ascertain whether any remedial to the PTE Connection to the WTH was required and the following was agreed: - Zone 1 & 2 (As per sketch attached) : Discoloration and honey combing respectively, to be use as is. - Zone 3 : Exposed bar below tam box, to be repaired following activity plan attached.
| 01CV - Civils | Cxxx-NCR-002172 | NCR | HLC Computer in Mayfair Exchange, 34 Brook Street Re: NCR-002142 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-06-25 | 2015-06-13 00:21 | -12 | 2015-05-14 10:36 | Surveying - Instrumentation and Monitoring | 500 |  | Software | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | The PC which serves the HLCs in BOS 1 and 4 area is located in 34 Brook Street. /__ have experience loss of real time data on 3 occasions (18/04/15, 25/04/15/15 and 02/05/15) with no known cause. 18/04/2015: it was suspected a power surge tripped the system off. rang the contact received from the CARL team at that point in time to gain access but no access was provided until 20/04/2015. 25/04/2015: this issue repeated and couldn't access the PC until 27/04/2015 to reboot system. further investigation shows that data was retrievable which suggest on-going monitoring. __ replaced router and installed new a UPS should there be any form of power surge causing the disconnect. The above was all tested and working (re: Cxxx-NCR-002142 and attached SRG notes 01/05/15 ), it was further discussed and agreed that CRL will arrange with Mayfair Exchange and provide with new contact details for weekend access as the contact received from the CRL CARL team does not respond and the restaurant is shut during the weekends. 02/05/2015: the System went offline. with the installed new router and UPS backup. No access was granted with the new given contact from CRL until 04/05/2015. had to hold off rear injections within the area and increase manual monitoring to avoid delaying the tunnel. further investigation couldn't pin point the fault as the incident only occurs during the weekend where access is not available. In the CTC 05/05/15 (see attached) the following were discussed and agreed actions to take; 1. __ to enquire from __ any known issues in the area: __ confirmed no known fault with the line and in the area, and also __ cannot guarantee a fault not occurring. 2. __ to investigate installing a programme to allow automatic reboots (at most 6hrs data will be lost). : __ are unable to install automatic reboot system and currently reviewing running a cable externally (without drilling through walls and locating the PC (which will be boxed up) onto a pole nearby. Although there is the risk of vandalism. 3. __ to look into locating the system externally (i.e. drilling through external walls to locate the PC ): this is less favourable mainly due to time constraints (on-going concurrent grouting and access is only available is just during week 8-5) and other unknown constraints i.e. vandalism of the system - this is no longer being reviewed. 4. CRL to agreed/guarantee contact will allow access should the above points fail. /__ have since located the PC externally, onto a nearby pole by running an external cable through the underside of the door (without drilling through walls). The will be box in onto the pole but risk being vandalised.
| 01CV - Civils | Cxxx-NCR-002173 | NCR | Amber Breach between B07LB307 – B07LB308 (__s front of 14 South Molton Lane) |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-06-03 | 2015-06-12 14:21 | 9 | 2015-05-14 17:55 | Geotechnical Engineering - Settlement | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | An Amber breach was reported between B07LB307 – B07LB308 (location, façade of 14 South Molton Lane). This point has been resurveyed and verified as an amber. (see attachment for location and plot) The façade of 14 South Molton Lane has been inspected and no visible cracks observed.
| 01CV - Civils | Cxxx-NCR-002174 | NCR | BOS Vent Tunnel - Damage to SGI Ring Coating |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-11-27 | 2015-12-10 09:36 | 13 | 2015-05-15 12:07 | Tunnelling - Linings - SGI Rings | 600000 |  | Damaged | Repair | 1 (>60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During Installation and Construction of the SGI segments, the Bondon coating has been damaged by the manoeuvring of the segments by hand tools and general construction activities. It is thought the extent of damage to the topcoat is largely due to the brittleness of the polysiloxane coating, as suggested by the manufacturer. Some smaller areas have noticeably had the intermediate layer chipped off exposing the primer. And a smaller amount again has had all 3 coats damaged, exposing the bare iron. During the development of a repair product, it became apparent the original paint work was not tested to comply with LU 1085.
| 01CV - Civils | Cxxx-NCR-002175 | NCR | TCR - Termination Boxes - Clashes with Cxxx works |  | Contr | BFK |  |  | 2015-06-01 | 2015-06-12 14:23 | 11 | 2015-05-18 19:33 | Tunnelling - Tunnelling General | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Whilst carrying out corbel works, Cxxx contractor have noticed clashes in eight different locations between Cxxx & Cxxx works. The clash verified is as follows: * have installed termination boxes for reinjectable grout tubes to overcome lap issues with the waterproofing membrane. The locations were agreed with CRL and Cxxx. * From these eight locations mentioned above and shown in the sketch attached, CRL/Cxxx have only provided a level to a box in AP4W; * The level provided by CRL/Cxxx is not in line with Cxxx design and is also generating a clash with the corbel; * The sketch attached is showing every box that is creating a potential clash with Cxxx works. It was confirmed on site that box number 8 is not a problem. CRL, and __ have carried out a joint inspection and have agreed a procedure to overcome the issues aforementioned.
| 01CV - Civils | Cxxx-NCR-002176 | NCR | Lack of concrete compressive strength cube results for CP2,CP3 and CP4 (RT). |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-06-19 | 2015-06-17 22:47 | -2 | 2015-05-20 09:36 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Lack of concrete compressive results for CP2,CP3 and CP4 running tunnels @ BOS.
| 01CV - Civils | Cxxx-NCR-002177 | NCR | BOS Vent Tunnel - Missing Foam Concrete Cube result |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-06-02 | 2015-06-03 18:53 | 1 | 2015-05-19 13:24 | Tunnelling - Linings - SGI Rings | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | A concrete cube sample was not taken for the final pour of foam concrete backfill of the Vent Tunnel 2/794.
| 01CV - Civils | Cxxx-NCR-002178 | NCR | BOS VD1B - Inspection Waterproofing |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-06-02 | 2015-06-03 18:56 | 1 | 2015-05-19 19:08 | Tunnelling - Tunnelling General | 2000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | The soffit pour on the Running tunnel collar and the side wall on the WTH collar in VD1B were presented for sign off to commence shuttering works. The areas weren't sign due to some visible fibres. The area was grouted and waterproofed again. The masterseal was sign off Please find attached the approvals of the waterproofing.
| 01CV - Civils | Cxxx-NCR-002179 | NCR | BOS S2 Adits : Spacing of Galvanised Mesh to Main Steel |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-09-30 | 2015-09-01 22:36 | -29 | 2015-05-20 22:00 | Tunnelling - Linings - In-situ Concrete | 5000 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The spacing between the galvanised B385 mesh and the main reinforcing bars in the Cxxx S2 adit piers is not in accordance with the design. While the spacing has not explicitly been specified, the cover is detailed as 75mm to main reinforcement and 25mm to mesh on drawing Cxxx-OVE-S-DDD-CR001_Z-43100 [C02], implying a spacing of 50 − 7 = 43mm. Specifically, on pier 5 (furthest east), there are localised areas on the inner (western) face where the mesh is touching the links. Corrective actions (if required) to be discussed with Cxxx.
| 01CV - Civils | Cxxx-NCR-002180 | NCR | VD1C - Final As Built out of Tolerance |  | Contr | BFK |  |  | 2015-08-24 | 2015-08-18 22:37 | -6 | 2015-05-20 17:43 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Fire proofing as-built profile out of designed tolerance for VD1C according with the RFI 1546 - CH 0-6.5 : Normal Sprayed Concrete - CH 6.5- 8 : Transition Sprayed Concrete to Cast Collar - (The transition area profile was not provided by designers) - CH 8 - 10 : Cast Collar
| 01CV - Civils | Cxxx-NCR-002181 | NCR | VD1A - Final As Built out of Tolerance |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-08-24 | 2015-08-18 22:40 | -6 | 2015-05-26 16:41 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Fire proofing as-built profile out of designed tolerance for VD1A according with the RFI 1546 - CH 0-2 : Normal Sprayed Concrete - CH 2- 3.5 : Transition Sprayed Concrete to Cast Collar - (The transition area profile was not provided by designers) - CH 3.5 -5.5 : Cast Collar
| 01CV - Civils | Cxxx-NCR-002182 | NCR | BOS WTH Level -5 GL 4/K-L slight damage to edge of slab |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-07-06 | 2015-07-06 07:48 | 0 | 2015-07-02 12:57 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | The edge of the slab has been slightly damaged at the change in level along GL 4/K-L in level -5 of the WTH. This damage has been caused during construction works from the WTH. This damage is superficial, see attached photographs. The damage is along the corner of the slab at intermittent intervals. The worst case is 100mm length perpendicular to gridline 4 and ranges from 0 to 60mm depth (see attached sketch). Along the slab the areas of damage vary in size.
| 01CV - Civils | Cxxx-NCR-002183 | NCR | BOS PTE- Final As Built out of Tolerance ch 218-220 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-06-10 | 2015-05-29 09:49 | -12 | 2015-05-27 19:24 | Tunnelling - Tunnelling General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Fire proofing as-built profile out of designed tolerance for PTE- chainages 218 to 220
| 01CV - Civils | Cxxx-NCR-002184 | NCR | BOS S2 Adits : Position of Pier 4 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-06-25 | 2015-06-23 17:41 | -2 | 2015-05-28 23:48 | Tunnelling - Linings - In-situ Concrete | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Regarding drawing Cxxx-OVE-C4-DDL-CR001_Z-21112 [C03], GA for the S2 adit piers. Following the invert pour, in order to maintain cover requirements to the reinforcement, pier 4 (labelled from west to east) has been moved 35mm to the west. The spacings between piers 3–4 and 4–5 are therefore 2265 and 1485mm respectively. While this will not have an impact on the overall area of the openings for ventilation, it will mean that the steel beams in the soffit detailed on Cxxx-OVE-S-DDD-CR001_Z-43110 [C02] and RFI 1525, and amended on RFI 1541, will have a slightly shorter embedment length.
| 01CV - Civils | Cxxx-NCR-002188 | NCR | BOS CP1 Waterproofing damage during headwall break through |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-08-06 | 2015-08-17 10:00 | 11 | 2015-06-01 10:00 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the break through of the CP1 temporary headwall small areas of masterseal have been damaged, see attached photographs. These areas are closer than 200mm to the sprayed secondary lining already in place, thus the minimum lap will not be achieved.
| 01CV - Civils | Cxxx-NCR-002189 | NCR | BOS CP2 Advance 3 face not sealed according to the RESS |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-06-24 | 2015-06-17 23:11 | -7 | 2015-06-01 10:32 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Advance 3 was excavated and sprayed to allow the installation of the parent child link bars, the face was sealed with a minimum 75mm of shotcrete. This was left for more than 12 hours. When and excavation is stopped for between 12 and 72 hours 150mm is required to be sprayed. When this was realised and the initial of Advance 4 was being sprayed an extra 75mm was sprayed onto the face of Advance 3.
| 01CV - Civils | Cxxx-NCR-002190 | NCR | BOS S2 Adits : Lapping of Bars in Invert |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-06-16 | 2015-06-20 11:54 | 4 | 2015-06-02 11:17 | Tunnelling - Linings - In-situ Concrete | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | For the Cxxx invert between piers 2 and 3 at S2 (numbered west to east), the B2 longitudinal bars do not lap correctly. Picture attached. While there is the correct number of bars, the bars are not in contact at the lap locations.
| 01CV - Civils | Cxxx-NCR-002191 | NCR | Lack of lap lenght of Masterseal at AP4W ch 31 |  | Contr | BFK |  |  | 2015-06-19 | 2015-06-19 12:19 | 0 | 2015-06-04 09:42 | Tunnelling - Tunnelling General | 5000 |  | Workmanship | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During inspection of waterproofing, it became apparent the waterproofing in AP4W at ch 31 invert been damaged close to the previously cast invert and minimum lap length of waterproofing cannot be achieved.
| 01CV - Civils | Cxxx-NCR-002192 | NCR | BOS S2 Adits : Damage to Cxxx Invert |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-09-30 | 2015-09-01 22:38 | -29 | 2015-06-03 09:21 | Tunnelling - Linings - In-situ Concrete | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | While breaking out the Dwall in the invert outside S2, the Cxxx invert slab was damaged between piers 3 and 4 (numbered west to east), exposing some of the mesh and T1 links.
| 01CV - Civils | Cxxx-NCR-002193 | NCR | CH2 advance 42, only 5 core results received rather than ITP stipulated 6. |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-06-18 | 2015-06-17 22:38 | -1 | 2015-06-04 11:18 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | CH2 advance 42, only results for 5 cores were received by @ BOS rathher than ITP stipulated 6 cores with reference to compressive strength.
| 01CV - Civils | Cxxx-NCR-002194 | NCR | BOS WTH: CH2 Cross Passage 1 - Muck inclusion at joint |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-06-18 | 2015-06-20 12:00 | 2 | 2015-06-04 12:33 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the construction of the last top heading and invert advance in CP1 partial muck inclusions remained within the advances due to the position of the CP1 headwall that was constructed from within the eastbound platform tunnel last year 2014. After the removal of the headwall it became more apparent that the joint between both sides was affected by the position of the headwall and the thickness of shotcrete is not sufficient
| 01CV - Civils | Cxxx-NCR-002195 | NCR | BOS WTH: CH2 Headwall Steel |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-07-30 | 2015-08-05 22:55 | 6 | 2015-06-04 12:50 | Tunnelling - Linings - Sprayed Concrete | 2500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the spraying of the headwall reinforcement to CH2 some 20mm steels were not completely covered with plain concrete, as a result the rebar was left exposed.
| 01CV - Civils | Cxxx-NCR-002196 | NCR | AP8- Final As builts out of tolerance |  | Contr | BFK |  |  | 2016-11-03 | 2017-03-12 15:14 | 129 | 2015-06-04 18:28 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As agreed on the meeting of the 11/03/15 (Find sign off attached and profiles) this NCR cover the fireproofing as-built profile out of designed tolerance for AP8. Please find attached the spreadsheet and profile showing that all the areas tighter than 50mm have been removed.
| 01CV - Civils | Cxxx-NCR-002197 | NCR | BOS CP2 Waterproofing damage during headwall break through |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-07-10 | 2015-07-21 11:58 | 11 | 2015-06-05 13:22 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the break through of the CP2 temporary headwall small areas of masterseal have been damaged. These areas are closer than 200mm to the sprayed secondary lining already in place, thus the minimum lap will not be achieved. A sweep was also installed in this area and during the spraying of CP2 some overspray covered the masterseal which was not cleaned off in time and thus the bolt hole repair will not achieved the required 200mm overlap.
| 01CV - Civils | Cxxx-NCR-002198 | NCR | BOS S2 Adits : Cover to Rebar and Spacing to Mesh in Cxxx Piers |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-07-01 | 2015-07-03 18:00 | 2 | 2015-06-17 23:07 | Tunnelling - Linings - In-situ Concrete | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The cover to the main reinforcement and galvanised mesh in the Cxxx piers is not as per the design, which called for 25mm cover to the mesh and 75mm to the main reinforcement. The attached survey was carried out and agreed on site between __ () and __ (Cxxx) on 01/06/2015, based on the bars/mesh visible at the top of the piers.
| 01CV - Civils | Cxxx-NCR-002199 | NCR | BOS S2 Adits : Lintel Beam Notch |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-06-30 | 2015-07-03 17:53 | 3 | 2015-06-16 21:26 | Tunnelling - Linings - In-situ Concrete | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The 32mm __ __ B-series shear bolt couplers were too close together to fit the 305 × 102 × 33 UB lintel beams in the soffit of pier 5 (labelled west to east) of the BOS S2 adits. The clear spacing between the barrels of the couplers was approximately 85–90mm.
| 01CV - Civils | Cxxx-NCR-002200 | NCR | AP2A - Final As Built out of Tolerance |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-06-23 | 2015-06-18 14:53 | -5 | 2015-06-09 11:37 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Workmanship | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Fire proofing as-built profile out of designed tolerance for AP2A.Final profiles attached.
| 01CV - Civils | Cxxx-NCR-002201 | NCR | VD1A & B connection to the SGI ring leaks |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-08-12 | 2015-08-17 21:55 | 5 | 2015-06-16 13:52 | Tunnelling - Linings - In-situ Concrete | 1000 |  | System Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Several small damp patches have been found in VD1 A & B tunnels in the collar connecting to the SGI tunnel.
| 01CV - Civils | Cxxx-NCR-002202 | NCR | Bond St WTH: CH2 Curing of Invert |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-07-29 | 2015-07-28 22:47 | -1 | 2015-06-12 14:52 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Once the concrete was sprayed to the thickening layer in CH2 (chainage 32 - 48m Invert) the lining was not correctly cured as per the ITP requirement. Before spraying regulating a longitudinal crack was observed. Full investigation of the crack was done : 3 core taken ( core logs attached) the crack extends no further than the thickening, crack was injected, further monitoring readings were taken and the approval to regulate signed.
| 01CV - Civils | Cxxx-NCR-002203 | NCR | BOS - CP3&4 tunnels. Damaged overlap in masterseal |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-09-08 | 2015-09-07 14:27 | -1 | 2015-08-25 14:40 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Contamination | Completed |  | Small areas of masterseal were damaged near the sweep in CP3-CP4 tunnels. These areas were closer than 200mm to the sprayed secondary lining already in place, thus the minimum lap was not achieved. to install TAM pipe in the area, around the circunference of the tunnel.
| 01CV - Civils | Cxxx-NCR-002204 | NCR | BOS - quality core grading failed in CP3-CH2 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-09-10 | 2015-09-17 15:35 | 7 | 2015-06-19 16:40 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Quality core grading failed in CP3-CH2. Average over 2.5 (3, 3, 3. Av 2.66)
| 01CV - Civils | Cxxx-NCR-002205 | NCR | South Molton Lane between B07LP142 – B07LP144 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-07-06 | 2015-07-08 22:25 | 2 | 2015-06-22 09:56 | Geotechnical Engineering - Settlement | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | An Amber breach was reported between B07LP142 and B07LP144 (along South Molton Lane). The points have been resurveyed and verified as an amber breach. The street have been inspected and no noticeable/visible cracks observed.
| 01CV - Civils | Cxxx-NCR-002206 | NCR | South Molton Lane between B07LB356 – B07LB357 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-07-06 | 2015-07-10 14:15 | 4 | 2015-06-22 09:59 | Geotechnical Engineering - Settlement | 15000 |  | Design | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | An Amber breach was reported between B07LB356 – B07LB357 (58 Davies Street - South Molton Lane facade). The points have been resurveyed and verified as an amber breach. Cracks have previously been reported in the building (see attached Cxxx's report).
| 01CV - Civils | Cxxx-NCR-002207 | NCR | No daily monitoring reading on 15-6-15 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-08-12 | 2015-08-17 14:45 | 5 | 2015-06-19 16:44 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Monitoring points were removed in a section od CH2 (between CP3-4 and headwall) to allow regulating the area. As a result no monitoring took place on 15/6/15. The monitoring poinits were replaced and monitoring continued the following date.
| 01CV - Civils | Cxxx-NCR-002208 | NCR | WTH BOS damaged slab in -5 level of the box repaired without CRL cagreement |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-08-07 | 2015-08-05 23:17 | -2 | 2015-06-17 19:11 | Civil - Demolition/Site Clearance | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | The slab in level -5 of BOS WTH was damaged and proceeded to repair it following the activity plan in place but without a joint inspection / CRL / Cxxx.
| 01CV - Civils | Cxxx-NCR-002209 | NCR | TCR- Tunnel connection water ingress |  | Contr | BFK |  |  | 2015-08-21 | 2015-09-02 13:15 | 12 | 2015-06-21 14:40 | Tunnelling - Tunnelling General | 2000 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The connection between the westbound running tunnel and the Platform Tunnel East headwall shows signs of water ingress. Similar conditions can be observed at the connection between the Goslett Yard Box and VEW
| 01CV - Civils | Cxxx-NCR-002210 | NCR | Lack of overlap in CP1 and CP2 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-07-06 | 2015-07-08 22:35 | 2 | 2015-06-22 12:32 | Tunnelling - Tunnelling General | 5000 |  | Workmanship | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | While spraying regulating on CH2 at CP1 and CP2 there was an accidental overspray and as a result the Masterseal was oversprayed and lost the overlap in some places. immediately cleaned the surface
| 01CV - Civils | Cxxx-NCR-002211 | NCR | BOS SCL Lack of wet film tests PTW 4b |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-10-10 | 2015-10-21 22:25 | 11 | 2015-06-22 17:10 | Tunnelling - Linings - Sprayed Concrete | 10000 |  | Supervision/Management | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Lack of wet film tests in PTW 4b area as per the ITP Item B3.5 not completely fulfilled. Check sheet -089 attached Ch238 to headwall
| 01CV - Civils | Cxxx-NCR-002212 | NCR | BOS CP2 Fireproofing hollow sounding areas |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-09-24 | 2015-09-24 16:37 | 0 | 2015-06-23 13:56 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Systematic hammer testing of CP2 fireproofing (20/06/2015) detected 3 hollow sounding areas. See attached hammer test sheet. These areas are all below the next stage foam concrete fill. The level of the foam concrete infill and SSL which is 98.125m. See Cxxx-__-A-DDC-Cxxx-23300 and Cxxx-ATK-A-DDD-CR001_Z-33102. Area 1: 400mm x 400mm, Ch 8.79, Level 97.390m Area 2: 400mm x 400mm, Ch 9.97, Level 97.649m Area 3: 400mm x 400mm, Ch 17.36, Level 97.955m
| 01CV - Civils | Cxxx-NCR-002213 | NCR | BOS S2 Adits : Channel Drains |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-08-20 | 2015-09-01 16:19 | 12 | 2015-06-25 01:03 | Structural Engineering - Concrete Member | 2000 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 1. Drawing Cxxx-OVE-C4-DDL-CR001_Z-21116 [C01] shows drains in the invert, falling towards the track. These were not formed during the invert pour. As noted in Cxxx-RFI-001586, there are concerns that these drains would reduce cover to the mesh and reinforcement, and clash with the chamfers of the SGI segments. 2. Drawing Cxxx-OVE-C4-DDL-CR001_Z-21116 [C01] also shows notches for a foam backing rod. These notches were not formed in the Cxxx piers.
| 01CV - Civils | Cxxx-NCR-002214 | NCR | BOS S2 Adits : Position of Dwall Breakout on West Side |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-09-30 | 2015-09-01 22:44 | -29 | 2015-06-25 01:31 | Structural Engineering - Diaphragm Walls | 5000 |  | Planning | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Drawing Cxxx-OVE-C4-DDL-CR001_Z-21112 [C03] shows a 250mm thick wall of concrete in the plane of the Dwall (west side of S2), cast as part of the lining walls. This is also implied on drawings in “DDN Cxxx - Adit S2 Reinf - Reinforcement Details and Bar Schedule” issued on PMI 1773. In order to facilitate construction of the S2 adits and access into the eastbound running tunnel, have stitch drilled and broken out the Dwall a further 250mm wider than this on the LHS (west) only, so that the resulting wall here will be approximately 500mm thick in the plane of the Dwall. submitted a proposal for this in Cxxx-FCD-001225, which also forms a proposed corrective action for this NCR. propose to amend the reinforcement design suggested in “DDN Cxxx - Adit S2 Reinf - Reinforcement Details and Bar Schedule” to include two rows of vertical bars with horizontal straight and U-bars (together with horizontal L-bar dowels into the Dwall) — see attached sketch. A row of dowels into the invert and soffit (bar marks 20 and 22 respectively) would be included on all faces, as per DDN Cxxx. A similar detail has already been suggested by Cxxx in “DDN W05 - S2 Adit Horiz Reinf”, issued on PMI 1759 in response to RFIs 1518 and 1585.
| 01CV - Civils | Cxxx-NCR-002215 | NCR | AP7B Final profile out of tolerance |  | Contr | BFK |  |  | 2015-07-29 | 2015-07-28 22:50 | -1 | 2015-07-01 12:03 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Fire proofing as-built profile out of designed tolerance for AP7b
| 01CV - Civils | Cxxx-NCR-002216 | NCR | BOS CP4 Localised secondary lining under thickness |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-07-23 | 2015-07-23 22:35 | 0 | 2015-06-29 11:40 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | CP4 Chainage 18 to 19 there is an area where the seconndary SFR lining is less than 200mm (minimum 140mm). Mesh was installed in this area and the thickness made up with Mix 21 as per the agreed procedure. See attached sketch and profiles.
| 01CV - Civils | Cxxx-NCR-002217 | NCR | Lack of overlap CP3 & CP4 Invert |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-08-06 | 2015-07-29 10:51 | -8 | 2015-06-29 16:01 | Tunnelling - Tunnelling General | 5000 |  | Workmanship | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During inspection of waterproofing, it became apparent the waterproofing in some areas at CP4 and CP3 between has been damaged close to the cast invert and minimum lap length of waterproofing cannot be achieved. (photos and check sheet attached)
| 01CV - Civils | Cxxx-NCR-002218 | NCR | Missing Hammer Test Checksheet for CH3 Secondary Lining Ch.227-230 |  | Contr | BFK |  |  | 2015-07-14 | 2015-07-09 14:24 | -5 | 2015-06-30 17:42 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Missing hammer test checksheet for TCR CH3 ch. 227-230
| 01CV - Civils | Cxxx-NCR-002219 | NCR | Drilling formwork anchor into Cxxx permanent works |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2015-08-21 | 2015-09-01 20:51 | 11 | 2015-07-02 14:19 | Civil - Structural Engineering | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The temporary works formwork consisted of anchors and props for casting the Cxxx soffit. The anchors were drilled and fixed into the Cxxx columns without approval from Cxxx.
| 01CV - Civils | Cxxx-NCR-002220 | NCR | AP2A- Contraction Joint with WTH |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-07-17 | 2015-07-09 22:17 | -8 | 2015-07-03 16:50 | Tunnelling - Tunnelling General | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | understanding of Cxxx drawing for AP2A connection meant that a crack inducer needs to be installed in the invert and in the soffit as per DWG- Cxxx-MMD-C4-DDL-Cxxx_Z-00630. As per RFI 1549 cut the soffit and installed the crack inducer in the invert even though believes it was not required as per RFI 1388. Due to the method of construction the collar was cast and the tunnel sprayed which creates a natural contraction joint. There is also ambiguity between DWG - Cxxx-MMD-C4-DDL-Cxxx_Z-00630 and Cxxx-MMD-C4-DDA-Cxxx_6-00100 which shows different detail of extend of crack inducer/detail. In order to facilitate AP2A handover proceed with Cxxx request of saw cutting full circle in the Secondary Lining Meeting, however this cut is not aligned in the right hand side at axis level ( 40 mm difference) as per picture attached .The intention of this misalignment was to follow the cast collar in order to create the crack to appear where the injection tubes are. Please find attached the profile of cut followed.
| 01CV - Civils | Cxxx-NCR-002221 | NCR | AP1- Lack of waterproofing overlap |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-08-13 | 2015-08-17 13:37 | 4 | 2015-07-08 13:00 | Tunnelling - Tunnelling General | 5000 |  | Workmanship | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During inspection of waterproofing, it became apparent the waterproofing in some minor areas in AP1 ch 51-68 has been damaged close to the cast invert and minimum lap length requested of 200mm of waterproofing cannot be achieved.
| 01CV - Civils | Cxxx-NCR-002222 | NCR | S2 - Foam encapsulation in top adit pour. |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2015-08-28 | 2015-09-01 21:10 | 4 | 2015-07-10 02:11 | Tunnelling - Linings - In-situ Concrete | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Expanding foam was used during the top pour of S2 adit to seal the joint between the base shuttering and the D-wall. Some foam can be seen to have been encapsulated in the pour.
| 01CV - Civils | Cxxx-NCR-002224 | NCR | S2 - Inadequate steel reinforcement embedment depth |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2015-08-31 | 2015-09-01 21:03 | 1 | 2015-07-11 03:11 | Tunnelling - Linings - In-situ Concrete | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The embedment depth of all bars 52 and 53 installed in columns 2 and 3 of the lining wall are shy 20-40mm of the design embedment of 350mm.
| 01CV - Civils | Cxxx-NCR-002225 | NCR | BOS - lack of masterseal overlap CH2 to CP3&4 |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2015-08-10 | 2015-08-17 14:54 | 7 | 2015-07-13 12:01 | Tunnelling - Tunnelling General | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | While spraying regulating on CH2 leading up to the junction areas in CP3 and CP4 there was an overspray onto the masterseal up to the already sprayed secondary lining of both CP3 & CP4. As such masterseal overlap between CH2 and CP3&4 cannot be achieved due to the contamination and overspray of the masterseal that was left exposed at the junction of CP3&Cp4.
| 01CV - Civils | Cxxx-NCR-002226 | NCR | BOS WTH box walkover inspection to list concrete repairs for staged handover |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-07-28 | 2015-08-05 22:46 | 8 | 2015-07-14 16:26 | Civil - Civil Engineering General | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | BOS WTH box walkover inspection to list concrete repairs in multiple locations on level -5 for staged handover to follow-on Contractor. See attached list of items to see proposed repair
| 01CV - Civils | Cxxx-NCR-002227 | NCR | BOS LUL Ventilation Tunnel Diversion - Concrete repairs in dropshaft |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-09-21 | 2015-09-20 21:12 | -1 | 2015-09-03 09:04 | Tunnelling - Linings - SGI Rings | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | This NCR has been raised to cover repair to the concrete finish and removing cast in items from the construction process which need to be cut back and made good. This also includes a small section of under filled shutter above the first ring, this pocket is approximately 500mm x 300mm x 300mm wedge in size. These are proposed to be rectified using the approved concrete repair procedure. Cxxx--C4-STP-CRT00_ST005-50555 referenced below.
| 01CV - Civils | Cxxx-NCR-002228 | NCR | BOS S2 Lining Walls : Reduced Cover (Column 1) |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-09-30 | 2015-09-01 22:28 | -29 | 2015-07-15 13:13 | Structural Engineering - Reinforcement | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Regarding the reinforcement in the westernmost column of the S2 lining walls (drawings issued via CCM 10710), 2No links (bar mark 27) at the top of of the column have 35mm cover rather than the specified 50mm. Refer to sketch attached.
| 01CV - Civils | Cxxx-NCR-002229 | NCR | BOS- CH2 tunnel. Lack of overlap in the masterseal CH29 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-08-14 | 2015-08-18 21:52 | 4 | 2015-07-31 14:31 | Tunnelling - Tunnelling General | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During removal of the stop end, it became apparent the waterproofing in CH2 at ch 29 invert been damaged close to the previously cast invert and minimum lap length of waterproofing cannot be achieved.
| 01CV - Civils | Cxxx-NCR-002230 | NCR | BOS - AP1 tunnel. Lack of lap in the Masterseal CH25 to 32 RHS |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-08-31 | 2015-09-01 21:37 | 1 | 2015-08-17 18:48 | Tunnelling - Tunnelling General | 5000 |  | Damaged | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Plant tracked on the masterseal and lap of masterseal was compromised. The area was repaired and a line of __ was installed.
| 01CV - Civils | Cxxx-NCR-002231 | NCR | BOS S2 Lining Walls : Chamfers to Columns |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-08-03 | 2015-08-05 22:58 | 2 | 2015-07-20 19:41 | Structural Engineering - Concrete Member | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | KF10.3223(l)(ii) specifies that ’arrises‘ of cast in situ concrete should have 20 × 20mm chamfers. Chamfers were not installed on the vertical sides/edges of the S2 lining wall columns.
| 01CV - Civils | Cxxx-NCR-002232 | NCR | BOS AP1 invert slab repair chainage 50 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-08-28 | 2015-08-23 22:38 | -5 | 2015-07-21 14:07 | Tunnelling - Linings - In-situ Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After striking of the closed invert shutters in the rest area of AP1 an area required repairing. This was done imediately but prior to inspection with Cxxx and CRL. The area was repaired using the Cxxx--C4-STP-CRT00_ST005-50555 Activity Plan Concrete repair procedure.
| 01CV - Civils | Cxxx-NCR-002233 | NCR | BOS LUL Ventilation Tunnel Diversion - Loss of four signed original RESS sheet records |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-09-17 | 2015-09-16 17:08 | -1 | 2015-09-03 10:19 | Tunnelling - Linings - SGI Rings | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | operated a RESS/ SRG meeting minutes record for the Handworks excavation of the LUL Ventilation Tunnel Diversion Since completion of the works the signed ( + CRL) RESS/ SRG minutes for the LUL Ventilation Tunnel have been lost for the following dates: -VT034 05.04.15 -VT035 06.04.15 -VT047 18.04.15 -VT088 27.05.15 The RESS/SRG meetings were all completed as per the agreed process at the time and covered the 24hr period of construction for which they were intended, they were naturally superseded each 24hrs. These records have been since been lost before the final collation of the ITP documents. All other records are available on eB Cxxx--C4-MRC-CRT00_ST005-50539 - BOS LUL Ventilation Tunnel Handworks RESS/ SRG meeting minutes
| 01CV - Civils | Cxxx-NCR-002234 | NCR | AP1 - Lack of overlap dywidags |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-09-10 | 2015-09-10 20:59 | 0 | 2015-07-24 18:14 | Tunnelling - Tunnelling General | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After pouring the side walls in AP1 from ch 0 to 3.5 it has become apparent that there is a lack of waterproofing overlap to the dywidags as the pour accidentally reach a level slightly higher than expected.
| 01CV - Civils | Cxxx-NCR-002235 | NCR | VD1A & C - Incorrect installation of tam tube |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-08-07 | 2015-07-30 13:30 | -8 | 2015-07-24 19:00 | Tunnelling - Tunnelling General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Tam tubes in the WTH collars of VD1A and VD1C were not installed 100mm from the lining face as per drawings Cxxx-MMD-C4-DDL-Cxxx_Z-00600 and Cxxx-MMD-C4-DDL-Cxxx_Z-00602.(Photos attached).
| 01CV - Civils | Cxxx-NCR-002236 | NCR | VD1B - Final As Built out of Tolerance |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-08-11 | 2015-08-17 13:48 | 6 | 2015-07-28 14:21 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Fire proofing as-built profile out of designed tolerance for VD1B according with the RFI 1546 - CH 0-4.4 : Normal Sprayed Concrete - CH 4.4- 5.9 : Transition Sprayed Concrete to Cast Collar - (The transition area profile was not provided by designers) - CH 5.9 - 7 : Cast Collar
| 01CV - Civils | Cxxx-NCR-002237 | NCR | AP1- FF Steel not sign off |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-08-17 | 2015-08-17 22:33 | 0 | 2015-08-03 13:42 | Tunnelling - Tunnelling General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | In AP1 ch 58- 61, failed to follow the ITP as the FF steel was not sign off by CRL and Cxxx representatives. Please find attached pictures of the installation of the steel and the checksheet.
| 01CV - Civils | Cxxx-NCR-002238 | NCR | TCR- Oversprayed Profile PTE & PTW |  | Contr | BFK |  |  | 2015-08-26 | 2015-09-20 21:17 | 25 | 2015-08-03 18:58 | Tunnelling - Linings - Sprayed Concrete | 10000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Previous NCR's were raised and closed for final profile out of tolerance with the acknowledge that some localized rework may be necessary. NCR 2041 - PTE Final As Built Profile NCR 2077- PTW Final As Built Profile The areas that need rework has been discuss and agreed with Cxxx, this NCR is as a mechanize to record and formalize the agreed areas ( Spreadsheet attached)
| 01CV - Civils | Cxxx-NCR-002239 | NCR | BOS - Oversprayed Profile PTE & PTW |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-10-15 | 2017-10-05 16:09 | 721 | 2015-08-03 19:40 | Tunnelling - Linings - Sprayed Concrete | 10000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Previous NCR's were raised and closed for final profile out of tolerance with the acknowledge that some localized rework may be necessary. NCR - 2148/2183 PTE Final As Built Profile NCR - 2065 PTW Final As Built Profile The areas that need rework has been discuss and agreed with Cxxx, this NCR is as a mechanize to record and formalize the agreed areas ( Spreadsheet attached) Please note that there will be 2 areas that will end up with localized fireproofing underthickness. PTE side bracket ch 91-91.5 PTE top bracket ch 90.2-90.6
| 01CV - Civils | Cxxx-NCR-002240 | NCR | BOS CH2 - Lack of lap overlap waterproofing invert |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-08-24 | 2015-08-23 22:29 | -1 | 2015-08-06 20:52 | Tunnelling - Tunnelling General | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During inspection of waterproofing, it became apparent the waterproofing in CH2 at ch 15 invert been damaged close to the previously cast invert and minimum lap length of waterproofing cannot be achieved.
| 01CV - Civils | Cxxx-NCR-002241 | NCR | TCR CH3 Invert with junctions out of tolerances |  | Contr | BFK |  |  | 2015-08-31 | 2015-09-01 21:06 | 1 | 2015-08-13 14:12 | Tunnelling - Linings - In-situ Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After reviewing the profiles it has became apparent that the invert cast between CH3 and AP4E/AP3E is tight. Please find attached scans for ap4e and eupalinos as builts for AP3E. Note that the tight area in AP3E/W section is an access ramp.
| 01CV - Civils | Cxxx-NCR-002242 | NCR | AP1- Secondary Lining Contraction Joints not cut |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-09-20 | 2015-09-24 16:40 | 4 | 2015-08-06 20:37 | Tunnelling - Tunnelling General | 5000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | did not cut secondary lining contraction joint at AP1 ch.57 and 67.5 as required per design and Cxxx-FCD-001156. None of the secondary lining joints were cut prior the concrete strength of 20N/mm2.
| 01CV - Civils | Cxxx-NCR-002243 | NCR | BOS CH2 CP1 and CP2 Junction Masterseal Bond Strength |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-10-08 | 2015-11-02 10:06 | 25 | 2015-08-06 20:25 | Tunnelling - Linings - Sprayed Concrete | 10000 |  | Material | Use As-Is | 2 (6-60k) | Complete | Material/Preservation Problems - Other | Completed |  | were requested to undertake pull off tests to investigate the bond between Masterseal layers in localised areas at the CP1 and CP2 junctions. Although this is not part of the ITP or the KW20 to carry this out in situ this test was carried out. These additional tests were requested by Cxxx because they raised queries regarding the cleanliness of the first Masterseal layer prior to the application of the second Masterseal layer. consider that this testing is un-necessary because the substrate was clean and inspected prior to application of the second layer of Masterseal. However, in order to help resolve this issue, agreed to carry out the additional insitu pull-off tests. The required bond for Masterseal to the substrate is 0.5MPa as per KW20.1302 and Table KW20-03, and Cxxx have stated that they assume that this bond strength also exists for Masterseal to Masterseal layers. However, it should be noted that the test method for this bond (as per KW20) is on a horizontal flat test panel using a sandwich of shotcrete layers and waterproofing, rather than insitu testing of the exposed Masterseal on a vertical or near-vertical curved surface. Any results from the tests below are therefore not directly comparable with the KW20 bond strength requirements, but may an indication of quality of the surface preparation of the first Masterseal layer. All pull off tests were witnessed by Cxxx.
| 01CV - Civils | Cxxx-NCR-002244 | NCR | AP1- Lack of lap length in mesh reinforcement installation |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-09-08 | 2015-09-01 15:52 | -7 | 2015-08-25 19:51 | Tunnelling - Tunnelling General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | According to the Dwg Cxxx- MMD-C4-DDD-Cxxx_5-00048 the reinforcement detail for the FF of AP1 with vent tunnel connection is a combination of A252 mesh with 10mm longitudinal and 16 mm vertical bars. As shown in the pictures attached didn't achieved the longitudinal lap of the mesh in the two bottom bars. However as per previously approved FCD, which allows to spray SFR over reinforcement up to 16mm diameter bars, the reinforcement area was sprayed with SFR.
| 01CV - Civils | Cxxx-NCR-002245 | NCR | Lack of SCL Early Age Strength testing carried out @ BOS from April to August 2015, plus in April 2015 587.5m3 of mix17.2 delivered, thus 11.75 sets of compressive test needed but only 10 was carried out @ BOS. |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-08-28 | 2015-08-19 18:35 | -9 | 2015-08-07 12:10 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | At BOS during the months of April to beginning of August 2015, there was a lack of testing performed/recorded with reference to SCL Early Age Strength of SCL, which is contrary to ITP, plus in the month of April 2015, 587.5m3 of Mix 17.2 was delivered, thus requiring 11.75 sets, however only 10 was performed.
| 01CV - Civils | Cxxx-NCR-002246 | NCR | Lack of Washouts for Mix 29 carried out from April to August 2015. |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-08-28 | 2015-08-19 18:36 | -9 | 2015-08-07 12:46 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Software | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Lack of washouts for mix 29 as stipulated by ITP. @ BOS performed monthly washouts on mix 29 rather than 3 times weekly.
| 01CV - Civils | Cxxx-NCR-002247 | NCR | BOS - VD1C Cast Invert out of tolerance |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-08-25 | 2015-08-23 22:03 | -2 | 2015-08-11 13:58 | Tunnelling - Linings - In-situ Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | VD1C cast invert U1 finish (0-20mm tolerance) is out of specifications due to an inappropriate leveled. This NCR it is not complaint with the ITP Cxxx--C4-ITP-CRT00_ST005-50144 - BOS TCR CP Cast-in situ and Sprayed Secondary Lining section B4.10 and the general note G36 from the drawing Cxxx-MMD-C4-DDJ-N105-00001 reference below. According with the RFI 1546 find attached the agreed levels and the levels taken at those chainages.
| 01CV - Civils | Cxxx-NCR-002248 | NCR | BOS VD1B - Cast Invert Out of tolerance |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-08-25 | 2015-08-23 22:06 | -2 | 2015-08-11 14:17 | Tunnelling - Linings - In-situ Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | VD1B cast invert U1 finish (0-20mm tolerance) is out of specifications due to an inappropriate leveled. This NCR it is not complaint with the ITP Cxxx--C4-ITP-CRT00_ST005-50144 - BOS TCR CP Cast-in situ and Sprayed Secondary Lining section B4.10 and the general note G36 from the drawing Cxxx-MMD-C4-DDJ-N105-00001 reference below. According with the RFI 1589 find attached the agreed levels and the levels taken at those chainages.
| 01CV - Civils | Cxxx-NCR-002249 | NCR | BOS VD1A - Cast Invert out of Tolerance |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-08-25 | 2015-08-23 22:21 | -2 | 2015-08-11 14:27 | Tunnelling - Linings - In-situ Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | VD1A cast invert U1 finish (0-20mm tolerance) is out of specifications due to an inappropriate leveled. This NCR it is not complaint with the ITP Cxxx--C4-ITP-CRT00_ST005-50144 - BOS TCR CP Cast-in situ and Sprayed Secondary Lining section B4.10 and the general note G36 from the drawing Cxxx-MMD-C4-DDJ-N105-00001 reference below. According with the FCD 1106 find attached the agreed levels and the levels taken at those chainages.
| 01CV - Civils | Cxxx-NCR-002251 | NCR | BOS CH2- Waterproofing Issues ch 4 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-08-31 | 2015-08-23 22:47 | -8 | 2015-08-17 19:11 | Tunnelling - Tunnelling General | 5000 |  | Workmanship | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the spraying of the secondary lining in CH2 ch 4 there has been some over spray on the un inspected masterseal. This area at chainage 4 on the right hand side below axis was therefore un able to be inspected prior to spraying secondary lining. Furthermore it became apparent the waterproofing at the same chainage in the invert been damaged close to the previously cast invert and minimum lap length of waterproofing cannot be achieved. Prior to spraying however the area was looked at and it was dry. See attached approval of masterseal checksheet and also signed sheet showing the area was dry. Also install re-injectable tam tube installed along all the profile
| 01CV - Civils | Cxxx-NCR-002252 | NCR | BOS AP1- Lack of waterproofing overlap dwall connection |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-08-30 | 2015-09-01 21:12 | 2 | 2015-08-16 15:34 | Tunnelling - Tunnelling General | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After striking the shutter on the secondary lining cast side walls around AP1 D-Wall connection, it was discovered that there are areas of damage to the Masterseal on the Right Hand side. At 4 o'clock there are small damage which when repaired will not have the required 200mm overlap.
| 01CV - Civils | Cxxx-NCR-002253 | NCR | BOS AP1 - Side Wall Hole |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-08-31 | 2015-09-02 13:17 | 2 | 2015-08-17 13:21 | Tunnelling - Tunnelling General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After striking the side wall shutters of the LHS ch 34, it became apparent that there is a hole in the cast side wall.
| 01CV - Civils | Cxxx-NCR-002254 | NCR | BOS AP1 - Final As Built out of Tolerance ch |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-09-01 | 2015-09-01 21:17 | 0 | 2015-08-18 15:18 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Fire proofing as-built profile out of designed tolerance for Ap1- chainages 165 to 168 Please note the tight spots more than -50 in the scans it was rebound. Find attached scans and eupalinos asbuilt of the tight area showing is less than -50tight.
| 01CV - Civils | Cxxx-NCR-002255 | NCR | 1 set of cores crushed @ 4 days,plus 2 sets with only 2 cores @ 1 day compressive strength |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-09-02 | 2015-09-01 21:39 | -1 | 2015-08-19 17:40 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the Month of June , one set of cores was crushed at four days instead of within the window of 1 to 3 days including two sets of cores having only 2 core results rather than ITP stipulated 6 cores.
| 01CV - Civils | Cxxx-NCR-002256 | NCR | BOS LUL Ventilation Tunnel Diversion - Dropshaft invert concrete sample not achieving 28 day strength |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-09-10 | 2015-09-16 17:02 | 6 | 2015-08-21 10:29 | Tunnelling - Linings - SGI Rings | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The cube strength sample taken for the Dropshaft Invert slab (SSL) has failed to meet the expected 28 day result of 40N/mm2. Records indicate the time between concrete batching and cube samples being made by 's testing supplier may have affected the validity of the sample.
| 01CV - Civils | Cxxx-NCR-002257 | NCR | BOS CH2- Milling without approval |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-09-14 | 2015-09-16 17:03 | 2 | 2015-08-31 13:43 | Tunnelling - Tunnelling General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | During milling operations in CH2 there was an area that was milled without an approval to mill in place. The extend of the area is around 1m2 between ch 1 and 2 at axis level. Please find attached profiles showing the required thickness is still remaining.
| 01CV - Civils | Cxxx-NCR-002258 | NCR | At BOS for the months of June and July 2015, 22 sets of compressive results was required for mix 17.2 howver only 16 sets was done plus in June 1 set of cores was crushed @ 4 days rather than ITP stipulated 1 to 3 days. |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-09-07 | 2015-09-01 21:58 | -6 | 2015-08-24 13:34 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | @ BOS carried out testing on 16 sets only on mix 17.2 with regards to compressive strength rather than ITP stipulated 22 sets, thus is 6 sets lacking for the months of June and July 2015; also for the month of June for mix C20.0, 1 set was crushed @ 4 days rather than 1 to 3 days.
| 01CV - Civils | Cxxx-NCR-002259 | NCR | BOS ES1- Lack of waterproofing overlap ch.4 (Invert) |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-09-08 | 2015-09-09 11:41 | 1 | 2015-08-25 13:52 | Tunnelling - Tunnelling General | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | While spraying secondary lining on ES1 there was an overspray onto the masterseal although masterseal was protected with polythene plastic. As such masterseal overlap at ch 4 invert area cannot be achieved due to the contamination and overspray of the masterseal.
| 01CV - Civils | Cxxx-NCR-002260 | NCR | BOS AP1- WP Remedial works not signed ch 41-46 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-09-08 | 2015-09-02 11:11 | -6 | 2015-08-25 20:34 | Tunnelling - Tunnelling General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | The waterproofing in the flare area was approved from ch 50 to 35, while preparing for spraying the bays from ch 46 to 41 became aware that there were some damages. repaired them to a satisfactory level and those repairs were witnessed by CRL and Cxxx (photos provided by Cxxx) however another check sheet was not signed.
| 01CV - Civils | Cxxx-NCR-002261 | NCR | BOS WTH Mole Hole 3 blockwork damage |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-09-24 | 2015-09-24 16:50 | 0 | 2015-09-09 01:02 | Structural Engineering - Load Bearing Walls | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Due to lifting operations up and down Mole Hole 3 at the WTH GL J-K/2-3 the block work has been damage, see attached PDF BOS WTH Level -3 Blockwork damage at mole hole.
| 01CV - Civils | Cxxx-NCR-002262 | NCR | BOS WTH Mole Hole 3 concrete damage |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-09-24 | 2015-09-28 16:49 | 4 | 2015-09-17 14:42 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Due to lifting operations up and down Mole Hole 3 at the WTH GL J-K/2-3 the concrete in this area has been damaged, see attached PDF.
| 01CV - Civils | Cxxx-NCR-002264 | NCR | BOS ES1: Hand application of topshop applied by Masterseal accredited sprayer |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-09-17 | 2015-09-20 21:20 | 3 | 2015-08-27 15:30 | Tunnelling - Tunnelling General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Training Deficiency - No training provided | Completed |  | ES1 invert has been hand sprayed with topshop by a Masterseal accredited sprayer, non accredited for spraying permanent works. As agreed by CRL/Cxxx/ the quality of the regulating layer was up to satisfactory standards.
| 01CV - Civils | Cxxx-NCR-002265 | NCR | BOS S2 Adits : Possible Cold Joint in Soffit |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-09-12 | 2015-09-04 15:48 | -8 | 2015-08-29 16:01 | Tunnelling - Linings - In-situ Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After striking the soffit shutter to the Cxxx collar, a line on the concrete was visible, which could be a cold joint.
| 01CV - Civils | Cxxx-NCR-002266 | NCR | BOS CH2 - Hollow sounding patches |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-09-23 | 2015-09-24 16:53 | 1 | 2015-09-10 11:49 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Systematic hammer testing of CH2 fireproofing CH0-48 (31/7/2015) detected one area of de-bonded fireproofing. See attached hammer test sheets. Area 1: Ch 48 ,RHS Headwall, 590X820 Lamination Area 2: Ch 38, 820X430 Junction with CP3 Area 3: Ch 19, 800x400 Junction with CP1 Area 4 : Ch 12 1000x1000, 5 o'clock These areas are all below the next stage foam concrete fill. The level of the foam concrete infill and SSL which is 98.150m. See Cxxx-__-S-DDB-Cxxx-14309. Please find attached final hammer test records showing sound bond.
| 01CV - Civils | Cxxx-NCR-002267 | NCR | BOS ES1- Dywidags installation |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-09-18 | 2015-09-24 16:55 | 6 | 2015-09-03 17:33 | Tunnelling - Tunnelling General | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Some dowels were installed through the protection layer in the invert chainage 4, with no guaranties that they were not installed trough the Masterseal layer underneath, so the waterproofing can be by now compromised. It was agreed on site Cxxx/CRL/ to extended the Masterseal layer from the invert waterproof invert to the row of dowels that was potentially installed trough the Masterseal (and making sure that the minimum overlap is met). Also a grouting tube has been installed at the end of the Masterseal overlap (extending from the RHS to the LHS). Furthermore it has been installed hydrophilic mastic rings around the base of each of these dowels Please find checksheet attached
| 01CV - Civils | Cxxx-NCR-002268 | NCR | BOS ES1 Collar - Damage waterproofing |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-09-21 | 2015-09-24 16:57 | 3 | 2015-09-03 18:09 | Tunnelling - Tunnelling General | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After striking the LHS column shutter on ES1 D-Wall connection, it was discovered that there are areas of damage to the Masterseal. At 9 o'clock there are small damage which when repaired will not have the required 200mm overlap.
| 01CV - Civils | Cxxx-NCR-002269 | NCR | BOS ATS stopping monitoring |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2015-09-05 | 2015-11-16 14:59 | 72 | 2015-09-04 10:21 | Geotechnical Engineering - Geotechnical Monitoring | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | The Works Information requires all automated monitoring is carried out at BOS a minimum period of 3 months post main works (SCL tunnels) and can only be turned off once agreed by the PM. The Contractor has stopped monitoring as of 04-09-15 at approximately 5 am.
| 01CV - Civils | Cxxx-NCR-002270 | NCR | BOS ES1 - Lack of overlap |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-09-24 | 2015-09-24 16:59 | 0 | 2015-09-10 11:01 | Tunnelling - Tunnelling General | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During inspection of waterproofing, it became apparent the waterproofing in ES1 at ch 3 invert been damaged close to the previously cast invert and minimum lap length of waterproofing cannot be achieved.
| 01CV - Civils | Cxxx-NCR-002271 | NCR | CP3 - Final as Built out of Tolerance |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-09-29 | 2015-09-24 17:02 | -5 | 2015-09-15 10:07 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Fire proofing as-built profile out of designed tolerance for CP3
| 01CV - Civils | Cxxx-NCR-002272 | NCR | CP4 - Final As Built out of Tolerance |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-09-25 | 2015-09-24 17:05 | -1 | 2015-09-15 10:15 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Fire proofing as-built profile out of designed tolerance for CP4
| 01CV - Civils | Cxxx-NCR-002273 | NCR | ES1- Final As Built out of Tolerance |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-09-25 | 2015-09-24 17:07 | -1 | 2015-09-15 10:22 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Fire proofing as-built profile out of designed tolerance for ES1
| 01CV - Civils | Cxxx-NCR-002274 | NCR | CH2 - Final As Built out of Tolerance |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-09-25 | 2015-09-24 17:11 | -1 | 2015-09-15 10:24 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Fire proofing as-built profile out of designed tolerance for CH2
| 01CV - Civils | Cxxx-NCR-002275 | NCR | CP1- Final As Built out of Tolerance |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-09-24 | 2015-09-24 17:13 | 0 | 2015-09-15 15:44 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Fire proofing as-built profile out of designed tolerance for CP1
| 01CV - Civils | Cxxx-NCR-002276 | NCR | CP2- Final As Built out of Tolerance |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-09-24 | 2015-09-24 19:53 | 0 | 2015-09-15 19:38 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Fire proofing as-built profile out of designed tolerance for CP2
| 01CV - Civils | Cxxx-NCR-002277 | NCR | AP1- Final As Built Profile out of Tolerance |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-09-24 | 2015-09-28 17:25 | 4 | 2015-09-15 19:11 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Fire proofing as-built profile out of designed tolerance for AP1
| 01CV - Civils | Cxxx-NCR-002278 | NCR | CH2- Cast Invert out of Tolerance |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-09-25 | 2015-09-24 19:56 | -1 | 2015-09-15 11:16 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | CH2 cast invert U1 finish (0-20mm tolerance) is out of specifications due to an inappropriate leveled. This NCR it is not compliant with the ITP Cxxx--C4-ITP-CRT00_ST005-50144 - BOS TCR CP Cast-in situ and Sprayed Secondary Lining section B4.10 and the general note G36 from the drawing Cxxx-MMD-C4-DDJ-N105-00001 reference below. See attached the profiles.
| 01CV - Civils | Cxxx-NCR-002279 | NCR | CP3- Cast Invert out of Tolerance |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-09-25 | 2015-09-24 19:59 | -1 | 2015-09-15 11:51 | Tunnelling - Tunnelling General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | CP3 cast invert U1 finish (0-20mm tolerance) is out of specifications due to an inappropriate leveled. This NCR it is not compliant with the ITP Cxxx--C4-ITP-CRT00_ST005-50144 - BOS TCR CP Cast-in situ and Sprayed Secondary Lining section B4.10 and the general note G36 from the drawing Cxxx-MMD-C4-DDJ-N105-00001 reference below. See attached the profiles.
| 01CV - Civils | Cxxx-NCR-002280 | NCR | CP4 - Cast invert out of tolerance |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-09-24 | 2015-09-24 20:06 | 0 | 2015-09-15 11:55 | Tunnelling - Tunnelling General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | CP4 cast invert U1 finish (0-20mm tolerance) is out of specifications due to an inappropriate leveled. This NCR it is not compliant with the ITP Cxxx--C4-ITP-CRT00_ST005-50144 - BOS TCR CP Cast-in situ and Sprayed Secondary Lining section B4.10 and the general note G36 from the drawing Cxxx-MMD-C4-DDJ-N105-00001 reference below. See attached the profiles.
| 01CV - Civils | Cxxx-NCR-002281 | NCR | CP1 - Invert out of tolerance |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-09-24 | 2015-09-24 20:10 | 0 | 2015-09-15 16:54 | Tunnelling - Tunnelling General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | CP1 cast invert U1 finish (0-20mm tolerance) is out of specifications due to an inappropriate leveled. This NCR it is not compliant with the ITP Cxxx--C4-ITP-CRT00_ST005-50144 - BOS TCR CP Cast-in situ and Sprayed Secondary Lining section B4.10 and the general note G36 from the drawing Cxxx-MMD-C4-DDJ-N105-00001 reference below. See attached the profiles.
| 01CV - Civils | Cxxx-NCR-002282 | NCR | CP2 - Invert out of tolerance |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-09-24 | 2015-09-24 20:13 | 0 | 2015-09-15 19:41 | Tunnelling - Tunnelling General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | CP2 cast invert U1 finish (0-20mm tolerance) is out of specifications due to an inappropriate leveled. This NCR it is not compliant with the ITP Cxxx--C4-ITP-CRT00_ST005-50144 - BOS TCR CP Cast-in situ and Sprayed Secondary Lining section B4.10 and the general note G36 from the drawing Cxxx-MMD-C4-DDJ-N105-00001 reference below. See attached the profiles.
| 01CV - Civils | Cxxx-NCR-002283 | NCR | AP1 - Cast invert out of tolerance |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-09-24 | 2015-09-24 20:19 | 0 | 2015-09-15 19:18 | Tunnelling - Tunnelling General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | AP1 cast invert U1 finish (0-20mm tolerance) is out of specifications due to an inappropriate leveled. This NCR it is not compliant with the ITP Cxxx--C4-ITP-CRT00_ST005-50144 - BOS TCR CP Cast-in situ and Sprayed Secondary Lining section B4.10 and the general note G36 from the drawing Cxxx-MMD-C4-DDJ-N105-00001 reference below. See attached the profiles.
| 01CV - Civils | Cxxx-NCR-002284 | NCR | ES1- Cast invert out of tolerance |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-09-24 | 2015-09-24 20:21 | 0 | 2015-09-15 20:26 | Tunnelling - Tunnelling General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | ES1 cast invert U1 finish (0-20mm tolerance) is out of specifications due to an inappropriate leveled. This NCR it is not compliant with the ITP Cxxx--C4-ITP-CRT00_ST005-50144 - BOS TCR CP Cast-in situ and Sprayed Secondary Lining section B4.10 and the general note G36 from the drawing Cxxx-MMD-C4-DDJ-N105-00001 reference below. See attached the profiles.
| 01CV - Civils | Cxxx-NCR-002285 | NCR | ES1 Collar - Dywidags no repaired |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-09-23 | 2015-09-24 20:24 | 1 | 2015-09-17 12:33 | Tunnelling - Tunnelling General | 5000 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The waterproofing from the second pour of the RHS column of ES1 was approved and the collar was poured. Once the pour was finished, while reviewing some pictures it was apparent that the dywidags were not painted. The dywidags were installed in the lining wall area and 150 mm away from the edge of the masterseal.
| 01CV - Civils | Cxxx-NCR-002286 | NCR | Fibre Optic monitoring installation cable damage |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2015-09-30 | 2015-09-28 21:42 | -2 | 2015-09-16 18:05 | Civil - Tunnelling | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | One of the cables associated with the fibre optic monitoring in CH2 has been damaged adjacent to the ES1 collar.
| 01CV - Civils | Cxxx-NCR-002287 | NCR | ES1 Collar - Lack of overlap soffit |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-09-24 | 2015-09-24 20:27 | 0 | 2015-09-16 19:04 | Tunnelling - Tunnelling General | 5000 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After removing the stop end on ES1 D-Wall connection, it was discovered that there are areas of damage to the Masterseal. At 2 o'clock there are small damage which when repaired will not have the required 200mm overlap.
| 01CV - Civils | Cxxx-NCR-002288 | NCR | BOS LUL Ventilation Tunnel - Low concrete sample cube strength for 2no. pours in mass concrete locations |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-10-02 | 2015-09-20 21:39 | -12 | 2015-09-18 15:15 | Tunnelling - Linings - SGI Rings | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | On review of the compressive strength cube reports, it has become apparent that two pours in mass concrete locations of the SGI tunnel have failed to show specified strength at 28 days of 40N: Pour 1 - 2nd flight of cast steps and 1st flight of step curbs/ upstand The report demonstrates strength of 40.5N and 37.7 N @ 56days. A further Schmidt hammer test undertaken on the 18/09/15 after discussion with Cxxx/PM has shown the concrete strength is 47N Pour 2 - SGI invert slab - 11/6/15 The report demonstrates strength of 36N and 35.3 N @ 56days. A further Schmidt hammer test undertaken on the 18/09/15 after discussion with Cxxx/PM has shown the concrete strength is 47N Attached documents show the original strength reports and details of Schmidt hammer testing propose to use as is, as the concrete has achieved sufficient strength above 40N
| 01CV - Civils | Cxxx-NCR-002289 | NCR | Fireproofing layer de-bonding, above axis, and not in conflict with PES brackets. (Preliminary version) |  | Crossrail | XRL |  |  | 2015-11-01 | 2016-12-07 22:04 | 402 | 2015-10-02 08:55 | Tunnelling - Linings - Sprayed Concrete | 25500 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | This NCR pertains to all* de-bonded areas in the fireproofing layer of Sprayed Concrete Lining (SCL) works at Tottenham Court Road Station (TCR) above axis level of the tunnels and NOT in conflict with the location of Platform Edge Screen (PES) brackets as per the Cxxx design, and the subsequent treatment/repair as required. The obligations of the Contractor are defined in the Section KT20 – Materials and Workmanship Specification, Sprayed Concrete Linings, with requirements regarding bonding of layers set out in Clause KT20.3226 (Defects and Repairs) where a)ii) reads ‘Area of work shall be properly compacted and bonded and free from honeycombing, laminations, dry or sandy patches, voids, sagged or slumped material, rebound, excessive cracking and over spray.‘ As such, areas of de-bonding in the fireproofing layer are not in accordance with the agreed specification for the works. Areas of de-bonding within the fireproofing layer have been determined through the process of hammer testing where, as defined in clause KT20.2205 (Hammer Testing of Primary and Secondary Linings), ‘A hollow sound is indicative of lack of bond between layers of shotcrete.’ The areas of de-bonding encompassed by this NCR have been observed as a result of testing completed post handover of the SCL works to the Cxxx contract. Observed areas of de-bonding above axis at TCR but NOT in conflict with PES brackets currently number 7. Details are as follows: - 1. AP3W, ch 14, 700mm x 700mm, 40º - 2. PTE, ch 120, 600mm x 300mm, 30º - 3. PTE, ch 100, 600mm x 600mm, 30º - 4. PTE, ch 89, 1000mm x 500mm, 45º - 5. PTE, ch 89, 800mm x 600mm, 30º - 6. PTE, ch 58, 900mm x 900mm, 30º - 7. PTW, ch -5.5, 500mm x 500mm, 345º *Testing of Secondary Lining works is not yet complete and further areas of de-bonding in the fireproofing layer may be discovered and this NCR is to be inclusive of them.
| 01CV - Civils | Cxxx-NCR-002290 | NCR | Fireproofing layer de-bonding, above axis, and in conflict with PES brackets. (Preliminary version) |  | Crossrail | XRL |  |  | 2015-11-01 | 2016-12-07 22:58 | 402 | 2015-10-02 08:58 | Tunnelling - Linings - Sprayed Concrete | 10000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | This NCR pertains to all* de-bonded areas in the fireproofing layer of Sprayed Concrete Lining (SCL) works at Tottenham Court Road Station (TCR) above axis level of the tunnels and in conflict with the location of Platform Edge Screen (PES) brackets as per the Cxxx design, and the subsequent treatment/repair as required. The obligations of the Contractor are defined in the Section KT20 – Materials and Workmanship Specification, Sprayed Concrete Linings, with requirements regarding bonding of layers set out in Clause KT20.3226 (Defects and Repairs) where a)ii) reads ‘Area of work shall be properly compacted and bonded and free from honeycombing, laminations, dry or sandy patches, voids, sagged or slumped material, rebound, excessive cracking and over spray.‘ As such, areas of de-bonding in the fireproofing layer are not in accordance with the agreed specification for the works. Areas of de-bonding within the fireproofing layer have been determined through the process of hammer testing where, as defined in clause KT20.2205 (Hammer Testing of Primary and Secondary Linings), ‘A hollow sound is indicative of lack of bond between layers of shotcrete.’ The areas of de-bonding encompassed by this NCR have been observed as a result of testing completed post handover of the SCL works to the Cxxx contract. Observed areas of de-bonding above axis at TCR that are in conflict with PES brackets currently number 2. Details are as follows: - 1. PTE, ch 120, 2200mm x 250mm, 315º - 2. PTE, ch 99.5, 800mm x 700mm, 355º *Testing of Secondary Lining works is not yet complete and further areas of de-bonding in the fireproofing layer may be discovered and this NCR is to be inclusive of them.
| 01CV - Civils | Cxxx-NCR-002291 | NCR | Fireproofing layer de-bonding, above axis, and not in conflict with PES brackets. (Preliminary version) |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2015-11-01 | 2016-12-07 23:01 | 402 | 2015-10-02 09:02 | Tunnelling - Linings - Sprayed Concrete | 10000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | This NCR pertains to all* de-bonded areas in the fireproofing layer of Sprayed Concrete Lining (SCL) works at Bond Street Station (BOS) above axis level of the tunnels and NOT in conflict with the location of Platform Edge Screen (PES) brackets as per the Cxxx design, and the subsequent treatment/repair as required. The obligations of the Contractor are defined in the Section KT20 – Materials and Workmanship Specification, Sprayed Concrete Linings, with requirements regarding bonding of layers set out in Clause KT20.3226 (Defects and Repairs) where a)ii) reads ‘Area of work shall be properly compacted and bonded and free from honeycombing, laminations, dry or sandy patches, voids, sagged or slumped material, rebound, excessive cracking and over spray.‘ As such, areas of de-bonding in the fireproofing layer are not in accordance with the agreed specification for the works. Areas of de-bonding within the fireproofing layer have been determined through the process of hammer testing where, as defined in clause KT20.2205 (Hammer Testing of Primary and Secondary Linings), ‘A hollow sound is indicative of lack of bond between layers of shotcrete.’ The areas of de-bonding encompassed by this NCR have been observed as a result of testing completed post handover of the SCL works to the Cxxx contract. Observed areas of de-bonding above axis at BOS but NOT in conflict with PES brackets currently number 4. Details are as follows: - 1. PTE, ch 123, 500mm x 500mm, 300º - 2. PTE, ch 135.5, 1000mm x 1500mm, 0º - 3. PTE, ch 135, 500mm x 500mm, 300º - 4. PTE, ch 152, 750mm x 750mm, 30º *Testing of Secondary Lining works is not yet complete and further areas of de-bonding in the fireproofing layer may be discovered and this NCR is to be inclusive of them.
| 01CV - Civils | Cxxx-NCR-002292 | NCR | 1 day cores tested late |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-11-11 | 2015-11-02 10:54 | -9 | 2015-10-21 15:10 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The following sets of 1 day cores were tested late: SCL839, Fireproofing, CH2 - Tested at 6 days SCL840, Fireproofing, CH2 - Tested at 6 days SCL844, Fireproofing, S2 Set 1 - Tested at 4 days SCL848, Fireproofing, S2 Set 2 - Tested at 4 days SCL851, Secondary, ES1 Set 1 - Tested at 4 days SCL852, Secondary, ES1 Set 2 - Tested at 4 days
| 01CV - Civils | Cxxx-NCR-002293 | NCR | Lack of washouts July to September 2015 |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-11-04 | 2015-11-04 12:46 | 0 | 2015-10-21 15:21 | Tunnelling - Linings - Sprayed Concrete | 2000 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | No monthly washouts tests completed for mix 17.2 during July to September 2015
| 01CV - Civils | Cxxx-NCR-002294 | NCR | Backfilling of Grout Shaft BOS1 with CBM1 concrete, one cube strength test is missing. |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2015-11-17 | 2015-11-13 12:09 | -4 | 2015-11-03 14:12 | Geotechnical Engineering - Compensation Grouting | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | ITP Cxxx--C4-ITPCRT00_ST005-50172 rev 3.0 is applicable to backfilling of Grout Shaft BOS1 at Davies Mews. Section B.1.3. "Taking concrete cubes of the delivery wagons" requires 1 set of 4 cubes to be taken and tested per pour or 100m3. A total of 142.4m3 of concrete were poured into the shaft and only one set of cubes was taken. Therefore one more set would have been required according the ITP.
| 01CV - Civils | Cxxx-NCR-002295 | NCR | BOS - VD3 - Masterseal Overlap Reduced |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2015-12-15 | 2016-12-19 10:06 | 370 | 2015-11-17 10:20 | Tunnelling - Tunnelling General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | On 28/10/15 Cxxx(CRL) at the request of Cxxx(CRL) carried out an inspection to VD3 where it was established that there is insufficient lap available to the waterproofing membrane at the connection that Cxxx are constructing.
| 01CV - Civils | Cxxx-NCR-002296 | NCR | BOS - VD4 - Masterseal Overlap Reduced |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2015-12-15 | 2016-12-19 09:41 | 370 | 2015-11-17 10:20 | Tunnelling - Tunnelling General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | On 28/10/15 Cxxx(CRL) at the request of Cxxx(CRL) carried out an inspection to VD4 where it was established that there is insufficient lap available to the waterproofing membrane at the connection that Cxxx are constructing.
| 01CV - Civils | Cxxx-NCR-002298 | NCR | Bond Street - ES1 - Leaks |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2016-02-04 | 2016-10-16 20:28 | 255 | 2016-01-21 19:01 | Tunnelling - Tunnelling General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | The PM has recently notified us of the presence of minor water seepage / ingress at the ES1/d-wall interface at Bond Street station, and has requested that we raise an NCR to cover these works. We do not consider that an NCR is warranted because the works were constructed in accordance with the Works Information, and all the relevant ITPs and check sheets were signed to demonstrate this. In other words, there is no M&W specification clause against which to raise the NCR. However, we note that we have previously raised our concerns about the adequacy and robustness of the Employer's waterproofing design in this area, and we have suggested a variety of proposals to avoid leakage (e.g. the addition of Vandex into the joint, etc). These proposals were not followed up by the designer. There is an inherent weakness at this connection between the tunnel and shaft. On this basis, it may be appropriate to now raise an NCR against clause KW20.1301 "ii) Tunnels and shafts accessible to the public or containing plant and equipment shall be free from all leakage, seepage and damp patches so as to provide a dry environment.", but this NCR is raised against the design rather than workmanship. The fitness for purpose / performance requirement within the specification has not been achieved, but this is not attributed to workmanship.
| 01CV - Civils | Cxxx-NCR-002299 | NCR | TCR - VEW - Leaks |  | Contr | BFK |  |  | 2016-02-04 | 2016-12-13 21:05 | 313 | 2016-01-21 19:07 | Tunnelling - Tunnelling General | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Supervision - Other | Completed |  | The PM has recently notified us of the presence of minor water seepage / ingress at the VEW/d-wall interface at Tottenham Court Road station, and has requested that we raise an NCR to cover these works. We do not consider that an NCR is warranted because the works were constructed in accordance with the Works Information, and all the relevant ITPs and check sheets were signed to demonstrate this. In other words, there is no M&W specification clause against which to raise the NCR. However, we note that we have previously raised our concerns about the adequacy and robustness of the Employer's waterproofing design in this area, and we have suggested a variety of proposals to avoid leakage (e.g. the addition of Vandex into the joint, etc). These proposals were not followed up by the designer. There is an inherent weakness at this connection between the tunnel and shaft. On this basis, it may be appropriate to now raise an NCR against clause KW20.1301 "ii) Tunnels and shafts accessible to the public or containing plant and equipment shall be free from all leakage, seepage and damp patches so as to provide a dry environment.", but this NCR is raised against the design rather than workmanship. The fitness for purpose / performance requirement within the specification has not been achieved, but this is not attributed to workmanship.
| 01CV - Civils | Cxxx-NCR-002300 | NCR | PTW - West Headwall |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2016-02-11 | 2016-12-19 10:26 | 312 | 2016-01-28 09:46 | Tunnelling - Tunnelling General | 1500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The methodology used for the construction of PTW West Headwall included the installation of dywidag bars with sleeves to the face of the headwall. the dywidags were removed when striking the formwork of the headwall. As part of the works, should have filled the holes were the dywidags were installed with 5 Star Grout. These holes were not filled.
| 01CV - Civils | Cxxx-NCR-002302 | NCR | TCR PTE Tunnel De-bonding |  | Crossrail | XRL |  |  | 2016-03-23 | 2016-12-13 21:14 | 265 | 2016-02-24 17:47 | Tunnelling - Linings - Sprayed Concrete | 10000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | De-bonding to the under platform areas of PTE at TCR has been identified by Crossrail through third round of hammer testing of the SCL fireproofing lining. The areas of de-bonding have been found over a coverage area of approx. 143lm commencing from the far eastern end of the platform and continuing to the western end, i.e. Ch 1.0 to Ch 143.0. The areas of de-bonding found are detailed as follows: No. Ch Size of De-bonding found during hammer testing 1 1.0 400 x 500 mm 2 3.0 2.3 x 800 mm 3 5.0 3.0 x 1.6 mm 4 9.0 1.6 x 450 5 13.0 4.5 x 400 6 14.0 600 x 400 7 19.0 1.7 x 1.0 8 40.0 1.7 x 1.0 9 44.0 400 x 500 10 44.0 600 x 400 11 45.0 2.8 x 900 12 50.0 3.5 x 1.8 13 54.0 1.8 x 900 14 56.0 3.9 x 1.8 15 60.0 2.0 x 1.2 16 67.5 4.2 x 1.8 17 78.0 4.3 x 1.0 18 84.5 3.6 x 1.8 19 90.0 1.6 x 1.5 20 95.0 900 x 900 21 100.0 1.8 x 700 22 102.0 2.0 x 1.7 23 103 .5 400 x 400 24 105.0 1.7 x 400 25 106.5 1.6 x 800 26 108.0 2.1 x 1.6 27 27 110.0 1.6 x 1.0 28 112.5 1.7 x 1.4 29 114.0 1.7 x 500 30 119.0 3.1 x 1.7 31 126.0 1.9 x 1.7 32 130.5 3.5 x 1.7 33 137.0 3.1 x 1.7 34 143.0 800 x800
| 01CV - Civils | Cxxx-NCR-002303 | NCR | TCR - Leaks at S4, AP8, S3 and VWW |  | Crossrail | XRL |  |  | 2016-05-31 | 2017-08-24 10:04 | 450 | 2016-05-10 14:36 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following the site visit on 16/03/16 at TCR by Crossrail Cxxx/xxx, CEG and Cxxx at the request of Crossrial Cxxx to review a number of areas which had been identified as having water ingress by Cxxx, leaks have been confirmed at the following locations: 1. S4-WTH - Leak has been identified at the interface with the Western Ticket Hall and diaphragm wall construction 2. AP8-GYB - Leak has been identified at the interface with Gosslet Yard Box and diaphragm wall construction, where leak is present above axis near termination box 3. S3-GYB - Leak has been identified at the interface with Gosslet Yard Box and diaphragm wall 4. VWW - Leak identified along top of VWW
| 01CV - Civils | Cxxx-NCR-002313 | NCR | TCR Leaks at S1, VEW Vertical Stubb Shaft, PTW and PTE |  | Crossrail | XRL |  |  | 2017-09-07 10:00 | 2017-08-24 10:05 | -14 | 2016-05-23 15:09 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Following the site visit on 20/05/16 at TCR by Crossrail Cxxx/xxx, CEG and Cxxx at the request of Crossrial Cxxx to review a number of areas which had been identified as having water ingress by Cxxx, leaks have been confirmed at the following locations: 1. S1-GYB - Leak has been identified at the interface between the diaphragm wall and the Cxxx/xxx cast in-situ concrete collar. Re-injection grout hoses in termination boxes are located on both the RHS and LHS of the collar. The leak is at the sides of the collar (below axis) and at the soffit to the collar (crown level); 2. VEW Vertical Stuff Shaft at the far eastern end of PTW. The leak is at the higher level of the vertical section of VEW where a number of damp patches and a leak has been identified; 3. PTW above axis at approx. 10 o'clock position. Leak has been identified by Cxxx __ under Cxxx EWN 548. The location of the leak is recorded as 7m from Ch51 (marked up as part of de-bonding repairs and also recorded that crack is present through the leak; 4. PTE at axis at approx. 8-9 o'clock position. The leak has been identified at marked up de-bonding patch location number 14 and 15 (reference 4910.663 marked up at location also) and also recorded that crack is present through the leak. Photos have been attached showing the leak areas.
| 01CV - Civils | Cxxx-NCR-002314 | NCR | Re-Injection Grout Hoses Not Encased in Termination Box - No Termination Boxes Installed CP2 |  | Crossrail | XRL |  |  | 2017-09-05 10:29 | 2017-08-22 13:08 | -14 | 2016-05-23 15:53 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following the site visit on 20/05/16 at TCR by Crossrail Cxxx/xxx, CEG and Cxxx at the request of Crossrial Cxxx to review a number of areas which have been identified as having water ingress, it was recorded that the reinjection grout hoses at the slab level, are not encased within any termination boxes. On closer inspection, it is noted that the termination boxes have not been installed which are a requirement of the works information.
| 01CV - Civils | Cxxx-NCR-002315 | NCR | Contraction Joints Omitted to Fireproofing Layer - Bond Street Tunnels |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2016-07-19 | 2016-12-07 23:24 | 141 | 2016-07-05 08:29 | Tunnelling - Linings - Sprayed Concrete | 55000 |  | Incomplete Works | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Crossrail and Cxxx confirm on recent site inspection of SCL tunnels at Bond Street the omission of contraction joints in the fireproofing lining. The contraction joints have been omitted to the following areas: VD3: CJ.1202 not performed in all tunnel perimeter (saw cut performed on both sides to axis level). VD4: CJ.1102 not done. Secondary Lining cracked approximately at contraction joint position. AP3A: CJ.1003 not done. CP10: CJ.0904 not done; CJ at CP10/CH3 junction side not done. CP9: CJ.0901 not done; CJ at CP9/CH3 junction side not done. CP8: CJ.0804 not done; CJ at CP8/CH3 junction side not done. CP7: CJ.0801 not done; CJ at CP7/CH3 junction side not done. Secondary Lining cracked approximately at contraction joint position. CP5: CJ.0702 not done; CJ.0701 not done. CP4: CJ.0604 not done; CP2: CJ.0504 not done. Secondary Lining cracked approximately 800mm away from contraction joint position. CP1: CJ.0501 not done; AP2A: CJ.0405 not done; ES1: CJ.0201 not done; PTE: CJ.0101 not done. Secondary Lining cracked approximately at contraction joint position; CJ.0112 not done; CJ.0113 not done.
| 01CV - Civils | Cxxx-NCR-002316 | NCR | TCR:VWW - Insufficient Secondary Lining thickness and Fire Protection Layer ~Ch.22 to 25 |  | Contr | HAG |  |  | 2016-07-08 | 2017-04-20 09:59 | 286 | 2016-07-05 17:55 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following a CRL Cxxx/Cxxx/CEG site visit on Tuesday 14th June 2016, the as-built condition of the SCL Secondary Lining at the VWW connection constructed by Cxxx/xxx appears unsatisfactory. CRL consider the permanent works have not been carried out in accordance with the Works Information and are not in agreement with the As-Built Red-Line drawing records self-certified and submitted by Cxxx/xxx (see reference documents). urgently need to provide CRL with information on: 1. The as-built sprayed secondary lining thicknesses (which appears to be less than 100mm thick in places compared to the minimum design thickness of 250mm ref. drg. Cxxx-MMD-C4-DDB-N105_5-00212). 2. The extent/purpose of the black "visquine" membrane embedded in the secondary lining [overspray?] (see photo attachment). 3. The extent and thickness of sprayed Fire Protection layer (which appears to have been omitted for the last ~ 500mm of secondary lining). Cxxx and CEG's assessment is that the VWW SCL tunnel to WTH Box Connection (which was transferred from Cxxx/xxx's scope) cannot be completed by Cxxx in its current state and a remedial design will be needed to address the above Non-Conformances. At the time of inspection, Cxxx appeared to be 3 to 4 weeks away from casting the VWW/WTH connection and an urgent resolution was requested by CEG. Cxxx/xxx (__) was briefed at the end of the Cxxx Quality Meeting at 25 Canada Square on Wednesday 15th June 2016 with photos showing the membrane inclusion and sub-standard thickness of secondary lining. agreed to look at this issue over the next couple of days. This NCR has been raised by CEG on behalf of Cxxx/xxx. A plan of action needs to be agreed by the end of this week (08.07.16) so that a remedial design can be formulated and delay to Cxxx's construction programme can be mitigated.
| 01CV - Civils | Cxxx-NCR-002317 | NCR | TCR - Omission of post-milling Primary Lining profiles in Cxxx sub-construction/handover packages |  | Contr | HAG |  |  | 2017-10-14 10:27 | 2017-09-14 10:49 | -30 | 2016-09-19 14:49 | Civil - Tunnelling | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Not Defined | Completed |  | The TCR primary lining as-built records submitted in sub-construction packages (which have been accepted by CRL) have the following caveat: "Primary lining As-built profile in this section may change prior to regulating layer application. For primary lining as-built profiles prior to regulating application see...(relevant tunnel)...secondary lining ITP record." The above information has not been added to the Secondary lining ITP records and only exists as point cloud data (which will require further interrogation to determine the actual as-built primary lining thickness). Although the CRL Cxxx/xxx site team and Cxxx Resident Technical Engineer, reviewed and accepted the contemporaneous profile records during construction with , this evidence has not been submitted within the secondary lining sub-construction packages. The Chief Engineer's Group has difficulty accepting the sub-construction packages without these omissions addressed.
| 01CV - Civils | Cxxx-NCR-002318 | NCR | Embedment to Waterproofing - Bond Street CH3 Crown |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2016-08-11 | 2017-04-19 20:26 | 251 | 2016-07-14 12:50 | Tunnelling - Linings - Sprayed Concrete | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following recent walk on site with Crossrail Cxxx and Cxxx/xxx and Cxxx to CH3, Cxxx have identified a number of nails/bolts protruding out of the waterproofing at CH3 above crown level, which is most likely to have been used to secure the plastic sheeting during construction of bulkhead to CH3.
| 01CV - Civils | Cxxx-NCR-002319 | NCR | Damaged Waterproofing - Bond Street AP3A, AP3B and CH3 |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2016-08-11 | 2017-04-19 20:32 | 251 | 2016-07-14 13:15 | Tunnelling - Linings - Sprayed Concrete | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | On recent walk round of CH3, AP3A and AP3B with Crossrail Cxxx and Cxxx/xxx and Cxxx, it has been noted that there are number of areas of damage to the waterproofing, which is inclusive of plywood left in the spray applied waterproofing at AP3A and CH3, where plywood has been left in the area prior to spraying of waterproofing and then over sprayed preventing adequate coverage in the affected areas. Refer to attached photos which is to be cross referenced with NCR 002319.
| 01CV - Civils | Cxxx-NCR-002321 | NCR | BOS: AP1 access passage - Leaks in the invert |  | Contr | HAG | BOS - Bond Street Station (West) |  | 2017-09-21 | 2017-09-15 12:50 | -6 | 2017-08-30 12:48 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Water leakage was identified along the invert of the AP1 access tunnel by Cxxx during casting of the concrete passage-way slab. This had ponded in AP1 widening "rest area" (see attached photo). CEG has been advised that Cxxx damaged the reinjectable grout tubes which were installed in the AP1 invert as mitigation for previous NCR's associated with damage to the waterproofing membrane. Following a site visit with Cxxx/xxx, Cxxx, and Cxxx, on 13.07.16 it was agreed that leak treatment i.e. resin injection using packers was impractical and might push the leaks higher up towards the tunnel crown. It was agreed that Cxxx would install a water management system to intercept the water. Cxxx-RFI-002599 refers. This NCR can be closed.
| 01CV - Civils | Cxxx-NCR-002322 | NCR | TCR: Excess cover to rebar in sprayed secondary lining at junctions (e.g. AP4E/PTE) |  | Contr | HAG |  |  | 2016-11-06 | 2017-03-10 16:33 | 124 | 2016-10-23 20:14 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Cxxx __-designed "tusks", which support the GFRC cladding at junctions, clash at a number of locations with the as-built Sprayed Concrete Lined (SCL) surface. Following a lengthy programme of design review, Cxxx __ advised CRL that redesign of the tusks to accommodate the as-built SCL was not feasible. On 18th August 2016, Cxxx __ confirmed to CRL there were 7 no. junctions (16 no. patches), where the Cxxx __-designed "tusks" (which support the GFRC cladding at junctions) clash with the as-built Sprayed Concrete Lined (SCL) surface. CRL instructed further investigation of the SCL by Cxxx and Cxxx to permit localised hand-grinding of the SCL surface and ameliorate the clash, including determination of the as-built cover to the reinforcement (as requested by Cxxx). The grinding requirements and Cxxx response are captured in Cxxx-FCD-000714. Cover-meter surveys undertaken by Cxxx were able to locate the orientation (but not the depth) of the reinforcement. Trial drilling to 150mm depth failed to locate the bars. Cxxx-RFI-001433 refers. On 30th August 2016 __ advised that a 150mm diameter trial core drilled by Cxxx __ at the AP4E/PTE junction located reinforcement at a depth of 380mm. According to the Works Information Drawing Cxxx-MMD-C4-DDD-N105_5-00406, the minimum design cover is 60mm. (Allowing for construction [spraying] tolerances the maximum expected cover was 150mm.) So the excess cover of 380mm is a Non-Conformance. Cxxx has been instructed to assess the impact of localised grinding of the Fire Protection layer and the impact of excess cover (when known) on structural performance, durability and fire performance at all 7no. junctions identified by Cxxx. Refer to Cxxx-FCD-000714.
| 01CV - Civils | Cxxx-NCR-002323 | NCR | Persistant leaks at BOS tunnels |  | Crossrail | PDP | BOS - Bond Street Station (West) |  | 2017-10-13 13:06 | 2017-09-19 10:59 | -24 | 2016-09-29 12:18 | Tunnelling - Tunnelling General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There are a number of persistent leaks at BOS in the sprayed concrete tunnel linings and at the interfaces with between the shaft structures and tunnels The Contractor has attempted to seal by resin injection. Details of the locations can be found on the attached "BOS Leaks NCR Plan". Further injections are deemed unlikely to succeed. This NCR will superseded NCRs 2297, 2298 and 2301.
| 01CV - Civils | Cxxx-NCR-002324 | NCR | Patch 35 underthickness not required any more |  | Contr | BFK |  |  | 2016-11-22 | 2017-07-02 20:15 | 222 | 2016-11-08 12:11 | Tunnelling - Linings - Sprayed Concrete | 1500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | recently realised that patch 35 of underthickness in TCR had been overlooked, considering it was in the plenum area, as it seemed to indicate PMI 1915. The patch is approximately 500x500mm and although 96% of it is compliant and has an average of 68mm of FP, the remaining 4% has an average of 36mm, below the 40mm expected in the FP layer. requested to spray it, but it has been agreed by CRL and Cxxx that the patch will not need to be sprayed, although its location and existence should be captured, and therefore the need of this NCR.
| 01CV - Civils | Cxxx-NCR-002325 | NCR | De-bonding of Completed Secondary Lining at Bond Street Station - All Station Wide Tunnels Inclusive of Trackside Areas |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2016-12-21 | 2017-08-24 09:44 | 246 | 2016-11-23 23:44 | Tunnelling - Linings - Sprayed Concrete | 50000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The NCR has been raised as a result of de-bonded areas in the fireproofing layer of Sprayed Concrete Lining (SCL) works at Bond Street Station (BOS) throughout all areas inclusive of all tunnels within the Bond Street Station works (Contract Cxxx) and trackside tunnels (Contract Cxxx). The NCR relates to the Works Information not being met which as set out in Section KT20 – Materials and Workmanship Specification, Sprayed Concrete Linings, with requirements regarding bonding of layers in Clause KT20.3226 (Defects and Repairs) where a)ii) reads ‘Area of work shall be properly compacted and bonded and free from honeycombing, laminations, dry or sandy patches, voids, sagged or slumped material, rebound, excessive cracking and over spray.‘ As such, areas of de-bonding in the fireproofing layer are not in accordance with the agreed specification for the works. Areas of de-bonding within the fireproofing layer have been determined through the process of hammer testing where, as defined in clause KT20.2205 (Hammer Testing of Primary and Secondary Linings), ‘A hollow sound is indicative of lack of bond between layers of shotcrete.’ The areas of de-bonding encompassed by this NCR have been observed as a result of testing completed post handover of the SCL works to the Cxxx contract. This NCR supersedes all previous NCRs that have been raised for de-bonding of the fireproofing layer of the SCL.
| 01CV - Civils | Cxxx-NCR-002327 | NCR | Underthickness patches BOS station |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2016-11-24 | 2017-08-24 09:48 | 273 | 2016-11-10 16:53 | Tunnelling - Linings - Sprayed Concrete | 50000 |  | Design | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | After completion of BOS SCL Works, some underthickness areas were found and were agreed to be repaired with CRL and Cxxx. Purpose of this NCR is to record relevant underthickness area and necessary repairs as carried out within the Bond Street Station (Cxxx Scope of works). Underthickness repair documentation, check sheets and associated records are available on the eB document “BOS ITP Record. __ Application: Cxxx--C4-LRC-CRT00_ST005-53026”. This NCR replaces and supersed any other underthickness related NCR or Punchworks raised/open for individual Bond Street tunnels.
| 01CV - Civils | Cxxx-NCR-002328 | NCR | Underthickness patches TCR station |  | Contr | BFK |  |  | 2016-12-06 | 2017-08-24 09:49 | 261 | 2016-11-22 16:21 | Tunnelling - Linings - Sprayed Concrete | 50000 |  | Design | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | After completion of TCR SCL Works, some underthickness areas were found and were agreed to be repaired with CRL and Cxxx. Purpose of this NCR is to record relevant underthickness areas and necessary repairs as carried out within the Tottenham Court Road Station (Cxxx Scope of works). Underthickness repair documentation, check sheets and associated records are available on the eB document “TCR ITP Record for Application of __ Solution on SCL - Tottenham Court Road Station Tunnels: Cxxx--C4-LRC-CRT00_ST005-53019”. This NCR replaces and supersed any other underthickness related NCR or Punchworks raised/open for individual Tottenham Court Road tunnels.
| 01CV - Civils | Cxxx-NCR-002329 | NCR | De-bonding of Completed Secondary Lining at Tottenham Court Road Station - All Station Wide Tunnels Inclusive of Trackside Areas |  | Crossrail | XRL |  |  | 2017-01-04 | 2017-08-24 08:20 | 232 | 2016-12-07 21:13 | Tunnelling - Linings - Sprayed Concrete | 25500 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The NCR has been raised as a result of de-bonded areas in the fireproofing layer of Sprayed Concrete Lining (SCL) works at Tottenham Court Road Station (TCR) throughout all areas inclusive of all tunnels within the Tottenham Court Road Station works (Contract Cxxx) and trackside tunnels (Contract Cxxx). The NCR relates to the Works Information not being met which as set out in Section KT20 – Materials and Workmanship Specification, Sprayed Concrete Linings, with requirements regarding bonding of layers in Clause KT20.3226 (Defects and Repairs) where a)ii) reads ‘Area of work shall be properly compacted and bonded and free from honeycombing, laminations, dry or sandy patches, voids, sagged or slumped material, rebound, excessive cracking and over spray.‘ As such, areas of de-bonding in the fireproofing layer are not in accordance with the agreed specification for the works. Areas of de-bonding within the fireproofing layer have been determined through the process of hammer testing where, as defined in clause KT20.2205 (Hammer Testing of Primary and Secondary Linings), ‘A hollow sound is indicative of lack of bond between layers of shotcrete.’ The areas of de-bonding encompassed by this NCR have been observed as a result of testing completed post handover of the SCL works to the Cxxx contract. This NCR supersedes all previous NCRs that have been raised for de-bonding of the fireproofing layer of the SCL.
| 01CV - Civils | Cxxx-NCR-002330 | NCR | Rags incorporated into pipe arch at Western Ticket Hall/ES1 Escalator Tunnel Connection |  | Contr | HAG | BOS - Bond Street Station (West) |  | 2017-09-21 | 2017-09-15 12:53 | -6 | 2017-08-30 14:12 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During leak-sealing operations at the WTH/ES1 Connection, Cxxx's sub-contractor discovered rags which appear to have been used by the Cxxx/xxx SCL Contractor, to plug the ends of the pipe arch tubes used to form ES1, prior to grouting. The rags had rendered Cxxx's previous attempts to seal leaks at the ES1/WTH connection unsuccessful (see photos of blown waterproofing membrane and resin injection packers attached). Cxxx-RFI-003068 and Cxxx-RFI-003088 refer.
| 01CV - Civils | Cxxx-NCR-002331 | NCR | No Photos taken for Post Decommissioning Reports |  | Contr | BFK | BOS - Bond Street Station (West) |  | 2017-04-26 | 2018-04-12 11:46 | 351 | 2017-03-01 17:04 | Geotechnical Engineering - Settlement | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | The works specification, KX10.4101 (c), states that "Upon de-commissioning, the Contractor shall ensure that re-instatement is carried out to a standard that is equivalent or better to the condition indicated in the pre-installation condition surveys. The standard of re-instatement shall be detailed in the Method Statements for the acceptance of the Project Manager.” In some cases after decommissioning pictures of some HLCs have not been taken to prove that reinstatement was carried out in accordance with the specification. The properties where pictures are missing are the following: • 95-96 New Bond St • 2-6 Southampton Row • 1 Southampton Row • 51 South Molton St • 43 South Molton St
| 01CV - Civils | Cxxx-NCR-002332 | NCR | __ Testing |  | Crossrail | PDP | BOS - Bond Street Station (West) |  | 2017-09-13 08:02 | 2017-08-30 08:09 | -14 | 2017-06-09 11:55 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | Application of __ fireproofing system ITP (Cxxx--C4-ITP-CRT00_ST005-53003) states that an initial test of the bond between the __ and it's substrate is required (line B2.10). This test was not carried out initially and it did not meet the pass criteria given. The results of the test were captured in a __ Test Report, SA17322, Pull off Test at TCR, London.
| 01CV - Civils | Cxxx-NCR-002333 | NCR | Missing checksheet documentation |  | Contr | BFK |  |  | 2017-06-29 | 2017-09-15 12:58 | 78 | 2017-06-15 18:21 | Tunnelling - Linings - Sprayed Concrete | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Although patch No14 in CH1 below platform and A2E4 in tunnel AP2E above platform (both in TCR station) were repaired as it can be seen in Cxxx-XRL-C4-TSC-Cxxx-50001, the associated checksheets for them are missing or were not produced. Since the people involved are not in the project anymore has been requested to raise the present record to capture this non-conformance.
| 01CV - Civils | Cxxx-NCR-002334 | NCR | In Ground I&M not decommissioned |  | Crossrail | PDP | BOS - Bond Street Station (West) |  | 2018-12-10 12:38 | 2018-11-26 12:41 | -14 | 2018-09-25 15:51 | Consents - General | 500 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Cxxx-PMI-01963 states the following – The Project Manager confirms that the below listed in ground I&M, which the Contractor has stated has been decommissioned, does not need to have their covers removed and road re-instated by the Contractor. The covers fall into the local Urban Realm scheme at BOS and will be dealt with during its construction. - Cxxx-IE700007-CR084 - Cxxx-XR700009-CR084 - Cxxx-IE700008-CR084 - Cxxx-XR700010-CR084 - Cxxx-XR700011-CR084 The I&M has not been decommissioned.
| 02SL - Stations (LUL) | Cxxx-NCR-000089 | NCR | Precast concrete ring segments |  | Contr |  | BOS - Bond Street Station (West) |  | 2011-08-31 | 2011-10-04 16:04 | 34 | 2011-08-02 | Shafts - Shafts General | 500 |  | Material | Rework |  | Complete |  | Completed |  | Problem with the segments is the out of line 'T' bolt connections, which is occasionally causing a problem in locking the T bolt into position. There has also been a problem with 1no spear bolt insert that has pulled out during tightening. __ have been informed
| 02SL - Stations (LUL) | Cxxx-NCR-000135 | NCR | Diaphragm walling |  | Contr |  | BOS - Bond Street Station (West) |  | 2011-10-07 | 2011-10-04 15:56 | -3 | 2011-09-26 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | A section of temporary guidewall grid line J-K (7.8m lenght) has been concreted 30mm below design level.
| 02SL - Stations (LUL) | Cxxx-NCR-000159 | NCR | KSP sewer monitoring equipment eroneous readings |  | Contr |  | BOS - Bond Street Station (West) |  | 2011-11-04 | 2012-07-12 14:09 | 251 | 2011-11-01 | Shafts - Shafts General | 500 |  | Equipment Breakdown | Repair |  | Complete |  | Completed |  | In the early hours of 25 October the KSP sewer monitoring instrumentation recorded movement beyond the trigger levels, prompting the release of alerts. Subsequent review showed that this movement was probably not related to actual displacment of the sewer and an investigation of the function and possible failure of the instrumentation would be required.
| 02SL - Stations (LUL) | Cxxx-NCR-000161 | NCR | High slump result for concrete pour to Davies Mews base |  | Contr |  | BOS - Bond Street Station (West) |  | 2011-11-25 | 2012-01-04 14:24 | 40 | 2011-11-02 | Shafts - Shafts General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Slump taken from 2nd load was out of specification for a S3 mix ,concrete was allowed to be discharged into the works
| 02SL - Stations (LUL) | Cxxx-NCR-000166 | NCR | D-wall panel 1 works -initial loads from the 18.30 start until 20.30 were visually inspected & slump tested |  | Contr |  | BOS - Bond Street Station (West) |  | 2011-11-30 | 2012-01-04 14:28 | 35 | 2011-11-18 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Incorrect concrete workability test carried out
| 02SL - Stations (LUL) | Cxxx-NCR-000168 | NCR | Damaged to precast concrete ring segment |  | Contr |  | BOS - Bond Street Station (West) |  | 2011-12-09 | 2012-01-04 14:35 | 26 | 2011-11-29 | Shafts - Shafts General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | Damaged to precast concrete ring segment
| 02SL - Stations (LUL) | Cxxx-NCR-000172 | NCR | WTH panel 7 concrete out of delivery time from mixing too discharge on site |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-09-28 | 2012-10-12 17:34 | 14 | 2011-11-30 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Concrete delivered to site between 01:30 -07:35 hrs was not discharged into the works with in the time limit specified in the BS 8500-2:2006 CL 14.2
| 02SL - Stations (LUL) | Cxxx-NCR-000186 | NCR | Working to an non approved ITP |  | Contr |  | BOS - Bond Street Station (West) |  | 2011-12-16 | 2012-01-04 14:41 | 19 | 2011-12-09 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | Undertaking works for the installing of the CFA female piles. Site team working on an ITP that has yet not been approved. Working to Cxxx-SKA-04-ITP-Cxxx-50013 Rev 03 this document had not yet been approved.
| 02SL - Stations (LUL) | Cxxx-NCR-000187 | NCR | ITP |  | Contr |  | BOS - Bond Street Station (West) |  | 2011-12-31 | 2012-01-04 14:49 | 4 | 2011-12-09 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | The JV for not complied with the sign off against all witness/hold points for pile construction ITP.
| 02SL - Stations (LUL) | Cxxx-NCR-000198 | NCR | Pile 193 installed without the required conduit ducting. |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-01-12 | 2012-02-29 18:16 | 48 | 2011-12-20 | Civil - Civil Engineering General | 500 |  | Material | Rework |  | Complete |  | Completed |  | Pile 193 installed without the required conduit ducting.
| 02SL - Stations (LUL) | Cxxx-NCR-000199 | NCR | Pile P49 - due to issues with the cage fabrication the construction time for the pile exceed 60hrs. |  | Contr |  | BOS - Bond Street Station (West) |  | 2011-12-30 | 2012-02-14 17:56 | 46 | 2011-12-20 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | Pile P49 - due to issues with the cage fabrication the construction time for the pile exceed 60hrs. Incorrect fabrication of the cage resulted in the cage having to be sent back to the fabrication factory and amended. This process resulted in the pile bore being open over the 60hr construction time.
| 02SL - Stations (LUL) | Cxxx-NCR-000200 | NCR | No verticality checks undertaken by CSjv Setting Out Engineer on the first 4Nr male piles. |  | Contr |  | BOS - Bond Street Station (West) |  | 2011-12-30 | 2012-05-30 10:32 | 152 | 2011-12-20 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | No verticality checks undertaken by Setting Out Engineer on the first 4Nr male piles. Although __ had undertaken verticality checks on the casing and rig mast. No checks had been carried out by Setting Out Engineer using a plum bob or spinning disc. Confusion regarding who was responsible for this operation has resulted in this part of the verticality check being missed.
| 02SL - Stations (LUL) | Cxxx-NCR-000202 | NCR | Pile 167 lap used |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-01-12 | 2012-03-23 15:21 | 71 | 2011-12-20 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | Conventional lap used on 50mm bar extension to Pile 167.The late design change to Pile 167 resulted in the cage steel already being cut before the design change could be implemented. Short lead in time also meant that adequate couplers could not be sourced to undertake the works. Extension pieces welded with required lap. Process not deemed good practise under EC2.
| 02SL - Stations (LUL) | Cxxx-NCR-000203 | NCR | Pile 167-50mm extention bars |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-01-12 | 2012-03-23 15:27 | 71 | 2011-12-20 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Only possible to weld 15Nr 50mm extension bars, as opposed to the required 18Nr 50mm extension bars for Pile 167.
| 02SL - Stations (LUL) | Cxxx-NCR-000226 | NCR | Pile 187 installed without the required conduit ducting. |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-02-29 | 2012-02-29 18:19 | 0 | 2012-01-18 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Pile 187 installed without the required conduit ducting.
| 02SL - Stations (LUL) | Cxxx-NCR-000228 | NCR | Starter bars for pile 41 into pile capping beam |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-01-31 | 2012-02-29 18:21 | 29 | 2012-01-19 | Civil - Civil Engineering General | 500 |  | Design | Rework |  | Complete |  | Completed |  | Orientation of extension / starter bars for Pile 41 into capping beam incorrect. Bars were 90 degress out of position
| 02SL - Stations (LUL) | Cxxx-NCR-000229 | NCR | Orientation of extension / starter bars for Pile 25 into capping beam |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-03-30 | 2012-03-29 14:04 | -1 | 2012-01-19 | Civil - Civil Engineering General | 500 |  | Design | Rework |  | Complete |  | Completed |  | Orientation of extension / starter bars for Pile 25 into capping beam incorrect. Bars were 90 degress out of position
| 02SL - Stations (LUL) | Cxxx-NCR-000230 | NCR | C40/50 was poured in to panels 1,2,7,8,12,14b,24,25,36,37 |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-01-31 | 2012-03-23 15:33 | 52 | 2012-01-19 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | C40/50 was poured in to panels 1,2,7,8,12,14b,24,25,36,37.in lieu of C32/40 as called for in D wall specification
| 02SL - Stations (LUL) | Cxxx-NCR-000245 | NCR | Pile 40 |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-02-29 | 2012-03-23 15:53 | 23 | 2012-02-14 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Pile 40 finish cage level is 90mm lower than allowed tolerance/cage has potentially slumped during extraction of the casing
| 02SL - Stations (LUL) | Cxxx-NCR-000249 | NCR | Failure to supply daily inclinometer monitoring |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-02-29 | 2012-03-23 16:03 | 23 | 2012-02-14 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | System Defect | Repair |  | Complete |  | Completed |  | Failure to supply daily inclinometer monitoring readings as required by Instrumentation and Monitoring Plan document number Cxxx-SKC-G-STP-Cxxx-5001 entitled Instrumentation and Monitoring Plan A ETH, WTH and Grout Shaft Construction (excluding LU Asset Monitoring).
| 02SL - Stations (LUL) | Cxxx-NCR-000250 | NCR | Pile 023 3No. Rows of 20mm Lining Wall couplers missing over the splice zone. |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-02-29 | 2012-04-05 16:41 | 36 | 2012-02-14 | Civil - Geotechnical Engineering | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Pile Nr 23, 3No. Rows of 20mm Lining Wall couplers missing over the splice zone.
| 02SL - Stations (LUL) | Cxxx-NCR-000251 | NCR | Orientation of extension / starter bars for Pile 33 into capping beam incorrect. Bars were 90 degress out of position |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-02-29 | 2012-02-29 18:23 | 0 | 2012-02-06 | Civil - Geotechnical Engineering | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | The orientation of the starter bars into the capping beam had not been detailed clearly enough on fabrication drawing. Mistake did not get picked up until on-site.
| 02SL - Stations (LUL) | Cxxx-NCR-000252 | NCR | Pile 031 |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-03-08 | 2012-04-05 16:44 | 28 | 2012-02-14 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Design | Rework |  | Complete |  | Completed |  | P31: 2No. Rows of 20mm Lining Wall couplers missing.Unable to construct cage to current designed format. Issue with installing required couplers as detailed.
| 02SL - Stations (LUL) | Cxxx-NCR-000254 | NCR | Pile 33 casing out of verticality. |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-03-31 | 2012-06-18 11:13 | 79 | 2012-02-06 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Pile 33 casing out of verticality. Pile kicking in north direrction. Approximately 35mm out at base slab.
| 02SL - Stations (LUL) | Cxxx-NCR-000255 | NCR | Pile 29 |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-03-31 | 2012-03-29 14:06 | -2 | 2012-02-10 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Pile 29 over dug by 5.0m. Required depth 75.0m ATD actual depth 80.0m ATD. Human error. Setting oout engineer gave driller wrong information, before mistake was highlighted required toe level had been over dug by 5.0m
| 02SL - Stations (LUL) | Cxxx-NCR-000257 | NCR | Testing and sampling methodologies |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-02-17 | 2012-03-07 14:29 | 19 | 2012-02-08 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | Records were not available to demonstrate that testing and sampling methodologies included in the guidance section of the SPERW and BS 8500 referenced documents were in place for ambient temperature measurement and on site calibrations of the mud balance and Marshal funnel.
| 02SL - Stations (LUL) | Cxxx-NCR-000258 | NCR | Protection of compression test specimens |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-02-17 | 2012-03-07 14:32 | 19 | 2012-02-08 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | The specified requirement to protect the test specimen in the mold from dehydration was not evident.
| 02SL - Stations (LUL) | Cxxx-NCR-000260 | NCR | Extensometer (number 9) |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-03-31 | 2012-03-23 16:06 | -8 | 2012-02-14 | Surveying - Instrumentation and Monitoring | 500 |  | System Defect | Rework |  | Complete |  | Completed |  | Failure to deliver a working extensometer in order to detect possible ground movements as detailed in the contract specifications volume 2C and as required by Instrumentation and Monitoring Plan document number Cxxx-SKC-G-STP-Cxxx-5001 entitled Instrumentation and Monitoring Plan A ETH, WTH and Grout Shaft Construction (excluding LU Asset Monitoring).
| 02SL - Stations (LUL) | Cxxx-NCR-000261 | NCR | Panel 22 |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-02-29 | 2012-02-29 18:13 | 0 | 2012-02-09 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | 6 No. loads of C40/50 concrete was poured in to panels 22 instead of C32/40
| 02SL - Stations (LUL) | Cxxx-NCR-000262 | NCR | Panel 22 incorrect steelwork |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-03-31 | 2012-03-29 14:08 | -2 | 2012-02-09 | Civil - Civil Engineering General | 500 |  | Material | Rework |  | Complete |  | Completed |  | In panel 22 a central 32mm bar from cage C2 joinging to cage C3 (NF BM16) c/w coupler prevented the remaining bars coupling up as this projected too far. The coupler was removed and a 32mm splice bar inserted to replace the removed coupler projecting 2250mm above and below the coupler (44 times bar diameter with a 1.5 factor for bentonite influence)
| 02SL - Stations (LUL) | Cxxx-NCR-000265 | NCR | Western Ticket Hall Hoarding |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-02-24 | 2012-04-30 08:18 | 66 | 2012-02-14 | Civil - Civil Engineering General | 500 |  | System Defect | Repair |  | Complete |  | Completed |  | Hoarding is not complaint with the following sections, Kickboard not in accordance with Appendix A, Hoarding not in compliance with clause 4.4.2, Hoarding not in compliance with clause 4.4.5, Hoarding not in compliance with clause 4.4.6
| 02SL - Stations (LUL) | Cxxx-NCR-000283 | NCR | Panel 3 reinforcement that projects into the capping beam |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-03-31 | 2012-03-29 14:15 | -2 | 2012-02-27 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Material | Rework |  | Complete |  | Completed |  | The element of reinforcement that projects in to the capping beam, bar marks 11 to 14, on panel 3 is 158mm shorter than required as installed. Allowable tolerance within the specification is +50mm - 150mm. Drawings and bars bending schedules are as follows Cxxx-SKC-C-DWG-Cxxx-50005 Rev C01 Cxxx-SKC-C-DWG-Cxxx-50006 Rev C01 Cxxx-SKC-C-TSC-Cxxx-50005 Rev C01
| 02SL - Stations (LUL) | Cxxx-NCR-000284 | NCR | Pile 69 constructed with the incorrect strength concrete. The design required a C32/40 concrete mix, pile constructed using C40/50 concrete mix. |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-03-31 | 2012-03-23 16:27 | -8 | 2012-02-27 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The design required a C32/40 concrete mix, due to a mix up at the batching plant 5 loads of C40/50 were sent to site and the first load partially discharged before the mistake was picked up. As the mix was of a greater strength than required site management took the decision to complete the pile with C40/50 mix.
| 02SL - Stations (LUL) | Cxxx-NCR-000285 | NCR | Pile 131 finish cage level |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-03-31 | 2012-04-29 15:19 | 29 | 2012-02-27 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | On removal of the cage hanging chains the cage dropped to gOmm below the finished designed level.
| 02SL - Stations (LUL) | Cxxx-NCR-000288 | NCR | Water main pressure test |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-03-31 | 2012-04-29 17:14 | 29 | 2012-04-02 | Utilities Engineering - Water | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | During the pressure test on the new 125mm water main at Tenterden Street one of the electro fusion welds started leaking.
| 02SL - Stations (LUL) | Cxxx-NCR-000306 | NCR | No notification of inspection for pile breakdown |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-03-23 | 2012-03-23 15:57 | 0 | 2012-03-09 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | No notifications were provided for the inspections and test for the pile breakdown work at ETH as specified on the ITP Cxxx-SKC-O4-ITP-Cxxx-50020 rev 3.
| 02SL - Stations (LUL) | Cxxx-NCR-000307 | NCR | No notification of inspection for NW shaft excavation to formation and formwork erection |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-03-23 | 2012-03-23 16:00 | 0 | 2012-03-09 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | No notifications were provided for the inspections and test for the NW shaft excavation to formation and formwork erection at ETH as specified on the ITP Cxxx-SKC-O4-ITP-Cxxx-50019 rev 3.
| 02SL - Stations (LUL) | Cxxx-NCR-000311 | NCR | Pile 21 cage finish level 200mm above design level |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-03-30 | 2012-04-29 15:36 | 30 | 2012-03-15 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Pile 21 Cage lifted 200mm (above design level) on extraction of casing.
| 02SL - Stations (LUL) | Cxxx-NCR-000312 | NCR | Pile 136 unable to determine finish cage level so assumed to be low |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-09-07 | 2012-09-06 15:27 | -1 | 2012-03-15 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Pile 136 Cage installed high to allow for slumping during casing extraction, however the tape attached to the cage snapped so the final level could not be established.
| 02SL - Stations (LUL) | Cxxx-NCR-000314 | NCR | Curing to ETH NW shaft prop slab |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-04-06 | 2012-05-23 07:54 | 47 | 2012-03-15 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Curring of slab not in accordance with the WPP Cxxx-SKC-O1-STP-Cxxx-50035 & TB Cxxx-SKC-O1-RGN-Cxxx-50135
| 02SL - Stations (LUL) | Cxxx-NCR-000315 | NCR | Non tracerable marker tape |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-03-30 | 2012-04-29 15:45 | 30 | 2012-03-15 | Utilities Engineering - Water | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Non tracerable marker tape was used on a section of water main
| 02SL - Stations (LUL) | Cxxx-NCR-000316 | NCR | Pile 50 28 day concrete cube results low strength. |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-04-30 | 2012-04-29 15:51 | -1 | 2012-03-15 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | The two sets of 28 day concrete test results for pile 50 lower Ihan expected by 15.5% and 7.8%. The two sets of cubes taken had similar 7 day and 28 day results as detailed below Set 51076639 7 day - 33.1 Nfmm2 28 day - 42.25 Nfmm2 (average of 2 results) Sel 51076638 7 day - 28.5 Nfmm2 28 day - 46.1 Nfmm2 (average of 2 res ults)
| 02SL - Stations (LUL) | Cxxx-NCR-000322 | NCR | ETH - Piles 39, 44 and 49 (North West Shaft) |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-03-23 | 2012-04-29 17:12 | 37 | 2012-03-22 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | The above noted details was not agreed and developed in sufficient time to be captured by the construction team and built into the pre-fabricated pile cages. As a result the reinforcement intent details has been used in piles 39, 44 and 49. It will prove impossible to fix the capping beam with the anchor bars as currently fixed.
| 02SL - Stations (LUL) | Cxxx-NCR-000334 | NCR | This NCR covers Pile 23, 26, 29, 43, 48, 172, 174, 190, 191, 194 and 196 with the top layer of Temporary prop slab |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-04-30 | 2012-04-29 17:16 | -1 | 2012-04-02 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | This NCR covers Pile 23, 26, 29, 43, 48, 172, 174, 190, 191, 194 and 196 with the top layer of Temporary prop slab couplers being out of position- please refere to the attached as built drawings for the levels.
| 02SL - Stations (LUL) | Cxxx-NCR-000335 | NCR | Concrete seepage into pile 68 from pile 71 |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-04-30 | 2012-04-29 17:18 | -1 | 2012-04-03 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Piles 71 And 68 had been cased, drilled and flooded, with both bottom cages installed; the concrete was being placed in Pile 71 up until the first stage, circa 17 linear metres of concrete. It was noted that the concrete was not rising and it was discovered that concrete had burst through to Pile 68, located some 3.5 metres clear distance away. Pile 71 was completed and the concrete remained at a stable level. There are no quality defects with Pile 71. Pile 68 has - 12.6 metres of C40/50 concrete in which has seeped in from pile 71 which is 5m low. The quality of tile concrete cannot be guaranteed, however the concrete has gone off.
| 02SL - Stations (LUL) | Cxxx-NCR-000338 | NCR | Erection of Plunge column P01p |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-04-30 | 2012-05-08 12:54 | 8 | 2012-04-26 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Could not connect splice connections on site
| 02SL - Stations (LUL) | Cxxx-NCR-000343 | NCR | Non calibrated Torque wrench |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-04-30 | 2012-05-11 12:04 | 11 | 2012-05-08 | Utilities Engineering - Water | 500 |  | Equipment Breakdown | Reject |  | Complete |  | Completed |  | Use of Non calibrated torque wrench being used on site-have requested calibration cert on numerous occassions Torque wrench nomber SKU18289-001
| 02SL - Stations (LUL) | Cxxx-NCR-000350 | NCR | Drill and Post Fix of dowels from Pile 44 & 49 |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-04-30 | 2012-05-08 12:56 | 8 | 2012-04-18 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | had to drill and fix bars at Level 1 in Piles 44 and 49 as there were no threaded bars to complete the coupling. The bars were replaced by drilling and fixing the 25mm stock steel
| 02SL - Stations (LUL) | Cxxx-NCR-000351 | NCR | • P49 has been set out in the incorrect location and subsequently piled |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-05-31 | 2012-05-23 07:56 | -8 | 2012-04-23 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Supervision/Management | Reject |  | Complete |  | Completed |  | Bearing pile P49 has been set out in the incorrect location and subsequently piled there. The asbuilt position of the pile is: Easting: 79131.997 ; Northing: 35857.872 A list of pile setting-out coordinates was requested from the CAD technician. An uncontrolled list was created and uploaded into the Total Station. Unfortunately this list was based on the C1 revision of drawing number Cxxx-__-S-DDL-Cxxx-52171. The drawing had been superseded by revision C2 where pile P49 had been moved by 1.8 metres. The coordinates in the Total Station had not been updated, and neither had the uncontrolled co-ordinate list. The pile construction record had not been signed by the surveyor (although it had been checked in the surveyor’s notebook).
| 02SL - Stations (LUL) | Cxxx-NCR-000352 | NCR | Capping Beam pour has had a scaffold tube left in and been finished around. |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-08-31 | 2012-07-20 15:34 | -42 | 2012-07-20 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Scaffold handrail tube cast into top of capping beam on northern side of NW shaft.
| 02SL - Stations (LUL) | Cxxx-NCR-000372 | NCR | Reinforcement cage for panel 26 being installed with a Bentonite sand content above 4%. |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-05-31 | 2012-05-08 13:07 | -23 | 2012-04-26 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | __ started to install the reinforcement cage on Friday 13th April, at this point were satisfied that the sand content was below 4%, having stayed until 10pm on Thursday 3rd for desanding purposes. The problem with the cage installation and toe level difference was noticed at approx 1pm, which resulted in the reinforcement cage being removed from its position on the West side of the panel and placed into the East, this was done to allow the grab to excavate the panel and alleviate the toe difference. When cage installation continued, cementation came across the same problem, and decided that due to working hours due to exceed a 24hour period if concreting was to take place. The pour was re-scheduled for Monday 16th April. The top cage was removed and laid flat on the ground, but the couplers for the remaining cages were unable to be undone, and a decision was made to leave the bottom 3 cages in the panel. Saturday 17th April was spent excavating the panel toe from 48.2m, to 49.1m below guide wall. This operation would have disturbed the sand channels within the excavation, causing the bentonite sand content to rise. A test was taken at 1300hrs on Saturday with showed a 6% sand content. At the end of the shift, the bottom 3 cages we lowered back into the panel, the plan being to remove them on Monday 16th and jet wash the entire length, to remove any sand or fines which settled over the weekend period. On Monday 16th April, the cages were lifted from the panel, and all settled sand or fines were jet washed off. The cages were then replaced into the panel for safety reasons, we felt that the cages posed a high risk being suspended above ground by the crane for an extended period. The tremmies were then installed, and desanding was started again. At approx 1600hrs, a sample of Bentonite was taken and tested to be less than 4% sand content. This sample was kept for the CRL Pre concrete check, but was rejected as a true sample by __. At this point, __ were busy lowering cages into the panel and told Raj that a future sample would have to be taken at a later time, once the cage installation was complete, to avoid losing the sampling tool down the panel. At 1800hrs, a sample was taken with CRL and witnesses, which produced a sand content of 0.75%.
| 02SL - Stations (LUL) | Cxxx-NCR-000379 | NCR | Out of slump specification concrete used in capping beam pour 2 |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-05-31 | 2012-05-18 11:41 | -13 | 2012-05-08 | Architectural - General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | 1xload of concrete that was 10mm above the S3 slump tolerance of 80mm - 180mm was placed into the CB pour on Monday 16th April. This was the first load within this pour and was 10mm mix due to the dense rebar at the bottom of the CB. During this stage of the pour Engineer (__) was in attendance along with the CrossRail Inspector (__). Whilst the initial slump test was being carried out by __ the concrete skip was loaded and the concrete was placed into the CB. Once the Engineer witnessed the out of tolerance results the concrete was already placed into the CB.
| 02SL - Stations (LUL) | Cxxx-NCR-000380 | NCR | Cover meter surveys have shown that the cover to steel on the level 3 NWS slab is outside of tolerance |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-08-31 | 2012-08-17 15:06 | -14 | 2012-07-20 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Cover meter surveys have shown that the cover to steel on the level 3 NWS slab is outside of tolerance (on the high side) in some areas
| 02SL - Stations (LUL) | Cxxx-NCR-000382 | NCR | Couplers in Level 4 prop slab - inncorrectly detailed |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-05-04 | 2012-05-09 17:09 | 5 | 2012-05-01 | Civil - Civil Engineering General | 500 |  | Design | Rework |  | Complete |  | Completed |  | temporary works designers have reviewed the load cases and analysis and confirmed that B25 are required.
| 02SL - Stations (LUL) | Cxxx-NCR-000387 | NCR | Damage to the concrete in the NW Shaft on prop slab level 3 |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-08-03 | 2012-07-19 15:33 | -15 | 2012-07-10 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Damage to the concrete in the NW Shaft on prop slab level 3
| 02SL - Stations (LUL) | Cxxx-NCR-000394 | NCR | Error in fabrication of d wall panel 20 middle cage |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-05-18 | 2012-05-18 11:37 | 0 | 2012-05-09 | Civil - Civil Engineering General | 500 |  | Material | Rework |  | Complete |  | Completed |  | D Wall panel 20 middle cage was fabricated offsite with 28nr B25, bar mark 15, installed 1m lower than designed. (see attached sketch) Additionally the splice couplers between cages 2 and 3 were installed out of tolerance (see attached sketch for levels). The bars were installed at the wrong level by __ Reinforcements Ltd, but picked during the on-site check.
| 02SL - Stations (LUL) | Cxxx-NCR-000395 | NCR | Out of position of bearing piles P02t & P05t |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-06-30 | 2012-06-29 14:17 | -1 | 2012-05-10 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Design | Use As-Is |  | Complete |  | Completed |  | The above piles have not been constructed in accordance with __ design
| 02SL - Stations (LUL) | Cxxx-NCR-000397 | NCR | Temporary works design in Masterplan Shaft |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-05-31 | 2012-05-23 08:17 | -8 | 2012-05-11 | Civil - Civil Engineering General | 500 |  | Design | Rework |  | Complete |  | Completed |  | Design changes by __ have failed to be communicated to the temporary works designer, such that the completed proping and scheme has been designed with piles out of position. Piles P02 and 05 are in the correct position for the TW design but circa 1300 and 350mm. Pile P49 is 1800mm out of position whlist P06p has been installed in the correct position for the permanent works design but is out of position for the TW design.
| 02SL - Stations (LUL) | Cxxx-NCR-000398 | NCR | Pile 125 temporary segmental casing dropped into the bore |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-07-31 | 2012-06-18 11:17 | -43 | 2012-05-11 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Pile 125 before placing the reinforcement cage into the bore, 2No. Segmental sections of casing are removed. The casing is then secured with a " belly band" and 2No. "supporting legs" to ensure the casing does not drop into the bore under the weight of the reinforcement cage. In this case, the 2No. "supporting legs" were not attached to the casing prior to the installation of the reinforcement cage.
| 02SL - Stations (LUL) | Cxxx-NCR-000405 | NCR | Panel 17 was over-dug by 2.1metres |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-06-30 | 2012-05-22 15:23 | -39 | 2012-05-17 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Panel 17 was over-dug by 2.1metres. Designed toe was 81.000m ATD and actural toe was 78.900mATD. Banksman wrote down depth of adjcent panel of the sequence and placed this in the banksman book. During swapping over of banksman this was not picked up as the same banksman book is used thus it was not highlighted until the panel had been dug and preperations for an airlift were underway.
| 02SL - Stations (LUL) | Cxxx-NCR-000422 | NCR | BOS - ETH, Inclinometer within pile 59 |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-05-29 | 2012-07-19 15:30 | 51 | 2012-05-22 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Damaged | Use As-Is |  | Complete |  | Completed |  | Upon breaking down the piles for capping beam construction it has become evident that this tube is blocked.
| 02SL - Stations (LUL) | Cxxx-NCR-000423 | NCR | ETH Capping Beam, incorrectly cut/bent reinforcement |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-06-08 | 2012-06-18 11:19 | 10 | 2012-05-22 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Bar is incorrectly cut and bent. The __ drawing does not require a specific bob length and following discussions with JM it is agreed that the length od 500mm is suffice. As such it is proposed to use as is.
| 02SL - Stations (LUL) | Cxxx-NCR-000431 | NCR | ETH - Capping Beam Pour 4, Concrete Shortfall |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-05-24 | 2012-06-18 11:22 | 25 | 2012-05-24 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The site team formed a construction joint approx' 200mm deep in the beam approx 2m in length in order to finish the pour, see attached sketches. The joint will be prepared to remove laitence, and the __ slurry applied to the as-built construction joint. __ have confirmed that the joint is satisfactory for the performance of the waterproofing systema they will uphold the warranty. It is proposed to cast the shortage in pour 4 within pour 5.
| 02SL - Stations (LUL) | Cxxx-NCR-000444 | NCR | No flow test carried on concrete to pile 36 |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-06-29 | 2012-07-12 19:15 | 13 | 2012-05-28 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | No flow test carried on concrete to pile 36, four concrete cube were taken
| 02SL - Stations (LUL) | Cxxx-NCR-000445 | NCR | Plunge column P25p was delivered to site and installed with 10 no. 33mm diameter bolt holes omitted |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-08-03 | 2012-08-06 12:17 | 3 | 2012-06-07 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | Plunge column P25p was delivered to site and installed in the correct location but incorrect orientation ,resulting in 10 no. 33mm diameter bolt holes being out of position.
| 02SL - Stations (LUL) | Cxxx-NCR-000452 | NCR | Pile P125 exceeds 60 hrs construction time |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-06-30 | 2012-06-18 11:25 | -12 | 2012-05-30 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Pile P125 exceeds 60 hrs construction time
| 02SL - Stations (LUL) | Cxxx-NCR-000466 | NCR | Pile 26 construction exceeded the specified time limit of 48hrs |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-07-12 | 2012-07-12 19:20 | 0 | 2012-06-07 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Pile 26 was drilled below Cut Off Level at 09:30 on 30/05/12. The concrete was completed above this level at 16:25 on 01/06/12. The concrete was not completed above the raft slab level in the time specified for an open bore (48 hours) .Cage delivery did not occur on the expected time 08:00 on 31/05/12
| 02SL - Stations (LUL) | Cxxx-NCR-000467 | NCR | Migration of gravel from pile 43 into pile 42 during construction of pile 42. |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-07-31 | 2012-06-29 14:12 | -32 | 2012-06-11 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Design | Rework |  | Complete |  | Completed |  | Whilst drilling Pile 42, the single sized granular backfill from the previously completed Piles 41 and 43 has fallen into the bore hole. It is unclear at what level the stone breached from Piles 41 and 43. Pile 42 was drilled to a depth of approximately R.L. 78.00, a depth of 43 metres from Piling Platform when this occurred. The drilling reached and progressed past the raft slab formation level at 09:45 on 31/05/12. The excavation has been exposed below raft slab level in excess of the specified time limit (48 hours).
| 02SL - Stations (LUL) | Cxxx-NCR-000477 | NCR | Utilities-Reinstatement of NE connection pit area and installation of valve spindle covers |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-07-31 | 2012-07-19 15:24 | -12 | 2012-06-20 | Utilities Engineering - Utilities General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | __ reinstatement has not been carried out in accordance with the specfification for surface finish and tolerances. Valve spindle boxes have not been installed to the correct line and level
| 02SL - Stations (LUL) | Cxxx-NCR-000479 | NCR | ETH - Pile cage rotation P19 and P21 |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-08-31 | 2012-08-13 12:00 | -18 | 2012-06-13 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Capping beam bottom matt reinforcement has satisfactury been installed with out out the need to cut any of the piles starter bars. rotation of the cage can only be evaluated once the top down construction has commenced and the couplers exposed.
| 02SL - Stations (LUL) | Cxxx-NCR-000482 | NCR | ETH-Pile 095 cage fabrication error |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-07-30 | 2012-06-29 14:10 | -31 | 2012-06-13 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | The super reinforcement consist of 9B50 bars located as an inner cage within the main cage was fabricated by __ Ltd 600mm low in the cage. It should have commenced at 104.000mATD but actually commenced at 103.370mATD and is the correct length of 11.000m
| 02SL - Stations (LUL) | Cxxx-NCR-000493 | NCR | ETH-capping beam 09 incorrect strength concrete used in pour |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-07-31 | 2012-07-12 18:40 | -19 | 2012-06-21 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | ST4 concrete mix was used in capping pour 09 instead of the approved 32\40 mix
| 02SL - Stations (LUL) | Cxxx-NCR-000503 | NCR | ETH-Thurst block not constructed prior to backfilling to 7" connection |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-07-31 | 2012-08-10 10:59 | 10 | 2012-06-27 | Utilities Engineering - Water | 500 |  | Material | Rework |  | Complete |  | Completed |  | ETH-Thurst block not constructed prior to backfilling to 7" connection
| 02SL - Stations (LUL) | Cxxx-NCR-000504 | NCR | ETH- Bearing pile P76 was over dug by 2.2m |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-07-31 | 2012-07-17 09:45 | -14 | 2012-06-21 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | ETH- Bearing pile P76 was over dug by 2.2m and cast with this overdig
| 02SL - Stations (LUL) | Cxxx-NCR-000511 | NCR | ETH - Secant Piles 98 and 103 |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-07-12 | 2012-07-19 15:19 | 7 | 2012-06-26 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | As built
| 02SL - Stations (LUL) | Cxxx-NCR-000512 | NCR | Plunge Columns in GF Slab - GL D-F |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-06-27 | 2012-07-17 09:51 | 20 | 2012-06-26 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Columns constructed and groundfloor slab blinding cast.
| 02SL - Stations (LUL) | Cxxx-NCR-000516 | NCR | ETH - Sonic Logging of piles 66, 70 and 80 |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-06-28 | 2012-08-10 11:21 | 43 | 2012-06-27 | Civil - Geotechnical Engineering | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Piles have been completed and logged but there are blockages in the logging ducts now.
| 02SL - Stations (LUL) | Cxxx-NCR-000526 | NCR | ETH - Loss of GSHP network following pile breakdown |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-07-26 | 2012-07-19 16:43 | -7 | 2012-07-03 | Civil - Civil Engineering General | 500 |  | Damaged | Use As-Is |  | Complete |  | Completed |  | Following the top down construction of the NWS and the construction of the level 8 base slab. It has become evident that following testing of the loops there are blockages that will reduce the number of loops installed that are servicable to CRL for incorporating within the GSHP permanent works scheme.
| 02SL - Stations (LUL) | Cxxx-NCR-000531 | NCR | Top mat reinforcement high in GF slab |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-07-06 | 2012-07-19 15:16 | 13 | 2012-07-05 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | The top mat couplers (BMk 15) installed in the 750mm slab cast in for the lower 500mm slab betweenGL 3/4 and GL E and F have been fixed too high. As a result the cover availanle at the interface between the two sections will be reduced to 35mm nom.
| 02SL - Stations (LUL) | Cxxx-NCR-000540 | NCR | Pile 070 Bottom Cage |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-07-13 | 2012-07-19 15:13 | 6 | 2012-07-09 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | The pile construction record states that the cage has dropped by 360mm (with couplers 20 and 5mm low from the reference band). The couplers are therefore out of tolerance.
| 02SL - Stations (LUL) | Cxxx-NCR-000541 | NCR | ETH- Damage to west end of capping beam CB06,Master shaft area during blinding breakout |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-08-24 | 2012-09-03 14:56 | 10 | 2012-07-20 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | ETH- Damage to west end of capping beam CB06 Master shaft area during blinding breakout
| 02SL - Stations (LUL) | Cxxx-NCR-000545 | NCR | ETH - Embed plate PC8 |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-08-31 | 2012-08-13 12:05 | -18 | 2012-07-11 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Embed plate has been installed as per the attached survey using the available PC8 embed as the revised embed plate PC8a was not available on site to be installed.
| 02SL - Stations (LUL) | Cxxx-NCR-000546 | NCR | ETH - Couplers in CB10 for the 250mm thick recess slab. |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-08-31 | 2012-07-31 11:50 | -31 | 2012-07-11 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | Capping beam and slab have been poured.
| 02SL - Stations (LUL) | Cxxx-NCR-000547 | NCR | ETH - Wall starter bars installed incorrectly |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-08-31 | 2012-07-25 12:25 | -37 | 2012-07-11 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | Capping beam cast and complete.
| 02SL - Stations (LUL) | Cxxx-NCR-000548 | NCR | ETH - Location of PC9 |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-11-30 | 2012-11-28 15:39 | -2 | 2012-07-11 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Capping beam cast and embedment plate secured.
| 02SL - Stations (LUL) | Cxxx-NCR-000551 | NCR | ETH - Base of trough in GF Slab to high |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-08-31 | 2012-07-25 12:13 | -37 | 2012-07-12 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Concrete is sound but excessively high. It is proposed to scabble back the over pour concrete and to apply a polymer modified concrete repair material to the base in order to restore the required finish.
| 02SL - Stations (LUL) | Cxxx-NCR-000553 | NCR | ETH-Temporary concrete upstand to protect holding down bolts |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-08-31 | 2012-07-25 12:11 | -37 | 2012-07-12 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | C50/60 mix was actually used on site instead of the specified as a C20/25 concrete mix
| 02SL - Stations (LUL) | Cxxx-NCR-000554 | NCR | ETH-Male Wall Pile 84, on the corner of the south eastern edge of the site was bored out of vertically tolerance. |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-08-31 | 2012-07-25 12:06 | -37 | 2012-07-17 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The as built vertically is 1 in 85, with a tolerence of 1 in 200. There is still an interlock with female pile 1083 at 20m depth below ground level of 101mm, with an interlock of 233 with female pile 084. This is due to the fact the as built position of the top of the casing is 40mm north of its designed position.
| 02SL - Stations (LUL) | Cxxx-NCR-000555 | NCR | ETH - PC5 Embedment Plate |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-08-31 | 2012-08-17 15:03 | -14 | 2012-07-13 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | PC5 is cast into the capping beam circa 200mm out of position.
| 02SL - Stations (LUL) | Cxxx-NCR-000556 | NCR | ETH-ground floor slab pour 1 G/L e-f &1-2 localised reduced cover to bottom level slab reinforcement |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-07-21 | 2012-07-25 12:02 | 4 | 2012-07-13 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Reduced cover to bottom level reinforcement in G/F slab pour ,cover approx 35mmm over an area of 4-6 bars .this is due to the position of capping beam couplers ( Tentertan street)
| 02SL - Stations (LUL) | Cxxx-NCR-000563 | NCR | ETH-Male secant pile 102 was installed outside of the vertically tollerence of 1:200 |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-08-31 | 2012-08-06 12:27 | -25 | 2012-07-24 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Male secant pile 102 was installed outside of the vertically tollerence of 1:200. the reduced dimensions are 25mm north and 51mm east over 10metres, giving a tolerence of 1:174. interlock still remains at the toe of the females 20metres from Piling Platform Level
| 02SL - Stations (LUL) | Cxxx-NCR-000564 | NCR | ETH- capping beam CB09 -four number 150 dia galvanised steel sleeves |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-08-31 | 2012-08-06 12:23 | -25 | 2012-07-20 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Existing purchased 150 dia galvanised steel ducts did not extend the full width of the capping beam CB09
| 02SL - Stations (LUL) | Cxxx-NCR-000565 | NCR | ETH- Pile P21p Cage level out of tolerance |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-08-31 | 2012-08-17 15:09 | -14 | 2012-07-25 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Bearing Pile P21p cage was installed 300mm low. A dip too Top of Steel was given to the concrete ganger of 26.9. however a break down of communication occurred and the cage was attempted to be inserted to 27.6m. Once the error was found the cage could not be lifted up to its designed position and remained at 27.2m
| 02SL - Stations (LUL) | Cxxx-NCR-000568 | NCR | ETH- Pile 100 was bored with the casing installed outside of the 1 in 200 vertically tolerences |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-08-25 | 2012-08-13 12:10 | -12 | 2012-07-25 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Male Secant Pile 100 was bored with the casing installed outside of the 1 in 200 vertically tolerences. The piles vertically over 10m was 35mm east and 55mm south, resulting in a vertically of 1 in 153
| 02SL - Stations (LUL) | Cxxx-NCR-000572 | NCR | ETH - Clash of terminator units on the pile super reinforcement with capping beam bottom mat |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-08-31 | 2012-08-06 12:20 | -25 | 2012-07-27 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Piles are constructed and capping beam steel is ready to be fixed.
| 02SL - Stations (LUL) | Cxxx-NCR-000573 | NCR | ETH - Sonic logging pile 44 |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-08-31 | 2012-08-17 15:15 | -14 | 2012-08-01 | Civil - Geotechnical Engineering | 500 |  | Damaged | Rework |  | Complete |  | Completed |  | One of the logging tubes is blocked at 6m depth within the pile.
| 02SL - Stations (LUL) | Cxxx-NCR-000595 | NCR | ETH-Damage to underside of Slab 1 master shaft area |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-10-26 | 2012-11-09 08:39 | 14 | 2012-08-31 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | damage to underside of RC slab 1 in various location,rebar exposed and damaged this has beed cause by the pecker during the removeal of blinding material.
| 02SL - Stations (LUL) | Cxxx-NCR-000598 | NCR | ETH-Capping Beam CB03 |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-11-30 | 2012-11-14 17:26 | -16 | 2012-08-30 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | A post pour inspection of Capping Beam CB03 has raised an issue with the surface finish of one of the higher sections. Concrete does not seem to have surrounded the spacer blocks properly and has left a poor surface finish. The other section has some indentations from water pooling on the polythene soon after the concrete was poured
| 02SL - Stations (LUL) | Cxxx-NCR-000602 | NCR | WTH-Capping beam pour CB05 |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-09-29 | 2012-09-18 09:30 | -11 | 2012-09-03 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | Not following the ITP ,commence concrete pour before the installation of holding down bolts were complete and not completing the pre pour concrete check sheet, therefore not observing the hold point on the ITP.
| 02SL - Stations (LUL) | Cxxx-NCR-000603 | NCR | ETH-The cage for Pile 9- male secant pile dropped upon removal of the hanging chains |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-11-30 | 2012-11-15 11:06 | -15 | 2012-09-03 | Civil - Geotechnical Engineering | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The cage for Pile 9- male secant pile dropped upon removal of the hanging chains and extraction of the casings. The final Top of Steel level is 117.590, where designed is 117.800 mATD
| 02SL - Stations (LUL) | Cxxx-NCR-000604 | NCR | ETH-Pile 09P incorrect concrete used |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-11-30 | 2012-11-15 11:16 | -15 | 2012-09-10 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Pile 09p constructed with one load of incorrect strength concrete. The design required a C32/40 concrete mix, one load of C35/45 concrete mix was placed whilst concreting. The design required a C32/40 concrete mix, due to a mix up at the batching plant 1 load of C35/45 was sent to site by mistake. The load was for another __ job in Paddington, by arrived at site and the load was discharged into the bore. As the mix was of a greater strength than required site management took the decision to complete the pile.
| 02SL - Stations (LUL) | Cxxx-NCR-000605 | NCR | ETH-Bearing Pile P31p with a toe 400mm above design and the cage installed 395mm higher than designed. |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-10-27 | 2012-11-09 09:13 | 13 | 2012-09-10 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Bearing Pile P31p with a toe 400mm above design and the cage installed 395mm higher than designed.
| 02SL - Stations (LUL) | Cxxx-NCR-000613 | NCR | Low 56 days concrete strength pile P39,59,60,30 and 57 |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-05-09 | 2013-05-07 12:44 | -2 | 2012-11-29 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Low 56 days concrete strength pile P39.59,60,30 and 57
| 02SL - Stations (LUL) | Cxxx-NCR-000614 | NCR | WTH-GL G, ground beam W-B0-04 intersects the capping beam. Soffit of the ground beam is 300mm lower than the capping beam soffit. |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-10-26 | 2012-10-12 15:59 | -14 | 2012-09-10 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | GL G, ground beam W-B0-04 intersects the capping beam. Soffit of the ground beam is 300mm lower than the capping beam soffit. There was a requirement of extra d wall breakdown to accommodate the construction of the ground beam and to allow fixing of reinforcement. This detail has been over sighted.
| 02SL - Stations (LUL) | Cxxx-NCR-000616 | NCR | WTH Capping Beam CB07 wall starters BM20 have been cast in at wrong position and spacing. |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-11-30 | 2012-11-13 10:34 | -17 | 2012-10-08 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | During capping beam W-CB-07 &08 construction, wall starters BM20 have been cast in at wrong position and spacing.
| 02SL - Stations (LUL) | Cxxx-NCR-000619 | NCR | WTH-Piezo BST32R damaged during excavation for the capping beam |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-10-31 | 2012-10-05 09:28 | -26 | 2012-09-18 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Piezo BST32R damaged during excavation for the capping beam. Data cannot be read weekly as required in specification.
| 02SL - Stations (LUL) | Cxxx-NCR-000620 | NCR | WTH-Out of specification concrete used in CB03a/b pour |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-10-31 | 2012-10-12 15:55 | -19 | 2012-09-18 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | 2m3 concrete load delivered for WTH capping beam pour 3A/3B was out of specification (slump 240, instead of S3 slump (80-180).The concrete could not be rejected and was used due to batching plant closed. However only 1m3 was actually used, this was mixed with the existing concrete inside the pump/ lines.
| 02SL - Stations (LUL) | Cxxx-NCR-000621 | NCR | ETH- Damage to Capping beam pour ref 07 whilst breaking out Guide walls |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-11-09 | 2012-11-09 09:22 | 0 | 2012-09-18 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | ETH- Damage to Capping beam pour ref 07 whilst breaking out Guide walls and pile breakdown
| 02SL - Stations (LUL) | Cxxx-NCR-000627 | NCR | WTH- D wall panel 27 installation level of reinforcement cage |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-10-31 | 2012-10-12 15:40 | -19 | 2012-10-05 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Following excavation & initial breakdown of d-wall panel 27, the reinforcement cages have been found to be installed lower than design top of steel level. The required top of steel level is 119.000 for both the north & the east leaf cage sections (drawing Cxxx-SKC-C-DWG-Cxxx-50053, 54 & 78 Rev C01)
| 02SL - Stations (LUL) | Cxxx-NCR-000637 | NCR | ETH - Couplers in CB02 for GF Slab |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-10-26 | 2012-10-12 15:43 | -14 | 2012-10-02 | Civil - Structural Engineering | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Bars are cast into the pour. Information to be provided to Cxxx for ordering of continuity couplers.
| 02SL - Stations (LUL) | Cxxx-NCR-000644 | NCR | WTH- surface cracks to capping beam pour 2 |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-01-17 | 2013-01-09 17:46 | -8 | 2012-10-04 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | WTH-Surface cracks to capping beam pour 2
| 02SL - Stations (LUL) | Cxxx-NCR-000651 | NCR | WTH- Missing rebar from capping beam CB 06 /pour reference 06 |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-01-18 | 2013-01-21 10:21 | 3 | 2012-10-08 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | 1- 34 No bars (BM 20) have been missed out from the capping beam pour. (see attached sketch) 2- 18 No bars (BM58) have been missed out from the capping beam pour. )see attached sketch) 3- 32 No bars (BM50) within the up stand have been detailed as 20mm diameter bars. These are coupled with 16mm diameter bars some of which are already cast in the capping beam pour.
| 02SL - Stations (LUL) | Cxxx-NCR-000652 | NCR | WTH curing to capping beam pour17 |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-10-31 | 2012-11-13 10:22 | 13 | 2012-10-08 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | This has constantly been a problem on this section of works with reference to curing of concrete surface on completion of a pour .No curing of the concrete surface was carried out to the Capping beam pour 17 completed on Saturday 6th October until Monday morning 8th October. As a result of this we have raised this NCR on the above mentioned work activity.
| 02SL - Stations (LUL) | Cxxx-NCR-000653 | NCR | WTH Installation of 3no 200dia sleeves through capping beam 10 ,pour Ref 7 |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-12-07 | 2012-11-16 15:41 | -21 | 2012-10-08 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The 3no 200dia stainless steel sleeves though capping beam offset 3000mm from GL E (as shown in dwg Cxxx-__-S-DDL-Cxxx-11101) have been installed at I.L. 119.130. This is 100mm below designed specified level of I.L. 119.230.
| 02SL - Stations (LUL) | Cxxx-NCR-000658 | NCR | WTH- Capping beam pour 12 & 17(concrete testing) |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-11-30 | 2012-11-13 10:46 | -17 | 2012-10-09 | Civil - Civil Engineering General | 500 |  | System Defect | Rework |  | Complete |  | Completed |  | Concrete testing on site for Pour 12 & 17 was carried out by a qualified site engineer to the BS ,this is not inaccordance with the approved ITP which states that on site testing will be carried out by __.
| 02SL - Stations (LUL) | Cxxx-NCR-000659 | NCR | ETH- Cracks in capping beam pour 15 |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-11-30 | 2012-11-29 08:44 | -1 | 2012-10-09 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | surface cracking to capping beam 15 that exceed to requirement of the specification
| 02SL - Stations (LUL) | Cxxx-NCR-000664 | NCR | WTH-__ channels have been missed out of the capping beam pour |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-12-14 | 2012-12-06 15:01 | -8 | 2012-10-12 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is |  | Complete |  | Completed |  | __ channels have been missed out of the capping beam pour.
| 02SL - Stations (LUL) | Cxxx-NCR-000669 | NCR | ETH- Pile 137 reinforcement cage 275mm low |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-12-07 | 2012-11-16 15:45 | -21 | 2012-11-02 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Secant Wall Pile 137 cage dropped significantly upon release of the hanging chains. The cage's final position at Top of steel is 117.525m ATD. The lower steel level was only confirmed during the excavation of the Master Plan Shaft.
| 02SL - Stations (LUL) | Cxxx-NCR-000670 | NCR | ETH - Temporary base slab (-5) connection to future works |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-10-31 | 2012-11-13 10:24 | 13 | 2012-10-16 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | Piles correctly cast. All couplers on-site sized at B32.
| 02SL - Stations (LUL) | Cxxx-NCR-000675 | NCR | WTH-horizontal B20 couplers in the top of the upstand wall at gridline C/3 |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-11-23 | 2012-11-27 16:33 | 4 | 2012-10-18 | Civil - Civil Engineering General | 500 |  |  | Rework |  | Complete |  | Completed |  | The horizontal B20 couplers in the top of the upstand wall at gridline C/3 (BM 41 - 51106 Rev C01) have been cast into the wall incorrectly leaving insufficient cover to the western face & excessive cover to the eastern face.
| 02SL - Stations (LUL) | Cxxx-NCR-000676 | NCR | WTH-the horizontal starter bars cast into the upstand wall east of gridline B/4 |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-11-30 | 2012-11-28 15:40 | -2 | 2012-10-18 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | The horizontal starter bars cast into the upstand wall east of gridline B/4 (BM 130 - 51102 Rev C02) have been cast in with reduced cover to the eastern face.
| 02SL - Stations (LUL) | Cxxx-NCR-000677 | NCR | WTH-The holding down bolts for the pre-cast columns at gridline L/4 not included in pour |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-01-18 | 2012-11-28 15:43 | -51 | 2012-10-18 | Civil - Civil Engineering General | 500 |  | Design | Rework |  | Complete |  | Completed |  | The holding down bolts for the pre-cast columns at gridline L/4 (21104 Rev C01 section 378) were not cast into the capping beam pour. This was due to a misunderstanding of the detail for this element of the works. The bolt set should have been partially embedded into the capping beam to a depth of 249mm
| 02SL - Stations (LUL) | Cxxx-NCR-000678 | NCR | ETH exposed repar male piles 10 and 125 |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-11-30 | 2012-11-13 12:57 | -17 | 2012-10-18 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Exposed rebar on pile 10 at slab level 0 and pile 125 at slab level -1.
| 02SL - Stations (LUL) | Cxxx-NCR-000679 | NCR | ETH - Masterplan Shaft, cracking in level 5 slab |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-11-02 | 2012-11-13 12:59 | 11 | 2012-10-19 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Following inspection of the MPS level 5 slab, it is evident that the slab has extensive plastic settlement cracking. The slab is complete and intact otherwise.
| 02SL - Stations (LUL) | Cxxx-NCR-000680 | NCR | ETH PC plates out of position |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-12-07 | 2012-12-06 14:00 | -1 | 2012-10-19 | Civil - Structural Engineering | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Various PC plates are possitioned incorrectly. Please see as built survey.
| 02SL - Stations (LUL) | Cxxx-NCR-000681 | NCR | ETH-Secant Wall Pile 98 cage dropped significantly upon release of the hanging chains |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-12-13 | 2012-12-14 16:16 | 1 | 2012-10-24 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | Secant Wall Pile 98 cage dropped significantly upon release of the hanging chains. The cage's final position at Top of steel is 117.625m ATD. The lower steel level was only confirmed during the excavation of the Master Plan Shaft. A combination of a heavy cage, 15.966Tonnes, and release of hanging chains too early.
| 02SL - Stations (LUL) | Cxxx-NCR-000684 | NCR | ETH- Non compliance with ITP |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-11-30 | 2012-11-13 13:04 | -17 | 2012-10-24 | Civil - Civil Engineering General | 500 |  | System Defect | Repair |  | Complete |  | Completed |  | Inspection number 12.1 in the ITP states that a pre-start briefing should be given by the Engineers and Supervisors and a briefing attendance sheet completed to record this. However, this was not completed for every concrete pour for the MPS Capping Beam and Temporary Capping Beam
| 02SL - Stations (LUL) | Cxxx-NCR-000685 | NCR | WTH - Soffit slab couplers in capping beam low |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-11-30 | 2012-11-16 16:55 | -14 | 2012-10-25 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Couplers set into the capping beam (as noted in the attached sketches and photographs) have been set such that the connecting bars will not have the required minimum cover. Blinding has been cast to the design soffit level.
| 02SL - Stations (LUL) | Cxxx-NCR-000686 | NCR | WTH - Coupler installation GL4/A |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-12-14 | 2012-11-20 11:02 | -24 | 2012-10-25 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Capping beam has been cast, but the couplers for the upstand have been incorrectly positioned such that at the top of capping beam level the cover is less than the minimum required.
| 02SL - Stations (LUL) | Cxxx-NCR-000687 | NCR | ETH Blocked inclinometer tube (pile 113) |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-12-14 | 2012-11-20 17:27 | -24 | 2012-10-25 | Civil - Civil Engineering General | 500 |  | Damaged | Use As-Is |  | Complete |  | Completed |  | Inclinometer tube within pile 113 blocked at 17m below ground level.
| 02SL - Stations (LUL) | Cxxx-NCR-000693 | NCR | ETH - Concrete cube strength compliance failures for secant piles |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-12-21 | 2012-11-28 15:50 | -23 | 2012-11-05 | Geotechnical Engineering - Concrete - Bored Pile | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | Piles have been cast, cured and capping beam has been constructed. ETH has been handed over to CRL.
| 02SL - Stations (LUL) | Cxxx-NCR-000696 | NCR | WTH-Plunge column 61 in WTH on Gridline K3 |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-12-20 | 2012-12-21 13:10 | 1 | 2012-11-08 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | We have broken down P150 mix at Plunge Column 61 and level at top of column incorrect. Design Level is 117.345m and our as-built today is 118.140, meaning column is 795mm too high.
| 02SL - Stations (LUL) | Cxxx-NCR-000697 | NCR | WTH-Missed couplers in the capping beam which connect into the water beam on GL J |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-01-11 | 2012-12-21 13:15 | -21 | 2012-12-03 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | Missing couplers in the capping beam which connect into the water beam on GL J. 3No. 25mm BM61 couplers and are missing from each corner of the section where the capping beam drops deeper to form the water beam
| 02SL - Stations (LUL) | Cxxx-NCR-000698 | NCR | WTH-capping beam waterproof membrane detail |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-02-01 | 2013-02-06 17:28 | 5 | 2012-11-09 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | At construction joint between capping beam & Ground Floor Slab at Gridline E 1, __ membrane has been lapped incorrectly so that it is in the construction joint. The water path has been sealed by the use of bituthene
| 02SL - Stations (LUL) | Cxxx-NCR-000705 | NCR | WTH-capping beam coupler/reinforcement detail change on gridline 4 between gridlines H and K. |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-01-11 | 2012-12-21 13:13 | -21 | 2012-11-15 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | WTH-capping beam coupler/reinforcement detail change on gridline 4 between gridlines H and K. The couplers specified in the capping beam drawing (BM 34 on Cxxx-SKC-C-DWG-Cxxx-51076) are positional couplers which require fixing in such a way that the top section is protruding from the pour to facilitate this section being rotated onto the threaded L-bar in the slab steel. Details of the coupler top levels are not specified in the 51076 drawing. The threaded L bars (BM 05 on Cxxx-SKC-C-DWG-Cxxx-51113) are now sitting too high, once coupled into the positional coupler, to tie in with the top steel of the slab and as a result require remedial action.
| 02SL - Stations (LUL) | Cxxx-NCR-000709 | NCR | WTH -Level 0 lift pit at GL H-J/2-3 |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-12-21 | 2012-11-28 10:50 | -23 | 2012-11-15 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Please refer to attached drawing 51115. As per drawing (Section 2-2 and 3-3) bm 25 is to be provided at 150mm c/c, however when the slab at GL J/2-3 has been poured bm 25 has been cast in at 200 c/c. There are now not enough B20 bars (bm 25) in the wall at GL H-J/2-3
| 02SL - Stations (LUL) | Cxxx-NCR-000713 | NCR | WTH - Wall on GL-4, 4-3 |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-11-30 | 2012-11-28 10:53 | -2 | 2012-11-16 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | Wall has been fixed and the back form erected.
| 02SL - Stations (LUL) | Cxxx-NCR-000718 | NCR | WTH-Reinforcement - Gridline 2 (G to J) |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-12-21 | 2012-12-06 14:03 | -15 | 2012-11-20 | Civil - Civil Engineering General | 500 |  | Design | Rework |  | Complete |  | Completed |  | The detail for the reinforcement steel on Ground Beam GL2. Bar marks 20, 22, 69 and 71 have all been incorrectly detailed by __ on drawing Cxxx-SKC-C-DWG-Cxxx-51094. The reinforcing steel should have been brought to within 50mm of the concrete face 180mm West of Gridline J (Currently aprox 300mm short
| 02SL - Stations (LUL) | Cxxx-NCR-000722 | NCR | WTH - Hydrophylic strip in level 0 GLF01 (pour 1) |  | Contr |  | BOS - Bond Street Station (West) |  | 2012-12-21 | 2012-12-06 15:08 | -15 | 2012-11-26 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | A single hydrophylic strip has been applied to the north area of the slab between GL C-E+2 (see attachment for location).
| 02SL - Stations (LUL) | Cxxx-NCR-000737 | NCR | WTH- Damage to edge of concrete beam GFS between GL 3/4 ,A-B |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-01-31 | 2013-01-09 17:26 | -22 | 2012-12-06 | Civil - Excavation | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | WTH- Damage to edge of concrete beam GFS between GL 3/4 ,A-B damage carried out while excavating to Level-1.beam hit by boom of ecavator while turning.
| 02SL - Stations (LUL) | Cxxx-NCR-000738 | NCR | WTH - Failure to notify the inspection on site |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-01-11 | 2013-01-09 17:29 | -2 | 2012-12-07 | Civil - Civil Engineering General | 500 |  |  | Repair |  | Complete |  | Completed |  | Pre-pour inspection for outstanding holding down bolts pour (NCR 677) was not notified to CRL
| 02SL - Stations (LUL) | Cxxx-NCR-000739 | NCR | WTH - Pre Pour Inspection for remedial works to Holding Down Bolts at GL 4/L (NCR 677) completed and signed when it was not according to the agreed design. |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-01-11 | 2013-01-09 17:32 | -2 | 2012-12-07 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | The remedial works to Holding Down Bolts at GL 4/L was not carried out according to the agreed remedial method to NCR 677. A change to the method/design was made on site but the Pre Pour Inspection was signed off as compliant to the design without agreeing the change with the designers.
| 02SL - Stations (LUL) | Cxxx-NCR-000745 | NCR | WTH- Damaged coupler provided in plunge column C3 |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-01-31 | 2012-12-21 13:35 | -41 | 2012-12-10 | Civil - Civil Engineering General | 500 |  |  | Repair |  | Complete |  | Completed |  | -8 no. couplers have been provided in plunge column C3, however, 1 no. coupler is damaged and could not be used (south west coupler) -Consequently 1 no. bm 82 (Cxxx-SKC-C-DWG-Cxxx-51104, Section 4-4) has not been installed in the level 0 slab
| 02SL - Stations (LUL) | Cxxx-NCR-000749 | NCR | failure to notify the inspection on site |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-01-31 | 2013-01-02 09:36 | -29 | 2012-12-14 | Civil - Civil Engineering General | 500 |  | System Defect | Repair |  | Complete |  | Completed |  | Failure to notify the inspection on site of grillage up stand pour on 12th & 13th December in accordance with works information Vol 2B part 20 ( request for inspection form not submitted for Temporary works)
| 02SL - Stations (LUL) | Cxxx-NCR-000753 | NCR | WTH-Holding down bolt on the North end of the WTH at F+4 is out of position |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-02-14 | 2013-02-20 14:32 | 6 | 2013-01-23 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | The bolts were designed to go in at 876mm centres. One bolt in this set is in the correct position, however the bolt on the East side was put in 438mm from the correct bolt
| 02SL - Stations (LUL) | Cxxx-NCR-000761 | NCR | WTH soffit to ground floor concrete slab |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-11-30 | 2013-11-30 14:20 | 0 | 2013-01-17 | Civil - Civil Engineering General | 10000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Superfical damage to soffit off ground floor concrete slab as a result of removal of blinding layer (Top down construction)
| 02SL - Stations (LUL) | Cxxx-NCR-000762 | NCR | WTH-Out of tolerance concrete bulges protruding from the d-wall at level -1 |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-03-31 | 2013-02-12 10:10 | -47 | 2013-01-17 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Out of tolerance of exposed face of d-wall at level -1 (concrete bulges in wall)
| 02SL - Stations (LUL) | Cxxx-NCR-000773 | NCR | WTH - Local impact damage to plunge column C2 between collars |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-02-22 | 2013-02-20 14:36 | -2 | 2013-01-16 | Civil - Civil Engineering General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | Following the breaking out of the concrete surround from plunge column C2, it is evident that at one location the montabert chisel used to braek the concrete has damaged the south wall of the 600 x 600 SHS. The defect is approximately the size of a thumb nail and is circa 5mm deep.
| 02SL - Stations (LUL) | Cxxx-NCR-000775 | NCR | WTH - Splice details for hanging columns |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-02-22 | 2013-03-04 08:24 | 10 | 2013-01-17 | Civil - Civil Engineering General | 500 |  | Design | Rework |  | Complete |  | Completed |  | Splice has been fitted but on inspection prior to issuing the permit to load, and checking with the TW designer it has become evident that the plates installed are deficient.
| 02SL - Stations (LUL) | Cxxx-NCR-000778 | NCR | WTH - Local impact damage to soffit of Ground Floor slab |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-09-27 | 2013-09-27 14:57 | 0 | 2013-01-21 | Civil - Civil Engineering General | 10000 |  | Damaged | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | Damage to soffit off ground floor concrete slab as a result of removal of blinding layer (Top down construction).
| 02SL - Stations (LUL) | Cxxx-NCR-000784 | NCR | WTH- D wall couplers cast out of tolerance or missing/damaged at level-1 |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-02-28 | 2013-03-04 08:18 | 4 | 2013-02-08 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is |  | Complete |  | Completed |  | 1) The bottom row of couplers in the west leaf of diaphragm wall panel 17 have been surveyed by and appear to be 134mm below design level, and 84mm outside of the -50mm tolerance.
| 02SL - Stations (LUL) | Cxxx-NCR-000785 | NCR | WTH-buttress on G/L 4D |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-03-31 | 2013-03-04 08:34 | -27 | 2013-01-28 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair |  | Complete |  | Completed |  | the buttress on G/L 4D. The buttress steel was installed further North in the capping beam than was designed. Therefore we cannot achieve the design position of the buttress face which should be offset 70mm from the face of the capping beam. propose to move the face of the buttress wall in line with the face of the capping. See drawing attached of the proposed solution.
| 02SL - Stations (LUL) | Cxxx-NCR-000786 | NCR | WTH-Two missing couplers in Panel 15 |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-03-31 | 2013-03-04 08:30 | -27 | 2013-01-28 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | There are two missing couplers in Panel 15 as shown on drawing and photo
| 02SL - Stations (LUL) | Cxxx-NCR-000801 | NCR | WTH - no test records for GSHP |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-03-29 | 2013-03-22 10:05 | -7 | 2013-01-28 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | No flush or pressure test records are available for d-wall panels 17 and 26.
| 02SL - Stations (LUL) | Cxxx-NCR-000802 | NCR | WTH-Buttress on G/L 4J. 1 no BM44 was damaged during excavation works |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-03-31 | 2013-03-04 08:38 | -27 | 2013-01-29 | Civil - Civil Engineering General | 500 |  | Damaged | Repair |  | Complete |  | Completed |  | Buttress on G/L 4J. 1 no BM44 was damaged during excavation works.Coupler head was broken off as shown in the photo
| 02SL - Stations (LUL) | Cxxx-NCR-000810 | NCR | WTH-Out of position Butress reinforcement Level-1 GL4E |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-03-31 | 2013-03-04 08:44 | -27 | 2013-01-30 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | The buttress on G/L 4E. The buttress steel was installed further North in the capping beam than was designed. Therefore we cannot achieve the design position of the buttress face which should be offset 70mm from the face of the capping beam.
| 02SL - Stations (LUL) | Cxxx-NCR-000811 | NCR | WTH Missing couplers in Level-1 Buttress GL 4/H |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-03-31 | 2013-03-05 08:19 | -26 | 2013-01-31 | Civil - Civil Engineering General | 500 |  | Damaged | Rework |  | Complete |  | Completed |  | WTH Missing couplers in Level-1 Buttress GL 4/H. 1 no. missing coupler in the D-wall (for buttress 4H) and 2 no. missing couplers in the capping beam (for buttress 4H too).
| 02SL - Stations (LUL) | Cxxx-NCR-000812 | NCR | WTH-Replace damaged couplers level-1 Buttress A2 |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-03-31 | 2013-03-05 08:22 | -26 | 2013-01-31 | Civil - Civil Engineering General | 500 |  | Damaged | Rework |  | Complete |  | Completed |  | Damaged couplers in Butrress A2 level-1
| 02SL - Stations (LUL) | Cxxx-NCR-000827 | NCR | WTH -Out of position /missing couplers in D wall level-1 Panel 4,13 & 15 |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-03-31 | 2013-03-22 10:11 | -9 | 2013-02-14 | Civil - Civil Engineering General | 500 |  | System Defect | Repair |  | Complete |  | Completed |  | Panel 4-1 no coupler (BM41 from DWG Cxxx-SKC-C-DWG-Cxxx-50007) which was too low to couple steel into. The bar is just past the buttress on G/L 4H. Panel 13- 1 no coupler damaged. Drilled 3x25mm bars 350mm embedment as per procedure 50068. Panel 15- 2 couplers missing from D wall cage. Applied procedure 50068. Replaced with 6 no B25 bars. Panel 15- 3 bottom couplers 40mm in buttress B2 damaged. Replaced with 9 no 25mm bars.
| 02SL - Stations (LUL) | Cxxx-NCR-000831 | NCR | WTH-Buttress level -i grid line 3M |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-03-30 | 2013-04-11 13:51 | 12 | 2013-02-14 | Civil - Civil Engineering General | 500 |  | Damaged | Rework |  | Complete |  | Completed |  | Bar Mark 31 has been installed in capping beam with no cover on north face and minimal cover on south face as shown on the attached drg
| 02SL - Stations (LUL) | Cxxx-NCR-000832 | NCR | WTH-Buttress level -1 grid line 4L |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-03-30 | 2013-04-02 10:41 | 3 | 2013-02-15 | Civil - Civil Engineering General | 500 |  | Damaged | Rework |  | Complete |  | Completed |  | Couplers have been installed incorrectly in capping beam. On east face of buttress BM 44/45 has been installed as shown in an incorrect line
| 02SL - Stations (LUL) | Cxxx-NCR-000833 | NCR | WTH-Buttress Level-1 grid line M2 |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-03-31 | 2013-04-11 14:02 | 11 | 2013-02-15 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | BM 32 missing from capping beam at buttress area M2
| 02SL - Stations (LUL) | Cxxx-NCR-000836 | NCR | WTH- Out of tolerance couplers at Level-1 |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-03-31 | 2013-04-11 14:05 | 11 | 2013-02-22 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Couplers at level -1 are low in the following diaphragm wall panels: 17 (west leaf), 25, 26, 27 (north leaf), 35 and 36.See attached for survey showing details of as-built levels
| 02SL - Stations (LUL) | Cxxx-NCR-000845 | NCR | WTH- Concrete test sample not remixed prior to testing |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-03-16 | 2013-03-19 16:41 | 3 | 2013-02-21 | Civil - Civil Engineering General | 500 |  | Material | Repair |  | Complete |  | Completed |  | Concrete test sample not remixed prior to testing .Testing and sampling not carried out by __ in accordance with the BS EN 12350-2-2009 clause 5 test sample
| 02SL - Stations (LUL) | Cxxx-NCR-000846 | NCR | WTH Curing of concrete test specimens |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-03-16 | 2013-03-19 16:45 | 3 | 2013-02-21 | Civil - Civil Engineering General | 500 |  | Material | Repair |  | Complete |  | Completed |  | After cubes had been made and at the end of the concrete pour the cubes were removed from the back of __ vehicle to the site concrete testing lab/store. They were then left overnight in an uncovered state (not stored in sealed plastic bags as agreed with __) and not protected from dehydration.
| 02SL - Stations (LUL) | Cxxx-NCR-000847 | NCR | WTH-Concrete sampling for cube making not carried out in accordance with the ITP |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-03-16 | 2013-03-19 16:48 | 3 | 2013-02-21 | Civil - Civil Engineering General | 500 |  | Material | Repair |  | Complete |  | Completed |  | not taken ,spot concrete sample taken for cube strength instead of a composite sample as required in the ITP
| 02SL - Stations (LUL) | Cxxx-NCR-000853 | NCR | WTH-The beam on G/L 2 on the ground floor shows a step in the soffit |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-03-29 | 2013-04-11 14:09 | 13 | 2013-02-25 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The beam on G/L 2 on the ground floor shows a step in the soffit 100mm from the face of the plunge column on the East face at G/L D.The step in the beam was installed in line with the face of the column (300mm offset East of G/L D).
| 02SL - Stations (LUL) | Cxxx-NCR-000854 | NCR | WTH- upstand cast low |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-04-30 | 2013-04-19 17:09 | -11 | 2013-03-14 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | The link reinforcement to the blockwork upstand at minus 1 level GL A-C has been set approx 40mm low in this section
| 02SL - Stations (LUL) | Cxxx-NCR-000859 | NCR | WTH-The steel at buttress at G/L 4H does not allow enough cover to the face of the buttress |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-04-30 | 2013-03-22 08:31 | -39 | 2013-03-01 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | The steel at buttress at G/L 4H at minus 1 level does not allow enough cover to the face of the buttress
| 02SL - Stations (LUL) | Cxxx-NCR-000862 | NCR | WTH- Verticality of plunge columns |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-05-31 | 2013-04-19 17:18 | -42 | 2013-03-07 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework |  | Complete |  | Completed |  | Verticality of plunge columns installed out of tolerance. The acceptable verticality tolerance as stated in KP10.3210 is 1:400 (2.5mm p/m). The as-built tolerance of the columns surveyed at level -1 shows an installation gradient beyond 1:400. See attached table for as-built positions.
| 02SL - Stations (LUL) | Cxxx-NCR-000863 | NCR | WTH- __ channel |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-04-30 | 2013-04-29 14:50 | -1 | 2013-03-14 | Civil - Civil Engineering General | 500 |  | Material | Repair |  | Complete |  | Completed |  | Use of galvanised __ channels instead of stain less steel channels at the locations shown in red in the attached drawing
| 02SL - Stations (LUL) | Cxxx-NCR-000875 | NCR | Buttress A2 at Level -2 |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-04-30 | 2013-04-19 17:05 | -11 | 2013-03-18 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Buttress A2 at level -2. The positioning of 20mm couplers in D wall leave mininal cover to buttress south face when BM 20 (drawing 51177) is threaded in
| 02SL - Stations (LUL) | Cxxx-NCR-000877 | NCR | Buttress D4 Level -2 |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-04-30 | 2013-04-19 17:26 | -11 | 2013-03-18 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Buttress A2 at level -2n GL D . Photo shows the position of D wall couplers. We will have insufficient cover on the east face. Is it acceptable to increase the size of the buttress to ensure we achieve 50mm cover on east face
| 02SL - Stations (LUL) | Cxxx-NCR-000878 | NCR | WTH-Buttress F4 Level -2 |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-04-30 | 2013-04-19 17:31 | -11 | 2013-03-21 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | WTH-Buttress F4 Level -2 .The position of D wall couplers appears to be incorrect. Lines in blue show the correct concrete outline of the buttress
| 02SL - Stations (LUL) | Cxxx-NCR-000886 | NCR | WTH-Buttress at G/L 4 at -1 level |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-04-30 | 2013-04-29 14:45 | -1 | 2013-03-26 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | The steel at buttress at G/L 4 does not allow enough cover to the face of the buttress
| 02SL - Stations (LUL) | Cxxx-NCR-000887 | NCR | WTH-D wall Panel 21 missing Kwikastrip |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-05-31 | 2013-05-07 10:44 | -24 | 2013-03-26 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | D wall record for Panel 21. We are missing Kwikastrip
| 02SL - Stations (LUL) | Cxxx-NCR-000889 | NCR | WTH-C32/40 concrete used in pour prior to the MCR being approved |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-04-30 | 2013-04-19 17:34 | -11 | 2013-03-26 | Civil - Civil Engineering General | 500 |  | System Defect | Use As-Is |  | Complete |  | Completed |  | WTH-C32/40 concrete from __ con__e backup plant being used in pour prior to the MCR being approved.This is not in compliance with 's ITP item 2. MCR records for __ Kings Cross plant for the same mix has been approved code 1 and a MCR had been submitted for the Paddington plant.
| 02SL - Stations (LUL) | Cxxx-NCR-000892 | NCR | WTH D-wall panel position between level-1 & level -2 |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-05-09 | 2013-04-19 17:42 | -20 | 2013-03-27 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | The following WTH D-wall panels have been found to be out of tolerance between level -1 & level -2: Panel 16, 17, 23, 24, 27, 29, 30, 31, 33 & 37. See attached table for details of permitted deviance & as-built position.
| 02SL - Stations (LUL) | Cxxx-NCR-000897 | NCR | WTH-Panel 27 cage has been installed to incorrect Level. As a result couplers for Slab/Waling Beam at Level -2 are incorrect |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-05-31 | 2013-05-07 10:50 | -24 | 2013-04-03 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | Panel 27 cage has been installed to incorrect Level. As a result couplers for Slab/Waling Beam at Level -2 are incorrect .They are 752mm low. See photo attached, only the top row of couplers are visible.
| 02SL - Stations (LUL) | Cxxx-NCR-000898 | NCR | WTH – Level -2 NE Corner slab,connection between the D-wall panel and North East slab |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-05-31 | 2013-05-07 11:03 | -24 | 2013-04-03 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | The connection between the D-wall panel and North East slab is a pair of Dextra couplers located in the B3 and T3 reinforcement layers. One of the two cages in panel 28 is lower that the piling tolerance and as a result the Dextra couplers are low coming out of the D-wall. The spacing between the underside of the Dextra couplers on B3 and the blinding is 50 to 55mm, which ensures they are within the cover tolerances in the slab but does not allow for the B1 mat to pass underneath. (See steel drawing Cxxx-SKC-C-DWG-Cxxx-51165 Rev.C03)
| 02SL - Stations (LUL) | Cxxx-NCR-000899 | NCR | WTH- Verticality of plunge columns at -2 level |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-05-31 | 2013-05-31 11:05 | 0 | 2013-04-04 | Civil - Civil Engineering General | 500 |  | Material | Rework |  | Complete |  | Completed |  | Following survey of plunge columns at -2 level we wish to record that column C2, C3, E2, F3 and H3 will not be able to provide 50mm cover to the plunge column with the encasement.
| 02SL - Stations (LUL) | Cxxx-NCR-000906 | NCR | WTH- North Waling Beam Level -2 ,concrete cover to link at BM44 |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-05-31 | 2013-04-19 17:46 | -42 | 2013-04-08 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | When Bar mark 44 is coupled into bar mark 33 there is not enough cover achieved on the link at the face of the beam.
| 02SL - Stations (LUL) | Cxxx-NCR-000910 | NCR | WTH-level -2 GL 4/H, construction joint between slab and southern waling beam missing couplers |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-05-31 | 2013-05-07 11:42 | -24 | 2013-04-17 | Civil - Civil Engineering General | 500 |  | Design | Repair |  | Complete |  | Completed |  | level -2 GL 4/H, construction joint between slab and southern waling beam, drawing 51164 did not specify 4 no. B40 couplers in the slab for the 4 no. B40 bars (bm 62 and 63) in the OF4 on drawing 51152 for the adjacent waling beam.
| 02SL - Stations (LUL) | Cxxx-NCR-000911 | NCR | WTH- High concrete strength for buttresses and Lining walls |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-11-30 | 2013-05-31 11:09 | -183 | 2013-04-22 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is |  | Complete |  | Completed |  | The compressive strength of the ‘Top Flow’ self compacting concrete used in the column encasements, buttresses & lining walls on level -1 is beyond the parameters set within the reinforced concrete works ITP. These parameters are >36N/mm2, but <60N/mm2 after 28 days as stated in Table 14, BS EN 206-1:2000. The test results as shown in the attached table which are above the 60N/mm2
| 02SL - Stations (LUL) | Cxxx-NCR-000912 | NCR | WTH-Concrete Lining wall pour at gridline F-G4 is low |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-06-30 | 2013-06-27 15:48 | -3 | 2013-04-22 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | The lining wall between gridlines F-G/4 has been poured low, leaving a tapered gap from 15mm to 0mm running a distance of 800mm horizontally along the length of the wall. The gap is level from the front to back of the wall which is 600mm deep. There are 2no hydrophilic strips installed horizontally at the head of the wall which seal against the capping beam soffit above.
| 02SL - Stations (LUL) | Cxxx-NCR-000920 | NCR | WTH-2 no couplers (1 ef) were not installed for the wall on level -2, G/L 3K-3M |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-05-31 | 2013-05-31 11:01 | 0 | 2013-04-22 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | 2 no couplers (1 ef) were not installed for the wall on level -2, G/L 3K-3M.These bars should have been installed into the waling beam on level -1 between G/L’s 3M and 4M
| 02SL - Stations (LUL) | Cxxx-NCR-000923 | NCR | WTH-Level -2, Buttress D4 |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-06-30 | 2013-06-27 15:50 | -3 | 2013-05-09 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Level -2, Buttress D4. The starters from the D-Wall (BM01) were installed too far east in the D-Wall. These starter bars (on the east face of the buttress only) are clashing with the vertical bars in the buttress (BM30 & 04). See NCR 00877 referring to the incorrect position of the couplers in the D-Wall.
| 02SL - Stations (LUL) | Cxxx-NCR-000925 | NCR | WTH-Level -2, Buttress E4 |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-06-30 | 2013-06-27 15:51 | -3 | 2013-05-07 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair |  | Complete |  | Completed |  | Level -2, Buttress E4. The starters from the D-Wall (BM01) were installed too far east in the D-Wall. These starter bars (on the east face of the buttress only) are clashing with the vertical bars in the buttress (BM30 & 04)
| 02SL - Stations (LUL) | Cxxx-NCR-000930 | NCR | WTH-Extensometers No 01 Level -4 has become inaccessible |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-07-31 | 2013-07-25 13:53 | -6 | 2013-05-02 | Geotechnical Engineering - Geotechnical Monitoring | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete |  | Completed |  | In-box extensometers are required to be reported weekly. Extensometers No 01 Level -4 has become obstructed or inaccessible during the top-down excavation.
| 02SL - Stations (LUL) | Cxxx-NCR-000932 | NCR | WTH-In-box extensometers No 2 Level -1 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-07-31 | 2013-08-02 10:28 | 2 | 2013-05-07 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete |  | Completed |  | In-box extensometers are required to be reported weekly. Extensometers No 2 Level -1 has become obstructed or inaccessible during the top-down excavation.
| 02SL - Stations (LUL) | Cxxx-NCR-000939 | NCR | WTH-Diaphragm wall couplers on panels 8 and 9 at level -4 are out of tolerance |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-07-31 | 2013-07-25 13:56 | -6 | 2013-05-30 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete |  | Completed |  | Diaphragm wall couplers on panels 8 and 9 at level -4 are out of tolerance. Please see attached sketch for exact levels.
| 02SL - Stations (LUL) | Cxxx-NCR-000942 | NCR | WTH-plunge column verticality at level -4 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-07-31 | 2013-08-02 11:05 | 2 | 2013-06-03 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Verticality of plunge columns installed out of tolerance as recorded at Level -4 The acceptable verticality tolerance as stated in KP10.3210 is 1:400 (2.5mm p/m). The as-built tolerance of the columns surveyed at level -1 shows an installation gradient beyond 1:400. See attached table for as-built positions
| 02SL - Stations (LUL) | Cxxx-NCR-000943 | NCR | WTH-Wall W-B-2-05, Level -2, South East Corner |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-07-31 | 2013-07-25 13:59 | -6 | 2013-06-03 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete |  | Completed |  | The horizontal starter bars (BM39) coming out of Panel 37 (South face) have been installed in the incorrect position. These bars couple into BM37 from drawing Cxxx-SKC-C-DWG-Cxxx-51172. The West row of couplers are outside the face of the beam. However the East face of the couplers are within the wall and can be used.
| 02SL - Stations (LUL) | Cxxx-NCR-000944 | NCR | WTH-Plunge columns at Level -4 with no corrective action. |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-08-31 | 2013-08-15 17:58 | -16 | 2013-06-03 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete |  | Completed |  | Verticality of plunge columns installed out of tolerance as recorded at Level -4 The acceptable verticality tolerance as stated in KP10.3210 is 1:400 (2.5mm p/m). The as-built tolerance of the columns surveyed at level -1 shows an installation gradient beyond 1:400. See attached table for as-built positions.
| 02SL - Stations (LUL) | Cxxx-NCR-000949 | NCR | WTH-D-wall at level -4 |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-08-31 | 2013-06-27 15:53 | -65 | 2013-06-03 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework |  | Complete |  | Completed |  | A number of pockets have been exposed in the d-wall panels at the interface of the level -2 soffit at level -4. Lumps of clay have been trapped by the reinforcement cage during the casting of the d-wall panel. Once the clay has been cleared / removed following excavation, a pocket remains which in some locations, exposes the d-wall reinforcement. The approximate size of the pockets is 150mm long by 100mm high & 70mm deep. The pockets have been recorded in various locations.
| 02SL - Stations (LUL) | Cxxx-NCR-000951 | NCR | WTH-D-Wall Panel 24 at Level -4, coupler positions |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-07-31 | 2013-08-02 10:31 | 2 | 2013-06-04 | Civil - Civil Engineering General | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete |  | Completed |  | The horizontal slab couplers within Panel 24 at level -4 were installed at an incorrect level. The detail on __ __ drawing Cxxx-SKC-C-DWG-Cxxx-50047 showed a level of the top of beam at this location as 103.765. This should have been 104.140 as detailed in Panel 25. This meant that the bottom row of couplers was below the soffit level of the beam.
| 02SL - Stations (LUL) | Cxxx-NCR-000955 | NCR | Decommission BSTs 30R and 33 within the WTH Box |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-07-25 | 2013-07-30 13:51 | 5 | 2013-06-04 | Surveying - Instrumentation and Monitoring | 1500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | inherited 4 no. piezometers within the box: BST 30R, BST 31R, BST32 and BST 33. BST 31R was confirmed as redundant by BOS-CRL-RFI-Cxxx-00733, as it clashed with a moling hole and was replaced by one of the dewatering wells. BST 32 continues to be monitored successfully. BST 30R and BST 33 have not provided reliable data and falling head tests have failed to improve their connection to the sand channel (see attached report from __). As BSTs 30R and 33 have not been providing reliable data, only 2 no. piezometers are reporting reliable data as required by the specification.
| 02SL - Stations (LUL) | Cxxx-NCR-000961 | NCR | WTH - Buttress K2 at level -2 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-07-29 | 2013-07-24 14:59 | -5 | 2013-06-10 | Civil - Civil Engineering General | 2000 |  | Material | Repair | 4 (0.5-3k) | Complete |  | Completed |  | Upon striking the formwork to the buttress at gridline K4 at level -2, there is an area of honeycombing /grout loss to the eastern concrete face of the buttress approximately 3m up form level -2 slab level. The grout loss is clearly defined on the eastern face, continues across the front/northern face & discolouration is visible on the western face of the buttress but without grout loss. This defect in the concrete pour is as a result of continuity issues associated with the discharge of multiple loads of ‘Top Flow ‘self compacting concrete being kept live for the duration of the pour without compaction.
| 02SL - Stations (LUL) | Cxxx-NCR-000969 | NCR | Magnetic Extensometer Cxxx-XM100003-CR084: unable to read |  | Contr |  | BOS - Bond Street Station (West) |  | 2013-07-01 | 2013-06-28 14:34 | -3 | 2013-06-17 | Surveying - Instrumentation and Monitoring | 500 |  | Damaged | Use As-Is |  | Complete |  | Completed |  | Ext 03 was last reported on 20th May 2013. Following that date, the extensometer reservation tube was obstructed by the excavation works at the Level -4. Access was regained on Fri 14th June, but the reservation tube was found to be blocked and possibly disconnected from lower sections of the tube below the Level -4 formation level.
| 02SL - Stations (LUL) | Cxxx-NCR-000970 | NCR | WTH - Lining wall at gridline H-J/4, Level -2 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-07-15 | 2013-07-18 11:36 | 3 | 2013-06-17 | Civil - Civil Engineering General | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete |  | Completed |  | There are multiple cracks in the face of the lining wall at gridline H-J/4, Level -2. The cracks are approximately 0.2mm crack width & run horizontally & vertically between tie holes. Upon striking of the formwork, the wall was immediately covered with a layer of frost blanket for the required curing period.
| 02SL - Stations (LUL) | Cxxx-NCR-000972 | NCR | WTH-Starter bars in the level 0 and level -1 slab around escape stairs 3 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-07-31 | 2013-08-02 10:55 | 2 | 2013-07-01 | Civil - Civil Engineering General | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Starter bars in the level 0 and level -1 slab around escape stairs 3 have been detailed incorrectly which means there are inconsistencies between couplers provided in the slab and couplers required for the internal walls below level 0. The error has occurred due to detailing the level 0 starter bars as B16 @ 200 as shown on drawing 81721. The wall W-W-10 requirements shown on drawing 81700 are B20 @ 100.
| 02SL - Stations (LUL) | Cxxx-NCR-000976 | NCR | WTH-D-wall positions, level -2 to -4 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-08-31 | 2013-08-15 18:01 | -16 | 2013-06-25 | Civil - Civil Engineering General | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | The following WTH D-wall panels have been found to be out of positional tolerance between level -2 & level -4: This relates to Panel 6, 13, 21, 23, 24, 27, 29, 30, 31, 33 & 35. See attached table for details of permitted deviance & as-built position.
| 02SL - Stations (LUL) | Cxxx-NCR-000979 | NCR | WTH-Soffit of stairs 4&5 (East side) at level -4 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-11-30 | 2013-10-25 17:19 | -36 | 2013-07-01 | Civil - Civil Engineering General | 30000 |  | Workmanship | Rework | 2 (6-60k) | Complete | Supervision - Other | Completed |  | The east side of the stairs at level -4 has a soffit level of 103.015. However the slab soffit was constructed to a level of 102.95 which is the level on the West side of the stairs. Therefore the slab soffit was poured 65mm lower than it should have been.
| 02SL - Stations (LUL) | Cxxx-NCR-000984 | NCR | WTH-Rebar that was cut in the lining wall at level -4 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-08-13 | 2013-08-02 10:35 | -11 | 2013-07-23 10:35 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Electrical or instrument noise | Completed |  | 1no BM11 from drawing Cxxx-SKC-C-DWG-Cxxx-51203 was cut at the bottom of the wall. This was cut where the D-Wall changes direction between G/L A & B.
| 02SL - Stations (LUL) | Cxxx-NCR-000985 | NCR | WTH-Level -1, Staircase 3 – Walls W-W-12, W-W-11 & W-W-19 missing rebar |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-09-30 | 2013-08-15 16:43 | -46 | 2013-07-25 08:41 | Civil - Civil Engineering General | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete |  | Completed |  | Wall W-W-12,11 & 19 were poured to top of ground floor slab (120.230) However these walls had starter bars designed to catch the landing at level 0. These bars were not installed
| 02SL - Stations (LUL) | Cxxx-NCR-000986 | NCR | WTH-75mm stainless drainage pipes which are cast into the level -2 slab & protrude through the level -4 soffit. |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-12-13 | 2013-12-15 08:04 | 2 | 2013-08-12 14:33 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The condition & position of the 75mm stainless drainage pipes which are cast into the level -2 slab & protrude through the level -4 soffit. 2no of the pipes (north & south) have been cast slightly further back than intended & will conflict with the front face of the lining walls, possible causing an issue with the Cxxx follow on works connecting the straight section of pipe which is to be hung off the level -4 soffit. The other pipe (centre of west face) has been badly damaged during excavation & will not be usable as-is as the protruding section needs to be cut back flush with the slab soffit.
| 02SL - Stations (LUL) | Cxxx-NCR-000987 | NCR | WTH-Column encasement K2 at level -4 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-09-30 | 2013-09-30 15:14 | 0 | 2013-08-06 11:42 | Civil - Civil Engineering General | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Column encasement K2 was not fully compacted at the face. There is also some polystyrene which was lodged in the face of the column. The wall was initially poured up to the soffit of level -3. The polystyrene is lodged at this level when the remainder of the encasement was poured with the level -3 slab
| 02SL - Stations (LUL) | Cxxx-NCR-000988 | NCR | WTH-The web-based Argus system-Instruments: in-ground inclinometers (8 no.), in-ground extensometers (11 no.) and in-panel inclinometers (8 no.) |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-09-30 | 2013-09-13 12:17 | -17 | 2013-08-06 12:17 | Civil - Geotechnical Engineering | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The web-based Argus system that displays monitoring data for the automated Cxxx instruments: in-ground inclinometers (8 no.), in-ground extensometers (11 no.) and in-panel inclinometers (8 no.), was not functioning on 29th and 30th July 2013. did not have access to any data for these instruments and could therefore not present any data in the daily SRGs.
| 02SL - Stations (LUL) | Cxxx-NCR-000989 | NCR | WTH Lining wall panel 3 E/W corner level -4 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-12-13 | 2013-12-11 17:37 | -2 | 2013-08-06 11:14 | Civil - Civil Engineering General | 5000 |  | Material | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | WTH Lining wall panel 3 E/W corner level -4
| 02SL - Stations (LUL) | Cxxx-NCR-000990 | NCR | WTH-Plunge column positions at level -5 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-10-31 | 2013-11-04 16:38 | 4 | 2013-08-06 10:27 | Civil - Civil Engineering General | 10000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Verticality of plunge columns installed out of tolerance as recorded at Level -5 The acceptable verticality tolerance as stated in KP10.3210 is 1:400 (2.5mm p/m). The as-built tolerance of the columns shown in the attached as-built survey table shows an installation gradient beyond 1:400. Note: The attached table shows columns surveyed in line with the areas excavated to date. An early solution is requested for the columns installed out of tolerance to allow for the timely progression of the permanent works at level -5. The as-built table will be updated as the excavation progresses. See attached table for as-built positions
| 02SL - Stations (LUL) | Cxxx-NCR-000991 | NCR | WTH Pockets in D-wall at level -5 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-09-30 | 2013-09-30 16:03 | 0 | 2013-08-12 14:25 | Civil - Civil Engineering General | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Previous Construction - Other | Completed |  | A number of pockets have been exposed in the d-wall panels at the interface of the level -4 soffit at level -5. Lumps of clay have been trapped by the reinforcement cage during the casting of the d-wall panel. Once the clay has been cleared / removed following excavation, a pocket remains which in some locations, exposes the d-wall reinforcement. The size of the pockets varies & have been recorded in various locations
| 02SL - Stations (LUL) | Cxxx-NCR-000992 | NCR | WTH-Missing couplers in panel 29 at level -3. |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-11-29 | 2013-12-03 12:30 | 4 | 2013-10-24 08:47 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Error by manufacturer in shipping or marking | Completed |  | missing couplers in panel 29 at level -3.
| 02SL - Stations (LUL) | Cxxx-NCR-000993 | NCR | WTH-level -5, D-Wall panel 20 has couplers to Lining Wall. |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-09-30 | 2013-08-23 14:02 | -38 | 2013-08-09 08:16 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | At level -5, D-Wall panel 20 has couplers installed to catch the Lining Wall. One row of these couplers were installed outside the end of the lining wall.
| 02SL - Stations (LUL) | Cxxx-NCR-000994 | NCR | WTH- Level -4 Lining Wall G/L F-G South side(Pour #21) |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-09-30 | 2013-09-30 15:59 | 0 | 2013-08-12 14:18 | Civil - Civil Engineering General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | When striking the stop end of lining wall pour #20, a horizontal bar (BM01) was pulled back from the face of the lining wall in pour #21. When the bar was pulled back, it cracked the face of the lining wall of pour #20 and one of the horizontal bars (BM01) which was spliced into the pour #20 came loose and detached from the wall.
| 02SL - Stations (LUL) | Cxxx-NCR-000995 | NCR | The extensometer Cxxx-XR700010-CR084 has two faulty sensors |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-09-30 | 2013-10-16 16:40 | 16 | 2013-08-15 16:53 | Geotechnical Engineering - Geotechnical Monitoring | 1500 |  | System Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The extensometer Cxxx-XR700010-CR084 has two faulty sensors: Cxxx-XR700010B-CR084 (10m deep) and Cxxx-XR700010E-CR084 (25m deep). Another sensor, Cxxx-XR700010C-CR084 (15m deep) occasionally shows spikes in the data, but otherwise provides stable data. Filters have been applied to these sensors so that any readings outside the range 0Hz to 15000Hz are not shown on the calculated data graphs
| 02SL - Stations (LUL) | Cxxx-NCR-000996 | NCR | In-ground Inclinometer Cxxx-IE700006-CR084 has 5 no. faulty sensors |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-09-30 | 2013-09-16 10:48 | -14 | 2013-08-15 16:57 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In-ground Inclinometer Cxxx-IE700006-CR084 has 5 no. faulty sensors, which were giving erratic readings and therefore distorting the cumulative graphs. The following sensors have had a zero factor applied to them, so they no longer distort the data: Cxxx-IE700006O-CR084 A axis, Cxxx-IE700006H-CR084 A & B axis, Cxxx-IE700006F-CR084 A & B axis, Cxxx-IE700006E-CR084 B axis, Cxxx-IE700006A-CR084 B axis. There has been less than 5mm total movement in this instrument.
| 02SL - Stations (LUL) | Cxxx-NCR-000997 | NCR | WTH-Level -4 Column Encasement E3 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2014-01-10 | 2013-12-15 08:08 | -26 | 2013-10-24 08:41 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The top of the column encasement (approx 50mm) at E3 at level -4 has stepped out of position by approx 15-20mm from the rest of the column encasement
| 02SL - Stations (LUL) | Cxxx-NCR-000998 | NCR | WTH-Level -1, Staircase 3 – Upstand at West end of Wall W-W-20 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-09-30 | 2013-09-30 16:06 | 0 | 2013-08-19 08:55 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Walls W-W-11, 12 & 20 (adjacent to W-W-12) have been poured to the underside of the ground floor slab. 6 no. 20mm starter bars (bar mark 82) anchored in W-W-11, which run through the re-detailed 350mm upstand into wall W-W-12 were omitted at the time of construction.
| 02SL - Stations (LUL) | Cxxx-NCR-001000 | NCR | WTH-Level -3 Lining Wall Starters to SW Lining Wall |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-10-18 | 2013-10-16 16:38 | -2 | 2013-08-30 09:15 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Waling Beam W-WB-2-08 and upstand wall to level +2 slab soffit have been constructed without sufficient screw couplers for connection of Bar Mark 11 starter bars for the Level -3 lining wall (51210). Instead, 19 no. (9 IF, 10 OF) 20mm starter bars were cast into the W-WB-2-08 Waling Beam, with 6 no. (2IF, 4 OF) screw couplers provided in the upstand wall. There is a lack of clarity in drawings 51171 and 51153 for the upstand wall and waling beam and therefore suitable information was not present for the screw couplers to be provided for the Level -3 lining wall. Additionally screw couplers installed in the soffit of WTH – Level -2 slab are out of position at the front face of the wall.
| 02SL - Stations (LUL) | Cxxx-NCR-001001 | NCR | WTH-4 Couplers installed in the soffit of WTH – Level -2 for Staircase 1 east wall |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-09-30 | 2013-09-30 16:14 | 0 | 2013-08-30 08:52 | Civil - Civil Engineering General | 2000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Previous Construction - Other | Completed |  | 4 Couplers installed in the soffit of WTH – Level -2 for Staircase 1 east wall at WTH - Level -4 observed to be installed outside the setting out line (4 no couplers)
| 02SL - Stations (LUL) | Cxxx-NCR-001002 | NCR | WTH-Level -5, top south corner of west Lining wall pour #1 at interface to waling beam |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-09-30 | 2013-09-30 14:32 | 0 | 2013-09-03 12:57 | Civil - Civil Engineering General | 1500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Bar mark 43 is shown on drawing 51232 as threaded bars coupling into horizontal couplers within west waling beam at level -4. However on waling beam drawing 51185 couplers have not been detailed and subsequently not installed on site. Not having couplers cast-in resulted not being able to install Bar Mark 43 of lining wall as specified in drawing 51232.
| 02SL - Stations (LUL) | Cxxx-NCR-001003 | NCR | Temporary Faulty In-Ground Inclinometer |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-12-13 | 2013-12-15 08:12 | 2 | 2013-09-05 08:52 | Geotechnical Engineering - Geotechnical Monitoring | 1500 |  | Equipment Breakdown | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | The chamber for in-ground Inclinometer Cxxx-IE700005-CR084 continues to flood. This has caused the battery to fail and the instrument ceased providing data on 30th July 2013.
| 02SL - Stations (LUL) | Cxxx-NCR-001004 | NCR | WTH-Level -5 Western Lift Pit – Box Out on Northern Wall |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-10-31 | 2013-10-25 17:22 | -6 | 2013-09-09 16:56 | Civil - Civil Engineering General | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | Western lift pit at level -5, north wall, box out (325x475x165mm) in RC wall not vertical. See sketch for deviations from drawing
| 02SL - Stations (LUL) | Cxxx-NCR-001005 | NCR | WTH-Level -5 internal wall w-w-43, immediately above opening |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-10-31 | 2013-11-04 16:41 | 4 | 2013-09-09 17:04 | Civil - Civil Engineering General | 1500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | On-site setting out of the top of the opening in wall w-w-43 has been done according to RFI 588 (100.510m ATD). However, engineer has spotted a gap between the position of top of opening and the reinforcement around the opening. It is found that there is a potential discrepancy between the level shown on __ drawing Cxxx-SKC-C-DWG-Cxxx-51231 and the level specified in RFI 588. Drawing 51231 likely to have adopted a higher level than what is specified RFI 588. The reason for this discrepancy could be the fact that __ drawings were produced before the issue of RFI 588 and not have been updated accordingly after the issue.
| 02SL - Stations (LUL) | Cxxx-NCR-001006 | NCR | WTH-Installation of drainage voids in the lift shaft at Level -5. |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-10-31 | 2013-11-08 17:10 | 8 | 2013-09-10 08:37 | Civil - Civil Engineering General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Installation of drainage voids in the lift shaft at Level -5. The voids have been installed incorrectly at Fire Fighting Lift Shaft no 4. Timbers which were used to form the void have moved and floated during pouring of the kicker
| 02SL - Stations (LUL) | Cxxx-NCR-001007 | NCR | WTH-Level -4, Wall 28, wall started bars at west end of the wall beneath doorway |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-10-31 | 2013-10-09 11:36 | -22 | 2013-09-10 08:42 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | Wall 28, detailed on RC drawing Cxxx-SKC-C-DWG-Cxxx-51202 shows wall starter bars, BMs 09 and 24 coupling into the -4 slab. The -4 slab, detailed on RC drawing Cxxx-SKC-C-DWG-Cxxx-51191 doesn’t show any couplers to accept the threaded bars but instead shows a doorway opening. This doorway opening is 610mm higher up the wall and an RC re-detailing is required in the area.
| 02SL - Stations (LUL) | Cxxx-NCR-001009 | NCR | Level -4 Buttress H4, J4 & Lining wall H to J4 Concrete Pour Level |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-10-31 | 2013-11-06 16:23 | 6 | 2013-09-18 11:57 | Civil - Civil Engineering General | 5000 |  | Workmanship | Rework | 3 (3-6k) | Complete | Supervision - Other | Completed |  | The buttresses at grid line H4 & J4 at level -4 have been poured lower than the correct design level leaving a void up to the soffit level above. The lining wall connecting the two buttresses at gridline J to K has also been poured too low as this was poured with the J4 buttress.
| 02SL - Stations (LUL) | Cxxx-NCR-001010 | NCR | Staircase 1&2 central wall, missing reinforcement to tie in to level -1 slab |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-10-31 | 2013-10-18 10:05 | -13 | 2013-10-08 08:35 | Civil - Civil Engineering General | 5000 |  | Workmanship | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | The reinforcement detail connecting the north & south ends of the central wall to staircase 1&2 has been missed at both ends when the wall has been cast. Drawing
| 02SL - Stations (LUL) | Cxxx-NCR-001011 | NCR | Scabbling to face of wall adjacent to Stairmaster flight F3 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-10-17 | 2013-10-16 16:30 | -1 | 2013-10-03 09:49 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A verbal agreement was made between & Cxxx with regard to permission for scabbling 10mm into the vertical wall adjacent to Stairmaster flight F3. The proposal was made by to allow some installation tolerance for lifting in the Stairmaster permanent formwork units. This non conformance has been raised because the required documentation was not in place prior to commencement of the proposed works & that the scabbling works carried out exceeed the proposed depth by 10mm (20mm as-built depth) Ref: Cxxx-__-S-DDA-Cxxx-17101 Rev C05
| 02SL - Stations (LUL) | Cxxx-NCR-001012 | NCR | WTH D-wall panel position between level -2 & level -4 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-12-13 | 2013-12-11 12:40 | -2 | 2013-10-03 11:26 | Civil - Civil Engineering General | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The following WTH D-wall panels have been found to be out of positional tolerance between level -2 & level -4: This relates to Panel 6, 13, 21, 23, 24, 27, 29, 30, 31, 33 & 35.
| 02SL - Stations (LUL) | Cxxx-NCR-001013 | NCR | WTH-Level -1, Staircase 3 – Walls W-W-12, W-W-11 & W-W-19 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-10-17 | 2013-11-04 16:43 | 18 | 2013-10-03 11:33 | Civil - Civil Engineering General | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | Wall W-W-12,11 & 19 were poured to top of ground floor slab (120.230) However these walls had starter bars designed to catch the landing at level 0. These bars were not installed
| 02SL - Stations (LUL) | Cxxx-NCR-001014 | NCR | WTH-D wall Panel 27- level -5 (couplers) |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-11-29 | 2013-11-07 11:17 | -22 | 2013-10-03 11:42 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | At level -5, D-Wall panel 27 (SE corner) is lower than designed. Relating to NCR 627 the panel has dropped during installation by approx 750mm. As a result only the top row of Dextra couplers are visible. This row of 8 dextra couplers are located at mid point in the slab.
| 02SL - Stations (LUL) | Cxxx-NCR-001015 | NCR | WTH- Wall #28 Level -2 door opening |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-11-29 | 2013-11-12 15:43 | -17 | 2013-10-03 11:53 | Civil - Civil Engineering General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Steel that we have installed in Slab at Level -2, connection to W28 is incorrect. When setting out the door opening with the latest information ( See RFI) , the reinforcement installed in slab at this location looks incorrect. See attached photo of this area. On the left hand side of the photo, there are only 3 no starter bars installed. On the right hand side of the picture too many couplers have been installed,
| 02SL - Stations (LUL) | Cxxx-NCR-001016 | NCR | WTH-level -5, D-Wall panel 2 (SE corner) |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-11-29 | 2013-11-16 10:35 | -13 | 2013-10-03 12:02 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | At level -5, D-Wall panel 2 (SE corner) has couplers installed to tie into the Lining Wall at the opening for the Cxxx interface. One row of these couplers have been installed outside the end of the lining wall. There is an inconsistency in the reinforcement detail drawings for the D-Wall panel (50004) and the GA showing the Cxxx interface dimensions (11154)
| 02SL - Stations (LUL) | Cxxx-NCR-001017 | NCR | WTH-level -5, D-Wall panel 37 (SE corner) |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-11-29 | 2013-11-12 15:48 | -17 | 2013-10-03 12:11 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | At level -5, D-Wall panel 37 (SE corner) has couplers installed to tie into the Lining Wall at the opening for the Cxxx interface. These couplers have been installed approx 500mm in from the face of the lining wall. There is an inconsistency in the reinforcement detail drawings for the D-Wall panel (50075) and the GA showing the Cxxx interface dimensions (11154)
| 02SL - Stations (LUL) | Cxxx-NCR-001018 | NCR | WTH- D wall Panel #15 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-11-29 | 2013-11-22 12:01 | -7 | 2013-10-03 12:17 | Civil - Civil Engineering General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | D wall panel #15 at Level -2. The Kwikastrip in the D wall which connects to Wall 28 is positioned incorrectly. See attached photo. 1 no bar from the Kwikastrip catch’s the wall but the southern bar does not. We propose to drill and fix 16mm bars 260mm deep with __ RE500 to replace the missing bar from the Kwikastrip
| 02SL - Stations (LUL) | Cxxx-NCR-001019 | NCR | WTH- Level -5 D Wall panel 9 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-11-29 | 2013-11-22 16:51 | -7 | 2013-10-04 09:18 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Position of Dextra couplers in D wall Panel #9 at Level -5 is incorrect. See attached photo which shows one row of couplers located outside the extent of Lining Wall.
| 02SL - Stations (LUL) | Cxxx-NCR-001020 | NCR | WTH-Level -4, Eastern Lift Shaft, North Wall |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-12-13 | 2013-12-11 17:41 | -2 | 2013-10-24 09:29 | Civil - Civil Engineering General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Northern wall of the Eastern Lift Shaft on level -2 was poured low in a local area. The void does not fully extend through the wall and extends from the East side to the middle of the wall
| 02SL - Stations (LUL) | Cxxx-NCR-001021 | NCR | WTH-Level -1, N.W Corner upstand |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-11-08 | 2013-11-04 16:48 | -4 | 2013-10-16 09:05 | Architectural - Brickworks/Blockworks | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The upstand in the North West corner of level -1 (Parallel with G/L 1) has been set out 190mm too far North
| 02SL - Stations (LUL) | Cxxx-NCR-001022 | NCR | WTH-Level -5, Wall W-27B Box out |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-12-24 | 2013-12-11 11:08 | -13 | 2013-10-16 09:17 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | At Level -5, on Wall W-27B, 275 x 540mm box out is not as per drawing or within allowable tolerance. The box out shutter has bowed in the centre during the concrete pour and as a result reduced the height of the box. The worst deflection [in the midpoint] is 33mm. See sketch for variation in deflection. See also builders work drawing - Cxxx-__-M-DDA-Cxxx-66150,the 75mm void in wall shown has not been installed in this pour. This void is not show on the GA section on Cxxx-__-S-DDD-Cxxx-21151 and has been missed during construction.
| 02SL - Stations (LUL) | Cxxx-NCR-001023 | NCR | Westen lift shaft, level -4 to -2, Top of wall pour level defect |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-11-29 | 2013-11-30 15:05 | 1 | 2013-10-21 14:25 | Civil - Civil Engineering General | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | The nother wall to the eastern lift shaft between level -4 & -2 has been poured to low to the soffit of the level -2 slab. The defect is as a result of workmanship as the pour level was not adequately controlled.
| 02SL - Stations (LUL) | Cxxx-NCR-001025 | NCR | Reinforcement tie into Wall 4c from the ground beam at gridline C to D, Level -1 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-11-29 | 2013-11-16 10:39 | -13 | 2013-10-23 14:45 | Civil - Civil Engineering General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | There is a missing reinforcement tie in detail between the ground beam at gridline C to D & wall 4c.
| 02SL - Stations (LUL) | Cxxx-NCR-001026 | NCR | Escape stair 3, horizontal wall starter bars at level -1. Incorrect installation. |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-11-18 | 2013-11-22 17:53 | 4 | 2013-11-04 09:44 | Civil - Civil Engineering General | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | The stair wall running west to east at gridline G, tieing into the staircase 3 wall running north to south should be 300mm thick. The horizontal B16 wall starter bars projecting from the previously cast wall running north to south, have been incorrectly set for a 350mm thick wall & are spaced 240mm apart. Note: related attachments have been emailed to the CRL lead reviewer.
| 02SL - Stations (LUL) | Cxxx-NCR-001029 | NCR | __'s inclinometer sensors not compliant with contract requirements - angular measure & Calibration Cert temperature range |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-12-16 | 2014-01-16 16:10 | 31 | 2013-11-04 11:27 | Surveying - Instrumentation and Monitoring | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | __ did not have the Cxxx KX10 included in their contract documentation and therefore the instruments they installed did not comply with full requirements in two respects. Cxxx KX10 (Materials and Workmanship Spec) requires in-place inclinometer sensors to have a measuring range of ±10 degrees or greater (KX10.3214) - some installed are ± 5 degrees. It also requires that the calibration certificates cover the operating temperature range. The certificates provided do not cover the full operating temperature range.
| 02SL - Stations (LUL) | Cxxx-NCR-001030 | NCR | Concrete pour level to mezzanine landing slab |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2014-01-10 | 2013-12-15 08:18 | -26 | 2013-11-04 12:08 | Civil - Civil Engineering General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The concrete to the mezzanine landing slab has been poured to an incorrect level. Note: The reinforcment has been installed to the correct design level. The pour level issue is due to excess concrete placed. Note: related reference attacments to be sent to CRL lead reviewer.
| 02SL - Stations (LUL) | Cxxx-NCR-001031 | NCR | Con__e cold joint in level -5 lining wall 10. |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-12-16 | 2013-12-15 09:20 | -1 | 2013-11-04 12:43 | Civil - Civil Engineering General | 2000 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Upon striking the formwork to the lining wall 10 at level -5, a cold joint can be seen running horizontally through the wall at approximately 2m above raft slab level. Note: Supporting documentation will be emailed to the CRL lead reviewer.
| 02SL - Stations (LUL) | Cxxx-NCR-001032 | NCR | Missing Kwikastrip reinforcement within D-wall panel 9 at level -1 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-12-13 | 2013-12-15 09:22 | 2 | 2013-11-04 14:27 | Civil - Civil Engineering General | 2000 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There is missing Kwikastrip reinforcement within D-wall panel 9 at level -1 which was mintended to tie into wall 5. Note: supporting documents have been emailed to CRL lead reviewer.
| 02SL - Stations (LUL) | Cxxx-NCR-001033 | NCR | Bars in Buttress M2 not aligned |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-12-13 | 2013-11-30 15:09 | -13 | 2013-11-04 17:38 | Civil - Civil Engineering General | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | Bar mark 37 was installed too far in from the face of the buttress from a previous pour at level -1. The bars have been pulled out into the correct position at the base but unable to manouevre at the top of beam at level -2 for the subsequent pour. The bars therefore could not be tied to the link at the top - as they are too far apart. Also bar mark 06 on the North side of the buttress has been installed too far from the North face of the buttress and from the knuckle of the link.
| 02SL - Stations (LUL) | Cxxx-NCR-001034 | NCR | Level -2, Wall 2, Eastern Face - Kwikastrip |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-12-13 | 2013-12-11 17:42 | -2 | 2013-11-04 14:49 | Civil - Civil Engineering General | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | At Level -2 in Wall #2, Eastern Face of wall where Mezzanine Slab ties into Stairwall, Kwikastrip has been installed too low. This Kwikastrip is replacing BM 03 shown on drawing 51169. It is not currently possible to achieve 25mm cover on the bottom of the slab. Note: Supporting documentation will be emailed to CRL lead reviewer.
| 02SL - Stations (LUL) | Cxxx-NCR-001035 | NCR | Starter Bars BM39 from SF of Panel 37 installed out of position |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-12-13 | 2013-11-30 15:12 | -13 | 2013-11-05 12:02 | Civil - Structural Engineering | 1500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Previous Construction - Other | Completed |  | The horizontal starter bars (BM39) coming out of Panel 37 (South face) have been installed in the incorrect position. These bars couple into BM37 from drawing Cxxx-SKC-C-DWG-Cxxx-51172. The West row of 6 couplers are outside the face of the beam. However the East face of the couplers are within the wall and these 6 can be used.
| 02SL - Stations (LUL) | Cxxx-NCR-001036 | NCR | Slab soffit rework to level -2 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-12-21 | 2013-12-16 12:08 | -5 | 2013-11-11 14:58 | Civil - Civil Engineering General | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There are areas of the Level -2 slab soffit (viewed from level -4) where the finish contains imperfections that are deeper than the 5mm over 1m as specified for a plain smooth finish.
| 02SL - Stations (LUL) | Cxxx-NCR-001037 | NCR | Level -1 Eastern Lift Shaft Wall W-W8DWTH detailing error |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-12-16 | 2013-12-15 09:24 | -1 | 2013-11-14 08:38 | Civil - Civil Engineering General | 1500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | At level -1 Wall W-W8D shows vertical bars as B20 at 200mm spacings (BM01). However, the couplers detailed coming down from the beam (DWG Cxxx-SKC-C-DWG-Cxxx-51093) are shown as B16 at 150mm centres (BM 45).
| 02SL - Stations (LUL) | Cxxx-NCR-001038 | NCR | WTH-Level -5 Wall 27 missing 75mm diameter opening |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-12-13 | 2013-12-15 16:34 | 2 | 2013-11-14 08:50 | Civil - Civil Engineering General | 2000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | At level -5 Wall 27, there is a 75mm diameter opening missing,shown on the MEP builders works layout. This was not shown on the steel reinforcement or GA drawings and was not installed
| 02SL - Stations (LUL) | Cxxx-NCR-001040 | NCR | WTH-Level -5. Lining wall pour #4. The wall has not filled to the soffit of Level -4 slab |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-12-13 | 2013-12-15 16:38 | 2 | 2013-11-15 11:56 | Civil - Civil Engineering General | 2000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | At Level -5. Lining wall pour #4. The wall has not filled to the soffit of Level -4 slab. See attached location and photo.
| 02SL - Stations (LUL) | Cxxx-NCR-001041 | NCR | WTH-mastic joint at Mezzanine Blockwork Level -2 adjacent to Staircase 1/2 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-12-13 | 2013-12-11 17:44 | -2 | 2013-11-15 12:12 | Architectural - Brickworks/Blockworks | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Mastic Joint to block work Wall at Mezzanine Slab has been failed due to water ingress
| 02SL - Stations (LUL) | Cxxx-NCR-001042 | NCR | WTH-Stair Wall W2- Level -2 to -1 (Stairmaster F8) |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-12-13 | 2013-12-15 16:40 | 2 | 2013-11-15 12:20 | Civil - Civil Engineering General | 1500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | When installing stairmaster flight F8 between Level -1 and -2 the stair pans do not fit between walls W1 and W2. Walls are within specified tolerance
| 02SL - Stations (LUL) | Cxxx-NCR-001043 | NCR | WTH-Mezzanine Blockwork Level -2 adjacent to Staircase 4/5 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-12-13 | 2013-12-15 16:43 | 2 | 2013-11-15 12:31 | Architectural - Brickworks/Blockworks | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Inadequate/insufficient tooling. | Completed |  | Blockwork joint in Mezzanine Slab. 2nd row from the underside of Mezzanine Slab soffit has cracked. It appears that this has been caused by overtightening of the tiebolts for the Mezzanine slab formwork which sits on top of this wall. The tightening has induced a horizontal load into the joint and resulted in a crack
| 02SL - Stations (LUL) | Cxxx-NCR-001045 | NCR | WTH-Level -1, Wall #2 ( Incorrect Detailing to Wall and Slab) |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-12-13 | 2013-12-15 16:55 | 2 | 2013-11-18 08:47 | Civil - Civil Engineering General | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Detailed drawing for Wall 2 at level -1 shows an additional section of wall on the south side of wall which is not required and incorrect. This has been confirmed with __. 4 x 2 rows of 16mm additional couplers have been installed in slab to pick up these BM01 shown highlighted. ( Drawing 51101) These couplers are not required now and will need to be made good.
| 02SL - Stations (LUL) | Cxxx-NCR-001046 | NCR | WTH-At Level -5 Lining Wall Panel #7 there is a poor surface finish |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-12-13 | 2013-12-15 16:58 | 2 | 2013-11-18 13:48 | Civil - Civil Engineering General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | At Level -5 Lining Wall Panel #7 there is a poor surface finish. The poor finish is approximately 1m above top of Slab. See photos. It appears that the issue was Top Flow sitting in the pump line for an extended period while waiting for concrete wagon. When the next load started to pump the concrete sitting in the line has not bonded with the previous load satisfactorily and left a poor surface finish.
| 02SL - Stations (LUL) | Cxxx-NCR-001047 | NCR | Level -5, Lining Wall #10, reinforcement couplers |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-12-13 | 2014-01-16 15:40 | 34 | 2013-11-18 17:40 | Civil - Civil Engineering General | 2000 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Inadequate/insufficient tooling. | Completed |  | A series of B20 male threaded bars have been left projecting horizontally from the vertical face of the cast lining wall. The male threaded bars are intended to be coupled to the female counterpart for the follow on works. Attacments have been emailed to the CRL lead reviewer.
| 02SL - Stations (LUL) | Cxxx-NCR-001048 | NCR | Slab soffit rework to level 0, Ground floor |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-12-13 | 2013-12-16 12:10 | 3 | 2013-11-20 15:16 | Civil - Civil Engineering General | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There are areas of the Level -0 slab soffit (viewed from level -1) where the finish contains imperfections that are deeper than the 5mm over 1m as specified for a plain smooth finish & the 3mm over 1m for a fine smooth finish (H-M/3-4)
| 02SL - Stations (LUL) | Cxxx-NCR-001049 | NCR | Slab soffit rework to level -1 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-12-13 | 2013-12-11 08:27 | -2 | 2013-11-21 11:52 | Civil - Civil Engineering General | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There are areas of the Level -1 slab soffit (viewed from level -2) where the finish contains imperfections that are deeper than the 5mm over 1m as specified for a plain smooth finish.
| 02SL - Stations (LUL) | Cxxx-NCR-001050 | NCR | Level -2, as-built column encasement level for K3 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-12-13 | 2013-12-11 17:45 | -2 | 2013-11-21 17:19 | Civil - Civil Engineering General | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The RC column encasement for K3 at level -2 has been cast to a level of 109.233 & not to the underside of the thrust wall between J3 & M3 at 110.185
| 02SL - Stations (LUL) | Cxxx-NCR-001051 | NCR | Level -1 Pour level of internal wall at GL E-F/1-3. |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-12-13 | 2013-12-15 17:00 | 2 | 2013-11-22 15:24 | Civil - Civil Engineering General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The internal wall at GL E-F/1-3 has been poured low in 3no location approximately 2m long & tapering from 100mm to 20mm in height.
| 02SL - Stations (LUL) | Cxxx-NCR-001052 | NCR | Slab soffit rework to level -4 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-12-18 | 2013-12-16 12:11 | -2 | 2013-11-25 10:50 | Civil - Civil Engineering General | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There are areas of the Level -4 slab soffit (viewed from level -5) where the finish contains imperfections that are deeper than the 5mm over 1m as specified for a plain smooth finish.
| 02SL - Stations (LUL) | Cxxx-NCR-001053 | NCR | WTH-Level -1 Wall 23 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-12-14 | 2013-12-15 17:02 | 1 | 2013-11-27 08:35 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | level 0, BM34 is shown in the 2 RC columns between G/L’s H&J. In the Western RC column, there are 3no BM34 which do not allow for enough cover.
| 02SL - Stations (LUL) | Cxxx-NCR-001054 | NCR | Staircase 1&2, Stairmaster flight F7 delamination at half landing interface. |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2014-01-16 | 2013-12-15 17:04 | -32 | 2013-11-28 09:11 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The top horizontal edge of the Stairmaster flight F7 unit has delaminated at interface with the half landing at Mezzanine level (eastern end). The galvanised soffit sheet has come away from the concrete after the stairs have been poured. The length of the delamination is approx 400mm Supporting documents have been emailed to the CRL lead reviewer.
| 02SL - Stations (LUL) | Cxxx-NCR-001055 | NCR | Concrete pour level to lining wall panel 11 at level -5 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2014-01-10 | 2013-12-15 17:06 | -26 | 2013-11-28 12:00 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | At Level -5. Lining wall pour #11. The wall has not filled to the soffit of Level -4 slab. location sketch and photo emailed to CRL lead reviewer.
| 02SL - Stations (LUL) | Cxxx-NCR-001056 | NCR | WTH D-wall panel positions at level -5 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2014-01-10 | 2014-01-02 10:41 | -8 | 2013-12-02 09:49 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The following WTH D-wall panels have been found to be out of positional tolerance at level -5: This relates to Panel 3, 13, 17, 23 & 35. Note: Panels 27, 28, 29, 30, 31, 32 & 33 have not been excavated. A table of D-wall positions has been forwarded to the CRL lead reviewer. See attached table for details of permitted deviance & as-built position.
| 02SL - Stations (LUL) | Cxxx-NCR-001057 | NCR | Vertical crack to corner of upstand wall at level 0, GL G/4 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2014-01-10 | 2014-01-16 15:43 | 6 | 2013-12-02 10:36 | Civil - Civil Engineering General | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There vertical is a crack approximately 1mm wide in the interface between the upstand wall running esat west on GL 4 & the wall running north south on GL G. A photo of the affected area has been emailed to the CRL lead reviewer.
| 02SL - Stations (LUL) | Cxxx-NCR-001058 | NCR | Missing cavity drainage voids in internal RC walls at level -5 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2014-01-10 | 2013-12-15 17:11 | -26 | 2013-12-02 10:59 | Civil - Civil Engineering General | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Drawing Cxxx-__-S-DDD-Cxxx-21402-C01, detail F shows all internal walls on level -5 containing horizontal cavity drainage voids at slab level. The cavity drainage voids have only been cast into the lift shafts and the flank wall. Supporting documentation has been emailed to the CRL lead reviewer. Please note: The supporting sketch added on 06/12/13 has an additional wall missing voids highlighted
| 02SL - Stations (LUL) | Cxxx-NCR-001059 | NCR | ETH-Unexpected concrete along northern capping beam |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2014-01-10 | 2013-12-16 08:15 | -25 | 2013-12-03 08:30 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Cxxx have identified some additional concrete breakout works along the capping beam to the north of the NWS area which wasn’t expected or shown on the red line drawings. The mass concrete extends from the NW corner of the NWS at gridline B and extends along the North Capping beam to Gridline E, the depth of this varies as the capping beam changes in depth but goes from the bottom edge of the capping beam to the temporary slab.
| 02SL - Stations (LUL) | Cxxx-NCR-001060 | NCR | Expansion joints in permanent beams at level -2, H-M, 2-3 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2014-01-10 | 2013-12-16 08:16 | -25 | 2013-12-04 12:41 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Assitional expansion joints have been installed in the permanent beams installed at level -2, H-M, 2-3 in addition to those detailed on Cxxx-__-S-DDL-Cxxx-11123 & 11124. The additional joints have been installed in accordance with the details shown on Cxxx-__-S-DDD-Cxxx-21122 & have highlighted on the sketch emailed to the CRL lead reviewer.
| 02SL - Stations (LUL) | Cxxx-NCR-001061 | NCR | Concrete cold joint in level -4 lining wall 32, GL M/2-3 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2014-01-10 | 2013-12-16 08:18 | -25 | 2013-12-05 09:23 | Civil - Civil Engineering General | 2000 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A cold joint can be seen running horizontally through the RC lining wall 32 at level -4, gridline M/2-3 at approximately 2m above slab level. Note: Supporting documentation will be emailed to the CRL lead reviewer.
| 02SL - Stations (LUL) | Cxxx-NCR-001062 | NCR | Staircase 1&2, Stairmaster flight F14 & F15 delamination at half landing interface. |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2014-01-10 | 2014-01-08 13:05 | -2 | 2013-12-06 17:21 | Civil - Civil Engineering General | 1000 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | The top horizontal edge of the Stairmaster flight F14 & F15 unit has delaminated at interface with the half landing at Mezzanine level on both sides. The galvanised soffit sheet has come away from the concrete after the stairs have been poured. Note: it is possible that the same issue will affect additional stair 4&5 flights. An assessment will be made once the soffit falsework has been struck from the upper flights. The corrective action will remain the same for all affected stair flights. Supporting documents have been emailed to the CRL lead reviewer.
| 02SL - Stations (LUL) | Cxxx-NCR-001063 | NCR | WTH- Missing halfen channels at levels -1, -2 and -4 slab soffits |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2014-01-10 | 2014-01-16 15:54 | 6 | 2013-12-09 16:26 | Civil - Civil Engineering General | 1500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Inadequate/insufficient tooling. | Completed |  | At levels -1, -2 and -4 slab soffits, the halfen channels have been detailed to be installed at doorway openings. However the halfen channels in the soffits have not been installed in the doorway areas as highlighted in the attached drawings
| 02SL - Stations (LUL) | Cxxx-NCR-001064 | NCR | wth-Level-2 Eastern Lift shaft (North Wall). |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2014-01-10 | 2014-01-20 11:42 | 10 | 2013-12-09 16:39 | Civil - Civil Engineering General | 1000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | survey of the Level-2 Eastern Lift shaft (North Wall). The drawing shows the wall being approx 35mm smaller than is required. We also measured the thickness of the wall on site which was measured at 30mm smaller than required.
| 02SL - Stations (LUL) | Cxxx-NCR-001065 | NCR | Level -5 cracked __ gully at GL M/4 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2014-01-10 | 2013-12-16 08:25 | -25 | 2013-12-09 17:21 | Civil - Civil Engineering General | 1500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following the removal of the temporary timber protection boxes over the __ Drainage Gullies it has been observed that 1no. Gulley in the SE corner, GL M/4 has been damaged. The drainage Gulley in question is above the finished concrete level on one side and has been chipped in this location. The chip is over the outer flat part of the gulley radius and does not affect the main gulley cone, or connection to the upper gulley components to be fitted by Cxxx. Supporting documentation to be emailed to CRL lead reviewer
| 02SL - Stations (LUL) | Cxxx-NCR-001066 | NCR | WTH-Block work walls supporting landings on Staircase 1&2 at Levels -1, -2 and -5 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2014-01-10 | 2013-12-16 08:26 | -25 | 2013-12-11 09:00 | Architectural - Brickworks/Blockworks | 1500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | Block work walls supporting landings on Staircase 1&2 at Levels -1, -2 and -5 have been damaged due to grout loss when pouring the landing slab
| 02SL - Stations (LUL) | Cxxx-NCR-001067 | NCR | Stair 4&5 Flight 13, as-built position |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2014-01-10 | 2014-01-02 10:45 | -8 | 2013-12-11 12:10 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Flight 13 of Stairs 4 & 5 has been constructed approximately 50mm west of its design position as the setting out data provided by Cxxx was taken to be the structural location, not the finished architectural position including the 50mm finish around the nosing. Supporting documents have been emailed to the CRL lead reviewer.
| 02SL - Stations (LUL) | Cxxx-NCR-001068 | NCR | Ground floor walls at gridline A-B/1-2, Incorrect starter bar installation |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2014-01-10 | 2014-01-08 13:08 | -2 | 2013-12-11 17:45 | Civil - Civil Engineering General | 1500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Inadequate/insufficient tooling. | Completed |  | Drawing Cxxx-SKC-C-DWG-Cxxx-51107 shows Bar Mark 31 as couplers in the reinforcement detail. These have been incorrectly installed as vertical starter bars on site. BM13 is also detailed as couplers & have been installed as starter bars on site. In these locations the replacement bars are to the correct size, spacing & have adequate lap lengths. On drawing Cxxx-SKC-C-DWG-Cxxx- 51248, BM85 is detailed as couplers flush with the top of the landing. these bars were bent incorrectly and extend above the slab approx 100mm. Supporting documents have been emailed to the CRL lead reviewer.
| 02SL - Stations (LUL) | Cxxx-NCR-001069 | NCR | Ground floor - Damage to waterproof membrane adjacent to crane base, GLJ/4 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-12-20 | 2014-01-16 15:55 | 27 | 2013-12-13 13:08 | Civil - Civil Engineering General | 2000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The __ waterproof membrane 150mm lap onto the capping beam/crane base at gridline J/4 has been damaged in two location. The damage is 150mm x 150mm. A location plan has been emailed to the CRL lead reviewer.
| 02SL - Stations (LUL) | Cxxx-NCR-001070 | NCR | Stair 1&2, Level -4 half landing, Incorrect pour line. |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2013-12-20 | 2014-01-16 16:01 | 27 | 2013-12-13 16:25 | Civil - Civil Engineering General | 2000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | At level -4, the stair 1&2 half landing has been poured with an addition area in error. There is an RC non load bearing wall on the west side of the landing which is designed to come up from level -4 to level -2. The reinforcement has been detailed in error to cover the entire area of the slab including the area where the wall is designed to come through. The slab was cast in the area marked in red on the attached sketch (emailed to the CRL lead reviewer)
| 02SL - Stations (LUL) | Cxxx-NCR-001072 | NCR | Temporary Sheet Piles remain in the ground |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2014-01-24 | 2014-01-20 10:00 | -4 | 2014-01-10 14:40 | Civil - Civil Engineering General | 3000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Temporary sheet piles which were due to be extracted for Completion shown on the attached sketch have not been removed form the works. This is due to refusal during extraction or proximity to services.
| 02SL - Stations (LUL) | Cxxx-NCR-001073 | NCR | Cxxx WTH I&M Installation, Handover and UCIMS |  | Crossrail | PDP | BOS - Bond Street Station (West) |  | 2014-03-21 | 2014-06-30 12:01 | 101 | 2014-03-07 13:48 | Surveying - Instrumentation and Monitoring | 6000 |  | Incomplete Works | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | The Project Manager, together with Cxxx/Cxxx, have undertaken a comprehensive review of the Cxxx I&M installation at the WTH, I&M documentation and I&M UCIMS data that was handed over to CRL on 16/12/13. This review has identified number of comments and non-conformances of physical equipment conditions, system installation and documentation requirements as specified in Cxxx and Cxxx I&M specs KX10 (Cxxx-__-C2-RSP-Cxxx-00001 and Cxxx-OVE-Z4-RSP-CR001-00007 respectively). Please refer to Comments on WTH I and M Handover Document - Cxxx--Z-XCS-CRT00_ST005-59028 for a list of these comments and non-conformances. In addition to the above list, The Project Manager identified the following; Instrument Comment Cxxx-IE700005-CR084 - Erratic readings of sensors A & B throughout life. Last readings on 13/12/13. Cxxx-IE700008-CR084 - Data in UCIMS shows 30nos sensors Installation report records 15. Last UCIMS data on 22/08/12. Clarification required on which are X & Y sensors as this is not included in the installation report. Cxxx-XR700003-CR084 - on UCIMS, sensors A through F showing disproportionate readings at handover. Cxxx-XR700004-CR084 - Erratic readings on UCIMS Cxxx-XR700010-CR084 - Duplicate data on UCIMS. Cxxx-XR700011-CR084 - Sensor C last reading on 30/06/13.
| 02SL - Stations (LUL) | Cxxx-NCR-001074 | NCR | ETH in-pile inclinometers |  | Crossrail | PDP | BOS - Bond Street Station (West) |  | 2014-04-02 | 2014-06-30 13:10 | 89 | 2014-03-19 17:14 | Surveying - Instrumentation and Monitoring | 10000 |  | System Defect | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | The Project Manager’s other contractor (Cxxx) are unable to interpret raw data downloaded directly from the in-pile inclinometer datalogger at the ETH as it is in an unrecognisable format which is not defined in Cxxx documentation. Specifically, the datalogger is outputting data in an unrecognisable format, it is not possible to establish which data is for which instrument and for which sensor, and it is not known whether the data loggers are manipulating / applying correction factors to the data. Any proprietry software required to interpret instrumentation readings has also not been provided.
| 02SL - Stations (LUL) | Cxxx-NCR-001075 | NCR | ETH instrumentation and monitoring - in ground instruments |  | Crossrail | PDP | BOS - Bond Street Station (West) |  | 2014-07-30 | 2014-07-14 15:18 | -16 | 2014-04-17 07:59 | Surveying - Instrumentation and Monitoring | 10000 |  | Incorrect Installation | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | The Project Manager's review of the Cxxx I&M installation at the ETH has identified non-conformances in the equipment condition, system installation and documentation requirements as specified in Cxxx I&M specification KX10 (Cxxx-OVE-Z4-RSP-CR001-00007). Cxxx-XR700015-CR084 in the roadway in front of 21 Hanover Sq has a faulty vibrating wire interface. Cxxx-IE700010-CR084 has been configured such that it will not work without the proprietry software that has not been made avaialble to the Project Manager. Insufficient information has been provided to enable the full functional use of this equipment. Cxxx-XR700014-CR084 is only partially working as some sensors are faulty and was seen to be in very poor condition as a result of water ingress resulting from the incomplete chamber installation.
| 02SL - Stations (LUL) | Cxxx-NCR-000005 | NCR | ETH-missing shear rails at P18 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2014-02-21 | 2014-03-06 12:13 | 13 | 2013-12-09 14:00 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Missing shear rails at P18. These were missed and only the northern 4 rails have been installed in the slab pour
| 02SL - Stations (LUL) | Cxxx-NCR-000006 | NCR | ETH- use of Non approved concrete mix from __-Battersea plant |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2014-01-31 | 2014-01-16 14:23 | -15 | 2013-12-23 15:05 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | ETH- use of Non approved concrete mix from __-Battersea plant
| 02SL - Stations (LUL) | Cxxx-NCR-000009 | NCR | Eastern Ticket Hall Pile 113 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2014-02-28 | 2014-02-11 08:31 | -17 | 2014-01-27 08:38 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In pile 113 a reservation tube was installed for an inclinometer. were instructed to install the inclinometer tubing and the inclinometer into this pile under PMI 00115. Please note in Cxxx, NCR 00687 noted that the reservation tube in pile 113 was blocked 17m below ground. The response was Cxxx/xxx to install the inclinometer as part of the snagging of the masterplan shaft. The reservation tube is now inaccessible as the level 0 slab has been cast over it. To access this tube now would involve demolition of the permanent works and re-drilling of the tube
| 02SL - Stations (LUL) | Cxxx-NCR-000011 | NCR | Eastern Ticket Hall – Damage to Ground floor beam L-0-B2 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2015-10-05 | 2015-02-10 09:15 | -237 | 2014-03-10 11:28 | Civil - Civil Engineering General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The soffit of the North & South side of the beam L-0-B2 has been damaged during the breaking out of the temporary slab in the NWS.
| 02SL - Stations (LUL) | Cxxx-NCR-000012 | NCR | ETH-damage to the Cxxx GF slab soffit |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2014-07-31 | 2014-09-04 13:29 | 35 | 2014-03-13 13:59 | Civil - Civil Engineering General | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the blinding removal to the soffit of the ground floor slab, the breaker attachment fitted to an excavator has gone through the blinding into the permanent works exposing a section of reinforcement (location and photograph enclosed).
| 02SL - Stations (LUL) | Cxxx-NCR-000013 | NCR | ETH-Concrete strength is more than 20N/mm2 above the specified minimum cube strength |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2014-04-09 | 2014-04-17 10:21 | 8 | 2014-03-26 11:24 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Concrete strength is more than 20N/mm2 above the specified minimum cube strength-Level 0 Slab
| 02SL - Stations (LUL) | Cxxx-NCR-000014 | NCR | ETH-Damage Ground floor soffit |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-12-16 | 2016-12-09 11:46 | -7 | 2014-03-26 11:37 | Civil - Civil Engineering General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The soffit of the ground floor slab has been damaged due to the breaking out of the blinding.
| 02SL - Stations (LUL) | Cxxx-NCR-000015 | NCR | ETH-Damage to North West Shaft Capping Beam |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2014-10-03 | 2014-11-01 09:56 | 29 | 2014-03-28 12:02 | Civil - Civil Engineering General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | During removal of mass fill concrete sat directly below the permanent capping beam in the North West Shaft, a section of capping beam in the north west corner was mistaken for mass concrete and broken. 3no diamond cores were made through the area of the capping beam, severing some of the reinforcement. The damaged areas and reinforcement is identified on the attached drawings
| 02SL - Stations (LUL) | Cxxx-NCR-000016 | NCR | ETH- Ground floor slab additional reinforcement in Level 0 slab – Pour 5 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2014-04-30 | 2014-05-14 13:41 | 14 | 2014-04-11 09:21 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Correct process for RFI clarification close out not followed. Following issues with reinforcement identified on the 03/12/13, a review of areas of congestion & low cover were reviewed by __, __ & __ in 75 Davies St. & the following agreed:
| 02SL - Stations (LUL) | Cxxx-NCR-000018 | NCR | ETH-Damages/ defects to the level 0 Slab soffit |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2017-08-30 | 2017-09-03 11:10 | 4 | 2014-05-30 08:26 | Civil - Civil Engineering General | 10000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Other | Completed |  | Following a post pour between and CRL all damages/ defects to the level 0 Slab soffit have been identified and recorded on the enclosed attachments.
| 02SL - Stations (LUL) | Cxxx-NCR-000019 | NCR | ETH- Face of southern wailing beam between GL B-D has been damaged by retarder |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2014-06-30 | 2014-07-09 11:26 | 9 | 2014-06-09 10:50 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following a post pour between and CRL it has been identified a section of the front face of southern wailing beam between GL B-D has been damaged by retarder that has leaked down the face of the shutter , this has caused the surface 1- 2mm of concrete to come away
| 02SL - Stations (LUL) | Cxxx-NCR-000022 | NCR | Level -1, NWS slab soffit repairs |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2014-11-15 | 2014-11-21 13:01 | 6 | 2014-06-25 17:13 | Civil - Civil Engineering General | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Post pour inspection with and CRL personnel identified and recorded several areas of damage/ defects to the level -1 Slab soffit within the NWS - see enclosed attachments. Various honeycombing is the problem noted in several locations.
| 02SL - Stations (LUL) | Cxxx-NCR-000023 | NCR | ETH Level-1 (slab 1 & 3 soffit) honeycombing in concrete discovered |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2014-07-09 | 2014-07-11 10:16 | 2 | 2014-06-25 17:44 | Civil - Civil Engineering General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | An area of honeycombing was discovered when exposing the construction joint between Slab 1 & 3 at level -1.
| 02SL - Stations (LUL) | Cxxx-NCR-000025 | NCR | ETH-Beam 6 has been detailed with an ‘eazistrip’ connection |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2014-07-15 | 2014-07-10 14:34 | -5 | 2014-07-01 15:37 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Beam 6 (Cxxx-SKC-S-DWG-Cxxx-50022) has been detailed with an ‘eazistrip’ connection above a non-load-bearing wall. As per DWG: Cxxx-__-S-DDD-Cxxx-57040 cast in channel should have been detailed at this location.
| 02SL - Stations (LUL) | Cxxx-NCR-000026 | NCR | ETH-Insufficient cover to reinforcement in beam at 0 level in the West side of NW shaft |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2014-12-31 | 2015-03-04 11:21 | 63 | 2014-08-08 14:16 | Civil - Civil Engineering General | 5000 |  | Workmanship | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | Insufficient cover to reinforcement has been caused due to concrete spacers piercing polystyrene slab formwork at chamfered edges, beam at 0 level in the West side of NW shaft
| 02SL - Stations (LUL) | Cxxx-NCR-000028 | NCR | Design control and administration procedures not in place |  | Crossrail | PDP | BOS - Bond Street Station (West) |  | 2014-09-17 | 2014-10-24 16:56 | 37 | 2014-09-03 10:01 | Mechanical - Mechanical Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Survaillance QS 412-01 found Contractor's procedure Cxxx-SKC-O4-GPD-Cxxx-50005 rev 2.0 Approval Status –“ not approved” Document Status – “draft” therefore not a working document.Reveiw of the procedure found it incomplete, for example; absence of planed arrangements for programme change contro.l
| 02SL - Stations (LUL) | Cxxx-NCR-000029 | NCR | to __’s quality plan at Decal Status Code 2 for more than 7 months |  | Crossrail | PDP | BOS - Bond Street Station (West) |  | 2014-09-17 | 2014-10-31 12:12 | 44 | 2014-09-03 10:43 | Mechanical - Mechanical Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | __’s Quality Plan (QP) Cxxx-SKC-O4-STP-CR5-50002 rev 1.0 decal code 2 ( “Not accepted. Revise and resubmit. Work may proceed subject to incorporation of changes indicated”.) since 6th December 2013. Resubmission should have taken place within the period of reply
| 02SL - Stations (LUL) | Cxxx-NCR-000030 | NCR | Superseded document tabbed as current during surveillance QS412-01 |  | Crossrail | PDP | BOS - Bond Street Station (West) |  | 2014-09-17 | 2014-10-24 12:23 | 37 | 2014-09-03 11:11 | Mechanical - Mechanical Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | Superseded Cxxx Design Management Plan (DMP) Cxxx-SKC-N2-STP-Cxxx-50003 rev 2 tabbed as current during surveillance QS412-01, please see the report for details .
| 02SL - Stations (LUL) | Cxxx-NCR-000031 | NCR | No evidence of transmittals within the Aconex system for RFIs sected for surveillance QS412-01 |  | Crossrail | PDP | BOS - Bond Street Station (West) |  | 2014-09-17 | 2014-10-24 12:24 | 37 | 2014-09-03 11:19 | Mechanical - Mechanical Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | No evidence of transmittals within the Aconex system for RFIs 000662 and 000546, FCD 000013 and NCRs 000006 and 000022 or the associated red line drawings and Decal Code status.
| 02SL - Stations (LUL) | Cxxx-NCR-000034 | NCR | ETH: Slab 2 (Level -2), between GL 1-2 & C.5-D.plastic settlement cracking |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2015-01-31 | 2015-01-12 09:57 | -19 | 2014-09-10 16:25 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Suspected plastic settlement cracking has occurred on the surface of slab 2 (Level -2), between GL 1-2 & C.5-D.
| 02SL - Stations (LUL) | Cxxx-NCR-000035 | NCR | ICDs missing key information. |  | Crossrail | PDP | BOS - Bond Street Station (West) |  | 2014-09-17 | 2014-10-24 16:57 | 37 | 2014-09-03 14:40 | Mechanical - Mechanical Engineering General | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | ICD Cxxx-SKC-K1-STP-Cxxx-5001 & ICD Cxxx-SKC-K1-STP-Cxxx-50002 do not contain all the requred key information
| 02SL - Stations (LUL) | Cxxx-NCR-000036 | NCR | ETH Level -2: Southern Waling Beam (GL C-E) cast in sockets |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2015-11-30 | 2015-09-10 17:12 | -81 | 2014-09-11 15:26 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The cast in sockets for props 15-18 (4 No. in each) where cast in. 220mm high, resulting in them being unusable. 4No. 28mm cores to a depth of 300mm were undertaken at the correct positions for each prop (15-18). 24Ø threaded bar (embedment depth 300mm) have been installed using __- HY 200 as replacements to the detailed ancon sockets. All changes were confirmed with the temporary works designer and check cert re-issued
| 02SL - Stations (LUL) | Cxxx-NCR-000037 | NCR | Contradictory information supplied in FCD 038 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2014-10-07 | 2014-10-21 12:53 | 14 | 2014-09-23 18:11 | Civil - Civil Engineering General | 2000 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | This NCR is for providing contradictory survye information in FCD 038 and does not relate to a non conformace in the works executed on site. The enclosed excel sheet shows some discrepancies between the survey information and the installed drilled and fixed B25 bars which is apparent from details which were enclosed within FCD 038 (for piles 40 – 53). Also detailed within the excel sheet are the quantity of B25 bars actually installed as supported by attached photographs. The photographic survey provides contrasting information which clarifies the actual records of holes drilled to fulfil FCD/RFI requirements.
| 02SL - Stations (LUL) | Cxxx-NCR-000038 | NCR | ETH level -1 honeycombing in soffit of slab 1 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2014-10-10 | 2014-11-06 16:42 | 27 | 2014-09-26 18:40 | Civil - Civil Engineering General | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The soffit of slab 1 level -1 has honey combing and voids within the slab between GL 1 and 3 (photos and location attached)
| 02SL - Stations (LUL) | Cxxx-NCR-000039 | NCR | ETH-Horizontal joint within Lining wall between level -2 & -1 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2014-10-22 | 2014-10-21 09:27 | -1 | 2014-10-08 12:13 | Civil - Civil Engineering General | 1000 |  | Equipment Breakdown | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | During the pour of level -2 to -1 lining wall, ‘Pour 1’ (as per enclosed pour plan location) the concrete pump broke down, the pour was not completed in one lift to the soffit of level -1 slab.
| 02SL - Stations (LUL) | Cxxx-NCR-000040 | NCR | ETH Main Box Level -2 Lining wall Pour 2, NE corner between Wall 7 and 9-delaminated finish |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2014-12-31 | 2014-11-21 12:47 | -40 | 2014-10-17 08:31 | Civil - Civil Engineering General | 3000 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The top 1.2m section of lining wall has a delaminated finish to the front of the wall, with vertical streaks on the surface. This does not comply with KF10.3218 which states Voids, honeycombing, segregation and other large defects are not permitted.
| 02SL - Stations (LUL) | Cxxx-NCR-000041 | NCR | ETH Main Box Level -2 Lining Wall ,step in joint |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2015-01-31 | 2014-12-18 15:17 | -44 | 2014-11-13 11:46 | Civil - Civil Engineering General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | ETH Main Box Level -2 Lining Wall Pour 7 (North Wall) & Pour 12 (East Wall) There is 2no locations where the shuttering and formed a step in the face of approximately 15mm. KF10.3218 Section C states that there are to be no sudden irregularities more than 5mm. In the two locations stated, this is approximately 15mm. See attached location plan
| 02SL - Stations (LUL) | Cxxx-NCR-000042 | NCR | ETH-level -3 plunge column (P25,29,39,31,33,34,35)splicing detail,loose bolts |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2015-04-30 | 2015-05-11 14:40 | 11 | 2014-11-18 11:22 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following excavation for installation of collars to level -3, the plunge column splicing detail was exposed (P25,29,39,31,33,34,35). Various bolts on the plunge column splices were found to be loose and spinning. 2no bolts on P25 were completely undone from their nuts. Below is a list of the loose bolts on each plunge column. P25: 1no Loose, 2no Undone from their nut, 1no Tight P29: 1no Loose, 3no Tight P30: 2no Loose, 2no Tight P31: 3no Loose, 1no Tight P33: 4no Loose P34: 3no Loose, 1no Tight P35: 3no Loose, 1no Tight
| 02SL - Stations (LUL) | Cxxx-NCR-000043 | NCR | ETH Main Box Level -1 slab soffit, slab 4-Honey combing |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2014-12-31 | 2014-12-17 10:54 | -14 | 2014-11-26 15:39 | Civil - Civil Engineering General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Honey combing in the soffit of level -1 slab soffit, slab 4. Drawing showing location attached. Honey combing had been broken out by __s before the area was inspected so the only photos available show area once it had been broken back ready for repair.
| 02SL - Stations (LUL) | Cxxx-NCR-000044 | NCR | ETH-Level -2 Slab 3 missing B32 starter bars |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2015-09-30 | 2015-05-08 16:49 | -145 | 2014-12-03 10:31 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Level -2 Slab 3 .Cxxx-FCD-00047 Detailed that 5No. B32 starter bars needed to be installed within slab 3 at Level -2. These 32mm bars have not been installed.
| 02SL - Stations (LUL) | Cxxx-NCR-000045 | NCR | ETH_Level -2 Slab 1 pile connections for P57 and P65 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2015-02-28 | 2015-03-09 15:29 | 9 | 2014-12-03 10:34 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Level -2 Slab 1 pile connections for P57 and P65 .The drill and fix details approved in Cxxx-RFI-905 which was later superseded by Cxxx-FCD-00059 has not been followed in piles P57 and P65. Cxxx-FCD-00025 details what was completed and Pile P57 is missing 2No. B25 replacement dowels in the top layer and P65 is missing 1 No. B25 replacement dowel in the top layer.
| 02SL - Stations (LUL) | Cxxx-NCR-000046 | NCR | ETH-Level -2 Waling Beam WB2-3 Pile connections P80 – P83 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2015-02-28 | 2015-03-09 15:29 | 9 | 2014-12-03 10:39 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The drill and fix details approved in Cxxx-RFI-905 which was later superseded by Cxxx-FCD-00059 have not been followed in piles P80 to P83. Cxxx-FCD-00026 details what has been completed and Piles P80 to P83 have only had 4 B25 replacement bars drilled rather than the 12 No. specified in RFI-905 therefore there are 8No. B25 replacement dowels missing in the top layer from each pile.
| 02SL - Stations (LUL) | Cxxx-NCR-000047 | NCR | ETH-Level -2 Beam 1.working to non approved drawing |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2015-02-28 | 2015-01-09 11:48 | -50 | 2014-12-03 10:42 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | have installed an additional BM36 spacer and BM E148 and E149 are 1.5m longer than shown in the approved drawing Cxxx-SKC-S-DWG-Cxxx-50062 Rev C06. The attached Cxxx-SKC-S-DWG-Cxxx-50062 Rev C07 was issued for review prior to the beam being completed and details these changes- revision C07 is still awaiting acceptance from CRL. The amendments were made to ensure the B40 lacers extended past the opening between Beams 1 and 2 at Level -2 shown on the builder’s works drawing Cxxx-SKC-M-DDA-Cxxx-69120 within Cxxx-SKC-M-RGN-Cxxx-50002 mini gate submission.
| 02SL - Stations (LUL) | Cxxx-NCR-000048 | NCR | ETH Main Box Level -2 Lining Wall Pour 9 (North Wall)-step in the face of approximately 18mm |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2015-02-28 | 2014-12-19 15:51 | -71 | 2014-12-02 14:19 | Civil - Civil Engineering General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Level -2 there is a location where the shuttering has formed a step in the face of approximately 18mm. KF10.3218 Section C states that there are to be no sudden irregularities more than 5mm. See attached location plan
| 02SL - Stations (LUL) | Cxxx-NCR-000049 | NCR | ETH Main Box Level -2 Lining wall Pour 2, NW corner between Wall 8 and 9 -small area of delaminated finish |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2015-02-28 | 2015-01-08 16:04 | -51 | 2014-12-02 14:27 | Civil - Civil Engineering General | 2000 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The top 1.5m section of lining wall has a delaminated finish to the front of the wall, with vertical streaks on the surface (Photo 001, 003 & 004); this is believed to be sand scouring as a result of a high slump range self-compacting concrete mix. A section of lining wall 8 has punch marks in the formed face from nails (Photo 002). These do not comply with KF10.3218 which states Voids, honeycombing, segregation and other defects are not permitted.
| 02SL - Stations (LUL) | Cxxx-NCR-000050 | NCR | ETH-Level -2 Lining walls,hydrophilic strip |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2017-08-30 | 2017-08-12 14:30 | -18 | 2014-12-02 14:43 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | In accordance with details contained within drawing Cxxx-__-S-DDD-Cxxx-57030, hydrophilic strip is required along the horizontal construction joints between slabs and at the vertical construction joints between lining wall pours. Subsequent RFI’S have been raised in relation to this drawing to clarify and amend the existing details (RFI 329 & 591). We believe the misinterpretation of these amendments has led to the hydrophilic strips not being installed at the level -2 lining walls. Details of the missing hydrophilic strips are detailed in the enclosed drawing ‘Lining wall mark-up’. Please note __ detail has been installed in accordance RFI 319
| 02SL - Stations (LUL) | Cxxx-NCR-000051 | NCR | ETH-Level -2 Plunge Column Infill sections ,additional B16 couplers |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2015-02-28 | 2014-12-22 11:46 | -68 | 2014-12-03 14:24 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Additional B16 couplers have been installed around the temporary plunge columns as shown in the attached sketch. These have been installed to allow for reinforcement to be installed within the infill section after the columns have been removed. The B16 couplers are not shown on the RC drawings for level -2 and have not been detailed on either an RFI or FCD
| 02SL - Stations (LUL) | Cxxx-NCR-000052 | NCR | ETH-post pour inspection to the surface of slabs 3 + 4 (GL1-3, B-E) at level -1(Replaces NCR 000021) |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2015-03-31 | 2015-04-13 10:52 | 13 | 2014-12-03 16:01 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Post pour inspection to the surface of slabs 3 + 4 (GL1-3, B-E) at level -1 Non-conformances include poor surface finish, slab step, chip, and cracking, including the making good requirements. See attached for more details
| 02SL - Stations (LUL) | Cxxx-NCR-000053 | NCR | ETH-Level -2 Slab 2,working to code 2 drawings |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2015-02-28 | 2015-01-21 16:40 | -38 | 2014-12-05 15:22 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | have poured slab 2 at level -2 using an RC drawing (Cxxx-SKC-S-DWG-Cxxx-50054-C05) which was not accepted by CRL but was returned as decal code 2 with comments. The comments can be seen in Cxxx-__-S-XCS-Cxxx-50285 and were incorporated within Cxxx-SKC-S-DWG-Cxxx-50054-C06 which was submitted after the slab was poured so has not been accepted by CRL. Comment 1: Requested additional bars including 3 No. BM175 and 3 No. BM176 these have been installed as shown in the attached drawing. Comment 2 suggested that could reduce BM139 and BM 140 from 10No. to 6 No. but as had already installed 10No. bars this was not changed onsite. Comments 3 and 4 were incorporated onsite.
| 02SL - Stations (LUL) | Cxxx-NCR-000054 | NCR | ETH-Level -2 Slab 3-working to code 2 drawings |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2015-02-28 | 2015-01-21 16:49 | -38 | 2014-12-05 15:27 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | have poured slab 3 at level -2 using RC drawings (Cxxx-SKC-S-DWG-Cxxx-50055-C06, Cxxx-SKC-S-DWG-Cxxx-50056-C06, Cxxx-SKC-S-DWG-Cxxx-50057-C04) which have not been accepted by CRL but have been returned as code 2 decal with comments. These comments are detailed in the comment sheets Cxxx-__-S-XCS-Cxxx-50289, Cxxx-__-S-XCS-Cxxx-50290 and Cxxx-__-S-XCS-Cxxx-50002. All the comments have been incorporated in the reinforcement installed onsite but the drawings have not been revised and re submitted. The additional bars installed as per the comments can be seen on the attached marked up drawings.
| 02SL - Stations (LUL) | Cxxx-NCR-000055 | NCR | ETH-Void formed in the soffit of Slab 2, Level -1 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2017-06-17 | 2017-06-23 14:33 | 6 | 2015-01-07 08:22 | Civil - Civil Engineering General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | This NCR supersedes the incomplete work in NCR-000020. This NCR covers the void formed in the soffit of Slab 2, Level -1 (see attached drawing for location). The area in the soffit of the slab has been temporarily filled with concrete to protect the exposed reinforcement until we can access the area to carry out a full repair. The void is adjacent to MH1 so access will be restricted until we are working on the walls in that area.
| 02SL - Stations (LUL) | Cxxx-NCR-000056 | NCR | ETH-There is a step of up to approximately 10mm in the L-1 slab soffit at the join between the blinding in the main box |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2015-02-28 | 2015-03-03 10:43 | 3 | 2015-01-07 15:06 | Civil - Civil Engineering General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | There is a step of up to approximately 10mm in the L-1 slab soffit at the join between the blinding in the main box and the formwork in the NWS, including an area of indentation around the edge of the 2x2m
| 02SL - Stations (LUL) | Cxxx-NCR-000057 | NCR | ETH-There is one area of impact damage to L-1 slab soffit |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2015-02-28 | 2015-03-04 11:22 | 4 | 2015-01-07 15:13 | Civil - Civil Engineering General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | There is one area of impact damage to L-1 slab soffit which occured during the removal of the blinding using an excavator. The damage is approximately 50mm deep and there is some reinforcement exposed.
| 02SL - Stations (LUL) | Cxxx-NCR-000059 | NCR | ETH Level -2 Slab Beam 3-2 No. 300Ø sleeves IL = +111.950 were not installed within the drop down beam |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2015-02-27 | 2015-02-10 15:33 | -17 | 2015-01-27 08:49 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 2 No. 300Ø sleeves IL = +111.950 were not installed within the drop down beam which is shown on the general arrangement drawing Cxxx-__-S-DDL-Cxxx-52123 and Cxxx-SKC-S-DWG-Cxxx-50062. An RFI was raised (Cxxx-RFI-000819) which stated that Cxxx MEP had confirmed that they were not required. This RFI did not give an explanation indicating why they were not needed and as such was not answered satisfactorily. This is an NCR because there is no confirmation from Cxxx that the sleeves can be removed from the GA and the beam has already been poured. It is also noted that the reinforcement drawing Cxxx-SKC-S-DWG-Cxxx-50062 and the builder’s works drawing do not correlate, with the Sleeves shown on the RC drawing but not on the Builders works.
| 02SL - Stations (LUL) | Cxxx-NCR-000062 | NCR | ETH-Concrete pipe clip indent WB 2 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2015-04-30 | 2015-03-23 12:56 | -38 | 2015-02-25 09:20 | Civil - Civil Engineering General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the concreting of WB2 a concrete clip fell into the pour up against the shutter, This could not be removed during the pour and was taken off with the shutters. This has left a void in the concrete which can be seen in the attached photo. It can be seen in the photo that there has been no damage to the reinforcement.
| 02SL - Stations (LUL) | Cxxx-NCR-000063 | NCR | ETH-slab 1 at Level -3 missing Eazistrip |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2017-01-31 | 2017-01-04 11:57 | -27 | 2015-04-17 15:31 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During construction of slab 1 at Level -3 the Eazistrip highlighted in the attached drawing Cxxx-SKC-S-DWG-Cxxx-50094 was not installed. This is required for a down stand from the level -3 slab soffit. Section C312-__-S-DDC-Cxxx-563081 shows the wall that the Eazistrip was designed to tie into.
| 02SL - Stations (LUL) | Cxxx-NCR-000064 | NCR | T&P-Base Slab / Track Slab bar marks 11 adjusted on site |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2015-04-30 | 2015-04-13 10:56 | -17 | 2015-03-25 12:57 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | We have found an issue with one of the Base Slab / Track Slab bar marks on site. It affects every Base Slab / track slab schedule. The schedules don’t detail the required crank on BM 11. See attached photo – the one with the greater crank has been modified by us to suit the tunnel alignment prior to obtaining the PM instruction.This is because the schedules are missing a dimension.
| 02SL - Stations (LUL) | Cxxx-NCR-000065 | NCR | P&T- Dowel bars grout in concrete base slab |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2015-04-10 | 2015-05-01 15:00 | 21 | 2015-03-27 14:16 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Use of approved chemical resin material Cxxx-SKC-O4-QSV-Cxxx-50042 Revision 1.0 Material Compliance Record - Rawl R-KER 200 in a non approved location, for grouting in dowel bars into the concrete base slab of the running tunnel .Total number of dowels installed using chemical resin is 62 No.
| 02SL - Stations (LUL) | Cxxx-NCR-000066 | NCR | ETH Level -3 Slab 1 GL 2 -300 x 300 opening |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-12-11 | 2016-11-22 14:54 | -19 | 2015-04-17 15:36 | Civil - Civil Engineering General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Drawing Cxxx-__-S-DDL-Cxxx-52135 Rev C01 shows a 300 x 300 opening along GL 2. This was removed from the builder’s works drawing Cxxx-SKC-M-DDA-Cxxx-69130 after response from Cxxx-RFI-000990. The box out was not removed from the reinforcement drawings Cxxx-SKC-S-DWG-Cxxx-50077 and was subsequently installed onsite.
| 02SL - Stations (LUL) | Cxxx-NCR-000067 | NCR | ETH L0, -1, -2 Lift shaft |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2015-04-30 | 2015-10-07 15:22 | 160 | 2015-03-27 11:22 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | 2no 160mm diameter sleeves (as shown on the Cxxx structural GA’s Cxxx-__-S-DDL-Cxxx-52124, 52114, 52104) have been installed in the lift shaft on Level 0, -1, and -2 instead of 2no 300mm x 300mm box outs opening required and as shown on the assured builderswork drawings for each level.
| 02SL - Stations (LUL) | Cxxx-NCR-000068 | NCR | ETH- damage to concrete face at level -3 opening grid line D-E/2-3 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-09-30 | 2016-10-18 15:26 | 18 | 2015-04-02 11:16 | Civil - Civil Engineering General | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Damage to concrete face at level -3 opening grid line D-E/2-3
| 02SL - Stations (LUL) | Cxxx-NCR-000069 | NCR | ETH Main box – soffit Slab L-2 repairs |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-01-15 | 2016-01-14 15:48 | -1 | 2015-04-08 14:31 | Civil - Civil Engineering General | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | During the blinding removal to the soffit of the L-2 slab, the breaker attachment fitted to an excavator has gone through the blinding into the permanent works. There are 6no. locations shown on the attached drawing, with associated photos attached.
| 02SL - Stations (LUL) | Cxxx-NCR-000070 | NCR | ETH Level -3 NWS Soffit repairs |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-01-15 | 2016-01-14 15:47 | -1 | 2015-04-17 15:22 | Civil - Civil Engineering General | 2999 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | ETH Level -3 NWS Soffit repairs following post pour inspection
| 02SL - Stations (LUL) | Cxxx-NCR-000071 | NCR | ETH Level -3 Temporary infill slab,use of non approved material |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2015-05-29 | 2015-07-14 13:59 | 46 | 2015-04-21 08:46 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | have cast in __ M24/100 sockets in the level -3 slab, as per detail on drawing Cxxx-SKC-C-DWG-Cxxx-50082 Rev C01. This product has not been approved by the PM via the MCR process.
| 02SL - Stations (LUL) | Cxxx-NCR-000072 | NCR | P&T Base Slab (E/B & W/B)-Step at foot of BS upstand to TS |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2015-10-31 | 2015-11-20 12:31 | 20 | 2015-04-24 09:27 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | There are a number of locations on the base slab throughout the tunnel, where the concrete at the foot track slab upstand has been non-conformant with respect to KF10.3222 f) & v). Please note that the step change observed does not exceed 15mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000073 | NCR | P&T Base Slab (E/B & W/B)-Damage to BS Drainage Channel |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2015-10-31 | 2015-11-20 12:32 | 20 | 2015-04-24 09:31 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | There are a number of locations on the base slab throughout the tunnel, where the concrete around the edge of the cast drainage channel has been damaged. The resulting slab is non-conformant with respect to KF10.3222 f) v):
| 02SL - Stations (LUL) | Cxxx-NCR-000074 | NCR | P&T Track Slab W4 -low concrete pour |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2015-05-31 | 2015-05-19 08:47 | -12 | 2015-04-24 10:22 | Civil - Civil Engineering General | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A shortfall in concrete resulted in the construction joint of the track slab W4 deviating from its intent as shown on Cxxx-__-S-DDD-Cxxx-83180 C05 and Cxxx-SKC-S-DWG-Cxxx-50223 Rev 4.0. The area poured low sits within the track wall and upstand, to the east of pour four as shown on marked up drawing.
| 02SL - Stations (LUL) | Cxxx-NCR-000075 | NCR | Cxxx- Eastbound and Westbound Tunnels repairs local to the construction joint between the base and track slabs, |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2015-12-31 | 2015-11-20 12:33 | -41 | 2015-05-14 08:29 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Areas local to the construction joint between the base and track slabs, with the service and track wall respectively, have been in need of repair. These repairs are due to the following: - Chipped edges along the top of the kickers - Pour compaction at top of kicker These repairs happen at a frequency of approximately 1 per 25m section pour; but will be captured in the post-pour inspections. The repairs required range from up to: - approx. 100mm below the prescribed level of the construction joint - approx. 50mm penetration into the wall - approx. 650mm long sections The sample image is of TW W8/TS W4 construction joint (before the wall was poured). The section is 300mm long, 75mm below the prescribed level and 30mm penetration into the wall.
| 02SL - Stations (LUL) | Cxxx-NCR-000076 | NCR | Cxxx- Westbound Tunnel-Several GFRP rebar have rotated about its vertical axis during the concrete pour process |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2015-05-27 | 2015-06-15 17:32 | 19 | 2015-05-13 11:55 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Several of the hooked GFRP bars detailed on Cxxx-__-S-DDD-Cxxx-14322 C06, Typical Reinforcement Section and details have been rotated about its vertical axis during the concrete pour process. The number of bars will be captured in the post-pour inspection sheets
| 02SL - Stations (LUL) | Cxxx-NCR-000077 | NCR | P&T Westbound Tunnel (TS W9) bar bending operation |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2015-07-31 | 2015-10-08 09:51 | 69 | 2015-05-18 10:19 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | found an issue with one of the additional bars relating to Cxxx-FCD-000113 (approximately 88no.). The additional bar shown on the drawing was a B12, which is required to penetrate a minimum of 400mm into the pour. Hy-ten delivered this a straight bar which then clashed with the side of the SCL. Opportunities for communication between and __s were missed and this resulted in __s Formwork forming the kink in the “tail” of the bar without having an agreed bending procedure onsite and without specifically obtaining the PM instruction. The B12 bar was bent to for an approximate 140’ angle.
| 02SL - Stations (LUL) | Cxxx-NCR-000078 | NCR | P&T-Westbound Tunnel (SW W18) short concrete pour |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2015-06-30 | 2015-07-02 14:08 | 2 | 2015-05-18 10:36 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The service wall SW W18 pour was short by approximately half a metre of concrete. Retarder was applied along this construction joint in preparation for the remedial measures at the time of the pour, given the supply of additional concrete was impossible. The resulting construction joint does not conform with the intent shown on Cxxx-SKC-S-DWG-Cxxx-50254 (C04) and Cxxx-__-S-DDD-Cxxx-83180 (C05).
| 02SL - Stations (LUL) | Cxxx-NCR-000079 | NCR | P&T-Westbound tunnel – Service Walls top reinforcement detail |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2015-12-18 | 2016-01-15 11:47 | 28 | 2015-06-15 10:41 | Civil - Civil Engineering General | 3000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | noticed a variation between the Cxxx/__ reinforcement intent and Cxxx/__ approved reinforcement drawings with respect to the dowel projecting from service wall shown on: - Cxxx-__-S-DDD-Cxxx-14322 Detail 2 - Cxxx-SKC-S-DWG-Cxxx-50248-50249, 50253-50255 SECTION 1 – detailed as a B12 600 length, straight bar.The service walls listed below were poured to approve reinforcement drawings, which detailed the dowel as a straight bar. SW W4 Cxxx-SKC-S-DWG-Cxxx-50253 C03 SW W5 Cxxx-SKC-S-DWG-Cxxx-50253 C03 SW W6 Cxxx-SKC-S-DWG-Cxxx-50253 C03 SW W8 Cxxx-SKC-S-DWG-Cxxx-50253 C03 SW W10 Cxxx-SKC-S-DWG-Cxxx-50254 C03 SW W11 Cxxx-SKC-S-DWG-Cxxx-50254 C03 SW W12 Cxxx-SKC-S-DWG-Cxxx-50254 C03 SW W13 Cxxx-SKC-S-DWG-Cxxx-50254 C03 SW W15 Cxxx-SKC-S-DWG-Cxxx-50254 C03 SW W16 Cxxx-SKC-S-DWG-Cxxx-50254 C03 The remaining wall dowels have been replaced by bob bars which reflect the intent of the Cxxx design, as captured on Cxxx-__-S-DDD-Cxxx-14322.
| 02SL - Stations (LUL) | Cxxx-NCR-000080 | NCR | P&T Eastbound Tunnel (TS E7) Abandoned Pour |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2015-08-31 | 2015-06-30 10:12 | -62 | 2015-06-15 09:57 | Civil - Civil Engineering General | 50000 |  | Material | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | P&T Eastbound Tunnel (TS E7) Abandoned Pour
| 02SL - Stations (LUL) | Cxxx-NCR-000081 | NCR | P&T Eastbound Tunnel TS E8-abandoned track pour |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2015-08-31 | 2015-07-14 15:54 | -48 | 2015-06-15 10:07 | Civil - Civil Engineering General | 50000 |  | Material | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | P&T Eastbound Tunnel TS E8-abandoned track pour
| 02SL - Stations (LUL) | Cxxx-NCR-000082 | NCR | ETH Level -3 Damaged Beam 2 GL B-C/2-3 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-02-26 | 2016-03-09 14:53 | 12 | 2015-06-11 12:01 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Previous Construction - Other | Completed |  | The end of the beam 2 at GL B-C/2-3 was damaged during excavation works
| 02SL - Stations (LUL) | Cxxx-NCR-000083 | NCR | P&T Eastbound Tunnel, Track Wall E8/9 construction joint |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2015-07-31 | 2015-06-30 10:17 | -31 | 2015-06-15 14:59 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __ drawing Cxxx-SKC-S-DWG-Cxxx-50246 rev C01 shows the locations of the construction joints between walls TW E8 and TW E9. Wall TW E9 was poured on 28/05/15 alongside TW E10 which had already been poured. The stop end between TW E8 and TW E9 had inadvertently been placed approximately 4m into TW E8 meaning this portion of TW E8 was poured together with TW E9. The steel and GFRP reinforcement and the UPE opening box-out incorporated into TW E9 were correct as per the drawings.
| 02SL - Stations (LUL) | Cxxx-NCR-000084 | NCR | Platform Planks concrete quality |  | Crossrail | PDP | BOS - Bond Street Station (West) |  | 2015-07-17 | 2015-07-27 13:54 | 10 | 2015-06-19 15:42 | Civil - Structural Engineering | 500 |  | Manufacturing Defect | Reject | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Several Platform planks have quality issues relating to the quality of concrete at the corners of the units.
| 02SL - Stations (LUL) | Cxxx-NCR-000085 | NCR | P&T Track Slab E7 and E8 Starter Bars |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2015-07-06 | 2015-06-29 09:56 | -7 | 2015-06-22 18:04 | Civil - Civil Engineering General | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During break out of track slabs E7 and E8 (raised in NCR’s 00080 & 00081), wall starters BM22 on drawings Cxxx-SKC-S-DWG-Cxxx-50239/40 were damaged (bent out of shape). Please see attached photographs of damaged bars. E7 has 8no miss-shaped bars over approximately 4m. E8 has 12no miss-shaped bars over approximately 8m, these starter bars are at 150mm centres.
| 02SL - Stations (LUL) | Cxxx-NCR-000086 | NCR | Dowel depths drilled for Westbound Corbels |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2015-07-07 | 2015-07-16 13:20 | 9 | 2015-06-23 12:45 | Structural Engineering - Inserts | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As has been stated in TB 125 P&T Drilling and Fixing: Cxxx-SKC-O1-RGN-Cxxx-50121, no drill depths within the platforms and tunnels should be over 200mm in depth. An allowance of 10mm over the 200mm is acceptable due to the rough finish of the fireproofing allowing ambiguity in where the 200mm is measured from. Following a site inspection of dowel depths in westbound tunnel, it was apparent that there were some dowels over a depth of 210mm. A full comprehensive survey of all non-fixed dowels holes was undertaken and there were a number of dowel depths more than or equal to 215mm, up to a maximum depth of 300mm. The number of dowel over or equal to 215mm is 203no. The survey has been tabulated to incorporate position (co-ordinated) and height, including a sketched location plan. There is no evidence of: a) Waterproofing membrane fragments in the drill cuttings. b) Water ingress in the dowel holes drilled to date.
| 02SL - Stations (LUL) | Cxxx-NCR-000087 | NCR | P&T Commencement of TrackWall East 6 pour prior to finsl sign of by CSJV and CRL |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2015-07-08 | 2015-07-14 13:32 | 6 | 2015-06-24 10:24 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | and CRL engineers had arranged a final pre pour inspection of Trackwall East 6. Upon arriving to the location the wall had already begun pouring without final sign off. In accordance with the Platform and Tunnel Reinforcement Concrete Works ITP (Cxxx-SKC-04-ITP-Cxxx-50009) this is a hold point for
| 02SL - Stations (LUL) | Cxxx-NCR-000088 | NCR | Continuity of Pour to TSE9 not achieved due to insufficient concrete ordered |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2015-07-08 | 2015-07-17 15:43 | 9 | 2015-06-24 17:04 | Structural Engineering - Concrete Member | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | An approximate original quantity of concrete was requested by __ Formwork (80m), with a hold point at (72m). Pouring of TSE9 commenced at 16:40 with the last concrete wagon on site at 21:45. This was a part load of 6m. The incorrect amount was ordered by __ Formwork to finish off the slab, and subsequently the slab has been left at approximately 1.5m3 short of concrete. A stop end was installed (see attached photographs) to ensure a clean finish to the slab, and to ensure a sufficient construction joint can be achieved.
| 02SL - Stations (LUL) | Cxxx-NCR-000089 | NCR | ETH-Section of cast in drainage at Level -4 was installed without an approved ITP |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2015-07-31 | 2015-08-17 09:58 | 17 | 2015-07-01 11:25 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Section of cast in drainage at Level -4 was installed without an approved ITP. Drainage ITP has been accepted prior to completing the required testing of each drainage run
| 02SL - Stations (LUL) | Cxxx-NCR-000090 | NCR | ETH Mainbox Level -3 Lining Wall 1out of position coupler |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2015-08-31 | 2015-07-22 13:12 | -40 | 2015-07-01 15:43 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the installation of Lining wall 1 at Level -3 to -2 (Cxxx-SKC-S-DWG-Cxxx-50190) 1 No. B32 coupler was found out of position. This extends into the cover zone and therefore cannot be installed
| 02SL - Stations (LUL) | Cxxx-NCR-000091 | NCR | P&T (Eastbound Corbels) Dowel Depths |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2015-07-09 | 2015-07-16 13:15 | 7 | 2015-07-03 11:47 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As stated in TB 125 P&T Drilling and Fixing: Cxxx-SKC-O1-RGN-Cxxx-50121, no drill depths within the platforms and tunnels should be over 200mm in depth. An allowance of 10mm over the 200mm is acceptable due to the rough finish of the fireproofing allowing ambiguity in where the 200mm is measured from. Following a site inspection of dowel depths in eastbound tunnel, it was apparent that there were some dowels over a depth of 210mm. A full comprehensive survey of all non-fixed dowels holes was undertaken and there were a number of dowel depths more than or equal to 215mm, up to a maximum depth of 280mm. The number of dowel over or equal to 215mm is 22no. The survey has been tabulated to incorporate position (co-ordinated) and height, including a sketched location plan.There is no evidence of:a)waterproofing membrane fragments in the drill cuttings. b)water ingress in the dowel holes drilled to date.
| 02SL - Stations (LUL) | Cxxx-NCR-000092 | NCR | P&T (Westbound Corbels) reinforcement has occurred in positions where box outs are located |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2015-08-01 | 2015-07-28 17:35 | -4 | 2015-07-03 12:06 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following a site inspection, drilling + installation of reinforcement has occurred in positions where box outs are located on the builders work drawings. This is in two locations in the eastbound tunnel. These issues arose due operative confusion with the setting out. Please see attached images titled “Boxout A, B, C”, and location sketch “68163 + 68162”
| 02SL - Stations (LUL) | Cxxx-NCR-000093 | NCR | P&T (Westbound Corbels) Tunnel Dowels-Drilling out of Resin |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2015-07-09 | 2015-07-16 13:18 | 7 | 2015-07-03 11:57 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | Following a site inspection, drilling + installation of reinforcement has occurred but in wrong locations. These bars have then been cut insitu leaving the reinforcement exposed close to the SCL. This affects an approximate 1.5m section to the west of CP9 as shown on the location plan attached. Redrilling of holes has then taken place very close/adjacent to these dowels, and in some circumstances, a percentage of the resin has been removed in the drilling process. These issues arose due to operative confusion with the setting out. Please see attached images titled “Dowel A, B, C, D”, and location sketch “68164”
| 02SL - Stations (LUL) | Cxxx-NCR-000094 | NCR | P&T (Eastbound SW 12/13) short concrete pour |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2015-07-31 | 2015-07-14 10:02 | -17 | 2015-07-06 11:40 | Civil - Civil Engineering General | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Concrete pour to SW E12/13 on Friday 26th June was approx 0.6m3 short. The wall has since been recubed and it has been confirmed that the correct quantity of concrete was ordered. An investigation is taking place looking into the possibility of receiving an incorrect amount of concrete from the supplier despite delivery tickets stating this is not the case.
| 02SL - Stations (LUL) | Cxxx-NCR-000095 | NCR | P&T TW W17 starter bar incorrectly installed |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2015-07-20 | 2015-07-20 17:13 | 0 | 2015-07-06 11:47 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A starter bar from TW W17 hasn’t been installed in the correct position, meaning the starter bars are not complete and are not at 150mm centres throughout as per design. See attached image “TW W17 – showing the area in question.
| 02SL - Stations (LUL) | Cxxx-NCR-000096 | NCR | ETH - Lining Wall - Level -2 to -3 Wall 9 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2015-07-20 | 2015-07-22 13:14 | 2 | 2015-07-06 16:10 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Drawing 50094 Rev X01 shows 6No. BM-E110 couplers in the corner between walls 8 and 9. These were not installed as part of the slab pour. The corresponding BM-E103 on dwg 50186 Rev C01 has therefore not been installed (although BM21 has been installed). Since this section of wall has been detailed to fill the void in the corner between the piles, it is assumed that this reinforcement is not structural.
| 02SL - Stations (LUL) | Cxxx-NCR-000097 | NCR | ETH Mainbox Level -3 and Level -2,incorrect eazistrip installed |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2015-12-01 | 2015-12-08 12:39 | 7 | 2015-07-06 16:16 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | It has been found onsite that at level -2 the incorrect continuity strip has been installed for the upstand in the highlighted area. Cxxx-SKC-S-DWG-Cxxx-50047 details a type CS Eazistrip with a closed U and B12@300 spacing. The Eazistrip which has been installed is a Type S2 with B10@200 spacing. This does not have a closed U finish and extends 500mm from slab level, with the upstand only 250mm high.
| 02SL - Stations (LUL) | Cxxx-NCR-000098 | NCR | ETH-Incorrect Eazistrip Installed at Level -3 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2015-12-01 | 2015-12-14 09:19 | 13 | 2015-07-08 12:08 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | It has been found onsite that at level -3 the incorrect continuity strip has been installed for the upstand in the highlighted area (see attached Cxxx-SKC-S-DWG-Cxxx-50070 Level -3 Location). The RC drawings detail a type CS Eazistrip with a closed U and B12@300 spacing. The Eazistrip which has been installed is a Type S2 with B10@200 spacing. This does not have a closed U and extends 500mm from slab level, with the upstand only 250mm high. Cxxx-SKC-S-DWG-Cxxx-50092, Cxxx-SKC-S-DWG-Cxxx-50087, Cxxx-SKC-S-DWG-Cxxx-50085, Cxxx-SKC-S-DWG-Cxxx-50081, Cxxx-SKC-S-DWG-Cxxx-50077, Cxxx-SKC-S-DWG-Cxxx-50075, Cxxx-SKC-S-DWG-Cxxx-50073
| 02SL - Stations (LUL) | Cxxx-NCR-000099 | NCR | P&T Eastbound - Reinforcement to track upstand |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2015-08-31 | 2015-09-29 11:58 | 29 | 2015-08-27 12:44 | Civil - Civil Engineering General | 2000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Track slab upstand has varying amount of cover due to additional reinforcement being installed as per FCD-113. Due to position of SCL, some of these additional reinforcement bars have less than 25mm cover. If this is the case then they need to be removed, ensuring they are cut off 50mm below SSL. This will then be patch repaired using conbextra grout. (See note 11 on TB071 – Conc Repairs). See attached location plan “EB Upstand Reinforcement Mark Up” showing the area in question See attached image “Track Slab Upstand 001” showing additional reinforcement protruding on concrete cover
| 02SL - Stations (LUL) | Cxxx-NCR-000100 | NCR | P&T Concrete Short PS E4 |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2015-08-31 | 2015-11-16 11:14 | 77 | 2015-07-30 18:12 | Civil - Civil Engineering General | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the pouring of Platfrom Slab E4 there was a shortage of concrete around one of the PES base plates.
| 02SL - Stations (LUL) | Cxxx-NCR-000101 | NCR | ETH - Issue 336 - Missing eazi-strip for Level -2 upstand |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-01-29 | 2015-12-08 14:25 | -52 | 2015-07-31 12:04 | Civil - Civil Engineering General | 2000 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | No Easi-strip has been installed in the return section of upstand at L-2 (see attached marked up GA for location).
| 02SL - Stations (LUL) | Cxxx-NCR-000102 | NCR | B25 threaded side bars from Slab 2 to Slab 3 not positioned as required / missing |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2015-08-18 | 2015-08-17 11:35 | -1 | 2015-08-04 17:11 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Drawings Cxxx-SKC-S-DWG-Cxxx-50146 and 50149 show B25 threaded side bars to be installed in Slab 3. These are meant to be threaded into coupled bars poured as part of Slab 2 (reference drawings Cxxx-SKC-S-DWG-Cxxx-50140 and 50142). However, the coupled bars have either not been installed in the correct location or are not visible. For more detailed information please refer to the marked up versions of the aforementioned drawings attached. REFERENCE DOCUMENT: Cxxx-SKC-S-DWG-Cxxx-50146 Rev C05 SB Mark-up Cxxx-SKC-S-DWG-Cxxx-50149 Rev P05 SB Mark-up Cxxx-SKC-S-DWG-Cxxx-50140 Rev C07 SB Mark-up Cxxx-SKC-S-DWG-Cxxx-50142 Rev C06 SB Mark-up
| 02SL - Stations (LUL) | Cxxx-NCR-000103 | NCR | P&T Platform Slab E4 Edging |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2016-04-22 | 2016-04-07 09:59 | -15 | 2015-08-05 11:02 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Platform Slab E4 has been constructed with an obvious curve where the movement joint is to be installed. There is an overhang of approx 5mm from the service wall. This has potential to cause damage to the screed layer and/or the finished floor due to the repositioning of the movement joint on the nib of the slab.
| 02SL - Stations (LUL) | Cxxx-NCR-000104 | NCR | ETH - Cutting of Starter Bars at L-4 to Facilitate Prop Installation |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2017-12-01 | 2018-05-21 15:58 | 171 | 2015-08-12 08:26 | Civil - Civil Engineering General | 0 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Drawing Cxxx-SKC-S-DWG-Cxxx-50152 Rev C04 details B20 starter bars (BM-E110, Section 3-3) at Gridline B/3. A temporary prop is to be installed with an end plate sitting flush with the top of the slab. 4No. of these starter bars clash with the temporary prop end plate and therefore need to be cut flush with the L-4 slab level. See marked up version of drawing 50152 attached for clarity.
| 02SL - Stations (LUL) | Cxxx-NCR-000105 | NCR | ETH – Level -4 Slab Pour 3, between GL3&4 and GL B+1 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-03-31 | 2018-06-04 09:29 | 65 | 2015-08-19 13:35 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Drawing Cxxx-SKC-S-DWG-Cxxx-50144 C04 details 21 No each BM E104 and BM E105 installed, to form a coupled connection to the sloped slab constructed at a later date. The number of both BM’s have incorrectly been specified, as 21No bars at 200mm spacing does not allow for the bars to be installed for the full width as specified on the reinforcement drawing. See marked up of drawing Cxxx-SKC-S-DWG-Cxxx-50144 C04
| 02SL - Stations (LUL) | Cxxx-NCR-000106 | NCR | P&Tusing a material with no approved MCR |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2015-09-03 | 2015-09-03 14:36 | 0 | 2015-08-20 14:56 | Civil - Civil Engineering General | 3000 |  | Material | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Installation of non approved drainage pipe in P&T base slab W1 &W12. was aware of the situation and the pour was on hold untill MCR was approved.
| 02SL - Stations (LUL) | Cxxx-NCR-000107 | NCR | P&Tunapproved drawings being used on site to install the drainage in the Cross passages |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2015-10-31 | 2015-09-30 16:10 | -31 | 2015-09-02 08:32 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | Currently are working to drawings that have not officially been issued for approval in the P&T cross passages
| 02SL - Stations (LUL) | Cxxx-NCR-000108 | NCR | ETH-125mm cast iron drainage sleeves cast into the slab at Level -2 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-05-27 | 2016-05-27 15:19 | 0 | 2015-08-25 08:58 | Civil - Civil Engineering General | 500 |  | Planning | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 125mm cast iron drainage sleeves cast into the slab at Level -2 have been surveyed and it is deemed that 3no. sleeves will be “inside” the upstand when the 100mm x 100mm grating is in place. See marked up drawing “Cxxx-__-S-DDL-Cxxx-52120 Rev C06 – upstands Rev 02 – WO 5” for further information.
| 02SL - Stations (LUL) | Cxxx-NCR-000109 | NCR | P&T Track Slab E3, 23 No B25 coupler bars |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2015-10-31 | 2015-11-27 12:31 | 27 | 2015-09-02 08:30 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | When constructing Track Slab E3, 23 No B25 coupler bars were introduced at the stop end with E2 to receive B25 bars from E2 at the lower level of the floating track slab. The couplers were installed too high so that 3 No couplers clash with the drainage channel in the TS E2 slab. See attached photo.
| 02SL - Stations (LUL) | Cxxx-NCR-000110 | NCR | XR14 - Sensor |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-05-27 | 2016-05-25 15:01 | -2 | 2015-09-09 10:26 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Equipment Breakdown | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | XR14 The sensors in this instrument have gradually been failing. The last sensor has now failed. Given that the instrument is outside of the box, no significant ground movement is occurring, and the dig in the vicinity of the instrument is almost complete to base slab, we would propose that we do not attempt to repair it.
| 02SL - Stations (LUL) | Cxxx-NCR-000111 | NCR | Piezometers 01 and 02 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-05-27 | 2016-05-25 15:02 | -2 | 2015-09-09 10:26 | Geotechnical Engineering - Geotechnical Monitoring | 500 |  | Equipment Breakdown | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Piezometers 01 and 02 within the box have been cut down during this dig. They were scheduled for repair the week starting the 23rd August. We have attempted repair several times now, but have yet to achieve success as we have not found the issue. Therefore there will be slightly more missing data than is normal for a dig. As the data has historically been stable showing minor fluctuations, we do not consider this lack of data significant.
| 02SL - Stations (LUL) | Cxxx-NCR-000112 | NCR | P&T not working to the approved TB/MS during the installation of the PES top bracket |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2015-09-23 | 2015-10-06 09:45 | 13 | 2015-09-09 10:29 | Civil - Civil Engineering General | 500 |  | System Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not trained for the work being performed | Completed |  | P&T not working to the approved TB/MS during the installation of the PES top bracket
| 02SL - Stations (LUL) | Cxxx-NCR-000113 | NCR | P&T- Error had occurred in the PES layout model for the Westbound PES |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2015-09-30 | 2015-10-07 17:33 | 7 | 2015-09-16 10:29 | Mechanical - Platform Edge Doors | 25000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | An error had occurred in the PES layout model for the Westbound PES. All on-site checks were being carried out as required by the ITP, and fixings/brackets were showing an accuracy of setting out and installation of within 1mm. Due to the acceleration to be on site all setting out was being set to the 3D model prior to GA drawings being completed and reviewed. On further checking of setting out drawings released part way through, a discrepancy was picked up by __ following release of a __ layout drawing. A 175mm error in chainage was observed in the setting out. This was due to human error in the Centre lines of grids. The model had been snapped to the centre of a movement joint rather than the centre of the hanger on the Westbound tunnel. This error is for 24 sets of holes currently drilled for the Westbound Head Bracket (96No holes in total).
| 02SL - Stations (LUL) | Cxxx-NCR-000114 | NCR | 6No. Couplers for Lining Wall 7 at L-4 Damaged or at Incorrect Spacing |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2015-09-25 | 2015-09-30 16:07 | 5 | 2015-09-11 15:26 | Civil - Civil Engineering General | 3000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 6No. existing couplers for Lining Wall 7 at L-4 (north of Waling Beam 3) are either damaged or at the incorrect spacing. __ Formwork have drilled and installed 6no. 32mm bars in place of the couplers. These bars were drilled at 300mm embedment. Minimum embedment for a 32mm bar is 420mm. The location of the B32 bars is as follows: 1. 3.5m south of the stop-end in Pour 1 (Wall 7) 2. 4.3m south of the stop-end in Pour 1 (Wall 7) 3. 5.4m south of the stop-end in Pour 1 (Wall 7) 4. 5.6m south of the stop-end in Pour 1 (Wall 7) 5. 170mm south of Wall 9 kicker in Pour 2 (Wall 7) 6. 570mm south of Wall 9 kicker in Pour 2 (Wall 7) This was carried out without prior approval by . The Contractor has since discussed this issue with Cxxx and a solution has been agreed.
| 02SL - Stations (LUL) | Cxxx-NCR-000115 | NCR | __ Channels at L-4 Slab |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-04-01 | 2015-11-16 11:16 | -137 | 2015-09-14 09:51 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | Cast in service channels (__ channels) have been installed within the soffit of the level -4 slab in an area not detailed on the IFC builderswork drawing Cxxx-SKC-M-DDA-Cxxx-69140 Rev P06. The installation of the channels commenced to drawing revision P06.2, which later became superseded by Revision P06. The IFC version removed the requirement for channels to be installed on GL E/1-2. Due to the fact these had already been installed and the bottom mat of the steel had been fixed, it was decided to leave the channels in place. A marked up version of drawing Cxxx-SKC-M-DDA-Cxxx-69140 Rev P06 has been attached to this NCR to illustrate the location of the additional channels.
| 02SL - Stations (LUL) | Cxxx-NCR-000116 | NCR | P&T Cross Passage 5 – Structural Slab Topping |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2015-11-30 | 2015-11-09 10:29 | -21 | 2015-10-06 10:30 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Structural slab topping at Cross Passage 5 was cast on 10th September. The pour was completed and finished off using easyfloat, with an operative returning later in the shift to refinish the slab due to plastic settlement around the cast in mesh. This could not be rectified and in turn has left the mesh “pattern” throughout the entirety of the slab. See attached photo showing the slab post pour.
| 02SL - Stations (LUL) | Cxxx-NCR-000117 | NCR | Finish to Track Slab W1 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2015-11-30 | 2015-11-18 17:29 | -12 | 2015-10-06 10:44 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Track Slab W1 was cast on 2nd September. The pour was completed and finished off using easyfloat. Plastic settlement has occurred around the reinforcement leaving the “squared pattern” throughout the surface of the slab. See attached photo showing the slab post pour.
| 02SL - Stations (LUL) | Cxxx-NCR-000118 | NCR | P&T __ Failed __ Pull-out Test |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2015-10-30 | 2015-11-20 12:35 | 21 | 2015-09-21 16:36 | Civil - Civil Engineering General | 6000 |  | Material | Repair | 3 (3-6k) | Complete | Previous Construction - Problems based on previous construction errors | Completed |  | __ operatives have undertaken several pull-out tests on the top bracket __ bolts as per. Cxxx-ATK-S-DDD-CR001_Z-43053 (C03). To date, over 40 tests have been carried out. One of these tests failed in the Eastbound tunnel prior to reaching the 17kN required. The failed test occurs at Ch3871.231 drill hole N°4 (see sketch EB3871 Pull Test Check Sheet for a diagram of the area - in the Notes section. Operatives were using the procedure outlined in TB 230: Installing Head Brackets - Setting out of Lines, Levels, Drillings and Installing (Cxxx-SKC-O1-RGN-Cxxx-50222) and Cxxx - ITP: P&T Installation of top brackets and side brackets (LW) (Cxxx-SKC-O4-ITP-Cxxx-50025).
| 02SL - Stations (LUL) | Cxxx-NCR-000119 | NCR | P&T BS W12 Drainage Perforation |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-05-27 | 2016-04-27 13:49 | -30 | 2015-10-06 10:55 | Civil - Civil Engineering General | 3000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | 100mm diameter cast iron pipe penetrated by an operative drilling through the concrete at location Base Slab W12. Hole depth is 200mm, and has damaged the pipe is to be CCTV surveyed prior to any action being undertaken. See attached location plan and photo of drilled hole.
| 02SL - Stations (LUL) | Cxxx-NCR-000120 | NCR | Platforms and Tunnels __ Westbound Tunnel Setting Out |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-01-29 | 2016-02-06 12:58 | 8 | 2015-09-29 12:22 | Civil - Civil Engineering General | 10000 |  | Incorrect Installation | Use As-Is | 2 (6-60k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | have become aware of a setting out error that has affected the installation of the PES structure. Cxxx-OVE-R4-DDA-CR001_Z-11014 C02 contains an error of 21mm between the chainage markers on the drawings and the SOP chainages given (in the Westbound tunnel only). See Cxxx_SK_P&T_064 [Rev 1]. Through the RFI process (Cxxx-RFI-001287 & Cxxx-RFI-001449) several concerns over the SOP coordination were addressed and related drawings were re-issued for clarification. For instance, the installation of the PES Bolts cast-into the platform slab as per the drawings listed below are correct: - Cxxx-SKC-C-XSK-Cxxx-50039 C01 - Cxxx-SKC-C-XSK-Cxxx-50040 C01 - Cxxx-SKC-C-XSK-Cxxx-50041 C01 - Cxxx-SKC-C-XSK-Cxxx-50042 C01 However, it is apparent that the Cxxx surveying track chainage did not reflect this clarification. The PES __ top brackets were both installed and checked against this Cxxx surveying track chainage and therefore the error was not identified. This means that there is a 21mm relative error between the top brackets installed in the westbound tunnel and the PES post bolts as installed in the platform slab.
| 02SL - Stations (LUL) | Cxxx-NCR-000121 | NCR | ETH- Level -4 Lining Wall 1,missing starter bar |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2015-10-15 | 2015-11-30 10:48 | 46 | 2015-10-01 15:48 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | There are missing far face B32 coupled starters for Lining Wall 1 in the Level -4 slab. In addition there are various locations where spacing between far face coupled starters exceed 100mm centres specified in the design drawings.
| 02SL - Stations (LUL) | Cxxx-NCR-000124 | NCR | ETH Main Box Upstands at L-2 (Lining Wall 9) |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2015-12-01 | 2016-02-09 14:55 | 70 | 2015-10-09 14:46 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | Please see attached sketch, location diagram and photo of upstands at Level -2. Front face of the upstand has too much cover (up to 47mm) and the back face doesn’t have enough cover (approx. 8mm). The required cover is 25mm (+/- 10mm). Please note the exact same issue has occurred on Level -4. Cxxx-__-S-DDD-Cxxx-70000, Cxxx-__-S-DDL-Cxxx-52120 Mark-up, Cxxx-__-S-DDL-Cxxx-52140 Mark-up
| 02SL - Stations (LUL) | Cxxx-NCR-000125 | NCR | Late issue of ITP's |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2015-11-05 | 2015-11-09 10:18 | 4 | 2015-10-22 16:56 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | The two ITP's relating to the level -5 raft slab works to the Eastern ticket hall were not submit to Crossrail for review 4 weeks prior to works starting on site. Also, works commenced on site prior to the ITP's being accepted code 1 or 2. The ITP's are: 1. ITP: ETH Construction of Raft Slab Part 1 (Geothermal, Earthing and Redundant Tube Grouting Works) 2. ITP: ETH Construction of Raft Slab Part 2 (R.C and Drainage) This is not in line with the Works Information. The Contractor are currently carrying out these works at risk. This was discussed at the Quality Focus Meeting on the 8th October.
| 02SL - Stations (LUL) | Cxxx-NCR-000126 | NCR | Un-Approved Concrete Mix Incorporated into Permanent Works |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2015-12-18 | 2016-01-12 14:49 | 25 | 2015-11-03 15:32 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Due to the breakdown of the Kings Cross __ Plant (on 2/11/15 at approximately 18:00), and the unavailability of other __ plants (for which concrete mix MCRs have been submitted and accepted), the decision was made to continue supply from __'s plant at Park Royal. There are no MCRs covering mixes supplied by __ at Park Royal.
| 02SL - Stations (LUL) | Cxxx-NCR-000127 | NCR | P&T TW E21 - Finish |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-01-22 | 2016-01-22 16:18 | 0 | 2015-11-24 18:20 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | Face of Track Wall E21 has exposed concrete spacer blocks and a poorly finished face as per images “TW E21 – A” and “TW E21 – B” (attached).
| 02SL - Stations (LUL) | Cxxx-NCR-000128 | NCR | P&T Missing __s in SW W25c |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-02-26 | 2016-02-05 16:37 | -21 | 2015-11-23 18:09 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | Following check of __ requirements prior to pouring Service Wall W25c, it was stated by MEP Design Manager that the __s are no longer required, therefore they were not installed by the site team. As these __s are still shown on the drawing, this NCR is against procedure.
| 02SL - Stations (LUL) | Cxxx-NCR-000129 | NCR | P&T Missing Sleeve through Corbel W2 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-02-26 | 2016-02-11 14:44 | -15 | 2015-11-23 18:15 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Not Defined | Completed |  | Following check of CCTV sleeve requirements prior to pouring corbel W2, it was stated by MEP Design Manager that the sleeve is no longer required, therefore this was not installed by the site team. As this sleeve is still show on the drawing, this NCR is against procedure.
| 02SL - Stations (LUL) | Cxxx-NCR-000130 | NCR | ETH Level -5 InBox Instrument Extensometer MX3 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-05-27 | 2016-05-25 15:04 | -2 | 2015-11-24 12:15 | Surveying - Instrumentation and Monitoring | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | The instrument was boxed out to retain it ahead of the slab pour. Unfortunately concrete penetrated the boxing and flowed into the open extensometer pipe. We estimate that there is a minimum of 300mm below the soffit of the slab, but it is likely that as the concrete was being pumped it will have significantly penetrated the pipe.
| 02SL - Stations (LUL) | Cxxx-NCR-000131 | NCR | ETH Duct/draw pit works not covered by ITP |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-01-22 | 2016-01-13 09:55 | -9 | 2015-11-26 08:47 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Neither ITP for the ETH Level -5 Raft Slab works covers the duct/draw pit works currently ongoing.
| 02SL - Stations (LUL) | Cxxx-NCR-000132 | NCR | P&T PES Truss Cleats Missing |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-04-01 | 2016-04-07 14:26 | 6 | 2015-11-30 17:56 | Civil - Civil Engineering General | 1000 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | 2 no. cleats missing off assembly for the cover plates (Part number M200). See attached photo.
| 02SL - Stations (LUL) | Cxxx-NCR-000133 | NCR | Availability of Construction drawings on site |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2016-01-25 | 2016-01-15 11:49 | -10 | 2015-12-03 14:31 | Electrical - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | No sample drawings with geothermal system installation and setting out drawings for sleeves and ducts were provided by the Contractor within the given 3 day post surveillance period. Therefore, an NCR ref. no. Cxxx-NCR-000133 has been raised on the grounds that no evidence has been provided that all Construction drawings are available on site as required by WIv2B part 13.3.6.1 which states that ‘The Contractor shall keep a full set of the latest Issued for Construction (IFC) drawings, associated data and specifications on Site’. For details refer to surveillance report Cxxx-XRL-O4-RGN-CR001-50009.
| 02SL - Stations (LUL) | Cxxx-NCR-000134 | NCR | Failure to provide delivery traceability for materials. |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2016-01-25 | 2016-01-13 17:20 | -12 | 2015-12-03 14:40 | Materials - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The Contractor was asked to provide evidence that Clause 5.2.5.3 of their Procurement Procedures (Cxxx-SKC-V3-GDP-Cxxx-50001) had been satisfied for one of the systems looked at during the surveillance. At the time of writing this report evidence was not submitted within the given timescale and so it has not been possible to verify the traceability of the delivery process for any of the chosen systems. For further details refer to surveillance report ref. no. Cxxx-XRL-O4-RGN-CR001-50009.
| 02SL - Stations (LUL) | Cxxx-NCR-000135 | NCR | ETH Level -5 Missing reinforcement in Wall 2 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-04-01 | 2016-04-08 16:15 | 7 | 2015-12-10 12:26 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There are missing centre face bars, BM E98, detailed on drawing 50394 Rev C03. Please see attached marked up drawing for clarity of location (Cxxx-SKC-S-DWG-Cxxx-50394-C03 SB Mark-up).
| 02SL - Stations (LUL) | Cxxx-NCR-000136 | NCR | WTH - Vent Shaft - Southern Elevation Embedment of Cast In __ Channels |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-05-31 | 2018-03-16 15:24 | -76 | 2015-12-21 16:46 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There is a certain number of the cast in channels within the vent shaft that have been cast back from the face of the wall. These are on all walls at various levels and in some areas are up to 20mm back from the face of the wall.
| 02SL - Stations (LUL) | Cxxx-NCR-000137 | NCR | WTH - Vent Shaft - Cover Issues |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2017-05-31 | 2017-05-10 15:51 | -21 | 2015-12-21 16:36 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Certain areas of the vent shaft have reduced or increased cover to the reinforcement in the walls. To determine the extent of the problem a cover meter survey will be undertaken in the areas highlighted in post pour inspections and __.
| 02SL - Stations (LUL) | Cxxx-NCR-000138 | NCR | ETH L-5 ETH L-5 IW 67 Starter bars detailed incorrectly |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-09-30 | 2016-10-05 11:23 | 5 | 2016-03-03 17:19 | Civil - Civil Engineering General | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Drawing 50580 details starter bars to be installed for Internal Walls in L-5 slabs. For IW 67, Eazistrip was detailed (see marked up version of drawing 50580 for clarity). However, the intent drawing 72710 states that the vertical reinforcement should be B20s @ 250c/c.
| 02SL - Stations (LUL) | Cxxx-NCR-000139 | NCR | WTH - Vent Shaft - Missing Couplers to the Level +1 Slab |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2017-08-27 | 2017-09-28 08:58 | 32 | 2015-12-21 17:03 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There is a connection detail to RC slab at level +1 on the East Elevation to connect into the level +1 slab. Both couplers (BM 26- B16), pull out bar type 1 and 3 were missed out of the pour. Please see drawings attached highlighting the bars.
| 02SL - Stations (LUL) | Cxxx-NCR-000140 | NCR | WTH - Vent Shaft - Northern Elevation Missing __s |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-03-31 | 2018-02-12 13:50 | -47 | 2015-12-21 17:08 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 2 pairs of halfen channels were not installed on the Northern Elevation at level 135.710. These halfen channels are for the permanent cladding connection. Please see attached drawing for location.
| 02SL - Stations (LUL) | Cxxx-NCR-000141 | NCR | WTH - Vent Shaft - Position of Cast In __ Channels |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-05-31 | 2018-03-19 14:49 | -73 | 2015-12-23 14:17 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There is a certain number of the cast in channels on the vent shaft that have been installed out of alignment from the design position. Some channels were moved to avoid clashes with temporary works for openings.
| 02SL - Stations (LUL) | Cxxx-NCR-000143 | NCR | WTH - Vent Shaft - Step In Kicker |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2017-06-30 | 2017-05-22 10:58 | -39 | 2015-12-23 15:01 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There is a step in the Southern vent shaft wall at level 120.830. The step is approx. 20mm deep and runs along the length of the southern wall. The wall may have decreased by approx. 20mm in size and to be 280mm thick or may have stepped across. Please see as built and photo attached.
| 02SL - Stations (LUL) | Cxxx-NCR-000144 | NCR | P&T Eastbound Base Slab, NE Corner, WTH Ducts & Kicker |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-03-25 | 2016-04-05 09:54 | 11 | 2016-01-13 09:53 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Ducts and a kicker for a door have been missed from the Base Slab pour situated in the NE corner of the WTH. These are shown on marked up drawing Cxxx-SKC-S-DWG-Cxxx-50243 C09 (attached).
| 02SL - Stations (LUL) | Cxxx-NCR-000145 | NCR | ETH Level -5 to -4 Slab NE corner Wall starters |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-02-19 | 2016-02-18 13:33 | -1 | 2016-01-25 12:21 | Civil - Civil Engineering General | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Previous Construction - Improper As Built | Completed |  | 7 No. B32 E121 Couplers NF and 2 No. B32 E119 FF missing within soffit of slab. Please see attached photo showing location and area broken back to expose any couplers and it is evident that there are no couplers in this area. These couplers are required to connect to the Lining wall 7 threaded bars detailed in Cxxx-SKC-S-DWG-Cxxx-50583.
| 02SL - Stations (LUL) | Cxxx-NCR-000146 | NCR | P&T SW W33 - Starter Bars |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-02-26 | 2016-03-14 12:22 | 17 | 2016-01-27 13:41 | Civil - Civil Engineering General | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | The northern edge/face of the platform slab supporting SW W33 is 40mm north of its design position. This makes the forming void/duct 1960mm x 2000mm instead of the 2000mm x 2000mm specified in the design. The starter bars for SW W33 are set to allow for 200mm wall flush with the ‘incorrect’ inside edge.
| 02SL - Stations (LUL) | Cxxx-NCR-000147 | NCR | ETH Cast in Plunge Column Slab Detail |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-10-31 | 2016-10-28 10:02 | -3 | 2016-01-25 08:57 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Detail 2 shown on drawing Cxxx-__-S-DDD-Cxxx-58730 indicates a recess to be formed in the permanent slab around a cast in column. It is evident that this detail hasn’t been followed on site. As a result, upon column removal, the contractor will remove the column as close to structural slab and soffit levels as possible (20mm). The affected columns are as follows: Level -2: P10p, P14p, P16t, P18p & P21p Level -3: P12t, P14p, P15t, P16t, P19t, P20t, P21p & P23t
| 02SL - Stations (LUL) | Cxxx-NCR-000149 | NCR | ETH Vandex Waterproofing Membrane Location |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-02-26 | 2016-02-25 14:04 | -1 | 2016-01-27 10:28 | Civil - Civil Engineering General | 2500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Vandex membrane installed at back of piles rather than position shown on drawing Cxxx-MMD-C4-DDL-Cxxx_Z-00750 Rev C05
| 02SL - Stations (LUL) | Cxxx-NCR-000152 | NCR | ETH Damaged Geothermal Pipe Level -5 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-02-26 | 2016-02-11 16:56 | -15 | 2016-02-02 08:51 | Civil - Civil Engineering General | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | During prop preparation for a subsequent concrete pour, a geothermal pipe cast into Level -5 Slab 6 was inadvertently drilled through.
| 02SL - Stations (LUL) | Cxxx-NCR-000153 | NCR | WTH Vent Shaft OSD Plates Level +7 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2017-02-24 | 2017-03-30 08:56 | 34 | 2016-02-02 13:33 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | OSD Plates on L+7 of WTH Vent Shaft have been installed in a different position to that as designed due to a clash with the Slipform Climbing Tubes. See attached drawing “Cxxx-__-S-DDL-Cxxx-11032” for the actual as built positions (plates marked in red and dimensions in green). Please Note: This was originally raised as an RFI (-RFI-000518) but were told to raise as an NCR post event. CORRECTION: RFI Number is Cxxx-RFI-002073
| 02SL - Stations (LUL) | Cxxx-NCR-000154 | NCR | WTH Vent Shaft Construction Joint |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2017-04-21 | 2017-04-07 14:42 | -14 | 2016-02-06 12:00 | Civil - Civil Engineering General | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | The construction joint at level 147.500 was not properly prepared prior to concreting. It was spotted on the internal side of the wall in a number of places. It was noted that the external side of the wall was in much better shape. The defect shows honeycombing in a number of positions.
| 02SL - Stations (LUL) | Cxxx-NCR-000155 | NCR | WTH Vent Shaft Surface Finish |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2017-05-30 | 2018-06-04 09:52 | 370 | 2016-02-06 12:24 | Civil - Civil Engineering General | 2500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | There are various places on the WTH Vent Shaft where honeycombing occurs between levels 148.100 and 148.750.
| 02SL - Stations (LUL) | Cxxx-NCR-000156 | NCR | Concrete poured without pre pour inspection |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-02-26 | 2016-02-26 16:02 | 0 | 2016-02-06 12:25 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Concrete pour was started without a pre pour inspection being carried out, and the pour not being signed off.
| 02SL - Stations (LUL) | Cxxx-NCR-000157 | NCR | Level -5 Missing B32 Lining Wall Starters in Slab 8 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-02-25 | 2016-02-26 10:47 | 1 | 2016-02-04 10:53 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Works not completed as shown on IFC Drawing. 36 No. E109 couplers were not installed, detailed on Cxxx-SKC-S-DWG-Cxxx-50394 C03 please see attached marked up drawing.
| 02SL - Stations (LUL) | Cxxx-NCR-000158 | NCR | P&T PS W16 GFRP Bars Exposed |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-03-25 | 2016-02-10 15:56 | -44 | 2016-02-06 12:43 | Civil - Civil Engineering General | 0 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Concrete to PSW16 is approx 20mm short in an approx. 10m section at the far west end of PS W16. This left the tops of the GFRP bars exposed. A cover survey has been undertaken on the area and the lowest value was 26mm. Attached are photos of the cover meter in various areas on the platform slab, as well as a survey of both the top of the concrete and top of the GFRP bars. The level used is +98.150.
| 02SL - Stations (LUL) | Cxxx-NCR-000159 | NCR | ETH WB UPE Duct End Wall |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-02-26 | 2016-03-14 10:33 | 17 | 2016-02-06 12:54 | Civil - Civil Engineering General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | A small area of a permanent works wall was incorrectly broken out as part of breakout works of an adjacent slab for PMI 702. The steel remains undamaged, however the replacement/repair of wall concrete is required.
| 02SL - Stations (LUL) | Cxxx-NCR-000160 | NCR | Track Slab W2 Finished Surface |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-03-25 | 2016-02-12 11:10 | -42 | 2016-02-10 15:39 | Civil - Civil Engineering General | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Track slab has shallow but frequent damage to its finished surface where the overlaying temporary ramp was located.
| 02SL - Stations (LUL) | Cxxx-NCR-000161 | NCR | Cxxx non load bearing wall WTH level -5, low cover to reinforcement |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2016-07-08 | 2016-07-08 15:24 | 0 | 2016-02-12 13:16 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A non load bearing wall cast by Cxxxin the WTH level -5, along the route of Cxxx Wall 1-2 / C-L between gridlines G to H has a location at the top level, where six number 10mm diameter, 400mm long bars which are part of the pull out system bars have cover of approximately 10mm. The attached pictures demonstrate the situation.
| 02SL - Stations (LUL) | Cxxx-NCR-000162 | NCR | WTH Surface Finish to Level -5 Walls 3-4 / D-G, 3-4 / F-G, 3-4 / A-D |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-05-27 | 2016-04-27 13:51 | -30 | 2016-02-17 09:24 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Secondary tie bar holes placed in lower section pour at a height incompatible with temporary works design (Cxxx-SKC-C-CER-Cxxx-50073). For secondary lift, tie holes were required 200mm higher to allow 2.7M shutters to be utilised at full height.
| 02SL - Stations (LUL) | Cxxx-NCR-000163 | NCR | WTH Step in Construction Joint at Wall 1-2 / C-D North-West Face |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-05-27 | 2016-04-27 13:52 | -30 | 2016-02-17 09:30 | Civil - Civil Engineering General | 10000 |  | Workmanship | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Bow / abrupt change in surface finish between lower and upper pour of non-load bearing wall 1-2/C-L north-west face. The change of continuous surfaces (as measured on the nominal surface of the finished face) at construction joint is greater than 5 mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000164 | NCR | ETH Level -5 Lining Wall 7 Concrete Cover |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-04-01 | 2016-04-04 13:33 | 3 | 2016-02-16 09:07 | Civil - Civil Engineering General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 60mm concrete cover was required to be achieved for Lining Wall 7 as instructed within PMI’s 886, 915, 931, 961. This concrete cover to reinforcement has not been achieved to a portion of the lining wall.
| 02SL - Stations (LUL) | Cxxx-NCR-000165 | NCR | ETH Additional Construction Joint in Level -3 Lift 1 Shaft |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-03-04 | 2016-03-17 16:34 | 13 | 2016-02-16 09:15 | Civil - Civil Engineering General | 2000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | The concrete pour for the second lift of the Lift Shaft Walls at Level -3 was not cubed up correctly. This has resulted in the walls being left between 50-200mm low from the soffit.
| 02SL - Stations (LUL) | Cxxx-NCR-000166 | NCR | No cubes were taken for the mass fill concrete poured in Cross Passage 5 (CP5) |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-06-12 | 2016-06-02 15:32 | -10 | 2016-02-16 11:04 | Civil - Civil Engineering General | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | 150m3 of Mass fill (C8/10) concrete poured on 08/09/2015. KF10 Table-2 in the Cxxx Specification detailed below indicates rate of sampling for each type of concrete – where this concrete is deemed to fall into the category of “other” concrete, the rate of sampling is stated: 1 set of cubes for every 60m3 for testing at 28 days.
| 02SL - Stations (LUL) | Cxxx-NCR-000167 | NCR | P&T Missing __ in Platform Slab PS E16 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2017-06-30 | 2016-04-14 12:31 | -442 | 2016-02-17 09:20 | Civil - Civil Engineering General | 1500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | __ Channel has been missed in the WTH Platform Slab (PS E16). Please see photo attached.
| 02SL - Stations (LUL) | Cxxx-NCR-000168 | NCR | WTH Cracks in L-5 Mass Fill Slab GL K |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-05-27 | 2016-04-18 07:51 | -39 | 2016-02-19 08:56 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Cracks have appeared in the mass fill slab on L-5. This is due to boxouts having to be being formed within the mass fill. The cracks seem to propagate from the unreinforced boxout corners through the mass fill concrete.
| 02SL - Stations (LUL) | Cxxx-NCR-000169 | NCR | ETH L-5 Starter Couplers For IW33 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-04-01 | 2016-04-08 16:18 | 7 | 2016-02-22 11:28 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The starter couplers installed within the ETH Level -5 Raft Slab were found to be out of position when constructing the base pour of IW33 (lift pit wall). This resulted in no cover being achieved on the north side of the wall
| 02SL - Stations (LUL) | Cxxx-NCR-000170 | NCR | ETH Rebar Changes in Level-5 P12 Infill Reinforcement |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-04-08 | 2016-04-04 13:46 | -4 | 2016-02-26 11:22 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The following problems have been encountered regarding the installation of rebar for Level -5 P12 Infill: 1. 11no B20 threaded starter bars (BM E122) on drawing 50371 Rev C01 cannot be installed, as the couplers have been cut during removal of P12 plunge column. 2. 11no B16 @ 150mm centres positional couplers have been installed for the infill, in-lieu of Easi-strip detailed on section Y-Y of drawing 50370 Rev C01
| 02SL - Stations (LUL) | Cxxx-NCR-000171 | NCR | ETH Pecker damage to L-4 soffit above trackway |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-04-08 | 2016-04-07 13:04 | -1 | 2016-02-24 15:25 | Civil - Civil Engineering General | 3000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | During excavation works for L-5, whilst breaking out the blinding below the L-4 soffit, damage to the soffit has occurred. This has resulted in small dents in the soffit which means the concrete finish does not conform to the specification. Note this NCR relates to the L-4 soffit above the trackway only.
| 02SL - Stations (LUL) | Cxxx-NCR-000172 | NCR | ETH Lack of cover to reinforcement bar in Slab 12 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-04-08 | 2016-04-08 15:52 | 0 | 2016-02-25 09:42 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During a post pour inspection which was carried out on the side of Slab 12 on 22.02.16, it was noticed that, at the construction joint with Wall 2/3, 1No. 20mm lacer reinforcement bar in Slab 12 only had approx. 5mm cover. Please see photo attached for clarity.
| 02SL - Stations (LUL) | Cxxx-NCR-000173 | NCR | P&T EB WTH TW E1 Breakblock |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-03-25 | 2016-03-24 16:47 | -1 | 2016-03-03 14:23 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | All female couplers cast into TW E1 have been located incorrectly.
| 02SL - Stations (LUL) | Cxxx-NCR-000174 | NCR | P&T EB WTH TW E2 Breakblock |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-03-25 | 2016-03-24 16:48 | -1 | 2016-03-03 14:45 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Female couplers cast into TW E2 have been incorrectly located approximately 80mm out of chainage from the design location. Couplers cannot be found cast into the track slab.
| 02SL - Stations (LUL) | Cxxx-NCR-000176 | NCR | P&T Testing of PES Precast Planks |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-07-29 | 2016-07-29 13:59 | 0 | 2016-03-14 17:23 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Not Defined | Completed |  | The Works Information Volume 2B Section 20.8 Inspection and Testing requires all on-site and off-site testing to be carried out by a UKAS accredited test house. Cornish Concrete have not fulfilled this requirement for approx 50% of precast plank production days - of 47 pour days, results from a UKAS accredited laboratory are not available for 25 days.
| 02SL - Stations (LUL) | Cxxx-NCR-000177 | NCR | ETH L-5 IW50 Filling of tie holes |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-07-08 | 2016-07-08 12:05 | 0 | 2016-03-16 16:49 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | During a post pour inspection of IW50, it was observed that the tie holes were not being filled to the required depth of 60mm on the north face (60mm cover is required for fireproofing purposes).
| 02SL - Stations (LUL) | Cxxx-NCR-000178 | NCR | ETH L-4 Earthing Connection in Column C3 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-07-15 | 2016-06-28 09:00 | -17 | 2016-03-16 17:05 | Civil - Civil Engineering General | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The length of the B10 bars cast-in the Level -3 slab soffit has been damaged and is not sufficiently long to enable a crocodile clamp to be fitted for earthing connection tests and achieve a 200mm lap with the main B10 bar in the column. See attached photo.
| 02SL - Stations (LUL) | Cxxx-NCR-000179 | NCR | Size of ducts used in additional draw pit in Track Slab 2C |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2017-01-27 | 2017-01-25 09:40 | -2 | 2016-11-10 11:44 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Insufficient quantity of material to do the job | Completed |  | For the additional draw pit in Track Slab 2c (detailed in Cxxx-FCD-000328), 2No. 110mm ducts (90° bend 450mm radius) were installed instead of 150mm ducts. These are exiting the east side of the additional draw pit and are located adjacent IW50. See As built and marked-up sketches attached for clarity.
| 02SL - Stations (LUL) | Cxxx-NCR-000180 | NCR | ETH Level -6 Track Slab Pour 2a Rebar Lap |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-04-08 | 2016-04-08 15:48 | 0 | 2016-03-17 08:20 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 14No BM01 Bars protrude 1500mm outside of Slab Pour 2, instead of 2000mm which is the required lap length for 40mm dia bars.
| 02SL - Stations (LUL) | Cxxx-NCR-000181 | NCR | P&T SW W35 and SW W37 Builders Work Openings |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-07-26 | 2019-02-12 16:32 | 201 | 2016-03-22 16:06 | Civil - Civil Engineering General | 1500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Builders work openings have been missed from both SW W35 and SW W37. The openings are 300mm x 300mm in size. **** Update 26/04/18 **** Location: Platforms and Tunnels. Eastern end of WB Platform. Hole Reference: MH175 MH176 PMI: Cxxx-PMI-01559 Wall Ref: SW W35 & SW W37 Rebar/Concrete Drawing: Cxxx-SKC-S-DWG-Cxxx-500074 Rev X02 Update 30/1 **************** please ignore previous. See attachment NCR 181 MH175 and MH176 Ferro scanning detail.docx for details of NCR
| 02SL - Stations (LUL) | Cxxx-NCR-000182 | NCR | P&T Eastbound Tunnel TWE1b thickness |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-05-20 | 2016-05-19 14:27 | -1 | 2016-04-04 13:01 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The TWE1b is shown on approved construction drawings to be 200mm thick in the location clarified by Cxxx-RFI-002216. However, at the time of installation setting out errors meant the wall was installed 160mm west of the design location (as per sketch Cxxx_SK_P&T_108). The UPE void through the platform slab however remains in excess of 4.0m2.
| 02SL - Stations (LUL) | Cxxx-NCR-000183 | NCR | ETH - Lining walls 7, 8 & 9 at Level -5 Dyvidag Bars |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-04-08 | 2016-04-08 16:26 | 0 | 2016-03-17 17:32 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Dyvidag bars installed for the Lining wall shutter have been cut flush with the surface of the wall. These dyvidag bars are to be cut back and made good to achieve the required 60mm cover at Lining Walls 7, 8 & 9 at L-5.
| 02SL - Stations (LUL) | Cxxx-NCR-000184 | NCR | WTH Level -4 Lobby 5/086 North Wall Pre cast Concrete Lintel not installed as per spec |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-06-03 | 2016-05-31 07:40 | -3 | 2016-04-18 14:16 | Architectural - Brickworks/Blockworks | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In location WTH Level -4 Lobby 5/086 North Wall (Lintel 2 Test Panel), full length masonry block was not placed directly below concrete lintel ends as required by specification clause JF10 3213. Position of lintel was originally 30mm above bed joint in blockwork. Subcontractor has attempted to install by placing small cut pieces of block under lintel as shown in attached photograph.
| 02SL - Stations (LUL) | Cxxx-NCR-000185 | NCR | WTH Level -4 LCR Room 5/776 West Wall Pre cast Concrete Lintel not installed as per spec |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-07-29 | 2016-07-22 15:30 | -7 | 2016-04-18 16:21 | Architectural - Brickworks/Blockworks | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | In location WTH Level -4 LCR Room 5/776 West Wall, full length masonry block was not placed directly below concrete lintel ends as required by specification clause JF10 3213.
| 02SL - Stations (LUL) | Cxxx-NCR-000186 | NCR | WTH Level -4 Plant Ventilation Room 5/778 West Wall Pre cast Concrete Lintels not installed as per spec |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-11-14 | 2016-11-11 13:37 | -3 | 2016-05-27 08:56 | Architectural - Brickworks/Blockworks | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In location WTH Level -4 Plant Ventilation Room 5/778 West Wall Lintel 5, Full Masonry Block was not placed directly below concrete lintels ends. See attached IMAG1467
| 02SL - Stations (LUL) | Cxxx-NCR-000187 | NCR | Missing chamfers to exposed edges on side of slab 12 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-09-16 | 2016-09-15 10:28 | -1 | 2016-03-22 08:27 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Missing chamfers to exposed edges on side of slab 12 which is not in line with specification Cxxx-SKC-A-RSP-Cxxx-50003 - JE41.1203. Please see photo and mark up attached. CRL-OBS-08989
| 02SL - Stations (LUL) | Cxxx-NCR-000188 | NCR | P&T Platform nosing halfen channel cast out of position |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-04-29 | 2016-04-14 12:28 | -15 | 2016-03-22 09:28 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __ Channel has been displaced during concrete pour and subsequently has been cast out of position on a skew in platform slab 8. (See photo attached)
| 02SL - Stations (LUL) | Cxxx-NCR-000189 | NCR | ETH L-5 Lack of cover to reinforcement bar in Slab 11 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-08-26 | 2016-08-26 12:59 | 0 | 2016-03-22 17:33 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During a post pour inspection which was carried out on the side of Slab 11 on 03.03.16, it was noticed that, at the construction joint with Wall 2/3, 1No. 20mm lacer reinforcement bar in Slab 11 Approx 4m from GL D extending a further 3m only had approx. 5mm cover. Please see photo attached for clarity. In addition to this a cover block debris and tie wire was observed.
| 02SL - Stations (LUL) | Cxxx-NCR-000190 | NCR | ETH L-5 Track Slab Pour 3b Lack of cover |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-12-16 | 2016-12-16 14:12 | 0 | 2016-03-23 14:39 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During a pre pour inspection for ETH L-5 Track Slab pour 3b, it was noticed that cover to reinforcement in the side of the Track slab varied between 30mm-60mm (area affected is a 1.5m stretch from the face of LCE1). Please see attached photo for clarity.
| 02SL - Stations (LUL) | Cxxx-NCR-000191 | NCR | P&T 50mm Stainless Steel Pumped Drainage BS E1 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-08-05 | 2016-08-05 16:09 | 0 | 2016-04-04 10:32 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 50mm stainless steel pumped drainage has been installed in the incorrect position in Base Slab E1. Please find attached as-built survey showing the location it has been cast.
| 02SL - Stations (LUL) | Cxxx-NCR-000192 | NCR | P&T Builders work openings on SW W2a |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-08-05 | 2016-08-05 13:26 | 0 | 2016-04-04 10:36 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Builders work openings on SW W2a (both the 1050mm x 500mm and 120mm x 400mm openings) have been installed in the wrong position. Please see attached as-built survey showing the current position of the builders works openings. The “837mm” measurement has been measured from the wrong side of the wall, meaning the boxouts have shifted 200mm in total.
| 02SL - Stations (LUL) | Cxxx-NCR-000193 | NCR | ETH L-3 Earthing Connection in Column C2 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-08-05 | 2016-08-05 14:12 | 0 | 2016-04-05 08:21 | Civil - Civil Engineering General | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The length of the B10 bars cast-in the Level -3 slab is not sufficiently long to achieve a 200mm lap with the main B10 bar in the column. See attached photos.
| 02SL - Stations (LUL) | Cxxx-NCR-000194 | NCR | ETH L-4 Lining Wall 8 insufficient cover to LCE1 re-injectable grout tube |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-05-20 | 2016-05-18 16:33 | -2 | 2016-04-05 07:27 | Civil - Civil Engineering General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | The design of the re-injectable grout tubes for the LCE1 tunnel connection sets them 100mm from the LCE1 front face. This does not take into account that Lining Wall 8 at Level -4 (also in contact with the tubes) is less thick than LCE1. This results in a lack of cover to the re-injectable tube on the LCE1/Lining Wall 8 joint.
| 02SL - Stations (LUL) | Cxxx-NCR-000196 | NCR | ETH L-2 Earthing Connection in Column C2 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-08-05 | 2016-06-28 09:03 | -38 | 2016-04-06 12:44 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The length of the B10 bar cast-in the Level -2 slab is not sufficiently long to enable 2 rebar clamps to be fitted for earthing connection and achieve a 200mm lap with the main B10 bar in the column. See attached photo for clarity.
| 02SL - Stations (LUL) | Cxxx-NCR-000197 | NCR | ETH - Omission of coupled bars in IW21 L-3 to L-2 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-05-13 | 2016-05-13 16:14 | 0 | 2016-04-06 12:51 | Civil - Civil Engineering General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | With reference to drawings Cxxx-SKC-S-DWG-Cxxx-50104-C06 and Cxxx-SKC-S-DWG-Cxxx-50293-C02, the Contractor notes that there are missing couplers between BM02 on drawing 50293 and BME04 on drawing 50104. Please see marked up versions of these drawings attached for clarity.
| 02SL - Stations (LUL) | Cxxx-NCR-000198 | NCR | ETH ATS12 Dering St Communication Failure |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-05-27 | 2016-04-20 13:30 | -37 | 2016-04-08 09:43 | Surveying - Instrumentation and Monitoring | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Power failure or transient | Completed |  | ATS 12, situated at top of 19 Dering Street, developed relay fault inside the logger enclosure on 08/03/16. This prevented communication between the ATS and the logger itself. As result of this communication failure, no data could be received and processed by the logger. The logger is located on the top of the roof of the building, certain access measures and procedures were followed for gaining access to the building. Despite this the change in ownership of the building prevented a quick resolution despite many attempts by .
| 02SL - Stations (LUL) | Cxxx-NCR-000199 | NCR | ETH Missing In-Process Concrete Inspection Sheet |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-05-27 | 2016-05-27 13:44 | 0 | 2016-04-08 10:56 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Personnel Error - Not Defined | Completed |  | The In Process sheet for L‐5 Lining Wall 9 Pour 3 Lift 1 did not sync from the iPad completely. This can be seen on the attached In-Process sheet with the items in red having been entered post pouring the wall from the concrete tickets. These however do not have the testing results apart from ticket 53489 which had the slump recorded as part of the cube technicians report. It should be noted that all concrete was tested and verified before pouring and in some instances as shown was rejected if it did not meet the required specifications.
| 02SL - Stations (LUL) | Cxxx-NCR-000200 | NCR | ETH Level -5 Missing B10 Starters for non-load bearing walls |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-05-27 | 2016-05-27 15:45 | 0 | 2016-04-15 08:31 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | B10 Starters for non-load bearing walls were not installed as per construction drawing. The Highlighted details on the attached drawing were not installed during the construction of the structural internal walls.
| 02SL - Stations (LUL) | Cxxx-NCR-000202 | NCR | WTH Elevation E Chiller Room 0 to 0.5+ missing Cxxx coupler bars |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-05-13 | 2016-05-13 10:34 | 0 | 2016-04-25 07:33 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient work planning by the subcontractors | Completed |  | Three separate issues were identified with reinforcement connections between elevation E chiller room wall, Cxxx ground floor slab and ventilation shaft elevation L, namely: -Cxxx Missing couplers in ground floor slab -Cxxx Couplers cast with reduced cover in ground floor slab -Incorrectly positioned pull out bar in elevation L of slip form
| 02SL - Stations (LUL) | Cxxx-NCR-000203 | NCR | ETH L-2 Column C1 Reinforcement |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-05-27 | 2016-05-27 12:37 | 0 | 2016-04-26 10:36 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Column C1 on L-2 has 3no. reinforcement bars that have been drilled and fixed into L-1 soffit using __ Hit 200. (See image 6960 attached). There have also been some reinforcement that has been ‘cranked’ in the L-2 slab (as seen in image 6966). ***Updated NCR Details*** To clarify the details above, 9no. bars have been cranked, 70mm each bar (south) to match the outside face of the column (see photos 9792 and 9793). See attached sketch for the positions of these bars.
| 02SL - Stations (LUL) | Cxxx-NCR-000204 | NCR | WTH Installation of __ for Ducting without Assured Design |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-07-29 | 2016-07-29 13:04 | 0 | 2016-04-26 17:44 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Installation of __ for ducting has commenced at WTH Level -5 Circulation Areas without an approved or assured design. No Minigate or ‘By Exception’ design assurance process has been carried out for this area
| 02SL - Stations (LUL) | Cxxx-NCR-000205 | NCR | ETH Lift 2 upstands not constructed - all levels |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-08-12 | 2016-08-12 15:22 | 0 | 2016-04-29 16:09 | Civil - Civil Engineering General | 1500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The upstands on the Lift 2 doorway shown on the Cxxx section drawings (see attached sketch) have not been detailed on the Cxxx reinforcement drawings for L-1 to L-3, therefore have not been constructed (eazi-strip has been installed for L-4 and L-5).
| 02SL - Stations (LUL) | Cxxx-NCR-000206 | NCR | ETH Missing Continuity Reinforcement in Column C3 L-2 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-06-10 | 2016-06-17 15:41 | 7 | 2016-05-04 07:39 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the construction of Beam 6 at L-1, the B10 continuity bar for the earthing was not installed for Column C3 (it is installed at the base of L-2 only).
| 02SL - Stations (LUL) | Cxxx-NCR-000207 | NCR | ETH L-1 IW34A Drill and Fix |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-06-10 | 2016-06-17 14:15 | 7 | 2016-05-04 07:47 | Civil - Civil Engineering General | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the construction of IW34A on L-1, 18No. bars have been drilled and fixed as detailed on the attached marked-up drawing entitled ‘Cxxx-SKC-S-DWG-Cxxx-50123-C05 SB Mark-up’ and photos attached.
| 02SL - Stations (LUL) | Cxxx-NCR-000208 | NCR | ETH L-1 IW33 - Doorway position |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-06-24 | 2016-06-02 12:29 | -22 | 2016-05-04 07:47 | Civil - Civil Engineering General | 10000 |  | Incorrect Installation | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 1 side of the doorway on IW33 on L-1 has been cast in the wrong position (122mm west, see attached sketch).
| 02SL - Stations (LUL) | Cxxx-NCR-000209 | NCR | ETH L0 B5 Position Error |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2017-07-30 | 2017-06-09 13:21 | -51 | 2016-05-11 07:17 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | During the construction of the Ground floor slab B5 was constructed incorporating the internal wall IW31, this can be seen in Cxxx-SKC-S-DWG-Cxxx-50004 Section 7-7. The face of this extends 875mm from GL 2 which is 75mm greater than specified on Cxxx-__-S-DDL-Cxxx-52103. Please see attached marked up drawing highlighting final as-built position.
| 02SL - Stations (LUL) | Cxxx-NCR-000210 | NCR | WTH- Elevation M Ventilation Shaft Level 0.5+ to +1 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-07-29 | 2016-06-29 09:00 | -30 | 2016-05-12 16:24 | Civil - Civil Engineering General | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | Drawing Cxxx-SKC-S-DWG-Cxxx-50428 Rev C03 does not detail the pull out bar to be installed at the connection with elevation C of the Chiller Room. At the time of installation no chiller room drawings were detailed. P1 Pull out bar was installed during the slipform works which is an L bar, not the required U bar.
| 02SL - Stations (LUL) | Cxxx-NCR-000211 | NCR | ETH L-5 Gullies Level |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-08-19 | 2016-06-17 15:45 | -63 | 2016-05-17 14:49 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 2 No. Gullies have been installed where the lip of the gully is approx. 12mm above the existing concrete level. This will create an area where ponding can occur once the Hydroduct has been installed.
| 02SL - Stations (LUL) | Cxxx-NCR-000212 | NCR | ETH L-5 IW33 Crack |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-08-19 | 2016-08-18 11:56 | -1 | 2016-05-17 15:01 | Civil - Civil Engineering General | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | A crack above the door opening in the concrete wall IW33 is larger than specified within the spec.
| 02SL - Stations (LUL) | Cxxx-NCR-000213 | NCR | ETH L-1 Earthing Connection in Column C2 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-08-19 | 2016-06-28 09:02 | -52 | 2016-05-17 15:08 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The length of the B10 bars cast-in the Level -3 slab is not sufficiently long to achieve a 200mm lap with the main B10 bar in the column. The photo attached shows that a 100mm lap has been achieved.
| 02SL - Stations (LUL) | Cxxx-NCR-000214 | NCR | WTH Dust Sealant |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-06-24 | 2016-06-01 15:40 | -23 | 2016-05-18 07:03 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | applied dust sealant to an RC wall as part of a benchmark panel without the ITP update getting approval from CRL prior to the application.
| 02SL - Stations (LUL) | Cxxx-NCR-000216 | NCR | Cxxx Temporary Works Register |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-07-01 | 2016-06-16 14:44 | -15 | 2016-05-20 15:54 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | The WI v2B part 22.4 states that the Contractor shall update the temporary works register every 4 weeks and submit the revised register to the Project Manager for acceptance. The register has been updated by the Contractor more frequently than every 4 weeks, however, revised registers have not been submitted to the Project Manager for acceptance every 4 weeks.
| 02SL - Stations (LUL) | Cxxx-NCR-000217 | NCR | ETH Column C3 L-1 B10 Continuity Bar not installed |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-06-24 | 2016-06-17 15:52 | -7 | 2016-05-24 08:33 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Previous Construction - Improper As Built | Completed |  | During the construction of Beam 6 at L-1, the B10 continuity bar for the earthing was not installed for Column C3 therefore a B40 bar was used at L-2 to connect the previous B10 bar. This is detailed in Cxxx-NCR-000206.
| 02SL - Stations (LUL) | Cxxx-NCR-000218 | NCR | ETH Main Escape Staircase Flight 5 Bottom Landing |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-07-15 | 2016-06-28 13:53 | -17 | 2016-05-24 09:10 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | ETH Main Escape Staircase – Flight 5 Bottom Landing has been cast in the wrong position. The landing was cast 270mm from GL C, and has been cast 600mm in the wrong position (100mm from break point, see attached sketch).
| 02SL - Stations (LUL) | Cxxx-NCR-000219 | NCR | WTH Chiller Room - Couplers missing in Vent Shaft |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-10-28 | 2016-10-28 10:08 | 0 | 2016-05-24 10:08 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Personnel Error - Verbal communication problem | Completed |  | Couplers have not been installed in the vent shaft to accommodate the connection to the beam at the extract duct location. See attached DWG showing the location.
| 02SL - Stations (LUL) | Cxxx-NCR-000220 | NCR | ETH IW 24 L -1 Builders Work Recess |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-06-03 | 2016-06-03 13:09 | 0 | 2016-05-24 13:32 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Wall IW 24 on L-1 was cast without a builders work recess in the wall. Reinforcement was installed as per the drawing, with bars installed forming this recess, but the boxout was not installed and the wall was cast without it.
| 02SL - Stations (LUL) | Cxxx-NCR-000221 | NCR | ETH Subcontractor Inspection Records |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-07-22 | 2016-07-22 15:56 | 0 | 2016-05-25 11:54 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Subcontractor signing off works that have not even been built. The subcontractor has signed off for shutters for column C1 at level-2 of the ETH and IW’s 25, 27, 28, 29 at level-1 of the ETH. None of these shutters have been erected.
| 02SL - Stations (LUL) | Cxxx-NCR-000222 | NCR | ETH IW 48c L-2 Poured to wrong level |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-06-24 | 2016-06-06 14:55 | -18 | 2016-05-24 15:35 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | IW48c on L-2 was cast 450mm too high.
| 02SL - Stations (LUL) | Cxxx-NCR-000223 | NCR | Waterproof Concrete poured without accepted MCR |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-07-01 | 2016-05-26 16:16 | -36 | 2016-05-25 12:59 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Waterproof Concrete was poured to WTH Southern Capping Beam by prior having gained acceptance from Crossrail of an MCR for this material.
| 02SL - Stations (LUL) | Cxxx-NCR-000224 | NCR | ETH L-4 IW24 Missing 50mm Hole |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-06-17 | 2016-06-16 12:07 | -1 | 2016-05-25 15:06 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Wall IW24 on L-4 has a lift control panel cast into the wall and should contain a 50mm hole in the centre. This hole is missing in the recess - see attached 'Image 1’
| 02SL - Stations (LUL) | Cxxx-NCR-000227 | NCR | ETH Lift Pit 2 L-3 Doorway |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-07-15 | 2016-07-15 15:24 | 0 | 2016-05-26 08:02 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Formwork soffit was not cleaned prior to concrete pour. This has resulted in an excess amount of tie wire being left in the soffit of the doorway on Lift Pit 2 and L-3 - see attached photos.
| 02SL - Stations (LUL) | Cxxx-NCR-000228 | NCR | ETH Lift Shaft L-5/L-4 IW33 and IW35 Cover to Reinforcement |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-07-01 | 2016-07-01 15:16 | 0 | 2016-05-26 10:28 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 2no. bars on IW33 and IW25 at L-5 and L-4 respectively are exposed through the face of the concrete. (See image A and image B attached).
| 02SL - Stations (LUL) | Cxxx-NCR-000234 | NCR | ETH Damage to L-5 __ Channels |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-10-07 | 2016-10-07 16:31 | 0 | 2016-05-26 16:44 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | During the excavation of L-5 some damage occurred in localised areas to the __ Channels cast into the soffit
| 02SL - Stations (LUL) | Cxxx-NCR-000235 | NCR | ETH Damage to L-4 __ Channels |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-10-07 | 2016-10-14 10:14 | 7 | 2016-05-26 16:47 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | During the excavation of L-4 some damage occurred in localised areas to the __ Channels cast into the soffit
| 02SL - Stations (LUL) | Cxxx-NCR-000236 | NCR | ETH Main Escape Staircase Flight 7 Bottom Landing Cast in wrong position |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-07-15 | 2016-07-22 15:29 | 7 | 2016-05-26 17:11 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | ETH Main Escape Staircase – Flight 7 Bottom Landing has been cast in the wrong position. The landing was cast 270mm from GL C, and has been cast 600mm in the wrong position (100mm from break point, see attached sketch).
| 02SL - Stations (LUL) | Cxxx-NCR-000237 | NCR | ETH Escalator 13 - Truss section |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-08-26 | 2016-08-26 12:32 | 0 | 2016-05-26 17:28 | Mechanical - Escalators | 500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | During compliance checks of the Bond Street units a non-conformance has been identified in the brackets for the tension carriage springs and switches of Escalator 13. The design has been updated but one of the brackets installed was to the original design.
| 02SL - Stations (LUL) | Cxxx-NCR-000238 | NCR | WTH L -4 Non Load Bearing Wall 4/B-F out of tolerance |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-08-26 | 2016-08-04 09:02 | -22 | 2016-06-09 11:38 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | NLB Wall 4/B-F on L-4 has been cast in the incorrect position, up to a maximum of 34mm. Attached is an as-built survey showing the position of the wall, with a marked up drawing.
| 02SL - Stations (LUL) | Cxxx-NCR-000239 | NCR | WTH Works Commenced prior to ITP Acceptance |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-08-26 | 2016-08-05 14:18 | -21 | 2016-06-03 16:21 | Architectural - Doors | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | 7 no. doors were installed in Levels -5, -4 & -2 in the Western Ticket Hall prior to the acceptance of the installation ITP (Cxxx-SKC-O4-ITP-Cxxx-50015). The doors were also fabricated prior to acceptance of the fabrication ITP (Cxxx-SKC-O4-ITP-Cxxx-50014 R1 was Code 3).
| 02SL - Stations (LUL) | Cxxx-NCR-000240 | NCR | ETH L-1 Column C1 Couplers Missing |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-09-16 | 2016-09-15 10:56 | -1 | 2016-06-06 16:20 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As discussed with Cxxx (__) and (__) on 06.06.16, there are 5No. couplers missing in the soffit and 1No. coupler missing in the base of the slab for column C1 (the reasons for this are detailed in the marked up drawing 50019 attached).
| 02SL - Stations (LUL) | Cxxx-NCR-000241 | NCR | ETH L-5 Drilling into Completed Wall IW50 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-08-05 | 2016-08-05 13:04 | 0 | 2016-06-10 15:24 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | During the construction of Wall 1 and the associated mass infill between IW 31 and Wall 1 a number of 22mm dia. holes were drilled into the southern face of IW 50, and a number of holes drilled through IW31. This was required to facilitate the installation required for the construction of Wall 1 and the mass infill section.
| 02SL - Stations (LUL) | Cxxx-NCR-000242 | NCR | ETH Main Escape Staircase L3.5 to L-3 Couplers cast in wrong position |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-07-29 | 2016-07-28 07:50 | -1 | 2016-06-10 15:11 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Couplers cast too high in the Main Escape Staircase L3.5 to L-3 Flights 3 and 4
| 02SL - Stations (LUL) | Cxxx-NCR-000243 | NCR | WTH Chiller Room Mezzanine slab Level 0.5+ Reduced Strength after 28days |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-09-09 | 2016-09-16 10:35 | 7 | 2016-06-21 10:14 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Mix design C32/40 SUP-PUMP was poured on 9/05/16 to complete the construction of the mezzanine slab at level 0.5+ in the WTH Chiller Room. Test results received on document CSJ 106900 (attached) confirm the strength at 28 days to be 36.6 N/mm² whilst design strength is 40 N/mm².
| 02SL - Stations (LUL) | Cxxx-NCR-000244 | NCR | ETH Position of Eazi-strip in L-3 NLB Wall 11 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-07-29 | 2016-07-20 08:59 | -9 | 2016-06-21 10:51 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | Eazistrip cast in wrong position on NLB Wall 11, L-3 (see photo attached).
| 02SL - Stations (LUL) | Cxxx-NCR-000245 | NCR | ETH Lift 5 As Built Installed __ Channels |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-09-11 | 2018-10-03 16:22 | 22 | 2016-12-23 09:42 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Please find attached As Built Survey Lift shaft 5 (Originally Called Lift 1, now titled Lift 5. Please read attachments labelled Lift 1 as Lift 5). __ Channels - Dimensions and As Built Survey Lift shaft 5 Levels of __ Channels detailing the as-built location of the __ channels in Lift Shaft 5 compared to the design position.
| 02SL - Stations (LUL) | Cxxx-NCR-000246 | NCR | ETH Lift 6 As Built Installed __ Channels |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-12-31 | 2018-10-03 16:24 | -89 | 2016-12-23 09:42 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Please find attached ETH As Built Survey Lift shaft 6 __ Channels - Dimensions and ETH As Built Survey Lift shaft 6 __ Channels - Levels detailing the As-built location of the halfen channels in Lift Shaft 6 compared to the design position Note: Originally titled Lift 2, now titled lift 6. Please read attachments referring to Lift 2 as Lift 6.
| 02SL - Stations (LUL) | Cxxx-NCR-000247 | NCR | P&T Track Slab E1 and Platform Slab E12 Low Concrete Cube Strengths (28 day only) |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2017-01-27 | 2017-01-24 15:05 | -3 | 2016-07-04 09:33 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Lack or improper material identification and traceability | Completed |  | Two __ Certificates have 28 day strengths that have not reached the target of 40 Nmm2
| 02SL - Stations (LUL) | Cxxx-NCR-000248 | NCR | P&T Base Slab E10 / E11 and Platform SLab E7 (28 and 56 day results) |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2017-02-28 | 2017-02-09 17:46 | -19 | 2016-07-04 10:16 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Lack or improper material identification and traceability | Completed |  | Two __ Certificates have 28 day strength results that have not reached the target of 40 Nmm2 and additionally the 56 day compressive strength tests have subsequently fallen short of the 40N/mm2 target.
| 02SL - Stations (LUL) | Cxxx-NCR-000249 | NCR | P&T West Bound - Platform Service Wall W2D and Platfrom Slab Wall W1 part 1 (one 28 day) |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-09-23 | 2016-10-17 09:21 | 24 | 2016-07-04 10:44 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A __ Certificate has one of the 28 day strength results of two that has not reached the target of 40 Nmm2. The other 28 day result is just above - but the average of these two is 39.6N/mm2 . However the 56 day result is comfortably above 40 N/mm2 at 46.3N/mm2.
| 02SL - Stations (LUL) | Cxxx-NCR-000250 | NCR | Platform and Tunnel Eastbound Track Wall E20/E21 and Corbel E21/B - Unconventional 28 day result |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-11-04 | 2016-10-31 13:41 | -4 | 2016-07-04 12:15 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Lack or improper material identification and traceability | Completed |  | One 28 day __ Compressive test Result reached 59.1 N/mm2 and the other 28 day result shows 23.4 N/mm2. The average being above 40 N/mm2 but the difference greater than 15%. __ have not tested at 56 days and no longer have the cube.
| 02SL - Stations (LUL) | Cxxx-NCR-000251 | NCR | ETH Damage to Concrete Finish Benchmark |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-09-23 | 2016-09-26 16:03 | 3 | 2016-07-04 13:46 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Holes have been drilled and chips are evident in Wall IW 22a Level -5 (see attached photos 2855, 2856, 2857, 2858). This damage occurred to the wall subsequent to the CON-121 Benchmark for concrete finish being inspected and accepted on 27/04/2016 (see Inspection Sheet attached).
| 02SL - Stations (LUL) | Cxxx-NCR-000252 | NCR | ETH Unnecessary Couplers to IW67, L-5 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-12-02 | 2016-11-25 17:26 | -7 | 2016-07-04 13:53 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Redundant couplers have been cast into the Level -4 slab soffit. These were installed for IW 67 but installed along the incorrect line therefore were not included within the IW 67 pour - see attached photo. Please note that two rows of reinforcement are confirmed to have been installed.
| 02SL - Stations (LUL) | Cxxx-NCR-000253 | NCR | ETH L-1 IW33, Damage to Nib |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-11-14 | 2016-10-28 09:55 | -17 | 2016-07-04 14:08 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Following removal of the formwork, the nib to IW33 on L-3 was found to have some minor defects. Concrete damaged during formwork removal and a small amount of residual debris in the concrete. See attached photos. (Pic 1, Pic 2, Pic 3) The defects are localised and about 20mm deep within the concrete cover zone, and the remaining concrete is not honeycombed or affected. See attached copy of L-1 IW33 Nib Damage - Location Mark Up with arrows where photos taken from. Height of defects at +1211.00
| 02SL - Stations (LUL) | Cxxx-NCR-000254 | NCR | By Exception Design Reviews |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-09-23 | 2016-08-31 08:08 | -23 | 2016-07-04 15:21 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Procedure CRL1-XRL-O7-GPD-CR001-50023 Rev 1 requires an NCR to be raised for By Exception reviews held, since the construction released by these reviews is not in accordance with standard governance. The following By exception reviews have been held and are covered under this NCR: 7.1: WTH Blockwork and Buildersworks (level -5/-4), Cxxx-SKC-O-RGN-Cxxx-50032 Rev 2.0 7.4: WTH Blockwork and Buildersworks (level -1), Cxxx-SKC-O-RGN-Cxxx-50042 Rev. 1.0 24.2: ETH Blockwork and Buildersworks (L-4,-3,-2 & -1), Cxxx-SKC-O-RGN-Cxxx-50073 Rev 1.0 26: WTH Screed at level -5, Cxxx-SKC-O-RGN-Cxxx-50038 Rev. 1.0 27: WTH Architectural Finishes to level -4, Cxxx-SKC-O-RGN-Cxxx-50051 Rev 1.0 30: Prototype for architectural Bronze, Cxxx-SKC-O-RGN-Cxxx-50033 Rev. 1.0 31: Metal Doors (acoustic) located in WTH TVS areas, Cxxx-SKC-O-RGN-Cxxx-50043 Rev. 1.0 34: Prototype for structural pre-cast, Cxxx-SKC-O-RGN-Cxxx-50034 Rev. 1.0 45: PES Electrical Containment, Cxxx-SKC-O-RGN-Cxxx-50064 Rev. 1.0 47: LU Link Passage (concrete, drainage, screed), Cxxx-SKC-O-RGN-Cxxx-50069 Rev. 1.0 7.3: WTH Blockwork Blockwork Level -3/-2, Cxxx-SKC-O-RGN-Cxxx-50115 Rev 1.0
| 02SL - Stations (LUL) | Cxxx-NCR-000255 | NCR | ETH NLB Wall 2, L-5 Out of Alignment |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-10-07 | 2016-08-04 08:55 | -64 | 2016-07-05 07:57 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Wall 2 on L-5 has been cast out of alignment. The wall is up to 50mm thicker than design. Please see attached as-built sketch showing the 1.5m x 2.1m section of wall that is out of alignment, and the cover to reinforcement in this area.
| 02SL - Stations (LUL) | Cxxx-NCR-000256 | NCR | ETH NLB Wall 11, L-4 Out of Tolerance |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-10-07 | 2016-09-28 10:39 | -9 | 2016-07-05 11:03 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | NLB Wall 11 on L-4 has been cast out of tolerance on the northern elevation, adjacent to IW27. This is up to 30mm out of tolerance.
| 02SL - Stations (LUL) | Cxxx-NCR-000257 | NCR | WTH L+1 Trimming Detail |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-09-16 | 2016-09-16 10:40 | 0 | 2016-07-07 07:21 | Civil - Civil Engineering General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | On 06/07/16, completed the reinforcement fixing and poured WTH Level +1 slab chiller room slab in the north-west corner of the WTH site. principally fixed the slab to the Code 1 status drawings Cxxx-SKC-S-DWG-Cxxx-50442 C01 and Cxxx-SKC-S-DWG-Cxxx-50443 C02 . Unfortunately, these drawings remained uncoordinated with the response from Cxxx-RFI-002565 (closed on the 4th of July 2016). Therefore, referred to the drawings within 20160706_SK_WTH L1 Trimming Detail for the new trimming steel arrangement around the Builderswork openings described in Cxxx-RFI-002565 to supplement the approved drawings. seek confirmation that the trimming steel detailing (which supports Cxxx-RFI-002565) described in the sketch attached (20160706_SK_WTH L1 for), in addition to the Cxxx-SKC-S-DWG-Cxxx-50442 C01, remains acceptable.
| 02SL - Stations (LUL) | Cxxx-NCR-000258 | NCR | P&T Platform Slab Edge As-Builts |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2017-05-31 | 2017-04-03 15:52 | -58 | 2016-07-12 14:24 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | A small area of the Eastbound and Westbound tunnel platform edge is out of tolerance as shown in the latest referenced document "P&T Reinforced Concrete As-Built Records Cxxx-SKC-S-LRC-Cxxx-50036" Please ignore the previously attached survey.
| 02SL - Stations (LUL) | Cxxx-NCR-000259 | NCR | P&T __ Channels As-Builts |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2017-04-30 | 2017-05-15 14:57 | 15 | 2016-07-12 14:44 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A small number of cast in __ Channels in the Eastbound tunnel and westbound platform are out of tolerance as shown in the referenced document " P&T Reinforced Concrete As-Built Records Cxxx-SKC-S-LRC-Cxxx-50036" A Table of the reading summaries from Cxxx-SKC-S-LRC-Cxxx-50036 is provided in the attached Summary of Westbound and Eastbound Front & Back __ Readings Please ignore the previously attached as-built information pdf. for __ Channels in the EB tunnel.
| 02SL - Stations (LUL) | Cxxx-NCR-000260 | NCR | P&T ES1_CH2 Blocked Concrete Line |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-10-07 | 2016-10-05 11:11 | -2 | 2016-07-26 09:30 | Civil - Civil Engineering General | 10000 |  | Equipment Breakdown | Repair | 2 (6-60k) | Complete | External Phenomenon - Weather or ambient condition | Completed |  | Whilst pouring the first section of the ES1 / CH2 escalator steps the concrete pump line blocked. The blockage occurred during the changeover between the 2nd and 3rd Concrete wagons - approximately 2/3 of the way through the pour. The line blocked at Level 0 which meant the whole line needed to be taken apart and cleared. By the time this was completed the face of the concrete pour had hardened. As a result the concrete pour was stopped short.
| 02SL - Stations (LUL) | Cxxx-NCR-000261 | NCR | WTH - Chiller Room Elevation B Column Level 0.5+ |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-10-14 | 2016-10-14 10:18 | 0 | 2016-07-26 09:46 | Civil - Civil Engineering General | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Mix design C32/40 S4 was poured on 10/06/16 to complete the construction of the elevation B between levels 0.5+ to level 1.0+ in the WTH Chiller Room. Truck 160361 was batched at 17:08 and commenced discharge at 18:01, at 18:40 concrete began to set. Concrete was placed to column and compacted adequately; despite this the last section of pour (top of column C5a at level 1.0+ slab soffit) was not able to be compacted sufficiently.
| 02SL - Stations (LUL) | Cxxx-NCR-000262 | NCR | ETH MPS Level -5 Pour 2, 3 and 4 Incorrect Concrete Mix Used |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-10-14 | 2016-10-17 16:23 | 3 | 2016-08-02 09:56 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | During the construction of the MPS raft slab, it has been identified that a C32/40 non DC-3 concrete mix has been used within Pour 2, 3 and 4 (notation shown on the attached pour plan).
| 02SL - Stations (LUL) | Cxxx-NCR-000263 | NCR | WTH L-4 blockwork walls out of alignment |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-10-07 | 2016-09-26 09:52 | -11 | 2016-08-05 10:33 | Architectural - Brickworks/Blockworks | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In developing the redline drawings for Level -4 blockwork, an as-built survey of the alignment of blockwork walls was conducted and it was found that 4 no. block walls have been built to full height in the incorrect position in plan: Wall 5/746 East has moved 14mm East of design Wall 5/072 West has moved 22mm East of design Wall 5/071 West has moved 17mm West of design Wall 5/667 East has moved 15mm East of design A plan of the discrepancies has been attached for clarity. It should be noted that the Designer of the blockwork does not consider this NCR to have a negative impact on the design (refer attached Aconex correspondence from __)
| 02SL - Stations (LUL) | Cxxx-NCR-000265 | NCR | ETH MPS - Level-5 GL A/3 - Damage to cast in drain pipe |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-09-16 | 2016-09-15 10:22 | -1 | 2016-08-11 10:34 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | An in-slab cast-iron drain pipe (100mm dia.) was punctured during installation of additional starter bars into the MPS L-5 slab. The puncture is located near GL 3/A with the invert level of the pipe approximately +96.250m. The puncture is located on the southern side of the pipe and terminates in the top half of the pipe. A 500 x 500mm section of the +96.700m slab has been broken out around the damaged pipe to a depth of up to 400mm to expose and assess the extent of the damage, rebar continuity has been maintained.
| 02SL - Stations (LUL) | Cxxx-NCR-000266 | NCR | ETH Level -4 Cavity Drainage Cast In The Incorrect Position |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-09-16 | 2016-09-20 12:58 | 4 | 2016-08-11 14:56 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | During the construction of the ETH Level -4 slab, a cast in section of cavity wall drain has been set in the incorrect position. The as-installed position of the cavity drainage pipe is 1m south from the design installation position. The as-installed position can be seen on drawing "Cxxx-SKC-A-DDL-Cxxx-96141 annotated to show as built location". It should be noted that the grating has been cast into the cavity channel as per the design requirements, and is therefore non-removable. It should also be noted that the drainage runs through the middle of the Level -4 slab, and cannot be adjusted as it could require significant temporary works within the Eastbound running tunnel to support the slab in the partial demolition state.
| 02SL - Stations (LUL) | Cxxx-NCR-000267 | NCR | ETH Damage to L-4 Soffit |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-11-25 | 2016-09-13 08:49 | -73 | 2016-08-18 15:36 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | During the excavation of L-5 some damage occurred in localised areas to the soffit. Where the damage is determined to be deeper than 10mm, the following remedial procedure will be undertaken
| 02SL - Stations (LUL) | Cxxx-NCR-000268 | NCR | Competency assessment of Temporary Works Personnel |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2016-09-19 | 2016-10-21 09:05 | 32 | 2016-08-22 08:33 | Structural Engineering - Structural Engineering - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The Contractor stated that the procedure the Contractors Chief Engineer follows when assessing competencies was not held on site, therefore this could not be assesses during surveillance QS412-10
| 02SL - Stations (LUL) | Cxxx-NCR-000269 | NCR | ETH Damage to L-3 Soffit |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-10-28 | 2016-10-28 09:58 | 0 | 2016-09-08 10:58 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | During the excavation of L-4 some damage occurred in localised areas to the soffit. Where the damage is determined to be deeper than 10mm, the following remedial procedure will be undertaken
| 02SL - Stations (LUL) | Cxxx-NCR-000271 | NCR | Temporary Works Register does not record all planned dates |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2016-09-19 | 2016-10-06 13:38 | 17 | 2016-08-22 08:55 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Temporary Works Register does not record planned dates for Preparation of Inspection and Test Plan, Permit to load form, Bringing into use and Dismantling
| 02SL - Stations (LUL) | Cxxx-NCR-000272 | NCR | Temporary Works document control |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2016-09-29 | 2016-09-27 16:27 | -2 | 2016-08-22 09:18 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Surveillance QS412-10 found that an incorrect revision of the drawing PH15/53751-01/11 had been attached to the Task Briefing (Cxxx-SKC-O1-RGN-Cxxx-50313 revision 2.0 coded 1) Revision E was attached not the current revision F
| 02SL - Stations (LUL) | Cxxx-NCR-000273 | NCR | Changes between drawing revisions not identified |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2016-09-29 | 2016-09-27 16:46 | -2 | 2016-08-22 09:30 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | During surveillance QS412-10 it was found that drawing PH15/53751-01/11 rev F did not identify the changed made from that of rev E .
| 02SL - Stations (LUL) | Cxxx-NCR-000274 | NCR | ETH Level -4 KD12 south wall dust sealant |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-09-30 | 2016-10-07 16:33 | 7 | 2016-08-26 14:28 | Architectural - Brickworks/Blockworks | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | A non load bearing concrete wall was dust sealed without a pre-dust seal inspection carried out. This wall was inspected for structural post-pour and was satisfactory prior to dust sealing work being completed.
| 02SL - Stations (LUL) | Cxxx-NCR-000275 | NCR | ETH MPS L-5 - Breakout of Pile P128 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-10-27 | 2016-10-17 16:22 | -10 | 2016-08-31 16:14 | Civil - Civil Engineering General | 3000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | Drawing Cxxx-SKC-S-DWG-Cxxx-50628 section 3-3 shows 3no piles with 2no rows of couplers each. These couplers are normally required to be exposed in order to install threaded terminator bars (BM-E109). It is not uncommon to have to remove various waterproofing and concrete layers in order to expose the pile couplers. After breaking out and exposing the couplers in Piles P129 and P130 the site team continued to break away concrete on pile P128 but stopped when it became apparent the pile couplers were not in place as shown on Drawing 50628. Further investigation using as-built drawings showed Pile P128 had been removed as part of the Cxxx contract, however this information was not readily available to the site team. Site survey shows approx 150mm of Cxxx concrete and one layer of mesh has been removed as a result of the unplanned breakout works.
| 02SL - Stations (LUL) | Cxxx-NCR-000276 | NCR | WTH Sagging of internal and external doors on elevation H and J ventilation shaft |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2017-04-28 | 2017-06-17 13:05 | 50 | 2016-09-01 11:36 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Both internal doors (RL 125.750) and the northern external door (RL 126.000) in the Western Elevation of the ventilation shaft have sagged at the top during the slipform concreting works. Please note that this NCR is raised to supersede Cxxx-NCR-000142.
| 02SL - Stations (LUL) | Cxxx-NCR-000277 | NCR | WTH- Chiller Room Level 1.0+ slab detailing |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-12-11 | 2016-10-19 10:17 | -53 | 2016-09-21 16:12 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | Inspection of level 1.0+ slab on 06.07.16 identified the following issues in relation to inadequate detailing of reinforcement drawings; Reinforcement changes below were not formally accepted prior to placement of concrete (1) Elevation L drawing Cxxx-SKC-S-DWG-Cxxx-50427 C03 does not detail pull out bar at the connection with level 1.0+ slab (refer to appendix mark-up) – 3 x 4no. B16 bars (2T, 2B) - see pic 2,3,4. (2) Elevation T at level 1.0+ runs at an angle for 250mm on the west of elevation X, it is impossible to install pull out bar in this location and is not detailed (refer to appendix mark-up) – 4no. B16 bars (2T, 2B) - see pic 1. (3) Reinforcement not detailed connecting to elevation A on drawing Cxxx-SKC-S-DWG-Cxxx-50442 Rev. C01(refer to appendix mark-up) – 10no. B16 bars (5T, 5B))- see pic 9. (4) Reinforcement not detailed connecting to elevation B on drawing Cxxx-SKC-S-DWG-Cxxx-50442 Rev. C01 (refer to appendix mark-up) – 4no. B16 bars (2T, 2B) )- see pic 16, 15. (5) Reinforcement is not detailed on accepted drawing Cxxx-SKC-S-DWG-Cxxx-50442 Rev. C01 as extending through elevation D at level 1.0+ slab. Therefore, top and bottom mats of reinforcement to this area match adjacent bar detailing, ensuring sufficient lap lengths are maintained. 'Also, 16mm diameter wall starter L-Bars were also installed at 200mm c/c, at NF2 and FF2 lines for the wall to Elevation D, (these wall starter bars are not detailed on Cxxx-SKC-SDWG-Cxxx-50414 C03). See pics 6, 7, 8 and 20 attached (6) As per RFI 2565 penetration on east of slab between gridline 1 and 2 was not cast, this was reinforced as per main slab reinforcement – refer to appendix mark up and NCR-257 for detailing. (7) Pull out bar installed as per wall drawings for elevation E and T – Cxxx-SKC-S-DWG-Cxxx-50449 C01, & Cxxx-SKC-S-DWG-Cxxx-50424 C01. Bar Marks 21 and 22 U-bars, (as shown on Cxxx-SKC-S-DWG-Cxxx-50424 C01) were not installed, – (refer to appendix mark-up). (8) L bars were installed in lieu of U bars detailed on elevation X (bar mark 13) - Cxxx-SKC-S-DWG-Cxxx-50436 C01.-(refer to appendix mark-up) -see pic 5. (9) Incorrect detailing on drawing Cxxx-SKC-S-DWG-Cxxx-50442 Rev. C01 – Bar mark 06 is incorrect, penetration is 800mm wide therefore only 4no. bars are required in lieu of 6no. (refer to appendix mark-up) See pic 17. 10) The small concrete slab section that runs north-south at GL.A/1 has 4x16mmᴓ bars drill and dowelled at 2xnumber at B2 level and 2xnumber at T2 levels on the north elevation. See pic 10 attached. The very narrow concrete slab section that runs east-west from adjacent to GL.A/1 to the north of the void does not detail any rebar in Cxxx-SKC-S-DWG-Cxxx-50442 Rev. C01. However on site 2x16mmᴓ bars were drill and dowelled in to the west elevation wall, 1 at B2 level and 1 and B3 level. A 16mmᴓ long U-bar has also been added at T1 level, (refer to appendix mark-up) See pic 11. In all cases above 16mm diameter bars were drill and fixed with __ Hit HY-200 min 200mm embedment.
| 02SL - Stations (LUL) | Cxxx-NCR-000278 | NCR | ETH Spraying waterproofing prior to inspection |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-10-07 | 2016-09-13 08:36 | -24 | 2016-09-05 10:43 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | On Friday 2/9/16, the application of the waterproofing product (Masterseal 345) commenced at CH3 prior to the inspection of the substrate {item 8 (HP),16 (R) and 17 (R) from ITP}. The inspection was arranged for 11am, however, due to a communication breakdown between the sub-contractor and the engineering staff, the waterproofing commenced at 9am. Approx. 40% of the waterproofing had been completed mainly the crown and the walls inside the tunnel connections. The waterproofing works were ceased immediately and no additional works were completed for the day.
| 02SL - Stations (LUL) | Cxxx-NCR-000279 | NCR | ETH Damage to L-2 Soffit |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-11-25 | 2016-11-22 14:55 | -3 | 2016-09-08 14:49 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | During the excavation of L-3 some damage occurred in localised areas to the soffit. Where the damage is determined to be deeper than 10mm, the following remedial procedure will be undertaken
| 02SL - Stations (LUL) | Cxxx-NCR-000280 | NCR | ETH Damage to L-1 Soffit |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-11-25 | 2016-11-25 12:53 | 0 | 2016-09-08 15:06 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | During the excavation of L-2 some damage occurred in localised areas to the soffit. Where the damage is determined to be deeper than 10mm, the following remedial procedure will be undertaken
| 02SL - Stations (LUL) | Cxxx-NCR-000281 | NCR | ETH Damage to L0 Soffit |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2017-05-30 | 2017-06-01 15:59 | 2 | 2016-09-08 15:17 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | During the excavation of L-1 some damage occurred in localised areas to the soffit. Where the damage is determined to be deeper than 10mm, the following remedial procedure will be undertaken
| 02SL - Stations (LUL) | Cxxx-NCR-000282 | NCR | ETH Damage to L0 __ Channels |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-12-16 | 2016-12-16 14:01 | 0 | 2016-09-08 15:36 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | During the excavation of L-1 some damage occurred in localised areas to the __ Channels cast into the soffit
| 02SL - Stations (LUL) | Cxxx-NCR-000283 | NCR | ETH Level -4 Incorrect Installation of RC Lintel |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-11-30 | 2016-11-30 15:04 | 0 | 2016-09-13 11:36 | Architectural - Brickworks/Blockworks | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The cast in-situ RC lintel at L-4, in Lobby 5/097, has been installed 20mm too high and without the required notch detail at the end (as per attached documents and photos). The concrete has been poured flush with the cleat, rather than having the 20mm step down required to complete the fire board detail, as per detail 1, 40103 (see attached).
| 02SL - Stations (LUL) | Cxxx-NCR-000284 | NCR | WTH ES1 Mass Fill Stair Finish |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2016-10-07 | 2016-10-06 13:23 | -1 | 2016-09-21 07:41 | Civil - Civil Engineering General | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Personnel Error - Inattention to detail | Completed |  | Due to the location of super slims soldiers required to support the riser formwork (refer to approved temporary works design Cxxx-SKC-C-CER-Cxxx-50184 C01), concrete was unable to be finished beneath each soldier. Post striking of formwork it was identified the finish beneath each RMD solider did not meet the requirement of KF10.3218 b).
| 02SL - Stations (LUL) | Cxxx-NCR-000285 | NCR | ETH MPS L-5 Damaged Drainage Gullies in Slab 1 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2017-06-30 | 2017-01-10 17:26 | -171 | 2016-09-26 14:49 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | During works in the MPS on L-5, damage occurred to the flanges of 2 No. gullies at the locations shown on attached drawings Cxxx-SKC-P-DDA-Cxxx-52161 Rev P12 and Cxxx-SKC-P-DDA-Cxxx-52164 Rev P08.
| 02SL - Stations (LUL) | Cxxx-NCR-000286 | NCR | ETH IW66 on Mezzanine Slab out of tolterance |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-02-28 | 2018-12-12 17:41 | 287 | 2018-11-01 09:53 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please see attached as-built for the IW66 on the L-2 Mezzanine Slab. This sketch shows the position of the wall being out of tolerance as per the KF10 tables
| 02SL - Stations (LUL) | Cxxx-NCR-000287 | NCR | ETH L-4 IW33 (Western End) Finishing Defect |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-04-01 | 2018-10-26 13:55 | 208 | 2016-09-28 14:06 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | During works on level -4, a section on the western end of IW33, beyond the blockwork wall has been stained with a construction material (see attached photo L-4 IW33.jpg). The location is highlighted on the attached drawing Cxxx-SKC-A-DDL-Cxxx-69141-P09 CW Mark-Up. This is not in accordance with Architectural Specification JE20 - Finishes to In-Situ Concrete, which states in clause JE20.1209 that for Type CON-131 Ordinary In Situ Concrete Finish, "Variation in colour resulting from the use of an impermeable form lining is permitted but the surface shall be free from discolouration due to contamination or grout leakage."
| 02SL - Stations (LUL) | Cxxx-NCR-000288 | NCR | P&T Code 3 MCR - __ HST Stud Anchors |  | Contr | COS | BOS - Bond Street Station (West) |  | 2016-11-30 | 2016-10-11 16:24 | -50 | 2016-10-10 15:59 | Architectural - General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | It was found that the MCR (Cxxx-SKC-A-LRC-Cxxx-50036) for the __ HST Stud Anchors was Code 3 during an inspection (Cross passage 5) of the installation of the steel support system.
| 02SL - Stations (LUL) | Cxxx-NCR-000289 | NCR | WTH - Damaged Firestopping |  | Contr | COS | BOS - Bond Street Station (West) |  | 2018-05-31 | 2018-09-25 08:22 | 117 | 2016-10-11 07:52 | Mechanical - Mechanical Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Firestopping was installed around dampers going into rooms from the circulation areas. However the dampers were not completed through to the otherside of the circulation area at the time of the installation of the firestopping. When the dampers were then connection to the other side of the circulation area it moved the firestopping and cracked it on the surface around the damper.
| 02SL - Stations (LUL) | Cxxx-NCR-000291 | NCR | Mezz Slab U-Wall L-2, missing door opening |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-10-30 | 2017-09-11 08:01 | -49 | 2016-10-14 14:39 | Civil - Civil Engineering General | 5000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Personnel Error - Inattention to detail | Completed |  | A doorway is missing on NLB IW1 (U-Wall on Mezz Slab) on L-2. See attached mark up showing the location of which the wall is missing (Cxxx-__-S-DDL-Cxxx-52124) and ETH-NCR-L-2-Doorway-Markup. This wall is a NLB wall, and contains mesh only.
| 02SL - Stations (LUL) | Cxxx-NCR-000292 | NCR | ETH MPS Level -5 IW61 lacer bars lapping issue adjacent GL Y/6 |  | Contr | COS | BOS - Bond Street Station (West) |  | 2016-11-18 | 2016-10-31 12:31 | -18 | 2016-10-20 11:53 | Civil - Structural Engineering | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | On the south face of IW61, where it connects with Lining Wall 6 (i.e. the east end of IW61), the top 15 No. of the horizontal starter bars which are coupled into the Lining Wall (BM E31 on dwg 50802) have been cast approx. 80mm out of position This means that the coupled bar does not lap with the horizontal lacer bar (BM52 and 26 - both B16).
| 02SL - Stations (LUL) | Cxxx-NCR-000293 | NCR | MPS L-5 IW52 Pour 2 - Trimmer bars Missed |  | Contr | COS | BOS - Bond Street Station (West) |  | 2016-12-09 | 2016-11-15 09:26 | -24 | 2016-10-28 09:19 | Civil - Structural Engineering | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During inspection of MPS L-5 IW52 Pour 2 it was found that the diagonal and horizontal trimmer bars had not been fixed above the temporary hole Detail B as per referenced DWG: Cxxx-SC-S-DWG-Cxxx-50802 See attached pre-pour inspection MPS L-5 IW52 CRL Inspection 27-10-16
| 02SL - Stations (LUL) | Cxxx-NCR-000294 | NCR | WTH, Lvl 0, Central section kickers |  | Contr | COS | BOS - Bond Street Station (West) |  | 2016-11-30 | 2016-11-08 09:19 | -22 | 2016-10-31 10:46 | Civil - Structural Engineering | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Kickers cast at WTH Central Area for the Ground Floor Walls
| 02SL - Stations (LUL) | Cxxx-NCR-000295 | NCR | ETH MPS L-4 WB1 Reinforcement clash. |  | Contr | COS | BOS - Bond Street Station (West) |  | 2016-11-30 | 2016-11-17 10:43 | -13 | 2016-10-31 15:08 | Civil - Structural Engineering | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | have highlighted the FF1 B40 E102 bars clash with the FF B32 E121 lining wall starters. This clash extends across the first 12 no. bars as indicated on the attached drawing
| 02SL - Stations (LUL) | Cxxx-NCR-000296 | NCR | Concrete strength more than 20N/mm2 above the specified minimum cube strength |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-03-16 | 2017-02-15 10:13 | -29 | 2016-11-09 10:50 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | The attached concrete strength results for some of the WTH levels -1 and -2 non load bearing walls are more than 20N/mm2 above the specified minimum cube strength. The concrete results are all from the same concrete mix noted in the referenced MCR: Cxxx-SKC-C-LRC-Cxxx-50005
| 02SL - Stations (LUL) | Cxxx-NCR-000297 | NCR | ETH level-3 cracks to the lining walls |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-08-25 | 2017-12-01 10:24 | 98 | 2016-11-08 12:56 | Civil - Structural Engineering | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Further to a post-pour inspection carried out by (__) and CRL (__) on 05.10.16, a number of cracks in the Lining Walls at L-3 were noted. An initial crack survey was carried out by CRL (__) and Cxxx and they have advised that a monitoring period of 3 months is required to determine whether or not the cracks are stable.
| 02SL - Stations (LUL) | Cxxx-NCR-000298 | NCR | Temporary fire main in WTH |  | Contr | COS | BOS - Bond Street Station (West) |  | 2016-12-23 | 2016-12-21 12:45 | -2 | 2016-11-08 08:03 | Fire - Fire Systems & General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | The temporary fire main in the western ticket hall level 0 to -5 has been installed as per the attached Drawings: TFP-DRG_OPP05545-512 (C2); TFP-DRG_OPP05545-411 (C3), TFP-DRG_OPP05545-211 (C4); TFP-DRG_OPP05545-111 (C4) TFP-DRG_OPP05545-011 (C3); TFP-DRG_OPP05545-002 (C6) without an approved temporary works design check certificate..
| 02SL - Stations (LUL) | Cxxx-NCR-000299 | NCR | ETH Level -5 Construction of Plinth in KD23 |  | Contr | COS | BOS - Bond Street Station (West) |  | 2016-12-23 | 2016-12-08 12:57 | -15 | 2016-11-09 11:08 | Civil - Structural Engineering | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The unistrut foundation in KD23 at L-5 shown on attached drawing Cxxx-SKC-A-DDD-Cxxx-35804 Rev P08 (Detail 3) was constructed on 07.10.16. This was constructed beyond the tolerances provided in specification KF10 Appendix A (±10mm). An as-built survey was undertaken on 02.11.16 and the plinth was found to be out of tolerance according to the KF10 specification - see as-built survey drawing attached. -------------------------------------------------------------------------------------------------------- Part II:- Consequent to the above, it became apparent that there was a further drawing detail not issued to the Construction team at the time of installation. This detail issued under PMI Cxxx-PMI-01176 with drawing Cxxx-ALC-C-DDD-Cxxx_5-00404 clearly illustrates the required tolerances for the RC plinth to be constructed to +/- 3mm. This was not issued to until 29/10/2016 when the construction had already taken place on 07/10/2016. Previous opportunities for being alerted to the tight tolerances were as follows: 1- Details notified via Cxxx-PMI-00851 and the interface Document Cxxx-ALC-K1-STP-Cxxx-50010 issued on 04/11/2015. Within this document was a table illustrating "Key Requirements" including the detail that the "HV Switch room floor was to have cast in __ for securing the HV switchgear. The Contractor will determine the design/layout requirements and communicate these to the Site Specific Delivery Contractor, who will install the __ rails. Overall switch room floor level tolerances to be +/- 3mm. " The drawing DDD-Cxxx-35804 Rev P08 (Detail 3) issued and used to construct the plinths in RC concrete on 07/10/2016 did not include these tolerances clearly enough for a site team familiar with working to Reinforced Concrete (KF10 specification) structural concrete tolerances. 2 - A previous PMI Cxxx-PMI-00799 “Additional HV Room Works” was issued to 24/09/2015. Elements of this instruction were discussed in Cxxx-RFI-002350 with the designer (__ RFI 1224) in April 2016.
| 02SL - Stations (LUL) | Cxxx-NCR-000300 | NCR | Architectural Benchmarks |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2016-11-29 | 2016-11-30 15:09 | 1 | 2016-11-15 18:50 | Architectural - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | Cxxx-SKC-C-TSC-Cxxx-50013 Revision 3.0 lists the current status of the architectural "quality benchmarks" to be submitted by the contractor and inspected and accepted by CRL for the project. This version of the document lists the benchmarks that are currently outstanding for elements of the works that have been completed on site. As the benchmarks is a hold point on site for quality of finish, CRL are concerned that works have progressed that do not meet the project and quality requirements of the project. The contractor is to extract a list of the missing benchmarks, establish retrospectively the benchmark to be recorded and inspected and propose a list of mitigation measures when the quality of the works does not meet CRL expectations. Concrete and blockwork are examples of where benchmarks are not in place.
| 02SL - Stations (LUL) | Cxxx-NCR-000301 | NCR | ETH L-5 Fire Lift Channel |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-01-31 | 2016-12-23 12:44 | -39 | 2016-11-21 16:23 | Mechanical - Public Health Engineering | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | have identified that the P-traps cast within the L-5 slab are in the incorrect position. This will not allow the installation of the custom __ channel as detailed on 670-39229-01A. Please see attached marked up Builders work drawing for Level -5. This highlights the as-built dimension of the fire fighter lift channel position. It can be seen that the P-traps have not been cast as per design. The two p-traps have been cast too close to the lift walls therefore reducing the distance of the return channels to approximately 450mm. (Detailed As-built attached 'ETH Drainage Channel L-5)
| 02SL - Stations (LUL) | Cxxx-NCR-000302 | NCR | PTW Wall above Platform SW W30 - SW W37 - Grout Not Achieveing Design Strength |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-06-02 | 2017-04-03 14:49 | -60 | 2016-11-24 08:10 | Civil - Structural Engineering | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The cube results of the __ grout that is placed in the top lift of the walls above platform slab SW W30-37 (refer to Cxxx-PMI-845) has not reached the design strength of 40N/mm2. The 28 day result only achieves 33.4N/mm2. See attached Grout cube test result EN CSJ-101149-2016-03-10-8422
| 02SL - Stations (LUL) | Cxxx-NCR-000303 | NCR | Damaged Drainage Pipe in Room 6/914 at L-5 |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-02-24 | 2016-12-23 12:43 | -63 | 2016-11-25 08:25 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Drainage pipe in the slab soffit (as highlighted in attached photo) finishes flush with the underside of the slab and is therefore not in accordance with Detail 5 of drawing Cxxx-SKC-P-DDD-Cxxx-25111 rev P03 - the cast-in cavity drainage exiting underside of slab. The location of the drainage pipe has been highlighted on attached drawings Cxxx-SKC-P-DDA-Cxxx-52140 rev P03 and Cxxx-SKC-M-DDA-Cxxx-69140 rev P06.
| 02SL - Stations (LUL) | Cxxx-NCR-000305 | NCR | Couplers in Lining Wall L-4 MPS |  | Contr | COS | BOS - Bond Street Station (West) |  | 2016-12-16 | 2016-12-16 17:24 | 0 | 2016-11-30 13:01 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please see attached location mark up, MPS L-4 LW4 Coupler Survey and photo showing the location of the couplers. They have been cast out of position. There are 2no. couplers that will give only have 20mm cover to the front face of reinforcement once the horizontal bars has been installed. There are other affected couplers where the required cover will be less than 35 mm There are also bars indicated on the survey where there are bars with excessive cover.
| 02SL - Stations (LUL) | Cxxx-NCR-000306 | NCR | ETH L-4 As-built Survey of Blockwork Walls (tolerances of openings not to Specified requirements) |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-08-31 | 2018-09-11 08:36 | 11 | 2017-01-19 13:51 | Architectural - Brickworks/Blockworks | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The ETH L-4 Blockwork walls have been constructed using Rev 26 of the opening schedule Cxxx-SKC-A-TSC-Cxxx-50014. The attached as-built survey of openings in L-4 blockwork walls shows where openings are not within tolerance requirements stated in JF10.3218. Furthermore, as-built positions of blockwork walls that are not within tolerance stated in JF10.3218 are shown in the attached L-4 GA drawing.
| 02SL - Stations (LUL) | Cxxx-NCR-000307 | NCR | P & T - Break out of structural slab around drainage and ducts various areas. |  | Crossrail | PDP | BOS - Bond Street Station (West) |  | 2017-03-31 | 2017-03-27 16:20 | -4 | 2016-12-07 10:20 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | Structural slab has been broken out around ducts and hydro duct drainage at various location in the platform areas. It is due to Cxxx not having the correct information to build the ducts to the correct level. Crossrail were not informed of the break out of these areas. It was discovered in post pour check. Anoush has photographs of the damaged items.
| 02SL - Stations (LUL) | Cxxx-NCR-000308 | NCR | ETH - VD3 - Crack in tunnel soffit |  | Crossrail | PDP | BOS - Bond Street Station (West) |  | 2017-04-30 | 2017-04-11 17:02 | -19 | 2016-12-07 10:37 | Civil - Civil Engineering General | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | During post pour inspection a crack was observed in the tunnel lining. Potential water ingress was observed.
| 02SL - Stations (LUL) | Cxxx-NCR-000309 | NCR | ETH MPS Lining Wall 4 level -4 Cover Issues |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-03-31 | 2017-02-17 16:05 | -42 | 2016-12-08 16:52 | Civil - Structural Engineering | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A potential cover issue was noted during an inspection of the reinforcement to the ETH MPS west end of Lining Wall 4 level -4. Refer attached photos MPS, Lvl-4, LW4 west end - Pic 1 & Pic2 and mark up showing the results of the initial cover survey on Lining Wall 4 in the MPS L-4 as per DWG Cxxx-SKC-S-DWG-Cxxx-50194.
| 02SL - Stations (LUL) | Cxxx-NCR-000310 | NCR | CH2 (Part 1) Structural Slab - Not Achieving Design Strength |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-02-03 | 2017-01-24 15:07 | -10 | 2016-12-09 12:37 | Materials - General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The cube results of the C32/40 concrete structural slab in CH2 (Part 1) (refer to attached __ Lab. Ref. No: EN CSJ-93330-2015-11-20-66612) show that the structural slab has not reached the design strength of 40N/mm2. The 28 day result only achieves 37.8N/mm2 and 37.9N/mm2. There are no spare cubes to crush. See attached Tunnels and Platforms Pour Sequence [Rev 4.0] and CH2 - Part 1 marked up showing pour location.
| 02SL - Stations (LUL) | Cxxx-NCR-000311 | NCR | ETH L-5 As-built Survey of Blockwork Walls (tolerances of openings -not to Specified requirements) |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-06-15 | 2018-06-12 09:35 | -3 | 2016-12-21 21:20 | Architectural - Brickworks/Blockworks | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The ETH L-5 Blockwork walls have been constructed using Rev 28 of the opening schedule Cxxx-SKC-A-TSC-Cxxx-50014. The attached as-built survey of openings in L-5 blockwork walls shows where openings are not within tolerance requirements stated in JF10.3218.
| 02SL - Stations (LUL) | Cxxx-NCR-000312 | NCR | CH2 Escalator Sump Structural Slab Surface Finish |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-05-05 | 2017-04-19 15:26 | -16 | 2016-12-22 10:08 | Civil - Structural Engineering | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | CH2 Escalator Sump Structural Slab topping has a mesh “pattern” throughout the entirety of the slab due to plastic settlement. A cover survey has been undertaken. See attached cover meter survey (CCF16016_0002) and photos IMG_2288 &IMG_2289
| 02SL - Stations (LUL) | Cxxx-NCR-000313 | NCR | 'CON-121' Finish to ETH Stair Walls and Soffit |  | Contr | COS | BOS - Bond Street Station (West) |  | 2019-03-31 | 2018-12-07 11:28 | -114 | 2017-02-07 11:55 | Architectural - Walls | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The stairs have been cast and made good but do not meet the required finish of ‘CON-121'. There are a number of areas where the following specification JE20.1208 clauses are not met: b) ix) -Abrupt irregularities greater than 1mm b) xi) - Gradual irregularities, expressed as maximum permissible deviation from a 1m straightedge, greater than 3mm. d) i) -Areas of inconsistent colour. d) v) -Finish not as the agreed sample panel See attached photos – Pics 1 to 15 and Submittal 115 - ETH CON 121 Benchmark
| 02SL - Stations (LUL) | Cxxx-NCR-000315 | NCR | WTH, Lvl 0.5, Wall W-W21 missing starter bars |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-03-31 | 2017-01-19 16:53 | -71 | 2017-01-06 13:36 | Civil - Structural Engineering | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | During the pre-pour inspection of the reinforcement for Wall W-W21 it was noted that 10 No. bar mark 12, 12mm diameter reinforcement bars had been drilled and fixed. See attached photos and marked up Drawing Cxxx-SKC-S-DWG-Cxxx-50489. The drill and fix was carried out in accordance with Cxxx-FCD-000523. However prior agreement for the drill and fix had not been sought.
| 02SL - Stations (LUL) | Cxxx-NCR-000316 | NCR | WTH - Load & Non Load Bearing Walls Lvl -4 - Missing concrete cube Lab Test Report Results |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2017-04-30 | 2017-03-28 15:16 | -33 | 2017-01-06 19:34 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | ITP Record Package Submission "WTH - Load & Non Load Bearing Walls Lvl -4" (Lvl-4 ITP Record Pack:Cxxx-SKC-O4-LRC-Cxxx-50134) found in review to have a few concrete cube test results Certificates that have not been located and entered into the Records pack - for pours as follows: >1 / Wall 4/B-F Non Load Bearing wall (Pour Ref 2A) from Delivery Note Ticket No for truck 053441 on pour date 19/12/2015. Corresponding Concrete Laboratory test report for Compressive Strength of Concrete cubes - not located. Latterly understood that the site Engineer forgot to take a sample set - for this particular pour. >2 / Walls W-W-33 and W-W-35 Load Bearing Walls (both pour refs 1A) from Delivery Note Ticket No for truck 059362 and 059364 on pours dated 19/01/2016. Corresponding Concrete Laboratory test report for Compressive Strength of Concrete cubes - not located. >3 / Walls A-B/2-3 and A/1-2 Non Load Bearing Walls (both pour refs 1A) from Delivery Ticket No for truck 54960 on pour date 07/01/2016. Corresponding Concrete Laboratory test report for Compressive Strength of Concrete cubes - located as Lab Ref No: CSJ 98593. Cube MD3E spare not tested to provide a second 28 day nor 56 day test.
| 02SL - Stations (LUL) | Cxxx-NCR-000317 | NCR | WTH, Level 0.5 Gridline G to J Cover to Beam C |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-03-31 | 2017-02-08 16:36 | -51 | 2017-01-09 15:14 | Civil - Structural Engineering | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Reduced cover to beam C 600mm west of W-W-13 was identified prior to the casting of level 0.5+ slab on Cxxx-FCD-000515. PTR response stated; “Alternatively if the concrete has yet to be cast, an increased cover is preferable to achieve the design level”.
| 02SL - Stations (LUL) | Cxxx-NCR-000318 | NCR | ETH MPS L-3 NW Slab Eazistrip omission |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-08-30 | 2017-07-11 12:22 | -50 | 2017-01-11 08:19 | Civil - Structural Engineering | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate resources | Completed |  | Approximately a 5m section of Eazistrip has been omitted from the pour of the L-3 slab. This is detailed on Cxxx-SKC-S-DWG-Cxxx-50153-C01. Please see attached Cxxx-SKC-S-DWG-Cxxx-50153-C01-LS-Markup-100117 for area of Eazi strip omitted
| 02SL - Stations (LUL) | Cxxx-NCR-000319 | NCR | ETH L-1 IW40 West Face North End - Lack of Cover |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-03-31 | 2017-02-08 16:37 | -51 | 2017-01-16 09:11 | Civil - Structural Engineering | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | At L-1 IW40 West Face North End one exposed rebar has been identified as shown in images 'L-1 IW40 Lack of Cover Image 1' and 'L-1 IW40 Lack of Cover Image 2'. See attached Cxxx-SKC-S-DWG-Cxxx-50097-C02 JL Mark Up's for location. The required cover for IW40 is 30mm as per drawing Cxxx-SKC-S-DWG-Cxxx-50097-C02. The attached cover meter shows the extent of the reduced cover.
| 02SL - Stations (LUL) | Cxxx-NCR-000320 | NCR | ETH- exposed rebar on level-2 slab |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-03-31 | 2017-02-13 15:53 | -46 | 2017-01-24 08:39 | Civil - Structural Engineering | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A small area of exposed Rebar in the slab on L-2 in the ETH, was noted in the post pour inspection (See attached ETH, Lvl-2 slab area 1 post pour, ETH, Lvl-2 slab area 1 post pour pic and Exposed Bar Location ) The attached Cover survey shows the cover around the exposed rebar and a remedial works will need to take place.
| 02SL - Stations (LUL) | Cxxx-NCR-000321 | NCR | Use of P Status drawings during MPS L-3 Slab Construction |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-03-31 | 2017-01-18 15:09 | -72 | 2017-01-13 11:11 | Civil - Structural Engineering | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | During the construction of the Level -3 permanent slab in the MPS, reinforcement drawings were used which were not approved Construction Status drawings. All of the drawings had previously been approved as P status drawings, but the up-rev to C status drawings hadn't been fully closed out. Referenced drawings Cxxx-SKC-S-DWG-Cxxx-50288 Rev P02 and Cxxx-SKC-S-DWG-Cxxx-50153 Rev P03
| 02SL - Stations (LUL) | Cxxx-NCR-000322 | NCR | Station Entrance Gates - Mock up |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2017-08-30 | 2018-10-04 13:56 | 400 | 2017-04-03 17:18 | Architectural - Doors | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | A mock-up has been prepared for the Main Station Entrance Gates at __’s doors. Site inspections have taken place on a number of occasions with various members of the CRL Team being invited to attend. Attendees included LUCT Premises and Project Engineers, CEG Architects and CRL Security Advisor. Inspections took place on the 15th December 2015, 16th January 2016, 16th August 2016 and 16th October 2016. Additional inspections took place with __ CRL Security Advisor. During this process Inspection Request Forms and Inspection Records were not presented or updated to record and address comments made on the mock up as the design progressed. Over a period of time the entrance gates have been developed without attendance of the Cxxx architects. We believe that the design has been significantly developed without the appropriate input resulting in a design that does not reflect the original Works Information design intent and address the concerns identified by the IM on the Stage E design.
| 02SL - Stations (LUL) | Cxxx-NCR-000323 | NCR | ETH MPS Level -3 Eazistrip in Waling Beam WB4 |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-02-28 | 2017-03-02 15:00 | 2 | 2017-01-18 10:53 | Civil - Structural Engineering | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Drawing Cxxx-SKC-S-DWG-Cxxx-50846 section 4-4 shows Eazistrip cast in to the upper surface. This is a drawing error as drawing Cxxx-__-S-DDL-Cxxx-52132 shows no requirement for upstand in this location. In order to be compliant with the permanent works design, the eazistrip was removed, although this wasn’t communicated prior to pouring concrete. See attached Cxxx-__-S-DDL-Cxxx-52132 Rev C07 mark up and Cxxx-SKC-S-DWG-Cxxx-50846-C02 mark up
| 02SL - Stations (LUL) | Cxxx-NCR-000324 | NCR | ETH Missing Kwikastrip in L-3 MPS Slab |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-09-30 | 2017-09-23 15:02 | -7 | 2017-01-19 15:49 | Civil - Structural Engineering | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | All of the Kwikastrip has been left out of the MPS L-3 slab which is detailed on the referenced drawings. This NCR has been raised for not complying with the Construction drawings. See attached marked up drawing Cxxx-__-S-DDL-Cxxx-52130-MPS-L-3-Missing-Kwikastrip-Locations.
| 02SL - Stations (LUL) | Cxxx-NCR-000325 | NCR | Level -3 walls at SLD 2 connection into LU link Passage |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-08-31 | 2017-10-12 09:52 | 42 | 2017-01-19 08:02 | Civil - Structural Engineering | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The walls at level -3 were originally blockwork. These walls were then to be changed to RC under PMI 1270. The attached Drawing Cxxx-SKC-S-DWG-Cxxx-50169 Rev C01 was produced and approved prior to works commencing. However the return wall into the buttress was not detailed as RC and was left as blockwork as shown on Cxxx-SKC-A-DDL-Cxxx-19130 (attached). It was later agreed informally that this wall would be required to be changed to a non load bearing RC wall but was not agreed formally prior to the wall being poured. The detail at the return into the buttress can be seen on the sketch shown on Cxxx-SKC-S-DWG-Cxxx-50169 Rev C01. The connection detail into the buttress was a copy of the connection into the Link Passage area i.e. there was no drill and fix connection, the concrete was poured against the buttress and u-bars were installed at the end of the wall - also shown on the sketch on Cxxx-SKC-S-DWG-Cxxx-50169 Rev C01 (attached). It was later found that an opening should have been formed at the top of this wall in accordance with the blockwork opening schedule. This section of wall was cored without formal acceptance prior to carrying out the work. The size of the opening was 480mm from the soffit of the slab over the full length of the wall. The opening was cut with a number of cores and renderoc was applied to the reinforcement. The area will be fully sealed by firestopping after the services are installed.
| 02SL - Stations (LUL) | Cxxx-NCR-000326 | NCR | Use of Unapproved Drawings in KD14 and KD15 |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-02-28 | 2017-01-30 17:53 | -29 | 2017-01-19 11:52 | Electrical - General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | During a site inspection it was found that the drawings pinned to the door in KD14 and KD15 were not acknowledged in anyway as being issued for construction. The approved drawing for these works are Cxxx-SKC-O-RGN-Cxxx-50158; By Exception 63 – MEP ETH KD 14 & KD 15 Installation of MEP Services within MCC 3/764 & FCR 3/903 Level -2 As both these rooms were in the initial stage of the MEP installation, no variations were found between the approved (BE stamped) and non-approved drawings used for the installation. The works installed are in accordance with the approved drawings.
| 02SL - Stations (LUL) | Cxxx-NCR-000327 | NCR | ETH CMS route mass concrete fill poured with unnapproved details |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-03-31 | 2017-02-10 11:13 | -49 | 2017-01-20 08:58 | Civil - Structural Engineering | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | The CMS route concrete mass fill in ETH MPS L-5 CMS route was poured before having a formal approval of the hydroduct details around the cable ducts that were extended from AP3A, AP3B, Slab 8, Slab 9 and Slab 5. received informal approval of these details from Cxxx before the concrete pour. See attached photos of installed works.
| 02SL - Stations (LUL) | Cxxx-NCR-000328 | NCR | ETH IW33 L-2 - Bulge in South Face |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-04-03 | 2017-02-16 11:32 | -46 | 2017-01-20 15:53 | Civil - Structural Engineering | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following a post-pour inspection with CRL, __s, and , it was found that there was a slight bulge in an infill section of IW33 south face, within the Air Corridor Pressurisation Riser. See attached Post pour pics 1,2 and 3 and NCR 328 IW L-2 Bulge in South face As Built. The location is marked up on the attached GA drawing Cxxx-SKC-A-DDA-Cxxx-52121 SB Mark-up
| 02SL - Stations (LUL) | Cxxx-NCR-000329 | NCR | ETH Lift 1 L-4 and L-5 Door openings |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-08-30 | 2017-09-09 11:25 | 10 | 2017-01-20 16:23 | Civil - Structural Engineering | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The door openings at L-5 and L-4 within Lift 1 ETH have been cast to the wrong revision of the GA and hence are 1325mm wide rather than the later 1250mm. L-4 Drawing constructed as Cxxx-__-S-DDL-Cxxx-52153-C05 L-5 Drawing constructed as Cxxx-__-S-DDL-Cxxx-52143-C04
| 02SL - Stations (LUL) | Cxxx-NCR-000330 | NCR | ETH - Cleat position in L-5 Lobby 6/092 W |  | Contr | COS | BOS - Bond Street Station (West) |  | 2018-04-01 | 2018-10-03 12:55 | 185 | 2017-01-23 09:48 | Architectural - Masonary | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The cleat bracket installed to support Kingstone lintel for BWIC 6 in room 6/092 West wall (see attached drawing for Location of Bracket) is a type 1 which has one centrally located hole. The blockwork subcontractor continued to hit rebar whilst drilling into the RC wall, resulting in the cleat being set off centre. See attached installed bracket photo. The installed cleat has 5mm of block overhang on the western side and 35mm over hang on the Eastern side of the wall, which is not compliant with 20mm requirement to fireproof the steel bracket
| 02SL - Stations (LUL) | Cxxx-NCR-000331 | NCR | ETH - Plunge Column Infill L-2 Slab |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-03-31 | 2017-02-06 14:59 | -53 | 2017-01-23 16:34 | Civil - Structural Engineering | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Tie bar was left exposed in the top of the plunge column infill on L-2 slab. See attached Plunge Column Infill Location and Infill photo The attached "Reinforcement Cover Survey L-2 Infill" shows that the reinforcement is as per design.
| 02SL - Stations (LUL) | Cxxx-NCR-000332 | NCR | ETH & WTH Dust seal applied to rendered walls |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-06-30 | 2017-06-14 09:39 | -16 | 2017-03-03 10:35 | Architectural - Masonary | 0 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Certain walls and soffits in the ETH and WTH have been dust sealed which require render to be applied to them. Surfaces include RC and blockwork. PT 186 Dust Sealer: Prosocco Weatherseal Siloxane PD was the product used for dust sealing the surfaces and it is envisaged that testing for adhesion is required ahead of application without the need for additional mechanical fixing (metal lathe that will increase wall thickness). Rooms Affected: WTH: 6/409, 6/408, 6/410, 6/415, 6/634, 6/317, 6/316, 6/416, 6/047, 3/086, 2/402, 2/406, 2/318. ETH: 6/413 and 6/414
| 02SL - Stations (LUL) | Cxxx-NCR-000334 | NCR | No approval status for Level-6 Co-Ordinated Services Drawing |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-08-30 | 2018-02-26 16:12 | 180 | 2017-02-02 15:16 | Fire - Suppression | 500 |  | Planning | Repair | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | It was observed during the Surveillance of the Platform Invert Level Fire Main Installation that the 150mm dia. Fire main in the Eastbound and Westbound platform inverts has been installed as per __’s assured drawings and Level -6 Co-Ordinated Services Layout Sheet 1 of 7: Cxxx-SKC-Z-DWG-Cxxx-50001 was used for additional dimensional information. The Coordinated services drawing Cxxx-SKC-Z-DWG-Cxxx-50001 is based on the __ drawings. However, there is no record of approval for this drawing by __ as per Cxxx Subcontractor Design Procedure Cxxx-SKC-Z-GUI-Cxxx-50001,which is part of the Cxxx - Design Management Plan Cxxx-SKC-N2-STP-Cxxx-50003
| 02SL - Stations (LUL) | Cxxx-NCR-000335 | NCR | ETH & WTH Level -4 and ETH Level -5 missing Ductwork access doors |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-04-28 | 2017-04-21 10:32 | -7 | 2017-01-30 17:00 | Mechanical - Mechanical Engineering General | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | It was identified during a site inspection of ETH Level -4 and ETH Level -5 that there were a number of access doors not installed on the duct work as per the assured design drawings. See attached Annotated Cxxx-SKC-M-DDA-Cxxx-52245 and Annotated Cxxx-SKC-M-DDA-Cxxx-52246 for examples.
| 02SL - Stations (LUL) | Cxxx-NCR-000336 | NCR | ETH MPS L-3 Slab - Cxxx-FCD-555 not agreed before pour. |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-03-31 | 2017-02-20 15:24 | -39 | 2017-01-31 13:17 | Civil - Structural Engineering | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | noted that the area of lining wall 4 at the L-3 slab level was not correctly detailed. In addition it had not considered the connection of the lacers to the slab. Please see attached marked up drawings with changes made onsite. This increases the area the B20 links and B32 FF3 bars extent. It also adds couplers to the slab construction joints. As this area was poured with the 1.5m section of lining wall have removed the additional coupler joint shown for E106 on the drawing. Please could you confirm this is acceptable
| 02SL - Stations (LUL) | Cxxx-NCR-000337 | NCR | Ductwork insulation materials without approved MCR |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-05-31 | 2017-04-20 11:23 | -41 | 2017-02-01 13:29 | Mechanical - Mechanical Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | During a site inspection in the WTH, Level-5 PES extraction ductwork insulation works, it was found that there were no approved MCR's on eB for the __ insulation and Insulation tape. Update 19/04/2017 The applicable MCR's CRL-MCR-004505 and CRL-MCR-004506are now code 1 and have been linked to this NCR
| 02SL - Stations (LUL) | Cxxx-NCR-000338 | NCR | ETH MPS L-3 Lining Wall 2 - Cover Issue. |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-08-30 | 2017-09-25 14:37 | 26 | 2017-02-01 13:49 | Civil - Structural Engineering | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Please see attached location mark up, MPS L-3 LW2 Coupler Survey and photo showing the location of the couplers. They have been cast out of position. There are 9no. couplers that will not give the required cover and will be less than 45 mm. Please note that within this area 71 coupers have been installed along a 6.8m stretch the fore 3 no. bars are additional to the 100 centre requirement.
| 02SL - Stations (LUL) | Cxxx-NCR-000339 | NCR | ETH Level-5 Lining Wall 7 Grid F/4 - Cracks in Wall |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-09-30 | 2018-04-23 09:49 | 205 | 2017-02-06 11:41 | Civil - Structural Engineering | 2000 |  | Design | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | The attached photo (IMG_2804) shows a number of cracks in L-5 Lining Wall 7 adjacent GL F/4. These cracks were observed by as having water ingress in November 2016. They are still showing signs of water ingress.
| 02SL - Stations (LUL) | Cxxx-NCR-000340 | NCR | ETH Level-4 Lining Walls 1&7 GL E/4 & F/4 - Cracks in Wall |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-09-30 | 2018-04-23 09:53 | 205 | 2017-02-08 08:16 | Civil - Structural Engineering | 2000 |  | Design | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | The attached photos show a number of cracks showing water ingress in L-4 Lining Walls 1 & 7 GL E/4 and F/4 . No water ingress was present in June 2016 when post pours of the lining walls were carried out. See attached Locations of Cracks in L-4 Lining Wall
| 02SL - Stations (LUL) | Cxxx-NCR-000341 | NCR | WTH Wall W-W-8 level 0 to 0.5 changes |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2017-04-30 | 2017-04-22 11:41 | -8 | 2017-02-27 16:41 | Structural Engineering - Reinforcement | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The Contractor changed some construction details to wall W-W-8 between levels 0 to 0.5 at the WTH without agreeing them prior to pour. See 'Cxxx-NCR-000341 Attachment.docx.' Cxxx to review each of the points below to confirm if we may use-as-is: 1. Further to Cxxx-RFI-002611 and Cxxx-FCD-000480, the Contractor fixed trimming steel to wall W-W-8 CMS boxes in accordance with attached 'W-W-8 CMS Trimming detail sketch.pdf.' Also see 'WTH, Lvl 0, Wall W-W-8 north end - Pic 1' attached. 2. Further to Cxxx-RFI-002795, the Contractor constructed the west elevation lift wall at level 0 central core at the WTH in reinforced concrete instead of non-load bearing masonry. This was fixed in accordance with attached 'W-W-8 lift shaft RC Sketch.pdf.' Also see 'WTH, Lvl 0, Wall W-W-8 nibs - Pic 1 to 4' and 'WTH, Lvl 0.5, W-W-8 re-inspection - Pic 1.' The drill and fixed bars were drilled to a depth of 100xdiameter+100mm's using __ Hit HY200a resin. 3. Either side of the lift wall section for wall W-W-8, (in between walls W-W-14 and W-W-15) the Contractor installed: A/ 20mm diameter threaded L-bars to connect on to later in wall W-W-14. See pic 'WTH, Lvl 0 - Wall W-W-8 - Pic 1' B/ 20mm diameter threaded straight bars to connect to later in column C1. See pics 'WTH, Lvl 0, Column C1 - Pic 2, 4, 6.'
| 02SL - Stations (LUL) | Cxxx-NCR-000342 | NCR | ETH MPS Level-3 LW4 Steel Thickness |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-04-07 | 2017-03-03 16:17 | -35 | 2017-02-08 16:18 | Civil - Structural Engineering | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | It has been noted that the reinforcement starter bars are incorrectly positioned within the lining wall 4 from L-3 to L-2. see attached photo. The minimum lining wall thickness as per design is 600mm and the current starter bar positions cannot be extended to achieve the required cover to all faces. The starter bar positions are tapered from 350mm to 460mm in plan view at the construction joint. 16/2/17 - Update following Cxxx initial review: have provided a more detailed survey of the affected area of wall which is attached (Cxxx-SKC-S-DWG-Cxxx-50393-C01-LW4-L-3-NCR-Propsoal 2.0). Measurements are taken at every 5th bar approximately 600mm apart. The first point is taken from the back of IW61 3670 from GL X-X. Please not the centres of the B32 bars across this section equate to 127mm centres rather than 150mm detailed.
| 02SL - Stations (LUL) | Cxxx-NCR-000343 | NCR | Electrical CMS supported by Ductwork unistrut brackets |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2017-03-13 | 2017-03-10 11:35 | -3 | 2017-02-13 15:18 | Electrical - Cable Management | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Electrical CMS appears to be supported by Ductwork unistrut brackets via flat 2 hole unistrut joining plates.
| 02SL - Stations (LUL) | Cxxx-NCR-000344 | NCR | ETH Level -5, IW52 out of Tolerance |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-09-29 | 2017-12-22 11:29 | 84 | 2017-02-21 09:09 | Civil - Structural Engineering | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following a post-pour inspection with CRL and , it was found that IW52 appeared out of tolerance. The results of the As-built survey indicate the wall thickness of IW52 at L-5 is +14mm out of plumb in its worst position. See attached IW52 survey mark up and Post pour inspection
| 02SL - Stations (LUL) | Cxxx-NCR-000345 | NCR | ETH Level-1 IW42 South Face Out of Tolerance |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-04-28 | 2017-02-23 10:13 | -64 | 2017-02-14 11:58 | Civil - Structural Engineering | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following a post-pour inspection with CRL, __s, and , it was found that IW42 south face appeared out of tolerance. An as-built survey of the wall was carried out shows wall is out of tolerance in regards to position on plan >10mm and verticailty over the height of the wall as per dimensional deviation set out in KF10.3222 - Cxxx-__-S-RSP-Cxxx-00009 Rev. 14. See as-built survey attached 'IW42 and Beam L1 - Elevation As Built Survey'. Location shown on at attached: 'Cxxx-SKC-S-DWG-Cxxx-50119 JL Mark Up'
| 02SL - Stations (LUL) | Cxxx-NCR-000346 | NCR | ETH Level -5 IW28 cast without Builders Work Openings |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-06-30 | 2017-07-05 12:08 | 5 | 2017-04-12 09:42 | Civil - Structural Engineering | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | During the construction of internal walls within the ETH, Cxxx-RFI-2011 was used in order to locate builderswork penetrations through the walls. The process followed was for an RFI to be raised and accepted by Cxxx prior to structural reinforcement drawings being updated by Cxxx for the void locations. During the construction of the internal walls at L-5, owing to the time constraint of construction of key walls to achieve Sectional Completion 1, the RC drawings were not updated in line with the penetrations agreed in RFI 2011, and therefore the reinforcement drawings did not align with the openings to be formed in the walls. This wall was cast without openings as shown on the IFC structural drawing, although these were not the correct openings required at the time of construction
| 02SL - Stations (LUL) | Cxxx-NCR-000347 | NCR | Escalator Manufacture Commenced prior to project specific ITP Acceptance |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-04-28 | 2017-04-02 15:10 | -26 | 2017-02-21 14:04 | Mechanical - Escalators | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | __ commenced Escalator Manufacture without an accepted project specific ITP in place. The ITP: Cxxx-SKC-O4-ITP-Cxxx-50013 is still a placeholder on eB. They have manufactured the Escalators in accordance with their standard Pan Tfl ITP, to mitigate any risk Orton L&E and LUL have been inspecting the fabrication of the escalators & providing records issued EWN 014 Failure to Provide Outstanding Information to __ 22/12/2016
| 02SL - Stations (LUL) | Cxxx-NCR-000348 | NCR | MCR still under CEG review after installation has taken place. |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2017-03-22 | 2017-03-16 15:36 | -6 | 2017-02-22 09:47 | Mechanical - Mechanical Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | A Crossrail surveillance was undertaken on 10/02/17 at Cxxx Bond Street Station. During post surveillance review it was found that the MCR (CRL-MCR-004504) for Non-Fire Rated Ductwork was still under review by CEG. The MCR had been submitted for approval on 08/02/17. The installation of ductwork has been going on this last year. Works Information Volume 2B 13.3.8 Materials Compliance Record states “The Contractor shall utilise the template attached in Appendix 13J for the purpose of recording material and product acceptances for the works and submit such records to the Project Manager for acceptance.” In addition the Demonstration of Material Compliance Procedure 8.2 Materials Compliance Record states “The Contractor will use the eB MCR system for MEP MCRs.”
| 02SL - Stations (LUL) | Cxxx-NCR-000349 | NCR | No NCR raised for By Exception Reports 72 & 74. |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2017-04-30 | 2017-04-21 08:33 | -9 | 2017-02-22 09:52 | Mechanical - Mechanical Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | A Crossrail surveillance was undertaken on 10/02/17 at Cxxx Bond Street Station. During post surveillance review of By Exception Reports 72 and 74 for the WTH Level -5 and Level -4 (Cxxx-SKC-O-RGN-Cxxx-50084 and *50143) respectively it was noted that no NCR had been submitted to cover the by exception process. The By Exception Process Procedure (CRL1-XRL-O7-GPD-CR001-50023) states under section 7 “A Non Conformance Report (NCR) shall be issued by the Crossrail Engineering Manager relating to the scope of work presented stating that the construction proposed is not in accordance with standard governance.”
| 02SL - Stations (LUL) | Cxxx-NCR-000351 | NCR | WTH – Vent Shaft Level 7.0+ Slab Missing Pull Out Bars |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-04-28 | 2017-03-26 13:02 | -33 | 2017-02-23 16:47 | Civil - Structural Engineering | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Insufficient placement of pull out bar to elevation N during slip forming operation resulted in bars missing on the eastern edge of level 7.0+ ventilation shaft slab. See attached photos
| 02SL - Stations (LUL) | Cxxx-NCR-000352 | NCR | ETH Level -4 Lining Wall 9 Pour 3, Record Pack - Missing Pre Pour Sheet |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-03-31 | 2017-03-26 13:06 | -5 | 2017-02-28 09:23 | Civil - Structural Engineering | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | cannot locate the level -4 lining wall 9 pour 3 pre-pour sheet required for the submission of the level -4 record packs. Please note all checks were carried out by the relevant parties prior to pouring. Please see attached Lining wall Pour plan for location.
| 02SL - Stations (LUL) | Cxxx-NCR-000354 | NCR | P&T's Upstand drainage channels |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-08-30 | 2017-08-01 16:45 | -29 | 2017-03-20 09:07 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Areas of the drainage upstand in both the EB and WB platforms have been cast incorrect, this is both levels and condition. The levels between the high points and the low points vary in places throughout both the EB and WB. See attached photos. Update 21/03/2013 The undulations in the drainage channels are generally ± 10mm as seen in the attached photos, there are a few instances where the lowest point is -20mm and the highest point is +20mm
| 02SL - Stations (LUL) | Cxxx-NCR-000355 | NCR | ETH MPS L-5 Slab 5 Concrete cube frequency |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-06-30 | 2017-03-26 13:09 | -96 | 2017-03-09 10:03 | Structural Engineering - Structural Engineering - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | After reviewing the ITP documents for the L-5 MPS Slab 5 pour it has been noted that the frequency of cubes taken is not in line with the ITP procedure or specification KF10.2205 (Appendix KF10-2). Cubes to be taken every element and every 60m3 poured. The total pour quantity was 347.6m3 of which have taken 7 sets of cubes, 2 of these however have been taken as additional water was added to the load onsite. This is inline with s water adding procedure (Cxxx-SKC-O4-GPD-Cxxx-50004). The 5 set of cubes was taken at 224m3, There should have been an additional set taken at 300m3 to comply with the frequency set out in Appendix KF10-2. Please see attached MPS L-5 Slab In-Process sheet with details.
| 02SL - Stations (LUL) | Cxxx-NCR-000356 | NCR | ETH MPS L-5 Slab 9 Upper pour: Missing concrete cubes |  | Contr | COS | BOS - Bond Street Station (West) |  | 2018-09-23 | 2018-08-31 16:02 | -23 | 2017-03-09 15:06 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | MPS L-5 Slab 9 (Upper pour): Missing 28 day cube results for Slab 9 pour. The total pour quantity was 9.5m3 of which a set of 6 no. cubes were taken, however cubes were collected without paperwork. As such, test consult have not produce any results for this concrete pour.
| 02SL - Stations (LUL) | Cxxx-NCR-000357 | NCR | VD3 Ladder Rack |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-06-30 | 2017-05-10 12:07 | -51 | 2017-03-09 15:23 | Electrical - General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | 900m Ladder rack and 150mm Tray in KD13 Westbound Draught Relief VD3 has been installed without an assured design in place
| 02SL - Stations (LUL) | Cxxx-NCR-000358 | NCR | ETH L-2 to L0 - Sleeves for Fire Fighting Lift Drainage Channel |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-08-30 | 2017-09-03 11:41 | 4 | 2017-03-13 16:47 | Civil - Civil Engineering General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Due to insufficient builders work information at the time of the slab pours at Levels 0, -1 and -2, 165mm diameter circular holes were cast into the slab in front of the Fire Fighting Lift Shaft. 300mm x 300mm holes should have been cast (as per Levels -3 and -4). The holes are required to be larger than what has been installed to enable a 160mm diam blucher pipe to be installed as part of the fire fighting lift channel drainage detail.
| 02SL - Stations (LUL) | Cxxx-NCR-000360 | NCR | ETH MPS L-5 Internal wall weep holes missing |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-07-31 | 2017-08-04 13:21 | 4 | 2017-03-17 08:53 | Structural Engineering - Structural Engineering - General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | The drainage drawing (Cxxx-SKC-S-DWG-Cxxx-50108 - Detail 10) details weep holes within the L-5 internal walls to allow water to pas throughout the Hy-droduct system. These holes have not been installed within the walls in the MPS as highlighted on the attached drawing.
| 02SL - Stations (LUL) | Cxxx-NCR-000361 | NCR | ETH MPS L-4 IW61 Cover Issue Noted |  | Contr | COS | BOS - Bond Street Station (West) |  | 2018-12-31 | 2017-10-03 13:18 | -454 | 2017-03-17 16:32 | Structural Engineering - Structural Engineering - General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | It was noted during the Pre-pour inspection some starter bars from Lining Wall 4 extending into IW61appeared to have reduced cover on the North side of the wall. See attached Cxxx-__-S-DDL-Cxxx-52141-L-4- Location Mark-up
| 02SL - Stations (LUL) | Cxxx-NCR-000362 | NCR | Section of CMS in Invert level unsuitable for Fibre Optic Cables |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-05-31 | 2017-06-01 15:06 | 1 | 2017-03-22 15:46 | Electrical - Cable Management | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | It has been observed during a site walk that a section of the trunking provided for the installation of fibre optic cables in the invert is unsuitable to accommodate the minimum bending radius associated with that particular type of cable. See attached photos; Invert CMS 1 and 2
| 02SL - Stations (LUL) | Cxxx-NCR-000363 | NCR | Storage of material in CER (KD11) |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-04-28 | 2017-04-05 13:00 | -23 | 2017-03-22 16:56 | Communications and Control Systems | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper storage of material | Completed |  | It was observed during a site inspection that the CER at the Western Ticket Hall is currently been used for storage of Cxxx equipment. See attached Photos 1-5
| 02SL - Stations (LUL) | Cxxx-NCR-000364 | NCR | Incorrect Check Sheet for Dust Sealing |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-04-28 | 2017-04-25 15:46 | -3 | 2017-03-22 16:39 | Architectural - Brickworks/Blockworks | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | WTH RC ITP Rev 9.0 check sheet was used to record cleaning and dust sealing of RC walls and soffits, after Rev 10.0 check sheet.
| 02SL - Stations (LUL) | Cxxx-NCR-000365 | NCR | Missing cube results for MPS L-4 Slab |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-05-31 | 2017-03-28 15:34 | -64 | 2017-03-23 18:53 | Civil - Civil Engineering General | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | MPS L-4 Slab Pour: 08/11/2016 1 no. cube certificate is missing from __ for __ concrete ticket reference no. 136207. Out of 6 sets of cubes, 5 sets of results have been delivered to . 1 set of cubes results have not been delivered, as specified incorrect test date requirements for the cubes. Therefore, __ have not tested any cubes from this set of 4 no. cubes. As noted on the attached In-Process form, 20 litres of water was added to the concrete mix and 4 no. cubes were cast to test at a later date. However, no actual test date was specified on the cube record sheet resulting in no cubes being tested and later being disposed after 56 days as per test consults office procedures
| 02SL - Stations (LUL) | Cxxx-NCR-000366 | NCR | Fused Connection Unit without Neon indicator |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-05-31 | 2017-06-01 12:00 | 1 | 2017-03-24 17:04 | Electrical - Electrical Engineering General | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | It was noticed that the Fused Connection Units did not have neon indicators as per clause JY74.1403. This was observed at SLD07 (WTH -5 OHLE) and also noticed in other areas. Refer CRL-OBS-15093
| 02SL - Stations (LUL) | Cxxx-NCR-000367 | NCR | ETS Earth Bars Installation without approved MCR |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-05-26 | 2017-05-26 12:36 | 0 | 2017-03-29 07:21 | Electrical - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | It was noticed that the ETS Earth Bars installed was installed without an approved MCR (Material Compliance Record) in place. See attached Photos MCR (CRL-MCR-004754) for ETS Earth Bar is still in process.
| 02SL - Stations (LUL) | Cxxx-NCR-000368 | NCR | Installation without approved for Distribution Board |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-05-12 | 2017-06-09 14:36 | 28 | 2017-03-29 08:52 | Electrical - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | It was noticed that Distribution Boards within KD 11 and KD 12 were installed without a approved Inspection and Test plan.
| 02SL - Stations (LUL) | Cxxx-NCR-000369 | NCR | ETH, L-4 Cavity Drainage |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-08-30 | 2017-06-17 13:17 | -74 | 2017-05-17 15:39 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | After the lining wall was cast, it was found that the sleeve in the slab at ETH L-4, GL X was partially within the wall line as per the photo "L-4 NW Sleeve A". See attached Cxxx-SKC-P-DDA-Cxxx-52241 mark up for location
| 02SL - Stations (LUL) | Cxxx-NCR-000370 | NCR | ETH L-4 Exposed Bar Between NLB 11 and Waling Beam |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-05-26 | 2017-05-05 15:49 | -21 | 2017-04-03 14:17 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A steel reinforcing bar was located running between the south face of NLB Wall 11 and the north end of the waling beam at L-4 (location highlighted in 'L-4 Cxxx-SKC-S-DWG-Cxxx-50194 JL Mark Up'). The bar is approximately 25mm above the surface of the slab and 200mm west of lining wall 7. See attached 'exposed bar images 1,2 and 3'. A design change from Cxxx resulted in the removal of an upstand beam in this location. During the breakout of the upstand, removal of 1no. bar was missed. See referenced RFI 2445 for details of design change.
| 02SL - Stations (LUL) | Cxxx-NCR-000371 | NCR | ETH L-5 IW23 Exposed Rebar / Lack of Cover |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-05-26 | 2017-04-28 15:48 | -28 | 2017-04-03 15:04 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Exposed rebar was identified in 5no. locations within the door reveal in IW23 L-5 as highlighted on attached 'Cxxx-SKC-S-DWG-Cxxx-50108 JL Mark Up'. A cover meter survey was carried out on the wall and results are attached (see 'L-5 IW23 Cover meter survey'). It was further identified that a lack of cover (<25mm) was present along the East and West facing elevations of the door opening. See attached Exposed Rebar image 1and 2
| 02SL - Stations (LUL) | Cxxx-NCR-000372 | NCR | CRL not notified of Witness point for inspection and testing of Cxxx cables |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-05-05 | 2017-06-01 15:12 | 27 | 2017-04-04 15:51 | Communications and Control Systems | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Verification Problems - Inspection points not adequate | Completed |  | CRL not invited to Witness point inspections identified on ITP Cxxx-SKC-O4-ITP-Cxxx-50055 for inspection and testing of __ fibre cables in SLD Cable Routes 11 & 12.
| 02SL - Stations (LUL) | Cxxx-NCR-000373 | NCR | WTH Vent Shaft Top of Wall Northern Elevation |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-06-30 | 2017-06-17 13:44 | -13 | 2017-04-10 11:38 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The top of the wall on the northern elevation of the WTH Vent Shaft between GL and GL B has minor exposed reinforcement and an uneven level. This is due to the method of construction with jacking the slipform rig up the wall as early as possible due to the climbing tubes that are cast in. This has then caused some concrete to come away during this process as per the attached image, thus causing the level to be inconsistent throughout
| 02SL - Stations (LUL) | Cxxx-NCR-000374 | NCR | ETH MPS L-2 Perimeter Walls - missing down conductors VS1 and VS5. |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2017-07-30 | 2017-07-28 14:57 | -2 | 2017-04-11 16:57 | Electrical - General | 2500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Drawing Cxxx-SKC-E-DDA-Cxxx-52520 Rev C01 shows copper tape is to be installed within the perimeter walls at MPS L-2 at DC VS1 and DC VS5. The copper tape was not installed within the perimeter walls.
| 02SL - Stations (LUL) | Cxxx-NCR-000375 | NCR | ETH L-2+ Slab north east corner detailing error |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-05-03 | 2017-04-28 15:02 | -5 | 2017-04-19 16:03 | Structural Engineering - Structural Engineering - General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | have noted a discrepancy on the L-2+ Slab RC drawing Cxxx-SKC-S-DWG-Cxxx-50581-C01. E313 and E314 have been scheduled as B20 bars in the T2 rather than B32 as required on the intent drawing Cxxx-__-S-DDA-Cxxx-72131-C04. In addition to form the lining wall east of the slab couplers were cast in the lining wall as indicated on the attached sketch. The couplers were installed as B20 bars to match the reinforcement drawing rather than the intent
| 02SL - Stations (LUL) | Cxxx-NCR-000376 | NCR | PC4 Connection, Vent Shaft GL 4/C |  | Contr | COS | BOS - Bond Street Station (West) |  | 2018-09-15 | 2018-08-15 14:03 | -31 | 2017-04-20 10:56 | Structural Engineering - Structural Engineering - General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __ channel Cast ins were missed during the construction of the WTH Vent Shaft on GL 4/C
| 02SL - Stations (LUL) | Cxxx-NCR-000377 | NCR | By Exception reviews (48, 49, 53, 55 ,56, 57, 61, 63, 72, 73, 74, 75 ,81, 82 ,83, 86) |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-05-26 | 2017-04-21 11:23 | -35 | 2017-04-20 13:39 | Mechanical - Mechanical Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | Procedure CRL1-XRL-O7-GPD-CR001-50023 Rev 2 requires NCR to be raised for By Exception reviews held since the construction released by the reviews is not in accordance with standard governance. The drawings released through the By Exception reviews are incorporated in the design and will be presented through GIRs. The By exception reviews covered under this NCR are listed on the attached schedule and the document references linked to the NCR. This NCR also includes By Exception Reports 72 & 74 which are linked in the document references, this is in response to Cxxx-NCR-000349 (No NCR raised for By Exception Reports 72 & 74. )
| 02SL - Stations (LUL) | Cxxx-NCR-000378 | NCR | ETH - Cover to localised area of L0-B5 |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-06-30 | 2017-06-26 15:09 | -4 | 2017-04-25 15:30 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | Further to NCR-209, there is a local area of reduced cover to a small portion of the L0-B5 beam. The cover ranges from 6-12mm; In addition, there are 4 instances of exposed reinforcement, with the worst position of the reinforcement being 846mm south of GL2. NCR-209 states that cover is to be no less than 15mm and the line of the wall is to be no more than 850mm south of GL 2. This means that there it is possible to apply a 4mm thick layer to the exposed reinforcement. A cover meter survey is attached (section highlighted yellow), along with photos of the relevant section. See Marked up photo of beam L0-B5
| 02SL - Stations (LUL) | Cxxx-NCR-000380 | NCR | Tray Installation |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2017-06-30 | 2017-06-02 13:11 | -28 | 2017-04-24 14:58 | Electrical - Cable Management | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Tray had been cut through the perforations and not along the plain, JY63.3201.D) Cutting of cable tray shall be along a line of plain material i.e. not through perforations. Earth Braids were missing or not connected to containment. JY63.3201 – B) The entire system shall be electrically and/or mechanically continuous to BS7671. Continuous system or via earth links on gaps. Anti vibration washers not installed on vertical tray, but has been installed on all other containment in CER and FOR’s. Live temporary supplies for the CER had been installed on tray that hadn’t been bonded or tested. JY63.4200 – B) before offered for handover the containment and supports shall be fully complete. Cable tray (and ladder) shall be tested and labelled accordingly.
| 02SL - Stations (LUL) | Cxxx-NCR-000381 | NCR | Conduit Installation |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2017-06-30 | 2017-06-02 13:13 | -28 | 2017-04-25 07:50 | Electrical - Cable Management | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Conduits had been installed in parallel between multi-compartment trunking and the ceiling and conduits had been installed on the ceiling at different angles. JY60.3218 – B) Use trunking to avoid multiple parallel conduit runs, subject to approval. Multiple conduits from same compartment has been installed between the trunking and ceiling. Four conduits had been vertically installed at high level between multi-compartment trunking and the ceiling with no additional supports. This span was approx. 1.5m and the conduits were fixed to the trunking via bushes and lock rings, JY60 – 3201 - D) Appearance; arrange conduit, trunking and ducting to present neat appearance, parallel with other service runs and lines of building construction, except where in screed or situ concrete. Ensure plumb vertical runs.
| 02SL - Stations (LUL) | Cxxx-NCR-000383 | NCR | Trunking Installation |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2017-08-25 | 2018-07-17 13:44 | 326 | 2017-04-25 08:03 | Electrical - Cable Management | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Screws protrude through the captive nuts on trunking joiners, JY60 – 1306 – S) Use purpose made jointing piece to achieve IP4X fixed with screws in to captive nuts. Ensure screws do not protrude through the nuts. Cables float from open ended trunking onto basket with no end plate fitted.JY60.3201 – E) Cable installation: install cable in conduit, trunking or equipment enclosures only when completely erected throughout its length. Cables shall be laid and not drawn into trunking
| 02SL - Stations (LUL) | Cxxx-NCR-000384 | NCR | Incorrect use of Cxxx 24 Core __ |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-05-31 | 2017-06-05 12:01 | 5 | 2017-04-27 10:35 | Communications and Control Systems | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | TEW Plus did not follow the __ Cable pulling schedule issued on 15th March 2017 under Aconex __-GC-020568
| 02SL - Stations (LUL) | Cxxx-NCR-000385 | NCR | ETH Mezzanine L-2 Floor Winch Points |  | Contr | COS | BOS - Bond Street Station (West) |  | 2018-06-01 | 2018-04-23 10:04 | -39 | 2017-04-28 13:38 | Structural Engineering - Structural Engineering - General | 0 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Please find attached as-built record of the Floor Winch Points installed within the L-2 Mezzanine slab. The East FWP was moved due to a clash with the temporary Plunge column running through the slab. This does not comply with the drawings and was not raised before pouring. Please note the WWP noted is yet to be installed.
| 02SL - Stations (LUL) | Cxxx-NCR-000386 | NCR | MPS L-2+ Slab Eazistrip for Upstand Not Cast In |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-12-15 | 2018-05-01 15:24 | 137 | 2017-05-09 15:21 | Structural Engineering - Structural Engineering - General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A 150x150mm upstand is shown on the Cxxx-__-S-DDL-Cxxx-52122 GA drawings on the MPS L-2+ slab however, it is not detailed on the __ reinforcement drawing Cxxx-SKC-S-DWG-Cxxx-50849-C01. -RFI-003188 was therefore raised to __ requesting clarification and detailing information. A response was not received in sufficient time and therefore the slab was cast without an upstand at (GL X-A/3) See attached Cxxx-__-S-DDL-Cxxx-52122-C06_Markup for location and extent of missing Eazi Strip
| 02SL - Stations (LUL) | Cxxx-NCR-000387 | NCR | Opening not detailed on the __ reinforcement drawing, builderswork drawing and Cxxx drawings |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-12-15 | 2018-11-12 10:33 | 332 | 2017-05-09 14:38 | Structural Engineering - Structural Engineering - General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Drawing Cxxx-SKC-P-DDA-Cxxx-52224 indicates a drainage opening in the MPS L-2+ slab (for detail '8' which is shown on drawing Cxxx-SKC-P-DDD-Cxxx-25113_CW) however this opening is not shown on the __ reinforcement drawing Cxxx-SKC-S-DWG-Cxxx-50851-C01 or Cxxx-SKC-S-DWG-Cxxx-50850-C01. It is also not shown on the builderswork drawing Cxxx-SKC-M-DDA-Cxxx-69120 or the Cxxx drawings. As such the L-2+ slab has been cast without an opening at this location. Following -RFI-003269, __ have confirmed that an opening for drainage is required (see attached correspondence)
| 02SL - Stations (LUL) | Cxxx-NCR-000388 | NCR | GFRC Infill Strip Installation prior to Accepted Benchmark |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-09-29 | 2017-09-17 18:38 | -12 | 2017-05-10 10:44 | Architectural - General | 5000 |  | Supervision/Management | Rework | 3 (3-6k) | Complete | Management Problem - Inadequate administrative control | Completed |  | It was observed in the Platform and tunnel areas that have installed a small number of GFRC Infill Strips prior to the acceptance of an agreed Benchmark
| 02SL - Stations (LUL) | Cxxx-NCR-000389 | NCR | ETH Stairs Spine Wall L0 |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-10-31 | 2017-11-04 17:14 | 4 | 2017-05-23 15:12 | Civil - Structural Engineering | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The verticality of the ETH Stairs spine wall was surveyed after construction of the adjacent stairs and found to be leaning/ out of plumb by max 29mm from South to North (See attached marked up drawings, surveys and photos). The top of the wall at L 0 is measured at 2229mm (South - should be 2205mm as per design) and 2171mm (North - should be 2200mm as per design). The spine wall at L-1 slab level is however casted in the correct designed position along the full length of the wall. The verticality of the wall was not picked up during the post pour inspection and neither during construction of the adjacent stairs. ******update 04/09/2017******* Further to the Enhanced Answer (Correction) the Cxxx Architects have assessed the impacts on setting out of handrails and stairs and found that that the dimension required from handrail to handrail needed is 2000mm. If the cores were left as they are, the dimensions from handrail to handrail would be 1987mm. This is 13mm less than the minimum tolerance.
| 02SL - Stations (LUL) | Cxxx-NCR-000390 | NCR | MPS L-1 Pile 14 connection to Lining Wall 5 and Beam 5 |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-06-30 | 2017-05-30 08:43 | -31 | 2017-05-22 06:54 | Structural Engineering - Structural Engineering - General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | Bar Mark E139 (4No. B40 bars) have not been installed within Lining Wall 5. Please see attached marked up drawing Cxxx-SKC-S-DWG-Cxxx-50022
| 02SL - Stations (LUL) | Cxxx-NCR-000391 | NCR | ETH MPS L-5 Slab Cube Results marginally below strength at 28days |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-06-30 | 2017-06-17 13:46 | -13 | 2017-05-22 07:29 | Structural Engineering - Structural Engineering - General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | It has been noted that four of the Concrete loads used in the ETH MPS L-5: Slab 1 Extension, Slab 8 Slab 9 and Slab 5 pours, have recorded 28 cube strengths marginally below the specified strength 40N/mm2; however the 56 day cube results satisfy the required 40N/mm2 minimum strength.
| 02SL - Stations (LUL) | Cxxx-NCR-000392 | NCR | WTH L0, Circular Columns on Grid Line E/2, MEP services |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-10-27 | 2017-07-21 09:06 | -98 | 2017-06-06 07:47 | Civil - Civil Engineering General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The WTH Level 0 circular column Grid Line E/2 was cast without the MEP Services required as per GIR 18 design.
| 02SL - Stations (LUL) | Cxxx-NCR-000393 | NCR | MPS L-5 - Slab 8 Pour 2 – Pile P49 Spare reinforcement earth test |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-07-31 | 2017-06-09 10:39 | -52 | 2017-05-23 09:06 | Civil - Civil Engineering General | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | During the testing of Pile P49, the nominated reinforcement connection was tested and had a reading of 0.01 ohms. The 3No. spare pile reinforcing bars were not tested for continuity as per the referenced ITP: Cxxx-SKC-O4-ITP-Cxxx-50008 Line Item 19 See attached Cxxx-SKC-E-DDA-Cxxx-52701 mark-up for location
| 02SL - Stations (LUL) | Cxxx-NCR-000394 | NCR | ETH Lvl-1 IW39 Crack - adjacent to temporary opening |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-12-31 | 2018-04-09 15:56 | 99 | 2017-05-23 14:13 | Civil - Civil Engineering General | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Further to a post-pour inspection carried out by (H. Rysdale) and CRL (__) on 16.05.17, an out of tolerance crack (max 0.5mm) was identified from the east corner of the temporary opening on both sides of the wall, running at approximately 45 degrees (see photo attached). See attached Cxxx-__-S-DDB-Cxxx-54270 Rev C04 SB Mark-up and Cxxx-__-S-DDL-Cxxx-52113 Rev C13 SB Mark-up for location.
| 02SL - Stations (LUL) | Cxxx-NCR-000395 | NCR | ETH MPS CMS route: form 50027/04(b) not available during pre-pour inspection |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-07-31 | 2017-08-01 14:28 | 1 | 2017-05-23 10:25 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | ITP form Cxxx-SKC-O4-ITP-Cxxx-50027/04(b) for the inspection of pipework was not available during the pre-pour inspection at the MPS CMS route area. Ducting checks were only signed off on form 50027/03 (pre-concreting inspection), and form 50027/04(b) has been completed after the works on site were complete
| 02SL - Stations (LUL) | Cxxx-NCR-000396 | NCR | MPS L-1 Waling Beam 1 - Eazistrip not Installed |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-12-22 | 2017-10-03 15:22 | -80 | 2017-05-25 08:43 | Structural Engineering - Structural Engineering - General | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate resources | Completed |  | The Eazistrip on top of Waling Beam 1 (for the upstand) in the MPS at L-1 has not been installed. Please see attached mark-up Cxxx-SKC-S-DWG-Cxxx-50296_CW
| 02SL - Stations (LUL) | Cxxx-NCR-000397 | NCR | Gap between Cxxx Lining Wall 1, L-1 and Cxxx Capping Beam (1.5m long) |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-08-30 | 2017-11-09 14:38 | 71 | 2017-05-26 10:13 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | It was noted in the post-pour inspection in the mainbox at L0, that there is a gap of approx. 5mm-10mm between the top of Lining Wall 1 and the Cxxx capping beam over a distance of approx. 1.5m to the east of GL B. See attached photos and LW1 Post Pour 23-5-17
| 02SL - Stations (LUL) | Cxxx-NCR-000398 | NCR | ETH Monitoring Prisms Removed |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-07-28 | 2017-06-07 14:37 | -51 | 2017-05-30 13:23 | Surveying - GIS Engineering & Land Surveying | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | had been instructed (Cxxx-PMI-01423 (ext.991,1050, 1138 and1268)) to installed monitoring prisms in the escalator barrel of ETH, to monitor expected ground movement, potentially caused by the Over Site Development at 18 Dering Street and between 64 and 72 New Bond Street. installed four (4) arrays of monitoring prisms, where each array contains five (5) targets. During recent site visit we noticed that some monitoring prisms had been removed without our knowledge
| 02SL - Stations (LUL) | Cxxx-NCR-000399 | NCR | WTH Waterproofing Inspection |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-08-31 | 2017-09-03 12:14 | 3 | 2017-06-16 14:52 | Civil - Civil Engineering General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | A number of issues were raised during the WTH Waterproofing Inspection on 24/05/2017, as follows: 1. Tears in the perimeter vertical waterproofing visible, See attached photos IMG_0467 & IMG_0468 and NCR 399 location Mark Up 2. Crossrail were not invited out to any of the previous ITP intervention points. 3. The deliverable ITP inspection check sheet was not available for the inspection. 4. CRL queried that a 600mm deep excavation was required at the perimeter area to expose the waterproof membrane to be lapped. However this depth only relates to PMI 1016 previously issued by CRL for all works South of GL4. As the minimum overlap required for these works is 100mm, there was only a requirement to excavate by 300mm, to allow for installation of the waterproof membrane. Therefore, this will ensure waterproofing integrity as per the specifications and Waterseal's warranty(See attached Silicor e-mail)
| 02SL - Stations (LUL) | Cxxx-NCR-000400 | NCR | WTH, Level-2 RC plinths - rebar inspection |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-08-31 | 2017-09-03 12:54 | 3 | 2017-06-02 15:53 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | WTH, Level-2 RC upstand plinths - rebar inspection __ Formwork installed L bars to upstand plinth to align with design spacing and bar numbers as per schedule. Six number positions did not receive any L bars as reinforcement was fixed aligned to the T1 and T2 reinforcement layers and not sufficient bar quantities was detailed by __. completed the pre pour inspection and invited CRL who pointed out that the 6 No. locations should also receive L-bars. This was verified by __ and the contractor cut and bent additional L Bars on site and installed in the required location; however failed to invite CRL for a second inspection to complete the pre pour prior to placing concrete. See attached CRL pre-pour photos IMG_0452 to IMG_0456
| 02SL - Stations (LUL) | Cxxx-NCR-000401 | NCR | Inspection Request Process |  | Contr | COS | BOS - Bond Street Station (West) |  | 2018-05-31 | 2018-09-21 13:46 | 113 | 2017-06-02 14:16 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | A number of concerns have recently been raised regarding the Inspection Request Process as below: 1. CRL-OBS-16322 ( ETH, MPS, LW1) - Pre-pour sheet signed prior to completion of the works. 2. NCR-373 pre-pour inspection - Works not checked by prior to CRL inspection.(e-mail attached) 3. WTH, Lvl-3, ES1 coring works - CRL not notified of ITP witness point. (e-mail attached)
| 02SL - Stations (LUL) | Cxxx-NCR-000402 | NCR | ETH L-1 IW31 As-built survey of North Face |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-09-30 | 2017-06-20 09:12 | -102 | 2017-06-13 07:34 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following a post-pour survey, the north face of IW31 at L-1 appeared to be out of tolerance. An as-built survey was undertaken and the Contractor confirms the element is out of tolerance when compared to Appendix A of the KF10 specification as follows: 1) Table KF10-8 - Verticality of elements - With regards to 'Single storey of height h': Delta h/600 = 5350/600 = 8.9mm limit. 2) KF10-4 - Walls - Linear dimensions - With regards to 'wall thickness': +10 / -5mm limit.
| 02SL - Stations (LUL) | Cxxx-NCR-000403 | NCR | MPS L-1 Step in IW47 at the Northern End/Connection with Waling Beam 1 |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-12-29 | 2018-02-07 14:39 | 40 | 2017-06-02 09:43 | Structural Engineering - Structural Engineering - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The western end of Waling Beam 1 in the MPS at L-1 is terminated with a B40 bob bar (E19) within IW47. Please see attached marked up drawings Cxxx-SKC-S-DWG-Cxxx-50296 and Cxxx-__-S-DDL-Cxxx-52111. This bar was scheduled with an 'A' dimension of 260mm. This is not compliant with BS 8666:2005 and therefore cannot be manufactured by our Suppliers, Hyten.
| 02SL - Stations (LUL) | Cxxx-NCR-000404 | NCR | Rodding Points/Hatches (20 Number) - Platform Adits - Public Areas at Level -5 |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2019-07-20 | 2019-07-16 15:01 | -4 | 2017-06-02 18:24 | Architectural - Flooring | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The 20 access hatches for the rodding eyes for the adits leading from the concourse/platforms have not been fully co-ordinated with the public health design. This results in pipework clashing with the frame required to support the hatch unless the outlets can be diverted.
| 02SL - Stations (LUL) | Cxxx-NCR-000405 | NCR | ETH MH1 infill slab to level 0 - construction joint leaks |  | Contr | COS | BOS - Bond Street Station (West) |  | 2018-02-28 | 2018-01-16 15:29 | -43 | 2017-06-15 10:42 | Civil - Civil Engineering General | 2000 |  | Material | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | The MH1 infill on the ground floor is showing dampness on the slab soffit at a number of locations along the construction joint. See attached photos IMG slab infill 1 to 3 and Pre-pour sheet and marked up dwg The construction joint was constructed with 1 No. hydrophilic strip to full circumference. The MH1 infill will not be exposed to the elements at L0 level and will receive follow on floor finishing at a later date.
| 02SL - Stations (LUL) | Cxxx-NCR-000406 | NCR | C50/60 Self Compacting Concrete - MCR code 3 |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-10-31 | 2017-08-10 14:25 | -82 | 2017-06-06 15:27 | Civil - Civil Engineering General | 0 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The MCR for C50/60 Self Compacting Concrete Cxxx-SKC-C-LRC-Cxxx-50006 2.0 is currently at Code 3 status. The concrete was used in the Blockwork bespoke beams in the ETH and WTH. This mix design is identical to Revision 1 and performs as before without issue, the only change was for the scope of usage following issue of Cxxx-PMI-00970
| 02SL - Stations (LUL) | Cxxx-NCR-000407 | NCR | NLB Wall 11 at L-1, cracks 0.35mm to 0.4mm |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-12-31 | 2017-09-25 15:06 | -97 | 2017-06-16 13:35 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following post-pour inspections (attached) with CRL of the NLB Wall 11 at L-1 (north and south elevation), cracks of between 0.35 mm to 0.4mm width have been seen. (see attached photos Cxxx-NCR-000407 - Pic 1 to Pic 8) These are evident on both sides of the wall and the cracks connect at the top of the wall in the same location. On the north face, the crack is evident at the top of the wall for approximately 850mm, whereas the crack on the south side is full height (approximately 2.9m). See attached marked up a photo of exact locations for both sides of the wall. These appear to be isolated cracks and are located in the central section of the wall (away from the construction joint). These are outside the limit specified in the Cxxx-SKC-A-RSP-Cxxx-50003 - Architectural Specification - Section JE41 - Worked Finishes to In-Situ Concrete - clause JE41.1203 states ‘Crack widths in the exposed surfaces of the concrete shall not exceed 0.3mm.’
| 02SL - Stations (LUL) | Cxxx-NCR-000408 | NCR | ETH MPS L-3 to L-2 IW52/61 Redundant Slab Starters |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-08-31 | 2017-07-07 10:42 | -55 | 2017-06-14 14:19 | Structural Engineering - Structural Engineering - General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | There was a detailing error in Cxxx-SKC-S-DWG-Cxxx-50804-C01 which resulted in starter bars being installed within IW52/61 (L-3 to L-2) for the escalator soffit slab. See attached photos 150617 1 & 150617 2 and Cxxx-SKC-S-DWG-Cxxx-50804-C01-Markup-LS-140617 Cxxx-__-S-DDD-Cxxx-72212-C01 instructed within Cxxx-PMI-01362 shows a movement joint between the sloping slab and the internal walls. Therefore starters should not have been detailed on the adjoining walls IW52/61.
| 02SL - Stations (LUL) | Cxxx-NCR-000409 | NCR | ETH MPS L0 B13 and IW21 Re-work |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-07-14 | 2017-06-30 11:00 | -14 | 2017-06-14 15:15 | Structural Engineering - Structural Engineering - General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please see attached photo of the current state of IW21 and marked up reinforcement drawings. These show that an area of IW21 has been constructed without installing couplers to connect to L00 B13. This was due to incorrect detailing of IW21 on Cxxx-SKC-S-DWG-Cxxx-50554-C01
| 02SL - Stations (LUL) | Cxxx-NCR-000410 | NCR | Beam W-B+1-03 couplers not correctly cast into the vent shaft slip form elevation M |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-11-30 | 2017-10-03 13:36 | -58 | 2017-06-14 15:49 | Structural Engineering - Structural Engineering - General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Beam W-B+1-03 couplers were not correctly cast into the vent shaft slip form elevation M. Couplers have not been cast into the 600mm thick vent shaft wall bottom row. There should have been 10no. B40 couplers cast into the top and 10no. B32 couplers into the bottom (Bar Mark 29 and 30). In reality, 16no. B40 couplers have been cast in the top row and no couplers have been cast in the bottom.
| 02SL - Stations (LUL) | Cxxx-NCR-000411 | NCR | MPS L-3 Escalator Slab Starter Bars not cast in to Lining Wall 4 |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-08-31 | 2017-06-29 08:17 | -63 | 2017-06-19 15:54 | Structural Engineering - Structural Engineering - General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | MPS L-3 Escalator Slab Starter Bars not cast in to Lining Wall 4 1) The MPS L-3 Lining Wall 4, 1.5m high section was poured on 16/01/2017 and the remainder of the wall was poured on 01/03/2017. At the time of construction, the Code 1 approved drawing Cxxx-SKC-S-DWG-Cxxx-50393-C01 was used. Drawing Cxxx-SKC-S-DWG-Cxxx-50393-C02 was only issued to by __ on 10/04/2017 and this revision indicates the requirement for an additional 10No. B25 bars E99, these have not been cast in to Lining Wall 4 in the MPS at L-3. Please see attached marked-up drawing Cxxx-SKC-S-DWG-Cxxx-50393-C02. 2) Drawing Cxxx-SKC-S-DWG-Cxxx-50286-C01 and C02 are the L-3 Slab drawings which indicates bars that are required to be cast into the Lining Wall 4 (BM E125 and E123); however these bars are not shown on the Lining wall 4 drawing Cxxx-SKC-S-DWG-Cxxx-50393-C01, and therefore were not cast in to Lining Wall 4 in the MPS at L-3. Please see attached marked-up drawing Cxxx-SKC-S-DWG-Cxxx-50286- C02 . The highlighted bar marks; E125 (3No. B20s on 50286) and E123 (7No. B40s on 50286); on Rev C01 (E123 shown as B32s) 3) Drawing Cxxx-SKC-S-DWG-Cxxx-50287-C01 is the L-3 Slab drawing which indicates bars that are required to be cast into the Lining Wall 4 (BM E313 and E314).; however these bars are not shown on the Lining wall 4 drawing Cxxx-SKC-S-DWG-Cxxx-50393-C01, and therefore were not cast in to Lining Wall 4 in the MPS at L-3. Please see attached marked-up drawing Cxxx-SKC-S-DWG-Cxxx-50287 -C01. The highlighted bar marks; E313 (7No B25s on 50287) and E314 (3No. B20s on 50287)
| 02SL - Stations (LUL) | Cxxx-NCR-000412 | NCR | WTH Level -5 Winch Points (W-06-71-H01 and W-06-71-H02) |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-11-30 | 2017-09-06 15:42 | -85 | 2017-06-22 15:42 | Architectural - Flooring | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Drawing Cxxx-SKC-A-DDD-Cxxx-35802 - Detail 3, requires angles around the winch point to be installed to a size of 420mm x 420mm. The As built dimensions of the winch point openings in question are as follows: 406 x 412 and 408 x 416. See attached Cxxx-SKC-A-DDE-Cxxx-27650 - Winch Point mark up for location These dimensions are unsuitable for the installation of the winch point hatches.
| 02SL - Stations (LUL) | Cxxx-NCR-000413 | NCR | GFRC Benchmark (ES1) |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2018-12-29 | 2018-11-20 13:51 | -39 | 2017-06-27 09:49 | Architectural - Finishes | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Cxxx-SKC-O4-ITP-Cxxx-50071 Version 2.0 - 6.0 Inspection/Benchmark clearly states that the installation of the benchmark (ES1) of GFRC is a hold point. Acceptance of the benchmark is required to allow the works to progress. Comments remain outstanding on the benchmark; colour range, accuracy of installation, method and frequency of repair (as captured on the inspection record) and works have progressed on site. The Benchmark in its current state is unacceptable to CRL.
| 02SL - Stations (LUL) | Cxxx-NCR-000414 | NCR | GFRC Installation - ES1 |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2019-05-29 | 2019-01-04 15:08 | -145 | 2017-06-27 11:09 | Architectural - Finishes | 500 |  | Material | Reject | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | GFRC Panels have been installed in ES1 (Escalator barrel leading from Level - 3 Western Ticket Hall to Platform Level) without an approved design (drawings - Cxxx-SKC-A-LRG-Cxxx-50072 - RIR for ES1 and associated comment log).
| 02SL - Stations (LUL) | Cxxx-NCR-000416 | NCR | ETH Lightwell - Damage to L-0 Capping beam Grid F/3-4 |  | Contr | COS | BOS - Bond Street Station (West) |  | 2018-02-28 | 2017-12-22 11:42 | -68 | 2017-06-30 07:31 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During excavation works for the ETH Lightwell, a temporary propping frame supported from the L0 capping beam dropped approximately 65mm. As a result of the drop and the induced moment at the end-plate, a wedge of concrete immediately behind the prop end-plate has pulled away from the capping beam. The damaged section of capping beam is at +122.900, and is located between Grid 3-4/F, refer photos attached.
| 02SL - Stations (LUL) | Cxxx-NCR-000417 | NCR | Torqueing activity and associated parameters omitted from ITP and Checksheet for GFRC Steelwork Installation |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2017-08-30 | 2017-10-31 17:08 | 62 | 2017-07-05 10:12 | Architectural - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | A planned Crossrail surveillance was undertaken on 04th July 2017 to look at onsite installation of the GFRC Stainless Steel Support System at Bond Street Station. During the site visit torqueing of the __ fixings was discussed. It was stated by that the fixings (size dependant) had been/are tightened in accordance with the __ technical data sheet requirements. Two areas were sampled, Area 1 in PTW and CH2, to enable a check of the records associated with this activity to show evidence that it had been completed/checked. On checking the Installation ITP (Cxxx-SKC-O4-ITP-Cxxx-50071) it was identified that it did not include torqueing as an activity, including the parameters as defined by __. Furthermore, on checking the checksheets, it was also identified that they did not include a check item for torqueing of the __ fixings into the SCL lining. Based on this, no evidence exists assuring that torqueing has been completed, and to the correct values stipulated by __ for each type fixing, for all installed sections to date. Works Information Vol 2B Part 20.8 states; “The Contractor … shall maintain ITPs for the services they provide” … “These ITPs shall stipulate the necessary level and frequency of tests and inspection for each aspect of the works” … “The Contractor shall conduct inspections and tests in accordance with his details ITPs … which shall include activities of structural or operations, significance, and inspections which are of a subjective nature or release work that is to be covered up.”
| 02SL - Stations (LUL) | Cxxx-NCR-000418 | NCR | GFRC Steelwork studs fixed into SCL at CP2/CH2 junction with nuts showing minimal surface bearing with the lining |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2017-12-31 | 2017-10-09 16:28 | -83 | 2017-07-05 10:15 | Architectural - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not trained for the work being performed | Completed |  | A planned Crossrail surveillance was undertaken on 04th July 2017 to look at onsite installation of the GFRC Stainless Steel Support System at Bond Street Station. During the site visit the GFRC Stainless Steelwork connections were checked within PTW and the bridging between CP2 and CH2. On checking, it was noticed that due to the SCL profile/irregularity, the nuts tightened to the SCL surface showed minimal surface bearing (see photo attached). Based on this, the performance of the washer and nut would be limited which may reduce the performance of the support system over its intended design life. National Structural Steelwork Specification (NSSS) 5th Edition Section 6.1.6 states “If the bold head or nut is in contact with a surface which is inclined at more than 2o from a plane at right angles to the bolt axis, a taper washer shall be placed to achieve satisfactory bearing”. As the surveillance was based on a sample, it should be investigated to identify how many nuts have been installed like this. A solution should also be proposed and accepted to ensure adequate surface bearing.
| 02SL - Stations (LUL) | Cxxx-NCR-000419 | NCR | ETH Level -5 &-4 Circulation area: Inverted Trunking |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-10-31 | 2019-03-25 17:05 | 510 | 2017-07-07 10:38 | Electrical - Cable Management | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Additional inverted 50mm x 50mm Trunking has been install to accommodate Cxxx Fibre cables within ETH L-5 and L-4 circulation area. This was installed due to long manufacturing lead times of design trunking. See attached Inverted trunking route drawings and photos The Communication trunking had to be installed via a different route down the circulation area, the only available route was to install the CMS inverted across along the blockwork wall but in close proximity of a drainage pipe. The trunking was inverted to connect to the underside of the CMS into each system wide room, the 50mmx 50mm trunking could not be routed above the CMS as it would have clashed with the mechanical services, the only viable option was to install underneath the CMS which provide a larger opening and adequate bending radius for the fibre cables.
| 02SL - Stations (LUL) | Cxxx-NCR-000420 | NCR | WTH Level -3 Escalator Infill slab |  | Contr | COS | BOS - Bond Street Station (West) |  | 2018-07-31 | 2018-10-17 15:42 | 78 | 2017-07-31 12:42 | Structural Engineering - Finishes | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The WTH Escalator Infill slab at levels -5 and -3 have been cast with a fall into the gully, which is less then the specified fall of 1:75. See attached As built surveys.
| 02SL - Stations (LUL) | Cxxx-NCR-000421 | NCR | Precast Column PC1 (2no) Incorrect Position of Cast in Provisions |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-09-30 | 2017-09-08 09:01 | -22 | 2017-07-10 08:35 | Structural Engineering - Concrete Member | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | 2no PC1 WTH precast columns cast in Holland (__ Facility), have 2no Demu 1558 M20 anchors installed out of position (2no anchors per column). See attached Cxxx-SKC-A-DWG-Cxxx-51147 Mark-up and Cxxx-NCR-000421 Precast Column PC1 Photos
| 02SL - Stations (LUL) | Cxxx-NCR-000422 | NCR | ETH MPS L-3 to L-2 IW52/61 Redundant Slab Starters Between IW45/46 |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-08-31 | 2017-07-24 07:44 | -38 | 2017-07-11 09:09 | Structural Engineering - Structural Engineering - General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Further to Cxxx-NCR-000408 it has been identified that works still need to be completed for the Redundant Slab Starters to ETH MPS L-3 L-2 IW52/61 between IW45/46. Please see attached Cxxx-SKC-S-DWG-Cxxx-50804-C01-Markup-LS-100717 As Cxxx-NCR-000408 "There was a detailing error in Cxxx-SKC-S-DWG-Cxxx-50804-C01 which resulted in starter bars being installed within IW52/61 (L-3 to L-2) for the escalator soffit slab. Cxxx-__-S-DDD-Cxxx-72212-C01 instructed within Cxxx-PMI-01362 shows a movement joint between the sloping slab and the internal walls. Therefore starters should not have been detailed on the adjoining walls IW52/61."
| 02SL - Stations (LUL) | Cxxx-NCR-000423 | NCR | WTH-Beam W-B+1-04 couplers not correctly cast into the vent shaft slip form elevation M |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-10-31 | 2017-10-03 14:01 | -28 | 2017-07-20 09:53 | Structural Engineering - Structural Engineering - General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | WTH Beam W-B+1-04 couplers were not correctly cast into the vent shaft slip form elevation M. Couplers have not been cast into the vent shaft wall bottom row. There should have been 3no. B32 couplers cast into the bottom row, in reality these have been cast in too high for use.
| 02SL - Stations (LUL) | Cxxx-NCR-000424 | NCR | ETH MPS L-2 WB4 Eazistrip omission |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-10-31 | 2018-03-12 13:00 | 132 | 2017-07-12 07:45 | Structural Engineering - Structural Engineering - General | 500 |  | Planning | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate resources | Completed |  | Approximately 15m section of Eazistrip has been omitted from the pour of the L-2 WB4. This is detailed on the attached Cxxx-SKC-S-DWG-Cxxx-50854-C02-Missing-Eazi-Strip.
| 02SL - Stations (LUL) | Cxxx-NCR-000425 | NCR | No evidence of Calibration for Torque Wrench used for GFRC Steelwork |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2017-12-31 | 2017-10-19 13:12 | -73 | 2017-07-13 08:37 | Architectural - General | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Inadequate/insufficient tooling. | Completed |  | A planned Crossrail surveillance was undertaken on 04th July 2017 to look at onsite installation of the GFRC Stainless Steel Support System at Bond Street Station. Two Torque Wrenches were checked on site. The calibration certificate was made available for one (Part No. 15004 40-200 Nm Range) which was in date. A post surveillance request was made for the second (Nr. 821704 20-200 Nm Range) as the certificate was not available on site. During a post surveillance meeting, it was confirmed that no calibration certificate was available for the Torque Wrench 821704. It was further stated that this tool was not purchased new and had come from another project. Based on this, confirmation of in date calibration can not be confirmed. The National Standard (BS EN 6789) requires a calibration every 12 months from point of first use, the first use date cannot be confirmed. Moreover, locations where each of the tools has been used to tighten the fixings are not documented. Based on this, as part of closure to this NCR, the Contractor should detail the locations where this tool may have been used and how this has been worked out, and undertake a regime of checking to ensure those fixings have been tightened to the correct Torque.
| 02SL - Stations (LUL) | Cxxx-NCR-000426 | NCR | No progressive Pull Testing completed on GFRC Steelwork fixings as required by KM10 |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2017-10-12 | 2017-09-21 16:18 | -21 | 2017-07-13 08:40 | Architectural - General | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | A planned Crossrail surveillance was undertaken on 04th July 2017 to look at onsite installation of the GFRC Stainless Steel Support System at Bond Street Station. Evidence of progressive Pull Testing was requested for the Steelwork fixings as required by the 3% or 5% KM10.2203 frequency; with the testing completed in accordance with the CFA Guidelines. A Pull Test Report was noted (Cxxx-SKC-A-RGN-Cxxx-50059), however on checking this was initial testing to confirm he suitability of the fixing. During a post surveillance meeting it was confirmed that no further testing had been completed at the required frequency to assure the installation, workmanship and substrate associated. The Contractor should propose a regime of testing which is to include testing of fixings already installed. In addition the documentation (ITP and Checksheets) should be updated to include Pull Testing as an activity. Moreover, the Proof Load should be confirmed and documented as extracted from the Structural Calculations.
| 02SL - Stations (LUL) | Cxxx-NCR-000427 | NCR | Thixotropic Grout for GFRC Steelwork used approx. 8 months past its Storage Life |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2017-12-31 | 2017-09-26 15:19 | -96 | 2017-07-13 08:47 | Architectural - General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | A planned Crossrail surveillance was undertaken on 04th July 2017 to look at onsite installation of the GFRC Stainless Steel Support System at Bond Street Station. During the site visit, it was witnessed that grout has been used to level the SCL surface on 3 out of the 7 brackets for each bays Steelwork Strut. It was stated that this is to allow adequate setting out where the SCL’s rough surface limits. The thickness of the grout between the SCL and steel plate contact surface varied. The grout product details were checked onsite to allow for traceability back to an approved MCR. On checking the batch on site, it was noticed that the Date of Manufacture was 06-05-16 (see photo). On checking the Parex Technical Data sheet, the Storage and Shelf Life details are noted as follows; “TJF will have a storage life of 6 months in unopened bags when kept in dry conditions at a temperature between 5oC and 35oC” (see attached). Based on the 6 month shelf life, the product (batch) should not have been used from November 16 onwards. The batch on site was 8 months past its shelf life. The DOM can not be known for batches previously used. It was stated that the grout was not a new supply from the manufacturer; it was taken from a storage facility. Although the grout has been used (sated by ) only to provide a level surface between the SCL and steel plates, should the grout matrix deteriorate over time, what impact would this have on the steel work structure? Would this allow for movement? Technical justification for its use (or further testing etc) as agreed with the CRL Team should form closure to this NCR. The grout on site should be removed to ensure it is no longer used.
| 02SL - Stations (LUL) | Cxxx-NCR-000428 | NCR | GFRC Structural Steel connection detail change (U Plate – Sliding Support) without CRL acceptance of revised Structural Calculations |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2017-10-26 | 2017-10-23 16:22 | -3 | 2017-07-13 10:25 | Architectural - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | A planned Crossrail surveillance was undertaken on 04th July 2017 to look at onsite installation of the GFRC Stainless Steel Support System at Bond Street Station. During the site visit, the U Plate connection detail was checked. In locations it was witnessed that the plate had been connected with 2 fixings each side (photo attached) whilst in other areas it was witnessed that only 1 fixing had been installed each side (see photo). This was queried. It was stated that initially the design was to use 2 fixings each side of the U Plate, however it had been agreed/confirmed to the site team that only 1 was required. Based on this, the Structural Calculation Report was requested to show that the revised connection detail had been accounted for and agreed. During a post surveillance meeting, the Structural Calculations Report (GFRC Wall Cladding – Alternative Fixing of the Sliding Support) was provided (dated July 2016). This showed the fixing detail change from 2 each side to 1. However, on review it was identified that this was showing as a Placeholder on eB (No. Cxxx-SKC-A-RGN-Cxxx-50057) with no CRL acceptance. CRL acceptance of this report is a Hold Point within the ITP, Cxxx-SKC-O4-ITP-Cxxx-50071 No. 1.3. Based on this, the installation with 1 fixing cannot be confirmed as acceptable until such time as CRL acceptance has been received. This also demonstrates a breakdown in the change control process.
| 02SL - Stations (LUL) | Cxxx-NCR-000429 | NCR | MPS L0 Slab - Shear Links not Detailed on __ Reinforcement Drawings |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-09-30 | 2017-09-05 10:33 | -25 | 2017-07-18 15:04 | Structural Engineering - Structural Engineering - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The attached MPS L0 Slabs drawings Cxxx-SKC-S-DWG-Cxxx-50795-C01 and Cxxx-SKC-S-DWG-Cxxx-50796-C01 did not detail any requirements for shear links within the slab. This was queried by to __ on 04/07/2017 (please see attached email) A response was received detailing the requirement for shear links to be included in the slab (see attached __ sketch '170704_Lap detail non staggered'). As such, instructed sub-contractor __ Formwork to cut and bend site stock reinforcement to produce the required links and install within the slab during the nightshift ready for the pour on 05/07/2017.
| 02SL - Stations (LUL) | Cxxx-NCR-000430 | NCR | MPS L0 Missing Starter Bars in Beam 13 for IW49 |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-12-22 | 2017-07-22 15:20 | -153 | 2017-07-18 13:16 | Structural Engineering - Structural Engineering - General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The attached MPS L0 Beam 13 drawing 'Cxxx-SKC-S-DWG-Cxxx-50600-C03' does not detail starter bars for IW49 and were therefore not installed. The Beam has been poured up to 121.900.
| 02SL - Stations (LUL) | Cxxx-NCR-000431 | NCR | ETH, Lvl-4, East end drop beam out of tolerance |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-09-30 | 2017-08-03 10:34 | -58 | 2017-07-18 17:04 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The drop beam on L-3 soffit has been cast out of tolerance See attached marked up location drawings, 7 No. photos of the area and Level -4 Drop Beam As-Built and Cover Survey
| 02SL - Stations (LUL) | Cxxx-NCR-000432 | NCR | ETH L-1 - As-built survey of Southern OSD Shaft |  | Contr | COS | BOS - Bond Street Station (West) |  | 2018-05-31 | 2018-10-03 16:29 | 125 | 2017-07-18 16:22 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following a post-pour inspection, an as-built survey of the southern OSD shaft at L-1 was undertaken by __s; this comprised the inside face of walls IW25, 27, 28 and 29. The as-built survey shows that the walls are out of tolerance with regards to the KF10 spec Table 10-8 for line/level (tolerance +/-11.5mm). Please see as-built survey attached along with marked up GA showing the relevant wall reference numbers. The areas in red on the as-built survey are out of tolerance.
| 02SL - Stations (LUL) | Cxxx-NCR-000433 | NCR | L-2 Slab Infills (for Temporary Piles) - Damaged Couplers |  | Contr | COS | BOS - Bond Street Station (West) |  | 2018-07-31 | 2017-08-03 14:51 | -362 | 2017-07-21 15:05 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please see attached marked-up drawing Cxxx-SKC-S-DWG-Cxxx-50862-C02. There are 8No. B25 couplers in total which have been damaged during the removal of the temporary piles
| 02SL - Stations (LUL) | Cxxx-NCR-000434 | NCR | WTH L-3 Room 4/414 SLD 02 Screed Damage |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-08-31 | 2017-09-15 15:16 | 15 | 2017-07-28 10:53 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Personnel Error - Inadequate work environment | Completed |  | As seen in the attached photo the screed in WTH L-3 Room 4/414 SLD 02 has been cracked due to materials being taken in and out of the room without adequate protection being installed.
| 02SL - Stations (LUL) | Cxxx-NCR-000435 | NCR | ETH L-5 IW46 Cast-In Drainage Sleeve Not Installed |  | Contr | COS | BOS - Bond Street Station (West) |  | 2018-04-01 | 2018-03-12 17:40 | -20 | 2017-07-24 13:26 | Civil - Civil Engineering General | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The 100mm diameter drainage sleeve in the north end of IW46 at L-5, highlighted in attached 'Cxxx-SKC-P-DDA-Cxxx-52251 JL Mark Up' was not installed.
| 02SL - Stations (LUL) | Cxxx-NCR-000436 | NCR | ETH L-4 Upstand infront of Lining Wall 5 Eazistrip Installed Out of Position |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-09-30 | 2017-10-23 16:32 | 23 | 2017-08-03 06:42 | Civil - Civil Engineering General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Supervision - Other | Completed |  | No setting out information was provided for the cavity upstand on the GA Cxxx-__-S-DDL-Cxxx-52141. RFIs 'Cxxx-RFI-001556' which was then superseded by 'Cxxx-RFI-002962' were raised in order to obtain the setting out information. Cxxx-RFI-002962 states that the cavity should be 125mm in this area (see attached DDN C698 - RFI-2962 - ETH MPS L-4 Upstand Setting Out Information North Wall and DDN C347 - Setting out dimensions ETH RFI-1556). Eazistrip has been cast into the L-4 Slab 210mm away from the wall in order to incorporate the cast-in cavity drainage - as per the attached Cxxx-SKC-P-DDA-Cxxx-52241 C02. As-built setting out dimensions are shown on attached 'Cxxx-__-S-DDL-Cxxx-52141 JL mark up' therefore a greater distance from the lining wall than the 125mm in Cxxx-RFI-002962.
| 02SL - Stations (LUL) | Cxxx-NCR-000437 | NCR | WTH Level 0 – Column PC1N (Gridline G/4) 3 mm out of tolerance on plan |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-12-31 | 2018-01-17 10:29 | 17 | 2017-08-09 14:16 | Architectural - General | 0 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Column PC1N has been installed and as built surveyed, whereby it is noted the insitu rebate is 2mm – 3mm to the east therefore the column PC1N is 2mm & 3mm outside the position on plan tolerance of ±5mm. See attached __-9838-002_01 - As Built 29.07.17 - Intermediate for PC1N NCR The following items are of importance to note; • The column complies with all other tolerances and therefore this has NIL impact visually. • Drawing Cxxx-SKC-A-DWG-Cxxx-50131 attached (for the __ external cladding design) confirms the assumed tolerance of the column within the cladding system design is + or – 10mm – therefore no impact to cladding. The Rebate was surveyed prior to production of unit PC1N and couplers were positioned to the ‘line of best fit’ i.e. 80mm from gridline G. Note : Cxxx-RFI-002943 accepted the reversed order of installation in order to mitigate further program movements as a result of design delays impacting precast production. Wall W-W-9 (GL G4) was cast prior to the installation of precast colonnade unit PC1 in accordance with Cxxx-FCD-00501.
| 02SL - Stations (LUL) | Cxxx-NCR-000438 | NCR | Various tools used for dimensional control at __ not calibrated |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2017-09-12 | 2017-11-20 15:27 | 69 | 2017-08-09 10:08 | Architectural - General | 500 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | A planned Crossrail surveillance was completed at __ on 3rd August 2017 to check the processes and quality control for the manufacture of the GFRC cladding panels. During the factory walk around, it was observed that various tools were being used for a) the setting out of the steel sickles and b) dimensional control of the moulds/panels. The tools observed were; digital and non-digital vernier callipers, tape measure, wooden rules and steel rules (see photos attached). A calibration record was only provided for 1 x vernier calliper and 1 x tape measure. Calibration for the other equipment could not be provided. No equipment list was in place documenting what equipment had been issued to the operatives for use and serial numbers associated, to allow for control and traceability. In addition, no records of calibration could be provided for the thermometer and humidity sensor which monitors the environmental conditions. The tools being used at the factory should be rationalised. Those which do not hold appropriate calibration should be withdrawn until such calibration is in place.
| 02SL - Stations (LUL) | Cxxx-NCR-000439 | NCR | A number of __ manufactured panels do not align with the fabrication drawings |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2017-12-31 | 2017-12-30 12:05 | -1 | 2017-08-09 10:17 | Architectural - General | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | A planned Crossrail surveillance was completed at __ on 3rd August 2017 to check the processes and quality control for the manufacture of the GFRC cladding panels. Panels awaiting dispatch were checked where it was observed that a number of panels showed inconsistencies where the steel sickle is cat into the GRC mix. This being, the internal edge being chamfered at an approx... 45 degree angle to the inside face where the fabrication drawings (twf 250 and 251) requires a 90 degree bend (see attached images/photos). In addition, there appeared to be differing embedment depths when measuring the distance between the top of the sickle and the top of the GRC mix on either side. Two panels were measured at A and B. Panel 1 measured A = 65.2mm and B = 66.5mm (1.3mm difference) and Panel 2 measured A = 69.9mm and B = 73.5mm (3.6mm difference). This is shown in the photos/drawings attached. The embedment depth is unknown; as such the above differences cannot be confirmed. It is not known how many panels have been manufactured this way and what impact the reduced cover and inconsistent embedment may have on 1) the performance of the sickles and 2) alignment when supported to the steel structure.
| 02SL - Stations (LUL) | Cxxx-NCR-000440 | NCR | GFRC hardened testing for __ manufacture not carried out for 20 production weeks |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2017-12-31 | 2017-12-08 09:26 | -23 | 2017-08-09 10:33 | Architectural - General | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | A planned Crossrail surveillance was completed at __ on 3rd August 2017 to check the processes and quality control for the manufacture of the GFRC cladding panels. Testing of cured test boards was discussed as required by the GRCA Specification, and the /__ Offsite Manufacture ITP (Cxxx-SKC-A-ITP-Cxxx-50027) Section 5 GFRC Characteristics Control which requires weekly production testing (Water Absorption and Flexural Strength (MOR/LOP)) to be completed on manufactured cured test boards at both 7 and 28 days. At the time of the visit, the production week was Week 22. Testing had been completed at Day 4 (for Week 1) by a laboratory in Leipzig, Germany. The results for Water Absorption and Flexural Strength (LOP/MOR) were compliant with the Specification. However, since this initial testing, no further testing has been carried out. Test boards have been manufactured however these remain at __. Following the initial testing at Leipzig, proposed alternative test houses due to the cost of testing at Leipzig. A number of RFIs ( internal and CRL PTR) have been submitted however an agreement has yet to be fully reached. Communication and cost aside, no further testing has been completed which is not in compliance with the ITP and GRCA Specification which is written into the Cxxx Specification. This lack of testing puts at risk those panels manufactured (and installed) where testing has yet to validate their respective manufacture and performance.
| 02SL - Stations (LUL) | Cxxx-NCR-000441 | NCR | ETH Step in Lining Wall 4, Level-3 |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-10-30 | 2017-10-16 13:57 | -14 | 2017-08-11 07:32 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The attached photo shows a step in ETH Lining Wall 4 on L-3 in the escalator slab area. The step is situated behind the escalator upstand. Also see attached location mark up, position survey and cover survey
| 02SL - Stations (LUL) | Cxxx-NCR-000442 | NCR | ETH Step to IW46, Level-3 |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-10-30 | 2017-09-08 15:18 | -52 | 2017-08-11 09:10 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The attached photo shows that there is a step in IW46, Level-3. An as built and a cover survey have been done (attached).
| 02SL - Stations (LUL) | Cxxx-NCR-000443 | NCR | ETH Position of IW61, L-4 |  | Contr | COS | BOS - Bond Street Station (West) |  | 2018-05-31 | 2018-05-02 13:23 | -29 | 2017-08-11 09:16 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | IW61 has been cast out of position as per attached position survey. A cover survey has also been undertaken (attached). Cover is not out of tolerance, but position is. *** 08.03.2018 *** Please see attached updated surveys of the affected IW61 for review. In addition Drawing Cxxx-__-S-DDL-Cxxx-52150 has been marked up to clearly show the affected area. Below is some guidelines to be used when reading the surveys. MPS IW61 L-5 @A3 Rev 3.0 This view is from IW61 South looking North. Red Points are of the South Elevation and Black the North. Positive deviation from design means that surveyed points / wall is leaning towards the north. This applies to both faces of the wall. IW61 Cover Surveys 26.02.18 All readings are to be taken as the total cover to the rebar
| 02SL - Stations (LUL) | Cxxx-NCR-000444 | NCR | MPS L-5 CMS Topping Slab Slip Membrane Not Installed |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-12-31 | 2017-09-06 17:09 | -116 | 2017-08-23 06:37 | Structural Engineering - Structural Engineering - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The MPS L-5 CMS route topping slab has been cast without the slip membrane installed - as per detail highlighted on 'Cxxx-__-S-DDD-Cxxx-57151 JL mark up'. The extents of the slab which have been cast without this are shown on 'Cxxx-SKC-S-DWG-Cxxx-50363 JL Mark Up' & 'Cxxx-SKC-S-DWG-Cxxx-50857-JL Mark Up'.
| 02SL - Stations (LUL) | Cxxx-NCR-000445 | NCR | MPS L-2 Escalator Slab Missing Couplers in WB4 and Column C1 |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-12-31 | 2017-09-03 14:12 | -119 | 2017-08-18 09:35 | Structural Engineering - Structural Engineering - General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please see attached marked up drawings Cxxx-SKC-S-DWG-Cxxx-50859_CW and Cxxx-SKC-S-DWG-Cxxx-50480_CW which indicate the missing or out of position couplers within Waling Beam 4 and Column C1 at L-2.
| 02SL - Stations (LUL) | Cxxx-NCR-000446 | NCR | ETH- Escape Staircase Exposed Reinforcement on L-0.5 and L-1 |  | Contr | COS | BOS - Bond Street Station (West) |  | 2019-06-25 | 2019-04-11 15:00 | -75 | 2017-09-05 11:15 | Civil - Civil Engineering General | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Exposed reinforcement (1no. lacer) in IW34A (eastern elevation) on both L-1 and L-0.5 landing. See attached cover meter surveys for both areas. Note that the area where the exposed lacer is is the area that is highlighted in red. The location of the exposed lacer is marked with 'X'. *** 27/03/2018 *** Additional survey provided for -1
| 02SL - Stations (LUL) | Cxxx-NCR-000447 | NCR | ETH L0 - Sleeves for Fire Fighting Lift Drainage Channel |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-12-31 | 2018-09-21 13:58 | 264 | 2017-10-13 14:11 | Civil - Civil Engineering General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Due to insufficient builders work information at the time of the slab pours at Level 0, 165mm diameter circular holes were cast into the slab in front of the Fire Fighting Lift Shaft. 300mm x 300mm holes should have been cast (as per Levels -3 and -4). The holes are required to be larger than what has been installed to enable a 160mm ID blucher pipe to be installed as part of the firefighting lift channel drainage detail. Note this is the same issue as was raised in NCR-358 for L-1 and L-2.
| 02SL - Stations (LUL) | Cxxx-NCR-000448 | NCR | ETH L0 – Cover survey and damage to sloping face of L0 slab – east of GL B/2 |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-12-31 | 2018-01-17 10:24 | 17 | 2017-08-30 15:58 | Civil - Civil Engineering General | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | This NCR relates to Item 35 of Cxxx-NCR-000018 (and supersedes NCR-018). The sloping face of the ground floor beam was identified as potentially having insufficient cover as mars bars were protruding past the face of the beam. The mars bars have since been cut back flush. See attached Cxxx-__-S-DDL-Cxxx-52103 Outstanding Items - SB Mark-up, Cxxx-SKC-S-DWG-Cxxx-50012 Rev X01 SB Mark-up and Snagging sheet sign off
| 02SL - Stations (LUL) | Cxxx-NCR-000449 | NCR | MPS L-1 Incorrect Slab Starters for IW53 |  | Contr | COS | BOS - Bond Street Station (West) |  | 2018-06-20 | 2018-08-13 09:00 | 54 | 2017-09-07 07:01 | Structural Engineering - Structural Engineering - General | 5000 |  | Design | Repair | 3 (3-6k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | As per the attached email it was realised that there is a discrepancy in the connection detail between MPS slab at level -1 and Wall IW53 both above and below the slab. The wall above (L-1 to L0) was poured based on discussions between __ and to resolve this detailing issue. (see attached email) A similar detail is now proposed to deal with the discrepancy to the wall below (L-2 to L-1). This wall has not yet been constructed Please see attached marked up drawings. 30No. B20 starter bars were cast in to the MPS L-1 slab for IW53 as per drawing 50811, however, 38No. B25 starter bars are detailed within IW53 on drawing 50555 updated at the surface and soffit of the L-1 slab.
| 02SL - Stations (LUL) | Cxxx-NCR-000450 | NCR | Pre-cast Concrete Elements forming Ground Level Structure at Western Ticket Hall |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2018-09-23 | 2018-10-18 13:11 | 25 | 2017-09-08 12:42 | Structural Engineering - Pre-cast | 10000 |  | Documentation and Records | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | The (architectural) pre-cast elements forming the Western Ticket Hall structure at ground level are installed on site. These are exposed to the elements which may result in damage to the finishes. Works Information Specification JE50 - document reference Cxxx-SKC-A-RSP-Cxxx-50004 Clause 3205 - Protection - Protection of the works. This clause includes protection from the effects of weather until the building is watertight, against damage along with protective measures to prevent damage and marking. These activities should have been agreed and included in the Installation ITP - Cxxx-SKC-O4-ITP-Cxxx-50075. A means of progressive surveillance to ensure the quality requirements of the project are met should also be recorded and agreed.
| 02SL - Stations (LUL) | Cxxx-NCR-000451 | NCR | Transport damage to Coffer TP-38A |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-12-31 | 2017-09-26 15:30 | -96 | 2017-09-11 14:22 | Civil - Civil Engineering General | 5000 |  | Damaged | Reject | 3 (3-6k) | Complete | External Phenomenon - Other | Completed |  | Small end side of coffer TP-38A is damaged, as shown on attached pictures 001 to 003
| 02SL - Stations (LUL) | Cxxx-NCR-000452 | NCR | WTH Damaged Precast Beams |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-12-31 | 2017-10-03 14:24 | -89 | 2017-09-22 13:07 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | During Inspection on 08/09/2017 of the PCC beams prior to re-installation, some minor damage to the not architecturally exposed (not visible) side of the precast elements was found. See attached photos __01A and __02A
| 02SL - Stations (LUL) | Cxxx-NCR-000453 | NCR | Commence Electrical installation without ITP |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2017-12-31 | 2017-12-06 16:00 | -25 | 2017-09-13 14:04 | Electrical - Cable Management | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | Works commenced on the installation of Coffers CMS without an accepted ITP and MCR for bespoke coffer box. In addition and agreed method of installation and pre concrete pour sealant has been provided to Crossrail.
| 02SL - Stations (LUL) | Cxxx-NCR-000454 | NCR | MPS L-2 Incorrect Starter Bars Installed within IW21 at L-2 for IW53 |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-12-31 | 2018-10-02 16:09 | 275 | 2017-09-14 07:25 | Structural Engineering - Structural Engineering - General | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Drawings Cxxx-SKC-S-DWG-Cxxx-50554-C04 CW and Cxxx-SKC-S-DWG-Cxxx-50452 CW detail B16 Eazistrip within IW21 (for starters for IW53) however there were no starter bars detailed at the L-2+ slab level of 114.800 - 115.550. B16 coupled u-bars were installed instead of Eazistrip within IW21 however drawing Cxxx-SKC-S-DWG-Cxxx-50555-C01 details B25's within IW53, coupling into IW21. Above referenced drawings attached.
| 02SL - Stations (LUL) | Cxxx-NCR-000455 | NCR | MPS Lvl -4 Builderswork Hole Missing |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-12-31 | 2017-10-03 15:02 | -89 | 2017-09-21 07:44 | Structural Engineering - Structural Engineering - General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | Builders work hole has not been cast into level -4 slab where there is a construction joint between MPS slab and infill area of temporary piles. Centre of opening should coincide with joint. See attached marked up drawings Cxxx-SKC-S-DWG-Cxxx-50156-C01, Cxxx-SKC-S-DWG-Cxxx-50157-C01 and Cxxx-SKC-S-DWG-Cxxx-50384-P02 for affected rebar details and drawing Cxxx-SKC-P-DDA-Cxxx-52254 highlighting drainage pipe which this opening is for.
| 02SL - Stations (LUL) | Cxxx-NCR-000456 | NCR | WTH level 0 Column PC1b crack |  | Contr | COS | BOS - Bond Street Station (West) |  | 2018-03-31 | 2018-03-12 10:18 | -19 | 2017-10-13 15:36 | Structural Engineering - Pre-cast | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Column PC1b damage /crack to the not architecturally exposed (not visible) side of the precast element (north eastern face) just above baseplate (see photos PC1B crack - 20170728 and PC1B crack - 20170730)
| 02SL - Stations (LUL) | Cxxx-NCR-000457 | NCR | ETH MPS L-1 LW4 - Kicker and Couplers in correct position |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-12-31 | 2017-12-13 12:35 | -18 | 2017-10-03 15:32 | Structural Engineering - Structural Engineering - General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | It has been noted the Kicker for Lining Wall 4 at GL A has been cast in the incorrect position and an additional row of couplers were installed which are not required. The kicker has been cast at 1141 from GL 6 and the additional coupler position can be seen on the attached sketch "ETH-Sketch-LS-24-021017"
| 02SL - Stations (LUL) | Cxxx-NCR-000458 | NCR | Drainage Upstands in Eastbound & Westbound platforms |  | Contr | COS | BOS - Bond Street Station (West) |  | 2018-05-31 | 2018-04-24 12:14 | -37 | 2017-10-04 15:07 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Drainage upstands in the EB & WB platforms have not been cast to accommodate the architectural skirting to provide a minimum 6mm gap. See attached EB and WB upstand survey
| 02SL - Stations (LUL) | Cxxx-NCR-000459 | NCR | Excess cover to reinforcement - WTH l+1 central upstands |  | Contr | COS | BOS - Bond Street Station (West) |  | 2017-10-31 | 2017-11-02 17:34 | 2 | 2017-10-09 12:25 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | WTH Level +1. Central upstand reinforcement has been installed at incorrect level leaving excess cover to reinforcement. (see attached Upstands identified in WTH Level +1 3D Structural View)
| 02SL - Stations (LUL) | Cxxx-NCR-000460 | NCR | WTH Level +1 Chiller Room: 60N instead of 40N Concrete used in walls |  | Contr | COS | BOS - Bond Street Station (West) |  | 2018-02-28 | 2017-11-08 17:27 | -112 | 2017-10-09 14:42 | Structural Engineering - Structural Engineering - General | 0 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | 60N instead of 40N Concrete was used in two small wall pours (4m3 and 3m3) in the chiller room elevation T wall (0.5+ to 1.0+) & the lower exhaust slab. Refer to the referenced record packages Cxxx-SKC-C-LRC-Cxxx-50067 (page 47) and Cxxx-SKC-C-LRC-Cxxx-50068 (page 82), and related CRL comments sheets. See attached lab Report - CSJ 110248 and lab Report -CSJ 107252 for concrete strengths for the concerned pours. For locations see attached marked drawings Cxxx-SKC-LRC-Cxxx-50068 mark up lower exhaust slab and Cxxx-SKC-C-LRC-Cxxx-50067 mark up T wall ******location Attachments updated 17.10.2017**** See attached Cxxx-__-S-DDL-Cxxx-11091 markup and Cxxx-__-S-DDL-Cxxx-11096 markup *****proposal updated 30/10/2017****** Ignore Attachment reference Cxxx-__-S-DDL-Cxxx-11091 and refer to attached Cxxx-__-S-DDL-Cxxx-11096 Rev C05 - Mark UP as per Ben Scott e-mail attached
| 02SL - Stations (LUL) | Cxxx-NCR-000461 | NCR | ETH Escalator Slab - The movement Joint in Pour 2 only 10-20mm |  | Contr | COS | BOS - Bond Street Station (West) |  | 2018-10-05 | 2018-06-25 13:23 | -102 | 2017-10-13 10:55 | Structural Engineering - Structural Engineering - General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | An area of slab within pour 3 of the escalator has 10mm PFC __ C144 as shown on Cxxx-__-S-DDD-Cxxx-72217-C03 Section B. This area should have had 50mm __ installed as shown on Cxxx-__-S-DDB-Cxxx-53201-C03 Section 1. Please see attached marked up drawings of location where this has occurred.
| 02SL - Stations (LUL) | Cxxx-NCR-000462 | NCR | ES2 Corbel Installed Incorrectly (Cxxx-FCD-000573) |  | Contr | COS | BOS - Bond Street Station (West) |  | 2018-02-28 | 2018-02-28 14:40 | 0 | 2017-10-16 13:50 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Two options were given for the construction of the RC corbel and these options were included in Cxxx-FCD-000573(Sketch attachment DDN C734-FCD-573-FCD for Corbel Design). It was decided to install RC Corbel 1000 X 1000 X 365mm which included 10No. B20 positional couplers (5T, 5B) cast into LW5 in the MPS at L-2 for a 1000x1000mm corbel. . Due to program constraints and the imminent pouring of Lining Wall No.5 the Contractor was unable to install the corbel reinforcement as per the design.
| 02SL - Stations (LUL) | Cxxx-NCR-000463 | NCR | Internal Pre-cast Cladding - LIN 403 - Western Ticket Hall - Level -3 |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2019-02-02 | 2018-10-04 15:22 | -121 | 2017-10-23 14:40 | Architectural - Finishes | 1000 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Error by manufacturer in shipping or marking | Completed |  | CRL were invited to an Factory Inspection on 12.10.2017. ITP - Cxxx-SKC-O4-ITP-Cxxx-50032 Revision 4.0 - Activity - 2.13 - Production Control Units - Visual Inspection. A panel of each "Type" which in the context of the Works Information means "Tag Sheet" Reference Type as listed in the contents page of each Architectural Specification. This inspection relates to LIN-403 (Western Ticket Hall at Level -3) and the mould for LIN - 405. The quality of one of the two borescope holes cast into the panel is not acceptable to CRL as noted at the time of the inspection (notes attached).
| 02SL - Stations (LUL) | Cxxx-NCR-000464 | NCR | Platform skirting and GFRC interface |  | Contr | COS | BOS - Bond Street Station (West) |  | 2018-02-01 | 2018-12-17 17:19 | 319 | 2017-10-27 14:26 | Architectural - Finishes | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Following the installation of a sample of platform skirting on the westbound platform (24.10.17) it has become apparent to the Contractor that the interface between the bottom row of GFRC and the skirting does not align with the Works Information. See attached photos
| 02SL - Stations (LUL) | Cxxx-NCR-000465 | NCR | Contamination of Escalator E17 Step Chain |  | Contr | COS | BOS - Bond Street Station (West) |  | 2018-04-01 | 2018-05-29 08:24 | 58 | 2017-11-02 16:48 | Mechanical - Escalators | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | Slurry from adjacent core drilling works to E17 splattered the escalator step chain. See attached photos
| 02SL - Stations (LUL) | Cxxx-NCR-000466 | NCR | WTH Vent Shaft Level 3 South Opening |  | Contr | COS | BOS - Bond Street Station (West) |  | 2019-06-08 | 2019-03-26 16:43 | -74 | 2017-11-24 17:14 | Structural Engineering - Structural Engineering - General | 2000 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Reinforcement exposed on the top of the opening at L+3 on the western elevation Inner wall . See attached photos
| 02SL - Stations (LUL) | Cxxx-NCR-000467 | NCR | Winch points in room 6/915 L-5, ETH |  | Contr | COS | BOS - Bond Street Station (West) |  | 2018-06-30 | 2018-09-21 13:55 | 83 | 2017-12-07 11:40 | Civil - Civil Engineering General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | The Cast-in M16 Anchor Bolts have been cut off at SSL during the screed enabling works. This applies to 2 out of the 3no type FWP1 winch points within Draught Relief room 6/915 on L-5, ETH. See attached marked up copies of Cxxx-__-S-DDL-Cxxx-52155 C08 and Cxxx-__-S-DDL-Cxxx-52156 C04
| 02SL - Stations (LUL) | Cxxx-NCR-000468 | NCR | ETH Lightwell - Level -1 Walls - Missed cast-in channels on walls |  | Contr | COS | BOS - Bond Street Station (West) |  | 2018-09-01 | 2018-07-18 10:38 | -45 | 2017-12-08 15:15 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Cast in channels have not been installed on the ETH Lightwell walls along Gridline F+ See attached marked up drawings Cxxx-__-S-DDL-Cxxx-52115 C09 and Cxxx-__-S-DDL-Cxxx-52116 C08 for locations.
| 02SL - Stations (LUL) | Cxxx-NCR-000469 | NCR | ETH Lightwell - Insufficient cover to rebar on a section of RW3 (1st pour) |  | Contr | COS | BOS - Bond Street Station (West) |  | 2018-04-30 | 2017-12-21 15:21 | -130 | 2017-12-12 12:01 | Structural Engineering - Structural Engineering - General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | From cover meter surveys carried out on 08/12/17 (__'s) and 11/12/17 () it's been identified that a strip approximately 5m long by 0.5m wide at the __ chamber location has a reduced cover as shown on the attachments. The strip is approximately 2m high from L-1 SSL. See attached cover meter and mark-up drawing which shows the extent of the reduced cover.
| 02SL - Stations (LUL) | Cxxx-NCR-000470 | NCR | ETH - Water ingress to MPS L-4 NW room (PMC-2263) |  | Contr | COS | BOS - Bond Street Station (West) |  | 2018-07-31 | 2018-06-04 14:47 | -57 | 2017-12-13 16:09 | Structural Engineering - Structural Engineering - General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Not Defined | Completed |  | Further to a joint inspection with the Contractors representative J.Lord and Crossrail representative __ on 14/08/17 to the NW room at level-4 in the ETH, it was observed that two lining walls contained cracks with visible dampness. There are two leaks to the north lining wall and one to the west lining wall. The two small damp patches on the north lining wall are approx. 300mm’s high and are slightly damp only. It is agreed these leaks are minor and within spec and can be left as-is. The cracks on the west lining wall are measuring at 0.25 – 0.30mm’s and dampness visible. See attached related photos The contractor considers that this is within allowable limits for Tightness class 0 of applicable Eurocode 2 – Design of concrete structures Part 3, but is raising this NCR as requested in Cxxx-SCM-00009
| 02SL - Stations (LUL) | Cxxx-NCR-000471 | NCR | ETH - Water ingress to Lining wall 1, Level-4 (PMI-1751) |  | Contr | COS | BOS - Bond Street Station (West) |  | 2018-07-31 | 2018-07-18 10:42 | -13 | 2017-12-13 15:11 | Structural Engineering - Structural Engineering - General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | External Phenomenon - Not Defined | Completed |  | Further to a joint inspection with the Contractors representative S.Binder and Crossrail representative __ on 17/08/17 to lining wall 1 at level-4 in the ETH, 9 x cracks were observed and surveyed. Remedial works have already been instructed to crack numbers 1, 2, 6, 7, 9 under Cxxx-PMI-01751, (works not yet commenced on site). It is agreed that crack number 5 is small, dry and is considered to be within spec and can be left as-is. The contractor considers Crack numbers 3, 4 and 8 are within the allowable limits of Cxxx-__-S-RSP-Cxxx-00009 but is raising this NCR as requested in Cxxx-SCM-00009
| 02SL - Stations (LUL) | Cxxx-NCR-000472 | NCR | ETH L-5 Critical sump. Damaged couplers Pour 10 |  | Contr | COS | BOS - Bond Street Station (West) |  | 2018-04-01 | 2018-01-16 09:09 | -75 | 2017-12-19 09:18 | Civil - Civil Engineering General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The male threads of 23 number couplers for the Slab 10 pour in the critical sump are damaged and unusable. See attached marked-up Cxxx-SKC-S-DWG-Cxxx-50316-og with BM E205 that have been damaged, and Cxxx-SKC-S-DWG-Cxxx-50361-OG5 where a 5 number of BM-E215, 8 number of BM-E201 and 10 number of BM-E218 are affected. Please refer attached photos showing the affected bars.
| 02SL - Stations (LUL) | Cxxx-NCR-000473 | NCR | Platform Edge Screen - Progressing with installation of works without approved Prototype/Key Benchmark. |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2019-02-28 | 2019-06-12 09:16 | 104 | 2017-12-29 15:33 | Architectural - Finishes | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Works are currently being carried out on the Platforms for the installation of the PES Grilles. A considerable amount of work has been completed without acceptance of a Key Benchmark as discussed and agreed with Cxxx (recorded in MoM - CRL1-XRL-Z-MRC-Cxxx-50036 Revision 1.0). The importance of the Key Benchmark is that this is to be used to close out final comments on the PES Prototype and to establish an acceptable setting out/quality of works on site.
| 02SL - Stations (LUL) | Cxxx-NCR-000474 | NCR | Testing not carried out inline with Cxxx-SKC-O4-ITP-Cxxx-50132 |  | Contr | COS | BOS - Bond Street Station (West) |  | 2018-05-31 | 2018-03-19 11:36 | -73 | 2018-01-05 08:55 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Management Problem - Improper resource allocation | Completed |  | Quality Assurance testing not carried out inline with the approved ITP (Cxxx-SKC-O4-ITP-Cxxx-50132) During the reinstatement works associated with the Haunch of Venison Yard tried to book someone to carry out a NDM test over a week in advance inline with the approved ITP. continued to try and arrange this tester up until the point of testing (prior to laying asphalt), the decision was then made to carry out a plate bearing testing in accordance with Cxxx-SKC-D-RSP-Cxxx-50001.
| 02SL - Stations (LUL) | Cxxx-NCR-000475 | NCR | WTH - Wall 15 and Wall 17 Damaged Concrete Panels |  | Contr | COS | BOS - Bond Street Station (West) |  | 2018-06-30 | 2018-06-06 14:11 | -24 | 2018-01-09 10:09 | Structural Engineering - Pre-cast | 500 |  | Damaged | Reject | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | 6 Number Precast Concrete Panels for the WTH Escalator Area -3 Level - Wall 15 and 17 have been damaged during transport from NL to the UK. See attached: - Marked up drawings for panel locations: Cxxx-SKC-A-DWG-Cxxx-50585 - NCR 475 and Cxxx-SKC-A-DWG-Cxxx-50591 - NCR 475 - Photo IMG_0001 - panels in lorry - Photos KW001 (1) & KW001 (2) for Panels code 17-72 and 17-73 - Photos KW013 (1) to KW013 (4) for Panels code 15-70 and 15-61 - Photo KW015 for Panels code 15-18 and 15-17
| 02SL - Stations (LUL) | Cxxx-NCR-000476 | NCR | ETH Vent Shaft - Pour 5 - VS3 Earth plate position. |  | Contr | COS | BOS - Bond Street Station (West) |  | 2018-03-30 | 2018-02-05 16:50 | -53 | 2018-01-17 15:34 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The earth plate VS3 in Wall 6 Pour 5 of the ETH Vent shaft has been cast incorrectly. This should have been cast flush with the top of the wall 141.100 as seen in detail 1 of attached drawing Cxxx-SKC-E-DDA-Cxxx-52592. However it has been mistakenly pulled higher after installation as seen in the attached photo "Vent Shaft Wall 6 - VSU - 5 Wrong Level."
| 02SL - Stations (LUL) | Cxxx-NCR-000477 | NCR | ETH L-5 Cable tray installed blocking Duct work inspection hatch |  | Contr | COS | BOS - Bond Street Station (West) |  | 2018-05-31 | 2019-10-15 18:55 | 502 | 2018-01-18 14:39 | Electrical - Electrical Engineering General | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A power cable tray has been installed in the circulating area from room the __R connecting to the main CMS trays. The tray a has taken an alternative route to the design and blocks access to the inspection doors of the ducts above. See attached "ETH Level -5 Mech Systems inaccessibility_TJ_180109" Please see the attachment Closure mark up.The NCR is now complete
| 02SL - Stations (LUL) | Cxxx-NCR-000478 | NCR | ES1 GFRC Quality Issues |  | Contr | COS | BOS - Bond Street Station (West) |  | 2018-07-31 | 2019-07-04 15:42 | 338 | 2018-01-25 14:26 | Architectural - Finishes | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | There are approx. 30 GFRC panels in the WTH ES1 lower escalator barrel GFRC cladding that do not meet the required quality standards: - Panels outside the accepted colour range of the GFRC Cladding Sample: Cxxx-SKC-A-LRC-Cxxx-50030 - Panels alignment outside JH40.3000 tolerance limits. See attached ES1 GFRC Mark Up.pdf for locations and attached photos of quality issues. has proceeded with the installation of panels in this area without addressing all the comments made following a Crossrail benchmark inspection; see referenced - Tunnel and Platform Linings - GFRC Benchmark: Cxxx-SKC-A-MCR-Cxxx-50069 inspection date 30/05/2017 Code 2 status. and ES1 Benchmark Inspection Sheet 26.06.17. This NCR supersedes Cxxx-NCR-000413 relating to acceptance of the ES1 Benchmark.
| 02SL - Stations (LUL) | Cxxx-NCR-000479 | NCR | ETH - Wall IW73 Builders Work Opening - Built to Incorrect Height |  | Contr | COS | BOS - Bond Street Station (West) |  | 2018-05-31 | 2018-02-16 13:03 | -104 | 2018-01-23 14:43 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | Builders work opening in ETH -3 4/934 - Wall IW73, built to the incorrect height in a RC wall. Survey set-out error. Design IL +110.860m. Actual IL +111.220m. All other dimensions are as per design. See attached BW Opening Location
| 02SL - Stations (LUL) | Cxxx-NCR-000480 | NCR | ETH Fabrication of Column PC2 |  | Contr | COS | BOS - Bond Street Station (West) |  | 2018-05-31 | 2018-07-18 10:46 | 48 | 2018-01-26 10:42 | Civil - Civil Engineering General | 500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The ETH Column Base Plate PC2 has been fabricated to MBL detailed design drawing Cxxx-SKC-S-DWG-Cxxx-50965-P03; with 8 holes instead of 10. See attached PC2 baseplate photos incl comments
| 02SL - Stations (LUL) | Cxxx-NCR-000481 | NCR | ETH Vent shaft pour 7 - water added to load 4 & 5 giving W/C ratios exceeding specified limit of 0.45 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-07-05 | 2018-07-18 13:34 | 13 | 2018-02-06 17:07 | Civil - Civil Engineering General | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Pour 7 of the ETH vent shaft commenced at 20:00hrs.on Wednesday 24/01/18. During pour 7 (of 9) there were complications with the concrete from the 4th and 5th (final) wagons of the pour, and water was added. On further investigation it was found that the amount of water added exceeds the maximum w/c ratio of 0.45 specified in the concrete specification. (Cxxx-__-S-RSP-Cxxx-00009 Rev 14.0) Load 4 - 533397 Batched W/C ratio - 0.44 Water added in transit - 1.4L/m3 W/C ratio upon arrival at site - 0.44 Water added at site - 81.9L W/C ratio after water addition at site - 0.47 Time on-site - 2hr 20mins Age of concrete at time of Leave Site - 2hr 54mins Load 5 - 533398 Batched W/C ratio - 0.41 Water added in transit - 7.3L/m3 W/C ratio upon arrival at site - 0.44 Water added at site - 179L W/C ratio after water addition at site - 0.53 Time on-site - 1hr 59mins Age of concrete at time of Leave Site - 2hr 28mins
| 02SL - Stations (LUL) | Cxxx-NCR-000482 | NCR | WTH L+1 Soffit |  | Contr | COS | BOS - Bond Street Station (West) |  | 2018-06-30 | 2018-08-14 08:04 | 45 | 2018-02-01 11:07 | Civil - Structural Engineering | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The as struck condition of the WTH L+1 slab soffit (GL- G-J/-3-4), has small areas of honeycomb in various locations, and some other areas have excess tie wire and exposed concrete spacer blocks. Please see attached photos and WTH L plus 1 Slab Soffit Defect Markup
| 02SL - Stations (LUL) | Cxxx-NCR-000483 | NCR | 12 Core Fibre Cable Cxxx-DAT-00189 Damaged |  | Contr | COS | BOS - Bond Street Station (West) |  | 2018-06-30 | 2018-10-02 10:24 | 94 | 2018-02-01 11:37 | Communications and Control Systems - Fibre Optic Network | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 12 Core Fibre Cable Cxxx-DAT-00189 failed the Fibre testing procedure, upon inspection the cable was damaged at the 30 meter mark of a 95 meter run.
| 02SL - Stations (LUL) | Cxxx-NCR-000484 | NCR | WTH - Elevation C Level 1.0+ Chiller Room Bar Mark E97 NF3 replacement |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-02-19 | 2018-02-07 15:14 | -12 | 2018-02-02 16:05 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Unable to instal Bar Mark "E97" via cast in couplers (to level 1.0+ slab) due to them being installed in the incorrect location as per reference drawing Cxxx-SKC-S-DWG-Cxxx-50412 C03. The adjoining couplers were cast within the slab 25mm west of there design location.
| 02SL - Stations (LUL) | Cxxx-NCR-000485 | NCR | ETH Level-2 _ 3/091N BW Opening |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-04-27 | 2019-04-10 16:53 | 348 | 2018-02-08 14:22 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | BW opening in wall "3/091N" has been cast in the wrong position as detailed on drawing "Cxxx-SKC-M-DDA-Cxxx-69120". See attached photo for the opening in question. The opening should have been cast at IL 117.464 but has in fact been cast at IL 117.330. *****Update 21/02/2018********************************** “3/091N is the wall reference number, which is wall IW33 on ETH level -2. The opening is now clearly highlighted on the marked-up drawings including the Cxxx structural concrete drawing.” ("Wall Plan NCR-000485" & "Location Plan NCR-000485"). Furthermore included is: PDF of TB-071 – TB071 Rev13.0, Void shown on Cxxx drawing – Cxxx-__-S-DDC-Cxxx-56303 and Rebar drawing - Cxxx-SKC-S-DWG-Cxxx-50103-C06.
| 02SL - Stations (LUL) | Cxxx-NCR-000486 | NCR | ETH Vent Shaft Pour 8 wall 1 - position. |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-04-27 | 2018-04-23 10:09 | -4 | 2018-02-14 12:10 | Civil - Civil Engineering General | 0 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please see attached sketch showing the as-built position of the internal elevation of the wall between GL/5 and GL/6. The position of this wall is out of construction tolerance. The worst instances are 24mm out of position, increasing the size of the opening and 13mm out of position decreasing the size of the opening.
| 02SL - Stations (LUL) | Cxxx-NCR-000487 | NCR | ETH L0 Walls - Omitted Starters in Internal Walls - L0 to L+1 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-03-02 | 2018-03-01 16:47 | -1 | 2018-02-15 17:26 | Civil - Civil Engineering General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | During a Cxxx review of Contractor rebar detail drawings to walls between levels 0 to +1 at the ETH, it has been discovered that some vertical rebar detailing has been omitted. Plan drawing attached ‘Walls affected by omitted rebar detailing.pdf’ provides an overview of walls that are affected. Marked up drawings ‘DDN C811 ETH - Required Omitted Starters in Internal Walls - L0 to L+1.pdf’ provides details of what is required to bring the affected rebar wall detail drawings in alignment with Cxxx design intent. The problem appears to be that the rebar intent Note ‘Vertical bars to be extended tension anchorage into top most and bottom most horizontal elements – e.g. raft’ in drawing Cxxx-__-S-DDJ-Cxxx-72700 C03 has not been following in every case.
| 02SL - Stations (LUL) | Cxxx-NCR-000489 | NCR | WTH Level 1.0+ Northern Edge Beam Out of Tolerance Sandstone Lintels |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-06-17 14:12 | -79 | 2018-02-15 13:57 | Architectural - General | 100000 |  | Workmanship | Repair | 1 (>60k) | Complete | Management Problem - Inadequate supervision | Completed |  | Post completion of the phase 02 pour of level 1.0+ reinforced concrete slab on the 20th of December 2017 a survey has been completed identifying 7no. lintels on the gridline 01 edge beam which are outside the specified tolerance of ±5mm (KH10).
| 02SL - Stations (LUL) | Cxxx-NCR-000490 | NCR | NCR LIN-403 substructure bolts strength class |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-05-30 | 2018-04-26 14:06 | -34 | 2018-02-20 15:24 | Archaeology - General | 0 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | At the locations marked on the attached drawings bolts with strength class 70 are used instead of strength class 80.
| 02SL - Stations (LUL) | Cxxx-NCR-000491 | NCR | WTH L+1 OSD Cast In Plate, North Elevation and south Elevation |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-09-09 | 2019-10-17 11:33 | 403 | 2018-02-23 16:24 | Civil - Civil Engineering General | 2000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please see attached photo. Concrete hasn't been poured to the underside of the OSD plates on the northern elevation. **** 12/03/18 **** See attached survey showing affected plates and depths and included extract from TB071 extract
| 02SL - Stations (LUL) | Cxxx-NCR-000492 | NCR | Column C1 extension - missing QA |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-12-31 | 2018-10-31 16:49 | -61 | 2018-02-23 14:26 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | have been unable to locate records for the additional pour undertaken to extend Column C1 ETH L-1, as detailed in Cxxx-FCD-000431. This effects the close out of attached Record Pack - ETH L-1 Internal Walls Part 1
| 02SL - Stations (LUL) | Cxxx-NCR-000493 | NCR | LIN-403 escalatorbox Access panel area hook amendments |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-04-30 | 2018-08-13 09:04 | 105 | 2018-02-27 08:37 | Civil - Civil Engineering General | 500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Due to the subconstruction being slightly warped and the hooks in the access panels not all being placed within tolerance, the panels in the Access panel area cannot be placed in line with the precast panels above and underneath. Please refer to attached photo 1.
| 02SL - Stations (LUL) | Cxxx-NCR-000495 | NCR | WTH Level -5 Room 7/772 South Wall Sump Room - Blockwork Stepping |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-06-29 | 2018-06-12 09:17 | -17 | 2018-02-27 18:26 | Architectural - Brickworks/Blockworks | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | To account for various design issues in lintel height the wall shown in the attached picture has various steps and changes to blockwork levels.
| 02SL - Stations (LUL) | Cxxx-NCR-000496 | NCR | Drainage upstands in the platform cross-passages and concourse halls - CP1, 2, 3, 4, 5, 7, 8, 9, 10, CH2, CH3 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-04-30 | 2018-12-05 18:11 | 219 | 2018-03-08 19:09 | Civil - Drainage | 2000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | The drainage up-stands in the cross passages and concourse halls (CH2 and CH3) have not been cast to accommodate the architectural skirting to provide a minimum 6mm gap.
| 02SL - Stations (LUL) | Cxxx-NCR-000497 | NCR | Incorrect location of drainage pipes |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-07-20 | 2019-07-31 12:44 | 11 | 2018-05-04 09:06 | Civil - Civil Engineering General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A design change increasing the width of the cross passages caused drainage pipes to become exposed after up-stands were brought into the correct line. Mark up and photos to be provided.
| 02SL - Stations (LUL) | Cxxx-NCR-000498 | NCR | LIN-403 escalator box substructure bolts strength class |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-04-05 | 2018-04-10 08:29 | 5 | 2018-03-02 17:11 | Architectural - Walls | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Error by manufacturer in shipping or marking | Completed |  | Further to Cxxx-NCR-000490 bolts with strength class 70 instead of 80 were also used on the locations marked on the attached drawings.
| 02SL - Stations (LUL) | Cxxx-NCR-000499 | NCR | LIN-403 escalatorbox horizontal brackets Access Panels not fitting |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-06-13 | 2018-10-09 07:53 | 118 | 2018-03-05 10:27 | Architectural - General | 2000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Interfacing problems | Completed |  | Due to the amount of rebar in the walls, it was not possible to position the anchors at the right positions. The brackets as located on the attached marked drawings had to be remade to fit.
| 02SL - Stations (LUL) | Cxxx-NCR-000500 | NCR | WTH LIN-403 L0 __ anchor close to door opening |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-07-02 | 2018-08-15 17:09 | 44 | 2018-03-05 10:38 | Architectural - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | On approved drawings an incorrect substructure detail was drawn for this location (WTH L0 wall on GL G). During the setting out of the anchors it became clear that an anchor would be located too close to the edge of the concrete.
| 02SL - Stations (LUL) | Cxxx-NCR-000501 | NCR | ETH Level 0 IW23 - U bars for NLBW1 future connection not installed |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-05-25 | 2018-07-18 13:39 | 54 | 2018-03-12 09:03 | Structural Engineering - Structural Engineering - General | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | No U bar cast on IW23 for future connection with NLBW1. U bar is not shown on steel drawing 50652 but drawing 50167.
| 02SL - Stations (LUL) | Cxxx-NCR-000502 | NCR | WTH Loose Holding Down Bolts to RC Columns |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-02-28 | 2019-06-28 16:10 | 120 | 2018-04-24 13:46 | Civil - Civil Engineering General | 0 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Following a reinforcement inspection of W-W-24 at WTH, Cxxx (__) identified "loose" M36 nuts to column PC3 hold down bolts directly adjacent to the W-W-24. conducted a survey of precast column base connections along gridline 4/H-L and L/1-3 to identify any further "loose" connections. Results of survey are as per "Column Bolt Survey" attachment whereby a number of column to base plate connections were identified as hand/finger tight. Requirement for connections are to be "snug tight" as per "BS EN1090-3:2008 8.3.1 Non-preloaded connections"
| 02SL - Stations (LUL) | Cxxx-NCR-000503 | NCR | Damage to column stone PC2 ETH |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-03-28 | 2020-02-21 12:07 | 330 | 2018-03-09 16:04 | Architectural - General | 3000 |  | Material | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The ETH column PC2 Stone panelling shows the following damage: - 1 small chip (photo 20180306_172056); - 1 big chip (photo 20180306_132415).
| 02SL - Stations (LUL) | Cxxx-NCR-000504 | NCR | WTH, Lvl 0, Grout loss stains down signed off RC walls |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-06-15 | 2018-07-18 13:44 | 33 | 2018-04-04 17:26 | Architectural - General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The walls to the South and West of the WTH Entrance Hall L0 have been previously signed off prior to the grout loss. During the placement of concrete for the L+1.0 slab the compriband failed allowing grout to leak through to the wall and stain the surface.
| 02SL - Stations (LUL) | Cxxx-NCR-000505 | NCR | Damaged __ fibre cable |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-07-17 | 2019-02-28 11:51 | 226 | 2018-07-10 15:22 | Communications and Control Systems - Fibre Optic Network | 2000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Location -CER I to CER II 40meters approx from CER I. For fibre cable that had been previously installed and verification testing completed. Upon __ splicing the cables they undertook retesting which indicated damaged cable. Test results confirmed damage at 40 meters from CER
| 02SL - Stations (LUL) | Cxxx-NCR-000506 | NCR | Platform and Tunnel - GFRC Installation |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2019-03-29 | 2018-11-23 15:28 | -126 | 2018-06-12 09:36 | Architectural - Finishes | 5000 |  | Supervision/Management | Repair | 3 (3-6k) | Complete | Management Problem - Inadequate supervision | Completed |  | Quality Inspection carried out on GFRC generally. Invited to attend a GFRC Benchmark Inspection to allow sign off and completion of benchmark acceptance however, inspection did not take place. Whilst on site a general quality surveillance and assessment of protection of installed works was completed with photographic evidence attached to this observation. Refer to Cxxx-SKC-A-RSP-Cxxx-50057 - Cxxx-ATK-N2-RSP-CR002-00001 - Section JH40 - Clause JH40.3900 GFRC Installation - .3905 - Finishes - "Surface areas likely to be damaged during installation or by other Contractors shall be fully protected until completion of all work in the area of installation. If during installation any damage does occur, this shall be rectified by the Sub-contractor, progressively and shall not be allowed to accumulate." Areas of GFRC remain unprotected and are being damaged. Generally poor house keeping with rubbish and equipment being left alongside and leaning against in many instances the final installation of the GFRC.
| 02SL - Stations (LUL) | Cxxx-NCR-000507 | NCR | __ Package/LIN - 405 |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2019-01-31 | 2018-11-28 14:03 | -64 | 2018-03-14 16:01 | Architectural - Finishes | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Bronze cladding has been installed on site without an accepted design/drawings and an ITP in place for installation.
| 02SL - Stations (LUL) | Cxxx-NCR-000508 | NCR | ETH _Lvl-4 to-3.5 Main Fire Escape Staircase stairflight 5 & 6 : Missing Pre-Pour Inspection Check sheet |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-05-15 | 2018-06-04 15:51 | 20 | 2018-03-16 17:32 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Upon compilation of the Record Pack for the ETH: Main Fire Escape Staircase, the L-4 to L-3.5: Flight 5 & 6 pre pour inspection check sheet has been mislaid and cannot be located for use in the Record pack.
| 02SL - Stations (LUL) | Cxxx-NCR-000509 | NCR | ETH L-2 and L-1 IW 21 Missing Couplers |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-04-23 | 2018-04-23 10:19 | 0 | 2018-03-19 17:05 | Civil - Structural Engineering | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | It has been found when constructing the sections of slab as highlighted on the attached drawings that the couplers required within IW21 have not been installed. At L-2 this has been raised as Cxxx-PWK-00080 At L-2 the IW21 drawing Cxxx-SKC-S-DWG-Cxxx-50293-C02 does not indicate couplers are to be installed, these couplers can be seen on Cxxx-SKC-S-DWG-Cxxx-50057-X01. At L-1 the IW21 drawing Cxxx-SKC-S-DWG-Cxxx-50104-C06 does reference Cxxx-SKC-S-DWG-Cxxx-50297-C03 however this note has not been action-ed and no couplers installed.
| 02SL - Stations (LUL) | Cxxx-NCR-000510 | NCR | WTH Column Verticality out of tolerance - Structural NCR |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-06-05 | 2018-07-18 13:36 | 43 | 2018-04-24 12:55 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following a review of the as-built position and verticality of the installed structural precast columns to the WTH. It has been made apparent through surveys that the precast is out of the specified tolerance for verticality. Verticality in reference to plan within the KH10 (KH10.3208 C iii) is +-7.5mm, as shown on the attached survey information this is installed to a maximum 14mm. It has been agreed that this NCR will cover structural concerns only. Additional NCrs to be raised to resolve Architectural effects Attached is a PDF survey and a Pointcloud 3D scan
| 02SL - Stations (LUL) | Cxxx-NCR-000512 | NCR | Fire dampers inaccessible (ETH -5 FOSC rooms) – Unable to maintain replace |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-06-25 | 2018-05-31 14:59 | -25 | 2018-04-05 10:29 | Fire - Fire Systems & General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Various M&E services have been installed on ETH Level -5 outside FOSC rooms 6/737 and 6/738 , which is obstructing __ fire dampers which are located away from the walls: AS-E-FD008 AS-E-FD007 . The access and maintenance to damper controls, VCDs, inspection points and general removal/replacement capabilities is not possible. These fire dampers are for ancillary supply ductwork. Previously this was raised as an issue under CRL-OBS-16975. It was subsequently closed after dampers were moved further into lobby areas. CMS has now been installed underneath this too and equipment is now inaccessible again. . This installation is conflicting the Cxxx Work Information; Crossrail programme functional requirements CPFR5011. All equipment should follow the required access and maintenance attributes within.
| 02SL - Stations (LUL) | Cxxx-NCR-000513 | NCR | WTH L0 upstands adjacent to radius column |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-07-01 | 2018-08-13 09:08 | 43 | 2018-04-24 10:48 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | See attached photo. Cxxx upstand broken back to facilitate the installation of the radius column that is situated on GL/E.
| 02SL - Stations (LUL) | Cxxx-NCR-000514 | NCR | WTH - Bracing to L0 South Elevation Columns |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-30 | 2019-02-14 17:19 | -228 | 2018-03-27 14:25 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Structural bracing to L0 south elevation precast columns (Grid 4/H-L) has not been installed prior to removal of edge beam back propping in contravention to temporary support requirements on Cxxx documentation.
| 02SL - Stations (LUL) | Cxxx-NCR-000515 | NCR | Platform FFL out of tolerance |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-12-31 | 2019-03-05 09:12 | 64 | 2018-05-04 09:28 | Architectural - Flooring | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Several areas of the platform floor finishes have been identified as out of tolerance in areas close to the PSD doors. This is causing the PES doors to scrape in some areas.
| 02SL - Stations (LUL) | Cxxx-NCR-000516 | NCR | Coring of openings WTH slab L-2/-4, Room 3/780 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-07-11 | 2019-05-13 17:11 | 306 | 2018-03-27 08:37 | Architectural - Brickworks/Blockworks | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In line with Cxxx-RFI-004357, 4no. 150mm openings at 400mm centres were to be cored. Due to workforce mistake one of the opening was shifted by 200mm changing the centre-to-centre dimension to 600mm and 200mm (see attached sketch - as-built spacings). The other opening is installed at the design spacing of 400mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000517 | NCR | Inspection and Test Plan not being followed TEW Communications |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-05-04 | 2018-07-24 09:55 | 81 | 2018-03-27 09:55 | Communications and Control Systems - Fibre Optic Network | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | For cabinets DC5 and DC6 and cabling, TEW + Inspection and Testing Plan process not being followed: When IRN process was undertaken it was found that various check sheets and cable drum numbers were not available. • Drum test Certs don’t tie up as the documentation is saying 1 x 12 core and 1 x 24 core. However all cabling associated with these IRN is 12 core fibre. • Delivery note in the file doesn’t tie in to the drum test Certs that’s been carried out. They used the PIC number as there ID for the drum on the test cert • Drum test certs don’t tie into the information inputted onto the cable and wiring schedule • PULL test documentation missing on DC6
| 02SL - Stations (LUL) | Cxxx-NCR-000518 | NCR | ETH, Level 0 - Kicker to IW21 |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2018-06-20 | 2018-08-23 10:32 | 64 | 2018-03-30 14:15 | Structural Engineering - Concrete Member | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | ETH, Level 0 - IW21 kicker should have been poured monolithically with the slab which is not what has occurred on site. The Contractor are to survey and attach a marked up plan drawing to show the extent of this kicker and propose a remedial action.
| 02SL - Stations (LUL) | Cxxx-NCR-000519 | NCR | Builders Works - WTH -3 - MH46 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-05-18 | 2018-06-05 08:32 | 18 | 2018-04-05 08:47 | Architectural - General | 500 |  | Planning | Repair | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | WTH -3 SLAB / -4 SOFFIT - Builders Work Opening MH46. Opening was originally requested and approved in Cxxx-RFI-002425 (Opening "I"). CRL stipulated that the opening was OK to core if no reinforcement was damaged in the coring process. This is a 100mm diameter opening for a drainage pipe. The coring has been completed, and one single rebar has been cut in the soffit (bottom mat). There is no damage to rebar on the slab (top mat). Refer to "MH46 __.pdf" for details of the bar which has been cut, and the surrounding reinforcement.
| 02SL - Stations (LUL) | Cxxx-NCR-000521 | NCR | Earthing, Traction Earthing, LVA, LVB, LVE and PMR Tray installation at ETH -5 Circulation Areas |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-08-31 | 2018-07-17 13:57 | -45 | 2018-07-11 08:29 | Electrical - Earthing & Bonding | 2000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | As per CRL-OBS-21542 CRL FAE Elec were invited to witness the Earthing, Traction Earthing, LVA, LVB, LVE and PMR Tray installation at ETH -5 Circulation Areas. Please see below CRL comments from the inspection (IRF 67) carried out on the 08/03/18. Outside the LV Switchrooms there is approximately a 3m section where maintenance access is restricted for various Traywork.
| 02SL - Stations (LUL) | Cxxx-NCR-000522 | NCR | Lack of Access to Fire Damper Actuators ETH -5 (6/713,6/778,6/687) |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-06-22 | 2019-04-12 09:32 | 294 | 2018-04-16 09:19 | Mechanical - Mechanical Engineering General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Various other M&E services have been installed in the ETH Level -5 Lobby which are obstructing the access to the following dampers: GE-E-FD002 GE-E-FD004 AS-E-FD003 GE-E-FD005
| 02SL - Stations (LUL) | Cxxx-NCR-000523 | NCR | Cracks in PC5 & PC5A |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-08-10 | 2018-10-05 14:19 | 56 | 2018-05-03 16:42 | Architectural - General | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Columns PC5&5A damage /crack to the not architecturally exposed (not visible) side of the precast elements and a chip on the top of PC5A (see attached photos )
| 02SL - Stations (LUL) | Cxxx-NCR-000524 | NCR | WTH Column Verticality out of tolerance - Architectural Elements |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-12-31 | 2019-09-12 15:10 | 255 | 2018-07-03 16:33 | Architectural - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Column Verticality out of tolerance as detailed in Cxxx-NCR-000510 This NCR is to cover the follow on effects of this NCR with respect to Architectural elements
| 02SL - Stations (LUL) | Cxxx-NCR-000525 | NCR | Electrical ducts in the cross passages and concourse halls |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-07-22 | 2019-08-30 13:48 | 404 | 2018-05-22 08:20 | Electrical - Cable Management | 0 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Electrical conduits in cross passages and concourse halls have been installed using plastic conduits which protrude approximately 200mm above the concrete drainage channel creating an increased fire hazard. Conduits should have been installed below the line of the concrete upstand with a cast iron sleeve to remove any Fire Hazard. Conduits should have been cut down prior to pouring the concrete upstand. **** Update 20.06.18 **** Mark-up of locations attached - NCR-000525-Location Markup - Rev 1.pdf
| 02SL - Stations (LUL) | Cxxx-NCR-000526 | NCR | WTH - Level -4 NLB RC Wall Builders Work Hole Missed |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-02-28 | 2019-02-12 12:36 | -16 | 2018-04-24 08:59 | Architectural - Brickworks/Blockworks | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A 150mm diameter builderswork/MEP opening was not boxed out of Level -4 NLB RC Wall 5/786N. Wall was altered to RC from blockwork under Cxxx-RFI-004071/PMI 1804
| 02SL - Stations (LUL) | Cxxx-NCR-000527 | NCR | ETH -1 - Builders Works MH155 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-05-31 | 2019-05-14 10:45 | 348 | 2018-04-24 15:22 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | . Refer to "MH155 NCR Sketch" for details. Design CL is 122.430. Cored CL 121.564. Wall thickness is 300mm, core was drilled 200mm through the wall. RC remains intact. This was cored from the South side of the wall. It is confirmed that only one vertical bar and one horizontal bar has been cut, in the Southern face of the wall. Reduced cover to one horizontal bar. No damage to the Northern face rebar. The builders work has not been cored at the correct location, and will not until resolution of this NCR. The opening is however still required at the original location. ***********************UP DATE: 01/03/2019******************* Builders Work MH155 which was initially partially cored at the incorrect location, is now cored right through (north- south) this will identify exact number of cut bars and appropriate remedial action .
| 02SL - Stations (LUL) | Cxxx-NCR-000528 | NCR | Scratched Terrazzo Tiles on the platform |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-08-30 | 2018-08-09 09:09 | -21 | 2018-05-01 15:06 | Architectural - Flooring | 10000 |  | Damaged | Repair | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Some terrazzo tiles have be installed on the platforms with a scratch on the surface of the tile.
| 02SL - Stations (LUL) | Cxxx-NCR-000529 | NCR | P&T Damaged MEP Electrical Ducts |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-03-28 | 2019-08-23 11:45 | 148 | 2018-05-08 11:01 | Architectural - General | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | At 6 location Electrical ducts have been damaged during up-stand scabbling works at locations :CP2 (NE), CP4 (NE and SW) and CP5 (NE) ,CP8 SE end, CP10
| 02SL - Stations (LUL) | Cxxx-NCR-000530 | NCR | ETH L0 NLBW1 Starter bars out of position |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-05-30 | 2018-06-04 16:07 | 5 | 2018-05-08 11:50 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the pre-pour inspection it has been identify that approx. 50% of the starter bars within the eazi-strip were out of position (too far close to the west face of the wall) and there fore cover will be insufficient. Some of this bars have been bent to achieve minimum cover but this is not acceptable.
| 02SL - Stations (LUL) | Cxxx-NCR-000531 | NCR | ETH L+1 Slab Pour 2 - 5 no. bars not installed within Pour 1 at Beams 13/21 connection at IW36 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-05-29 | 2018-06-04 16:21 | 6 | 2018-05-08 12:53 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 5 no. Bar Mark E58 from drawing 50178 weren't installed within ETH L+1 Pour 1 on Beam 13 at IW36 location. As a result of this omission 5 no. Bar Mark E14 from drawing 50178 have no couplers to connect to within the existing construction joint. See picture attached.
| 02SL - Stations (LUL) | Cxxx-NCR-000532 | NCR | WTH LIN-403 L0 wall 14 anchor positions |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-08-06 | 2018-08-01 12:20 | -5 | 2018-05-08 14:26 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Due to clashes between the anchors and the rebar in wall 14 on WTH L0, new positions for the anchors in the substructure are required. See attached 180611_mark up of affected area.pdf
| 02SL - Stations (LUL) | Cxxx-NCR-000533 | NCR | PC8B column baseplate without holes |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-12-31 | 2018-09-21 14:17 | -101 | 2018-05-08 16:44 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The blank baseplate which was accepted to be cast in precast column PC8F (E) (GL 4 / E+12mtrs) on the ETH as per Cxxx-RFI-004263, has been cast in precast column PC8B (E) (GL 4 / E+6 mtrs). The precast Column PC8F (E) has been cast with the baseplate of PC8B (E) as per Cxxx-SKC-S-DWG-Cxxx-50994 (attached)
| 02SL - Stations (LUL) | Cxxx-NCR-000534 | NCR | Scada & Telephony cabling ETH & WTH |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-06-11 | 2018-05-30 08:19 | -12 | 2018-05-10 09:28 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Other | Completed |  | IRN paperwork to support the Scada & Telephony required for Dynamic Testing ( Appendix 8 items only) are missing the Cable drum allocation sheets for each cable installed.
| 02SL - Stations (LUL) | Cxxx-NCR-000535 | NCR | WTH Level 0 - Column PC2a - Ommited __ Couplers for OSD Upstand |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-12-31 | 2018-11-22 13:10 | -39 | 2018-05-17 15:00 | Civil - Civil Engineering General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | WTH Level 0 OSD upstand at location grid L/4 (MU Cxxx-__-S-DDL-Cxxx-11104 Rev C07) is detailed to tie into precast column PC2a via bar mark E03 B16 lenton thread end (Cxxx-SKC-S-TSC-Cxxx-50279-C04). There is no B16 lenton coupler cast into the precast column PC2a to receive the reinforcement detail. PC2a drawing MU Cxxx-SKC-A-DWG-Cxxx-51559 Rev P08 does not show couplers and has therefore not been manufactured with the couplers.
| 02SL - Stations (LUL) | Cxxx-NCR-000536 | NCR | WTH, Lvl 0 - Scabbling works to the RC structure not agreed |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-12-31 | 2018-10-01 15:38 | -91 | 2018-05-17 15:26 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | It has been identified scabbling works have been carried out to vent shaft structural RC wall located WTH level 0/Grid C/3-4. This has not been agreed with Cxxx These works have been undertaken due to survey conducted by __ identifying the RC wall is out of tolerance in relation to the installation of __ bracketry. A further survey was conducted by confirming the wall was cast within structural tolerance by RC subcontractor however fell outside of __ tolerance and had an excess of 15mm cover required to be removed.
| 02SL - Stations (LUL) | Cxxx-NCR-000537 | NCR | Coffer Box Water Ingress |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-06-29 | 2019-06-18 10:46 | 354 | 2018-05-16 12:35 | Electrical - Cable Management | 3000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Following the bench mark inspection yesterday of the JBs in the WTH coffers it was found that some of the JBs were filled with water and there was corrosion inside the boxes. See attached picture.
| 02SL - Stations (LUL) | Cxxx-NCR-000538 | NCR | Incorrect connection of earthing cables |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-05-30 | 2018-07-17 09:32 | 48 | 2018-05-16 12:58 | Electrical - Earthing & Bonding | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Earthing cables have been installed on station earth bar incorrectly within KD20. The main earth cable lugs are required to be fitted directly against the earth bar body and not on the terminal nut. The main earth cables are also required to be terminated on the supply side of the drop link. The CMS earth bond is required to be installed on the load side of the drop link.
| 02SL - Stations (LUL) | Cxxx-NCR-000539 | NCR | Radius Skirtings Installation Continued before benchmark approval was gained |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-04-04 | 2018-11-26 14:28 | -129 | 2018-05-16 16:04 | Architectural - General | 500 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | 6no. sections of radius skirtings have been installed before approval of the benchmark was gained.
| 02SL - Stations (LUL) | Cxxx-NCR-000540 | NCR | IW31/32 Riser |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-05-25 | 2018-08-29 15:45 | 96 | 2018-05-16 17:01 | Civil - Civil Engineering General | 0 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please see attached photos showing the as-struck condition of the riser at IW31/IW32 on the ground floor. The polystyrene former crushed during the pouring of this wall, and has left the riser small than design. Due to the size of the opening, both an as-built survey and a cover meter survey cannot be undertaken.
| 02SL - Stations (LUL) | Cxxx-NCR-000541 | NCR | WTH - Level +1 Chiller Room - Damage to Permanent Wall |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-08-30 | 2018-09-21 14:21 | 22 | 2018-05-17 16:28 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Upon completion of demolition of the WTH Chiller Room temporary wall (Level +1 Elevation C) by __, upon removal of protective ply layers by __'s it has been identified that demolition works have penetrated the protective layers and struck the rc wall at numerous locations. Refer to attached images.
| 02SL - Stations (LUL) | Cxxx-NCR-000542 | NCR | Conduit fixing into Pre-cast columns |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-06-29 | 2018-10-09 14:35 | 102 | 2018-05-22 13:13 | Electrical - Cable Management | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 32mm conduit has been installed approximately 1M from WTH +1 slab down to the transom beam in required bays for Comms equipment. The conduits have been fixed using distance saddles with 6mm rawplugs and 1 1/2 x 8 screws. The hole depth drilled is 30mm into the pre-cast concrete.
| 02SL - Stations (LUL) | Cxxx-NCR-000543 | NCR | ETH L-2 and L-1 IW34a |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-06-15 | 2018-06-18 09:10 | 3 | 2018-05-23 08:06 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | L-2 Opening After breaking back opening as detailed in Cxxx-PWK-000248 - It was found there was insufficient cover to 1 NO. B32 (MK36) trimmer bar when re-casting the edges for making good. (Please see 50104-X01-LS-220518). L-1 Opening During demolition of the IW34a opening at L-1 the top links were damaged due to them being cast in the design cover zone. In addition the over break resulted in the 2 No. B20. top bars no longer protruding into the north end as required for Cxxx-NCR-000207. (Please see 50123-C06-LS-180518)
| 02SL - Stations (LUL) | Cxxx-NCR-000544 | NCR | WTH Level -4 Liner Wall Crack repair |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-08-31 | 2018-07-18 13:48 | -44 | 2018-05-24 16:40 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate resources | Completed |  | Cxxx were instructed under Cxxx-PMI-1663 to carry out remedial works to cracking in WTH L-4 liner wall nib within KD30 on 04/07/2017. Since this instruction a damper has been installed in this location and the cracks have not been repaired. This damper is now preventing access to repair some of the cracking.
| 02SL - Stations (LUL) | Cxxx-NCR-000545 | NCR | Screed Crack to Level -4 KD 30 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-07-19 | 2020-01-17 14:55 | 182 | 2019-06-19 07:58 | Architectural - General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | One crack (5mm wide) has been identified in the 50mm Unbonded Screed (SCR-115) in KD30 on level -4. Screed type SCR-155 has been installed as per specification JM10 (Cxxx-SKC-A-RSP-Cxxx-50024) clauses JM10.1209 & JM10.1203 and setout (MU Cxxx-SKC-A-DDE-Cxxx-27640 P19). No movement joints were documented or required under JM10.1203 (a Unless specified otherwise, screeds shall be cast continuously, as far as possible without defined joints, using 'wet screeds' between strips or bays.
| 02SL - Stations (LUL) | Cxxx-NCR-000546 | NCR | ETH Coffer TP18BE __ anchors out of tolerance |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-06-30 | 2018-07-26 16:08 | 26 | 2018-05-29 15:41 | Civil - Civil Engineering General | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __ anchors in coffer wall are installed slightly out of tolerance 164 mm from bottom coffer wall instead of 130 mm (See marked up drawing Cxxx-SKC-A-DWG-Cxxx-52092 Coffer TP18BE Tfix anchor out of tolerance 23-05-2018)
| 02SL - Stations (LUL) | Cxxx-NCR-000547 | NCR | ETH coffer TP18BE and TP18CE missing __ anchors |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-06-30 | 2018-10-17 16:21 | 109 | 2018-05-29 17:13 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There are __ anchors missing in coffers TP18BE and TP18CE. The missing __ anchors are indicated in pink on drawings Cxxx-SKC-A-DWG-Cxxx-52092 Coffer TP18BE and Cxxx-SKC-A-DWG-Cxxx-52093 Coffer TP18CE
| 02SL - Stations (LUL) | Cxxx-NCR-000548 | NCR | PC9 and PC10 were cast out of tolerance |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-07-30 | 2018-07-18 14:39 | -12 | 2018-05-31 12:55 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The cast in embedded plates for PC9 and PC10 were cast out of tolerance, please refer to the attached surveys ETH PC9 Bolts Survey & ETH PC10 Bolts Survey. For embedded plate PC9 1No M24 threaded stud has been welded out of position. This is due to the embedded plate being cast out of tolerance. For embedded plate PC10 the treaded bar is cast in with the base plate which was cast out of tolerance.
| 02SL - Stations (LUL) | Cxxx-NCR-000549 | NCR | WTH fire barrier works undertaken without accepted ITP & MCR |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-09-14 | 2018-09-04 10:03 | -10 | 2018-06-11 14:33 | Fire - Compartmentation | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Fire barriers installed in the WTH without a CRL accepted ITP and MCR
| 02SL - Stations (LUL) | Cxxx-NCR-000552 | NCR | Non-compliant electrical supply cable to DOO cameras |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-07-05 | 2018-09-25 09:06 | 82 | 2018-06-14 14:50 | Electrical - Electrical Engineering General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | DOO cameras electrical supply cabling. The electrical cable that has been used to supply the DOO cameras on both WTH and ETH platforms has not followed the required specification detailed in the design. The cable routes from the durasteel box housed in the fire hydrant cabinet on the platform to the camera connection socket in the PES. The associated termination pin crimp will have to be changed to accommodate the non-compliant installed cable. The associated cable labelling will have to be changed to correctly describe the as installed cable.
| 02SL - Stations (LUL) | Cxxx-NCR-000553 | NCR | Non-compliant CMS (Conduit) for electrical supply cable to DOO cameras from DC11 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-07-07 | 2019-12-05 18:47 | 516 | 2018-06-14 14:43 | Electrical - Electrical Engineering General | 10000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | DOO cameras electrical supply CMS (Conduit). The CMS that has been installed to supply the electrical feed (24V) to the DOO cameras from DC11 has not been installed as per the design. The CMS route is from DC11 __ box housed in the fire hydrant cabinet on the platform to the cameras located in the PES. The as installed CMS routes from the top of the __ box, turns at 90 degrees across the back of the fire hydrant cabinet, turns 90 degrees vertically and over the crown to the PES. The containment installed across the back of the fire hydrant will obstruct the installation of the PHP, SAP and Comms equipment on the left of the fire hydrant cabinet.
| 02SL - Stations (LUL) | Cxxx-NCR-000554 | NCR | ETH Level +1 slab steel anchorage south of grid line 2 - reference __ RFI-2770 (Rev 01) |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-08-13 | 2018-09-21 14:23 | 39 | 2018-06-18 09:44 | Civil - Civil Engineering General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | RFI raised by __. Please raise as an NCR Location: ETH > Drawing Cxxx-__-S-DDA-Cxxx-72083 provides the top reinforcement intent for the slab south of grid line 2 as B25-150 in both directions. Drawing Cxxx-__-S-DDA-Cxxx-72087 provides the bottom reinforcement intent for the slab south of grid line 2 as B25-150 in both directions. Both top and bottom steel running north-south is assumed to anchor into beam L1B14, however, B20-150 bars (with female couplers to align with a construction joint to the south of L1B14) have been provided for the top steel rather than B25-150 – see Cxxx-SKC-S-DWG-Cxxx-50178 bar mark B85 top row.
| 02SL - Stations (LUL) | Cxxx-NCR-000555 | NCR | Clash of NLBW1 with Coffer |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-08-22 | 2018-12-14 17:19 | 114 | 2018-06-22 13:24 | Civil - Civil Engineering General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | ITEM 1:- went to install coffer TP22E to discover that the central beam of the coffer clashes with NLBW1. In order to fit the coffer over the wall require to break out the end of the wall as marked out on the attached photo (Pic NLBW1). The dims of the break out are 350mm wide by 715mm deep (internal depth of coffer). ITEM 2: To allow the installation of coffer TP22E on 12/06/18, a small section of the top of NLBW1 was broken out on its southern end. However, it has now been realised that 2 no. B20 couplers provided for the connection of IW77 drop beam to the East of NLBW1 fall within this section and therefore they cannot be used anymore. Please see mark-up attached.
| 02SL - Stations (LUL) | Cxxx-NCR-000556 | NCR | Platform and cross passages gaps between GFRC and Skirtings |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2019-03-08 | 2018-12-12 11:21 | -86 | 2018-06-22 10:18 | Architectural - Flooring | 2500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | CRL were invited to attend a benchmark inspection of the corner skirting for the Platform and Tunnel Grannazzo corner tile on 25.05.2018 (SK-707/708). During the inspection it became clear that the setting out of the skirting and the interface with the GFRC corner panel do not meet the requirements of the Works Information. Comments were given on the site installation of the skirting only, with a Cxxx action to provide detailed information on the drawings used for manufacture and installation. This information remains outstanding. A number of inspections have subsequently taken place and it is Crossrail Architect’s conclusion that the non-compliance could be a result of mis-aligned setting out information or the manufacture of skirting tiles outside of tolerances. This non-conformance has been raised as the installed works do not met the requirements of the Works Information as follows: Inspection and Test Plan - Cxxx-SKC-A-ITP-Cxxx-50003 - Revision 2.0. (Refer to drawings referenced in ITP for design intent). Architectural Specification Cxxx-SKC-A-RSP-Cxxx-50057/Cxxx-ATK-N2-RSP-CR002-00001 – Clauses JM40.1215/JM40.2101 v)/JM40.2104 ii)/JM40.3205 g)/JM40.3214. Cxxx-NCR-000539 has been raised for the installation of the skirtings without an approved benchmark and should be referenced in the closure of this NCR.
| 02SL - Stations (LUL) | Cxxx-NCR-000557 | NCR | steel covering grout boxes in ES2 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-09-23 | 2022-03-03 16:16 | 1257 | 2018-06-21 17:46 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | have installed the __ decking support steel base plates partially covering access to the grout boxes at the base of ES2 on Level -5 where the SCL meeting RC concrete (supporting photos attached).
| 02SL - Stations (LUL) | Cxxx-NCR-000558 | NCR | Damaged FP600S SWA cable supply to DC11 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-07-20 | 2018-09-28 14:26 | 70 | 2018-07-10 10:44 | Electrical - Cable Management | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A joint / CRL inspection highlighted a damaged FP600S 4mm 3C supply fed from distribution board DB-W-UPS-06 to DOO power cubicle DC11 on the west end of the Eastbound platform. The outer insulation has been cut away down to the armouring, and the fire retardant blue seal around the armouring is also cut / damaged. The damage is located on a internal bend below the comms durasteel box
| 02SL - Stations (LUL) | Cxxx-NCR-000559 | NCR | ES2 Incorrect hole sizes in manufactured PFC channels |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-07-25 | 2018-08-13 09:10 | 19 | 2018-06-22 12:37 | Architectural - General | 500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Subcontractor found out that 15no. slotted holes in PFC channel (Fixing plate 7) were manufactured in smaller size (22mm diameter) than the holes drilled on site. Therefore, the intended fixing of M24 size will not fit through the holes in the PFC channel. Included is a photo of the location and a location plan
| 02SL - Stations (LUL) | Cxxx-NCR-000560 | NCR | Installation without MCR/ITP |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-08-06 | 2019-09-18 15:35 | 408 | 2018-06-29 08:27 | Electrical - Switchgear | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Battery Charger Units and Busbar have been installed on site without MCR approval from CRL.
| 02SL - Stations (LUL) | Cxxx-NCR-000561 | NCR | CMS too close to ductwork |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-08-31 | 2019-04-29 09:46 | 241 | 2018-06-29 08:32 | Electrical - Cable Management | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | 225mm PMR Tray has been installed to close to the ductwork within WTH Level -5 Circulation Area 6/071.
| 02SL - Stations (LUL) | Cxxx-NCR-000562 | NCR | Damaged GSMR Cable |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-07-13 | 2018-10-02 11:02 | 81 | 2018-06-29 08:40 | Communications and Control Systems - Radio | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | GSMR cable has been damaged on installation and taped up using insulation tape. Damaged cable is located on high level PMR tray on Eastbound Platform WTH tunnel mouth.
| 02SL - Stations (LUL) | Cxxx-NCR-000563 | NCR | CMS Bracketry Calculations |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-08-31 | 2019-05-22 14:32 | 264 | 2018-06-29 08:45 | Electrical - Cable Management | 5000 |  | Design | Rework | 3 (3-6k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Load calculations are required for the Containment Management System (CMS) that has been installed throughout the station. These load calculations should take into account the fire requirements.
| 02SL - Stations (LUL) | Cxxx-NCR-000564 | NCR | Non-Compliant vertical tensile fixings |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-07-31 | 2018-10-30 08:52 | 91 | 2018-06-29 08:50 | Electrical - Cable Management | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __ Chemical resin fixings have been utilised to fix primary trunking CMS to the ceiling in a vertical tensile manner, of tunnel sections in all passageways between the east and westbound platforms. Some fixings for unistruts supporting conduits on both platforms have also been used in the same manner.
| 02SL - Stations (LUL) | Cxxx-NCR-000565 | NCR | Site Made Top Hat Tee's |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-08-31 | 2019-05-01 08:12 | 243 | 2018-06-29 08:56 | Electrical - Cable Management | 0 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Site made Top Hat Tees have been manufactured on site and do not allow enough capacity for cables to be installed correctly.
| 02SL - Stations (LUL) | Cxxx-NCR-000566 | NCR | Trays have been cut through the perforations |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-07-06 | 2019-01-30 16:45 | 208 | 2018-06-29 13:11 | Electrical - Cable Management | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Cable tray has been cut through the perforations creating a jagged edge on TVS installation WTH -1 KD7.
| 02SL - Stations (LUL) | Cxxx-NCR-000567 | NCR | Damaged 150mm Power tray to be repaired |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-07-13 | 2019-06-11 15:47 | 333 | 2018-06-29 13:18 | Electrical - Cable Management | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | 150mm cable tray in KD30 WTH Level -4 has been damaged following installation.
| 02SL - Stations (LUL) | Cxxx-NCR-000568 | NCR | Fire stopping detail cannot be achieved |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-08-31 | 2019-12-03 18:35 | 459 | 2018-06-29 13:20 | Electrical - Cable Management | 0 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Cable tray installation in KD7 WTH Level -1 through penetration is to close to the edge of the hole. This means the fire stopping detail cannot be installed as this requires 50mm clearance.
| 02SL - Stations (LUL) | Cxxx-NCR-000569 | NCR | ETH Level 0 Column PC9 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-03-29 | 2019-02-19 10:39 | -38 | 2018-06-29 10:16 | Architectural - General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The precast column PC9 was manufactured in accordance with the approved drawings, however, when installed and surveyed on site, it was identified that the stone facing of PC9 along Grid Line A, on the western face was protruding 50 mm further west than the design intent.
| 02SL - Stations (LUL) | Cxxx-NCR-000570 | NCR | Damaged Single core cables |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-07-13 | 2018-11-30 16:05 | 140 | 2018-06-29 14:17 | Electrical - Lighting | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Single core cables and the Dali supply cables have been damaged following the installation into the Besa box and left coiled. These cables are supplying the circulation area lighting at WTH Level -5.
| 02SL - Stations (LUL) | Cxxx-NCR-000571 | NCR | Bronze Patination Level -3 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-02-28 | 2018-10-03 09:43 | -148 | 2018-10-03 07:43 | Architectural - Ceilings & Soffits | 500 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Bronze Patination in the panels delivered and installed on site on level -3 did not match the previously presented sample
| 02SL - Stations (LUL) | Cxxx-NCR-000572 | NCR | ETH Damaged TP26 Coffer |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-08-29 | 2018-10-04 11:40 | 36 | 2018-07-05 14:42 | Architectural - General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | The Coffer TP26E was damaged during transportation and was returned to the manufacturing facility. The precast subcontractor has inspected the coffer and there were areas where the concrete was cracked, chipped and scratched. Upon completion of the inspection, the following actions are proposed be taken to repair the coffer: 1. Remove the loose concrete parts via hydro jet 2. Cut free visible reinforcement with a minimum surround of 1,5 x maximum aggregate dimension: 15mm; 3. Supply and install formwork to the area which will be repaired; 4. Prepare existing concrete surface of the area to be repaired 5. Pour concrete (MCR: Cxxx-SKC-A-LRC-Cxxx-50116) to the area to be repaired 6. Remove formwork (on the following day); 7. Finish concrete surface 8. Cover repaired area with plastic film 9. Transport to site 10. Remove plastic film (after 3 days) 11. Spray finish concrete Furthermore, additional concrete cubes will be taken and photos as well as the applicable inspection records will be kept to record the remedial works
| 02SL - Stations (LUL) | Cxxx-NCR-000573 | NCR | Asset Protection of Cabling |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-07-23 | 2018-12-05 11:10 | 135 | 2018-07-09 11:47 | Communications and Control Systems - Fibre Optic Network | 2000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | During the course of an inspection with Cxxx sheets of Timber were found to be leaning against comms CMS, which houses various fibre cables and coaxial radio cables running up from the invert to platform level. These cables could potentially be damaged, and would be very costly to replace.
| 02SL - Stations (LUL) | Cxxx-NCR-000574 | NCR | Drawings not reviewed by Cxxx 50380 50018 50792 50814 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-12-31 | 2019-03-15 13:37 | 74 | 2018-07-13 16:30 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Carried out construction using drawings that have not been reviewed by Cxxx Cxxx-SKC-S-DWG-Cxxx-50380 C02 – Cxxx did not review this pre-pour and have recently reviewed it Code 1. Cxxx-SKC-S-DWG-Cxxx-50018 C02 – Cxxx did not review this pre-pour and have recently reviewed it Code 1. Cxxx-SKC-S-DWG-Cxxx-50792 C02 – Cxxx did not review this pre-pour and have still not been issued it for review. Cxxx-SKC-S-DWG-Cxxx-50814 C04 – Cxxx did not review this pre-pour. Sent for review on eB 05/07/18. Drawing currently under review. Cxxx-SKC-S-DWG-Cxxx-50648 C04 – This was used for Construction when code 2 however was marked up with the changes - see attached Cxxx-SKC-S-DWG-Cxxx-50646 C04 – This was used for Construction when code 2 however was marked up with the changes - see attached
| 02SL - Stations (LUL) | Cxxx-NCR-000575 | NCR | Damaged Comms PAVA Cabinet |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-09-28 | 2018-12-05 16:43 | 68 | 2018-07-10 08:42 | Communications and Control Systems - Public Address Systems | 0 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Personnel Error - Other human error | Completed |  | Within CER 1 WTH Level -5 PAVA Cabinet door has been damaged causing the glass door to shatter.
| 02SL - Stations (LUL) | Cxxx-NCR-000576 | NCR | Damaged GSMR Cable WTH WB |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-07-17 | 2018-10-02 11:05 | 77 | 2018-07-10 09:02 | Communications and Control Systems - Radio | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Damaged GSMR cable was found WTH westbound Platform in 6/954 approximately 4M from Platform end wall.
| 02SL - Stations (LUL) | Cxxx-NCR-000577 | NCR | potential cable damage by pop riveted bends and partitions in new trunking CMS |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-08-10 | 2019-05-22 14:05 | 285 | 2018-07-10 11:20 | Electrical - Cable Management | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Site fabricated bends utilised in 4 different positions between PSD and the eastbound platform. This is the case for all three CMS (PSD data 75 x 75), PSD power (75 x 75), and 2 comp (100 x 75) for media power and data. These need replacing with factory manufactured bends Pop rivets have been utilised within the three trunkings which has the potential for causing damage to cabling that is pulled through. Draw wires have been identified as having already been used to wire through the CMS in this method. The reason for this is lack of access outside of the maintenance lobby 6/107.
| 02SL - Stations (LUL) | Cxxx-NCR-000578 | NCR | Tile misalignment to CP4/WB platform interface |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-09-01 | 2018-10-09 07:56 | 38 | 2018-07-17 07:58 | Architectural - Flooring | 2000 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Due to an incorrect size cut being installed adjacent to a structural movement joint in the bay opposite CP4 the tiles now do not line through from the passage to the platform by 10mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000579 | NCR | Coaxial drum testing process. |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-07-31 | 2018-07-24 09:51 | -7 | 2018-07-17 10:05 | Communications and Control Systems - Driver only Operation CCTV | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Other | Completed |  | IRN paperwork to support the Doo CCTV required for Dynamic Testing are missing the Cable drum allocation sheets for each cable installed.
| 02SL - Stations (LUL) | Cxxx-NCR-000580 | NCR | Damaged PES Lighting Cables |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-08-02 | 2018-12-04 16:30 | 124 | 2018-07-19 11:09 | Electrical - Lighting | 2000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 3 x Damaged single core cables have been found during a electrical surveillance for PES lighting cable installation. One of the damaged cables had been taped up to hide the damage.The surveillance was carried out on the Westbound Platform on the following circuits:- W-EL05/4L2, W-B05/1L2, W-EL05/6L3.
| 02SL - Stations (LUL) | Cxxx-NCR-000581 | NCR | WTH L-3 RC Slab - Building to P Status Drawing 11134 Rev P29 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-09-20 | 2018-08-20 17:19 | -31 | 2018-07-23 10:01 | Civil - Civil Engineering General | 0 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Following offline submission of WTH L-3 redlines it has been noted that drawing Cxxx-__-S-DDL-Cxxx-11134 Rev P29 was used for construction of the slab. This drawing had not been officially released to for construction. The next released drawing revision for construction was Rev C09. No changes have been identified between the revisions.
| 02SL - Stations (LUL) | Cxxx-NCR-000582 | NCR | Pouring RC Plinth Without Approved FCD |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-12-31 | 2018-12-05 17:26 | -26 | 2018-07-25 16:29 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | A concrete pour proceeded prior to Crossrail being provided the requested information to review and approve an FCD.
| 02SL - Stations (LUL) | Cxxx-NCR-000583 | NCR | AP1 Slab Out of Tolerance |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-02-28 | 2019-03-22 16:36 | 22 | 2018-07-26 08:14 | Civil - Civil Engineering General | 0 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As per the attached as-built, the AP1 floor slab is out of height tolerance in a number of areas.
| 02SL - Stations (LUL) | Cxxx-NCR-000584 | NCR | ETH L-0 position of Kiwistrip and PFC Channel |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-12-11 | 2018-08-13 09:56 | -120 | 2018-07-26 09:20 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The cast in position of the Eazistrip in the L-0 Beam 1 drawing no. Cxxx-SKC-S-DWG-Cxxx-50004 was placed incorrectly at the time of pouring. __s are unable to use the Eazistrip on the southern side of the PFC channel (see attached photo 180720DP). Thus a drill and fix detail is required.
| 02SL - Stations (LUL) | Cxxx-NCR-000585 | NCR | Secondary Containment Blocking access to Mechanical Equipment |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-08-09 | 2019-02-11 14:33 | 186 | 2018-07-26 11:00 | Electrical - Cable Management | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 25mm conduit and support bracketry has been installed in front of the actuator on the smoke damper at ETH L-3.
| 02SL - Stations (LUL) | Cxxx-NCR-000587 | NCR | ETH L-1 slab (west of GLB) Post pour inspection not carried out prior to screeding. |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-12-31 | 2018-10-22 08:13 | -70 | 2018-07-26 14:28 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Post pour inspection for ETH L-1 slab (west of GLB) was not carried out/signed off prior to screeding ( As per requirement of ITP 50001 ) the screed work is now complete.
| 02SL - Stations (LUL) | Cxxx-NCR-000588 | NCR | Cable damage within CMS |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-08-10 | 2019-09-18 15:43 | 404 | 2018-07-27 11:59 | Electrical - Lighting | 2000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During a quality surveillance inspection report, it was found that one of the 16mm CPC's within the 110V compartment of the multi compartment trunking was damaged to the extent that exposed copper was prevalent. The cable had a wrapping of white insulation tape around it. The damage is located close to the eastbound platform in passageway 6/219. The surveillance was being carried out on circuit W-LVA05/6.
| 02SL - Stations (LUL) | Cxxx-NCR-000591 | NCR | ETH Level + 1 slab edge out of tolerance |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-08-02 | 2019-01-25 11:18 | 176 | 2018-07-30 16:01 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Level + 1 slab edge GL D to E (OSD Lift shaft) out of tolerance by up to 20mm the affected area is only over the depth of the beam. The wall below (IW32a constructed A few month in advance) and the upstand above (constructed a few days days after) are not affected because they weren't part of the same pour. It is clearly shown on the supporting documentation areas affected see drawing :Cxxx-SKC-S-DWG-Cxxx-50178 referenced below
| 02SL - Stations (LUL) | Cxxx-NCR-000592 | NCR | WTH - Level 0 - ES1 Upstand Repair level 0 Grid E/3-4 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-08-07 | 2018-08-15 16:28 | 8 | 2018-07-30 16:41 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | During the installation of an escalator truss section onto the southern end of the RC plinth (located WTH level 0 Grid E/3-4) a failure has been identified whereby a small section of the RC upstand has cracked up to the thickness of the cover zone and become loose. Works were immediately halted and a joint inspection of the affected area was undertaken by Cxxx & with repair procedure agreed.
| 02SL - Stations (LUL) | Cxxx-NCR-000593 | NCR | ETH L+1 - OSD Lift shaft (IW25, IW27, IW28 & IW29) |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-08-30 | 2018-08-13 10:07 | -17 | 2018-07-31 08:50 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Location 1 (IW25 south end) Excessive cover to last 2 no. verticals bar mark E68 (drawing 50162) on the south end of IW25 (approx. 100mm) Location 2 (IW25-IW29 connection) Excessive cover to last 2 no. verticals bar mark E68 (drawing 50162) on IW25-IW29 (approx. 60mm). Last pair of bars seems to be approximately on the middle of IW29 rather than on the face of it. Location 3 (IW27-IW28 connection) Last pair of verticals bar mark E65 (drawing 50161) is not installed within IW27-IW28 connection but included within IW27 itself (ie 11 no. pairs or bars instead of 10 no. pairs of bars as shown on the drawing have been installed within the section of IW27 between IW28 and IW29). Location 4 (IW27) Opposite gender of bar mark E65 (drawing 50161) has been provided (ie threaded bars rather than socketed bars)
| 02SL - Stations (LUL) | Cxxx-NCR-000594 | NCR | ETH - L-1 IW43 - Missing Opening MH192-MH196 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-09-06 | 2018-12-03 15:58 | 88 | 2018-08-07 09:02 | Civil - Civil Engineering General | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | 830w x 1350h wall opening was not cast during construction of RC wall (West wall, IW43). Was previously accepted to be formed under Cxxx-RFI-002529 (which includes SK-MEP-096_69111_RCwalls_rev 04.pdf, Cxxx-RFI-002529.pdf, DDN C670.pdf) and confirmed Route of services shown on Cxxx-SKC-P-DDA-Cxxx-52214-IFC Annotated.pdf attached
| 02SL - Stations (LUL) | Cxxx-NCR-000595 | NCR | ETH L-1 NLB Wall 11 OSD Corrider GL 1C -1D - Low Level Defect |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-09-06 | 2018-09-27 12:59 | 21 | 2018-08-07 13:53 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Defect noted in the lower section of NLB wall 11. Foam found within concrete wall.
| 02SL - Stations (LUL) | Cxxx-NCR-000596 | NCR | WTH - Level 0 - Lift 7 - __ Cores - Reinforcement Cut |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-03-31 | 2019-03-25 18:00 | -6 | 2018-08-09 07:38 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Coring works to lift 7 - Level 0 (2x127mm & 1 x107mm diameter) have been carried out under accepted Cxxx-RFI-003922. RFI notes reinforcement is not to be cut ,however Upon inspection reinforcement have been identified as cut in all 3 cores against the direction of the RFI.
| 02SL - Stations (LUL) | Cxxx-NCR-000597 | NCR | ETH - Riser 925 - Final post-pour of walls not completed |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-09-08 | 2018-11-14 17:03 | 67 | 2018-08-09 12:59 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | In order to meet the planned handover date for MEP installation in the Services Riser 925, the scaffold access was struck and the MEP works commenced ahead of signing off the snags recorded on the riser walls post-pour inspection (attached). Due to ongoing MEP installation, some areas of the riser walls are now inaccessible for a final post-pour inspection
| 02SL - Stations (LUL) | Cxxx-NCR-000598 | NCR | PSD switchroom CMS design non compliances |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-08-24 | 2019-09-18 15:46 | 390 | 2018-08-10 09:26 | Electrical - Cable Management | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | This NCR relates to three issues related to the CMS installation within the PSD room ETH. 1) There is no electrical design for the vertical trunking CMS drops to the PSD panels, where they turn down the wall from the primary horizontal CMS 2)There is no electrical design for temporary isolators installed to the permanent ATS switch's nor associated CMS traywork and bracketry. 3)The power cables and comms cables are both in the wrong compartments going into the PSD panel on the RHS. This may be due to a lack of co-ordination between __ and Cxxx
| 02SL - Stations (LUL) | Cxxx-NCR-000599 | NCR | WTH - Level 0 - Wall W-W-14 Opening/__ Bracketry |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-09-09 | 2018-10-02 15:37 | 23 | 2018-08-10 14:48 | Civil - Civil Engineering General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | __ are currently installing rail and brackets for Lift 7 at WTH located Grid G/2-3. They have reached the top of level 0/Level +0.5 Soffit and advised bracketry is required to be installed directly in the location of a 400x400mm opening cast into the wall (W-W-14). Both the bracketry and wall opening have been installed according to approved design. There has been a coordination issue in design of the rail bracketry and structural opening resulting in the clash.
| 02SL - Stations (LUL) | Cxxx-NCR-000600 | NCR | Escalator 11-13 lower pit back wall out of tolerance |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-10-15 | 2018-10-17 15:35 | 2 | 2018-08-15 12:26 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Escalator 11-13 lower pit back wall out of tolerance to the design location required for __ to install the escalator. This is the eastern side of wall A on drawing Cxxx-SKC-S-DWG-Cxxx-50258. There is insufficient cover over the rebar in the wall to be able to scabble back the wall to bring it within tolerance and maintain min 15mm of concrete over rebar. Design tolerance for esc pit defined in DWG "Cxxx-SKC-M1-DWG-Cxxx-50052" Refer to attachment for summary of survey details and required scabbling depths, In addition, Located at the top of ES2, the L-00 Slab Edge. (Similar to Cxxx-RFI-003814) The slab edge was found to be within tolerance a per the KF10 specification (+-10mm) but encroached on the escalator area by 5mm, which is not acceptable to otis (+30mm-0mm). The cover in this area was found to be between 38mm-45mm. Works completed.
| 02SL - Stations (LUL) | Cxxx-NCR-000601 | NCR | Missed Post Pour Inspections to the top of the level+1 slab at the ETH |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2018-12-31 | 2018-09-05 08:42 | -117 | 2018-08-16 11:58 | Structural Engineering - Concrete Member | 0 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Post pour inspections to the top of the level+1 slab at the ETH are incomplete. It is not possible to complete some of these inspections now as they are now covered in a waterproof layer and a protective concrete topping slab. The Contractor are to upload an attachment that clearly identifies these area/s and propose how to rectify this shortfall in quality assurance. All affected ITP Record Packs are to be Linked.
| 02SL - Stations (LUL) | Cxxx-NCR-000602 | NCR | ETH level -3 to -4 stair detail |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-12-31 | 2018-11-20 11:29 | -41 | 2018-09-04 07:18 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | The ETH MPS level -3 slab was poured before the stair detail on the northern strip of sloping slab had been developed i.e. the magenta outline in Cxxx-SKC-S-DWG-Cxxx-50334-C01-LS-210518 JRP was poured, versus the blue outline which is what is currently shown on the Cxxx-structural/architectural drawings.
| 02SL - Stations (LUL) | Cxxx-NCR-000603 | NCR | Lack of spare capacity in __ designed ladder rack |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-09-28 | 2018-09-03 11:12 | -25 | 2018-08-22 13:30 | Electrical - Cable Management | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Currently -RFI-005455 is awaiting __ response for confirmation of cleating arrangements to achieve 25% spare capacity following an __ error when calculating cleat size. Only after installation can the spare capacity issue be assessed but will be limited locations following the agreement with CEG to use cable ties in the horizontal and cleats in the vertical. Cable cleat benchmark attached.
| 02SL - Stations (LUL) | Cxxx-NCR-000604 | NCR | Lintel GPO3 damaged lintel stones |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-12-31 | 2018-09-04 11:18 | -118 | 2018-08-23 12:51 | Architectural - General | 500 |  | Damaged | Reject | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Lintel GP03 is damaged during handling on site off loading crate
| 02SL - Stations (LUL) | Cxxx-NCR-000605 | NCR | Omitted Protective Screed on L-2 Perimeter Wall Capping Beam |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-12-31 | 2018-10-12 08:49 | -80 | 2018-08-24 13:22 | Architectural - General | 500 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | As indicated in Cxxx-SKC-A-DDD-Cxxx-82903 & Cxxx-__-A-DDD-Cxxx-82903 mark-ups, a protective screed was not installed over the L-2 Capping beam.
| 02SL - Stations (LUL) | Cxxx-NCR-000606 | NCR | Non Conforming Trunking Top Hat located in KD20 6/668 HV Switchroom (HV1) |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-09-28 | 2020-01-31 10:21 | 490 | 2018-08-28 10:51 | Electrical - Cable Management | 0 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The top hat installed for the Comms trunking has not been installed correctly and is not a factory manufactured component.
| 02SL - Stations (LUL) | Cxxx-NCR-000607 | NCR | Escalator 11-13 Upper pit back wall out of tolerance |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-12-31 | 2018-09-21 14:36 | -101 | 2018-08-28 14:40 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | This NCR is raised to document the works completed at the Upper ES2 landing, which were not agreed prior to completion. It does not identify a defect with the concrete slab, as this was constructed within the Structural concrete specification (KF10). Located at the top of ES2, the L-00 slab edge is marked on the attached drawing "Cxxx-SKC-S-DWG-Cxxx-50006-C03-LS-Markup-220818.pdf" The slab edge was found to be within tolerance as per the KF10 specification (+-10mm) but encroached on the escalator area by upto 5mm (Seen in attached survey.). This is not acceptable to otis (+30mm-0mm) shown on Cxxx-SKC-M1-DWG-Cxxx-50052. The cover in this area was found to be between 38mm-45mm. Therefore the contractor completed the following works which had been previously agreed within Cxxx-RFI-003814 for the wing slab edges either side of the upper landing. a. Plane surface back 7mm. b. Apply 2mm of __ ST05 to new surface to replace cover. (Cxxx-SKC-O4-QSV-Cxxx-50062 Rev 1.0) c. Total concrete cover achieved 31-38mm + 26mm from ST05.
| 02SL - Stations (LUL) | Cxxx-NCR-000608 | NCR | GFRC Package: __ Deck Steel - incorrect installation of anchors |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-10 | 2019-05-30 16:05 | -103 | 2018-08-29 07:27 | Architectural - General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Subcontractor found out that some of the anchors for __ deck support steel were installed incorrectly. Due to this fact the anchors did not match the fixing holes in the stainless steel baseplates. The Subcontractor drilled oversized holes, however, the threaded rod protruding above the plate was not sufficient to tighten the nut properly.
| 02SL - Stations (LUL) | Cxxx-NCR-000609 | NCR | ETH L+1 Pour 4a & 4b - GL A Beam - 2 no. rows of __s on top of the beam not installed |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-12-31 | 2018-10-11 12:38 | -81 | 2018-08-29 15:33 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate resources | Completed |  | 2 no. rows of __ channels have not been installed on top of the beam from GL#1 to GL#4 ************ 11/09/18 ************** New attachments showing affected area
| 02SL - Stations (LUL) | Cxxx-NCR-000610 | NCR | OSD Base plate EP4 L+1 ETH case out of tolerance |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-12-31 | 2018-09-27 10:20 | -95 | 2018-08-29 16:09 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 1no. EP4 base plate cast 7mm out of tolerance to KF10.3222 Dimensional deviation n) i) Horizontal plates for connection to OSD Columns Marked up plan and survey attached to indicate area
| 02SL - Stations (LUL) | Cxxx-NCR-000611 | NCR | ETH Level + 1: Upstand cast out of tolerance – Grid line 1 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-12-31 | 2018-10-05 14:00 | -87 | 2018-09-26 11:31 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following an as-built survey of the L+1 upstands undertaken by __s; 1no upstand was cast out of tolerance. The RC upstand around base plate EP2 GL1/GLE was cast as an RC upstand for base plate EP1. This has resulted in the upstand surrounding the EP2 base plate to be out of tolerance to specification KF10.3222 (see attached ETH Out of Tolerance Alignment Upstand At Grid 1/E Survey). The areas in red on the as-built survey are out of tolerance.
| 02SL - Stations (LUL) | Cxxx-NCR-000613 | NCR | ETH - L+0.5 Slab - Incorrect Architectural concrete finish on slab surface |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-07-17 | 2019-02-28 08:40 | -139 | 2018-09-17 07:27 | Architectural - Flooring | 2000 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Incorrect concrete finish on the slab have been applied. Drawing Cxxx-SKC-A-DDE-Cxxx-77295 C02 shows that the area inspected should be "CON-151 Power trowelled concrete finish". After inspection slab shows to be "CON-154 Hand trowelled finish". See picture attached.
| 02SL - Stations (LUL) | Cxxx-NCR-000614 | NCR | Earth cable not sufficeintly crimped within lug SLD 21 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-12-31 | 2019-03-05 12:01 | 64 | 2018-09-17 08:15 | Electrical - Electrical Engineering General | 3000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During a pre inspection by the SAP it was found that the main 300mm Earth cable to the LV panel was insufficiently crimped and cold be easily removed from the lug
| 02SL - Stations (LUL) | Cxxx-NCR-000615 | NCR | South Elevation of IW31 at level 0 in the ETH Crack |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-12-31 | 2018-10-30 10:08 | -62 | 2018-09-20 15:44 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Management Problem - Improper resource allocation | Completed |  | Following on site inspection 06/09/18 with CRL, & MACE. The crack width was recorded to a max width of 0.5mm outside the tolerance of KF10.2214
| 02SL - Stations (LUL) | Cxxx-NCR-000616 | NCR | Use of products not approved by Crossrail |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-12-31 | 2018-12-17 09:15 | -14 | 2018-09-24 09:08 | Electrical - General | 500 |  | Material | Reject | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Two Products have been found on site that are not approved by Crossrail. The first product is Ideal Aqua-Gel 2 and the second is Red Expansion wall plugs. There is no approved cable lubricant on the MCR system and the only approved rawl plug product is the __ brand.
| 02SL - Stations (LUL) | Cxxx-NCR-000617 | NCR | Obstructed access to smoke damper actuators |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-12-31 | 2019-11-22 09:06 | 326 | 2018-09-24 10:01 | Electrical - Cable Management | 0 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | There are a number of different locations where access to smoke control damper actuators have been blocked by electrical services. The I.D. of these dampers are GE-W-FD039, AS-W-FD030 and ARR-W-SD003 located in Circulation area 5/071.
| 02SL - Stations (LUL) | Cxxx-NCR-000618 | NCR | Damaged Chiller Unit ETH |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-12-31 | 2021-05-04 08:47 | 855 | 2018-09-24 13:31 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient work planning by the subcontractors | Completed |  | Top Centre Chiller Panel has been bent upon an un-authorised lift being carried out.
| 02SL - Stations (LUL) | Cxxx-NCR-000619 | NCR | ETH L-1 to L+1 - IW53 East elevation - __ channels missing at specific locations |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-02-27 | 2019-01-07 16:41 | -51 | 2018-09-25 12:20 | Civil - Civil Engineering General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __s channles on the East elevation of IW53 (inside OSD goods lift shaft) from L-1 to L+1 haven't been installed completely at 2 no. locations, see attached marked up drawing .
| 02SL - Stations (LUL) | Cxxx-NCR-000620 | NCR | ETH Installation Of Busbar Joint Pack In Wall |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-12-31 | 2018-10-19 08:10 | -73 | 2018-10-02 07:16 | Electrical - LV Equipment | 15000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | Busbar joint pack was installed within a wall section that is required to be fire stopped which would leave the section inaccessible for future maintenance
| 02SL - Stations (LUL) | Cxxx-NCR-000621 | NCR | WTH Chiller Room L+0 to L+0.5 Staircase |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-12-31 | 2019-02-19 15:54 | 50 | 2018-10-02 07:41 | Civil - Civil Engineering General | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following a review of the blockwork details at Ground Floor it has been found that the Chiller room Staircase shown in detail 1 in drawing 17103 has been constructed to only 1100mm in width as opposed to design requirement of 1290mm. This addtional nib of 190mm is to support a blockwork wall running up the flight of stairs shown in drawing 01100.
| 02SL - Stations (LUL) | Cxxx-NCR-000622 | NCR | WTH - Escalator 14 to 16 - Datum Plate Discrepancy |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-12-31 | 2018-11-13 10:56 | -48 | 2018-10-02 08:21 | Architectural - General | 4000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | During a survey of finished floor heights on Level 00 of the Western Ticket Hall by __ on 05.09.18, it became apparent that the datum plates installed for Escalators 14 to 16 (ES1 upper) have been installed 6mm above design height. The lower datum plates have been installed as designed. The Escalators have been Lined & Levelled using these plates which was has been signed off by Crossrail. __ have been notified of this and confirmed that this will not affect their assurance
| 02SL - Stations (LUL) | Cxxx-NCR-000623 | NCR | WTH L-1 Room KD18 Coring through wind post |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-12-31 | 2019-06-07 16:13 | 158 | 2018-10-02 11:59 | Communications and Control Systems - Station Management System | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | __ Subcontractor was instructed to install conduit from the Comms trunking as per the attached marked up drawing and photo (outside of the room KD18) for the temperature sensor in the FCR room (KD18) on WTH Level -1. The Subcontractor drilled a 32 mm hole through the wind post with standard 110V drill and masonry drill bit. The Subcontractor did not damaged any of the rebar as shown on the attached photo.
| 02SL - Stations (LUL) | Cxxx-NCR-000624 | NCR | Damage to service ducts |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-05-02 | 2019-08-14 17:05 | 104 | 2018-10-04 09:18 | Civil - Civil Engineering General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | were instructed to drill into the floor of AP2 to fix the baseplates of the steel posts that will support the cladding. Drill depth required is 155mm in all locations at 28mm dia. At 3no. locations at 80-85mm depth, ductwork was struck in the setout bolt locations.
| 02SL - Stations (LUL) | Cxxx-NCR-000625 | NCR | Hold Point Missed |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-01-12 | 2018-11-09 17:33 | -64 | 2018-10-04 11:46 | Structural Engineering - Structural Engineering - General | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Pull out tests were not carried out to the __ decking supports to escalators 1 and 2.These are a requirement in ITP Cxxx-SKC-A-ITP-Cxxx-50053 section 5.1 which is a hold point and required 5% of fixings to be inspected.
| 02SL - Stations (LUL) | Cxxx-NCR-000626 | NCR | ETH L0 GL C-3 - RC slab edge damaged |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-12-31 | 2018-12-14 17:23 | -17 | 2018-10-04 14:26 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | The exposed edge of the ground floor concrete slab is damaged at GL C-3
| 02SL - Stations (LUL) | Cxxx-NCR-000627 | NCR | Incorrect installation of bolts to ES1/2 steel plates |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-02-13 | 2018-12-05 17:47 | -70 | 2018-10-05 12:44 | Structural Engineering - Structural Engineering - General | 0 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Some threaded anchors fixed through the SCL for the __ deck support steel work have little to no thread protrusion through the nut (see photos attached)>
| 02SL - Stations (LUL) | Cxxx-NCR-000629 | NCR | Missing segregation in Trunking in Passage 6/229 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-12-31 | 2019-06-14 15:20 | 165 | 2018-10-09 08:45 | Electrical - Cable Management | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Top hat tee has been incorrectly installed and has no cable segregation.
| 02SL - Stations (LUL) | Cxxx-NCR-000630 | NCR | Top hats incorrectly installed KD29 High level trunking |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-12-31 | 2019-11-10 20:33 | 314 | 2018-10-09 09:17 | Electrical - Cable Management | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Two Top hat Tee's have been incorrectly installed onto main spine trunking.
| 02SL - Stations (LUL) | Cxxx-NCR-000632 | NCR | Inadequate storage for Busbar Outside SLD14 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-12-31 | 2019-01-29 09:56 | 29 | 2018-10-09 10:16 | Electrical - LV Equipment | 0 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper storage of material | Completed |  | Required Busbar to be relocated to a storage area avoiding risk of any damage.
| 02SL - Stations (LUL) | Cxxx-NCR-000633 | NCR | ETH. Level 0 East corner of North face Wall IW-54 out tolerance |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-12-31 | 2019-01-21 14:37 | 21 | 2018-10-10 10:00 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following a post-pour inspection with CRL, it was found that Wall IW54 north elevation top east corner appears to be out of tolerance. An as-built survey of the wall was carried out which indicates that the wall is out of tolerance on the eastern upper section of the wall by 18mm verticality as per dimensional deviation set out in KF10.3222 - Cxxx- __-S-RSP-Cxxx-00009 Rev. 14. As-built survey for“ETH North face of IW54” and pictures are attached. Location shown on at attached: Cxxx-__-S-DDL-Cxxx-52101
| 02SL - Stations (LUL) | Cxxx-NCR-000634 | NCR | Inadequate storage of light fittings WTH -5 Staff Locker Room 6/317 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-12-31 | 2019-02-23 17:14 | 54 | 2018-10-10 13:03 | Electrical - Lighting | 1000 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper storage of material | Completed |  | Light fittings have been inadequately stored in the staff locker room on -5 WTH. There is no protection on the fittings which could lead to the integrity of the IP rating being jeopardised.
| 02SL - Stations (LUL) | Cxxx-NCR-000635 | NCR | 50 x 50 trunking not fixed correctly to trunking above ETH -5 Lobby 6/103 outside room 6/736 (KD29) |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-12-31 | 2019-02-11 13:52 | 42 | 2018-10-10 13:19 | Electrical - Cable Management | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 50 x 50 trunking not fixed correctly to trunking above leaving cables exposed and containment IP rating does not conform at present.
| 02SL - Stations (LUL) | Cxxx-NCR-000636 | NCR | Void to back of CH2 and CH3 skirtings |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-06-28 | 2019-11-21 12:21 | 146 | 2018-10-10 14:58 | Architectural - Flooring | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A gap between the upstands and granazzo skirting was identified at several locations. This became evident when GFRC panels were taken down.
| 02SL - Stations (LUL) | Cxxx-NCR-000638 | NCR | Site manufactured bend EB ETH |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-12-31 | 2019-05-22 13:57 | 142 | 2018-10-11 15:12 | Electrical - Cable Management | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Site fabricated bend dropping down to PES- no segregation, no gusset poorly manufactured
| 02SL - Stations (LUL) | Cxxx-NCR-000639 | NCR | Positioning of the fire adaptable box. ETH -5 Lobby 6/103 outside room 6/671 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-02-28 | 2019-03-25 15:42 | 25 | 2018-10-17 14:33 | Fire - Fire Systems & General | 0 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The position of the adaptable boxes installed for fire services has been positioned leaving minimal space for access and future maintenance.
| 02SL - Stations (LUL) | Cxxx-NCR-000640 | NCR | Trunking with trunking bolts missing ETH -5 AP3 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-02-28 | 2019-01-24 16:44 | -35 | 2018-10-17 14:54 | Electrical - Cable Management | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | No trunking screws have been installed where the two trunkings join. See attached photo for evidence.
| 02SL - Stations (LUL) | Cxxx-NCR-000641 | NCR | ETH L-5 Critical sump topping slab. Post pour inspection not carried out prior to screeding |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-11-18 | 2019-02-12 16:54 | 86 | 2018-10-19 10:12 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Post pour inspection for ETH L-5 topping slab (See mark up drawing attacyed) was not carried out/signed off prior to screeding ( As per requirement of ITP 50027 ) the screed work is now complete
| 02SL - Stations (LUL) | Cxxx-NCR-000642 | NCR | Level -5, CH3 outlet locations constructed in wrong locations |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-06-21 | 2019-07-18 13:41 | 27 | 2018-10-19 10:50 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | Pressure relief drainage points have not been constructed to the drawing Cxxx-__-S-DDA-Cxxx-13162 and the drainage points now fall within the 3d GFRC panels. This is causing an issue due to the fact that vermin mesh now needs to be installed and with the 3D GFRC panels being in-place, it is not possible to access the pressure relief drains and install the vermin mesh. It is not possible to take the 3D GFRC panels down as the equipment to do so is not on site and there is no way to bring the equipment back to the site hence removing the GFRC panels to install the vermin mesh is not possible.
| 02SL - Stations (LUL) | Cxxx-NCR-000643 | NCR | Full Capacity Ladder rack SLD 21 & SLD 22 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-04-30 | 2019-12-17 20:01 | 231 | 2018-10-25 11:54 | Electrical - Cable Management | 0 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Ladder rack installed in SLD 21 & SLD 22 are at full capacity and does not leave the 25% spare capacity required.
| 02SL - Stations (LUL) | Cxxx-NCR-000644 | NCR | Incorrectly fitted Trunking 90 degree bend |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-06-29 | 2019-10-04 15:43 | 97 | 2018-10-30 11:24 | Electrical - Cable Management | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 90 Degree trunking bends on the Westbound platform are not fitted as per drawing.
| 02SL - Stations (LUL) | Cxxx-NCR-000645 | NCR | Inverted trunking installed with no Micanite |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-06-28 | 2019-12-04 14:25 | 159 | 2018-10-30 11:49 | Electrical - Cable Management | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | High level trunking installed high level in 6/219 has not been installed with Micantie between the Top hat T and in the primary trunking route.
| 02SL - Stations (LUL) | Cxxx-NCR-000646 | NCR | No cable segregation on the GRP Tray |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-06-28 | 2019-05-09 13:59 | -50 | 2018-10-30 12:58 | Electrical - Cable Management | 2000 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A temporary GRP tray has been installed where a GRP trunking is temporarily unavailable. Cable segregation needs to be added to the tray.
| 02SL - Stations (LUL) | Cxxx-NCR-000647 | NCR | Insufficiant __ Support on high level trunking in 6/219. |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-06-28 | 2019-01-28 10:17 | -151 | 2018-10-30 13:05 | Electrical - Cable Management | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There is insufficient support on the high level trunking in 6/219.
| 02SL - Stations (LUL) | Cxxx-NCR-000648 | NCR | Fire barrier lid installed incorrectly on Cable tray penetration |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-06-28 | 2019-05-07 10:20 | -52 | 2018-10-30 13:15 | Electrical - Cable Management | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Cable tray lid used to protect cabling from the firestop protection has been installed using the incorrect product size located in area 5/097.
| 02SL - Stations (LUL) | Cxxx-NCR-000649 | NCR | Incorrect aperture cut to WTH floor plates |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-02-06 | 2018-12-07 10:57 | -61 | 2018-10-29 10:21 | Architectural - General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | A 95mm hole has been cut incorrectly into the chequer floor plates that were to be used in the WTH.
| 02SL - Stations (LUL) | Cxxx-NCR-000650 | NCR | Trunking Top hats not fixed correctly WTH Passage |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-06-28 | 2019-10-28 12:37 | 122 | 2018-10-30 13:36 | Electrical - Cable Management | 1000 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Two Top hat T's have not been fixed down.
| 02SL - Stations (LUL) | Cxxx-NCR-000651 | NCR | 110v Sockets left unprotected WTH 5/071 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-06-28 | 2019-02-11 15:22 | -137 | 2018-10-30 13:48 | Electrical - LV Equipment | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | 110v Socket outlets have been fully installed but have had no added protection
| 02SL - Stations (LUL) | Cxxx-NCR-000653 | NCR | Drawings used for construction not Code 1 in eB. |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-03-31 | 2019-03-18 09:48 | -13 | 2018-10-30 15:21 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | 1-Drawing (Cxxx-SKC-S-DWG-Cxxx-50363 C01 ) not in eB used for construction of trench slab Level -5 M.P.S. Area . 2- Two drawings were used for Waterproofing in the Lightwell & Lightwell Extension construction, both drawings were issued under Cxxx-SKC-C-LRG-Cxxx-50248 Rev 26.0 had been reviewed and comments closed by __ however, this was never change to Code1, this can be found in Cxxx-SKC-C-XCS-Cxxx-50117_Rev26_CRLupdate13Feb2018. Cxxx-SKC-A-DDD-Cxxx-82900 P04 Cxxx-SKC-A-DDD-Cxxx-82901 P04 3-__ also spotted that Drawing Cxxx-SKC-S-DWG-Cxxx-50059 is not on eB and we have completed the construction of these walls
| 02SL - Stations (LUL) | Cxxx-NCR-000654 | NCR | MCR required for Flat Flexible Trunking used in the LU Link passage WTH |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-12-21 | 2019-05-08 14:29 | 138 | 2018-11-05 13:05 | Electrical - Cable Management | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | An MCR needs to be submitted for the flat flexible trunking in the LU link passage LV-3.
| 02SL - Stations (LUL) | Cxxx-NCR-000655 | NCR | No evidence provided for Floor Tiling Sample Acceptance |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2019-10-02 | 2019-05-08 08:29 | -147 | 2018-11-08 10:02 | Architectural - Flooring | 0 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other management problem | Completed |  | A planned surveillance carried out on Platforms and Tunnels (PES,GFRC and Flooring) ITP Deliverables. The Contractor was requested to provide evidence of formal acceptance submitted for the following Flooring samples in line with JM40.2102; c) Terrazzo Flooring & Accessories. i) 3No. full size tiles of Type FL-601, sufficient to illustrate the complete range variation in colour, textures and other material characteristics of the proposed Terrazzo, this shall include proposed finishing processes undertaken during fabrication where described. ii) A full size Terrazzo insert tile Type FL-602 iii) A full size corduroy tactile Type FL-603 iv) A full size contrasting Terrazzo flooring tile Type FL-618 v) A full size skirting Type SK-601 vi) 3 No. 300mm x 300mm in situ terrazzo tiling samples illustrating the range variation. Following multiple requests no response had been received.
| 02SL - Stations (LUL) | Cxxx-NCR-000656 | NCR | No evidence provided for Floor Tiling Benchmark Acceptance. |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2019-06-28 | 2019-06-12 15:38 | -16 | 2018-11-08 10:08 | Architectural - Flooring | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A planned surveillance carried out on Platforms and Tunnels (PES,GFRC and Flooring) ITP Deliverables. The Contractor was requested to provide evidence of formal acceptance submitted for the following Flooring Benchmarks; a) d) Terrazzo Flooring i) The first installed area of the proposed Terrazzo flooring tiles Type FL-601, not less than 5m² in area to include interface conditions with movement joints, PES wall, Platform Screen Door threshold plate and skirting kerb Type SK-601/ 701 whichever is applicable ii) The first full installation of Type FL-602 in to a maintenance access hatch. iii) The first installed 3No. corduroy tactiles of Type FL-603. iv) The first installed 3No. contrasting flooring tiles of Type FL-618. v) The first installed 2m length of skirting Type SK-601. b) Movement and Structural Expansion Joints i) The first installed 2No. lengths of movement joint Type M__-101 prior to installation of the floor tiles. ii) The first installed 2No. lengths of movement joint Type M__-106 prior to installation of the floor tiles. iii) The first installed 2No. lengths of structural expansion joint Type M__-502 prior to installation of the floor tiles. iv) The first installed area of movement joint with 2m depth of floor tile Type FL-201/ FL-601 on each side. Following multiple requests no response had been received.
| 02SL - Stations (LUL) | Cxxx-NCR-000657 | NCR | Contractor unable to supply floor tiling performance test reports |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2019-07-31 | 2019-06-20 13:07 | -41 | 2018-11-08 10:12 | Architectural - Flooring | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | A planned surveillance carried out on Platforms and Tunnels (PES,GFRC and Flooring) ITP Deliverables. The Contractor was requested to provide evidence of Floor Tiling performance as follows; JM40.2202 Sealant Testing JM40.2203 Grout Staining JM40.2204 Slip Resistance Testing Following multiple requests no response had been received.
| 02SL - Stations (LUL) | Cxxx-NCR-000658 | NCR | No evidence provided for PES Samples Acceptance |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2019-07-31 | 2019-06-13 11:08 | -48 | 2018-11-08 10:18 | Architectural - Flooring | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | A planned surveillance carried out on Platforms and Tunnels (PES,GFRC and Flooring) ITP Deliverables. The Contractor was requested to provide evidence of formal acceptance submitted for the following PES samples in line with JH11.2101; d) 500x500 sample of each type of grille. e) All accepted gasket types, extrusions, caps, trims and flashings, including at least one joint and one corner joint and including accepted finishes and colours where applicable. f) Accepted ironmongery and hardware. g) All visible fixings (where visible fixings form part of the design intent). h) Samples of fastening devices and anchors. i) Operating mechanisms, switches and controls, including mounting. Following multiple requests no response had been received.
| 02SL - Stations (LUL) | Cxxx-NCR-000659 | NCR | Services clash |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2018-11-23 | 2019-02-27 15:57 | 96 | 2018-11-09 08:27 | Communications and Control Systems - Public Address Systems | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Service clash was raised to between Speaker location and Drain Cock, WTH L-2 3/240. Speaker has been moved roughly 250mm with the Connection box now located under the Drain Cock.
| 02SL - Stations (LUL) | Cxxx-NCR-000660 | NCR | ETH Ground Floor - IW21 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-02-28 | 2019-02-18 13:59 | -10 | 2018-11-09 08:22 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | ETH Ground Floor IW21. Thickness of lower section of IW21 cast incorrectly with the L0 slab. Survey shows the areas affected on both north and south face of IW21. Reinforcement is in the correct design position with excessive cover.
| 02SL - Stations (LUL) | Cxxx-NCR-000661 | NCR | Level +0.5 Blockwork interface with coffers |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-06-30 | 2019-04-11 11:45 | -80 | 2018-11-14 15:39 | Architectural - Brickworks/Blockworks | 2000 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | With reference to Cxxx-RFI-004031 Cxxx have provided details for the interface between the soffit of the coffers and the blockwork, see attached DDN C799 - RFI-4031 - ETH L 0.5 BOH Blockwork Wall-to-Coffer Interface. Within this document (1.a With Wi System head fixing) Cxxx have detailed 'cast-in ferrules' to be installed in the coffers which will receive the fixings for the 2no. m16 reinforcing bars which are installed in each wind-post, see ‘__ - Wi System details attached for reference. The cast-in ferrules have not been communicated during the procurement of the coffers and have not been installed.
| 02SL - Stations (LUL) | Cxxx-NCR-000662 | NCR | Incorrect screed level to ETH ground level 0 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-04-25 | 2019-02-08 15:45 | -76 | 2018-11-09 17:14 | Architectural - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Drawing Cxxx-SKC-A-DDE-Cxxx-77500 was accepted Code 1 as part of GIR 42 shows an incorrect top of screed level of +123.935 that doesn't account for a 50mm granite tile with 30mm Topcem bedding required as per current accepted tile design, in the FFL of +124.000.
| 02SL - Stations (LUL) | Cxxx-NCR-000663 | NCR | Non Compliant Top Hat Trunking T's WTH 5/073 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-06-28 | 2019-11-10 16:50 | 135 | 2018-11-13 11:57 | Electrical - Cable Management | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Non manufactured Top Hat Trunking T's have been installed in passageway 5/073. These need to be replaced for Factory manufactured T's.
| 02SL - Stations (LUL) | Cxxx-NCR-000664 | NCR | Domestic Pipework too close to other services WTH |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2018-12-21 | 2018-12-07 12:26 | -14 | 2018-11-14 09:02 | Mechanical - Piping | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Domestic pipework is too close to other services, preventing insulation to be installed. Cxxx-SKC-P-DDA-Cxxx--11120 C02 was used in may 2017 which shows this routing. Cxxx-SKC-P-DDA-Cxxx--11120 P08 was stamped IFC for GIR 53 which shows the pipe staright and enough space for Insulation.
| 02SL - Stations (LUL) | Cxxx-NCR-000665 | NCR | WTH -AP1 tunnel link - gridline 12 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-01-31 | 2019-03-18 17:23 | 46 | 2018-12-06 09:05 | Architectural - General | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | were instructed to trimming SCL only within AP1 tunnel link in isolated locations. Subcontractor proceed to trim in an isolated location of the RC section. Cxxx-RFI-004825 response was to avoid cutting of the RC section.
| 02SL - Stations (LUL) | Cxxx-NCR-000666 | NCR | Access Door Obstructed by CMS and bracketry WTH L-2 PFR1 3/777 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-23 | 2019-10-30 22:29 | 37 | 2019-07-15 14:25 | Electrical - Cable Management | 0 |  | Design | Rework | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | CMS and Bracketry is preventing access to the maintenance access door of the ducting.
| 02SL - Stations (LUL) | Cxxx-NCR-000671 | NCR | Damper actuators Fully obstructed by CMS WTH L-4 Circ Area 5/072 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-23 | 2021-02-28 18:03 | 524 | 2019-03-01 12:44 | Electrical - Cable Management | 2000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | CMS obstructing damper actuators AS-W-FD096 and GE-W-FD135 on WTH Level -4 Circ area 5/072. Trunking and top hats need to move to allow necessary access.
| 02SL - Stations (LUL) | Cxxx-NCR-000672 | NCR | FFP-W-SF001 Stair pressurisation fan obstructed by PIR WTH L-2 3/777 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-02-21 | 2020-02-18 10:09 | -3 | 2019-12-10 16:10 | Electrical - Cable Management | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | PIR is obstructing FFP-W-SF001 Stair pressurisation fan: the subcontractor did not install PIR as per the AFC current rev.
| 02SL - Stations (LUL) | Cxxx-NCR-000674 | NCR | NCR for Cable Glands with no MCR |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-27 | 2019-03-18 17:03 | -193 | 2018-11-30 14:45 | Electrical - Power Distribution | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Cable glands have been Installed that have no MCR.
| 02SL - Stations (LUL) | Cxxx-NCR-000675 | NCR | MCR's required on installed electrical equipment |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-27 | 2019-11-18 20:01 | 52 | 2018-11-30 15:58 | Electrical - General | 0 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Material Compliance Register needs to be completed for the following equipment installed: 230V sockets. __ Bypass Module. __ UPS Board. PIR Sensors. PES Earth Cleats. __ Din rail terminals. __ Distribution Board. Heat shrink. Unbranded brown wall plugs.
| 02SL - Stations (LUL) | Cxxx-NCR-000676 | NCR | MCR Required for 110v Transformers |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-27 | 2019-03-18 15:02 | -193 | 2018-11-30 16:07 | Electrical - LV Equipment | 0 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Material compliance register (MCR) needs to be completed for the 110v transformers installed throughout the station.
| 02SL - Stations (LUL) | Cxxx-NCR-000677 | NCR | ETH Escape Stairs out of tolerance |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-11-30 | 2019-09-27 16:13 | -64 | 2018-12-06 09:16 | Civil - Civil Engineering General | 125000 |  | Incorrect Installation | Repair | 1 (>60k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | ETH staircase ESS7 & ESS8 are out of tolerance with the JL30 specification. An as-built survey was undertaken on all levels the results are attached "Final report - Green staircase Rev. 2.0.pdf" & "Final report - Purple staircase Rev. 3.0.pdf" ****** Update 14.03.19 ********* An as-built survey was undertaken on all levels and it was found that ETH staircase ESS7 & ESS8 are out of tolerance with the JL30 specification.
| 02SL - Stations (LUL) | Cxxx-NCR-000678 | NCR | Meters not provided on the LV Submain Switchboard |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-27 | 2019-09-18 15:54 | -9 | 2018-11-30 16:25 | Electrical - Switchgear | 20000 |  | Incomplete Works | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Meters have not been provided on the __ LV Sub main Switchgear panels.
| 02SL - Stations (LUL) | Cxxx-NCR-000679 | NCR | Damaged Attenuator |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-27 | 2019-02-13 09:06 | -226 | 2018-11-30 16:36 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Two damaged attenuators were noticed after delivery had taken place. This damage was not seen on the delivery vehicle, only when they were about to be lowered did engineering notice.
| 02SL - Stations (LUL) | Cxxx-NCR-000680 | NCR | ETH L+1 IW31/32 riser infill missing dowels (north side) |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-01-04 | 2019-01-07 15:53 | 3 | 2018-12-05 12:14 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | L+1 IW31/32 riser infill unable to drill and fix dowels along the north edge due to an OSD wall have been constructed on the south of the infill (see attached photos).
| 02SL - Stations (LUL) | Cxxx-NCR-000681 | NCR | WTH, Between Level +0.5 to +1 Slabs, Lift Shaft 8 Lifting Eye Sockets Not Cast In Vertical |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-01-06 | 2019-05-20 17:03 | 134 | 2018-12-07 16:06 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __ has cast 2 of the lifting eye sockets in the soffit of lift shaft 8 not completely vertical. is yet to ascertain by exactly how much they are out of plumb, but these 2 lifting eyes do not meet the __'s requirements. These lifting eyes are No. 28328/5 and 28328/12, as per the attached photos and lifting eye layout markup.
| 02SL - Stations (LUL) | Cxxx-NCR-000682 | NCR | ETH Tunnel Fire Main Testing |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-10-01 | 2018-12-12 11:36 | -293 | 2018-12-12 09:43 | Systems - Fire Detection systems and Mains | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient work planning by the subcontractors | Completed |  | Cxxx are responsible to complete the hydrostatic test of the Tunnel Fire Main (TFM) from the breeching inlet point to the Cxxx interface point. During hydrostatic testing the breeching inlet point was in a temporary position due to incomplete RC works on site. Also the PN16 breeching inlet point weeped from the 2.5" push fit connection and its connection to the body of the unit when the hydrostatic test of the TFM was sitting at the 19 bar test pressure.
| 02SL - Stations (LUL) | Cxxx-NCR-000683 | NCR | ETH - Stair Escape 7 (1/581) & Stair Escape 8 (1/582) Top Step Not Cast |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-01-12 | 2019-03-14 17:48 | 61 | 2018-12-13 10:27 | Civil - Civil Engineering General | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The top step of both Stair Escape 7 (1/581) and Stair Escape 8 (1/582) have not been cast monolithically as per the drawing Cxxx-SKC-S-DWG-Cxxx-50339 C01 (see Flight 11 & 12). They were not cast in the first instance due to the the stairs being used as the predominant access way and would create an unnecessary trip hazard for anybody using the stairs
| 02SL - Stations (LUL) | Cxxx-NCR-000684 | NCR | Fire Damper Doors Blocked for Access |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2018-12-27 | 2019-06-20 09:46 | 175 | 2018-12-13 10:57 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Service clash onsite with CMS/ Bracketry and high Level Duct Fire Damper Actuator, Lobby 4/097outside cooling room LCR (ESR 1). Dampers AS-E-FD030 and GE-E-FD030 unmaintainable due to __ and Conduits blocking access
| 02SL - Stations (LUL) | Cxxx-NCR-000685 | NCR | West Ticket Hall Fire Main Testing |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-08-06 | 2018-12-13 13:03 | -236 | 2018-12-13 11:31 | Systems - Fire Detection systems and Mains | 500 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | Cxxx are responsible to complete the hydrostatic test of the Tunnel Fire Main (TFM) from the breeching inlet point to the Cxxx interface point. During hydrostatic testing the breeching inlet point was not connected & the pipework was blanked off. Thus the final joint was not tested.
| 02SL - Stations (LUL) | Cxxx-NCR-000686 | NCR | AS-E-FD022 , GE-E-FD022, service clash |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2021-02-08 | 2021-02-07 08:22 | -1 | 2018-12-13 11:34 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | While on site inspection, it was found that there is a service clash with Conduits and Bracketry for Comms / Fire Damper panel and High Level Access to Duct Fire Damper Actuators. These have already been relocated 180 degrees to allow for a previous clash. See drawing Cxxx-SKC-M-DDA-Cxxx-63246
| 02SL - Stations (LUL) | Cxxx-NCR-000687 | NCR | Calibration Cert Invalid |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-08-31 | 2019-07-25 09:48 | -37 | 2019-01-16 15:57 | Electrical - Electrical Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Counterfeit Items | Completed |  | __ have been using a torque wrench that was out of date. In order to cover up this fact an individual from __ has counterfeited a calibration cert which was then provided to . Calibration certificates has been confirmed to be counterfeited with __, who's name was used on the counterfeit.
| 02SL - Stations (LUL) | Cxxx-NCR-000688 | NCR | ETH -5 PMR tray at full capacity |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-06-28 | 2019-04-04 12:16 | -85 | 2018-12-15 11:43 | Electrical - Cable Management | 1000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Cable tray is at full capacity not leaving the 25% spare capacity as required.
| 02SL - Stations (LUL) | Cxxx-NCR-000689 | NCR | WTH -5 CER Earth tray at full capacity |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-07-26 | 2019-11-19 10:08 | 116 | 2018-12-15 11:51 | Electrical - Cable Management | 1000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Cable tray is at full capacity not leaving the 25% spare capacity as required.
| 02SL - Stations (LUL) | Cxxx-NCR-000690 | NCR | Staircase Pressurisation Fans |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-04-30 | 2021-02-03 16:53 | 645 | 2018-12-19 09:46 | Mechanical - Mechanical Engineering General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Staircase pressurisation fans FFP-SF001 and FFP-W-SF002,situated WTH L-2 Room 3/777, have no access to install or remove wall side nuts and bolts to allow for future maintenance. see attached Drawing Cxxx-SKC-M-DDA-Cxxx-11121 As per the MEP Fit-out Specification JY41, Clause JY41,1304, Item (b). Elements of the work shall be independently removable ensuring access for maintenance or delivery. The removal of the units shall not affect the performance or safety of any part of these, or adjacent, works. __s have produced a document; Aerofoil Axial Flow Fans, Safety, Installation and Maintenance Instructions part No. 416421, which recommends the required maintenance regime to be followed for Safety Critical Fans.
| 02SL - Stations (LUL) | Cxxx-NCR-000691 | NCR | Accommodation Air Release fans |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-11-03 | 2021-04-13 12:06 | 527 | 2019-03-04 10:33 | Mechanical - Mechanical Engineering General | 15000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | AAR-W-EF001 and AAR-W-EF002 located in WTH L-2 Room 3/778, will need to be accessible for future maintenance, One of the the proposed access routes is blocked by the thrust bracket which had to be installed for the Tunnel Fire Hydrant Main installation. See Drawing Cxxx-SKC-M-DDA-Cxxx-61123 However, it has been noted that the Ductwork contractors will demonstrate the removal of the fan sets on the opposite side to the hydrant bracket.
| 02SL - Stations (LUL) | Cxxx-NCR-000692 | NCR | P&T, CH2 and CH3 area incorrect positioning of conduit feeding signage totems |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-03-31 | 2019-05-30 14:30 | 60 | 2018-12-18 11:07 | Architectural - General | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | When attempting to install signage totem base plates in the level minus 5 concourse halls it was noted that the conduits required to feed services to the totems were installed in the incorrect location. The conduits ranged from 40mm to 240mm out of the required location in the North-South direction.
| 02SL - Stations (LUL) | Cxxx-NCR-000693 | NCR | Damaged SWA sheath SLD 22 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-10-31 | 2019-12-22 13:32 | 52 | 2019-01-04 13:55 | Electrical - Electrical Engineering General | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The outer sheath on the SWA cable in SLD 22 has been damaged on installation
| 02SL - Stations (LUL) | Cxxx-NCR-000694 | NCR | Damaged Cable 5/919 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-10-31 | 2019-12-16 19:16 | 46 | 2019-01-04 14:24 | Electrical - Electrical Engineering General | 8000 |  | Damaged | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Cable is damaged in 5/919. It looks like the cable has been damaged on install.
| 02SL - Stations (LUL) | Cxxx-NCR-000695 | NCR | Damaged radio cables |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-08-22 | 2019-08-08 17:48 | -14 | 2019-08-08 08:39 | Communications and Control Systems - Radio | 5000 |  | Damaged | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Damaged cables FD2107 and FD2114
| 02SL - Stations (LUL) | Cxxx-NCR-000696 | NCR | WTH - Level +1 - Edge Beam Grid 1/G-H+3m - Out of Tolerance |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-02-13 | 2021-09-21 13:13 | 951 | 2019-01-14 09:32 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The L+1 RC edge beam shutter on GL 1 & G to H+3m has been found to have shifted during the concrete pour. The edge beam has been surveyed (refer WTH __ & Edge Beam Survey North Elevation) with the findings being the 9m section protrudes outwards (north) from design in a bowed/convex shape. Tolerances are as per KF10 Rev 14 Appendix KF10-10 Bow of Elements Further to above the halfen channels cast into the edge beam were fixed to the shutter and have also shifted out of position in line with the RC edge beam's deviation.
| 02SL - Stations (LUL) | Cxxx-NCR-000697 | NCR | WTH - Level +1 RC Edge Beam - Grid 1 - Missing __ Grid K |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-04-22 | 2019-03-01 12:51 | -52 | 2019-01-14 10:19 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During the formation of L+1 Grid 1 RC edge beam it has been identified an approximate 1m length of 2 x halfen channel layers has not been cast at Grid K (Refer WTH __ & Edge Beam Survey North Elevation).
| 02SL - Stations (LUL) | Cxxx-NCR-000698 | NCR | WTH RC works / L+1 Upstands GL 1-4 / G-L - No concrete cubes taken |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-04-30 | 2019-02-12 17:19 | -77 | 2019-01-14 16:24 | Civil - Civil Engineering General | 0 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | On 13/01/18, L+1 Upstands GL 1-4 / G-L were poured and no concrete cubes were taken. The concrete tickets have been attached to show that the correct concrete was used, however the strength of the upstands in the section mentioned cannot be ascertained.
| 02SL - Stations (LUL) | Cxxx-NCR-000699 | NCR | ETH - Vent Shaft Level +3 Wall 5 has been cast low between 30mm - 125mm |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-03-29 | 2019-05-14 14:34 | 46 | 2019-01-22 14:58 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | ETH - Vent Shaft Level +3 Wall 5 has been cast low between 30mm - 125mm
| 02SL - Stations (LUL) | Cxxx-NCR-000700 | NCR | ETH. Level 0 - North and South face Wall IW-21 out tolerance |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-04-20 | 2019-06-07 07:22 | 48 | 2019-01-23 12:39 | Civil - Civil Engineering General | 0 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following a post-pour inspection with CRL, it was found that L-0 IW-21 North and south elevation appears to be out of tolerance. An as-built survey of the wall was carried out showing that IW 21 is out of tolerance on both north and south elevation. See as-built survey "ETH - IW-21 South Elevation and Cover meter survey. attached See also an as-built survey of the North Elevation. attached
| 02SL - Stations (LUL) | Cxxx-NCR-000701 | NCR | ETH Smoke dampers - Brackets blocking access/maintenance |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-25 | 2019-06-21 10:23 | -96 | 2019-01-25 11:23 | Fire - Fire Systems & General | 1000 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | __ support installed clashes with the Smoke damper in passageway 5/073 in the ETH.
| 02SL - Stations (LUL) | Cxxx-NCR-000702 | NCR | ETH L-2 Corridor AAR smoke damper actuator obstructed by __ (lighting support) |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-01-30 | 2021-02-18 14:05 | 385 | 2020-01-16 16:03 | Fire - Fire Systems & General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Please see attached image which shows that A&M impeded by 2 no __.
| 02SL - Stations (LUL) | Cxxx-NCR-000703 | NCR | Lift 6,7,8 additional builders works required due to incorrect recesses and core holes missing |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-03-29 | 2021-04-20 12:40 | 753 | 2019-01-25 12:46 | Civil - Civil Engineering General | 500 |  | Incomplete Works | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There are outstanding builders works to be carried out on lift shaft 6, 7 and 8 that were either missed or constructed incorrectly originally for the installation of __'s panels that need to be installed on the outside of the lift shafts at various levels. For lift shaft 6, there are 3 outstanding holes that need to be cored for cables to run through into the lift shaft at ground floor. A marked up drawing showing the holes that are required 'LIFT 6 level 0 210219' is attached. Lift shaft 7 has 2 recesses that required additional scabbling to allow the panels to be installed, one at level -5 and one at level -1. These have also been marked on site by __, see 2 mark ups attached, 'LIFT 7 level -1 210219' and 'LIFT 7 level -5 210219'. For liftshaft 8, additional scabbling needs to be done to allow panels into the recesses at level -1, -2, -4 and -5. See mark-up ‘LIFT 8 Level -1,-2,-4,-5 210219’ attached. We require approval to core and scabble back these areas for __ to be able to install their equipment.
| 02SL - Stations (LUL) | Cxxx-NCR-000704 | NCR | Temp cable incorrectly installed and damaging Fire Alarm install(Device L20/D73) |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-26 | 2019-12-10 19:12 | 75 | 2019-01-25 10:45 | Fire - Fire Systems & General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Temp supply pulled into surface water sump room 6/771. Temp supply tied to uni strut supporting conduit to devise L20/D73. Weight of cable has pulled uni strut and conduit. Coupler has pulled out of adaptable box and damage to adaptable box
| 02SL - Stations (LUL) | Cxxx-NCR-000705 | NCR | incorrect MCR details-Spacenet Selectrabox |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-23 | 2019-11-09 20:48 | 47 | 2019-01-25 13:46 | Electrical - Cable Management | 0 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | __ has an incorrect data sheet submitted on the MCR a New MCR needs to be raised with the correct data sheet added.
| 02SL - Stations (LUL) | Cxxx-NCR-000706 | NCR | overtighten Coffer box adaptable box's |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-23 | 2019-06-14 13:14 | -101 | 2019-01-25 14:39 | Electrical - Cable Management | 2000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Inadequate/insufficient tooling. | Completed |  | __electricians have been overtightening adaptable box lid in the coffers using impact drivers, this is causing the fixings to fail.
| 02SL - Stations (LUL) | Cxxx-NCR-000707 | NCR | Insufficient protection of assets |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-24 | 2019-04-12 14:47 | -165 | 2019-01-26 10:21 | Electrical - Lighting | 3000 |  | Material | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper storage of material | Completed |  | Lights have been removed and are being stored without protection, damage is more than likely to occur the longer they have been left.Contractors are to protect electrical assets at all times. Any damage endured will be at the cost of the contractor.
| 02SL - Stations (LUL) | Cxxx-NCR-000708 | NCR | Fitting left open to the elements |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-02-22 | 2019-04-29 11:28 | 66 | 2019-01-26 12:54 | Electrical - Lighting | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper storage of material | Completed |  | Fittings have been installed with the lights left open exposed to the outside environment
| 02SL - Stations (LUL) | Cxxx-NCR-000709 | NCR | Heat Shrink has been installed without an MCR. |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-02-09 | 2019-05-01 11:03 | 81 | 2019-01-26 13:51 | Electrical - Electrical Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Heat shrink was used on a cable without a relevant MCR in place
| 02SL - Stations (LUL) | Cxxx-NCR-000710 | NCR | Incorrect lug used on CPC |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-25 | 2019-04-11 15:35 | -167 | 2019-01-26 14:36 | Electrical - General | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Hole in lug has been drilled to fit bolt instead of using the correct size lug.
| 02SL - Stations (LUL) | Cxxx-NCR-000711 | NCR | WTH - Level +1 Slab - Structural - Missing As Built Survey - Grid 1/4-G/L |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-02-28 | 2019-06-21 15:23 | 113 | 2019-01-29 13:45 | Civil - Civil Engineering General | 0 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | WTH Level +1 Structural slab between Grids 1-4/G-L has not been surveyed prior to the installation of waterproofing membrane and 100mm protection slab. This is not in line with ITP process requirements. It should be noted the slab has been post pour inspected and all rectification works allowing the waterproofing and protection slab to be installed have been completed.
| 02SL - Stations (LUL) | Cxxx-NCR-000712 | NCR | ETH Lv-5 OPE Smoke Dampers SD001 & SD002 access blocked by CMS |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-17 | 2020-01-27 20:18 | 132 | 2019-01-30 13:14 | Electrical - Cable Management | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | OPE Duct Smoke damper Actuator is obstructed by Primary CMS LV-5
| 02SL - Stations (LUL) | Cxxx-NCR-000714 | NCR | Mechanical hatch blocked by light fitting |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-23 | 2019-11-22 10:52 | 60 | 2019-01-30 14:09 | Electrical - Lighting | 0 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Access door to maintain mechanical equipment is being blocked by Light Fitting and bracketry.
| 02SL - Stations (LUL) | Cxxx-NCR-000715 | NCR | dampers obstructed by Drop rods and CMS ETH L-2 3/904 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-23 | 2019-04-11 15:20 | -165 | 2019-01-30 14:41 | Electrical - Cable Management | 2000 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Access door to maintain mechanical equipment is being blocked by CMS and bracketry
| 02SL - Stations (LUL) | Cxxx-NCR-000716 | NCR | Access hatch obstructed by cable tray ETH L-3 Circulation area 4/097 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-25 | 2020-01-12 21:23 | 109 | 2019-01-31 12:39 | Electrical - Cable Management | 0 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Cable tray has been installed to design service hatch positions were added by FPL and had not taken into consideration locations of CMS
| 02SL - Stations (LUL) | Cxxx-NCR-000717 | NCR | Inspection hatch obstructed by double conduit boxes ETH Circulation Area 4/073 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-23 | 2019-12-03 18:44 | 71 | 2019-01-31 15:36 | Electrical - Cable Management | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The mechanical maintenance hatch is currently being blocked by a PIR sensor including CMS and __ Drop.
| 02SL - Stations (LUL) | Cxxx-NCR-000718 | NCR | Motorised dampers obstructed by Cable tray ETH L-3 Circulation Area 4/073 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-23 | 2019-03-11 17:20 | -196 | 2019-01-31 16:08 | Electrical - Cable Management | 500 |  | Planning | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | Access door to maintain Motorised damper is being blocked by PIR sensor and bracketry.
| 02SL - Stations (LUL) | Cxxx-NCR-000719 | NCR | ETH -missing Pre-cast Architectural fixing inspection sheets For Record pack 50124 & 50125 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-03-06 | 2019-03-14 18:04 | 8 | 2019-02-04 08:37 | Civil - Civil Engineering General | 0 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Pre-cast Architectural fixing inspection sheet are missing for ETH L+1 Pour 4a & 4b
| 02SL - Stations (LUL) | Cxxx-NCR-000720 | NCR | WTH L-0 Column C1 - Additional theaded bar(B20)included in reinforcement installation |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-03-07 | 2019-03-18 17:34 | 11 | 2019-02-05 14:28 | Civil - Civil Engineering General | 0 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Threaded bar (B20) horizontal bars being installed to maintain continuity of the rebar along north face of Column C1. This was installed as no similar sized bar was available at the time. An FCD should have been raised at the time however this was not done by Cxxx, hence the NCR being raised now by Cxxx as correctly identified by __. See attached photos (Pictures 2, 4, 6 jpg.). Refer to attached Cxxx-SKC-S-DWG-Cxxx-50490 & Cxxx-SKC-S-DWG-Cxxx-50489 for adjacent wall reinforcement details and Key plan.
| 02SL - Stations (LUL) | Cxxx-NCR-000721 | NCR | Incorrect Secondry point from Transformer |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-12-31 | 2020-04-28 13:39 | 119 | 2019-02-06 10:47 | Electrical - Transformers | 3000 |  | Material | Rework | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | Incorrect links installed from Transformer secondary connection point the LV busbar unit. Laminated flexible units installed rather than braided type.
| 02SL - Stations (LUL) | Cxxx-NCR-000722 | NCR | WTH escalator box wall 15 & 17-__ - Clash between LIN-403 and FX-914 substructure |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-03-12 | 2019-02-25 12:11 | -15 | 2019-02-07 15:17 | Architectural - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | There was a clash between the LIN-403 substructure and the lightbox substructure. Photos of the situation are attached.
| 02SL - Stations (LUL) | Cxxx-NCR-000723 | NCR | Incorrect Eathing between ETH Transformer Room to LV Switchroom |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-02-21 | 2020-09-23 15:01 | 580 | 2019-02-07 14:54 | Electrical - Earthing & Bonding | 10000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 12 no earth cable have been installed from the ETH transformer room to the incorrect LV switch room. A & B rooms have been crossed
| 02SL - Stations (LUL) | Cxxx-NCR-000724 | NCR | WTH Level -3 AP1 Link Tunnel, AP1 Evaporation Channel Modification |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-03-13 | 2019-07-08 16:59 | 117 | 2019-02-11 16:32 | Civil - Civil Engineering General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Evaporation channel within AP1 clashing with substructure of GFRC cladding
| 02SL - Stations (LUL) | Cxxx-NCR-000725 | NCR | WTH Vent Shaft, L+3 North internal and external Opening |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-30 | 2019-05-14 14:53 | -139 | 2019-02-15 11:06 | Civil - Civil Engineering General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | As __'s scabbling the opening sides and repairing them to correct lines and levels we found -2no of reinforcement in the internal face and 1no on the external face of structural opening walls/soffit will have less cover to the reinforcement after repair work carried .Required cover to all faces is 25mm as per drawing Cxxx-SKC-S-DWG-Cxxx-50417
| 02SL - Stations (LUL) | Cxxx-NCR-000726 | NCR | P&T,Clash between and Sobra cladding on ES2 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-07-29 | 2019-03-21 11:39 | -130 | 2019-02-15 11:54 | Architectural - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | ES2 steel work/support structure clash with Sobra panels and top of ES2 GFRC /Sobra panels interface
| 02SL - Stations (LUL) | Cxxx-NCR-000728 | NCR | ETH: RC6 Column L+0.5 to L1 cast to an older revision drawing |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-07-29 | 2019-03-21 11:52 | -130 | 2019-02-21 14:09 | Civil - Civil Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | It has been noted that the RC6 Column from Lev +0.5 to Lev +1 at the ETH has been cast to an older revision I.e. Rev C 06 instead of Rev C 08. Refer to GA Drawing No. Cxxx-__-S-DDL-Cxxx-52097 The latest GA drawing Rev C08 changed the offset dimension from 325mm to 275mm from GL. A to the east face of the column. As an effect the column has been cast to the 325mm design position. It has also been noted that the Reinforcement Drawing wasn't revised to include for this change in detail. Refer to attached Cxxx-SKC-S-DWG-Cxxx-50167 Reinforcement Details C05. We propose to leave the column as is and external cladding and architectural substructures be modified to accommodate the existing position.
| 02SL - Stations (LUL) | Cxxx-NCR-000730 | NCR | Twin pair Dali cable being stripped then wired |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-07-05 08:17 | -61 | 2019-02-19 09:47 | Electrical - Lighting | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The twin pair Dali cable has had the outer sheath stripped in certain locations. (For this specific cable the outer sheath should remain fully intact until the point of termination)
| 02SL - Stations (LUL) | Cxxx-NCR-000732 | NCR | PES1 and PES2 Cxxx-DAT-03546 and Cxxx-DAT-03547 Damaged |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-23 | 2019-11-19 10:17 | 57 | 2019-02-19 11:35 | Electrical - Cable Management | 3000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Cxxx had received instruction to remove the two Cat6 Scada cables PES1 and PES2 from the PSD cabinet within room6/961. This was undertook by Cxxx on the night 31.01.19. It has been found that both cables have been damaged during the removal of said cables. Both cables have been IRN'd Cxxx-SKC-R3-NOX-Cxxx-50010 on the 30.11.18
| 02SL - Stations (LUL) | Cxxx-NCR-000733 | NCR | WTH - Level -1 __ Clash with RC Edge Beam/FX-914 - Substructure Profile Change |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-06-28 | 2019-03-15 16:02 | -105 | 2019-02-19 16:38 | Architectural - General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __ have identified a section of the L-1 RC Slab/Edge beam located at Grid 3/H that clashes with their bracketry. __ bracketry identified in 6272-M3403e.pdf. will be amended by __ however this is not sufficient to pass the clash with the Level -1 slab. are requesting a section identified in attachment “RC Beam – FX-914 Interface Clash Sketch Marked up 2” be allowed to be scabbled back 20mm. The document also contains the result of the cover meter survey carried out by . The cover meter survey indicates scabbling back 20mm will retain a minimum 25mm cover to reinforcement within the affected area. Further attachments are images of the area to be scabbled, marked up Cxxx reinforcement as built drawings and Cxxx elevation/sections in the affected area
| 02SL - Stations (LUL) | Cxxx-NCR-000734 | NCR | ETH - Staircase Type STR 307 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-10-23 | 2019-09-27 14:36 | -26 | 2019-02-20 08:18 | Civil - Civil Engineering General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Following an as built survey of all stairs on site, several type STR-307 maintenance stairs are out of tolerance when compared to specification JL30 (Cxxx-SKC-A-RSP-Cxxx-50021). These are MNS 11, MNS 12, MNS 22 & MNS 23. Please see attached as-built survey of staircases.
| 02SL - Stations (LUL) | Cxxx-NCR-000735 | NCR | Cables in VSD insufficiently crimped |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-23 | 2019-04-04 09:35 | -172 | 2019-02-21 08:20 | Electrical - LV Equipment | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Cable lugs have been installed incorrectly. Lugs are loose and are easily removed by gently pulling the lug.
| 02SL - Stations (LUL) | Cxxx-NCR-000736 | NCR | Potential fan access issue (for fan removal) ETH Level -4 OPE fans |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-22 | 2019-05-22 15:55 | -123 | 2019-02-21 08:53 | Mechanical - Heating Ventilation & Air Conditioning | 2500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | There is a potential fan access issue for the ETH Level -4 OPE fans. With the installed CMS (to the Right Hand Side) the lighting positions and the conduit drops progressing fast it is difficult for me to imagine the fan being access with equipment and removed without obstruction.
| 02SL - Stations (LUL) | Cxxx-NCR-000737 | NCR | ETH - Incorrect Fabrication of Wind Posts -ETH G.L 4 (G.L E to F) |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-07-01 | 2019-03-14 18:11 | -109 | 2019-02-26 09:39 | Civil - Civil Engineering General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | During the installation of the Windposts located along GL 4 between the PC Columns at the eastern end of Colonnade (for location refer to drawing Cxxx-SKC-A-DDE-Cxxx-77500), it has been identified that there is a discrepancy between the design for the __s cast in the PC Columns (Refer to drawing No. Cxxx-SKC-A-DWG-Cxxx-50979 P09 PC8B) and the design for the Windposts (Refer to drawing No. Cxxx-SKC-S-DWG-Cxxx-51030-P01 - CODE 1 (__ Status A)). Upon review it appears the incorrect information has been issued to Bridge for the fabrication of the 3 No. wind posts and associated supports and fixings at the ETH. As an effect 2No discrepancies have been highlighted. • Firstly, the __ channels that have been cast in the soffit are smaller than the fixings used for the top connection of the wind posts. • Secondly, the end plates for the 4 No. SHS horizontal transoms have the incorrect dimensions for the pre-drilled fixing holes. The end plates have been fabricated with a spacing of 165mm in-between the pre-drilled holes for the __ T bolts, where they should have been 94mm as per the __ spacing on Cxxx-SKC-A-DWG-Cxxx-50979 P09 PC8B.
| 02SL - Stations (LUL) | Cxxx-NCR-000738 | NCR | WTH - AP1 Structural Slab - No Post Pour Inspection |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-05-01 | 2019-04-02 15:01 | -29 | 2019-02-26 10:30 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | As a result of NCR-583, it was found that a post pour inspection was not completed for the structural slab at level -3 WTH - AP1 slab .
| 02SL - Stations (LUL) | Cxxx-NCR-000739 | NCR | ETH L-4 small supply duct - damper acess restricted AS-E-FD026 lobby 5/095 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-24 | 2021-03-16 14:37 | 539 | 2019-02-26 16:38 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient work planning by the subcontractors | Completed |  | t relates to poor access to fire damper AS-E-FD026. It is blocked by pipework and associated supports. It is at ETH L-4
| 02SL - Stations (LUL) | Cxxx-NCR-000740 | NCR | P&T Out of Alignment of -5 LEVEL Floor Skirtings at Corners of Cross Passage |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2022-09-04 | 2022-06-17 14:10 | -79 | 2019-02-27 13:28 | Architectural - Flooring | 6000 |  | Design | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | The inconsistent alignment of the floor skirtings at the corners of the cross passages at some locations.
| 02SL - Stations (LUL) | Cxxx-NCR-000741 | NCR | Incorrect Fixings (__ HST3-R)used on sprayed concrete lined walls and ceiling |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-23 | 2019-04-04 09:56 | -172 | 2019-02-28 11:35 | Electrical - Cable Management | 0 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | The __ HST3-R is approved for use in cracked and normal concrete ,but the MCR clearly that these products are not to be used in Sprayed Concrete Lining (SCL), brick or concrete blocks. The fixings have been used station wide on SCL and is not fit for purpose.
| 02SL - Stations (LUL) | Cxxx-NCR-000742 | NCR | P&T Trimming of RC Concrete collar in AP2 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-05-31 | 2019-05-20 17:18 | -11 | 2019-02-28 14:31 | Civil - Civil Engineering General | 50 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | The cantilever steel was installed on Friday 22/02/19. During the install the Subcontractor identified a 30mm clash with the RC concrete collar on site. The Supervisor proceeded to locally cut into the collar to allow the steel to be installed. Site photo is attached. This did not follow process, as CRL approval had not be gained before proceeding to cut into the concrete collar.
| 02SL - Stations (LUL) | Cxxx-NCR-000743 | NCR | ETH Level -5 Drilling through Rebar in AP3 Soffit |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-06-24 | 2019-04-02 15:14 | -83 | 2019-03-07 14:53 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Subcontractor drilled through rebar which was not in line with RFI parameters in AP3 . Our Subcontractor have been installing steelwork in AP3 was originally instructed under PMC 2965 -which at point 3 confirms that the load bearing walls are as detailed on drawings :Cxxx-__-A-DDL-Cxxx-19150 and Cxxx-__-A-DDL-Cxxx-69151. (both drawings linked) The particular locations of drilling in AP3 covered under this NCR are adjacent to a load bearing wall. Once drilled, we were then issued DDN C877 (attached) under Cxxx-RFI-004816.(linked) DDN C877 has hand-drawn the load bearing walls of which were different to the previously sent drawings. DDN C877 (attached) shows the adjacent wall is not load bearing and details the head plate design to avoid drilling through rebar in the soffit. Our subcontractor () was issued with these details, however site operatives were still drilling in line with previously issued drawings and have cored through rebar at 7 no. of locations. See AP3 cut rebar (attached) Upon review of the RFI-004816 and PMI002507 attached response, and of the understanding that they were drilling adjacent to a load bearing wall we realized that we have not conformed with the parameters outlined at Location 4 only. (See AP3 cut rebar) attached have undertaken rebar scanning and believe that the same bar have been hit at all locations running parallel to the wall, however two bars within 400mm spacing were drilled through at this location. Hence, an NCR has been raised.
| 02SL - Stations (LUL) | Cxxx-NCR-000744 | NCR | P&T AP1 DAL Support Steel Installation |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-05-28 | 2019-03-21 11:33 | -68 | 2019-03-01 15:49 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Works on the DAL support steel began in Access Passage 1 prior to an ITP being approved by CRL.
| 02SL - Stations (LUL) | Cxxx-NCR-000745 | NCR | WTH - Missing cube result - Vent Shaft L+3 Door Reduction W-D-792-D03 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-04-03 | 2019-06-06 15:02 | 64 | 2019-03-04 08:16 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | WTH Vent Shaft Level +3 Door W-D-792-D03 was reduced in dimension by RC infill as per Cxxx-PMI-01121/Cxxx-RFI-003278. Door is located between eastbound and westbound draft reliefs at Gridline 2/B. Cube results were not taken/cannot be located.
| 02SL - Stations (LUL) | Cxxx-NCR-000746 | NCR | __ panel doors not aligning |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-01-31 | 2020-11-06 14:17 | 280 | 2019-03-07 15:14 | Electrical - LV Equipment | 5000 |  | Manufacturing Defect | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | __ Distribution panels do not align as designed. Photos attached show clear gaps in the panel doors where the doors have dropped and do not align correctly. Panels are not as shown in Design Drawings the doors are considerably misaligned.
| 02SL - Stations (LUL) | Cxxx-NCR-000747 | NCR | Termination Lugs insuficiantly Crimped |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-23 | 2019-05-07 12:59 | -139 | 2019-03-08 08:45 | Electrical - General | 2000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Termination Lugs have been incorrectly crimped. During inspection cable lugs used to terminate have been removed by gently pulling on the Lug.
| 02SL - Stations (LUL) | Cxxx-NCR-000748 | NCR | __ not installed according to manufacturers recommendation |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-23 | 2020-01-09 22:06 | 108 | 2019-03-12 10:00 | Electrical - Cable Management | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Damage to the __ supports have been reported by Crossrail and NCR was asked to raised. __ slots have been damaged by widening the slots to accommodate 12mm studs. This could weaken the tensile strength of the Strut. The contractor will need to seek confirmation from the manufacturer if the supports is still fit for purpose.
| 02SL - Stations (LUL) | Cxxx-NCR-000749 | NCR | Incorrect Nuts,washers and spring washers installed on __ HST-3 in cross passages |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-10-23 | 2020-06-08 15:44 | 229 | 2019-03-12 16:33 | Electrical - Cable Management | 0 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __ HST3-R fixing bolts have been installed using the incorrect Nuts, washers and spring washers in the cross passages that will invalidate the manufacturers warranty. __ specify only stainless steel components must be used with this fixing or it will invalidate the warranty.
| 02SL - Stations (LUL) | Cxxx-NCR-000750 | NCR | 100x50m trunking not suiteable for wiring |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-23 | 2019-05-22 14:43 | -124 | 2019-03-13 13:41 | Electrical - Cable Management | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Trunking unsuitable for wiring as its not free of burrs, swarf and spot welding on the partitioning
| 02SL - Stations (LUL) | Cxxx-NCR-000752 | NCR | ETH Level 0 Ramp and Screed Detail. GL B-D / 3-4 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-04-14 | 2019-03-18 09:51 | -27 | 2019-03-15 15:11 | Architectural - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Following Cxxx’s RFI response to Cxxx-RFI-004845 to change the proposed screed design for the ramp to RC due to the ramp being ‘subjected to heavy wheel loads for various equipment and plant entering and leaving the building’, have not confirmed with CRL through PTR that there is no intention for any equipment to pass over the wheelchair access ramp and have installed the screed as per proposed design.
| 02SL - Stations (LUL) | Cxxx-NCR-000753 | NCR | ETH ESS7 and ESS8 Half Landings - Finish |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-30 | 2019-09-27 16:17 | -3 | 2019-03-15 16:06 | Civil - Civil Engineering General | 5000 |  | Incorrect Installation | Repair | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following Post-Pour Inspections of the ETH ESS7 (Purple) and ESS8 (Green) half landings it has been noted that they do not comply with the required finishes of Troweled finish for wearing surfaces. In addition some areas are found to be out of positional tolerances. Please see attached As-built information of Half Landings and marked Section of out of tolerance landings.
| 02SL - Stations (LUL) | Cxxx-NCR-000754 | NCR | Broken concrete riser 932 L-3 ETH |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-06-19 | 2019-05-30 15:44 | -20 | 2019-03-19 10:43 | Civil - Civil Engineering General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | The concrete face on riser 932 L-3 ETH has been broken when pull testing M16 __ anchors – see Cxxx-SKC-A-DWG-Cxxx-51458 and photographs. The anchors have been drilled and installed in option 2 positioning due to clashes with reinforcement in option 1 position. Reinforcement likely encountered in option 1 position are highlighted in Cxxx-SKC-S-DWG-Cxxx-50081_markup Minimum cover in the area is 50mm, the anchor has been drilled and fastened in the cover zone, no reinforcement was encountered on the outside face. Concrete face post break to edge of bolt was measured at 39mm – see attached photo.
| 02SL - Stations (LUL) | Cxxx-NCR-000755 | NCR | ETH: ES2 - primary steel snag items |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-05-19 | 2019-06-07 11:55 | 19 | 2019-03-20 09:31 | Architectural - General | 500 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | During a site walk on the ES2 Escalators, it was observed that several fixings on the primary steel are not tightened correctly (refer to the attached photos). This was not flagged to previously.
| 02SL - Stations (LUL) | Cxxx-NCR-000756 | NCR | Cxxx-SKC-S-DWG-Cxxx-50565 C01 - Code 2 used for construction |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-04-19 | 2019-05-15 16:26 | 26 | 2019-03-22 09:13 | Civil - Structural Engineering | 0 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Cxxx-SKC-S-DWG-Cxxx-50565 C01 was not accepted Code 1 by Crossrail during a requested informal review. used this drawing for construction provided they actioned the comments at the pre-pour stage which had been stated on the marked up drawing.
| 02SL - Stations (LUL) | Cxxx-NCR-000757 | NCR | ETH - LIN 407 Clash With RC Wall |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-04-05 | 2019-04-02 10:43 | -3 | 2019-03-22 14:01 | Architectural - General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Incorrect Installation. The bottom precast panel (right hand side) has been cast 33mm shorter. As an effect it cannot be installed / fixed on the steel support as it’s clashing with the RC wall. Refer to attached sketch “SKT 22032019 ETH – Lev 00 Portal Precast Cladding Panel clash with RC Wall”
| 02SL - Stations (LUL) | Cxxx-NCR-000758 | NCR | Level -5 AP2 and AP3 Steelwork clash with Blockwork wall |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-05-31 | 2019-10-04 16:27 | 126 | 2019-03-26 08:41 | Architectural - General | 3000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | In AP2 and AP3 on level -5 the current setting out locations for the primary steel structure cannot be installed as it is clashing directly with the existing blockwork wall. An as-built has been completed of the blockwork wall (attached) in AP2 and it shows that the blockwork has not been constructed out of tolerance. Therefore to allow for the installation of the support steelwork the blockwork wall requires scabbling up to 25mm. In one location this scabbling is required through the lintel over a door and also in one location it is necessary to scabble in to a WI-column. The width of the support steelwork is 120mm and will run the full height of the wall.
| 02SL - Stations (LUL) | Cxxx-NCR-000759 | NCR | Historic NCR - Non Compliant Fixings for CMS installation |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-02-25 | 2020-02-11 19:50 | -14 | 2020-02-11 16:50 | Electrical - Cable Management | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | 11/02/2020 - email from __ detailing the original problem - linked to observation: "Various types of fixings have been used on various CMS within the Critical Sump room (ETH -5). To date no fixing matrix or bracketry support calcs have been issued to verify the installation against "
| 02SL - Stations (LUL) | Cxxx-NCR-000760 | NCR | Misalignment between the Cxxx TLPP cabinet enclosure and the Cxxx TLPP distribution cabinet |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-01-19 | 2020-01-29 13:22 | 10 | 2020-01-15 16:41 | Electrical - Cable Management | 5000 |  | Workmanship | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Other | Completed |  | On the ETH; Westbound; it was observed that the Cxxx enclosure, around the Cxxx TLPP, was installed such that the doors of the TLPP could not be opened fully.
| 02SL - Stations (LUL) | Cxxx-NCR-000761 | NCR | ETH, Lining Wall 1 and 7 leaks |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-12-25 | 2019-07-17 14:53 | -161 | 2019-03-27 16:58 | Civil - Civil Engineering General | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Leaks have emerged in lining walls 1 and 7 at levels -2 and -3 of the ETH. Annotated plan drawing attached, 'Cxxx-SKC-A-DDA-Cxxx-5213.pdf'. This NCR is linked to closed NCR-297 which has been linked. Photos attached showing scale of issue.
| 02SL - Stations (LUL) | Cxxx-NCR-000762 | NCR | WTH Level -3 AP1 floor slab out of tolerance |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-05-28 | 2019-05-02 10:53 | -26 | 2019-03-28 14:04 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | It has been found that the there is a hump in the structural floor slab of AP1 in GL1 to GL2. This area did not fall under previous NCR-000583 as it covered up to GL2.
| 02SL - Stations (LUL) | Cxxx-NCR-000764 | NCR | Crossraill not being invited to the CTP for the LV Switchboards |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-23 | 2019-04-02 10:48 | -174 | 2019-03-29 09:55 | Electrical - LV Equipment | 0 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Crossrail were not invited to witness item 2.3 from the LV Switchboard CTP. This NCR is required to sign of the PCC.
| 02SL - Stations (LUL) | Cxxx-NCR-000765 | NCR | WTH Front Entrance Gates - __ - Throwout track support brackets |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-05-31 | 2019-04-10 14:38 | -51 | 2019-03-29 17:04 | Architectural - Doors | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __ have installed the throwout track brackets 10mm higher than the design level without seek approval for this change. __' approved design drawings (see Cxxx-SKC-C-LRG-Cxxx-50580) shows these brackets are to be fixed at a RL124.295. The entrance beam stiffener has been installed 10mm higher than design thus clashing with the __ brackets. Rather than seeking approval to change the location of these fixings, __ proceeded to site drill and fix the entrance beam at the higher level (RL124.305).
| 02SL - Stations (LUL) | Cxxx-NCR-000766 | NCR | Corrosion on Spacenet Selectra boxes ETH |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-23 | 2019-05-03 09:58 | -143 | 2019-04-01 15:42 | Electrical - Cable Management | 1000 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Manufacturer welded stainless steel earth stud and used galvanized nuts to secure earthing and used mild steel captive nuts ,which causes electrolytic oxidization.
| 02SL - Stations (LUL) | Cxxx-NCR-000767 | NCR | Damage to inner sheath of SWA cable E026 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-04-16 | 2019-10-28 12:32 | 195 | 2019-04-02 14:57 | Electrical - LV Equipment | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Brown sheath protecting the copper conductor has been damaged when stripping back the inner sheath of SWA Cable E026
| 02SL - Stations (LUL) | Cxxx-NCR-000768 | NCR | Cuts through site made bend ETH -5 Crit Sump Room |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-03-27 | 2021-01-27 14:07 | 306 | 2020-02-13 10:14 | Electrical - General | 0 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Please see photos of cuts (site made bends), 2number.
| 02SL - Stations (LUL) | Cxxx-NCR-000769 | NCR | Spacing between CMS and Fire main does not meet the specification |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-01-24 | 2020-01-27 19:56 | 3 | 2019-12-06 12:35 | Electrical - Cable Management | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Historic NCR - Original details lost - some information has been retrieved from members of the current CS-JV delivery team: The detailed design for the Fire main system does not show sufficient clearance/separation distance between CMS and fire mains.
| 02SL - Stations (LUL) | Cxxx-NCR-000770 | NCR | LVB supply to MCC cable has become rippled due to the bending radius of the CMS. |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-07-13 | 2019-06-13 15:26 | -30 | 2019-06-13 13:21 | Electrical - Cable Management | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | LVB supply to MCC cable has become rippled due to the bending radius of the CMS. Also the sharp edge of the CMS looks to be digging into the cable. This is to be checked for damage by undoing the tie raps and inspecting.
| 02SL - Stations (LUL) | Cxxx-NCR-000772 | NCR | Drawings Cxxx-SKC-S-DWG-Cxxx-50288 and -50153 C01 not in eB |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2019-05-03 | 2019-10-04 16:05 | 154 | 2019-04-05 17:07 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Drawings Cxxx-SKC-S-DWG-Cxxx-50288 C01 and Cxxx-SKC-S-DWG-Cxxx-50153 C01 are not in eB and have been Redlined. This indicates that they were used for Construction.
| 02SL - Stations (LUL) | Cxxx-NCR-000773 | NCR | Damage cable found in ETH Level-5 in top hat. |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-23 | 2019-11-13 17:14 | 51 | 2019-04-08 11:02 | Electrical - Cable Management | 2000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Damage Brown single Cable found on ETH -5 on the a top hat in the circulation Area 6/73 in front of lobby 6/104.
| 02SL - Stations (LUL) | Cxxx-NCR-000774 | NCR | WTH-AP1 Link Tunnel ,unuthorized modification to galvanized steel work for DAL Lighting |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-05-08 | 2019-06-12 15:34 | 35 | 2019-04-08 09:46 | Architectural - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The Subcontractor was observed site modifying galvanised steelwork for the DAL lighting using a magdrill to introduce new hold down bolts to achieve the correct level. The new detail and procedure has not been approved by the Contractor
| 02SL - Stations (LUL) | Cxxx-NCR-000775 | NCR | WTH Level -3 AP1 Link Tunnel Smoke Barrier Modification Prior to Accepted Detail |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-06-08 | 2019-04-10 15:02 | -59 | 2019-04-08 12:03 | Archaeology - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | During a site walk it was identified that a number of smoke barriers have been modified to avoid a clash with the DAL light steel support prior to being accepted by , see attached markup for location reference. The detail used was an extract from the platform design detail (Cxxx-SKC-A-DWG-Cxxx-51112) however not accepted for AP1.
| 02SL - Stations (LUL) | Cxxx-NCR-000776 | NCR | WTH - Vent Shaft -CON-121 Proposal Finish, Not Achievable . |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-05-08 | 2019-05-08 07:58 | 0 | 2019-04-08 14:27 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | WTH Vent shaft constructed via slipform ,therefore unable to meet required CON-121 Plain In situ Concrete finish JE20 .1208 reference:Plain smooth finish Cxxx-__-A-RSP-Cxxx-50003 Rev 4.0
| 02SL - Stations (LUL) | Cxxx-NCR-000777 | NCR | Damage valves on the Falling fire main |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-23 | 2019-09-10 09:45 | -13 | 2019-04-08 14:55 | Fire - Fire Systems & General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Permanent valves on the ETH Station Fire Main have been damaged by concrete slurry.The valves need to repaired or replaced prior to pressure testing can commence.
| 02SL - Stations (LUL) | Cxxx-NCR-000778 | NCR | ETH L-5 Room 6/413 South Door Frame Render Damage |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-06-10 | 2019-05-21 15:23 | -20 | 2019-04-10 08:11 | Architectural - Doors | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | South side of the door frame was damaged by other trades despite signage in place. The rendered panel is cracked and the beading on the corner is bent out of shape.
| 02SL - Stations (LUL) | Cxxx-NCR-000779 | NCR | ETH L0 1/406 Store Room Render Damage |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-05-17 | 2019-05-21 15:24 | 4 | 2019-04-10 08:43 | Architectural - General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Personnel Error - Not Defined | Completed |  | The render on the south elevation near the builders-work opening was damaged, it is unclear how the damage occurred. The render will need to repaired and tied in with the surrounding render.
| 02SL - Stations (LUL) | Cxxx-NCR-000780 | NCR | More civil drawings used for construction not Code 1 on eB |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2019-06-20 | 2019-10-24 13:30 | 126 | 2019-04-10 09:58 | Civil - Civil Engineering General | 0 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | On review of revision 1 of ITP Record Pack Cxxx-SKC-C-LRC-Cxxx-50122 Cxxx - Record Pack - ETH L0 – L+1 Internal Walls and L+0.5 Slab RC Works – Section 2 it was found that some drawings noted as used for Construction were not on eB. I asked for a NCR to be raised on this issue but this was not actioned. On review of revision 2 of the ITP Record Pack the following issues remain: 1. Drawing Cxxx-SKC-S-DWG-Cxxx-50162 C08 is now on eB but is Code 2. See email attached 'RE NEW NCR NEEDED.msg' and comments 10 and 43 in Cxxx-SKC-C-XCS-Cxxx-50526 linked to this NCR. 2. Drawing Cxxx-SKC-S-DWG-Cxxx-50163 C08 is now on eB but is Code 2. See email attached 'RE NEW NCR NEEDED.msg' and comments 23 and 45 in Cxxx-SKC-C-XCS-Cxxx-50526 linked to this NCR. 3. Drawing Cxxx-SKC-S-DWG-Cxxx-50863 C03 is not in eB. See email attached 'RE NEW NCR NEEDED.msg' and comment 49 in Cxxx-SKC-C-XCS-Cxxx-50526 linked to this NCR. Other drawings identified as not being on eB code 1 include: 4. Drawing Cxxx-SKC-S-DWG-Cxxx-50167 C04 version redlined. This version is code 2 in eB. This should not have been used for construction. Relevant sub-cert Cxxx-SKC-C-CER-Cxxx-50497 and redline pack Cxxx-SKC-C-LRG-Cxxx-50689 Rev 37 linked to this NCR. 5. Drawing Cxxx-SKC-S-DWG-Cxxx-50793 C03 version redlined. This version is not in eB. This should be in eB Code 1 and listed in the sub-cert. Relevant sub-cert Cxxx-SKC-C-CER-Cxxx-50497 and redline pack Cxxx-SKC-C-LRG-Cxxx-50689 Rev 37 linked to this NCR. 6. Drawing Cxxx-SKC-S-DWG-Cxxx-50555 C01 is on eB however has not been sent to CRL for review. Redlines have been provided to CRL for approval. 7. Drawing Cxxx-SKC-S-DWG-Cxxx-50553 C01 is on eB however has not been sent to CRL for review. Redlines have been provided to CRL for approval. 8. Drawing Cxxx-SKC-S-DWG-Cxxx-50281 C05 is on eB but not code 1.
| 02SL - Stations (LUL) | Cxxx-NCR-000781 | NCR | ETH - Escape Staircase Exposed Reinforcement on L-0.5 and L-1 Pre-Pour Missing |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-05-17 | 2019-05-17 16:00 | 0 | 2019-04-10 15:15 | Civil - Civil Engineering General | 0 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other management problem | Completed |  | While closing Cxxx-NCR-000446 for ETH - Escape Staircase Exposed Reinforcement on L-0.5 and L-1 it was noted that the pre-pour inspection sheet was missing.
| 02SL - Stations (LUL) | Cxxx-NCR-000782 | NCR | AP1 Overbridge blockwork damage |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2019-06-07 | 2019-06-07 07:13 | 0 | 2019-04-11 11:11 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | An inspection of the AP1 overbridge area was carried out on 05/04/19 to inspect some blockwork damage. This was sustained when __ broke out some concrete upstand areas to make way for cladding support column baseplates. Here is a summary of the findings: 1. 12 areas broken out 2. 1 area had missing blockwork mortar 3. 1 area had damaged blockwork mortar 4. 10 areas sustained light damage to the blockwork surfaces only, (more pics available upon request) 5. 2xblocks were a bit loose. These blocks did not fall within the areas that had been broken out. So the balance of probability would indicate this is not due to /__ works. 6. The joints at the top of the circular areas were not fully sealed. This was due to shrinkage and/or movement and is historic. So this is not due to /__ works. Points 1 – 4 are down to /__ works. Points 5 – 6 were not down to /__ works. During discussion with LU’s representative on site was agreed that the following remedial works approach would probably be acceptable: 1. Fill the missing and damaged blockwork mortar with new, strong semi-dry blockwork mortar. Not a grout – we do not want to risk tipping cementitious material over a live railway line. 2. Paint the blocks that had sustained light damage with a compound to seal them/retain their durability, (not certain what’s suitable, consider Flexcrete or __*) 3. Fit the cladding support columns and re-concrete the broken out concrete upstand areas. *Flexcrete Cxxx-SKC-A-LRC-Cxxx-50260 __ Cxxx-SKC-O4-QSV-Cxxx-50062
| 02SL - Stations (LUL) | Cxxx-NCR-000783 | NCR | P&T Use of non-compliant gasket behind all GFRC panels on L-5 AP1, ES1 & ES2 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-05-31 | 2019-09-13 13:12 | 105 | 2019-04-16 13:51 | Architectural - General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | The original gasket proposed for the GFRC panels at L-5 AP1, ES1 & ES2 was approved Code 1. This was however later rejected due to the appearance of the rebate in the panel. Following this, another type of gasket was proposed which did not require a rebate in the panel. Following installation of the GFRC panels with this gasket it was identified that the gasket was non-compliant.
| 02SL - Stations (LUL) | Cxxx-NCR-000784 | NCR | ITP has no allowances for the installation and assurance of the ATSs for the PES doors |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-04-30 | 2019-04-29 14:29 | -1 | 2019-04-17 07:02 | Electrical - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | __ current ITP has no allowances for the installation and assurance of the ATSs.
| 02SL - Stations (LUL) | Cxxx-NCR-000785 | NCR | __ CTP for testing of Sub-main cables to be updated |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-05-17 | 2019-05-07 08:37 | -10 | 2019-04-17 14:50 | Electrical - General | 0 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Verification Problems - Not Defined | Completed |  | __ CTP for testing of Sub-main cables do not allow for from evidence of compliance to be achieved by calculation.
| 02SL - Stations (LUL) | Cxxx-NCR-000786 | NCR | ETH Busbar Test Results |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-05-17 | 2019-10-30 22:41 | 166 | 2019-04-17 15:16 | Electrical - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | The test sheet within the Assurance Documentation issued for the testing of the Busbar is not the same as the record sheet detailed within CTP Cxxx-SKC-E-STP-Cxxx-50020
| 02SL - Stations (LUL) | Cxxx-NCR-000787 | NCR | ETH L-1, OSD area, on GL F around GL 2 and 3 - Lightwell earthpits |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-05-31 | 2019-05-30 16:11 | -1 | 2019-04-18 07:35 | Civil - Civil Engineering General | 0 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Due to other contractor's programmed works, the lightwell earthing pits have since been completed without completing its own assurance process. handed over 3 No. formed and cast openings containing the earthing rods, due to project constraints had to hand over the level -1 OSD basement to Mace without completing these works. were unable to carry out a post pour inspection as the OSD contractor has now completed the earth pits. A plastic form has been installed and the remaining area around the earth pits have been cast and screeded. It is now no longer possible to visually inspect the original Cxxx concrete structure.
| 02SL - Stations (LUL) | Cxxx-NCR-000788 | NCR | CMS components installed without the appropriate MCR |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-23 | 2019-09-20 18:05 | -3 | 2019-04-23 09:55 | Electrical - Cable Management | 0 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | CSS manufactured support components have been installed, however no MCR has been produced for this manufacturer.
| 02SL - Stations (LUL) | Cxxx-NCR-000789 | NCR | WTH __ Artwork Panel Damage |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-07-12 | 2019-11-15 13:39 | 126 | 2019-04-25 14:30 | Architectural - General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not trained for the work being performed | Completed |  | Please find attached to this NCR a marked up drawing, as well as the photos to match, aiding a brief description of each below: 9F – During an inspection with CRL and DA (artist) on the 19.03, panel 9F was found damaged post installation – no photos taken before installed. Replaced with 3H 5H – During an inspection with CRL on 20.03, panel 5H was found damaged post installation – no photos taken before installed. Replaced with 4D. 4D Trial – As 4D were going to take to long to have re-polished, we replaced 4D with a trial panel that’s the exact same (top of 4).
| 02SL - Stations (LUL) | Cxxx-NCR-000790 | NCR | ETH L-0 Slab GL B-D / 1-3 slab and L-0 cantilever slab post pour inspections not carried out prior to screeding |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-07-05 | 2019-09-16 16:17 | 73 | 2019-04-30 12:47 | Civil - Civil Engineering General | 0 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Post pour inspection for ETH L-0 slabs and soffit of the L-0 cantilever slab was not carried out/signed off prior to screeding (as per requirement of ITP 50001), the screed work is now complete. NCR related to Cxxx-PWK-00340
| 02SL - Stations (LUL) | Cxxx-NCR-000791 | NCR | WTH L-1: Ancillary Supply Access Door 2/086 impeded by other services |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-23 | 2020-01-15 16:30 | 114 | 2019-05-01 09:57 | Mechanical - Mechanical Engineering General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Access door impeded by other services (toilet extract) on the ancillary supply ductwork line.
| 02SL - Stations (LUL) | Cxxx-NCR-000792 | NCR | WTH L-1: An access door on the PSE duct from 2/903 into corridor 2/074 is impeded by CMS traywork |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-06-10 | 2019-07-29 08:45 | 49 | 2019-05-01 10:16 | Mechanical - Mechanical Engineering General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | An access door on the PSE duct from 2/903 into corridor 2/074 is impeded by CMS traywork. See "Cxxx-SKC-M-DDA-Cxxx-11112_2-903 Access Hatch.pdf" for clarity.
| 02SL - Stations (LUL) | Cxxx-NCR-000793 | NCR | WTH L-1: Access to fire damper GE-W-FD121 from 2/074 into 2/675 is impeded by other services |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-06-11 | 2020-01-14 19:09 | 217 | 2019-05-01 10:56 | Mechanical - Mechanical Engineering General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Access to fire damper GE-W-FD121 from 2/074 into 2/675 is impeded by other services (CHW pipework, CMS). Please refer to Cxxx-SKC-M-DDA-Cxxx-11111_NCR2 for location.
| 02SL - Stations (LUL) | Cxxx-NCR-000794 | NCR | WTH L-1 2/074 (outside 2/331) Fire Damper Access (AS-W-FD123) Blocked |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-05-31 | 2021-11-17 09:58 | 901 | 2019-05-01 11:54 | Mechanical - Mechanical Engineering General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | On ancillary supply ductwork route from 2/331 into 2/074, a fire damper at high level (AS-W-FD123) is blocked from access due to lower services (toilet extract and general extract). Please see (Cxxx-SKC-M-DDA-Cxxx-11111_NCR.pdf) for location.
| 02SL - Stations (LUL) | Cxxx-NCR-000795 | NCR | WTH L-1 2/074 (outside riser 2/903): AAR Smoke Damper blocked by __ |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-27 | 2019-12-27 12:17 | 91 | 2019-05-01 12:17 | Mechanical - Mechanical Engineering General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | CMS is blocking access to the actuator on AAR-W-SD007, this needs to be amended to allow access and maintenance. Please refer to "Cxxx-SKC-M-DDA-Cxxx-11112_NCR.pdf" for location details.
| 02SL - Stations (LUL) | Cxxx-NCR-000796 | NCR | WTH Failed torque test: L+3 Large VS Doors - W-D-791-D01/02 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-05-31 | 2019-07-22 07:05 | 52 | 2019-05-01 12:51 | Architectural - General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | 1no. fixing out of 48no. fixings has failed to meet the torqued to 45 Nm during installation achieving only 20 Nm.
| 02SL - Stations (LUL) | Cxxx-NCR-000797 | NCR | Lack of Access to Fire Damper Actuators ETH -5 (6/713,6/778,6/687) |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-06-17 | 2021-03-05 16:23 | 627 | 2019-05-01 14:35 | Mechanical - Mechanical Engineering General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Cxxx-NCR-000522 was incorrectly closed. Various other M&E services have been installed in the ETH Level -5 Lobby which are obstructing the access to the following dampers: GE-E-FD002 GE-E-FD004 AS-E-FD003 GE-E-FD005
| 02SL - Stations (LUL) | Cxxx-NCR-000798 | NCR | Critical sump roo ETH -5 cable tray spare capacity |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-12-12 | 2019-12-18 19:15 | 6 | 2019-05-08 12:31 | Electrical - Cable Management | 0 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | No spare capacity provided on LVA, LVB or UPS trays.
| 02SL - Stations (LUL) | Cxxx-NCR-000800 | NCR | ETH, Lvl 0, Structural Opening E-01-75-D01 |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2019-06-30 | 2019-08-09 09:45 | 40 | 2019-05-08 14:40 | Structural Engineering - Concrete Member | 3000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | It was agreed in Cxxx-RFI-004063 that the opening to IW77 adjacent to GL.C at level 0 in the ETH could be enlarged by 169mm's. However this agreement was not instructed so the Works Information was not updated. The Contractor therefore continued to construct this opening inline with latest Works Information drawing Cxxx-__-S-DDL-Cxxx-52104 P13.
| 02SL - Stations (LUL) | Cxxx-NCR-000801 | NCR | WTH MCC to FOSC CMS routes |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-23 | 2019-05-09 11:06 | -137 | 2019-05-09 07:50 | Electrical - Cable Management | 2000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The CMS route designed for the MCC to FOSC route in support of Cxxx does not achieve the 25% spare capacity with the cable specified by Cxxx.
| 02SL - Stations (LUL) | Cxxx-NCR-000803 | NCR | ETH L-5 Slab defects in AP3 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-06-08 | 2020-01-30 10:55 | 236 | 2019-05-09 10:50 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | L-5 Slab Service trench - During a post pour inspection, the following defects were identified: 1. MH199 slab break out was not controlled properly, this caused areas of uneven breakouts, protruding bars, possible damage to the hydroduct and poor slab finish requirements. 2. Within the trench, the hydroduct was applied as required. However, the tape de-laminated and caused the surrounding concrete to spall and exposed the tape. This is issued is located near a construction joint where the concrete was prepared prior to pouring cause the concrete to spall off.
| 02SL - Stations (LUL) | Cxxx-NCR-000804 | NCR | ETH L -4 removal and reinstatement of services |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-23 | 2019-12-03 15:55 | 71 | 2019-05-10 14:42 | Electrical - Cable Management | 3000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | The secondary containment requirements for the fan installation was issued to __, -GC-049726, and was subsequently approved , __1-GC-008618. Thereafter the issue of the fan replacement came to the for and as a result the agreed CMS had be removed along with the cabling and rerouted to avoid the fan removal equipment location for the MARS
| 02SL - Stations (LUL) | Cxxx-NCR-000805 | NCR | Procedural NCR re: RFI-5095 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-06-08 | 2020-12-02 09:34 | 543 | 2019-05-09 13:58 | Structural Engineering - Structural Engineering - General | 0 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | There are several issues connecting issues associated with this NCR. First, for the __ detailed in RFI-5095, MH215A and B, more rebar was cut than was permitted in Cxxx's RFI response. Level -1.5 approx 8x bars in bottom slab and 6x in top. Level -2 approx. 4x bars in bottom slab and 2xbars in top. Secondly, RFI-3981 requests an additional 3 cores adjacent to the scope of RFI-5095. The two RFIs were raised separately and apparently in isolation, therefore not giving Cxxx an opportunity to assess the structure with all the required openings considered.
| 02SL - Stations (LUL) | Cxxx-NCR-000806 | NCR | ETH Procedure for close out of NCR-703 not followed |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-06-07 | 2020-04-22 14:26 | 320 | 2019-05-09 13:52 | Civil - Civil Engineering General | 0 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | There have been procedural non-conformances in 3 instances regarding the close out of NCR-703. 1. NCR-703, Post core inspection, ETH, Lvl 0, Lift 6 – - Checksheet for pre-core works not complete - NCR advice not followed and alternative core works carried out, (2x52mm diameter cores instead of 1x152mm diameter core) - The 2x32mm diameter cores are very close together. Too close for horizontal rebar to pass between the cores and maintain any type of cover - Unable to confirm if the 2x32mm diameter cores cut rebar as the internal surfaces of the core have now been painted covering the core surfaces 2. NCR-703, Post remedial works inspection, WTH, Lvl-1, Lift 7 – - Checksheet for pre-core works not complete - NCR advice not followed. Overbreak and recasting of concrete not carried out 3. NCR-703, Post remedial works inspection, WTH, Lvl-5, Lift 8 – - Checksheet for pre-core works not complete - NCR advice not followed. Overbreak and recasting of concrete not carried out
| 02SL - Stations (LUL) | Cxxx-NCR-000807 | NCR | OSD installation in Eastern Ticket Hall - Wind post into the Cross Rail coffer soffit slab. |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2019-05-23 | 2019-07-02 17:18 | 40 | 2019-05-09 13:49 | Civil - Civil Engineering General | 0 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Following our previous conversations we (Mace) are required to raise an NCRI to cover works we have undertaken without Cross rail approval. This being – the fixing of a single block work wind post into the Cross Rail coffer soffit slab. Please see attached two photos showing the works in question. Once the block work wall has been complete - the fixing points and all markings will be covered. I also attach a copy of the ground floor plan – with the location of the wind post in question highlighted.(WP4). This drawing also shows the head fixing – M12 Resin Anchors. I also attach the calculations for the wall panel and wind post design – for your information. ***************UPDATE 10/06/19********************* 1 - Location can be found in attachment 'Ground floor wind posts.pdf ' 2 - The centre of the bolt hole is 60mm's away from the nearest face of the concrete 3 - For loadings: The total unfactored shear load at the head support of windpost 186 is 2.0 kN. If there are two number anchors/bolts then each must resist 1.0 kN of unfactored shear. There is no tension force on the anchors/bolts. Pages 11 – 16 of the calculations (33478-3700-OSD-X-CA-0002-rev C3) sets out the windpost design for the worst case location at this level
| 02SL - Stations (LUL) | Cxxx-NCR-000809 | NCR | ETH:level -1 Riser 931 the installed Granting and handrails are 20mm low |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-06-09 | 2019-05-31 08:42 | -9 | 2019-05-10 08:09 | Architectural - General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | The floor granting and handrails at ETH Level -1 Riser 931 have been installed 20mm too low.
| 02SL - Stations (LUL) | Cxxx-NCR-000810 | NCR | P&T L-3, AP1 Overbridge progressed with works without relevant approvals |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-05-24 | 2019-05-30 16:35 | 6 | 2019-05-10 12:44 | Civil - Civil Engineering General | 0 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | A procedural failure resulted in subcontractor proceeding with works in advance of TB approval.
| 02SL - Stations (LUL) | Cxxx-NCR-000811 | NCR | TWUL Public Sewer Connection (WTH - Weighhouse St - Gully PG01 Connection) |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-06-30 | 2019-07-04 13:01 | 4 | 2019-05-10 13:24 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | When making the drainage connection from PG01 to the existing brickwork sewer the construction detail Cxxx-SKC-D-DDD-Cxxx-00300 D.14 was not followed. The connection was not made using a flexible saddle connection, it was made by coring into the sewer, inserting a stub pipe and making good around this.
| 02SL - Stations (LUL) | Cxxx-NCR-000812 | NCR | __ Primary Injection Broken Calibration Seal |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-23 | 2019-05-15 14:04 | -131 | 2019-05-10 14:55 | Electrical - General | 0 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Inadequate/insufficient tooling. | Completed |  | As part of the power on activities a primary injection test is to be carried out on the LV Panel. Crossrail representative Steve Argrave noticed that the 'Calibration is void if seal broken' stickers had actually been broken and therefore refused to accept the test results.
| 02SL - Stations (LUL) | Cxxx-NCR-000813 | NCR | MEP Material Proposal Schedule (MPS) does not reflect Fire Systems materials proposed and accepted |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2019-08-30 | 2019-11-11 16:16 | 73 | 2019-05-13 08:34 | Fire - Fire Systems & General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | On review of MEP Material Proposal Schedule Cxxx-SKC-M-TSC-Cxxx-50005 (Rev 3) it was found that proposed/accepted materials for Fire Suppression Systems have not been included.
| 02SL - Stations (LUL) | Cxxx-NCR-000814 | NCR | WTH area4 external work Davis St ,Unapproved recycled Type1 was used for backfilling the grout shaft |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-06-12 | 2019-07-04 17:06 | 22 | 2019-05-13 13:30 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Unapproved recycled Type1 was used for backfilling the grout shaft at WTH Davies street area4. These works are the pre requisit to installtion of sub base and formation of road surface on Davies street
| 02SL - Stations (LUL) | Cxxx-NCR-000816 | NCR | ETH - Drawing Cxxx-SKC-S-DWG-Cxxx-50569 not issued for construction on eB |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-06-13 | 2019-09-13 15:11 | 92 | 2019-05-14 15:50 | Civil - Civil Engineering General | 0 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | The ETH L-5 VD4 slab infill was constructed to drawing Cxxx-SKC-S-DWG-Cxxx-50569 rev P01. The status of this drawing was "Code 2 - Not Accepted. Revise and resubmit. Work may proceed subject to incorporation of changes indicated". The drawing hasn't been resubmitted yet, nor being issued as C01 and achieved Code 1 status.
| 02SL - Stations (LUL) | Cxxx-NCR-000817 | NCR | ETH Level -5 Slab Post Pour Documentation |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-06-16 | 2020-01-28 14:14 | 226 | 2019-05-17 07:16 | Civil - Civil Engineering General | 0 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Further to Punchworks Cxxx-PWK-00117, Cxxx-PWK-00118 and Cxxx-PWK-00217, post pour snag repair inspections and/or post pour inspections have not been completed prior to proceeding with follow on construction activities. Therefore, it is no longer possible to visually inspect these punchwork locations.
| 02SL - Stations (LUL) | Cxxx-NCR-000818 | NCR | Procurement of __ ATS Unit Prior to Approved Design |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-27 | 2019-10-14 18:36 | 17 | 2019-05-17 08:48 | Electrical - Switchgear | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | procured the sitewide ATS units prior to obtaining a design approval. Specific issues relate to ATS derating factor due to the utilisation category. JY71.1201 General q) To complete the detailed design, the Contractor will liaise and interface with other project interface parties to finalise equipment ratings. JY71.1311 Automatic Transfer Switches (ATS) Automatic Changeover Switches (ATS) shall conform to BS EN 60439-6-1, JV20.1307 and to the following requirements: i) Rating Amperes as indicated on the Design Drawings
| 02SL - Stations (LUL) | Cxxx-NCR-000819 | NCR | Installation of Fire Suppression System has commenced without an accepted Inspection and test Plan (ITP) in place |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2019-06-18 | 2019-12-27 11:47 | 192 | 2019-05-21 08:26 | Fire - Suppression | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Not Defined | Completed |  | During a planned Fire Systems Quality surveillance, it was witnessed that the Watermist Fire System had commenced installation. On Request the Contractor was unable to submit an accepted Inspection and Test Plan (ITP)
| 02SL - Stations (LUL) | Cxxx-NCR-000820 | NCR | Installation of Water Storage Tank for the Watermist Suppression System commenced without an accepted Materials Compliance Record (MCR) in place. |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2019-11-15 | 2019-11-18 14:54 | 3 | 2019-05-21 09:08 | Fire - Suppression | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | During a Fire Systems Quality Surveillance it was witnessed that the Water Storage Tank for the Watermist Fire Suppression System had been installed. On request the Contractor was unable to submit an accepted Material Compliance record (MCR) for the installed Water tank.
| 02SL - Stations (LUL) | Cxxx-NCR-000821 | NCR | Watermist Fire Suppression System Installation commenced without an accepted F2 design in place |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2019-06-18 | 2021-02-04 12:38 | 597 | 2019-05-21 09:32 | Fire - Suppression | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | During a planned Fire Systems Quality Surveillance, it was found that the Contractor has commenced the installation of the Watermist Suppression System without F2 design acceptance.
| 02SL - Stations (LUL) | Cxxx-NCR-000822 | NCR | The Contractor was unable to provide deliverable records for the installation of Watermist Fire Suppression System |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2019-11-15 | 2019-11-18 14:57 | 3 | 2019-05-21 09:48 | Fire - Suppression | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | During a Planned Fire Systems Quality Surveillance, the Contractor on request was unable to provide deliverable records for the Watermist Fire Suppression installation.
| 02SL - Stations (LUL) | Cxxx-NCR-000823 | NCR | The 'By Exception Procedure has not been followed correctly. |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2020-01-01 | 2019-12-18 13:25 | -14 | 2019-05-22 08:50 | Fire - Fire Systems & General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | A post surveillance review of submitted ‘By Exception’ submissions for ‘Installation of Fire Alarm System‘ Cxxx-SKC-O-RGN-Cxxx-50276 and ‘Installation of Firemain Pipework and Thrust Brackets’ Cxxx-SKC-O-RGN-Cxxx-50277. Found that NO NCR’s have been raised in line with ‘By Exception Construction Prior to Gate Acceptance for Station, Shafts and Portals’ Procedure CRL1-XRL-O7-GPD-CR001-50023. (Rev 2).
| 02SL - Stations (LUL) | Cxxx-NCR-000824 | NCR | ETH L-3 MH218 __ the correct size opening not casted in to RC Wall |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-07-31 | 2019-11-01 16:23 | 93 | 2019-05-22 10:18 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | MH218 has not been formed as per RFI-3301 A 250mm core hole couldn't be cored due to the spacing between horizontal rebars is only 175mm
| 02SL - Stations (LUL) | Cxxx-NCR-000826 | NCR | Materials installed not on MCR |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2019-12-13 | 2020-02-12 13:20 | 61 | 2019-05-22 11:54 | Electrical - Cable Management | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | The contractor has procured and installed a nylon washer as part of the bracketry installation on the cross passages and AP1 without an MCR or data sheet being in place
| 02SL - Stations (LUL) | Cxxx-NCR-000827 | NCR | WTH L-4.5 Finished Stair Landing Works Incorrectly Painted |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-10-31 | 2021-06-23 15:42 | 601 | 2019-05-23 14:10 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Finished floor works on ESS2 landing between levels -5 and -4 has been painted over. In addition there are screw holes present.
| 02SL - Stations (LUL) | Cxxx-NCR-000828 | NCR | WTH AP1 L-3 Structural opening out of design tolerance |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-06-22 | 2019-10-11 16:02 | 111 | 2019-05-23 14:59 | Civil - Civil Engineering General | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Door W-04-414-D01 is 29mm out of design location. This will impact on the architectural finishes around the door opening.
| 02SL - Stations (LUL) | Cxxx-NCR-000829 | NCR | ETH Missing wall post pour inspection sheets for MPS from L-1 to L-5 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-27 | 2020-01-21 15:32 | 116 | 2019-05-29 10:00 | Civil - Civil Engineering General | 0 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The post pour folder with all the sign off inspection sheets has been misplaced. Also, no evidence of dust seal inspections being carried out.
| 02SL - Stations (LUL) | Cxxx-NCR-000830 | NCR | ETH Mabey Bridge NCR - IFC Drawings not issued on eb |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-06-24 | 2019-11-01 16:37 | 130 | 2019-05-29 11:59 | Civil - Civil Engineering General | 0 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | The drawings for the base plates which are cast in to the ETH precast columns, on Grid Line 4, ref. Cxxx-SKC-S-LRG-Cxxx-50012 (3.0), were not issued as IFC on eb. The drawings were accepted (Code 1) as rev. P0X.
| 02SL - Stations (LUL) | Cxxx-NCR-000831 | NCR | ETH L-5 AP3 Mass fill Post pour missing |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-07-05 | 2020-09-02 15:21 | 425 | 2019-05-29 12:32 | Civil - Civil Engineering General | 0 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | L-5 AP3 Mass Fill was not post poured prior to RC CMS trench slab being poured. This did not provide CRL opportunity to carry out a post pour inspection. Due to the RC CMS trench slab being poured circa 29/07/2017, this has covered the L-5 Mass fill slab surface and prevents access for inspection.
| 02SL - Stations (LUL) | Cxxx-NCR-000832 | NCR | Corroded earth connections ETH |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-23 | 2021-02-11 18:04 | 507 | 2019-05-30 07:37 | Electrical - Earthing & Bonding | 2000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Corroded earth connections at ETH Lightning Protection Earth Pits (Further to Cxxx-NCR-000787)
| 02SL - Stations (LUL) | Cxxx-NCR-000833 | NCR | CRL not invited to ETH dead/live testing |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-23 | 2019-05-31 11:22 | -115 | 2019-05-30 08:07 | Electrical - General | 0 |  | Planning | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | CRL not invited to Dead/Live Testing of Busbar at ETH
| 02SL - Stations (LUL) | Cxxx-NCR-000836 | NCR | WTH L-1 Access to ducts blocked |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-07-31 | 2020-02-21 15:07 | 205 | 2019-06-04 06:32 | Electrical - Cable Management | 3000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | WTH L-1 Access to ducts blocked by other services; cms, bracketry and pipework.
| 02SL - Stations (LUL) | Cxxx-NCR-000838 | NCR | WTH L-5 CMS and supports blocking access to duct hatch |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-12-20 | 2019-11-28 15:08 | -22 | 2019-06-04 08:07 | Electrical - Cable Management | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | WTH L-5 CMS and supports blocking access to duct hatch. MEWP demonstration with CRL showed that the duct hatch could not be accessed.
| 02SL - Stations (LUL) | Cxxx-NCR-000839 | NCR | ETH L-1 Access Doors Blocked by CMS |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-06-28 | 2020-01-21 09:49 | 207 | 2019-06-04 10:30 | Electrical - Cable Management | 1000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | ETH L-1 Access Doors blocked by CMS. IRF 224. NCR to be raised Lobby 2/086 Near LV Switch Room 2/933
| 02SL - Stations (LUL) | Cxxx-NCR-000840 | NCR | WTH L-1 Access to ducts blocked |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-23 | 2021-02-07 10:19 | 503 | 2019-06-26 14:26 | Electrical - Cable Management | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Access to the ductwork and access hatch have been blocked by bracketry and CMS.RFI needed to be raised to redirect the CMS
| 02SL - Stations (LUL) | Cxxx-NCR-000841 | NCR | WTH L-5 Access Door Blocked by Drop rod |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-06-28 | 2020-01-12 21:22 | 198 | 2019-06-04 10:59 | Electrical - Cable Management | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | WTH L-5 Access Door Blocked by light fitting. Sump Room SWR 7/772 CRL-OBS-27868
| 02SL - Stations (LUL) | Cxxx-NCR-000842 | NCR | ETH L-5 Fire Damper access blocked |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-06-28 | 2021-02-17 12:13 | 600 | 2019-06-04 11:12 | Electrical - Earthing & Bonding | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | ETH L-5 Fire Damper access blocked by CMS in Lobby 6/094 GE-E-FD016 and AS-E-FD016
| 02SL - Stations (LUL) | Cxxx-NCR-000843 | NCR | WTH L-5 6/316 Fire Damper Access blocked |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-06-18 | 2020-01-12 19:29 | 208 | 2019-06-04 11:33 | Electrical - Cable Management | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Access to fire damper GE-W-FD016, AS-W-FD009 blocked by CMS
| 02SL - Stations (LUL) | Cxxx-NCR-000844 | NCR | WTH L-4 Sump extact 5/397 fan block by lighting drop rod |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-23 | 2020-01-14 19:56 | 113 | 2019-06-04 11:42 | Electrical - Cable Management | 2000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | WTH L-4 Sump Extract Fan - Lighting Drop rod for lighting blocking access to Fan CRL-OBS-27863
| 02SL - Stations (LUL) | Cxxx-NCR-000845 | NCR | Fire dampers blocked ETH L-4 outside 5/781 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-06-28 | 2020-03-11 16:22 | 257 | 2019-06-04 13:17 | Electrical - Cable Management | 0 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | ETH L-4 Blocked FDs and adjacent access doors. AS-E-FD023 and also GE-E-FD023.
| 02SL - Stations (LUL) | Cxxx-NCR-000846 | NCR | ETH L-4 outside 5/732 Duct access door blocked |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-06-28 | 2021-03-17 10:11 | 628 | 2019-06-04 13:38 | Electrical - Cable Management | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | ETH L- 4 Access doors blocked by CMS in corridor area near to CER room 5_732
| 02SL - Stations (LUL) | Cxxx-NCR-000847 | NCR | Access Duct Door Blocked ETH L-4 5/775 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-06-28 | 2022-01-24 10:13 | 941 | 2019-06-04 13:48 | Electrical - Cable Management | 2000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Access Duct Door Blocked by CMS outside 5/775 ETH L-4
| 02SL - Stations (LUL) | Cxxx-NCR-000848 | NCR | WB Invert (WTH End) fire main coupling clash with CMS |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-23 | 2020-01-29 13:18 | 128 | 2019-06-05 13:45 | Mechanical - Piping | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | WB invert (WTH End) - Station fire main victaulic coupling is in contact with a CMS tee piece. It is a requirement to have a clearence of 150mm between services under JY60.
| 02SL - Stations (LUL) | Cxxx-NCR-000850 | NCR | ETH Channel Installation |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-06-19 | 2019-06-10 10:33 | -9 | 2019-06-05 14:46 | Electrical - Cable Management | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Solid Channel has been installed in various locations which has been drilled to either fix to building fabric or for containment to be fixed to the Channel.
| 02SL - Stations (LUL) | Cxxx-NCR-000852 | NCR | ETH MPS L-4 Slab - missing post pour QA |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-07-06 | 2019-10-29 12:15 | 115 | 2019-06-06 15:29 | Civil - Civil Engineering General | 0 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Following the construction of the level -4 MPS RC slabs, could not carry out the post pour inspections to the slab surfaces as per the ITP (Cxxx-SKC-O4-ITP-Cxxx-50001) due to construction of the subsequent lining walls blocking access to visually inspect the slab. These outstanding records were raised in Cxxx-PWK-00188. have proceeded onto the next phase of construction, screeding over the surface of the slab without undertaking the post-pour inspections.
| 02SL - Stations (LUL) | Cxxx-NCR-000853 | NCR | Non-approved Cores in WTH-0 wall 1/661.S |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-07-10 | 2020-07-21 12:25 | 377 | 2019-06-10 08:19 | Civil - Civil Engineering General | 0 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | 3 small diameter cores (approx. 60mm) have been made through the RC wall, all of which have cut reinforcement. There is not an approved Permit to Core or Cxxx-RFI permitting these cores.
| 02SL - Stations (LUL) | Cxxx-NCR-000854 | NCR | WTH, Existing / Non Identified __'s within 6/087.S (Wall 3-4/A-D) |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-07-10 | 2019-10-04 16:19 | 86 | 2019-06-10 11:49 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | WTH-5 wall 6/087.S (Wall 3-4/A-D) Cxxx-RFI-005316 (EH169) approved a large (450 x 150mm) __, however, it was not noted on the RFI that there was already an existing large opening in the wall. When / CRL attended the pre-core inspection this was identified.
| 02SL - Stations (LUL) | Cxxx-NCR-000855 | NCR | P&T AP1, Level-3, Incorrect manufacturing of GFRC panel cast in hook-in profile GL1-2 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-08-30 | 2019-11-08 12:07 | 70 | 2019-06-11 12:51 | Architectural - General | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the installation of the top row of GFRC panels between L1-L2, it was identified that there is an issue with the joint between the top two panels, please find attached photos and location map Following to an investigation, it was identified that the cast in hook-in profiles where set up incorrectly resulting in the difference. The total number of affected panels is 8No.
| 02SL - Stations (LUL) | Cxxx-NCR-000856 | NCR | ETH LIN403 sub structure - Lift Lobby |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-07-11 | 2019-06-18 14:53 | -23 | 2019-06-11 13:28 | Architectural - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | A wall bracket to support the CLG-721 steel frame clashes with a wall bracket to support the LIN-403 steel frame. Due to the big amount of CMS above it is not possible to replace the LIN-403 wall bracket. Due to design reasons the CLG-721 wall bracket can also not be replaced.
| 02SL - Stations (LUL) | Cxxx-NCR-000857 | NCR | Outstanding floor finish works in ETH local cooling rooms |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-12-31 | 2022-03-02 09:02 | 792 | 2019-06-12 11:08 | Architectural - General | 500 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | In a number of locations within the ETH local cooling rooms, MEP equipment has been permanently placed onto the screed prior to being coated with the design epoxy resin finish.
| 02SL - Stations (LUL) | Cxxx-NCR-000858 | NCR | Missing CCU Inspection sheet - CHW System |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-12-31 | 2019-10-10 10:37 | -82 | 2019-06-12 15:44 | Mechanical - Mechanical Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Inspection points not adequate | Completed |  | Identification of missing check sheet within ITP for associated Plant: Existing ITP: Cxxx-SKC-O4-ITP-Cxxx-50107 Proposal to either review & resubmit ITP or provide standalone ITP to be used in parallel to close the issue out.
| 02SL - Stations (LUL) | Cxxx-NCR-000859 | NCR | ETH L-3 Slab surface NWS infill incomplete post pour |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-07-13 | 2019-06-20 17:24 | -23 | 2019-06-13 15:00 | Civil - Civil Engineering General | 0 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | ETH L-3 Slab surface at NWS infill location has not been post poured since the works have been completed. The L-3 slab soffit has been inspected on 13.06.2019, however, no access is available as works have progressed and screed has been placed above this slab infill. With screed in place, the post pour is no longer possible on the L-3 slab surface.
| 02SL - Stations (LUL) | Cxxx-NCR-000860 | NCR | WTH L-0 damaged lightning protection tape |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-23 | 2020-10-21 15:55 | 394 | 2019-06-17 07:50 | Electrical - Electrical Engineering General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Damage to lightning protection tape on the south elevation shaft WTH Lv-0
| 02SL - Stations (LUL) | Cxxx-NCR-000862 | NCR | WTH Vent Shaft, Level 0 - Exposed Rebar to KD7 internal west elevation |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2019-07-02 | 2019-12-06 13:57 | 157 | 2019-06-18 16:21 | Structural Engineering - Reinforcement | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Exposed rebar has been observed on the internal west elevation of KD7 at level 0 in the WTH vent shaft. See attached pics and location plan.
| 02SL - Stations (LUL) | Cxxx-NCR-000863 | NCR | ETH MPS L-2 IW47, 49, 53 (Lift 2) - Missing Pre-Pour |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-07-19 | 2019-08-02 15:53 | 14 | 2019-06-19 13:16 | Civil - Civil Engineering General | 0 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | It has be found when compiling the Record Pack for the L-2 to L-00 MPS Walls there is no pre-pour sheet for the 2nd lift of IW47, 49, 53.
| 02SL - Stations (LUL) | Cxxx-NCR-000864 | NCR | WTH L-2 Room 3/778 Pipework blocking access hatch |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-23 | 2021-05-05 10:15 | 590 | 2019-06-19 15:26 | Electrical - Cable Management | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Pipework support Bracket is blocking the access hatch of Ductwork
| 02SL - Stations (LUL) | Cxxx-NCR-000865 | NCR | ETH MPS L-3 Slab - missing post pour QA |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-07-21 | 2019-09-06 09:52 | 47 | 2019-06-21 10:10 | Civil - Civil Engineering General | 0 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Following the construction of the level -3 MPS RC slabs, could not carry out the post pour inspections to the slab surfaces as per the ITP (Cxxx-SKC-O4-ITP-Cxxx-50001) due to construction of the subsequent lining walls blocking access to visually inspect the slab. These outstanding records were raised in Cxxx-PWK-00198. have proceeded onto the next phase of construction, screeding over the surface of the slab without undertaking the post-pour inspections.
| 02SL - Stations (LUL) | Cxxx-NCR-000866 | NCR | Missing document deliverables for Comms Cabinets 6733U1 and 6734U1 (WTH & ETH Lvl -4 & -5) |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-12-28 | 2020-09-23 10:58 | 270 | 2019-06-21 13:40 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Submitted IRN's Cxxx-SKC-R3-NOX-Cxxx-50106 and 50107 have missing deliverables for the their respective Site Assurance Files
| 02SL - Stations (LUL) | Cxxx-NCR-000867 | NCR | Manufactured Lid needed on tray Circulation Area 2/75 and Lobby 2/92 for Firestopping detail |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-23 | 2019-12-16 19:04 | 84 | 2019-06-25 08:38 | Electrical - Cable Management | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Lack of assessment for the requirements to provide firestopping systems through penetrations to maintain fire compartmentation as indicated in the Fire Strategy. The tray work going through the penetration in Circulation Area 2/75 and Lobby 2/92 have not been fitted with manufactured lid and fire stopping detail cannot be achieved.
| 02SL - Stations (LUL) | Cxxx-NCR-000868 | NCR | ETH MPS Level-1 and Level-2 Slab - missing post pour QA |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-07-25 | 2019-11-18 10:08 | 116 | 2019-06-25 14:12 | Civil - Civil Engineering General | 0 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Following the construction of the level -2 and -1 MPS RC slabs, could not carry out the post pour inspections to the slab surfaces as per the ITP (Cxxx-SKC-O4-ITP-Cxxx-50001) due to construction of the subsequent lining walls blocking access to visually inspect the slab. These outstanding records were raised in Cxxx-PWK-00249, Cxxx-PWK-00276. have proceeded onto the next phase of construction, screeding over the surface of the slab without undertaking the post-pour inspections.
| 02SL - Stations (LUL) | Cxxx-NCR-000869 | NCR | ETH L-3 Tunnel Vent 4/394.W towards Forced Ventilation 4/800 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-07-26 | 2019-08-14 16:45 | 19 | 2019-06-26 12:28 | Civil - Civil Engineering General | 100 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | x3 small diameter 45mm cores over the pressure sealed door have been made through the RC wall, In ETH L-3 tunnel Vent 4/394.W (EH186) in wall between GL’s 3-4 along GL-C. one of the 3 cores (bottom core) have cut reinforcement. This is not approved as per the Cxxx-RFI-005327.
| 02SL - Stations (LUL) | Cxxx-NCR-000870 | NCR | Cut more bars than allowed in Cxxx-RFI-005319 response |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2019-07-10 | 2019-09-20 13:57 | 72 | 2019-06-26 16:19 | Structural Engineering - Concrete Member | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | 1. EH132 Builderswork Void, (covered under Cxxx-RFI-005319): __ carried out a joint pre-core inspection for Cxxx-RFI-005319 with __. __ noticed the setting out of the cores were inside the remedial works area instructed under Cxxx-PMI-02021. __ therefore requested the setting out of these cores be moved 500mm's south to avoid the additional lapped rebar installed as instructed under Cxxx-PMI-02021. This advice was not followed. As a result the Contractor cored through rebar not in alignment with Cxxx's response to Cxxx-RFI-005319 - 'It will be ACCEPTABLE to core ALL of the requested holes PROVIDING they are suitably positioned to AVOID CUTTING of ANY RE-BAR - which might result in the holes needing to be slightly repositioned if the dimensioned locations clash with rebar...Where reinforcement laps occur it is definitely likely that there will be insufficient space for coring holes while avoiding cutting of rebar. It will be ACCEPTABLE to cut HORIZONTAL BARS. However this should be kept to a minimum. If there is a position where no horizontal-bar-cutting would occur then the hole should be cored there. Where a cored hole might be dimensioned in a position that it cuts through 2no parallel lapping bars then it shall be moved upwards or downwards so that only one bar is cut...' The Contractor have cut through 2xhorizontal lapped bars in each of the 2xEH132 cores. 2. EH133 Builderswork Void, (covered under Cxxx-RFI-005319): A joint post pour inspection of these builderswork voids was not possible as the Contractor had already installed services in the voids. 3. EH134 Builderswork Void, (covered under Cxxx-RFI-005319): A joint post pour inspection for this builderswork void was not possible as the Contractor did not provide access. 4. All of the above - Metal circular sockets were left insitu from the core drilling rig. The Contractor are to propose remedial actions for each of the points raised above.
| 02SL - Stations (LUL) | Cxxx-NCR-000871 | NCR | ETH Lvl 0 cores through 2 adjacent locations |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-20 | 2019-10-08 12:15 | 18 | 2019-07-11 13:13 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 2no. 320mm DIA cores have been identified within the ETH-0 slab (Annotated Cxxx-SKC-S-DWG-Cxxx-50011 rX01). Both cores have struck numerous reinforcement bars of the top and bottom layers as per NCR-871 Rebar As-built r02. No clear RFI evidence has been found to support penetration coring. No evidence of pre or post core inspection has been found, nor any remedial works carried out to validate the works. 2no. 210 DIA broken out circular openings at the location were approved within Cxxx-RFI-003408 (refer to SKB_ETH_00_11000_00 - Opening A2 and F1 (fire inlets) - Option 3.pdf). NOTE: This RFI addresses 3no cores however only two have been cored, with no evidence of being broken out. The coring caveats within RFI-003408 were “in line with the response to the related NCR 358”. The Actual Answer (Cxxx) within Cxxx-NCR-000358 states : “Although FCD title includes Level 0, no details have been submitted for Level 0 in this query.” Corrective action then states “Level 0 will be covered under referenced Cxxx-NCR-000447”. Cxxx-NCR-000447 (ETH L0 - Sleeves for Fire Fighting Lift Drainage Channel) is located within FF Lobby 1/084. Despite providing a workable proposal/completion, NCR-000447 is not specific to the current location. Therefor a new Cxxx assessment and solution is required for to undertake remedial works.
| 02SL - Stations (LUL) | Cxxx-NCR-000872 | NCR | WTH Lvl 0 central core, north lift wall, internal face - old builderswork void not correctly cast |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-08-31 | 2019-12-13 17:34 | 104 | 2019-07-02 15:23 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During inspection of W-W-14 south face with BW team & CRL (__) inside lift 7 it was identified an RC in-fill carried out under Cxxx-NCR-599 was not completely infilled with concrete at the top.
| 02SL - Stations (LUL) | Cxxx-NCR-000873 | NCR | ETH Level -1, IW65 Builders Holes Voids |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-08-07 | 2020-05-22 12:27 | 289 | 2019-07-08 14:56 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | X11 __ ETH L -1 room 2/173. W in Wall IW65 X11 openings has been cored as agreed between __ and Cxxx as per Cxxx-RFI-004467/__1-SUBRFI-002231 which it supersede Cxxx-RFI-004330. However, some of the cores have cut more than the allowable reinforcement. This is not approved as per the Cxxx-RFI-004467 parameters.
| 02SL - Stations (LUL) | Cxxx-NCR-000874 | NCR | Top hats in Switchroom 3(between 3/676 and 3/684) cannot be firestopped. |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-02-21 | 2021-03-11 10:46 | 384 | 2019-06-28 09:58 | Electrical - Cable Management | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | There are two top hat Switch room 3 (between 3/676 and 3/684) that cant be fire stopped. an RFI needs to be raised to __
| 02SL - Stations (LUL) | Cxxx-NCR-000875 | NCR | LV ROOM BATTERY CHARGER ISOLATORS |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2019-08-16 | 2019-09-03 14:33 | 18 | 2019-06-28 11:37 | Electrical - Switchgear | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The 25Amp __ isolators installed for the battery chargers have a stated maximum cable conductor size of 4mm, the cables installed are 6mm and therefore do not comply to .
| 02SL - Stations (LUL) | Cxxx-NCR-000876 | NCR | Tx Braids Installed without Approved MCR |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2019-07-12 | 2020-01-21 10:06 | 193 | 2019-06-28 13:43 | Electrical - Power Distribution | 0 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | The Contractor has installed the braided flexible links from the busbar to the transformer without an approved MCR or design. They have also been heat shrink which will also require an approved MCR and detailed in the design.
| 02SL - Stations (LUL) | Cxxx-NCR-000877 | NCR | AP1, Level -3, P&T, RC wall section to be trimmed to allow GFRC substructure install |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-08-30 | 2019-09-06 11:47 | 7 | 2019-07-01 08:21 | Civil - Civil Engineering General | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The RC wall was poured out of tolerance in localised area within AP1 interchange. There is now a clash with the cladding install. Therefore, would like to locally scabble the RC wall to allow the cladding to be installed as per minimal design build up required.
| 02SL - Stations (LUL) | Cxxx-NCR-000878 | NCR | ETH L-2, __ (EH132) in E.B.D.R 3/935.E cores damaged horizontal reinforcement |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-08-02 | 2019-08-19 16:27 | 17 | 2019-07-03 12:48 | Civil - Civil Engineering General | 0 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Management Problem - Other | Completed |  | During coring 2 x lapped bars in both cores (EH132 2X45mm) were cut contrary to the requirement of RFI-005319 During pre-core inspection CRL had instructed that the cores be moved away form the heavily reinforced area of the wall (See attached pre-core check sheet) In accordance to MEP electrical Regulations the cores could not have been moved any further than 500mm south of door-way. Moving the cores up or down would have not been beneficial as the wall reinforcement in this section is lapped from top to bottom.
| 02SL - Stations (LUL) | Cxxx-NCR-000879 | NCR | ETH L-5 Drainage Pipe displaced joint |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-08-04 | 2019-08-29 13:59 | 25 | 2019-07-05 10:47 | Civil - Civil Engineering General | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During installation of the drainage runs between DP.16 and joint at 2.4m south of GL#2. The joint at this location may have not been installed and aligned correctly or the during installation of the drainage pipe joint collar, the pipes may have moved during tightening of the collar to create a water tight seal. See survey photos attached.
| 02SL - Stations (LUL) | Cxxx-NCR-000880 | NCR | WTH -3 CMS Design not Co-ordinated with Steel Work |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2019-07-22 | 2019-11-22 14:27 | 123 | 2019-07-08 10:18 | Electrical - Cable Management | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | During an IRF for CMS at WTH -3 Zone 3, it was found that the PMR tray has not been installed as per the design (see attached mark up). A single piece of unistrut has been installed instead (see attached photo). This was not marked up on the redline drawing. The reason given for changing from tray to unistrut was that there is no space to install all the CMS as per the design as it will clash with the steel work. Location: WTH -3 4/071
| 02SL - Stations (LUL) | Cxxx-NCR-000881 | NCR | Below Strength Concrete Cubes at WTH Vent Shaft L0 500mm Upstand |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-08-09 | 2019-09-13 15:52 | 35 | 2019-07-10 13:03 | Civil - Civil Engineering General | 500 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Concrete cube test results for concrete used in the 500mm upstand at WTH Vent Shaft L0 are found to be below strength.
| 02SL - Stations (LUL) | Cxxx-NCR-000882 | NCR | WTH-2: AS-W-FD128 Blocked Access |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-23 | 2021-02-04 12:45 | 500 | 2019-07-10 15:36 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Planning | Reject | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Access to AS-W-FD128 has access impeded by electrical ATS boards. Please see "Cxxx-SKC-M-DDA-Cxxx-11124_NCR.pdf" for clarity on location
| 02SL - Stations (LUL) | Cxxx-NCR-000883 | NCR | INCORRECT LIDS USED FOR FIRESTOPPING TO CABLE MANAGEMENT |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2019-12-20 | 2020-01-17 20:13 | 28 | 2019-12-06 13:06 | Electrical - Cable Management | 0 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Firestopping of submain cables emanating from LV switchrooms in ETH has not been completed as per specification
| 02SL - Stations (LUL) | Cxxx-NCR-000884 | NCR | AP1, Level -3, P&T, tiling install to incorrect setout GL12-13 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-08-10 | 2019-09-05 15:11 | 26 | 2019-07-11 14:51 | Architectural - Flooring | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The curved section between GL12 - GL13 has not been installed to the correct setout points, causing the curve radius to be slightly skewed through this section in AP1
| 02SL - Stations (LUL) | Cxxx-NCR-000885 | NCR | AP2/3 Level -5, P&T, Blockwork chasing for structural openings in AP2/3 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-08-11 | 2020-02-20 16:58 | 193 | 2019-07-12 09:15 | Architectural - Brickworks/Blockworks | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Structural openings within AP2 and AP3 are built outside the design tolerances and therefore remedial works are required to ensure the doors can be installed as per design locations.
| 02SL - Stations (LUL) | Cxxx-NCR-000886 | NCR | WTH L+1 Slab - Incorrect architectural concrete finish on slab surface |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-08-11 | 2020-10-22 10:49 | 438 | 2019-07-12 09:46 | Architectural - General | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Incorrect concrete finish to slab has been applied. Drawing Cxxx-SKC-A-DDE-Cxxx-27090 C02 shows that the area inspected should be "CON-155 Power trowelled concrete finish". After inspection slab shown to be "CON-154 Hand trowelled finish".
| 02SL - Stations (LUL) | Cxxx-NCR-000887 | NCR | ETH L-3 Damper AS-E-FD031 access is obsrtucted. Lobby 4/097 Outside Room ESR 4/665 |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2019-07-29 | 2021-02-07 10:08 | 559 | 2019-07-15 14:42 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | ETH L-3 Damper AS-E-FD031 access is obstructed by electrical containment, CMS and Secondary Fixings.. Lobby 4/097 Outside Room ESR 4/665 Com Lot: Cxxx-HCV-AAV-FD031-SE003 IRN: Cxxx-SKC-M-NOX-Cxxx-50043
| 02SL - Stations (LUL) | Cxxx-NCR-000888 | NCR | Tray Firestopping Lid Exceeds Requirements at WTH -3 AP1 area |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-07-31 | 2021-02-04 12:03 | 554 | 2019-07-17 10:49 | Electrical - Cable Management | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Lid on tray work to achieve firestopping detail through penetration exceeds the 75mm max length in the specifications.Cxxx-SKC-E-DDD-Cxxx-16100 specifies that lid shall be 25mm and the maximum shall be 75mm.
| 02SL - Stations (LUL) | Cxxx-NCR-000889 | NCR | Tunnel Pumped Drainage NCR |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-07-26 | 2019-11-25 13:46 | 122 | 2019-07-17 08:09 | Mechanical - Piping | 20000 |  | Design | Rework | 2 (6-60k) | Complete | Design Problem - Not Defined | Completed |  | The 34 l/s pumping requirement (critical sump to sewer) for Cxxx TPD is listed in the following documents; 1) M&E Interface Between Cxxx & Cxxx Critical Sump (Cxxx-SKC-K1-STP-Cxxx-50009) – point 2.11 (page 13) states, under the heading ‘Sewer Connection’, that Cxxx shall ensure each of the two Critical Sump Pumps shall deliver a minimum of 17 l/s. 2) ETH & WTH Public Health Calculations (Cxxx-SKC-P-XCL-Cxxx-50001) – page 139 clearly states fire water discharge is to be taken as 34 l/s. This figure is extracted from ‘Design Criteria for the Remodelling of discharges to __ Sewers’ (CRL1-XRL-P-RGN-CRG01-50001) – so this figure applies to the pipework connection from Critical Sump up to sewer, as well as CP4a to Critical Sump. Page 142 of the same document shows a schematic, which shows the flow rates coming from each sump within the ETH. This also clearly shows a flow rate of 36 l/s (34 l/s from TPD, in addition to 1 l/s being pumped into the critical sump from two other station sumps located on L-5). 3) ETH __ Drainage Application (Cxxx-SKC-U-QAP-Cxxx-50001) is a document submitted by Cxxx to TW to apply for the discharge consent – this document states the discharge rate in to the sewer will be 41.64 l/s, and also states this figure includes fire water in addition to station drainage. This has not been incorporated into the design as the demarcation points where the pipework demarcates from Pumped to gravity do not give a large enough diameter pipework to dissipate pressure.
| 02SL - Stations (LUL) | Cxxx-NCR-000890 | NCR | WTH L-4 CCUs in Room 5/776 maintenance doors obstructed by room luminaires and other trades. |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2021-10-15 | 2021-11-03 12:12 | 19 | 2019-07-17 09:42 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | CCUs (in Cxxx-M-IRF-00231) having their maintenance doors obstructed by room luminaires in WTH L-4 Local Cooling Room 5/776 specifically for CHW-CCU-010, CHW-CCU-011, CHW-CCU-016). IRN: Cxxx-SKC-M-NOX-Cxxx-50075 IRN: Cxxx-SKC-M-NOX-Cxxx-50076
| 02SL - Stations (LUL) | Cxxx-NCR-000891 | NCR | Incorrect Damper orientation in WTH L-1 FCR 2/763 GE-W-FD128 - No access to actuator |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2019-12-19 | 2020-01-05 11:17 | 17 | 2019-07-17 10:54 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Visited WTH L-1 FCR 2/763, damper orientation of GE-W-FD128 is not correct. Motor has been installed the wrong side of the damper for access (but on the right side of the compartment wall). IRN: Cxxx-SKC-M-LRC-Cxxx-50032
| 02SL - Stations (LUL) | Cxxx-NCR-000893 | NCR | WTH -5: Fire Damper Impeded Access 6/409 GE-W-FD011 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-23 | 2020-01-12 21:23 | 111 | 2019-07-18 08:23 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | GE-W-FD011 access is impeded by CMS and lighting a low level - please refer to "Cxxx-SKC-M-DDA-Cxxx-11155_NCR_GE-W-FD011.pdf" for location details.
| 02SL - Stations (LUL) | Cxxx-NCR-000894 | NCR | Submain W064 “B” supply is terminated into “Supply No 1” isolator at ATS |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2019-08-01 | 2020-01-17 19:57 | 169 | 2019-07-18 09:51 | Electrical - LV Equipment | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During an inspection of Submain W064 it has been found that the cable which is the “B” supply, is terminated into “Supply No 1” isolator at ATS (see attached NCR photo).
| 02SL - Stations (LUL) | Cxxx-NCR-000895 | NCR | No Seperate CPC Installed with Submain E033 |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2019-12-20 | 2019-12-22 15:32 | 2 | 2019-09-10 17:30 | Electrical - Power Distribution | 1000 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | CRL were recently invited to witness dead testing of cable E033, however the works were not complete as this cable required an additional CPC to be installed.
| 02SL - Stations (LUL) | Cxxx-NCR-000896 | NCR | Sub main cable E066 installation incomplete, and possible incorrect size CPC selected |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2019-12-20 | 2020-02-14 10:04 | 56 | 2019-12-06 13:19 | Electrical - Power Distribution | 0 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On a recent invitation to witness dead testing of Sub Main E066, it was found that the installation of the CPC was not complete and not sized according to the specifications.
| 02SL - Stations (LUL) | Cxxx-NCR-000897 | NCR | WTH L-2 Accessibility of PSE Fan Compromised by other services Room 3/769 |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2019-10-25 | 2020-01-27 19:52 | 94 | 2019-07-18 14:06 | Mechanical - Mechanical Engineering General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | WTH L-2 Room 3/769 SPF Fan Access Blocked by: - Drain Pipes - CMS for power and controls - Light Fittings IRN: Cxxx-SKC-M-NOX-Cxxx-50021
| 02SL - Stations (LUL) | Cxxx-NCR-000898 | NCR | WTH L-3 FD (AS-W-FD083) access blocked Outside Cleaning Service Store 4_407 |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2019-08-01 | 2021-02-07 16:28 | 556 | 2019-07-18 16:35 | Mechanical - Mechanical Engineering General | 500 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | WTH L-3 FD blocked Outside Cleaning Service Store Room 4_407 AS-W-FD083 GE-W-FD097 Access is blocked IRN: Cxxx-SKC-M-NOX-Cxxx-50026 IRN: Cxxx-SKC-M-NOX-Cxxx-50033
| 02SL - Stations (LUL) | Cxxx-NCR-000899 | NCR | ETH WB TLPP, No space capacity on CMS |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-23 | 2019-11-01 20:45 | 39 | 2019-07-19 08:48 | Electrical - Cable Management | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The 300mm tray identified in the photo appears to not have sufficient space capacity.
| 02SL - Stations (LUL) | Cxxx-NCR-000900 | NCR | WTH WB TLPP, No A&M to CMS |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-23 | 2020-01-28 11:25 | 127 | 2019-07-19 11:48 | Electrical - Cable Management | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | As shown on the photo attached, the CMS rising from the invert to the TLPP has restricted access behind the durasteel
| 02SL - Stations (LUL) | Cxxx-NCR-000901 | NCR | ETH Westbound TLPP, CMS/__ setting out not to design |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-23 | 2019-07-31 14:52 | -54 | 2019-07-19 12:35 | Electrical - Cable Management | 0 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The 300mm tray and the durasteel setting out is not to design.
| 02SL - Stations (LUL) | Cxxx-NCR-000902 | NCR | ETH L-3 Obstructed Fire Dampers Installed incorrectly Outside Room STR 4/371 |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2019-08-05 | 2020-02-19 10:29 | 198 | 2019-07-22 09:42 | Mechanical - Mechanical Engineering General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Fire Dampers have not been installed as per the design drawings. The damper actuators cannot be accessed and are obstructed. Damper AS-E-FD036 IRN: Cxxx-SKC-M-NOX-Cxxx-50043 Damper GE-E-FD035 IRN: Cxxx-SKC-M-NOX-Cxxx-50055 ETH L-3 – Outside Room Step STR 4/371
| 02SL - Stations (LUL) | Cxxx-NCR-000903 | NCR | ETH L+0.5 Extract Fan Room A/906 Fire Damper Actuators blocked by CMS. |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-23 | 2021-04-20 12:59 | 575 | 2019-07-22 13:12 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Insufficient information made available to the worker. | Completed |  | ETH L +0.5 Fire Damper Actuators and duct hatches are blocked by CMS GE-E-FD108 IRN: Cxxx-SKC-M-NOX-Cxxx-50053 AS-E-FD099 IRN: Cxxx-SKC-M-NOX-Cxxx-50038
| 02SL - Stations (LUL) | Cxxx-NCR-000904 | NCR | ETH L-5 Damper Actuators and duct access hatches not accessible outside TX room (6/682) |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2019-08-05 | 2021-02-08 15:40 | 553 | 2019-07-22 15:13 | Mechanical - Heating Ventilation & Air Conditioning | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | ETH L-5 in corridor outside TX room (6/682) - Fire Damper actuators (PS-E-FD004, and PR-E-FD004) on the TX room ventilation ducts (above TX room door) obstructed by CMS. Access to hatches also blocked by CMS. IRN: Cxxx-SKC-M-NOX-Cxxx-50059
| 02SL - Stations (LUL) | Cxxx-NCR-000905 | NCR | ETH L +0.5 Fire Damper Actuator and Duct Access Hatches Blocked by CMS |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-24 | 2019-11-06 10:45 | 43 | 2019-07-22 15:24 | Electrical - Cable Management | 0 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | ETH L +0.5 Fire Damper Actuators and duct hatches are blocked by CMS GE-E-FD108 IRN: Cxxx-SKC-M-NOX-Cxxx-50053 AS-E-FD099 IRN: Cxxx-SKC-M-NOX-Cxxx-50038
| 02SL - Stations (LUL) | Cxxx-NCR-000906 | NCR | ETH L-5 Sump Room SWR 6/771 Drainage Pipework in contact with CMS |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2019-08-07 | 2019-12-05 09:36 | 120 | 2019-07-24 08:51 | Mechanical - Piping | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | ETH L-5 ~Surface Water Sump Room SWR 6/771 Drainage pipework in contact with low level CMS
| 02SL - Stations (LUL) | Cxxx-NCR-000907 | NCR | WTH L-4 LCR – Fire Damper actuators actuators blocked (GE-W-FD044 & AS-W-FD046) |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2019-11-22 | 2020-01-17 10:23 | 56 | 2019-07-24 15:18 | Mechanical - Mechanical Engineering General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | WTH L-4 LCR – Fire Damper actuators on the ventilation supply and extract ducts (above the LCR room door) obstructed by CMS/Conduit/drop rods. GE-W-FD044 IRN: Cxxx-SKC-M-NOX-Cxxx-50034 AS-W-FD046 IRN: Cxxx-SKC-M-NOX-Cxxx-50027 Room 5_776 Duct drawing Cxxx-SKC-M-DDA-Cxxx-11142
| 02SL - Stations (LUL) | Cxxx-NCR-000908 | NCR | WTH L-4 LCR – ventilation duct access doors blocked Room 5_776 |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2019-08-07 | 2020-01-17 09:53 | 163 | 2019-07-24 15:58 | Mechanical - Mechanical Engineering General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | WTH L-4 LCR – ventilation duct access doors above the CCUs CHW-CCU-014, and CHW-CCU-015, and CE-W-02 are blocked by CMS and drop rods. IRN: Cxxx-SKC-M-NOX-Cxxx-50034 IRN: Cxxx-SKC-M-NOX-Cxxx-50027
| 02SL - Stations (LUL) | Cxxx-NCR-000909 | NCR | WTH L-4 LCR – Ventilation Duct access doors above and near the CCUs CHW-CCU-010, and CHW-CCU-011 Room 5_776 |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2019-08-08 | 2021-03-12 13:30 | 582 | 2019-07-25 16:02 | Mechanical - Mechanical Engineering General | 0 |  | Design | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | WTH L-4 LCR – Ventilation Duct access doors above and near the CCUs CHW-CCU-010, and CHW-CCU-011 Room 5_776
| 02SL - Stations (LUL) | Cxxx-NCR-000910 | NCR | WTH, -5, WB Forced Vent, Zone 6,Poor Site Made Bend |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-11-15 | 2019-11-09 21:33 | -6 | 2019-07-26 10:00 | Electrical - Cable Management | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Site made bend used on Cxxx CV ICA 75mm cable tray.
| 02SL - Stations (LUL) | Cxxx-NCR-000911 | NCR | WTH L-5 in corridor outside TX room (6/669) Plant Supply - FD003 |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2019-11-22 | 2019-12-17 12:42 | 25 | 2019-07-26 10:00 | Mechanical - Mechanical Engineering General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | WTH L-5 in corridor outside TX room (6/669) - Fire Damper actuator PS-W-FD003 on the ventilation duct (above TX room door) obstructed by CMS drop rods. Actuator is on the wrong side of duct. Duct drawing Cxxx-SKC-M-DDA-Cxxx-11155 , 1. the Gas Suppression pipe will obstruct the damper actuator unless it is routed so that turns immediately in the corridor and so that it runs close to the wall, 2. and the new fire panel in the photo is going to cause an access issue for the MEWP or Picco lift. It will need to be moved. Please include this in the NCR / NCR notes. IRN: Cxxx-SKC-M-NOX-Cxxx-50037
| 02SL - Stations (LUL) | Cxxx-NCR-000912 | NCR | WTH L-4 Emergency switch room /UPS (5/667) - ventilation duct access doors are blocked by CMS below |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2020-01-30 | 2020-01-29 20:43 | -1 | 2019-07-29 09:47 | Mechanical - Mechanical Engineering General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | WTH L-4 Emergency switch room /UPS (5/667) - ventilation duct access doors are blocked by CMS below. Asset IRN Ref to be confirmed by contractor - Refer to Drawing mark-up attached. IRN: Ancillary Area Vent Cxxx-SKC-M-NOX-Cxxx-50027 IRN: Plant Supply Cxxx-SKC-M-NOX-Cxxx-50037
| 02SL - Stations (LUL) | Cxxx-NCR-000913 | NCR | WTH L-4 Fire Damper Actuator GE-W-FD035 for RM 5_667 blocked for access |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-23 | 2020-01-17 10:00 | 116 | 2019-07-30 10:12 | Mechanical - Heating Ventilation & Air Conditioning | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | WTH L-4 Fire Damper Actuator GE-W-FD035 for RM 5_667 cannot be accessed for maintenance. Installation is not as per drawing due to site conditions. Access to FD actuator is blocked by lower duct system.
| 02SL - Stations (LUL) | Cxxx-NCR-000914 | NCR | Cable E004 - Damaged Outer Cable Sheath |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-08-15 | 2019-12-15 10:23 | 122 | 2019-08-01 07:37 | Electrical - General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The outer cable sheath of cable E004 has been damaged which exposes the inner sheath. The cable is a 25mm 4C __ FP600s. The location of the damaged cable is within ETH, Level -4, Room 5/775.
| 02SL - Stations (LUL) | Cxxx-NCR-000915 | NCR | WTH L-0 - Grid 2/J Drainage not cast in upstand |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-30 | 2019-09-20 15:39 | -10 | 2019-08-05 15:27 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | 50mm S/S drainage pipe was not cast in RC upstand to connect the western section of the entry matwell to the eastern.
| 02SL - Stations (LUL) | Cxxx-NCR-000916 | NCR | WTH - Level 0.5 Chiller room gridline 1 North elevation columns alignment |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-06 | 2019-09-12 11:17 | 6 | 2019-08-07 09:43 | Civil - Civil Engineering General | 0 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | On the WTH, L0.5 chiller room there are 4 columns located on gridline 1 which are the wrong dimensions for supporting the louvres. The current 350x350mm column have been cast flush with L+0.5 and L+1.0 exterior face. In order to support the louvres these columns need to be modified to reflect the latest construction drawing. The 2 middle columns where case back in June 2016 to drawing Cxxx-__-S-DDL-Cxxx-11096 rev C03 prior to rev C04 being issued in January 2017. Drawing Cxxx-__-S-DDL-Cxxx-11096 rev C04 & C05 require the columns to extend back to gridline 1 on the inside of the chiller room and hence all 4 columns need to be extended 100mm back towards gridline 1 from their original location as shown in rev C03. Please confirm reinforcement detail to extend these columns 100mm back to gridline 1 The 2 columns that were cast back in 2016 prior to the PMI-1432 issued indicate a change to the size and location of these columns.
| 02SL - Stations (LUL) | Cxxx-NCR-000917 | NCR | ETH L-5 Obstructed by CMS, Access Hatch and Fire Damper AS-E-FD012 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-08-22 | 2019-12-27 12:04 | 127 | 2019-08-08 08:15 | Mechanical - Mechanical Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | ETH L-5 Obstructed by CMS, Access Hatch and Fire Damper AS-E-FD012
| 02SL - Stations (LUL) | Cxxx-NCR-000918 | NCR | WTH Level 0 W-01-792-D01- Large __ Vent Shaft Door |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2021-06-15 | 2021-06-15 14:25 | 0 | 2019-08-08 11:20 | Architectural - General | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | External Large Acoustic Door W-01-792-D01 (__ made) has been damage whilst being moved either in the factory or whilst being transported to site . 14/6/21. DD. This NCR has been expanded to include paint film thickness in addition to damage to the doors. A new NCR (Cxxx-NCR-000026) has subsequently been opened to cover the damage and this NCR is now solely for the paint film thickness issue. It has been reclassified from damaged to manufacturing defect.
| 02SL - Stations (LUL) | Cxxx-NCR-000919 | NCR | ETH - Stairs ESS7 and ESS8 Stairs, Strips on various location caused by different shades of paint |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-14 | 2021-06-06 07:43 | 631 | 2019-08-15 13:28 | Architectural - General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Previous Construction - Other | Completed |  | As per PWK 579, the remaining snagging works within ESS7 & ESS8 were to be carried out prior to MEP handover. The finish quality of the remedial works provided by Cousins was not finished properly, leaving: > Drip marks > Feathered edges > Roller brush streaks > Painting over pencil or pen marks An SI was sent requesting the sub-contractor to de-snag/prep the works (JM60.3204-e:) and repainting walls while blending the paint into the wall finish. However, the preparations works were not carried out. Furthermore, the sub-contractor is required to ensure there is no variation to the final surface finish (JM60.3209-d), however, upon completion there is a visible shade difference between the works carried out under NCR 313 and the instructed works.
| 02SL - Stations (LUL) | Cxxx-NCR-000920 | NCR | WTH -2: AAR-W-SD005 Install Blocked |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-08-30 | 2019-11-06 11:02 | 68 | 2019-08-08 13:12 | Electrical - Cable Management | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | When the eastern wall of 3/681 was compromised, the wall was re-built - to make this possible all the services were removed in 3/240 around AAR-W-SD005. Once this wall was re-built the CMS was installed prior to the smoke damper (AAR-W-SD005) at high level - thus the uncoordinated install has blocked any access to make the install possible. Please refer to the attached for clarity on location.
| 02SL - Stations (LUL) | Cxxx-NCR-000921 | NCR | P&T Mis-Alignment of Platform Curved Signage with adjacent GFRC Panels at LEVEL -5 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-08 | 2019-09-03 10:39 | -5 | 2019-08-09 07:44 | Architectural - Signage | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Interfacing problems | Completed |  | During the installation of the platform curved glazed signage panels along the platform, it was noted that the finger gap behind the glazed sigange panel with the GFRC strips was quite excessive and some glazed panels were also proud of the GFRC panels by an excessive amount.
| 02SL - Stations (LUL) | Cxxx-NCR-000922 | NCR | ETH ,West Bound non public platform, MNS 15 RC plinth poured at incorrect height |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-12 | 2019-10-04 11:26 | 22 | 2019-08-13 13:16 | Architectural - General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The RC plinth installed on the non-public platform has been installed at 98.300 as per the drawing Cxxx-SKC-A-DDE-Cxxx-77552. The drawing by __ Cxxx-SKC-A-DWG-Cxxx-51351 shows that __ were expecting a 150mm additional upstand on top of the FFL. The design was never fully integrated and have installed the plinth as per Cxxx-SKC-A-DDE-Cxxx-77552, to be flush with the screed levels.
| 02SL - Stations (LUL) | Cxxx-NCR-000923 | NCR | ETH Level +0.5 EH236 & EH237; Struck Re-bar contrary to Conditions of Cxxx-RFI-005511 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-12 | 2019-09-13 16:07 | 1 | 2019-08-13 15:20 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | 45mm core has cut through: EH236 - We cut through 1xhorizontal bar per face . EH237 - We cut through 1xdiagonal anti-crack bar on the south elevation. We also cut off the end only of a horizontal bar on the north elevation. Conditions of RFI being to avoid doing so.Occurred despite wall __ and adjustment of core location between bars.
| 02SL - Stations (LUL) | Cxxx-NCR-000924 | NCR | ETH L-5 Room 6/680 - EH249; Struck Re-bar contrary to Conditions of Cxxx-RFI-005511 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-14 | 2019-08-23 14:17 | -22 | 2019-08-15 12:26 | Civil - Civil Engineering General | 50 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 45mm core has cut 1no Vertical bar on east side. reinforcement bar. Conditions of RFI being to avoid doing so. Occurred despite wall __ and adjustment of core location between bars.
| 02SL - Stations (LUL) | Cxxx-NCR-000925 | NCR | SVP & busbar clash on WTH -5 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-08-30 | 2020-01-14 19:44 | 137 | 2019-08-16 10:23 | Electrical - Power Distribution | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Clearance between the 100mm SVP pipework - from the trapped outlet at H/L in circ area 6/071 - and the LV busbar from 6/669 into 6/071, is only 54mm as per the IFC drawings.
| 02SL - Stations (LUL) | Cxxx-NCR-000926 | NCR | WTH -Vent shaft __ Door W-05-83-D02 manufactured with Ironmongrey on the wron side |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-10-06 | 2020-03-06 11:43 | 152 | 2019-08-19 12:51 | Architectural - General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __ have manufactured W-05-83-D02 without taking into account the advisory comments and as such the door ironmongery is on the wrong side. The door will need to be re-manufactured to suit as the door can not be flipped 180deg as the clashes with the existing installation in the WTH vent shaft.
| 02SL - Stations (LUL) | Cxxx-NCR-000927 | NCR | All Escalators,the uni-strut Clashes with the surrounding interfaces |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-19 | 2019-09-03 13:04 | -16 | 2019-08-20 11:12 | Architectural - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | On all three banks of Escalators the uni-strut substructure that is bonded to the underside of __ decking has clashed with surrounding interfaces as it does not appear on any design coordination drawings. The clashes include: 1) E17-19: the uni-strut clashes with the escalator uplighter fixings (see photo 1) 2) E14-16: the uni-strut clashes with __'s smoke barrier trim (see photo 2) 3) E11-13: the uni-strut clashes with horizontal smoke barrier (see photo 3). __ have confirmed this uni-strut is only shown on their 'fabrication' drawing which were not provided to during the design coordination phase. It's believed if these drawings were provided, these clashes may have been avoided.
| 02SL - Stations (LUL) | Cxxx-NCR-000928 | NCR | Access to 2x AD (on Plant FAI & Plant Exhaust) hindered by Light fitting |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-08-05 | 2021-03-10 16:14 | 217 | 2019-08-21 11:37 | Electrical - Lighting | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Access to 2x AD (on Plant FAI & Plant Exhaust) hindered by Light fitting ,Plant Ductwork in NE corner of Fan II room 5/778
| 02SL - Stations (LUL) | Cxxx-NCR-000929 | NCR | Parallel conduit runs |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-01-24 | 2020-01-27 10:21 | 3 | 2019-08-21 13:18 | Electrical - Cable Management | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Multiple runs of conduit have been used instead of providing a multiple compartment trunking. Location: ETH -3 Zone 3 and ETH -4 Zone 1
| 02SL - Stations (LUL) | Cxxx-NCR-000930 | NCR | Cxxx-SKC-E-NOX-Cxxx-50103 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-11-29 | 2019-09-10 09:16 | -80 | 2019-08-21 13:49 | Mechanical - Public Health Engineering | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Split Washers are sporadically installed meaning that the pipe clips are not tightened in areas. Rods through split bands are of an uneven size meaning they are of a different orientation. The loads are not split evenly as the Split bands are not square to the wall. Painting of galv cuts have not been completed from cutting on site. This has the potential of corroding pipework at a fast rate. Static support calculations have not been issued as part of the inspection Stack support is not provided in Riser 925, meaning pipework is unsupported vertically. No snags completed from supervision after agreeing 5 days prior to do so. QA was brought out to inspect with the aim of handing over to CRL.
| 02SL - Stations (LUL) | Cxxx-NCR-000931 | NCR | CMS fixed to third party support brackets |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-04 | 2019-12-15 10:23 | 102 | 2019-08-21 14:41 | Electrical - Cable Management | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __ have used third party (BMS and Ductwork) support brackets to fix lights, CMS and conduit. Third party support brackets would not take into account the additional load. Location: Eastern ticket hall Level-2, 3/904
| 02SL - Stations (LUL) | Cxxx-NCR-000932 | NCR | ETH Level -5 - Pressure Test Report not as per ITP |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-08-30 | 2019-09-03 14:25 | 4 | 2019-08-22 11:22 | Mechanical - Public Health Engineering | 0 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | During the pumped drainage pressure tests, The __ Way pressure testing report template (OPS-T-2000) was used instead of the __ template (Cxxx-PRT-001) that was in their ITP.
| 02SL - Stations (LUL) | Cxxx-NCR-000933 | NCR | WTH -4: 5/777 General Extract Access Door Impeded |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-08-29 | 2019-12-27 12:07 | 120 | 2019-08-22 13:38 | Mechanical - Mechanical Engineering General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Access door is impeded by CMS traywork and CHW pipework, between 5/777 & 5/778, after PR-W-ATT004. It is noted that the access door is not installed inside 5/778 as per the drawing, however this would also be impeded by station drainage pipework.
| 02SL - Stations (LUL) | Cxxx-NCR-000934 | NCR | WTH, Gate line ITP not code 1 on eB |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-28 | 2019-09-27 13:48 | -1 | 2019-08-29 06:59 | Architectural - General | 0 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | requested CRL to witness pull testing of Gateline Anchors but __ ITP was not Code 1 on eB .
| 02SL - Stations (LUL) | Cxxx-NCR-000935 | NCR | WTH Busbar Trunking Bracketry Support |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-06 | 2019-09-05 09:29 | -1 | 2019-08-23 08:07 | Electrical - Power Distribution | 500 |  | Planning | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Busbar Trunking between (1) LV Switchroom LV I 6/660 & LV Switchroom LV II 6/673, and (2) LV Switchroom LV II 6/673 & Circulation Area 6/071 can not be clipped unable to 2 no. support brackets due to the protruding __ fire barrier. See drawings attached.
| 02SL - Stations (LUL) | Cxxx-NCR-000937 | NCR | ETH Level 0, Concourse unpaid side - Waterproofing |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-05-16 | 2020-04-30 10:30 | -16 | 2019-08-27 08:46 | Architectural - General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In a number of areas loose debris has been covered by the waterproofing membrane. This includes tie wire and polystryene beads. The membrane has also not been applied to all areas.
| 02SL - Stations (LUL) | Cxxx-NCR-000939 | NCR | WTH Urban Realm - MH02 Concrete surround defects |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-09 | 2019-09-26 08:46 | 17 | 2019-08-27 13:15 | Architectural - Walls | 500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Upon striking the shutter around WTH-MH02 a large section of honeycombing within the 150mm C20 concrete surround was identified
| 02SL - Stations (LUL) | Cxxx-NCR-000940 | NCR | WTH,areas of vent shaft and chiller room R/C walls were outside the required tolerance for installtion of __ Columns |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-28 | 2019-10-08 09:24 | 10 | 2019-08-29 12:13 | Architectural - General | 0 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Survey completed by __ on behalf of __. Survey showed, from document references above, that areas of vent shaft and chiller room concrete formation were outside the required tolerance for __ to install the structural columns on the exterior of the vent shaft and chiller room
| 02SL - Stations (LUL) | Cxxx-NCR-000941 | NCR | ETH L-0 to L-4,ESS Core Expansion |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-29 | 2020-01-10 16:59 | 103 | 2019-08-30 13:16 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | A series of 9 slab penetrations have been previously approved with C415-RFI-005496 as 250x100mm. Due to CMS manufacturing constraints, penetrations are required to be enlarged to 310x100mm. NCR is required to capture Cxxx reassessment of potential impact on slab stability.
| 02SL - Stations (LUL) | Cxxx-NCR-000942 | NCR | ETH Level -3 4/939 Architectural concrete up stand missing MNS 21 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-14 | 2019-10-24 14:20 | 40 | 2019-08-30 16:04 | Architectural - General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Policy not adequately defined, disseminated, or enforced | Completed |  | Surrounding detail of the maintenance hatch in the Eastbound draught relief, in the North East corner of Basement -3 has been installed incorrectly. As shown in Cxxx-SKC-A-DDE-Cxxx-77530-C02 and Cxxx-SKC-A-DDD-Cxxx-35843-C01 there was to be an additional architectural usptand surrounding the MNS21 Hatch. However at the time of construction the architectural concrete up stand was missed surrounding MNS 21 and is now required to be installed.
| 02SL - Stations (LUL) | Cxxx-NCR-000943 | NCR | GFRC - Gap between ES2 GFRC and __ Decking |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-18 | 2021-10-29 08:15 | 772 | 2019-09-04 09:11 | Architectural - General | 500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A survey was carried out in ES2 GFRC and identified a gap between the ES2 decking and the GFRC cladding .The gap is most pronounced at the Escalator tangent point. A site measurement of 3 no panels confirmed that the GFRC panels were circa 44~ 89mm shorter than designed The survey also revealed that the gap between the ES2 Decking and the GFRC S/S access hatches was in excess of the designed gap
| 02SL - Stations (LUL) | Cxxx-NCR-000944 | NCR | WTH/ETH Side Entrance Gate Design in relation to SR3 Lock |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-10-03 | 2019-09-17 15:08 | -16 | 2019-09-03 13:47 | Architectural - General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | __ Side Entrance Gates: Following design development to meet the SR3 rating requirements for the side entrance gates to the ticket halls, the supplier of the lock required to meet the standard amended their 'off the shelf' item, this resulted in the cylinder guard bezel now being 10mm larger than the previous model shown in the drawings.
| 02SL - Stations (LUL) | Cxxx-NCR-000945 | NCR | ETH L0 Chiller room: Incorrectly tested bolts in North RC wall |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-11-29 | 2019-09-18 11:43 | -72 | 2019-09-04 11:22 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | ETH L0 Chiller Room:- __ are required as per Cxxx-SKC-A-ITP-Cxxx-50090 rev 1.0, whilst on site. Supervisors offered up 3 no. bolts, that upon later inspection are not being used to support the acoustic lining panels fixed to the North Wall within 1/776. Although these bolts are closely located to the bottom track, __ should have provided opportunity to test bolts on other locations. This voids the RC bolts results ONLY, received on the 17.07.2019.
| 02SL - Stations (LUL) | Cxxx-NCR-000946 | NCR | WTH L-3 - 2x Access Doors required |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-18 | 2021-04-01 09:58 | 561 | 2019-09-04 13:15 | Mechanical - Mechanical Engineering General | 500 |  | Incomplete Works | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | WTH L-3 - Fit 2x access doors currently omitted from Ancillary ductwork in room 4/407 as per drawing: Cxxx-SKC-M-DDA-Cxxx-11223 C01 (as marked on attachment) IRF-00265 for IRN-50026
| 02SL - Stations (LUL) | Cxxx-NCR-000947 | NCR | Cable E003 - Isolator within BOS East Comms UPS ATS unable to accept designed cable |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-18 | 2019-11-18 19:30 | 61 | 2019-09-04 15:18 | Electrical - General | 1500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The UPS ATS incoming Isolator is rated at 160A which has a max cable termination capacity of 70mm. Supply cable E003 is a 95mm 4C SWA cable which has been installed to the Isolator. This is in accordance with the __ calcs
| 02SL - Stations (LUL) | Cxxx-NCR-000948 | NCR | Cable E052 - Isolator within BOS East Comms UPS ATS unable to accept designed cable |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-18 | 2019-11-18 19:39 | 61 | 2019-09-04 15:44 | Electrical - Electrical Engineering General | 1500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The UPS ATS incoming Isolator is rated at 160A which has a max cable termination capacity of 70mm. Supply cable E052 is a 95mm 4C SWA cable which has been installed to the Isolator. This is in accordance with the __ calcs.
| 02SL - Stations (LUL) | Cxxx-NCR-000949 | NCR | Cxxx-RFI-002663 Missing CRL Pre & Post Core Sign-off |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-19 | 2020-01-17 13:15 | 120 | 2019-09-05 07:40 | Civil - Civil Engineering General | 0 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Along the WTH Temporary Fire Main route, additional RC builders work penetrations were required and requested within Cxxx-RFI-002663 (DDN C658 - RFI 2663 builders work openings.pdf). There are no records of pre or post core Crossrail inspections of these works.
| 02SL - Stations (LUL) | Cxxx-NCR-000950 | NCR | ETH Colonnade lighting adaptable box |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-11-05 | 2019-11-01 20:55 | -4 | 2019-09-05 14:05 | Electrical - Lighting | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | In the ETH Colonnade coffers the adaptable box for transition of lighting cabling has not been fixed to the fabric building
| 02SL - Stations (LUL) | Cxxx-NCR-000951 | NCR | ETH Fire Main - Missing CRL Pre & Post Core Sign-off |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-20 | 2020-01-31 17:03 | 133 | 2019-09-06 07:44 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Along the ETH Temporary Fire Main route, additional RC builders work penetrations were required and requested within Cxxx-RFI-003113 (2no. Openings) and Cxxx-RFI-004439 (1no Opening). Check sheet records do not contain post core Crossrail inspection signoff on these works.
| 02SL - Stations (LUL) | Cxxx-NCR-000952 | NCR | Fire Rating of __ Stainless Steel Cable Ties do not match Fire Rating of __ FTP120 & __ FP600s Cables |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-12-20 | 2021-02-05 16:56 | 413 | 2019-09-06 12:30 | Electrical - Electrical Engineering General | 0 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | __ Stainless Steel Cable Ties have been used to secure __ FTP120 & __ FP600s type cables. This has been used on both horizontal and vertical orientations. The fire rating of the cable ties do not match the fire rating of the cable.
| 02SL - Stations (LUL) | Cxxx-NCR-000953 | NCR | ETH FF Lift 6 ATS failing to changeover to B supply on loss of A supply |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-28 | 2020-01-27 14:48 | 121 | 2019-09-09 09:13 | Electrical - General | 1000 |  | Testing and Commissioning | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | FF Lift 6 ATS failed to change-over to supply 'B' upon loss of 'A' supply
| 02SL - Stations (LUL) | Cxxx-NCR-000954 | NCR | ETH FF Lift 6 ATS not installed to specified height |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-23 | 2019-09-17 12:16 | -6 | 2019-09-09 09:41 | Electrical - General | 0 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | FF Lift 6 ATS mounted not as per design (too high) which impedes visual inspection of 'state' of ATS.
| 02SL - Stations (LUL) | Cxxx-NCR-000955 | NCR | Cable E030/073 - Use of Tube Safe cable not as per design. |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-23 | 2019-11-04 19:51 | 42 | 2019-09-09 11:47 | Electrical - General | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | Cable E030/073 - Use of Tube Safe cable not as per design; Original __ calculation and __ design states to used __ FTP120 Cu for the connection between ATS-FFL-06 & the associated Castell Isolator. Due to unforeseen site constriction, the use of Tube Safe LU 1-085 IEC-60331-3 singles cables within metallic trunking was required. Cable is acceptable under specification but FCD required to capture the site change.
| 02SL - Stations (LUL) | Cxxx-NCR-000956 | NCR | Fire Main Bracketry Calculation Documents not Issued for Acceptance on eB |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-12-23 | 2020-01-05 09:26 | 13 | 2019-09-10 14:57 | Mechanical - Mechanical Engineering General | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Tunnel Fire Main ‘bracket calculations’ not uploaded to eB at time of IRN issue. • Cxxx-SKC-S-CER-Cxxx-50111 Revision 1.0 • Cxxx-SKC-S-CER-Cxxx-50109 Revision 1.0 • Cxxx-SKC-S-XCL-Cxxx-50088 Revision 1.0
| 02SL - Stations (LUL) | Cxxx-NCR-000957 | NCR | Fire Main Bracketry Drawings attached to RFIs but not Issued for Acceptance on eB |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-12-23 | 2020-01-05 13:30 | 13 | 2019-09-10 15:10 | Mechanical - Mechanical Engineering General | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | Tunnel Fire Main bracket drawings uploaded as attachments to RFI instead of as part of an RIR. • Cxxx-RFI-004670 • Cxxx-RFI-004677 • Cxxx-RFI-004716
| 02SL - Stations (LUL) | Cxxx-NCR-000958 | NCR | E-06-102-D02 - Latch not aligning with strike plate |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-11-05 | 2019-12-09 10:37 | 34 | 2019-09-11 07:51 | Architectural - General | 500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Latch not aligning with strike plate - door E-06-102-D02
| 02SL - Stations (LUL) | Cxxx-NCR-000959 | NCR | Escape staircase 8 landing -3.5 A2 light fitting |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-26 | 2019-11-09 21:00 | 44 | 2019-09-12 12:57 | Electrical - Electrical Engineering General | 4000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 3 x A2 light fittings installed on landing -3.5 entry holes drilled in wrong position resulting in 2 holes being drilled on side of light fitting
| 02SL - Stations (LUL) | Cxxx-NCR-000960 | NCR | Fire Main Tanks Installed without Approved ITP |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-09-26 | 2019-09-13 15:48 | -13 | 2019-09-12 14:47 | Mechanical - Mechanical Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Not Defined | Completed |  | Tunnel and Station Fire Tanks (manufactured by Braithwaite) were installed by and an ITP was not created prior to the installation.
| 02SL - Stations (LUL) | Cxxx-NCR-000961 | NCR | ETH, -2, CMS, Plant room 3/904, Contravention of specification, Parallel conduit runs |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-01-31 | 2020-01-22 20:18 | -9 | 2019-09-13 14:51 | Electrical - General | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | Secondary CMS has been installed throughout room 3/904 as multiple long parallel conduit routes, causing non-complaince to JY60.1401
| 02SL - Stations (LUL) | Cxxx-NCR-000962 | NCR | TFM system installation without all MCRs submitted and approved |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-12-23 | 2019-12-19 11:19 | -4 | 2019-09-16 07:45 | Fire - Fire Systems & General | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | The following MCRs have not been Coded 1 on eB __, Cast Iron Fittings (BSP) CRL-MCR-006001 Rapidrop AARV and Isolation Valves CRL-MCR-007113 Cxxx Braithwaite Water tanks CRL-MCR-006881 Fire Main Non-Return Valve CRL-MCR-008203 The following MCRs have not been submitted on eB for Crossrail approval Galvanised Ring Clip CRL-MCR-008204 Flow Switch (MCR reference not created) Float Switches (MCR reference not created) Ball Valve (__) (MCR reference not created)
| 02SL - Stations (LUL) | Cxxx-NCR-000963 | NCR | IRN-50021 WTH PSE - Perforated Plates |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-10-01 | 2019-09-17 13:21 | -14 | 2019-09-17 12:03 | Mechanical - Mechanical Engineering General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Previous Construction - Other | Completed |  | WTH Over Platform Smoke Extract - Perforated Plates not installed as per schematics Cxxx-SKC-M-DDE-Cxxx-16340 and, for ETH Cxxx-SKC-M-DDE-Cxxx-1634
| 02SL - Stations (LUL) | Cxxx-NCR-000964 | NCR | ETH - IRN-50010 Fan inspection Access Doors |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-10-02 | 2019-12-03 15:14 | 62 | 2019-09-18 11:50 | Mechanical - Mechanical Engineering General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Fan FFP-E-SF001 (ETH -2 in Pressurisation Fan Rooms) – no access doors for Fan inspection are fitted either side of this. See Photo & Schematic attachements.
| 02SL - Stations (LUL) | Cxxx-NCR-000965 | NCR | WTH - Damage to Cable Sheath of W062A |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-10-02 | 2019-11-22 10:19 | 51 | 2019-09-18 15:44 | Electrical - Electrical Engineering General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Cable sheath damaged to W062A where it transits into TVF Control Room 2/763
| 02SL - Stations (LUL) | Cxxx-NCR-000966 | NCR | WTH Pre-Cast Mullions - West & North of (Chiller room/Vent shaft) - Scabbling Required |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-10-19 | 2019-11-15 16:40 | 27 | 2019-09-19 17:00 | Architectural - General | 2000 |  | Design | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Reference: Cxxx-SKC-A-DWG-Cxxx-52068 MU for Plan view of columns During the survey works in preparation for the pre-cast __ column installation on Grid 1-4 & A-C at the WTH, Mammot have identified 4 x columns (PM4A, PM2a, PM1A, PM1a3 noted in __-9838-021_02 MU.pdf, __-9838-020 MU.pdf & SK2503_WTH___ Western facade column plate clashes ) where plate connections clash with the existing RC on the vent shaft and chiller room. This has occurred due to the vent shaft slipform positional tolerance (+/-25mm) and chiller room RC tolerances differ to __ precast tolerance for the RC structure being 10mm. To complete the column installation, a number of plated connection areas for the 4 x identified columns will require scabbling back to within __ tolerance. To clarify the clashes have been split into the following issues: 1. Unapproved Sawcut works @ Column PM4/A - Located Grid 4/A 2. Unapproved Scabbling works @ Column PM1/A - Located Grid 1/A - west upper 3. Other areas requiring remedial works for tolerance issues - Column - PM2a, PM1a3 & PM1/A (north, west lower) - Grid 2/A , 1/B, 1/A
| 02SL - Stations (LUL) | Cxxx-NCR-000967 | NCR | ETH Level -5 UPE Riser 7/933 - NLB Wall |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-10-04 | 2019-12-13 17:40 | 70 | 2019-09-20 13:09 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | ETH Level -5 UPE Riser 7/933 NLB wall along the western elevation of the UPE riser from basement level -5 to basement level -4 4/933. As shown in Cxxx-FCD-000364 - proposed detail sketch, the gap between RC elements is supposed to be 40mm. However upon inspection, the wall has been poured short by 40mm leaving reinforcing involved
| 02SL - Stations (LUL) | Cxxx-NCR-000968 | NCR | ETH -4 Extract Fan 5/775 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-01-17 | 2021-01-29 10:58 | 378 | 2020-01-03 15:39 | Electrical - Electrical Engineering General | 0 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Conduit running through lifting zone.
| 02SL - Stations (LUL) | Cxxx-NCR-000970 | NCR | ETH - ESS8 FF Staircase, Lighting design, Luminiares are obstructing safe movement through space |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-10-07 | 2019-11-29 22:06 | 53 | 2019-09-23 11:36 | Electrical - Electrical Engineering General | 100000 |  | Design | Rework | 1 (>60k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Incline lighting that has been designed for ESS8 & ESS7 is causing unsafe obstructuion at the heights that they are proposed to be installed. Where they are proposed, they are causing untolerable risk that they will cause danger and obstruction at head height.
| 02SL - Stations (LUL) | Cxxx-NCR-000971 | NCR | WTH Submain cable W007 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-10-08 | 2019-09-26 15:19 | -12 | 2019-09-24 13:27 | Electrical - Electrical Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Submain Cable W007, Insulation is cut down to the copper on some of the cores at the panel end of the cable.
| 02SL - Stations (LUL) | Cxxx-NCR-000972 | NCR | WTH , level -1 dry shrinkage cracks to the underside of mole hole slab |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-03-31 | 2020-12-21 18:09 | 265 | 2020-03-05 13:22 | Civil - Civil Engineering General | 3000 |  | Material | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A post pour inspection of the level -1 mole hole infill slab identified dry shrinkage cracks in places along the perimeter and surface. This may be a result of the increased concrete strength to C50/60 under Cxxx-FCD-001224 irregardless that correct curing measures were followed. Due to the level -1 slab being handed over to OSD and potential for water penetrating the perimeter shrinkage cracks along the perimeter, it is deemed prudent to proceed with resin injection. The soffit of the level-1 infill slab was also inspected with no shrinkage cracks of concern raised
| 02SL - Stations (LUL) | Cxxx-NCR-000973 | NCR | ETH Wall Hatches - Incorrect Procurement |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-10-09 | 2019-12-16 09:01 | 68 | 2019-09-25 14:01 | Architectural - General | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | The spreadsheet that was issued to Profab to procure the ETH wall hatches had the site as build measurements listed as WxH without the headers titled. An assumption was made and noted by Porfab that the measurement were recorded HxW (as per the design measurements noted in the same spreadsheet). This error was not picked up and all hatches were procured based on this incorrect assumption.
| 02SL - Stations (LUL) | Cxxx-NCR-000974 | NCR | All conduit installations |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-11-17 | 2019-11-13 17:33 | -4 | 2019-09-25 15:58 | Electrical - General | 0 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Misunderstand the definition of the requirement | Completed |  | __ have drilled all device conduit boxes. Conduit boxes supporting luminaires or Electrical equipment will require seperate fixing
| 02SL - Stations (LUL) | Cxxx-NCR-000975 | NCR | Non Approved MCR-008227 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-10-10 | 2019-10-30 10:53 | 20 | 2019-09-26 12:37 | Electrical - General | 0 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Use of Material with Non approved MCR , ( Wrap Around Heat Shrink - Shrink Polymer Systems)
| 02SL - Stations (LUL) | Cxxx-NCR-000976 | NCR | WTH - Damage to Cable Sheath of W062B |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-10-10 | 2019-10-30 22:24 | 20 | 2019-09-26 13:23 | Electrical - Electrical Engineering General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | Cable W062B sheath damaged.
| 02SL - Stations (LUL) | Cxxx-NCR-000977 | NCR | ETH - Current CMS design in ESR I |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-10-11 | 2019-10-06 14:05 | -5 | 2019-09-27 11:19 | Electrical - Electrical Engineering General | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | CMS at high level is not subtle to take the cables installed on it. (Within the ESR I, ETH L-3)
| 02SL - Stations (LUL) | Cxxx-NCR-000978 | NCR | WTH -4: Access blocked to Ductwork Access Doors |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-10-11 | 2021-04-08 07:00 | 545 | 2019-09-27 11:48 | Mechanical - Mechanical Engineering General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient work planning by the subcontractors | Completed |  | Blockwork access doors limited by traywork, drop rods and lights. Please see "Cxxx-SKC-M-DDA-Cxxx-11143 P10_IFC WTH L-4 obstructed hatches.pdf" for clarity.
| 02SL - Stations (LUL) | Cxxx-NCR-000979 | NCR | ETH Clonnade coffer cladding eyebolts tampered / removed by __ |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-10-11 | 2019-10-25 14:47 | 14 | 2019-09-27 15:47 | Architectural - General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Following completion of the coffer cladding substructure by __, and handover to __ for CMS installation, __ have modified and/or removed some eyebolts of the substructure during their works.
| 02SL - Stations (LUL) | Cxxx-NCR-000981 | NCR | ETH - Redundant concrete nibs on bottom on precast columns GL-1,C/D |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-10-15 | 2019-11-21 17:19 | 37 | 2019-10-01 07:56 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | When pouring the upstand on GL-1, concrete was pour in front of 7 number precast column up to upstand level, this concrete nib will clash with the arquitectural stones. See .pdf attached.
| 02SL - Stations (LUL) | Cxxx-NCR-000982 | NCR | ETH, Missing post-pour of the Lightwell roof slab between GL2-4 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-10-31 | 2020-08-12 13:06 | 286 | 2019-10-01 14:56 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Prior to a handover of the SE corner of the haul road, had the lightwell roof slab post-poured and waterproofed. The slab was waterproofed with __ 900 MP, as per normal process. Due to unknown circumstances, the post-pour records have gone missing, however, the waterproofing records have been located.
| 02SL - Stations (LUL) | Cxxx-NCR-000983 | NCR | ETH - ESS8 Corduroy Tile Set Out |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-10-15 | 2019-12-10 10:44 | 56 | 2019-10-01 15:45 | Architectural - General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The ESS8 stairs corduroy tile angles have not been installed parallel resulting in a uneven corduroy tile set out. As explained in -RFI-009600, we have to rectify the Angles and the Tile Set out to match "Approved Document M" for the Corduroy tiles 400mm from the nosing & 800mm of corduroy paving. Further to this the Corduroy tiles themselves are 400mm each and there has been no allowance for grout within the set out
| 02SL - Stations (LUL) | Cxxx-NCR-000984 | NCR | Cables laying on structural floor within the UPS Panels. |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-11-29 | 2019-11-19 09:38 | -10 | 2019-10-02 09:29 | Electrical - General | 1000 |  | Design | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Where the cables move from the cable chamber to the UPS panels they go under the plinth of the Panel and lay on the structural floor.
| 02SL - Stations (LUL) | Cxxx-NCR-000985 | NCR | ETH - Level -4, Lobby 5/095, Access restriction to Fire Damper AS-E-FD027 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-10-16 | 2021-01-22 14:59 | 464 | 2019-10-02 10:07 | Mechanical - Mechanical Engineering General | 0 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Fire Damper AS-E-FD027 has restricted access for maintainability/inspection due to General Extract ductwork and CHW pipework directly below it.
| 02SL - Stations (LUL) | Cxxx-NCR-000986 | NCR | Fixing to Building Fabric JY90 - HUS3-H8 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-12-13 | 2019-12-09 17:49 | -4 | 2019-10-02 11:59 | Mechanical - Mechanical Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | Contractors have been informed that these fixings are permissable for installation into breezeblock, however install/testing not covered in the ITP
| 02SL - Stations (LUL) | Cxxx-NCR-000987 | NCR | Pull out stress tests. ITP 3.2 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-10-16 | 2019-12-17 20:14 | 62 | 2019-10-02 12:21 | Electrical - Electrical Engineering General | 5000 |  | Documentation and Records | Repair | 3 (3-6k) | Complete | Verification Problems - Other | Completed |  | Pull out proof tests need to be produced for CMS Bracketry thats been installed into concrete.
| 02SL - Stations (LUL) | Cxxx-NCR-000988 | NCR | ETH - L-3, ESR 1 (4/665) Submain cable E101AB damaged during install |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-10-17 | 2019-10-28 12:40 | 11 | 2019-10-03 07:46 | Electrical - Electrical Engineering General | 3000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Submain Cable E101AB, Cable has a split in the insulation and fire protection may need replacing if the blue core has been damaged also.
| 02SL - Stations (LUL) | Cxxx-NCR-000989 | NCR | ETH L-2 Fire Dampers in LCR 3_967 Obstructed by other services. |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-12-02 | 2021-12-22 14:53 | 751 | 2019-10-03 10:11 | Electrical - Electrical Engineering General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Various M&E services have been installed in the ETH Level -2 LCR which are obstructing the access to the following dampers: LC-E-FD040 LC-E-FD036
| 02SL - Stations (LUL) | Cxxx-NCR-000990 | NCR | ITP's for staircase rectification works |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2019-10-17 | 2020-01-17 12:16 | 92 | 2019-10-03 16:28 | Civil - Civil Engineering General | 0 |  | Supervision/Management | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | 1. Cxxx ITP - WTH Staircase Rectification Works Cxxx-SKC-A-ITP-Cxxx-50113 2.0 was used for Construction, but is not Code 1 in eB. 2. Cxxx ITP - ETH Staircase Rectification Works (__) Cxxx-SKC-A-ITP-Cxxx-50120 1.0 checksheets should have been used for the staircase remedial works at the ETH, but the checksheets from ITP for the Reinforced Concrete Works were used instead. 3. Cxxx ITP - ETH Staircase Rectification Works (__) Cxxx-SKC-A-ITP-Cxxx-50120 is not referenced or linked to NCR's 677 or 753.
| 02SL - Stations (LUL) | Cxxx-NCR-000992 | NCR | Station wide: 95mm Copper reducing pin terminals and Din-rail terminal Dividers do not have an approved MCRs. |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-10-20 | 2020-01-08 14:44 | 80 | 2019-10-07 12:27 | Electrical - LV Equipment | 0 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | This NCR is for the use of 95mm Pin crimps and Din-rail terminal Dividers that do not have an approved MCR. (Multiple IRNs)
| 02SL - Stations (LUL) | Cxxx-NCR-000993 | NCR | IRN-M-50045 ETH -5 room 6/414 AS-E-FD002 access restriction |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-11-05 | 2020-02-21 09:34 | 108 | 2019-10-10 13:55 | Mechanical - Mechanical Engineering General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Fire Damper FD002 has access restricted by 2x CMS trays directly below - see location and photo on attached drawing.
| 02SL - Stations (LUL) | Cxxx-NCR-000994 | NCR | ETH L-5 Duct Access Hatch obstructed by CMS and other bracketry. |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2019-10-23 | 2020-01-05 09:31 | 74 | 2019-10-09 15:32 | Mechanical - Mechanical Engineering General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | IRN: Cxxx-SKC-M-NOX-Cxxx-50045 2 No Access Doors obstructed by CMS and bracket as shown in drawing attachment. Outside room STR1 6/414 Within Circ Area - 6/075
| 02SL - Stations (LUL) | Cxxx-NCR-000995 | NCR | WTH-ES1 L-4 to L-5 Escalator Slab missing pre-pours |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-11-09 | 2019-10-23 15:14 | -17 | 2019-10-10 11:24 | Civil - Civil Engineering General | 0 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | WTH ES1 L-4 to L-5 Lower escalator pour: Upon investigation, have been able to locate the 3 of the 4 concrete records; In-process, Cube results and Post pours. Due to unknown circumstances, have mislaid the Pre-pours that relate to the lower escalator slabs and plinths. Based on the attached photos prior to pouring the slab, the slabs and plinths were fixed and sufficiently ready prior for pouring. There were a total of 6 pours carried out, we currently are missing 4 pre-pours for the escalator slab. These are: Mass fill 3: 16/08/16 poured Mass fill 4: 23/08/16 poured Mass fill 5: 30/08/16 poured Mass fill 6: 06/09/16 poured
| 02SL - Stations (LUL) | Cxxx-NCR-000996 | NCR | Poor Workmanship to CMS Header Transition to Distribution Boards at ETH -4 CER |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2019-10-31 | 2019-10-28 14:50 | -3 | 2019-10-10 08:07 | Electrical - Power Distribution | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | During a formal inspection of submain cables E116 and E118 to distribution boards DB-E-UPS02 and DB-E-UPS04, it was noticed that the slotted transition from the header trunking to the DB's were poorly constructed (see attached photos). This is against the JA specification to maintain quality assurance of workmanship by the Contractor.
| 02SL - Stations (LUL) | Cxxx-NCR-000997 | NCR | ETH L-5 General Extract Duct not installed as per drawing. Supply Duct insulation now compromised. STR1 6/414 |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2019-10-24 | 2020-06-20 12:25 | 240 | 2019-10-10 13:38 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Not Defined | Completed |  | General Extract Ductwork installation is not as per drawing. Insulation spacing is now compromised by poor spacing between supply and extract ducts. NCR is raised on the basis that no FCD/RFI is in place. IRN: Cxxx-SKC-M-NOX-Cxxx-50045 (Ancillary Supply) IRN: Cxxx-SKC-M-NOX-Cxxx-50057 (General Extract)
| 02SL - Stations (LUL) | Cxxx-NCR-000998 | NCR | ETH&WTH - ATS Fixings Not As Per Design (Site Wide) |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-11-29 | 2019-11-22 12:01 | -7 | 2019-10-10 13:32 | Electrical - Electrical Engineering General | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | During a site survey of ATS units on 09/10/19, it has been raised that the design approved __ HUS3 fixings have not been used to fix the support bracketry to the floor and wall. Instead, threaded 10mm rod, spring washers and a nut has been used and fixed below the surface with chemical resin.
| 02SL - Stations (LUL) | Cxxx-NCR-000999 | NCR | Both ETH-3 & WTH-4 UPS Emergency Lighting LV Switchboards are not FAT tested |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-11-29 | 2019-11-21 21:44 | -8 | 2019-10-11 10:57 | Electrical - Electrical Engineering General | 5000 |  | Testing and Commissioning | Repair | 3 (3-6k) | Complete | Procedure Problem - Other | Completed |  | UPS Emergency Lighting LV Switchboards are not FAT tested. WTH-4 - BOS/UPS/W01 & ETH-3 - BOS/UPS/E01 Relating to IRN's Cxxx-SKC-E-NOX-Cxxx-50403 and Cxxx-SKC-E-NOX-Cxxx-50400 SCI Critical
| 02SL - Stations (LUL) | Cxxx-NCR-001000 | NCR | ETH-Southern Passageway Entrance Beam. GL F-3/4,4 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-11-10 | 2021-11-09 10:49 | 730 | 2019-10-11 14:47 | Architectural - General | 10000 |  | Incorrect Installation | Use As-Is | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Installed ETH Southern Passageway Entrance Beam deviates from the theoretical position by max 19mm at the top and as a result the beam is leaning inwards.
| 02SL - Stations (LUL) | Cxxx-NCR-001001 | NCR | ETH,Out of Tolerance Extended Decking on ES2 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-11-14 | 2021-11-02 08:37 | 719 | 2019-10-15 14:35 | Architectural - General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | have surveyed the interface between the GFRC and __ extended decking on ES2. The findings of this survey (attached) have revealed that the __ extended decking has been installed lower than designed (78mm below in the worst case) - refer to the attached survey information. It is 's understanding that the 3D model was provided to __ prior to fabrication of the extended decking for __ to incorporate into their design. __ are requested to provide design documentation to ascertain how their design heights were derived
| 02SL - Stations (LUL) | Cxxx-NCR-001002 | NCR | ETH L-2, circulation area 3/073 Fire Damper AS-E-FD042. Access obstructed. |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2019-10-30 | 2021-02-07 11:06 | 466 | 2019-10-16 09:58 | Mechanical - Heating Ventilation & Air Conditioning | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Access is about to be compromised by fire stopping wall and is obstructed by CMS. ComLot Required and to be added to: IRN: Cxxx-SKC-M-NOX-Cxxx-50042 Possible solution: The fix is to move the CMS, or put the damper on the other side of the wall (same side as GE-E-FD049). The actuator needs to face ‘into the corridor’. (The CMS doesn’t appear to be on __ drawings).
| 02SL - Stations (LUL) | Cxxx-NCR-001003 | NCR | ETH L-2, in lobby 3/097 – Fire Damper AS-E-FD052 is obstructed by drainage pipework and CMS |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2019-10-30 | 2021-02-07 10:40 | 466 | 2019-10-16 15:56 | Mechanical - Heating Ventilation & Air Conditioning | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Subcontractor Problems - Insufficient work planning by the subcontractors | Completed |  | ETH L-2, in lobby 3/097 – Fire Damper AS-E-FD052 is obstructed by drainage pipework and CMS IRN: Cxxx-SKC-M-NOX-Cxxx-50042 (Ancillary Supply) IRN: Cxxx-SKC-P-NOX-Cxxx-50013 (Drainage) IRN: Cxxx-SKC-E-NOX-Cxxx-50009 (Prim. Containment) IRN: Cxxx-SKC-R3-NOX-Cxxx-50036 (PAVA) IRN: Cxxx-SKC-R3-NOX-Cxxx-50017 (CCTV) IRN: Cxxx-SKC-R3-NOX-Cxxx-50047 (Tel) IRN: Cxxx-SKC-09-NOX-Cxxx-50001 (FIRE) Possible solution: Reposition the damper on the other side of the wall (see photo 2262) The actuator needs to face ‘into the room- Unallocated room 3/765.
| 02SL - Stations (LUL) | Cxxx-NCR-001004 | NCR | Poor Workmanship to Site Manufactured Bend at ETH outside ECR 2/713 |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2020-02-14 | 2020-11-06 09:00 | 266 | 2019-10-16 16:12 | Electrical - Cable Management | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A site manufactured trunking bend was noticed manufactured to a poor quality standard and had a cable already installed (see attached photos). This is non compliant with JY60 (see technical requirements for details).
| 02SL - Stations (LUL) | Cxxx-NCR-001005 | NCR | Cable W031 (IRN Signed) was found Dissconnected at the LV Board |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2019-10-31 | 2020-02-09 08:56 | 101 | 2019-10-17 22:59 | Electrical - Power Distribution | 1000 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Before commencing a live test of cable W031 it was found that the cable was disconnected at the LV Board end. The cable IRN was signed off as complete (including termination) on 9th August 2019 and the live test was planned for 9th October 2019. See attached RIVO incident report for further details.
| 02SL - Stations (LUL) | Cxxx-NCR-001006 | NCR | Cxxx-SKC-E-NOX-Cxxx-50188 SC1 E112 Submain Cable ETH no CMS spare capacity |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-11-01 | 2019-12-09 10:26 | 38 | 2019-10-18 10:28 | Electrical - Cable Management | 3000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | ETH Level -5 bottom of Electrical Services riser 920 -No CMS spare capacity on tray at the bottom of riser 920 at Level -5 and therefore not compliant with the project specification requirements for 25% spare capacity on all CMS.
| 02SL - Stations (LUL) | Cxxx-NCR-001007 | NCR | ETH L-2 LCR IRN-M-50089, IRN-M-50042, IRN-M-50054. Fire Dampers and Access Doors obstructed by other services Local Cooling Room LCR 3/910. |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-03-31 | 2021-12-02 15:52 | 611 | 2019-10-18 12:38 | Mechanical - Mechanical Engineering General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | ETH L-2 LCR Fire Dampers and Access Doors obstructed by other services Local Cooling Room LCR 3/910. Affected IRNs below: IRN-M-50089 CCUs (507 & 508) IRN-M-50094 (Pipework) IRN-M-50042 •Ancillary Supply Duct Access Doors - 2 No. of •AS-E-FD044 IRN-M-50054 •General Extract Duct - 2 No. of •GE-E-FD043
| 02SL - Stations (LUL) | Cxxx-NCR-001008 | NCR | ETH-The Risers on MNS 8 stair is out of tolerance |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-11-17 | 2019-11-22 15:54 | 5 | 2019-10-18 12:56 | Architectural - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The Risers on MNS 8 have been found to be out of tolerance, the top step being 10mm higher than the other 2
| 02SL - Stations (LUL) | Cxxx-NCR-001009 | NCR | Fire Detection ( __ Systems ) |  | Crossrail | PDP | BOS - Bond Street Station (West) |  | 2020-05-15 | 2020-05-07 10:36 | -8 | 2019-10-18 13:01 | Fire - Detection | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | HSSD/__ panels and associated pipework have been installed in areas that are not detailed on code 1 drawings in eB, (Eg ) Cxxx-SKC-E-DWG-Cxxx-50820-P01.and is therefore not assured. Area, ETH,L-1, rooms 2/408 & 2/409.
| 02SL - Stations (LUL) | Cxxx-NCR-001010 | NCR | BOS Air Sampling ( __ ) Drawings |  | Crossrail | PDP | BOS - Bond Street Station (West) |  | 2020-05-14 | 2020-05-07 10:44 | -7 | 2019-10-18 13:15 | Fire - Fire Systems & General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | CRL have noted that there are a number of air sampling drawings as placeholder only in eB, as __ have installed air sampling pipework in a number of areas around the station without an assured design, a NCR is required.
| 02SL - Stations (LUL) | Cxxx-NCR-001011 | NCR | Out of date calibration cert (FLUKE) |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-12-31 | 2019-11-05 19:40 | -56 | 2019-11-05 15:10 | Electrical - Power Distribution | 0 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Prerequisites not satisfied | Completed |  | IRN-E-50400 - ETH Level -3 Emergency Lighting UPS LV Switchboard ETH BOS/UPS/E01 IRN-E-50404 - ETH Level -3 Communication UPS LV Switchboard ETH BOS/UPS/E02 IRN-E-50408 - WTH Level -4 Communication UPS LV Switchboard WTH BOS/UPS/W02 __ to provide updated calibration cert or re testing of the panels required with new equipment & in date calibration cert
| 02SL - Stations (LUL) | Cxxx-NCR-001012 | NCR | No FAT Test carried out |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-12-31 | 2020-11-19 17:13 | 324 | 2019-12-06 12:52 | Electrical - LV Equipment | 500 |  | Incomplete Works | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | FAT Testing has not been carried out in the following UPS Panel: IRN-E-50399 - BOS/E/UPS2 IRN-E-50411 - BOS/W/UPS2
| 02SL - Stations (LUL) | Cxxx-NCR-001013 | NCR | Station Fire Main Invert Pipework failing pressure test - distortion of pipe alignment and brackets |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2019-11-22 | 2020-01-20 14:16 | 59 | 2019-10-30 09:33 | Fire - Fire Systems & General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The station fire mains was installed within the platform inverts as per GIR 54. This design information did not have sufficient detail for thrust bracketry, static loading or a guiding system due to lateral movement. When the fire mains was tested to 12 bar, the pipework distorted due to this lack of restriant. The pipework should have been designed to take into account expansion and contraction along with lateral movement.
| 02SL - Stations (LUL) | Cxxx-NCR-001014 | NCR | CTP not Code 1 prior to UPS SAT |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-11-05 | 2020-01-27 10:27 | 83 | 2019-10-22 14:55 | Electrical - General | 0 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Lack of approval Code 1 procedures excessive | Completed |  | The CS-JV testing and commissioning team have started SAT testing the UPS system with Code 2 CTP in place: Cxxx-SKC-E-STP-Cxxx-50019 Rev 1.0 is currently Code 2 in eB, CRL comments as per Cxxx-SKC-E-XCS-Cxxx-50200. This NCR may affect IRN-E-50064, 50065, 50092 and 50093 (all SC1 relevant)
| 02SL - Stations (LUL) | Cxxx-NCR-001015 | NCR | WTH-__s - Lack of evidence of acoustic performance of acoustic hatches |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-11-22 | 2019-12-06 11:29 | 14 | 2019-10-23 08:22 | Architectural - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | __s have failed to provide evidence of the acoustic performance for the following hatches: E-01-76-H01 E-03-780-H01 W-D-791-H01 W-D-792-H01 W-E-791-H01 W-E-792-H01
| 02SL - Stations (LUL) | Cxxx-NCR-001016 | NCR | WTH L-4, Battery Room 5/665 Fire Damper GE-W-FD041 obstructed by other services. |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2019-11-07 | 2021-02-07 16:50 | 458 | 2019-10-24 10:35 | Mechanical - Mechanical Engineering General | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | WTH L-4, Battery Room 5/665 Fire Damper GE-W-FD041 obstructed by other services. Access to the actuator is now compromised by CMS, as well as conduit __ supports. IRN: Cxxx-SKC-M-NOX-Cxxx-50034 (General Extract) IRN: Cxxx-SKC-E-NOX-Cxxx-50019 (PMR Tray / PAVA Trunking / COMMS/ FA) IRN: Cxxx-SKC-E-NOX-Cxxx-50019 (Lighting & Small Power)
| 02SL - Stations (LUL) | Cxxx-NCR-001017 | NCR | Tunnel Fire Main Thrust Bracket fixing (Critical Sump Room) |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-11-07 | 2019-12-21 16:01 | 44 | 2019-10-24 12:19 | Mechanical - Mechanical Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | The Tunnel Fire Main Thrust Bracket has been fixed into mass concrete protective slab level 98.200 without Screeding/RC plinth constructed as a finished item. This has been done using __ HST3 M12 x 105mm wedge anchors with an embedment depth of 75mm. This depth is to be checked by Civi;s and Cxxx to identify whether waterproofing layer has been compromised. These bolts need to be used in the finished floor, whether that is via an RC plinth or confirmation the structural slab can be used with localised screeding
| 02SL - Stations (LUL) | Cxxx-NCR-001018 | NCR | Damper Actuator inaccessible ETH Level -1 Escalator Control room |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-11-30 | 2019-11-01 16:50 | -29 | 2019-10-25 15:21 | Mechanical - Mechanical Engineering General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The Fire damper within this room has been installed in the wrong orientation. The Actuator now site behind the __ cabling which is inaccessible
| 02SL - Stations (LUL) | Cxxx-NCR-001019 | NCR | ETH Tech Wall- Access Hatch to Oil Dampner not operational |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-12-21 | 2021-12-08 07:52 | 718 | 2019-10-29 10:13 | Architectural - General | 500 |  | Material | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | During the installation of the top access hatches at the ETH Tech wall it was identified that the oil dampers are not operating as the required design, which is under pressure and not extension.
| 02SL - Stations (LUL) | Cxxx-NCR-001020 | NCR | ETH, Level -4, room (5/669) to Level -5,(6/683) - Submain cable E074 Wrong separate CPC pulled in. |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-11-13 | 2019-11-01 09:02 | -12 | 2019-10-30 15:43 | Electrical - Electrical Engineering General | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The __ states that the separate CPC should be 35mm, But we found on our inspection today that a 35mm CPC has been installed at the Zend (DB-E-B07) and at the A end (LV Panel B) a 16mm CPC has been installed. We traced the cable and found both ends of the CPC’S coiled up in riser LVP R (5/919) Level -4.
| 02SL - Stations (LUL) | Cxxx-NCR-001021 | NCR | ETH, Level -4, LV SwitchRoom (5/668) - Damage to Submain Cable E027 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-11-22 | 2019-11-14 09:50 | -8 | 2019-10-30 14:38 | Electrical - Electrical Engineering General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Submain cable E027, the cable has been damaged due to what looks like other cables being pulled over it and burning it down to the armouring.
| 02SL - Stations (LUL) | Cxxx-NCR-001022 | NCR | ETH & WTH - MCR Required for Bicon 370GC07 Cleats Used |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-11-14 | 2019-12-03 16:34 | 19 | 2019-10-31 10:28 | Electrical - Electrical Engineering General | 0 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Following a site inspection on 30/10/19, it has been raised that 'Bicon 370GC07' cleats have been used on the Bond Street Station electrical installation without an approved site specific MCR. Although these cleats have been used on other stations such as Farringdon (CRL-MCR-005270), they have not yet been approved for Bond Street.
| 02SL - Stations (LUL) | Cxxx-NCR-001023 | NCR | WTH L+0.5 (1/583) & L0 (1/631) & ETH L0 (1/751) - Trace Heating Installation Proceeding without Approved MCR |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-11-21 | 2019-11-25 12:46 | 4 | 2019-11-01 11:27 | Mechanical - Mechanical Engineering General | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Personnel Error - Inattention to detail | Completed |  | Installation of the trace heating on the ETH & WTH fire mains proceeded without the submission or approval of an MCR specific to Cxxx Bond St. CRL-MCR-006562 from Whitechapel Station was used in lieu of this.
| 02SL - Stations (LUL) | Cxxx-NCR-001024 | NCR | ETH - ESS8 bottom and top step out of tolerance - SC1 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-11-18 | 2019-12-16 16:36 | 28 | 2019-11-04 10:37 | Architectural - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | ESS8 - the top and/or the bottom step has been found to be out of tolerance on each level, also they are not sitting level
| 02SL - Stations (LUL) | Cxxx-NCR-001025 | NCR | Unable to Install Plat Sign SGN 205 in Accordance with Cxxx Signage Schedule due to Incorrect GFRC Panel Configuration |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-12-20 | 2019-11-25 16:28 | -25 | 2019-11-04 10:47 | Architectural - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the installation of the curved Exit Guide sign Ref 711 on westbound platform between CP2 and 4 (highlighted on the attached drawing Cxxx-SKC-A-DDE-Cxxx-25450 Rev P11) it was noted that the width of the space provided between the GFRC panels was NOT sufficient to install the SGN 205 Type Curved Exit Guide. This is due to the GFRC sub contractor NOT installing the GFRC panels in accordance with the drawings they were instructed to use for installation of the GFRC panels by the contractor to meet signage requirements in this area.
| 02SL - Stations (LUL) | Cxxx-NCR-001026 | NCR | WTH, -2, 3/131 FF Lift 8, Reversal of A&B Supply Glanded into the ATS Unit |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-11-30 | 2020-02-25 08:01 | 87 | 2019-11-04 12:30 | Electrical - General | 0 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Standard practise sitewide for the ATS supply cables installation has the A supply cable on the left hand side and B supply cable on the right hand side. Lift 8 ATS unit has the cables reversed and if the cable are swapped to the correct orientation the B supply cable will be short and this cable runs back to the main LV switchroom on level-5.
| 02SL - Stations (LUL) | Cxxx-NCR-001027 | NCR | WTH, Level 0, 1/661 & 1/662 LV Switchroom, Electrical Equipment Installed At Incorrect Height |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-11-30 | 2022-02-02 12:45 | 795 | 2019-11-04 13:04 | Electrical - General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | All electrical equipment, earth bar, riser trunking fixed lids has been installed at the recommended height using the concrete slab as the finished floor datum rather than the actual FFL which approximately 300mm higher than the slab therefore when the screed is laid the boards will be 300mm too low.
| 02SL - Stations (LUL) | Cxxx-NCR-001028 | NCR | ETH Ticket hall L0 Matwell, waterproofing product not compliant |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-05-21 | 2020-04-30 10:33 | -21 | 2019-11-05 11:06 | Architectural - General | 500 |  | Material | Repair | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | The waterproofing material applied on the Matwell at the ticket hall is been pick up from CRL "__" that does not comply as it is a flamable product. __ is class E EN 13501. LU 1-085 requirement for floor application is Bfl or BS476:Part 7 Class 2, Silicor does not meet this requirement __ 900 is been use as waterproof material, see attached Code 1 MCR-50138 and code 1 drawing -35820 that state the use of the __, now rejected, the material is specified within JJ30 for use within this application and therefore a specified material. See mark up attached of the area that is already waterproof and will need remedial works.
| 02SL - Stations (LUL) | Cxxx-NCR-001029 | NCR | WTH, L-3 Molehole post pour |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-11-19 | 2020-02-05 10:15 | 78 | 2019-11-05 13:54 | Civil - Civil Engineering General | 0 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Following the WTH molehole closures, the L-3 molehole area was tiled by __. This NCR is to cover the molehole slab not being post pour inspected and signed off prior to the tiling being done.
| 02SL - Stations (LUL) | Cxxx-NCR-001030 | NCR | Incorrect Location of Curved Station Name Signage SGN 205 on Eastbound Platform (Ref 501) |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-12-07 | 2019-11-28 16:06 | -9 | 2019-11-07 16:08 | Architectural - Signage | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | NCR raisd by __ The location of a SGN 205 platform curved sign Ref 501 was incorrectly set out on site resulting in the sign being approx 1500mm east along the Eastbound platform from where the design shows the sign. A plan and elevation drawing have been attached for clarity showing where the station name sign should have been installed as per design and where the sign has been installed on site.
| 02SL - Stations (LUL) | Cxxx-NCR-001031 | NCR | ETH - Room 4/767 Submain Cable E18/E58 Damaged |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-11-29 | 2019-11-13 18:14 | -16 | 2019-11-08 10:48 | Electrical - Electrical Engineering General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following an inspection on cable E18/58 on 05/11/19, it was found that damage has been caused to the 'Z' end outer insulation. Although the damage is moderate, a repair is required to ensure the outer insulation is protected from further damage.
| 02SL - Stations (LUL) | Cxxx-NCR-001032 | NCR | DB Door Clashes at WTH L0 1/661 & 1/662 LV Switchroom |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2019-11-26 | 2022-02-02 15:46 | 799 | 2019-11-12 08:46 | Electrical - Power Distribution | 2000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | The doors on both DB-W-B01 and DB-W-EL01 (fed by W068 & W102) are restricted to opening no more than 80-90 degrees. For DB-W-B01 the CMS installation on the left hand side is restricting the DB door swing. For DB-W-EL01 the door swing is restricted by the blockwork and will be further restricted when the cupboard door frame is installed. See attached report for full details and photos. The rework of this NCR should be cordinated with the rework to Cxxx-NCR-001027 enclosed.
| 02SL - Stations (LUL) | Cxxx-NCR-001033 | NCR | Trace Heating - Lack of assurance documentation WTH +0.5 and ETH 0 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-11-26 | 2019-12-03 10:20 | 7 | 2019-11-12 14:59 | Mechanical - Mechanical Engineering General | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Previous Construction - Other | Completed |  | MCR and missing information – Current MCR does not include all materials -Incorporated in CRL-MCR-008374 Confirm Controller IP rating – needs to be specified on MCR description - Incorporated in CRL-MCR-008374 Heating cables – MCR currently states this is a winterguard cable. Specify Raychem FSB-2x on MCR submittal Incorporated in CRL-MCR-008374 End-terminations – Specify on MCR submittal Incorporated in CRL-MCR-008374 Rayclics and sensors - x 2 types - Specify 2x types of Racylics on MCR submittal Incorporated in CRL-MCR-008374 Controller - Specify type of controller on MCR submittal (with capability of interfaces included as well) Incorporated in CRL-MCR-008374 Supply & control cables - Specify on MCR submittal and provide data sheet Incorporated in CRL-MCR-008374 Fixings for controller into the walls - Specify on MCR submittal and provide data sheet UNISTRUT MCR TO BE ADDED? Tape - Specify on MCR submittal and provide data sheet Cladding is missing from installation. Confirm that all meet Spec. for Trace Heating (MEP JY24 - Cxxx-SKC-M-RSP-Cxxx-50076 Rev 3.0) Warning labels need to be fitted to the insulation now in place as per: Cxxx-PWK-00992/993 Trace Heating requires warning labels – please fit as per. Spec.; alternate sides/within 5m intervals. (Please ensure this is installed after the cladding) Covered in Cxxx-PWK-00992 & Cxxx-PWK-00993 Cladding to be installed Covered in Cxxx-PWK-01018 & Cxxx-PWK-01019 Require a relevant Task Briefing, installation carried out without one Competency Cards for Jointing Tech inspector. Jointing Tech rep Rhys has said A. Hills (who did the insulation resistance testing) does not have a JIB card. - __ have provided test results in lieu of this Rhys from Jointing Tech/Conor to provide competency cards and blurb regarding competency. __ have provided test results in lieu of this
| 02SL - Stations (LUL) | Cxxx-NCR-001034 | NCR | FP Cables require addressing in Ess8 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-11-16 | 2019-12-03 16:43 | 17 | 2019-11-12 15:17 | Fire - Fire Systems & General | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Non Conformity of FP Cables. Cables installed through Adaptable Box in a poor condition.
| 02SL - Stations (LUL) | Cxxx-NCR-001035 | NCR | WTH, -5, 6072, Circ Area, Addtional Capacity Required For Link Trunking Ref -5.70C |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-11-26 | 2019-11-13 17:54 | -13 | 2019-11-12 15:28 | Electrical - Cable Management | 6000 |  | Incorrect Installation | Use As-Is | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Currently trunking -5.70C has not been installed to design. The four compartment trunking has the following issues. PAVA - Should be 75mm wide and is 50mm wide Comms - Should be 150mm wide and is 100mm wide CCTV - Is correct at 75mm wide FA - Should be 50mm and is missing.
| 02SL - Stations (LUL) | Cxxx-NCR-001036 | NCR | ETH - ESS7 & ESS8 half landings - ESS8 L-3.5 & ESS7 L -1.5, -2.5, -3 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-12-20 | 2020-01-23 12:12 | 34 | 2019-11-13 15:58 | Architectural - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Further to NCR 753, the half landings on ESS8 and the landings of ESS7 were repaired with a levelling compound 'Mapei plantitop Smooth and repair R4' to meet the required troweled finish. However it has now been observed that small areas of the compound are cracking and chipping off at joins.
| 02SL - Stations (LUL) | Cxxx-NCR-001037 | NCR | ETH - Stairs Rectification works Missing Cubes |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-12-14 | 2020-01-30 17:11 | 47 | 2019-11-14 09:36 | Civil - Civil Engineering General | 3000 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | The Sub-contractor has failed to take site cubes for the 3-10mm repair material applied for the stair rectification works at locations: ESS7, ESS8, MNS11, MNS12, MNS22 , MNS23 This has been stated within ITP Cxxx-SKC-A-ITP-Cxxx-50120 Item 5.4
| 02SL - Stations (LUL) | Cxxx-NCR-001040 | NCR | Non-manufactured Top Hat used + installed incorrectly |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-01-17 | 2021-07-02 17:14 | 532 | 2019-11-14 12:39 | Electrical - Cable Management | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __ CMS not installed correctly 5/073 corridor outside FOSC room - Top Hat fixed underside of a joiner - Support brackets was not installed correctly - cables in/live
| 02SL - Stations (LUL) | Cxxx-NCR-001041 | NCR | BMS/PLC - LV supplies to dampers and BMS outstations/CEs sitewide – Upsizing of cables over original design details |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-02-14 | 2020-01-09 16:03 | -36 | 2019-11-18 14:04 | Electrical - Power Distribution | 0 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | In the AMTECH calculations provided by __ for their BMS/PLC installation works, they have indicated that 1.5mm² cables will be installed for the LV supply to dampers and BMS outstations/CEs. Their relevant specifications state that a minimum of 2.5mm² cable is to be used throughout the project to supply LV equipment. In complying with the specification they have created a departure from their own design, but haven’t provided any clarification or requested the design change with __/Crossrail.
| 02SL - Stations (LUL) | Cxxx-NCR-001042 | NCR | IRN-M-50092 ETH -2 3/910 LCR: Buffer Vessel Cladding Damage |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-12-31 | 2021-02-07 11:51 | 404 | 2019-11-18 15:37 | Materials - General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Error by manufacturer in shipping or marking | Completed |  | CHW Buffer Vessel (CHW-BV501) is located in Level -2 LCR 3/910 on the ETH. The Buffer Vessel external cladding has been damaged following positioning and installation
| 02SL - Stations (LUL) | Cxxx-NCR-001043 | NCR | WTH, -4, 5/777/ ATS Gland Plate Drilled Incorrectly, Replacement Required |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-12-09 | 2020-01-14 20:05 | 36 | 2019-11-19 12:03 | Electrical - Electrical Engineering General | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Cable W020/W058 - ATS MCC-W-04 Gland plate in the top of ATS panel has been drilled incorrectly and left. Gland plate to be replaced.
| 02SL - Stations (LUL) | Cxxx-NCR-001044 | NCR | WTH -5 Circulation Area 6/072 & 6/071 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-12-03 | 2020-01-21 20:44 | 49 | 2019-11-19 12:44 | Fire - Fire Systems & General | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __ are installing non appoved trunking onsite. They have started installig unitrunk trunking which is not on the MCR register
| 02SL - Stations (LUL) | Cxxx-NCR-001045 | NCR | ETH - Ground Floor Lift 6 Structural Opening Remedials |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-12-19 | 2020-01-31 10:55 | 43 | 2019-11-19 16:45 | Civil - Civil Engineering General | 1500 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The structural reinforced concrete header on Lift 6 at Level 0 is lower than required to achieve the specified clear lift door opening and architrave install - this discrepancy is understood to have occurred due to a previous change in finish floor heights through the Eastern Ticket Hall.
| 02SL - Stations (LUL) | Cxxx-NCR-001046 | NCR | ETH Riser 927 L0 - Grouting Required |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-12-04 | 2019-12-16 08:46 | 12 | 2019-11-20 08:49 | Architectural - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | As a result of a bow in the concrete slab __ were unable to install metal packers behind the steel beam end plate (refer to marked up layout)
| 02SL - Stations (LUL) | Cxxx-NCR-001047 | NCR | ETH L-2 Room 3/9004 SD-001 OBSTRUCTED BY CMS and conduit - Stair Pressurisation Systems |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-12-04 | 2020-01-23 19:23 | 50 | 2019-11-20 09:36 | Electrical - Electrical Engineering General | 1000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Smoke /damper -001 is currently blocked and inaccessible due to CMS
| 02SL - Stations (LUL) | Cxxx-NCR-001048 | NCR | Level -5, P&T Missing documents for Platform upstand QA pack |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-12-04 | 2020-05-22 14:46 | 170 | 2019-11-20 14:30 | Civil - Civil Engineering General | 0 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate administrative control | Completed |  | Record pack: EB & WB Platforms, Cross passages CH2 & CH3 & Concourses - Concrete Upstand Channels. Has missing 11 x missing post pour documents and 2x missing in-process sheets.
| 02SL - Stations (LUL) | Cxxx-NCR-001049 | NCR | ETH,ESS8 Stairs Handrail - Temporary Additional Sleeve |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-12-21 | 2019-12-17 15:34 | -4 | 2019-11-21 10:11 | Architectural - Handrail | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Due to the remedial works to the concrete treads on ESS8 the final asbuilt dimensions vary from the original survey completed by __ for the handrail design and construction. As a result of this the returns around the spine walls on each landing are not alligning.
| 02SL - Stations (LUL) | Cxxx-NCR-001050 | NCR | ETH External facade stones to be replace |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-02-28 | 2021-09-28 07:22 | 578 | 2019-11-21 10:39 | Architectural - General | 3000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | The (architectural) pre-cast stones elements forming the Eastern Ticket Hall structure installed on site, have been damaged, by others, and need to be repaired/replaced.
| 02SL - Stations (LUL) | Cxxx-NCR-001051 | NCR | Lack of FIRAS Installer certification - __s |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-12-21 | 2020-01-30 12:28 | 40 | 2019-11-21 11:08 | Architectural - Doors | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | __s do not have FIRAS Installer certification as required delivering item 3.3.9 of Cxxx-SKC-O4-ITP-Cxxx-50015.
| 02SL - Stations (LUL) | Cxxx-NCR-001052 | NCR | ETH L-4 Rm 5_775 MCC LV Power Supplies to Overhead Platform Extraction (OPE) Fans – Upsizing of cables from original design |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-12-06 | 2020-01-21 22:18 | 46 | 2019-11-22 13:41 | Electrical - Power Distribution | 0 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The design provided by __ stated in their cable schedules that the Cross Sectional Area (CSA) of the cable supplying all four OPE fans was 6mm. Upon inspection the cable that has been installed has a CSA of 10mm. The subsequent test results for the installed cable detail the CSA of the cable as 10mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001053 | NCR | Galvanic Corrosion/Moisture inside adaptable box, WTH & ETH Level 0 Concourse |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-12-20 | 2021-09-03 09:39 | 623 | 2019-11-22 11:31 | Electrical - General | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Contamination | Completed |  | Bespoke stainless steel Adaptable boxes were to be installed into the level +1 concrete, however, it was found that the welded earthing stud and the lid fixing threaded inserts are not stainless steel. Linked to IRNs: ETH Coffer 50007; WTH Coffer 50015
| 02SL - Stations (LUL) | Cxxx-NCR-001054 | NCR | Failed Pull Test ETH LCR (LER) A/133 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-12-06 | 2020-02-12 12:24 | 68 | 2019-11-22 14:45 | Electrical - Electrical Engineering General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Proprietary Pull Testing was required to provide the integrity of the fixings supporting the ATS installed within the room. The fixings used to fix the unistrut frame to the structure are 40mm __ HUSE3-P 6. A proprietary fixing was installed within the wall adjacent to the ATS to the agreed imbedded depth of 35mm. To carry out the test the fixing had to be 'unscrewed' by approx. to allow the __ Pull Testing clamp to fit. Therefore, the imbedded depth being ~25mm. The pull test criteria was 2.4kN for 60 seconds. Whilst the test was being carried out the __ HUS3-P 6 fixing failed and pulled out of the wall causing minor damage. The above was carried out a second time which failed again. No further tests was carried out.
| 02SL - Stations (LUL) | Cxxx-NCR-001055 | NCR | IRN-M-50114 - BMS/PLC - MCC-E-05 - Damage to installed and signed off works |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-03-06 | 2019-12-06 23:13 | -91 | 2019-11-27 15:17 | Mechanical - Mechanical Engineering General | 2000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Damage has been caused to installed and signed off __ works. This has the potential to affect commissioning and therefore the acceptance of an IRN. Extent of damage: FFP-E-SD-001 & FFP-E-HTMD-001 isolators damaged. Please see attached BIM360 Report. The labels given in this report are incorrect. Please see attached photos which show the dampers and their labels for clarity. E-SF-001 and E-SF-002 are the isolators for the inverters and motors and are the larger sheet steel type.
| 02SL - Stations (LUL) | Cxxx-NCR-001056 | NCR | WTH L-4, 5_171 Cable W018 - Damaged 'Z' End |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-01-17 | 2020-01-21 10:50 | 4 | 2019-11-25 14:27 | Electrical - Electrical Engineering General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following an inspection on cable W018, it was found that damage has been caused to the 'Z' end outer insulation. Although the damage is moderate, a repair is required to ensure the outer insulation is protected from further damage.
| 02SL - Stations (LUL) | Cxxx-NCR-001057 | NCR | ETH, -5, Zone 6, 6/090 Maint Lobby, Standard Firestopping Detail Not Acheived |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-12-10 | 2019-12-08 08:50 | -2 | 2019-11-26 15:32 | Electrical - Electrical Engineering General | 0 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The usual practise of 50mm spacing between CMS services and around the CMS service has not been acheived as the tray and trunking passes through the builders work hole.
| 02SL - Stations (LUL) | Cxxx-NCR-001058 | NCR | ETH MNS31 - Grating Modification Required |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-12-27 | 2020-01-06 09:58 | 10 | 2019-11-27 09:25 | Architectural - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | MNS31 staircase channel that supports the grating is sitting 50mm too low to allow for the grating to span the S/O in the RC wall located in the middle of the MNS31 staircase.
| 02SL - Stations (LUL) | Cxxx-NCR-001059 | NCR | ETH Incorrect manufacture of E-06-73-D01 (SC1 door) |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-12-11 | 2020-09-10 07:55 | 274 | 2019-11-27 09:24 | Architectural - Doors | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | __ were to provide a replacement door for E-06-73-D01 as the door was originally manufactured with the ironmongery swapped around. The replacement door has been manufactured to the incorrect dimensions.
| 02SL - Stations (LUL) | Cxxx-NCR-001060 | NCR | WTH - Ventilation Shaft Maintenance Doors. |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-12-11 | 2020-01-28 15:18 | 48 | 2019-11-27 11:11 | Architectural - General | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | The sub-contractor's manufacturing quality assurance records have not been populated during fabrication thus are unable to submit these documents as part of the ITP deliverable record pack.
| 02SL - Stations (LUL) | Cxxx-NCR-001061 | NCR | WTH L0 – Gilbert St OSD Upstand Grid A/2-3 Sleeves Cast at Incorrect Level |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-05-07 | 2020-12-21 16:59 | 228 | 2020-04-07 15:12 | Civil - Civil Engineering General | 1000 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | An RC upstand located WTH L0 Grid A/2-3 has been cast with 2no 200mm dia sleeves [__ Product Code 155448] at 1:100 fall, extended 100mm outside each end of the upstand. This was instructed to to facilitate OSD requirements under Cxxx-PMI-01689 and Cxxx-PMI-01728. The 2no 200mm dia sleeves were to be cast as specified invert levels and falls as per "Sketch 1 - Additional 2no cast in sleeves to OSD Satellite core REV 01 Upon as-built survey (Refer As Built Survey - WTH - L0 Gilbert Street sleeves Rev.1.pdf) information it appears the specified falls of the cast in sleeves were not achieved and the sleeves fall slightly in the opposite direction. It should be noted however the sleeves are cast within contractual specification tolerances (KF10.3222 e)iii) on page 45 of KF10 spec. doc Cxxx-__-S-RSP-Cxxx-00009)
| 02SL - Stations (LUL) | Cxxx-NCR-001062 | NCR | BMS/PLC - Pull testing not witnessed by CSJV or Crossrail |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-03-13 | 2020-03-04 10:42 | -9 | 2019-11-27 16:41 | Mechanical - Mechanical Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Inspection points not adequate | Completed |  | Pull testing has not historically been witnessed by or Crossrail.
| 02SL - Stations (LUL) | Cxxx-NCR-001063 | NCR | ETH 5/732 (CER II) Mounting Height of DB-E-UPS-02 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-12-11 | 2019-12-02 16:39 | -9 | 2019-11-27 16:45 | Electrical - General | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | DB-E-UPS-02 in 5/732 has been installed below the 0.85 metre requirement as outlined on typical detail section drawings. This distribution board was installed adjacent to a smaller board. As these distribution boards are supplied from the same source, they share a common header trunking, which subsequently has been installed level accross the top of the two DB's, for ease of wiring, installation of UPS cable tray directly above and for aestetic purposes.
| 02SL - Stations (LUL) | Cxxx-NCR-001064 | NCR | WTH L-2 3_779 RC Slab, Additional Re-Bar Struck |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-12-13 | 2020-02-07 15:44 | 56 | 2019-11-29 08:42 | Civil - Civil Engineering General | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 200mm DIA core has cut 2no. north-south reinforcement bars. Conditions of RFI allowing for 1no.
| 02SL - Stations (LUL) | Cxxx-NCR-001065 | NCR | WTH, -2, Zone 1, Fan III 3/769, Standard firestopping detail not achieved |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-12-13 | 2020-01-16 21:02 | 34 | 2019-11-29 16:39 | Electrical - Electrical Engineering General | 0 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The usual practise of 50mm spacing around the CMS service has not been acheived as the tray passes through the builders work hole.
| 02SL - Stations (LUL) | Cxxx-NCR-001066 | NCR | Cable Cores 10mm and above not Terminated with a Socket Crimped to the Core |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2019-12-31 | 2020-01-27 10:34 | 27 | 2019-12-04 10:08 | Electrical - Power Distribution | 0 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | As per JY61.3103 g) all cable cores 10mm and above shall be terminated by use of copper cable socket crimped to the core. The sockets shall be fixed by the use of crimping tools, used in strict compliance with the manufacturer’s recommendations. On site all DB’s have been terminated at the ‘Z’ end of the submain cable with the copper straight into the terminations without the use of copper cable socket crimped to the cores. This is a generic issue throughout all DB terminations on site (WTH & ETH). For example DB terminations that have not complied with the specification clause see below locations and attached photos. *Submain E118 terminated into DB-E-UPS-04 at ETH -4 CER 5/732 *Submain E112 terminated into DB-E-EL09 at ETH -5 LV Switchroom IV 6/680
| 02SL - Stations (LUL) | Cxxx-NCR-001067 | NCR | CMS Trunking is in contact with the Ductwork at WTH Level -1 (2/086) |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2019-12-15 | 2021-03-26 16:39 | 467 | 2019-12-01 09:06 | Electrical - Cable Management | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Following the IRF inspection on 22nd November at the WTH Level -1 (2/086) Zone 3 Primary CMS, it was observed that the Primary CMS (Trunking) was in contact with other services (Ductwork), see attached photos. This is non compliant to JY60.3203 part b) (see technical requirements) which requires 150mm spacing between trunking and other services (ductwork). Also the Project Manager was not notified of this instance and the services were not bonded together as required by JY60.3203 part a) (see technical requirements). Refer to Cxxx-SKC-E-DDA-Cxxx-11113, Cxxx-SKC-M-DDA-Cxxx-61112, Cxxx-FCD-001028 and Cxxx-FCD-001255 (linked to this NCR) for MEP design details for this area. This NCR may also have impact on Cxxx-NCR-000840 and Cxxx-NCR-001068 (linked to this NCR), and therefore should be considered during the implementation phase.
| 02SL - Stations (LUL) | Cxxx-NCR-001068 | NCR | CMS Tray is Inaccessible at WTH Level -1 (2/086) and not installed to the Design |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2021-07-14 | 2021-06-30 18:58 | -14 | 2019-12-01 09:25 | Electrical - Cable Management | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Following the IRF inspection on 22nd November at the WTH Level -1 (2/086) Zone 3 Primary CMS, it was observed that the Primary CMS (Tray) at high level was inaccessible, see attached photos. The top 300mm Tray is installed in parallel with the wall and Ductwork therefore providing limited space for access to the tray to install and dress cables. This is non compliant to JA.6402 part c) (see technical requirements). Also when comparing the install to the design drawings and related FCD's (Cxxx-SKC-E-DDA-Cxxx-11113, Cxxx-SKC-M-DDA-Cxxx-61112, Cxxx-FCD-001028 and Cxxx-FCD-001255 linked to this NCR) it can be seen that the tray work has not been installed to these design documents. This is non compliant to JA.3101 part c) (see technical requirements). This NCR may also have impact on Cxxx-NCR-000840 and Cxxx-NCR-001067 (linked to this NCR), and therefore should be considered during the implementation phase.
| 02SL - Stations (LUL) | Cxxx-NCR-001069 | NCR | WTH, -5, 6/576 Sump Room, CMS Poor Installation by Pumpserve (__ SUB-CON) |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-12-17 | 2020-10-08 14:13 | 296 | 2019-12-03 10:57 | Electrical - Electrical Engineering General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Poor Installation of secondary CMS to the sump pump. Tray cut through perforations on site made bends and poorly supported on cuts
| 02SL - Stations (LUL) | Cxxx-NCR-001071 | NCR | WTH-2, 3/779 RC Slab Cxxx-RFI-005227, MH273 NCR - Additional Re-Bar Struck |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-12-18 | 2020-01-09 12:54 | 22 | 2019-12-04 10:32 | Civil - Civil Engineering General | 500 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 152mm DIA core has cut 2no. east-west reinforcement bars of slab top mat. Conditions of RFI allowing for 1no.
| 02SL - Stations (LUL) | Cxxx-NCR-001072 | NCR | WTH L-5 Room 6_667 Non LU Compliant Cable Used |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-12-18 | 2019-12-18 11:00 | 0 | 2019-12-04 11:53 | Electrical - General | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | An inspection on DB-W-A06 was carried out on 03/12/19 which included the inspection of all internal final circuit cables within that DB. During the inspection it was found that circuits 1L3 & 9L3 CPC have been wired using a cable manufactured by 'El Sewedy Cables'. Although this cable has an approved MCR under CRL-MCR-005466, it is not CE compliant and states the following; "Approved for use in surface locations only where 1-085 is not applicable. This product must not be used where LU standard 1-085 is applicable." This location of the cable install do not meet the above requirements.
| 02SL - Stations (LUL) | Cxxx-NCR-001073 | NCR | Platforms & Tunnels - Tile Stains |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-12-19 | 2021-11-05 13:27 | 687 | 2019-12-05 16:07 | Architectural - General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Dampening down for dust suppression on the platforms has resulted in the tiles being stained, as the moisture on the ply protection seeps through and traps the water.
| 02SL - Stations (LUL) | Cxxx-NCR-001074 | NCR | WTH L-5 Duct Access Door Obstructed by CMS - AP2 WB Platform |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2019-12-19 | 2021-01-26 08:43 | 404 | 2019-12-05 14:21 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Obstructed by the CMS (PMR), IRN: Cxxx-SKC-E-NOX-Cxxx-50012 (Cable Number to be confirmed IRN No. recorded on eB) Duct Brackets IRN: Cxxx-SKC-M-NOX-Cxxx-50019 Pumped Drainage Pipe IRN: Cxxx-SKC-M-NOX-Cxxx-50003 Possible Solutions: Relocate duct access door if possible within DW144 and CRL duct specification guidelines. Trim back the duct bracketry Adjust PMR tray positon to create larger access space for a larger MEWP
| 02SL - Stations (LUL) | Cxxx-NCR-001075 | NCR | WTH L-4 Smoke Damper and Fire Damper Obstructed by CMS (Formerly Cxxx-NCR-000617) |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2019-12-19 | 2020-01-17 10:03 | 29 | 2019-12-05 16:25 | Mechanical - Mechanical Engineering General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Formerly Cxxx-NCR-000617 (Incorrectly closed) PTR Attached. There are a number of different locations where access to smoke control damper actuators have been blocked by electrical services. The I.D. of these dampers are GE-W-FD039, AS-W-FD030 and ARR-W-SD003 located in Circulation area 5/071.
| 02SL - Stations (LUL) | Cxxx-NCR-001076 | NCR | Inadequate Cavity barriers on the platform as they are not touching the back of the GFRC panels in some areas. |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-01-31 | 2020-01-23 12:06 | -8 | 2019-12-06 09:00 | Architectural - General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | AIS have reported that the cavity barriers on the platforms are inadequate as they are not touching the back of the GFRC panels in some areas.
| 02SL - Stations (LUL) | Cxxx-NCR-001077 | NCR | Incorrect LV Power Supplies/controls wired from MCC to OPE fan sets |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-01-03 | 2020-01-27 20:25 | 24 | 2019-12-06 11:55 | Electrical - LV Equipment | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __ have wired the incorrect LV Power Supplies and controls from MCC to Overhead Platform Extraction (OPE) Fan sets - locations/site of rework described as below: WTH - Room 3/769 (MCC-W-06) ETH – Room 5/775 (MCC-E-06)
| 02SL - Stations (LUL) | Cxxx-NCR-001078 | NCR | DB-E-A08, Circuit 11L2 wrong cable size |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-12-30 | 2019-12-22 12:47 | -8 | 2019-12-16 10:49 | Electrical - General | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On our inspection of the circuits from DB-E-A08, On Circuit 11L2 the cables from the DB out to the first __ are wired in 2.5mm as per the __ but from the first __ to the other 2 __ points it is wired in 4mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001079 | NCR | DB-E-A09 & DB-E-B09 on circuits 1L1 __ points have not been installed |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-12-30 | 2020-01-08 15:04 | 9 | 2019-12-16 10:58 | Electrical - General | 0 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | It has been highlighted on the inspections of the circuits for DB-E-A09 & DB-E-B09, that on circuits 1L1 of both these DB’s the first points have not been installed and have been deleted. No RFI's or FCD's have been raised to cover this design change.
| 02SL - Stations (LUL) | Cxxx-NCR-001080 | NCR | ETH AP3 Cable pits - Damaged Cable |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-01-31 | 2020-04-09 13:45 | 69 | 2019-12-09 15:27 | Communications and Control Systems - SCADA/Central Management System | 5000 |  | Damaged | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The cable in question is the Rail safe 4F 050 FR LSC-13.4-134-210-RE (Cxxx-DAT-00743); PAVA Fibre that runs from LU CER >>> CRL CER 2 (located in ETH level – 4) the run is approx. 800No meters.
| 02SL - Stations (LUL) | Cxxx-NCR-001081 | NCR | ETH Level -5 6/680 - Dist Board DB-EL-08 Circuit 8L1 Incorrect Cable Size Installed |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-12-20 | 2019-12-19 23:06 | -1 | 2019-12-10 08:53 | Electrical - Electrical Engineering General | 0 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | 6mm 1C cables have been installed for DB-E-EL08 circuit 8L1, whereas 10mm 1C __ L-Sifer should have been installed as per ETH & WTH Dist Board Schedule (Level -5, P&T) document ref Cxxx-SKC-E-TSC-Cxxx-50003 Rev 23.
| 02SL - Stations (LUL) | Cxxx-NCR-001082 | NCR | WTH -5 Switchroom 111 6_674 - Dist Board DB-W-A05 Circuit 1L1 & 1L2 Mixture of Cable Types Installed |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-12-24 | 2020-01-13 14:54 | 20 | 2019-12-10 09:01 | Electrical - Electrical Engineering General | 0 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | A mixture of Exane PC and Exane Circuit Safe has been installed for the DB-W-A05 Circuit 1L1 and a mixture of Exane PC Class 2 & Class 5 for Circuit 1L2
| 02SL - Stations (LUL) | Cxxx-NCR-001083 | NCR | Doors manufactured to RC openings rather than steelwork - GIR 5J Doors |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-01-31 | 2020-01-28 16:54 | -3 | 2019-12-10 10:26 | Architectural - General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | The below doors have been manufacture to meet the RC opening width as opposed to the surrounding steel frames (see GIR 5J). E-02-409-D02 E-02-411-D02 E-04-600-D01 P-7-594-D01 P-7-595-D01 The clear opening is reduced to 750mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001084 | NCR | WTH Level -5 (Switchroom III 6/674) Dist Board DB-W-B05 Circuit 11L3 Mixture of Cable Types Installed |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-12-20 | 2020-01-08 14:53 | 19 | 2019-12-10 11:35 | Electrical - Electrical Engineering General | 0 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | A mixture of Exane PC Class 2 & Class 5 has been installed for the DB-W-B05 Circuit 11L3
| 02SL - Stations (LUL) | Cxxx-NCR-001085 | NCR | WTH & ETH WB & EB Platform PES Lighting Circuits - Installation of Non-Compliant DIN Rail Terminal Connector Sizes in __ Platform Lighting Selectrabox (incl. DALI Connection) |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-12-24 | 2020-01-09 16:57 | 16 | 2019-12-10 15:54 | Electrical - Electrical Engineering General | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __ terminal blocks used for both the Lighting circuit and DALI circuit are not installed as per Cxxx-MCR-008013 PES Selectrabox. (1) Lighting Circuits: The MCR specifies that incoming Polyamide 6.6 terminals shall be able to accept 2 x 6mm cables. The terminals installed onsite are __ WDU6 DIN rail terminals which can only accept a maximum of 2 x 2.5mm cables. There are number of circuits wired in 4mm & 6mm in a loop-in loop-out configuration, therefore, not being compliant for the connector installed. (2) DALI Circuits: The MCR doesn't specify the terminal type and size, however, __ WDU2.5 DIN rail terminal have been installed which can accept 2 x 1.5mm cables. The DALI circuits are wired in 2.5mm on a loop-in loop-out configuration, therefore, not being compliant for the connector installed.
| 02SL - Stations (LUL) | Cxxx-NCR-001086 | NCR | EB & WB Platfrom (ETH & WTH) PES - Platfrom Lighting - Use of Polyamide DIN-Rail Connectors within Emergency Lighting __ Selectrabox |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-12-24 | 2020-01-09 11:18 | 16 | 2019-12-10 16:50 | Electrical - Electrical Engineering General | 0 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Polyamide DIN rail terminals have been used within the Emergency Lighting __ Selectrabox instead of the MCR approved and specified high temperature ceramic terminals.
| 02SL - Stations (LUL) | Cxxx-NCR-001087 | NCR | ETH L-5 Rm 6_681 Dist Board DB-E-B08 Incorrect Outgoing Circuit Cables Installed for 1L1, 3L1, 5L1, 10L1, 10L2 & 10L3 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-12-20 | 2020-01-13 08:46 | 24 | 2019-12-11 09:36 | Electrical - Electrical Engineering General | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Discrepancies have been found for DB-E-B08 outgoing circuits as follows: (1) Circuit 1L1 - Circuit has a mix of Exane PC Class 2 and Class 5 cables but should only should have one type installed; (2) Circuit 1L1 - Circuit has been wired to the 1st point from the DB in 2.5mm as per the __ calculations but from the 1st point on-wards the Line conductor has been wired in 4mm; (3) Circuit 10L3 - Circuit has a mix of Exane PC Class 2 and Class 5 cables but should only should have one type installed; (4) Circuit 10L3 - Circuit has been wired to the 1st point from the DB in 2.5mm as per the __ calculations but from the 1st point on-wards the Line conductor has been wired in 4mm; (5) Circuit 3L1 - Circuit has a mix of Exane PC Class 2 and Class 5 cables but should only should have one type installed; (6) Circuit 3L1 - Circuit has been wired in 4mm whereas the __ calculations specify 2.5mm; (7) Circuit 5L1 - Circuit has a mix of Exane PC Class 2 and Class 5 cables but should only should have one type installed; (8) Circuit 10L1 - Circuit has a mix of Exane PC Class 2 and Class 5 cables but should only should have one type installed; (9) Circuit 10L2 - Circuit has a mix of Exane PC Class 2 and Class 5 cables but should only should have one type installed;
| 02SL - Stations (LUL) | Cxxx-NCR-001090 | NCR | ETH L0 Colonnade, E-01-75-D01/D02- Steel work at incorrect location |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-01-31 | 2020-01-29 15:56 | -2 | 2019-12-12 07:49 | Architectural - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Located By __: The __ steel frame for doors E-01-75-D01 and D02 has been installed approx. 20mm too far towards Gridline D. If the __ doors are installed in the steel in its current location the bronze cladding fitted to the doors will be out of alignment with the cladding above the doorway.
| 02SL - Stations (LUL) | Cxxx-NCR-001091 | NCR | WTH, Level -5, Platform E/B from DB-W-A06 Dist Board Incorrect Outgoing Circuit Cables Installed for 1L2, 2L1, 9L3 & 10L1 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-12-24 | 2020-01-13 15:11 | 20 | 2019-12-12 08:41 | Electrical - Electrical Engineering General | 2000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | (1) Circuit 1L2 - 2.5mm cable has been installed whereas the specification (__) specifices 4mm; (2) Circuit 2L1 - Exane PC Class 2 and Class have been installed within the same circuit; (3) Circuit 9L3 - At fitting 45 2.5mm cable has been installed instead of 4mm as specified for this circuit (__); (4) Circuit 10L1 - Exane PC Class 2 and Class have been installed within the same circuit;
| 02SL - Stations (LUL) | Cxxx-NCR-001092 | NCR | ETH L0 Grid one, E-F Concrete upstands SSL poured high |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-01-06 | 2020-01-31 16:54 | 25 | 2019-12-12 08:56 | Civil - Civil Engineering General | 1500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | has surveyed the concrete upstands (bays 1-6 on gridline 1 (E-F)). We have found the finished reduced level of concrete (SSL) has been installed higher than design (ranging from 123.937 to 123.956m). This means we cannot get all of our tiling in to FFL of 124.000m. See attachments for more details. are proposing scabbling concrete to achieve sufficient room for: 1. Base of external tiling installed at a reduced level of 123.950m. Please confirm if a minimum cover of 25mm is permitted and any remedial actions that must apply to have this reduced cover.
| 02SL - Stations (LUL) | Cxxx-NCR-001093 | NCR | WTH -5 comms risor to -4 SC1 Damaged Fibre Cable |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-12-26 | 2020-04-09 13:41 | 105 | 2019-12-12 16:15 | Communications and Control Systems - Fibre Optic Network | 5000 |  | Damaged | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The below Cables have been found to have sever physical damage within Risor Cxxx-DAT-00202 Cxxx-DAT-00203
| 02SL - Stations (LUL) | Cxxx-NCR-001094 | NCR | ETH Level -5 Switchroom 3A 6/675 Dist Board DB-W-EL05 Damaged Neutral 6L3 (1st Leg) |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-12-20 | 2020-01-13 15:07 | 24 | 2019-12-12 16:41 | Electrical - Electrical Engineering General | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Dist Board DB-W-EL05 Circuit 6L3 neutral conductor from the Dist Board to the 1st Point has been damaged.
| 02SL - Stations (LUL) | Cxxx-NCR-001096 | NCR | ETH Level 0, Gridline 1 Gridline A (DC4), Earthing connection RC breakout |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-03-06 | 2020-07-01 13:07 | 117 | 2019-12-13 09:03 | Civil - Civil Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | The lighting protection earthing cables that extend out of the cantilever slab at GL B on GL 1 have been damaged. See attached sketch for location and photo.
| 02SL - Stations (LUL) | Cxxx-NCR-001097 | NCR | ETH EB & WB and WTH EB & WB - Labelling Installed Incorrectly to Platform Lighting __ Sockets |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-12-30 | 2020-01-13 08:55 | 14 | 2019-12-16 15:08 | Electrical - Electrical Engineering General | 0 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 1. Cable labels not installed to box covers as per JY82 and BS 7671; 2. Incorrect terminology used for labelling i.e. "E-EL08/1L3", where it should be "DB-E-EL08/1L3"; 3. Missing 230V Warning Labels as per JY82 and BS 7671.
| 02SL - Stations (LUL) | Cxxx-NCR-001098 | NCR | W030 Separate CPC not installed as per __ Calculation |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-01-31 | 2020-01-29 22:06 | -2 | 2019-12-16 15:51 | Electrical - General | 0 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Submain W030 has been installed not in accordance with Cxxx-SKC-E-XCL-Cxxx-50001 rev 14.0. Rev 14.0 of the aforementioned document indicated Submain W030 as 25 mm2 1 x 1 x 4c with a 35mm2 separate CPC. The Contractor has installed 70mm2 separate CPC instead of the required 35mm2.
| 02SL - Stations (LUL) | Cxxx-NCR-001099 | NCR | ETH, -5 Public Escape Route 6_230, Incorrect size trunking |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-01-23 | 2020-03-16 16:54 | 53 | 2020-01-09 16:08 | Electrical - Electrical Engineering General | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The seven compartment trunking installed in the public escape route (6/230) was suppose to be 700x50mm trunking with a 200mm comms compartment. However a 550mm trunking with a 50mm comms compartment was installed.
| 02SL - Stations (LUL) | Cxxx-NCR-001100 | NCR | UPS ATS-fixings not used with HY270 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-01-06 | 2020-07-24 11:44 | 200 | 2019-12-16 16:40 | Electrical - General | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Other | Completed |  | During an IRN site survey of UPS ATS, it has been observed that the __ fixings have not been used with the approved chemical resin, __ HY270. This affects the below ATS; • ATS BOS-W-UPS01 (W009/083) – IRN-E-50064 • ATS BOS-W-UPS02 (W003/052) – IRN-E-50065 • ATS BOS-E-UPS01 (E009/086) – IRN-E-50092 • ATS BOS-E-UPS02 (E003/052) – IRN-E-50093 The integrity of the fixing cannot be verified.
| 02SL - Stations (LUL) | Cxxx-NCR-001101 | NCR | W061 Separate CPC not installed due update of __ Calculation |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-12-31 | 2020-01-21 10:30 | 21 | 2019-12-17 08:31 | Electrical - Electrical Engineering General | 1000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | Submain W061 was installed at the point when the latest __ calculation report was rev 14.0 (document ref. Cxxx-SKC-E-XCL-Cxxx-50004). Rev 14.0 of the aforementioned document indicated Submain W061 as 50 mm2 1 x 1 x 4c without the need of separate CPC. Rev 15.0 of the aforementioned document indicated Submain W061 as 50 mm2 1 x 1 x 4c with a 16mm2 separate CPC.
| 02SL - Stations (LUL) | Cxxx-NCR-001102 | NCR | WTH L+6 EBDR ,Clash between booth door and screed level |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-12-18 | 2021-02-25 15:01 | 69 | 2019-12-18 07:33 | Architectural - General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Door Reference: W-G-795-D01 WTH - Vent Shaft - L+6 EBDR The floor finishes drawing does not show screed through the threshold of the structural opening of door W-G-795-D01. The door for this opening has been manufactured to the size of the structural opening (as per the attached door schedule and door survey). The current design subsequently causes a clash between the screed and door leaf.
| 02SL - Stations (LUL) | Cxxx-NCR-001103 | NCR | DB-E-EL08 & DB-E-EL09 Damaged Circuits |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-01-31 | 2021-01-31 10:59 | 366 | 2019-12-20 16:07 | Electrical - Electrical Engineering General | 2000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Cables found damaged within trunking in Circ Area 6/229 as follows: DB-E-EL08 - 6L1 & 4L2 DB-E-EL09 - 5L3
| 02SL - Stations (LUL) | Cxxx-NCR-001104 | NCR | Comms (PAVA) junction box is obstructing the PES Lighting __ socket |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2020-02-21 | 2020-02-24 09:02 | 3 | 2019-12-22 22:47 | Electrical - Lighting | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Comms (PAVA) junction box is obstructing the PES Lighting __ socket at Westbound Platform -5 between CP2 and CP5 (Speaker ref. Z17 B22). This will not allow the PES Light to be plugged into the socket without undue stress (See attached photos).
| 02SL - Stations (LUL) | Cxxx-NCR-001105 | NCR | Steel beam installed directly under __ socket making it inaccessible |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2020-01-05 | 2021-02-06 15:15 | 398 | 2019-12-22 23:03 | Electrical - Lighting | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Subcontractor Problems - Interfacing problems | Completed |  | A steel beam has been installed directly under a __ socket making it inaccessible (see attached photo). Location: WTH outside the lift on Level-5
| 02SL - Stations (LUL) | Cxxx-NCR-001106 | NCR | CRL not being Invited to Witness Live Testing of Submain Cables |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2020-01-31 | 2020-02-14 10:16 | 14 | 2019-12-22 23:12 | Electrical - Power Distribution | 0 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Inspection points not adequate | Completed |  | During the informal review of PCC documentation packs submitted by the Contractor, it was identified that the Project Managers Assurance team were not invited to witness the live testing of a number of Submain Cables. This constitutes a non-conformance to the CTP procedure (Cxxx-SKC-E-STP-Cxxx-50020, Rev 5.0) where the live testing of submain cables is a witness point for CRL. W105, W013, W061, W117, W072, W078, W007, E014, E017, E063 and E056 are some example submain cables were the Contractor proceeded with live testing without inviting the Project Managers Assurance team to witness.
| 02SL - Stations (LUL) | Cxxx-NCR-001107 | NCR | Dist Board DB-E-EL08 Mixture of Cable Types on SC1 Circuits 1L3, 8L1 & 8L2 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-01-31 | 2020-01-21 11:53 | -10 | 2019-12-23 08:26 | Electrical - Electrical Engineering General | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | ETH E/B Platform PES Lighting A mixture of Exane Circuit Safe and Firetec Tube Safe has been installed to DB-E-EL08 circuits 1L3, 8L1 & 8L2.
| 02SL - Stations (LUL) | Cxxx-NCR-001108 | NCR | PES Light Fitting Types Not Installed As Per Design and Approved MCR |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-12-31 | 2020-01-08 15:23 | 8 | 2019-12-23 08:36 | Electrical - Lighting | 0 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | PES Lighting East & Westbound __ SPL 901 Platform Screen PES Lightbox luminaires have been specified on the lighting layout drawings and within lighting calculations, whereas Selux Crossrail PES SPL 901/902 luminaires have been installed. MCR for Selux fitting - CRL-MCR-001624 which is currently not approved
| 02SL - Stations (LUL) | Cxxx-NCR-001109 | NCR | 12 x Platfrom Light Dist Board Circuitry Cross Contamination |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-12-24 | 2020-01-09 17:02 | 16 | 2019-12-23 08:47 | Electrical - Electrical Engineering General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | WTH & ETH East & Westbound Platforms Cross contamination of circuits and wiring within trunking systems within Circ Areas
| 02SL - Stations (LUL) | Cxxx-NCR-001110 | NCR | Dist Board DB-E-A08 Mixture of Cable Types to SC1 Circuits 5L1, 5L3, 10L3 & 11L2 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-12-31 | 2020-01-09 16:09 | 9 | 2019-12-23 08:59 | Electrical - Electrical Engineering General | 0 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | ETH Platform E/B A mixture of Exane PC Class 2 & Class 5 has been installed to DB-E-A08 circuits 5L1, 5L3, 10L3 & 11L2.
| 02SL - Stations (LUL) | Cxxx-NCR-001111 | NCR | Dist Board DB-E-UPS02 SC1 Circuit 5L3 Wired in Wrong Size |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2019-12-31 | 2020-01-28 13:10 | 28 | 2019-12-23 09:05 | Electrical - Electrical Engineering General | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | ETH Level -4 CER Room 2 Dist Board DB-E-UPS03 Circuit 5L3 has been wired in 4mm whereas the __ Schedule specifies 6mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001112 | NCR | EB & WB Platform And Staircase 8 - Testing of Permanent Assets Commenced Without Adhering to ITP/CTP Procedures |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-01-31 | 2020-11-06 10:05 | 280 | 2019-12-23 09:48 | Electrical - General | 5000 |  | Testing and Commissioning | Rework | 3 (3-6k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | The Platform Lights and ETH Staircase 8 Lights were dead and live tested without following the ITP/CTP procedures. The Submains and Final Circuits CTP Cxxx-SKC-E-STP-Cxxx-50020 rev 5.0 requires acceptance of IRN for DB’s and Final Circuits before proceeding to dead and live testing (see activity 2.0 in the CTP Plan).
| 02SL - Stations (LUL) | Cxxx-NCR-001113 | NCR | Cable E122 Damaged Cable Sheath |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-01-13 | 2020-01-06 17:29 | -7 | 2019-12-30 09:14 | Electrical - General | 1000 |  | Workmanship | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Cable sheath damaged to Cable E122
| 02SL - Stations (LUL) | Cxxx-NCR-001114 | NCR | Cable W124 Damaged Cable Sheath |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-01-13 | 2020-01-06 16:25 | -7 | 2019-12-30 09:28 | Consents - General | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The sheath of Cable W124 has been damaged at the Z end of the cable within the invert of Platform 7/121
| 02SL - Stations (LUL) | Cxxx-NCR-001115 | NCR | Rittal JBs For Cables E122, E123, W123 & W124 Installed Without Approved MCR |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-01-31 | 2020-01-13 15:15 | -18 | 2019-12-30 10:53 | Electrical - General | 0 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Rittal JBs have been installed within the Sub-Platform to allow the conversion of 4-Core cables to 2-Core to supply DBs DB-E-UPS07, DB-E-UPS08, DB-W-UPS06 & DB-W-UPS07. The conversion is required as the DBs fall under the Traction Earth System and not Station, therefore, the 2-spare cores had to be segregated with the JBs. Cxxx-RFI-005688 and associated Cxxx-FCD-001419 has been approved for the conversion, however, the Rittal JBs have yet to have an MCR submitted and approved.
| 02SL - Stations (LUL) | Cxxx-NCR-001116 | NCR | DB-E-A07, DB-E-B07 & DB-E-EL07 Incorrect Circuit Configuration (SC1) |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-01-31 | 2020-01-09 13:12 | -22 | 2020-01-02 09:17 | Electrical - Electrical Engineering General | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Normal and emergency fed lighting circuits have not been configured as per the stair lighting section detail drawing and instead they have been swapped around which means that the light fittings shown as fed by either A or B supplies are now fed by emergency supplies and vice versa throughout.
| 02SL - Stations (LUL) | Cxxx-NCR-001117 | NCR | ASD ( __ ) Pipework -No Earthbreaks Installed ( Platforms EB & WB ) |  | Crossrail | PDP | BOS - Bond Street Station (West) |  | 2020-01-19 | 2021-05-07 14:22 | 474 | 2020-01-05 09:26 | Fire - Fire Systems & General | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | Cxxx are aware of the requirement to install earth breaks at detailed locations within the platform areas, the breaks have been installed on the electrical CMS and tunnel & station firemains. CRL noted in early October 2019 that the earth breaks where missing on the ASD ( vesda pipework ) at both ends of the platforms, this pipework is situated at high level above the steel cladding. Drawings Cxxx-SKC-E-DWG-Cxxx-50815, 50816, 50824 & 50825 do not indicate the requirement for earth breaks so they have been missed. CRL have discussed this issue during the meetings held weekly with , they have also recently assisted with advising of suppliers for the required material. & the contractor __ now need to procure and install the earth breaks before the cladding is completed, retest, reinspections are required.
| 02SL - Stations (LUL) | Cxxx-NCR-001119 | NCR | ETH, Level 0 Bronze doors E-01-75-D01/D02 Paint Defects |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-02-07 | 2021-09-09 11:27 | 580 | 2020-01-08 13:46 | Architectural - Doors | 500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Very visible paint defects on both sides of the doors Left door inside jamb does not operate as it should when closing the door
| 02SL - Stations (LUL) | Cxxx-NCR-001120 | NCR | WTH, Level -5, CER 1 6/736 Dist Board DB-W-UPS04 3L2 & 3L3 - Incorrect Cable Size Installed |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-01-22 | 2020-01-21 21:12 | -1 | 2020-01-08 14:07 | Electrical - Electrical Engineering General | 1000 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | 6.0mm 3C FP600s cables have been installed instead of the specified 2.5mm 2C __ L-Sifer & 4.0mm 1C CPC.
| 02SL - Stations (LUL) | Cxxx-NCR-001121 | NCR | WTH AP2 WB Fire Main Thrust Bracket Damaged |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-01-22 | 2020-01-29 14:28 | 7 | 2020-01-08 14:54 | Mechanical - Mechanical Engineering General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | AP2 Tunnel Fire Mains Thrust bracket was struck by during steelwork installation
| 02SL - Stations (LUL) | Cxxx-NCR-001122 | NCR | WTH,Cxxx-RFI-004370, MH147 NCR - Additional Re-Bar Struck |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-02-20 | 2020-01-17 12:09 | -34 | 2020-01-09 11:46 | Civil - Civil Engineering General | 50 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | 1no. 275mm DIA core has cut: Top Matt: 2no. north-south reinforcement bars & 2no east-west. Conditions of RFI allowing for 1no.in each direction. Bottom matt: 1no. north-south reinforcement bar & 2no east-west. No conditions on bottom matt placed by RFI.
| 02SL - Stations (LUL) | Cxxx-NCR-001123 | NCR | BMS/PLC - MCC-E-05 - HTMD-001 - Damage to installed and signed off works |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-04-18 | 2020-01-22 20:24 | -87 | 2020-01-09 13:27 | Mechanical - Mechanical Engineering General | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Further to Cxxx-NCR-001055, additional damage has been caused to installed and signed off __ works. This has the potential to affect commissioning and PCC. Extent of damage: FFP-E-HTMD-001 isolator has been damaged. Please see attached BIM360 Report.
| 02SL - Stations (LUL) | Cxxx-NCR-001124 | NCR | Distribution boards within room 6/676 not installed as per elevation drawing |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-02-11 | 2020-01-13 16:15 | -29 | 2020-01-12 10:24 | Electrical - General | 0 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Distribution boards within room 6/676 have not been installed as per DB elevation drawing Cxxx-SKC-M-DDB-Cxxx-16408 (P07). Site measurements shown below; - DB-W-A05 to DB-W-A06 - 350mm gap between DB's (50mm increase). - DB-W-A06 to DB-W-A09 - 355mm gap between DB's (55mm increase). - DB-W-A09 to DB-W-B05 - 20mm gap between DB's (180mm decrease). - DB-W-B05 to DB-W-B06 - 350mm gap between DB's (50mm increase). As DB fixings are internal, changes will be illustrated on Cxxx-SKC-M-DDB-Cxxx-16408 (X01) which will seek approval of the changes made on site (Use As-Is).
| 02SL - Stations (LUL) | Cxxx-NCR-001125 | NCR | FCD 001437 - WTH - Rebar found within cover zone for opening W-01-792-D03 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-02-12 | 2020-01-29 16:57 | -14 | 2020-01-13 17:21 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Other management problem | Completed |  | FCD001437 prescribed solution was the scabbling of S/O W-01-792-D03 to provide the required S/O clearance for the door to fit. __ stated that the minimum clearance between rebar and the edge of the RC was 39mm. 20mm was to be extracted from the top of the opening. __ undertook the works a struck rebar within 15mm of the breakout. Rebar was cast within the minimum clearance zone of 30mm and hence was struck when breakout was carried out.
| 02SL - Stations (LUL) | Cxxx-NCR-001126 | NCR | Installtion of Additional JB to PES Lighting Circuit 10L1 DB-E-B09 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-01-29 | 2020-01-21 11:02 | -8 | 2020-01-15 08:06 | Electrical - Lighting | 3000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | An additional JB has been installed between DB-E-B09 and the 1st point on circuit 10L1 which is not part of the design or marked on any drawings.
| 02SL - Stations (LUL) | Cxxx-NCR-001127 | NCR | PES Light Fitting Glass Diffuser Shattered - DB-W-B05 Circuit 1L1 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-01-28 | 2021-07-21 10:47 | 540 | 2020-01-14 14:19 | Electrical - Lighting | 1000 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The glass diffuser to one of the PES light fittings on circuit 1L1 of DB-W-B05 has been damaged giving the appearance of being shattered.
| 02SL - Stations (LUL) | Cxxx-NCR-001128 | NCR | PTE - Missing Pressure Relief Drainage Outlets |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-02-14 | 2020-01-24 16:49 | -21 | 2020-01-15 09:10 | Civil - Civil Engineering General | 0 |  | Damaged | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | 5 of 11 transverse pressure relief drainage termination points on the platform side of the Eastern ticket hall non public platform have been covered by concrete.
| 02SL - Stations (LUL) | Cxxx-NCR-001129 | NCR | ETH TVS route -Evaporation chambers function not fulfilled |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-12-01 | 2021-05-07 12:58 | 157 | 2020-01-14 17:16 | Civil - Civil Engineering General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | It is unclear what events occurred prior to the decision to remove the 125mm cast in drain pipes from the cavity drains behind the upstand. The understanding currently* we have is __ were either informed or believe that the TVS fans would be active 24/7. Drainage pipework has subsequently being removed as a result of the formal response provided by the unknown party, refer to Cxxx-SKC-P-DDA-Cxxx-52236 C02. - *Further investigation into the historical information is being carried out. are co-ordinating a design to ensure that the drainage channels within the TVS and Draught Relief areas have a fully drained system, this will supersede Cxxx-PWK-00747 as the drainage voids are to be utilised to complete the drainage system within these areas. Additionally any leaks within levels -2 & levels -3 of the TVS and Drainage as per Cxxx-PWK-00703 will be catered for within the new drainage system
| 02SL - Stations (LUL) | Cxxx-NCR-001130 | NCR | NCR, WTH, -4 Service zone 5/788, Trunking installed on same run by different manufacturers |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-01-29 | 2020-06-12 15:57 | 135 | 2020-01-15 12:26 | Electrical - General | 0 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | The trunking installed by __ in the -4 WTH service area (5/788) on the same run is by two different manufacturers. The two manufacturers are __ and __.
| 02SL - Stations (LUL) | Cxxx-NCR-001131 | NCR | Unable to Install Curved Signage 735 due to GFRC Panels Installed to Incorrect Configuration on Westbound Platform-CP8 to10 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-02-16 | 2020-02-07 11:03 | -9 | 2020-01-17 11:50 | Architectural - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | NCR raised by: __ The signage sub contractor was unable to install the remaining curved signage Ref 735 on the westbound platform located between cross passages CP8 & 10 (see attached location plan for clarity) as the space provided between the GFRC sub structure was NOT in accordance with the Cxxx drawing issued to the GFRC sub contractor. The GFRC sub contractor installed a bespoke row of GFRC panels at the location where the sign was required in lieu of a standard 1450mm wide row of GFRC panels. A 1450mm wide row of GFRC panels should have been installed between CP8 to 10 to accommodate the signage panel install as per GFRC configuration drawing Cxxx-SKC-A-DWG-Cxxx-50481 Rev 06 (dated Oct 2016), Rev 07 (dated Aug 2017) and all drawing revisions proceeding these. The red line drawing submitted also highlights that this row of GFRC panels should consist of 1450mm wide panels to accommodate the sign install.
| 02SL - Stations (LUL) | Cxxx-NCR-001132 | NCR | Lack of MCR for E-01-76-D01 - SC1 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-02-16 | 2020-01-29 16:02 | -18 | 2020-01-17 14:26 | Architectural - Doors | 500 |  | Documentation and Records | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The Subcontractor is to provide the MCR for E-01-76-D01
| 02SL - Stations (LUL) | Cxxx-NCR-001133 | NCR | Water Ingress Corroding Electrical Containment ETH |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-02-15 | 2021-07-06 14:22 | 507 | 2020-01-20 10:35 | Electrical - Cable Management | 5000 |  | Design | Rework | 3 (3-6k) | Complete | External Phenomenon - Other | Completed |  | ETH 3/800, 3/785, 4/934, 4/800, 4/963 .In the areas highlighted, water has seeped through the blockwork and has over time corroded CMS and switches. The effected areas wilol need to be replaced, but this works cannot take place until the seepage ceases. If the seepage is to be accepted, then the electrical design will need to be amended to allow for the presence of water.
| 02SL - Stations (LUL) | Cxxx-NCR-001134 | NCR | non maintainable conduit installation level -2 3/904 pressurisation fan room |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-02-07 | 2020-01-30 18:39 | -8 | 2020-01-20 10:46 | Materials - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | NCR raised for poor workmanship, conduits boxes are for cable ways for a rewireable system and future maintenance
| 02SL - Stations (LUL) | Cxxx-NCR-001135 | NCR | Incorrect Size of "Z" Profile Installed at Some Platform PHP Cabinets (P&T) |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-02-19 | 2021-04-01 13:02 | 407 | 2020-01-20 16:09 | Architectural - General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Raised By __ ) The contractor noted last week w/c 13/01/20 on site that the height of the stainless steel "Z"-profiles installed at the top of each platform PHP Cabinet is NOT in accordance with the attached drawing Cxxx-SKC-A-DWG-Cxxx-51035 Rev 12 at some PHP cabinet locations (see attached photos for clarity). The measurement specified on the drawing is 24mm but at some locations in can be in excess of 50mm. 2) In addition, where the correct height of "Z"-profile is installed at PHP cabinets, an unacceptable gap is present between the bottom of the GFRC panels and the stainless steel "Z"-profile. This is also not in accordance with the drawing Cxxx-SKC-A-DWG-Cxxx-51035 Rev 12 which indicates a lap of approx. 4mm between both items. The contractor is aware that some of these GFRC panels have only been installed temporarily at the moment but these panels have been aligned correctly with adjacent panels suggesting that any final adjustment of the panels later would not rectify this issue. It also seems that the bottom of some of the panels installed have a curved edge in lieu of specified horizontal edge which may be the cause of the unacceptable gaps.
| 02SL - Stations (LUL) | Cxxx-NCR-001136 | NCR | Damage to Mounting Flange of Sump Panes WTH -6/SP001 and SP002 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-02-07 | 2020-12-10 16:54 | 307 | 2020-01-20 19:02 | Materials - General | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | The mounting flanges on 2no. Sump Pump panels have been broken off during lifting operations to get them into the inverts
| 02SL - Stations (LUL) | Cxxx-NCR-001137 | NCR | E-05-96-D02 - Damaged door leaf beyond repair |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-02-20 | 2020-09-25 10:18 | 218 | 2020-01-21 14:36 | Architectural - Doors | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Subcontractor Problems - Problems with execution, workmanship, or supervision | Completed |  | E-05-96-D02 - Damaged door leaf beyond repair
| 02SL - Stations (LUL) | Cxxx-NCR-001138 | NCR | Door schedule and Opening Schedule do not align - W-03-681-D01 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-02-20 | 2020-11-10 16:15 | 264 | 2020-01-21 16:09 | Architectural - Doors | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | Door schedule and wall opening schedule do not align and have resulted in a wall opening being formed 90mm too large for the manufactured door
| 02SL - Stations (LUL) | Cxxx-NCR-001139 | NCR | EH051 – Reinforcement struck contrary to Cxxx-RFI-003940 conditions. |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-04-12 | 2020-07-08 16:32 | 87 | 2020-03-13 09:00 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | WTH-4, 5/795.N 152mm core has cut 1no vertical and 1no. horizontal bar on both faces of wall 5/795.N. Conditions of RFI being to avoid doing so. Occurred despite wall __.
| 02SL - Stations (LUL) | Cxxx-NCR-001140 | NCR | SC1 Main Earthing - Installing to Non-IFC Earthing Schematics |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-02-06 | 2020-02-07 11:34 | 1 | 2020-01-23 15:48 | Electrical - Earthing & Bonding | 0 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Use of unapproved drawings | Completed |  | The installation of the SC1 required Main Earthing has been against Non-IFC Earthing Schematics: - Cxxx-SKC-E-DDE-Cxxx-16000 P19 - Cxxx-SKC-E-DDE-Cxxx-16001 P02
| 02SL - Stations (LUL) | Cxxx-NCR-001141 | NCR | 25% CMS Spare Capacity Not Maintained WTH Level -5, SIDs 6/673, 6/072 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-02-28 | 2020-03-13 13:46 | 14 | 2020-01-27 11:36 | Electrical - Cable Management | 0 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Failure to comply with the works information and maintain 25% spare capacity on CMS. Sections of CMS where the installation deviates from the requirement are identified in the attached SK-E-00236 Response to -RFI-010888.pdf.
| 02SL - Stations (LUL) | Cxxx-NCR-001142 | NCR | East Bound and West bound PES: Damaged Antennas, LUL East, CRL East, LUL West and CRL West |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-03-31 | 2020-11-04 14:07 | 218 | 2020-01-27 14:40 | Communications and Control Systems - SCADA/Central Management System | 5000 |  | Damaged | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | The following antennas are subject to damage: LUL East Bound, ANT 3123 ANT 3126 ANT 3127 ANT 3056 CRL East Bound, ANT 123 ANT 124 ANT 126 LUL West Bound, ANT 3131 ANT 3061 ANT 3063 ANT 3064 ANT 3066 CRL West Bound ANT 130
| 02SL - Stations (LUL) | Cxxx-NCR-001143 | NCR | Installation of Main Earth Bars - Discrepancy Between __ EB Schedule and As-Installed |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-02-10 | 2020-09-21 15:46 | 224 | 2020-01-27 15:25 | Electrical - Earthing & Bonding | 0 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | There is a discrepancy on a number on Main Earth Bars (MEBs) where the __s MEB Schedule (within EMP Cxxx-SKC-E-STP-Cxxx-50001 Rev 12.0) specify a number of connections ways to the that installed. For example __'s schedule specifies 8-connections ways and 2-disconnection links, whereas, 6-connection ways and 2-disconnection links have been installed. With the forthcoming Rev 13 of the EMP will request that __'s to carry out a check to ascertain the number of ways required. Refer to -RFI-01875. If any remedial works are required this will be carried out during the March '20 Construction Window.
| 02SL - Stations (LUL) | Cxxx-NCR-001144 | NCR | PAVA Zone 17 Damaged Speakers. Zone 17 on the Westbound platform: Speaker Z17/A15, Z17/C17, Z17/D18, Z17/C19 and showing actual damage. |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-02-11 | 2020-11-04 14:20 | 267 | 2020-01-28 09:42 | Communications and Control Systems - SCADA/Central Management System | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | We have come across few damaged speakers. Zone 17 on the Westbound platform: Speaker Z17/A15, Z17/C17, Z17/D18, Z17/C19 and showing actual damage. Please refer to pictures.
| 02SL - Stations (LUL) | Cxxx-NCR-001145 | NCR | WTH, -3, 3/132 Lift 7 Control Room, A&B Reversed Supplies |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-02-28 | 2020-02-16 09:01 | -12 | 2020-01-28 15:10 | Electrical - Electrical Engineering General | 0 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Standard practise sitewide for the ATS supply cables installation has the A supply cable on the left hand side and B supply cable on the right hand side. Lift 7 ATS unit has the cables reversed and if the cable are swapped to the correct orientation the B supply cable will be short and this cable runs back to the main LV switchroom on level-5.
| 02SL - Stations (LUL) | Cxxx-NCR-001146 | NCR | Fan Isolation Damper Actuators serving ETH FFP, ETH & WTH OPE fan sets do not achieve RFI Cxxx-RFI-005775 response |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-02-11 | 2020-12-09 16:15 | 302 | 2020-01-28 15:05 | Mechanical - Mechanical Engineering General | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Not Defined | Completed |  | The installed damper actuators serving ETH FFP, ETH & WTH OPE fan sets do not meet the maximum drive duration of 60 Seconds noted in RFI Cxxx-RFI-005775. The installed actuators require replacement and compliance with RFI to be re-witnessing to CRL once replacement works are completed. Locations where replacements are required – ETH – Room 3/904 (FFP fan sets 01 & 02), ETH – Room 5/775 (OPE fan sets 01 & 02) and WTH Room 3/769 (OPE fan sets 01 & 02).
| 02SL - Stations (LUL) | Cxxx-NCR-001147 | NCR | ETH, ESS7,Outstanding Stair/Landing Repair |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-03-25 | 2020-03-09 12:16 | -16 | 2020-02-24 17:21 | Architectural - General | 5000 |  | Damaged | Repair | 3 (3-6k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | to carry out repair to outstanding damaged or cracked Stairs or stairs landing on ETH as per repair procedure for NCR-001037 Stair ESS7
| 02SL - Stations (LUL) | Cxxx-NCR-001148 | NCR | WTH Accessibility Issues to Supplementary Earth Bars SEB-W-B3-01 & SEB-W-B4-03. LV Switchroom III (5/675) & LV Switchroom IIIa (3/675) |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-02-28 | 2020-07-20 12:23 | 143 | 2020-01-30 15:15 | Electrical - Electrical Engineering General | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | 2 x Supplementary Earth Bars have been installed as per the design drawings but have accessibility issues. See attached pictures and drawings for locations
| 02SL - Stations (LUL) | Cxxx-NCR-001149 | NCR | Corroded CMS Support Fixings at ETH -2 3/800 |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2020-02-13 | 2021-07-06 14:19 | 509 | 2020-01-30 19:18 | Electrical - Cable Management | 2000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | During a site walk with for SC1 readiness of ETH -2 3/800 TVF Fan room. It was found that the fixings to the CMS for the dampers were corroded (see attached photos and location detail).
| 02SL - Stations (LUL) | Cxxx-NCR-001150 | NCR | ETH version of Cxxx-NCR-001044 - "ETH Level -5 - __ have installed gas fire suppression trunking that is not approved" |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-01-31 | 2020-02-03 11:59 | 3 | 2020-01-30 19:25 | Fire - Fire Systems & General | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | __ have installed gas fire suppression trunking that is not approved or on the MCR register ETH Level -5 6/682, 6/076, 6/686
| 02SL - Stations (LUL) | Cxxx-NCR-001151 | NCR | Gas Fire Suppression Electronic Bells have been installed without an approved MCR, |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-02-29 | 2020-02-12 09:29 | -17 | 2020-01-30 19:33 | Fire - Fire Systems & General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Procedure Problem - Lack of procedure | Completed |  | Gas Fire Suppression Electronic Bells have been installed without an approved MCR, ETH and WTH Level -5
| 02SL - Stations (LUL) | Cxxx-NCR-001152 | NCR | Gas Fire Suppression Pipework - sleeves surrounding the pipe work into the TX rooms is unacceptable |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-03-06 | 2020-06-01 14:14 | 87 | 2020-01-30 19:48 | Fire - Suppression | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The above sleeve that has been fitted to the pipe passing through the wall far exceeds the maximum allowed 75mm protrusion. Therefore, it is not possible to verify that the fire stopping material is in line with the compartment line. The diameter also appears excessive.
| 02SL - Stations (LUL) | Cxxx-NCR-001153 | NCR | Supplementary Earth Bar SEB-W-B5-07 - Earth Link Can't Open Fully |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-02-29 | 2020-10-21 15:10 | 235 | 2020-01-31 15:20 | Electrical - General | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Earth link cant open fully as it's obstructed by SWA cables WTH LV Switchroom IIIb 6/688
| 02SL - Stations (LUL) | Cxxx-NCR-001154 | NCR | BMS Terminal Box above the LV Switchboards are not Suitably IP Rated |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2020-12-01 | 2020-11-29 14:12 | -2 | 2020-02-01 00:48 | Electrical - Power Distribution | 20000 |  | Incorrect Installation | Rework | 2 (6-60k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The BMS Terminal Box's on top of all four LV Switchboards are not suitably IP rated and will require re-working.
| 02SL - Stations (LUL) | Cxxx-NCR-001155 | NCR | ETH -5 - AP3 Cantilever Baseplate / Alternative Fixings |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-03-31 | 2020-02-14 15:51 | -46 | 2020-02-03 08:55 | Architectural - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | With reference to Cxxx-SKC-A-DWG-Cxxx-53604 Rev. C01 (and the attached location sketch), it was not possible to install the specified expansion anchors, as the slab on site was not fully poured, refer to Cxxx-NCR-000803 and Cxxx-RFI-005579.
| 02SL - Stations (LUL) | Cxxx-NCR-001156 | NCR | ETH - 5/398 Water Mist Fire Suppression Pipework |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-03-04 | 2022-01-31 08:30 | 698 | 2020-02-04 09:51 | Fire - Fire Systems & General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Previous Construction - Problems based on previous construction errors | Completed |  | Pipework is installed with insufficient support and is not level in numerous locations throughout the installation: - Lack/No brackets throughout all pipework - Drains not connected to gully as per west - IVs not able to terminate as too close to couplings - Lack of Drain cocks - Is gully fit for purpose? - Lack of split washers throughout - __ installed in gully - As galv, copper and expansion device weren't installed could not make comments on these.
| 02SL - Stations (LUL) | Cxxx-NCR-001157 | NCR | ETH Level 0 - E-01-75-D01 & E-01-75-D02 - Incorrect Fixing |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-02-25 | 2020-05-22 14:03 | 87 | 2020-02-04 16:38 | Architectural - Doors | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | Incorrect fixings installed on steel door frames E-01-75-D01 & E-01-75-D02.
| 02SL - Stations (LUL) | Cxxx-NCR-001158 | NCR | WTH -5_397 Water Mist Fire Suppression Pipework |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-03-04 | 2022-01-31 08:28 | 698 | 2020-02-05 11:05 | Fire - Fire Systems & General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Previous Construction - Problems based on previous construction errors | Completed |  | Pipework is installed with insufficient support and is not level in numerous locations throughout the installation. - Not enough brackets from tank on pipework - Pipework from tank installed at angle - No brackets around set on left as well as before tee before plinth - Nearly all __ installed on angle - Lack of drain points throughout install - AAV should be installed on copper - Not enough brackets on galvanised pipework at high level - Is gully fit for purpose? - Ladder only supported on one leg - Wiring to IVs not started - No brackets below manifold - Expansion vessel in walk way - Skid not fixed to ground in all points - Lack of split washers throughout - Clarification on removal of pumps - Feed from tank is running up hill and its gravity fed - Threaded rod used instead of pipe clips or u blots
| 02SL - Stations (LUL) | Cxxx-NCR-001159 | NCR | WTH L-5 AP2 EB side - Wiring within Multi-Compartment Trunking |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-02-19 | 2020-08-24 16:21 | 187 | 2020-02-05 17:03 | Electrical - Electrical Engineering General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Cross contamination and excess slack left on cables at WTH Level -5 AP2 EB side
| 02SL - Stations (LUL) | Cxxx-NCR-001160 | NCR | Conduit Box Extensions Being Modified to Accommodate Cabling & __ Socket Outlets |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-02-14 | 2021-02-26 10:33 | 378 | 2020-02-06 08:52 | Electrical - General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Design Problem - Error in equipment or material selection | Completed |  | Conduit extension boxes, box lids and conduit boxes have been modified to try and accommodate lighting circuitry and __ sockets. The cabling has been squeezed and pinched. The boxes have been site adapted poorly. ETH Level -5 6/773 & 6/102
| 02SL - Stations (LUL) | Cxxx-NCR-001161 | NCR | ETH, A_133 LER, FF Lift 6, ATS, Supply Healthly Indication Operation |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-02-28 | 2020-02-18 14:39 | -10 | 2020-02-07 09:48 | Electrical - Electrical Engineering General | 100 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Information not detailed | Completed |  | 1. The 'Supply Healthy' Lamp currently fitted to the ATS does not Illuminated when ATS is operating in Manual Mode. 2. The 'Supply Healthy' label differs from the schematic which states 'System Healthy'
| 02SL - Stations (LUL) | Cxxx-NCR-001162 | NCR | WTH L-5 Crossrail not being invited to witness live testing of submain cable W056 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-02-28 | 2020-02-19 20:52 | -9 | 2020-02-11 12:31 | Electrical - Electrical Engineering General | 0 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Inspection points not adequate | Completed |  | During the informal review of PCC packs submitted by the contractor, it was identified that the Project Managers Assurance team were not invited to witness the Dead and Live testing of Submain cable W056. This constitutes a non-conformance to the CTP procedure ( Cxxx-SKC-E-STP-Cxxx-50020) where Dead and Live testing of a submain cable is a witness point for CRL.
| 02SL - Stations (LUL) | Cxxx-NCR-001163 | NCR | WTH L-5 Crossrail not being invited to witness live testing of submain cable E017 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-02-28 | 2020-03-02 13:38 | 3 | 2020-02-11 16:01 | Electrical - Electrical Engineering General | 0 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | During the informal review of PCC packs submitted by the contractor, it was identified that the Project Managers Assurance team were not invited to witness the Dead and Live testing of Submain cable E017. This constitutes a non-conformance to the CTP procedure ( Cxxx-SKC-E-STP-Cxxx-50020) where Dead and Live testing of a submain cable is a witness point for CRL.
| 02SL - Stations (LUL) | Cxxx-NCR-001164 | NCR | WTH L-5 Crossrail not being invited to witness live testing of submain cable W103 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-02-28 | 2020-02-19 21:06 | -9 | 2020-02-11 16:11 | Electrical - Electrical Engineering General | 0 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Inspection points not adequate | Completed |  | During the informal review of PCC packs submitted by the contractor, it was identified that the Project Managers Assurance team were not invited to witness the Dead and Live testing of Submain cable W103. This constitutes a non-conformance to the CTP procedure ( Cxxx-SKC-E-STP-Cxxx-50020) where Dead and Live testing of a submain cable is a witness point for CRL.
| 02SL - Stations (LUL) | Cxxx-NCR-001165 | NCR | WTH L-5 Crossrail not being invited to witness live testing of submain cable W102 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-02-28 | 2020-02-26 09:18 | -2 | 2020-02-11 16:22 | Electrical - Electrical Engineering General | 0 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Inspection points not adequate | Completed |  | During the informal review of PCC packs submitted by the contractor, it was identified that the Project Managers Assurance team were not invited to witness the Dead and Live testing of Submain cable W102. This constitutes a non-conformance to the CTP procedure ( Cxxx-SKC-E-STP-Cxxx-50020) where Dead and Live testing of a submain cable is a witness point for CRL.
| 02SL - Stations (LUL) | Cxxx-NCR-001166 | NCR | WTH L-5 Crossrail not being invited to witness live testing of submain cable W054 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-02-28 | 2020-02-27 17:16 | -1 | 2020-02-11 16:30 | Electrical - Electrical Engineering General | 0 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Inspection points not adequate | Completed |  | During the informal review of PCC packs submitted by the contractor, it was identified that the Project Managers Assurance team were not invited to witness the Dead and Live testing of Submain cable W054. This constitutes a non-conformance to the CTP procedure ( Cxxx-SKC-E-STP-Cxxx-50020) where Dead and Live testing of a submain cable is a witness point for CRL.
| 02SL - Stations (LUL) | Cxxx-NCR-001167 | NCR | ETH Lobby 6_102 -5 Damage to Speaker |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-02-26 | 2020-09-18 01:13 | 205 | 2020-02-12 11:56 | Communications and Control Systems - SCADA/Central Management System | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Procedure Problem - Defective or inadequate procedure | Completed |  | Speaker; Z40- A25, Lobby 6/102 -5 ETH, damage to speaker.
| 02SL - Stations (LUL) | Cxxx-NCR-001168 | NCR | ETH Level -2 Circ/Lobby 3_98 Parallel Conduits |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-03-13 | 2021-01-27 17:41 | 320 | 2020-02-12 12:46 | Electrical - Electrical Engineering General | 5000 |  | Incorrect Installation | Rework | 3 (3-6k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | __ have installed parallel conduits from the circulation area to the tunnel ventilation fan room
| 02SL - Stations (LUL) | Cxxx-NCR-001169 | NCR | Terminal Connector Blocks on MCC Field Devices not Fixed |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2020-03-02 | 2021-10-01 15:48 | 578 | 2020-02-17 09:21 | Electrical - General | 0 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | During formal inspections of the field devices from the MCC panels it has been noted that the terminal connector blocks have not been fixed and have been left floating (see example photo). This has been installed in this manner in various locations across the station, primarily in the MCC plant rooms.
| 02SL - Stations (LUL) | Cxxx-NCR-001170 | NCR | Temporary LFEPA (Ch5) radio system not fit for purpose |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2019-10-20 | 2020-10-19 13:03 | 365 | 2020-02-17 08:41 | Communications and Control Systems - Radio | 500 |  | System Defect | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During the commissioning of Routeway radio services Engineers reported heterodyning whilst passing the BOS box that significantly impaired LFEPA performance. Subsequent testing by Cxxx found the root cause of this interference to be the BOS LFEPA (Ch5) temporary radio system and this problem was also prevalent across platform areas of BOS. Such interference matters should have been reported during regularly radio systems checks and ongoing maintenance, these procedures seems to be lacking.
| 02SL - Stations (LUL) | Cxxx-NCR-001171 | NCR | Incorrect Fixing used on Glass Panel CMS at Platform Level -5 |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2020-03-01 | 2021-05-01 02:38 | 426 | 2020-02-16 12:36 | Electrical - Cable Management | 0 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Following a CRL inspection it was found that incorrect fixings have been used on the Glass Panel CMS at Platform Level -5 (see attached photo and email). The fixing method used is not as per the FCD details (see Cxxx-FCD-001266 linked). In addition the fixing detail installed is not listed in the fixing matrix (Cxxx-SKC-E-RGN-Cxxx-50470 REV 1.0).
| 02SL - Stations (LUL) | Cxxx-NCR-001172 | NCR | WTH L-5 AP2 EB side and Outside CER - Wiring within Multi-Compartment Trunking |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2020-03-01 | 2021-02-26 14:29 | 362 | 2020-02-16 18:53 | Electrical - General | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Supervision - Insufficient supervision | Completed |  | Cxxx-EWN-04304 required an NCR to be raised for the poor quality issues identified in the wiring installation at circulation area outside CER1 and AP2 WTH Level -5 (Areas highlighted on pdf drawings attached). Cxxx-NCR-001159 was raised in regards to the cross contamination and slack on the cables. This NCR is raised for the following: • Cables pulled very tight past trunking sets and bends - lidding will not be achieved in current state • Cables have been graunched and insulation damaged during wiring installation • Trunking is dirty with swarf, dust and screws within A report with photo evidence has been attached for further details.
| 02SL - Stations (LUL) | Cxxx-NCR-001174 | NCR | ETH - Crossrail not being invited to witness live testing of submain cable E066 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-03-03 | 2020-03-02 13:48 | -1 | 2020-02-18 13:39 | Electrical - Electrical Engineering General | 0 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Inspection points not adequate | Completed |  | During the informal review of PCC packs submitted by the contractor, it was identified that the Project Managers Assurance team were not invited to witness the Dead and Live testing of Submain cable E066. This constitutes a non-conformance to the CTP procedure ( Cxxx-SKC-E-STP-Cxxx-50020) where Dead and Live testing of a submain cable is a witness point for CRL.
| 02SL - Stations (LUL) | Cxxx-NCR-001175 | NCR | WTH - Crossrail not being invited to witness live testing of submain cable W017 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-03-03 | 2020-03-02 13:57 | -1 | 2020-02-18 13:50 | Electrical - Electrical Engineering General | 0 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Inspection points not adequate | Completed |  | During the informal review of PCC packs submitted by the contractor, it was identified that the Project Managers Assurance team were not invited to witness the Dead and Live testing of Submain cable W017. This constitutes a non-conformance to the CTP procedure ( Cxxx-SKC-E-STP-Cxxx-50020) where Dead and Live testing of a submain cable is a witness point for CRL.
| 02SL - Stations (LUL) | Cxxx-NCR-001176 | NCR | LV Busbar Trunking System E01,E02,E051 A&M |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-12-04 | 2021-02-06 11:25 | 64 | 2020-02-20 10:17 | Electrical - Electrical Engineering General | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | Aconex: -NCR-000700. Location: ETH Level -4 SR LV I & II to Level -5 SR HV I & HV II A non-compliance has been found against Main LV Busbar Trunking Systems E01, E002 & E051 support bracketry and access for maintenance purposes. A&M is impacted due to the following: 1. The bus trunking system is not independently supported 2. Current installation does not facilitate the easy removal of trunking parts, i.e. without disturbance of other adjacent assets - other cables etc.
| 02SL - Stations (LUL) | Cxxx-NCR-001178 | NCR | COMMS PA/VA CABLES HAVE BEEN ROUTED THROUGH WRONG SLOT COMPARTMENT ON CMS TOP HAT MECHANITE CARD |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-03-06 | 2020-08-05 16:48 | 152 | 2020-02-21 14:49 | Communications and Control Systems | 1000 |  | Supervision/Management | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | COMMS PA/VA CABLES HAVE BEEN ROUTED THROUGH WRONG SLOT COMPARTMENT ON CMS TOP HAT MECHANITE CARD ETH +0.5 CIRCULATION AREA
| 02SL - Stations (LUL) | Cxxx-NCR-001179 | NCR | ETH Chilled Water Pipework - Prefab Welding |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-05-21 | 2020-06-09 13:03 | 19 | 2020-02-21 17:04 | Mechanical - Mechanical Engineering General | 2000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Chilled water header pipework in the ETH Chiller room has been prefabricated off site to an insufficient standard. The welding does not meet BS EN 10253-1 and BS EN 10253-2.
| 02SL - Stations (LUL) | Cxxx-NCR-001180 | NCR | (P&T) Removal of Lighting Boxes from Previously CRL Approved PES Benchmark (Westbound Platform) |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-03-25 | 2021-02-24 16:24 | 336 | 2020-02-24 13:51 | Architectural - General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | It was noted by CRL during a site walk around that some of the lighting boxes within the approved PES architectural benchmark have been removed without any prior warning to undertaken additional works requested by CRL.
| 02SL - Stations (LUL) | Cxxx-NCR-001181 | NCR | ETH L-4 Crossrail not being invited to Witness live testing of Submain Cable E044 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-03-18 | 2020-11-19 17:28 | 246 | 2020-02-26 08:38 | Electrical - Electrical Engineering General | 0 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Inspection points not adequate | Completed |  | During the informal review of PCC packs submitted by the contractor, it was identified that the Project Managers Assurance team were not invited to witness the Dead and Live testing of Submain cable E044. This constitutes a non-conformance to the CTP procedure ( Cxxx-SKC-E-STP-Cxxx-50020) where Dead and Live testing of a submain cable is a witness point for CRL.
| 02SL - Stations (LUL) | Cxxx-NCR-001182 | NCR | ETH L-3 Plant Supply Fire damper PS-E-FD022 access blocked by CMS |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2020-03-11 | 2021-02-07 17:09 | 333 | 2020-02-26 10:23 | Mechanical - Heating Ventilation & Air Conditioning | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | ETH L-3 Plant Supply Fire damper PS-E-FD022 access blocked by CMS IRN: IRN-M-50059
| 02SL - Stations (LUL) | Cxxx-NCR-001183 | NCR | WTH L-1 room 2/767 Ancillary Supply Duct – Access door blocked by light fitting. |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2020-03-11 | 2021-04-27 06:49 | 412 | 2020-02-26 10:47 | Mechanical - Heating Ventilation & Air Conditioning | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | WTH L-1 room 2/767 Ancillary Supply Duct – Access door blocked by light fitting. IRN: IRN-M-50025
| 02SL - Stations (LUL) | Cxxx-NCR-001184 | NCR | WTH L-2 Access Doors blocked by CMS along side wall near mcc panel |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2020-11-03 | 2020-11-03 10:50 | 0 | 2020-02-26 13:47 | Mechanical - Heating Ventilation & Air Conditioning | 0 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | WTH L-2 PSE room. Blocked access to hatches near mcc panel Room 3_769 General Extract RN: Cxxx-SKC-M-NOX-Cxxx-50033 Ancillary Supply IRN: Cxxx-SKC-M-NOX-Cxxx-50025
| 02SL - Stations (LUL) | Cxxx-NCR-001185 | NCR | Missing __ TDS for ETH Level +0.5 ATS Fire Fighting Lift Control Panel LFT-01 100A |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-03-25 | 2020-06-08 13:51 | 75 | 2020-02-26 14:05 | Electrical - Electrical Engineering General | 500 |  | Testing and Commissioning | Rework | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | __ to produce and issue test data sheets for ETH Level +0.5 ATS Fire Fighting Lift Control Panel LFT-01 100A
| 02SL - Stations (LUL) | Cxxx-NCR-001187 | NCR | Civil Engineering Drawings Redlined but not in eB |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2020-03-16 | 2022-05-27 09:29 | 802 | 2020-03-02 12:33 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Change to drawings not provided on time | Completed |  | The following drawings were Redlined and given to Crossrail to review. However these drawings are not in eB: 1. Cxxx-SKC-S-DWG-Cxxx-50617 P01 2. Cxxx-SKC-S-DWG-Cxxx-50477 P01 3. Cxxx-SKC-S-DWG-Cxxx-50892 C02 4. Cxxx-SKC-S-DWG-Cxxx-50269 C04
| 02SL - Stations (LUL) | Cxxx-NCR-001188 | NCR | ETH-Corridors Resin L-1, L-2, L-3 , MNS 8 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-04-02 | 2021-04-23 14:03 | 386 | 2020-03-03 16:47 | Architectural - Flooring | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | Resin was applied to the corridors of the ETH on part of level 0, All of level -1, -2 & -3. However the quality of the work was poor
| 02SL - Stations (LUL) | Cxxx-NCR-001189 | NCR | Dist Board DB-E-UPS02 - Dist Board transit not slotted as per Benchmark |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-03-06 | 2020-03-05 09:21 | -1 | 2020-03-04 08:55 | Electrical - Electrical Engineering General | 0 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Worker not correctly instructed | Completed |  | The transit from the header trunking into Dist Board DB-E-UPS02 has not been slotted as set out within the Dist Board Benchmark document Cxxx-SKC-E-LRC-Cxxx-50698 Rev. 1.0 The current transit has two separate slots not joining, therefore, reducing the capacity of cables being installed into the DB. CER II (5/732) ETH Level -4
| 02SL - Stations (LUL) | Cxxx-NCR-001190 | NCR | __ - ETH Entrance Fin (Module) |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-03-19 | 2020-04-23 06:58 | 35 | 2020-03-05 08:20 | Architectural - General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Not Defined | Completed |  | Fabrication/Assembly Issue resulting in deformed Fins (photo attached). Damage was noticed after installation.
| 02SL - Stations (LUL) | Cxxx-NCR-001191 | NCR | ETH L-4, DB-E-UPS-02/9L1 & DB-E-UPS-04/2L2, 5L1 Incorrectly wired |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-03-19 | 2020-08-08 11:46 | 142 | 2020-03-05 16:41 | Electrical - Electrical Engineering General | 3000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Outgoing final circuits: DB-E-UPS-02/9L1 & DB-E-UPS-04/2L2, 5L1 not wired to the latest approved design. ( Cxxx-FCD-001467, Cxxx-FCD-001469 & Cxxx-FCD-001108 & redline Cxxx-SKC-E-DDA-Cxxx-62140 Rev X04)
| 02SL - Stations (LUL) | Cxxx-NCR-001193 | NCR | Access issues to TLPP at Bond St EB Platform Eastend |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-05-18 | 2020-11-30 10:39 | 196 | 2020-03-06 08:03 | Architectural - General | 1000 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Cxxx-SKC-A-DDA-Cxxx-52151 P14 shows the location of demountable handrails installed by Cxxx near the Cxxx TLPP distribution cabinet. The location of these demountable sections have been agreed in Cxxx-SKC-O-RGN-Cxxx-50184 GIR31 Tunnel Walkway areas And Platform Ends. On Wednesday 12th February 2020, Cxxx maintenance operatives were unable to carry out the maintenance on the TLPP panel at Bond St EB platform East end because they were allowed to open the door but not go behind the yellow barriers (see attached pictures and markup).
| 02SL - Stations (LUL) | Cxxx-NCR-001194 | NCR | CMS not accessible service riser 2/931 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-03-23 | 2022-03-11 16:09 | 718 | 2020-03-09 12:07 | Electrical - Cable Management | 1000 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | CMS has been installed within riser and has blocked access to maintain or install for future requirements
| 02SL - Stations (LUL) | Cxxx-NCR-001195 | NCR | Temp Light Fitting and Trunking Lid resting on LV Cables |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-03-23 | 2020-04-30 14:33 | 38 | 2020-03-09 12:29 | Electrical - General | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Material/Preservation Problems - Improper preservation of material after installation | Completed |  | Temp light fitting and trunking lid resting on LV Cables (see attached photo) at WTH Level -5 Corridor outside CER.
| 02SL - Stations (LUL) | Cxxx-NCR-001196 | NCR | Normal and Emergency trunking compartments not segregated outside WTH CER |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-03-13 | 2021-02-11 10:51 | 335 | 2020-03-09 16:21 | Electrical - Cable Management | 1000 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | The transit between the 2 x trunking systems has been damaged, therefore, there is no segregation where emergency circuits pass from their respective compartment of the into another trunking. The emergency circuits cross over the top of normal compartment as per attached picture.
| 02SL - Stations (LUL) | Cxxx-NCR-001197 | NCR | Earth and Submain Cables not adequately dressed on to CMS tray - WTH Level -5 Corridor outside CER |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-03-13 | 2021-02-06 10:38 | 330 | 2020-03-09 17:35 | Electrical - Cable Management | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Earth and Submain Cables not adequately dressed on to CMS tray (see attached photo).
| 02SL - Stations (LUL) | Cxxx-NCR-001198 | NCR | Dead and Live Test carried out without a signed IRN (ETH & WTH CER UPS DB Final Circuits) |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2020-03-24 | 2020-11-21 11:09 | 242 | 2020-03-10 12:37 | Electrical - Power Distribution | 5000 |  | Testing and Commissioning | Rework | 3 (3-6k) | Complete | Procedure Problem - Other | Completed |  | Under the current certification process, dead and live testing is carried out at PCC. However the ETH & WTH CER UPS DB's (02 and 04) final circuits were dead and live tested without a signed IRN. Furthermore, following the dead tests it was found that some of the outgoing circuits from DB-E-UPS-02 did not go to the correct isolators as per the FCD design. A separate NCR has been raised for this (see Cxxx-NCR-1191), these circuits will now require rework invalidating the test results.
| 02SL - Stations (LUL) | Cxxx-NCR-001199 | NCR | Dead Test carried out without a signed IRN (WTH Coffer Lights DB Final Circuits) |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2021-03-31 | 2021-01-28 14:52 | -62 | 2020-03-10 12:38 | Electrical - Power Distribution | 0 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Inspection points not adequate | Completed |  | Under the current certification process, dead testing is carried out at PCC. However the WTH Coffer Lights DB final circuits were dead tested on 5th March without a signed off IRN.
| 02SL - Stations (LUL) | Cxxx-NCR-001200 | NCR | Dali belcom cabling damage |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-03-20 | 2021-01-25 17:11 | 311 | 2020-03-10 14:08 | Electrical - General | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Dali belcom cable installed damage to core sleeving conductor exposed EHT ESS8, level-4 to level -3.5
| 02SL - Stations (LUL) | Cxxx-NCR-001201 | NCR | ETH Access Panels to chiller duct osbsured by CMS |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2020-03-25 | 2021-04-27 15:44 | 398 | 2020-03-11 14:56 | Mechanical - Heating Ventilation & Air Conditioning | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Design Problem - Not Defined | Completed |  | The chiller exhaust ductwork at high level in the ETH chiller plant room level 0 has been obscured by electrical CMS and has precluded access to the panels.
| 02SL - Stations (LUL) | Cxxx-NCR-001202 | NCR | Client Signature Duplicated over multiple ITPs |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-04-13 | 2020-09-25 11:39 | 165 | 2020-03-12 16:53 | Civil - Civil Engineering General | 0 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Other management problem | Completed |  | Duplicate of Crossrail signatures within __ ITP check sheet (Cxxx-SKC-O4-ITP-Cxxx-50130 Rev 3.0).
| 02SL - Stations (LUL) | Cxxx-NCR-001203 | NCR | Dead and Live Test carried out without a signed IRN (4x Platform UPS DB's) |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2020-03-30 | 2020-09-07 16:16 | 161 | 2020-03-16 10:07 | Electrical - Power Distribution | 3000 |  | Testing and Commissioning | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Inspection points not adequate | Completed |  | Under the current certification process, dead and live testing is carried out at PCC. However the Platform UPS DB's (DB-E-UPS07, DB-E-UPS08, DB-W-UPS06 and DB-W-UPS07) were dead and live tested without a signed IRN. In addition following the inspection of the four DB's carried out on the 13th of March, a number of CAT A snags were found, see attached CRL email with list of snags for each DB. These snags were identified after the DB's had been energised.
| 02SL - Stations (LUL) | Cxxx-NCR-001204 | NCR | Incorrect Fixing location of __ door fixing |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-04-15 | 2020-12-22 10:03 | 251 | 2020-03-16 10:07 | Architectural - Doors | 1500 |  | Manufacturing Defect | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The __ door fixing location is clashing with the web of the door support steelwork. This has been caused by the fixing hole in the frame being manufactured in the incorrect location - see attached mark up with proposed solution (yet to be accepted by __). This has been made worse by framework being installed in the incorrect locations. Doors are located in ETH & WTH L-5: W-06-674-D01 W-06-678-D01 W-06-733-D01 W-06-410-D01 W-06-734-D01 W-06-576-D01 W-06-72-D01 W-06-406-D01 E-06-691-D01 E-06-692-D01 E-06-107-D01
| 02SL - Stations (LUL) | Cxxx-NCR-001205 | NCR | AP1, level -3,Concrete Collar, Guidance in Cxxx-RFI-005833 not followed |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-04-17 | 2020-03-24 17:18 | -24 | 2020-03-16 15:17 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | Cxxx-RFI-005833 proposed to break back 5x isolated locations of a Reinforced Concrete LU asset in AP1. The asset being the RC collar that abuts the SGI rings and SCL interface in AP1. 8x isolated locations have been broken back instead of the agreed 5. Additionally, in one location (location 4) a larger area was broken out than what was agreed. Location 3 remedial works has resulted in a small 70mm long vertical reinforcement bar being exposed. This has since been treated with __ paint. See photos attached. Additional breakout 4 is on the east/right hand side and is: 10mm deep x 150mm x 560mm W Additional location 6 is on the east/right hand side and is: 10mm deep x 300mm H x 150mm W Additional location 7 is on the west/left hand side and is: 25mm deep x 200mm H x 100mm W Additional location 8 is on the west/left hand side and is: 20mm deep x 160mm H x 150mm W No rebar has been damaged or exposed in these 4 x additional locations. Regarding location 7, an additional 10mm deep x 50mm H x 50mm W breakout is required to the northern side to compensate for a fixing that falls along the cut line of the concrete which has been broken out. See attached mark up.
| 02SL - Stations (LUL) | Cxxx-NCR-001206 | NCR | Damage to 110V circuity cables (within conduit installation) ETH, L0 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2021-06-01 | 2021-04-16 14:45 | -46 | 2021-03-05 10:11 | Electrical - General | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Damage to 110v cables found; cables are within conduit installation through back entry conduit box. See photos of damage attached.
| 02SL - Stations (LUL) | Cxxx-NCR-001207 | NCR | ETH- L-3 Upstands , PWK 374 Missing Documentation |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-04-18 | 2020-10-20 16:15 | 185 | 2020-03-18 15:43 | Civil - Civil Engineering General | 500 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | NCR 098 was raised to cover the incorrect continuity strip on level -3 upstands. PWK 107 was raised to cover the remaining upstands that were not inspected. PWK 374 was raised as PWK 107 was closed in error. This NCR has been raised as the documentation for the remaining upstands has been lost.
| 02SL - Stations (LUL) | Cxxx-NCR-001210 | NCR | Dist Board DB-W-FFL Damaged Door |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-04-03 | 2020-03-27 16:19 | -7 | 2020-03-20 15:21 | Electrical - General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Dist Board DB-W-FFL door has been damaged LCC (LER) 3/131)
| 02SL - Stations (LUL) | Cxxx-NCR-001211 | NCR | ETH -0 Tech Wall – Not Adhering To ITP And Proceeding To Wire Without CRL intervention Hold Points. |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2020-04-09 | 2022-01-25 15:45 | 656 | 2020-03-26 16:52 | Electrical - Cable Management | 0 |  | Supervision/Management | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Inspection points not adequate | Completed |  | During a formal inspection on the ETH -0 Tech Wall it was seen that have installed cabling into the CMS trunking/ conduits without CRL intervention sign off. Therefore, the contractor has not adhered to the ITP Surveillance requirements and an NCR will be raised as a result. to be brief out to supervision that all CMS should be signed off by CRL in accordance with the ITP intervention hold points before wiring commences.
| 02SL - Stations (LUL) | Cxxx-NCR-001212 | NCR | ETH -0 Tech Wall – Damaged Single Core Insulation within CMS Trunking |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2020-04-09 | 2021-11-24 10:20 | 594 | 2020-03-26 12:54 | Electrical - General | 1000 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On a formal IRF CMS inspection CRL FAE noticed that 1 single core cable (Brown 4mm - Circuit unknown) had a deep burn mark damage to the cable insulation. Likely cause was cables being pulled in on top of this cable causing friction. The location can been seen within the attached photo for the ETH Tech Wall trunking. Although visually only 1 cable was seen to be damaged which requires replacing, a in-depth inspection will be required by Quality Assurance to mitigate other damage.
| 02SL - Stations (LUL) | Cxxx-NCR-001213 | NCR | Use of Pre-Galvanised __ Channel on site |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2020-05-05 | 2021-02-03 15:16 | 274 | 2020-03-26 17:14 | Electrical - Cable Management | 0 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Verification Problems - Other | Completed |  | On a visual informal inspection carried out in the ETH Chiller room -0 it was noticed that Pre-Galvanised __ channel support systems has been used for MEP services. As this does not comply with JY63.1304 a NCR will be raised as a result of the findings. It has also been seen that multiple areas throughout the project has Pre-Galv __ installed instead of HDG.
| 02SL - Stations (LUL) | Cxxx-NCR-001214 | NCR | ETH -0. Trunking Top Hat Cable Protection Within Tech Wall Area |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2020-04-25 | 2021-05-19 13:10 | 389 | 2020-03-26 17:43 | Electrical - Cable Management | 500 |  | Workmanship | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | On a formal IRF inspection of the ETH Tech Wall where had not adhered to the ITP inspection hold process, it could be seen that __ had wired single core cables through a top hat for a change in direction of trunking. On closer inspection the top hat mechanite was not visible nor did the opening compartments have sufficient spacing around the edges to protect the cables from damage on the metal corners. This snag was captured on the BIM 360 report made on site with Q.A's. will must provide CRL with a suitable alternative solution to protect the cables given that the ITP hold point had not been adhered to and they now have cables drawn into the sections of trunking.
| 02SL - Stations (LUL) | Cxxx-NCR-001215 | NCR | P&T WTH W/B Frame 2 PES End nuts not fully engaged on to bolts |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-08-20 | 2020-04-17 13:49 | -125 | 2020-03-25 16:40 | Civil - Civil Engineering General | 0 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following the inspection of the Frame 2 bolted connections into the soffit 2 nuts were found to be not fully located onto their respective bolts. These can be seen in the attached markup and photos: Cxxx-SKC-A-DWG-Cxxx-51791 Markup.pdf, Frame 2 issue 1.jpg, Frame 2 issue 2.jpg. (For location of Frame 2 refer to the attached Platform Layout.pdf)
| 02SL - Stations (LUL) | Cxxx-NCR-001217 | NCR | ETH, L0, Lift 6 to capture the SC1 element of Cxxx-NCR-000703 |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-05-01 | 2020-12-18 12:10 | 231 | 2020-03-27 10:47 | Civil - Civil Engineering General | 0 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | This NCR serves to capture the SC1 element (Lift 6) within Cxxx-NCR-000703. At Lift 6 level zero, 3no. cores (2no. 35mm DIA & 1no. 150mm DIA) were initially missing with coring then approved within Cxxx-NCR-000703. Following Post Core inspection, procedural Cxxx-NCR-000806 was raised as it was noted that: - Checksheet (EH181) for pre-core works not complete - NCR advice not followed with alternative core works carried out, (2x52mm diameter cores instead of 1x152mm diameter core) - The 2x32mm diameter cores were very close together. The thought being too close for horizontal rebar to pass between the cores and maintain any type of cover - Unable to confirm if the 2x32mm diameter cores cut rebar as the internal surfaces of the core have now been painted covering the core surfaces.
| 02SL - Stations (LUL) | Cxxx-NCR-001218 | NCR | Defective GFRC panel on Eastbound Platform (next to CP3) |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-04-30 | 2021-11-09 13:00 | 558 | 2020-03-30 15:53 | Architectural - General | 500 |  | Manufacturing Defect | Rework | 4 (0.5-3k) | Complete | External Phenomenon - Other | Completed |  | Several of the large rectangular GFRC panels have developed a mottled pattern on the face of the panels (see attached photos). (Franz Maidl) have reviewed these panels on site with Luke Williams () and agreed to clean the panels to see if the imperfections wash out.
| 02SL - Stations (LUL) | Cxxx-NCR-001219 | NCR | Distribution Board IP Rating Not Maintained |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-04-27 | 2020-07-26 11:17 | 90 | 2020-03-31 07:14 | Electrical - Electrical Engineering General | 0 |  | Material | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Other | Completed |  | Failure to comply with the works information performance requirements and maintain stated Index Protection rating of distribution equipment . ETH Level -4 CER 5/732 & WTH Level -5 6/736
| 02SL - Stations (LUL) | Cxxx-NCR-001220 | NCR | AP2/AP3 steelwork for JJS Doors installed out of tolerance |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-04-28 | 2021-02-05 16:22 | 283 | 2020-03-31 08:38 | Architectural - General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Incorrect installation of fire boarding on some door frames in AP2 & AP3 has led to the doors being out of tolerance ( tolerance requirements = +/- 6mm). In these locations the installation operatives have used either 9mm or 20mm boards incorrectly.
| 02SL - Stations (LUL) | Cxxx-NCR-001221 | NCR | Frame 1: __s 20mm too high (Eastbound Platform: Western End) |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-04-30 | 2020-10-14 14:20 | 167 | 2020-03-31 09:52 | Architectural - General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | The Contractors site team have identified that the vertical unistruts installed on Frame 1 (WTH:EB) are 20mm too long.
| 02SL - Stations (LUL) | Cxxx-NCR-001222 | NCR | Use of Class2 and Class 5 cables in same circuit |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-04-14 | 2020-03-31 15:54 | -14 | 2020-03-31 09:37 | Electrical - General | 0 |  | Incorrect Installation | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Work not properly planned | Completed |  | The contractor has identified the use of Class 2 and Class 5 cables in the same circuit across approximately 92 circuits and 22 distribution boards.
| 02SL - Stations (LUL) | Cxxx-NCR-001223 | NCR | WTH - Damaged Damper Control Isolator |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2020-05-10 | 2021-04-15 13:57 | 340 | 2020-03-31 14:03 | Electrical - LV Equipment | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Material/Preservation Problems - Damaged material | Completed |  | On a general walk observation through the WTF -4 it was noted that W-B04/11L1 has sustained damage to the front of the isolator. The locking off bracket and leaver has broken off, there's no visibility of broken parts nearby. to ensure all assurance checks are completed in line with ITP checks (__ INS 008) when renewed. Drawing attached for location and damage information.
| 02SL - Stations (LUL) | Cxxx-NCR-001224 | NCR | AP2 ,Level -5, Uncoordinated winch point design |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-05-03 | 2021-04-09 15:56 | 341 | 2020-04-03 11:38 | Civil - Civil Engineering General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Conflicting information on drawings | Completed |  | In AP2 we have an issue where two of the pits do not align with the tiling module and the frame of the hatch would not be fully supported. You will notice in the attached" winch point proposal photo" that two winch points are in the incorrect position. However, W-06-88-H01 has now been realigned with the tile module. When broke out the concrete slab to allow for the hydroduct plinth works (as per detailed in -RFI-004685) this allow us to realign the winch point opening with the tiling module upon completion of works. The issue with W-06-88-H02 has not been resolved. This slab opening is much deeper (600mm width x 600mm length x 600mm deep). propose to break out approx. 250mm of the slab to re-aligned the winch point with the tiling module. To ensure the hatch frame is supported on both side, we will require to shutter and pour a small concrete inwall on the adjacent side (approx.. 250mm width x 600mm length x 600mm depth). Typical winch point details are shown in drawing Cxxx-SKC-A-DDD-Cxxx-35802. Can CRL please approval to re-align winch point W-06-88-H02, including details of the required rebar to fix and tie-in with the existing concrete slab.
| 02SL - Stations (LUL) | Cxxx-NCR-001225 | NCR | ETH L-4 & L-5,Mastic gap between door frame and fireboard less than 3mm (doors E-05-732-D01 & E-06-736-D01) |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-05-06 | 2020-05-14 06:57 | 8 | 2020-04-06 15:17 | Architectural - Doors | 500 |  | Incorrect Installation | Rework | 4 (0.5-3k) | Complete | Management Problem - Other management problem | Completed |  | Installation of fireboard to lintel support bracket has resulted in a mastic gap between fireboard and door frame to be less than the 3mm requirement as specified in mastic MCR Cxxx-SKC-A-MCR-Cxxx-50380 Rev 1.0. Although the gap is less than 3mm, mastic has been documented as installed to the correct depth of 15mm by the fire mastic installer.
| 02SL - Stations (LUL) | Cxxx-NCR-001226 | NCR | ETH Cast in Embedment Plates IFC Drawings not issued on eb |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-05-09 | 2020-10-06 16:14 | 150 | 2020-04-09 08:19 | Civil - Civil Engineering General | 0 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | The drawings for the embedment plates which are cast in, to the ETH level+1 beams, ref. Cxxx-SKC-A-LRG-Cxxx-50280 (1.0), were not issued as IFC on eb. The drawings were approved by __ (Code A) and (Code 2) by Crossrail as rev. P
| 02SL - Stations (LUL) | Cxxx-NCR-001227 | NCR | ETH L-2 & L-5,Mastic gap between door frame and blockwork/RC less than 3mm (doors E-03-764-D01 & E-06-91-D02) |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-05-07 | 2021-01-06 10:52 | 244 | 2020-04-07 13:01 | Architectural - Doors | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Doors installed in these structural openings have resulted in areas where gaps between door frame and blockwork/RC are less than 3mm. JJS fire detail specifies doors should be installed with a gap not smaller than 3mm and not greater than 20mm.
| 02SL - Stations (LUL) | Cxxx-NCR-001228 | NCR | ETH L-5 DB-E-EL09 Circuit 3L1 - Cable Damaged |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-05-15 | 2020-06-03 14:22 | 19 | 2020-04-08 11:04 | Electrical - Electrical Engineering General | 500 |  | Damaged | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Defective construction | Completed |  | Following an inspection on DB-E-EL09, it was found that the SWA cable within circuit 3L1 has minor damage to the outer armouring.
| 02SL - Stations (LUL) | Cxxx-NCR-001229 | NCR | FCD not closed out before RC pour went ahead, (Cxxx-FCD-000711 - ETH Cantilever + L-0 B6) |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-04-23 | 2020-05-29 10:54 | 36 | 2020-04-08 15:49 | Civil - Civil Engineering General | 0 |  | Documentation and Records | Repair | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | This NCR has been raised as Cxxx-FCD-000711 was not closed out before the concrete pour went ahead. FCD text as follows: "During the construction of the cantilever slab it was noted that some bars have been duplicated across two RC drawings related to the end of B6 L-0. Therefore have marked up the attached drawings detailing which bars have been duplicated and therefore not installed. In addition there are 2 questions which require confirmation. These have been discussed and agreed between L. Snape (Cxxx) and W. Maddumage Don (Cxxx) 1. Where bars E114/E118/E119 on 50003 do not have couplers in the capping beam to thread into, the bars will be installed with __ Hit 200Y-A with B25 bars given 400mm embedment and B20 bars with 350mm embedment. 2. To form the bobbed end in the 15 No. B40 bars M__ couplers will be used, this is due to the couplers in the capping beam not allowing bobbed bars to be installed. It is confirmed that all 15 No. B40 couplers were found and the bars installed as shown on "Cxxx-SKC-S-DWG-Cxxx-50003-C01-LS-Markup-280917" Could Cxxx review the above.
| 02SL - Stations (LUL) | Cxxx-NCR-001230 | NCR | WTH, Level -5, NPP, WB- Adjusting TLPP cabinet to avoid clash with CMS |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-04-17 | 2020-05-02 06:26 | 15 | 2020-04-08 16:29 | Architectural - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | At the WTH WB Non-Public platform we have a clash between the already installed CMS tray and the ceiling of the TLPP cabinet. The CMS tray had already been installed and contains 'live' fibres. The ceiling could not be installed without altering the existing CMS and cables. The TLPP cabinets have two layers of durasteel ceiling, therefore the subcontractor proposed to slope the top layer of durasteel backwards to avoid the clash with the tray. This is only visual from the side of cabinet and doesn't reduce the working space required within the cabinet.
| 02SL - Stations (LUL) | Cxxx-NCR-001231 | NCR | ETH L-1, Mastic gap between door frame and RC more than 20mm (door E-02-91-D01) |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-05-09 | 2020-05-28 19:47 | 19 | 2020-04-09 14:13 | Architectural - Doors | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | Installation of a door in this structural opening has resulted in gaps between door frame and RC that exceed 20mm. JJS fire detail specifies doors should be installed with a gap not smaller than 3mm and not greater than 20mm. Fire mastic has already been applied to this door.
| 02SL - Stations (LUL) | Cxxx-NCR-001232 | NCR | Installation of associated cables to IRN-E-50092 based on unapproved MCR |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-05-09 | 2021-09-10 10:35 | 489 | 2020-04-13 17:09 | Electrical - General | 0 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Material/Preservation Problems - Use of unapproved materials | Completed |  | Through __ IRN Audit check list it has been identified that the installation of associated cables to IRN-E-50092 is based on unapproved MCR (CRL-MCR-008319). The MCR is still at initiate stage pending compliance evidence with LU 1-085 as requested through the review process. Note - MCR 8391 has been cancelled, MCR 9351 is now approved (JOC 10/09/2021)
| 02SL - Stations (LUL) | Cxxx-NCR-001233 | NCR | WTH L0 RC Upstands - Missing As-Built Survey |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-04-30 | 2020-04-14 15:47 | -16 | 2020-04-14 11:39 | Civil - Civil Engineering General | 0 |  | Documentation and Records | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Work organization/planning deficiency | Completed |  | RC upstands cast at WTH L0 Grid 1/C-L, L/1-2, 4/C-G have not had an as built survey carried out to confirm with tolerances prior to being covered by architectural finishes. Refer to: Cxxx-__-S-DDL-Cxxx-11100 Rev C11 MU for location
| 02SL - Stations (LUL) | Cxxx-NCR-001234 | NCR | ETH EB, PES End Wall, L-5, Frame 3 Head plate bolts alteration |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-05-17 | 2020-10-23 10:59 | 159 | 2020-04-14 15:59 | Architectural - General | 500 |  | Incorrect Installation | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | Due to access restrictions at this location, the subcontractor is unable to install the nut at one of the head plate fixing locations at Frame 3 (ETH EB PES End). The subcontractor has proposed a new fixing location to be installed within a range of 130mm-200mm from the existing location, of which can be easily accessed to install. The photo attached labelled 'Frame 3 original position' shows the fixing location that operatives could not gain access to on site to tighten a nut. This is further shown on drawing labelled 'Identified Anchor'. The photo labelled 'Model showing new fixing location' shows the range of which the new bolt can be relocated along the axis from the original position. The structural calcs have been undertaken within Cxxx-SKC-A_XCL-Cxxx-50067 to verify this new fixing location. Frame 3 head plate location also shown on 'Extract from drawing 51792
| 02SL - Stations (LUL) | Cxxx-NCR-001235 | NCR | AP3, Level -5, Head plate connection offset modified design at lift lobby |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-06-26 | 2020-10-16 12:25 | 112 | 2020-04-21 08:48 | Architectural - General | 500 |  | Design | Repair | 4 (0.5-3k) | Complete | Design Problem - Inadequate or defective design | Completed |  | A 100x100x8 square hollow section used as a packer to offset the connection due to the restricted access to physically drill fixing due to CMS, and close distance the edge of the RC wall.
| 02SL - Stations (LUL) | Cxxx-NCR-001236 | NCR | Damged Acoustic Louvres on L+0.5, L+1 and L+2 WTH Chiller Room |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2021-04-20 | 2021-05-26 09:56 | 36 | 2020-04-21 10:42 | Architectural - Glazing | 500 |  | Damaged | Repair | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | Damage to various WTH Chiller Room acoustic louvres on levels +0.5, +1 and +2
| 02SL - Stations (LUL) | Cxxx-NCR-001237 | NCR | E-05-597-D01- Door manufactured incorrectly |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-05-13 | 2020-09-18 14:14 | 128 | 2020-04-22 16:54 | Architectural - Doors | 500 |  | Manufacturing Defect | Use As-Is | 4 (0.5-3k) | Complete | Management Problem - Inadequate supervision | Completed |  | E-05-597-D01 was manufactured incorrectly - see attached mark ups
| 02SL - Stations (LUL) | Cxxx-NCR-001238 | NCR | PAVA Zone 29 Western Ticket hall Lift Lobby 6/088 Architectural drawing and Cxxx drawing misalignment |  | Crossrail | XRL | BOS - Bond Street Station (West) |  | 2020-10-31 | 2020-09-25 10:35 | -36 | 2020-04-28 14:08 | Communications and Control Systems - Public Address Systems | 500 |  | Design | Use As-Is | 4 (0.5-3k) | Complete | Design Problem - Drawing, specification, or data errors | Completed |  | In recent design workshops at __ offices it was noted that there is a misalignment between Cxxx architectural layouts Cxxx-SKC-A-DDA-Cxxx-21155P and __ design layouts for PAVA speakers Zone 29 A1, B2, A3, B4, A5, Cxxx-SMN-R3-DDA-Cxxx_6-40001 in the lift lobby western ticket hall. Cxxx are providing panelling for PAVA speakers as per attached drawing within the lighting boom. This shows 4 speakers in close proximity down one side of the lobby closest to the lift with a substantial gap to the last speaker Z29/A5. The distance is approx. 8 - 9 metres. This Spacing does not match __ design and has been highlighted as an issue by the __ design engineers who attended the meeting. ( Haroon Ahmed)
| 02SL - Stations (LUL) | Cxxx-NCR-001239 | NCR | (P&T) Excessive Gap Between Section of Floor Skirting & Adjacent GFRC Panels (CH 2/ES 1) |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-05-29 | 2021-10-28 07:06 | 517 | 2020-04-29 08:36 | Architectural - General | 500 |  | Design | Rework | 4 (0.5-3k) | Complete | Discipline/Workmanship - Not Defined | Completed |  | NCR raised by __ There is currently a gap of approx 30-40mm between the back of a section of floor skirting and adjacent GFRC between the bottom of ES 1 escalator and the Fire Extinguisher Cabinet as highlighted on the attached location drawing. The gap is in excess of the gap shown on the Cxxx & Cxxx architectural drawings and will need to be rectified accordingly.
| 02SL - Stations (LUL) | Cxxx-NCR-001240 | NCR | __ UPS Cxxx-EWN-04357 units 001,002,003 and 004 ETH and WTH |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-07-31 | 2021-10-01 15:02 | 427 | 2020-04-30 13:48 | Electrical - Electrical Engineering General | 1000 |  | Design | Rework | 4 (0.5-3k) | Complete | Design Problem - Other | Completed |  | Cxxx-EWN-04357 The Contractor writes further to Cxxx-RFI-005174 ["RFI 5174"] raised on the 20/03/19 to raise concerns and seek advice on the routing of the aforementioned cables through the “wire way” (Transition Cabinet) of the __ UPS units 001,002,003 and 004. As per RFI 5174, the transition cabinet currently has LV Cables and DC Circuits running within, as well as the 400V DC busbar which in its current state imposes high potential risk to electric shock owing to insufficient barriers/splash guards. The Contractor advises that the Project Manager's response to RFI 5174 states: “the incoming cables are dressed in such a way that the AC and DC are not mixed, and in some cases the T1 has added tray work to enhance segregation. At some point the AC & DC cables will be in close proximity just before the point of termination within the UPS, at no point are the cables twisted together or cross over. The BMS cables are generally contained within a Copex sleeve running from a gland through the cabinet away from the DC Busbars past the main terminations into a chamber within the UPS.” Further Cxxx-RFI-005828 [RFI 5828] states: “Although the response and direction of how to proceed is relating to the BMS cables, are requesting advice for the Comms Cxxx Cables on how to proceed with the Comms cabling to the __ UPS units. I have attached current photos of the __ Transition Cabinets for information and clarity.” The Project Manager's response to RFI 5828 states: “EMC assessment needs to be carried out” Although the Contractor agrees that an electromagnetic compatibility assessment is, in part, one aspect of conformity, it is not limited to this response. The Contractor lists below several British Standards which deviate from BS 7671 and Crossrail specifications that the __ UPS units in their current configuration therefore also deviate from. Furthermore, the Contractor raises concerns with the expected maintenance regime in relation to the safe isolation of the UPS units. Current understanding of the safe isolation to the UPS units includes the manual wraparound bypass, where this is to completely isolate the UPS unit to make it safe to carry out maintenance/repairs. It is now understood that the DC busbar contained within the transition cabinet is not isolated under these conditions and remains live, which, without taking extensive isolation methods/procedures, may mean that we are at risk of putting ourselves in breach of the Electricity at Work Regulations 1989 Part II. Provision 7. Provision 12. Provision 14. This matter has been discussed between the Contractor's representatives C. Brown and C. Lesslie and the Project Manager's representatives J. O'Connor, D. Desmond and K. Alom.
| 02SL - Stations (LUL) | Cxxx-NCR-001241 | NCR | ETH LV Switch Room 1V 6_681. DB-E-A09 - M10 Bolt DB Fixing Inaccessible |  | Contr | SKC | BOS - Bond Street Station (West) |  | 2020-05-28 | 2020-06-02 15:50 | 5 | 2020-05-14 08:27 | Electrical - Electrical Engineering General | 0 |  | Workmanship | Use As-Is | 4 (0.5-3k) | Complete | Discipline/Workmanship - Other | Completed |  | During a site inspection on DB-E-A09 (IRN-E-50359), it was observed that 2no. M10 DB fixings are inaccessible as CMS has been installed adjacanet to the DB which overlay the fixings. For access and maintenance purposes, to remove/replace the DB, it will require the partial removal of the CMS tray prior in order to access the M10 DB fixings.